Draft

Format and Content Elements for the

OPERATION PLAN SUMMARY

As specified by the Executive Director of the

California Public Utilities Commission

Under Section 8.3.1 of General Order 167

Background: The Operations Plan, the Operations Plan Summary, and the Recommendation of the Standards Committee

As described by General Order (GO) 167, Section 8.2.1:

An Operation Plan is a paper or electronic document that shows how the Generating Asset Owner’s operation practices and policies comply with each Operation Standard for each Generating Asset.  The Operation Plan may be in the form of a narrative, index, spreadsheet, database, web site, or other form.  The Operation Plan shall specifically identify the procedures and criteria that are used to comply with each Operation Standard.  Existing equipment manuals, checklists, warranty requirements, and other documents may be identified to demonstrate compliance.  If any of these documents are contradictory, the Operation Plan should resolve the contradiction.  Where the Generating Asset Owner’s operation does not satisfy an Operation Standard, the Operation Plan shall show how and when operation will be brought into compliance.

According to GO Section 8.2.2, the GAO’s Operation Plan is kept at the plant site.

According to GO Section 8.3:

An Operation Plan Summary is a paper or electronic document that summarizes the Operation Plan.  It shall summarize how the Generation Asset Owner’s operation complies with each Operation Standard.  It shall be in the format and include the content elements specified by the Commission’s Executive Director, as shown below.  Where the Generating Asset Owner’s operation does not satisfy an Operation Standard, the Operation Plan Summary shall summarize how and when operation will be brought into compliance.

For each Generating Asset in Active Service, the Generating Asset Owner is required to  file an Operation Plan Summary with CPSD within 120 days of the date the Executive Director specifies the format and content elements of the summary.

In preparing this draft document, the Commission staff considered recommendations by the California Electric Generation Facilities Standards Committee that the Summary contain:

- A brief Unit Plan including the expected years the plant will remain in operation, whether the plant is regarded as a base load plant or peaking plant (or some intermediate designation), what level of availability the GAO intends for the plant, whether the plant will operate year-round or only seasonally, and whether the GAO views the plant as a long-term resource that requires continued maintenance and investment.

- A general description and timetable of how the GAO meets or plans to meet the provisions of each Operation Standard at each unit (or identical groups of units), identifying by title (and location) and summarizing the various operating policies, procedures, training programs and routines the GAO has in place (or will put in place) to demonstrate compliance with the Operation Standards.

Requirements for the Introductory Chapter of the Operation Plan Summary: The Unit Plan

The unit plan should include the following content elements (generally including at least a short section for each content element):

- Planned life of the plant

- Role of the plant in the system (e.g., base load)

- Seasonal or year-round operation

- Used regularly every year, or only in years of high demand or low supply

- The level of availability the GAO intends for the plant

- Current evaluation of plant condition

- Investment strategy the GAO plans for the plant

  - Design or operating issues that can be addressed economically

  - Design or operating issues that can not be addressed economically (with explanation)

The unit plan should be a narrative, with at least a substantial paragraph for each content element and section.  Where documents exist that explain the GAO’s plans for the plant in detail, reference those documents by name, document number, and location.

Requirements for Chapters 1 through 28 of the Operation Plan Summary (Corresponding to Operation Standards 1 through 28)

Each of Chapters 1-28 of the Operation Plan Summary should address the corresponding Operation Standard.  Each chapter should provide a general description of how the GAO meets or plans to meet the provisions of each Operation Standard at each unit (or groups of units if they are essentially identical).

Below we provide specific content elements that should be addressed by each chapter.  In general, each content element should be addressed in a section of the report.  These content elements are generally drawn from one (and usually, more than one) of the guidelines associated with each standard.  Therefore, content elements are far fewer in number than the guidelines.  It will be helpful to consult the guidelines if the wording of a content element is unclear.  In general, each content element should correspond to a section of the report.

Each chapter should summarize the various operating policies, procedures, training programs, and routines the GAO has in place (or will put in place) to comply with the Operation Standards.  Relevant documents should be summarized and identified by title, number (if any), location, and format (e.g., paper or electronic).  Such documents should be identified section-by-section and content-element-by-content-element where relevant.

Where the standards require repeated or regular actions to achieve compliance, the chapter and/or section should specify the frequency or cycle time for these actions.  (For example, the Plan Summary should specify whether a particular inspection routine will be conducted twice a day, once a week, once a year, or at some other frequency.)

Audits, inspections, and investigations by Commission staff will be directed in large part to determine whether GAOs are conducting their operations in compliance with their own Operation Plans.  It is understood that changing circumstances may make it impossible to keep exactly to a schedule or cycle specified in an Operations Plan Summary.   It is therefore acceptable for GAOs to specify frequencies, for example, as “normal” (that is , the GAO’s intention in the absence of special circumstances), and “no less than” (that is, the minimal acceptable frequency for reliable operation of the unit).  For example, maintenance might be planned quarterly under normal circumstances, but allowed to slip during periods of shortage on the system to semi-annually.

Below each standard is provided for your convenience in a text box.  Following are the required content elements and sections for that standard.

A few final comments:

- The sections and topics shown may not be an all-inclusive list.  Please supplement as necessary.

- Because the standards overlap somewhat, the reader may be referred to another standard where a section or topic is addressed.

Where the topic is not relevant to the GAO’s particular plant or plan, the Plan Summary may so state.

- Personnel evacuation and emergency action plans, possibly including

  - Frequency of updates

  - Staff training

  - Communication during emergencies

  - Availability of plans

- Plant hazards and safety problems; policies regarding:

  - Regular identification

  - Reporting and cessation of work when appropriate

  - Mitigation

  - Training

  - Possibly including: equipment, confined space entry, clearance or lockout/tagout procedures; chemical hazards, handling, storage, inventory, labeling, and MSDS; and safety training and formal safety meetings; and fall protection.

- Accident investigation and follow up, policies and procedures including

  - Root cause determination

  - Evaluation of similar hazards throughout plant

  - Mitigation

  - Record keeping and analysis

  - Training

Note:  Some of the Safety sections and topics above may be addressed in Standard 20: Preparedness for On-Site and Off-Site Emergencies

- Organization chart for the plant and for the GAO.

- Policies and procedures regarding:

  - Organization and chain of command

  - Support from and communications with other corporate offices

  - Support from and communication with outside contractors and other organizations

Policies and assignments regarding responsibility for:

- Personal and organizational priorities and goals, performance evaluation, and follow up.

- Teamwork,  communication and collaboration between different organizational groups,

- Communication of goals

- Personnel training and qualification

- Procedures and administrative controls

- Staff training and resources

- Administrative controls.

- Availability of resources.

- Business planning

- Planning of changes to equipment

- Performance trends

- Identifying problems; reporting, prioritizing, tracking

- Resolving problems;  root cause analysis and follow-up

- Use of best practices and benchmarking

- Development and updating of requirements for plant positions/functions

- Testing, evaluation, and follow up

- Schedules for re-evaluation of skills and qualifications

- Lists of positions and requirements

- Policy on qualification of contractors and temporary employees

- Description of training programs

  - Matching to job requirements

  - Mix of classroom, online, on-the job

  - Schedule, testing

  - Location of records

  - Coverage of startup, normal, and typical abnormal conditions

  - Evaluation of effectiveness.

  - Access to PC-based or other simulators for plant operators.

- Procedures for preparation, review, approval and revision of procedures

- Maintenance of a procedure list

- Procedures for start-up, shut-down, normal operation, and reasonably anticipated abnormal conditions.

- Usual contents of procedures, such as setpoints, tolerances, control logic, and equipment numbers; valve lineup sheets; system descriptions; startup operation; shutdown operation; normal operation; abnormal and emergency operation conditions

- Consideration of the audience, human factor considerations. etc.

- Strategy for monitoring plant status and making information available

- Procedures for determining operability of equipment.

- Procedures for tests and evolutions

- Procedures for temporary equipment modifications

  - Frequency of review for temporary modifications

- Procedures for plant design changes

  - Consideration of effect on plant operation

  - Notification off affected staff of plans and progress

  - Planning, scheduling, tracking

  - Update of documents

  - Incorporation into training materials, etc.

- Engineering staff qualifications

- Size and scope of engineering unit and plants to be covered

- Support for outage planning

- Frequency and scope of plant and equipment performance evaluations.

- Condition monitoring, leak rate testing, and in-service testing

- Availability/reliability information

- Unit operating history

- Evaluation of and support for plant modification

- Post-modification testing

- Communication of engineering recommendations to staff

- Consultant staff qualifications

- Monitoring and evaluation of technical developments

- Liquid waste management and monitoring

- Regular evaluation of effluent and emission processing equipment

- Maintenance and calibration of emissions equipment

- Lists and inventories of materials and equipment

- Frequency and scope of evaluations of facilities. tools, and equipment

  - ergonomics and human factors

- Identification of hazardous materials and facilities for handling them

- Frequency of equipment calibration and maintenance

- Policies on organization and labeling of materials and equipment

- Housekeeping and cleanliness

- Communications equipment

- Policies on use and deviations from procedures

- Policies on procedure evaluation and revision

- Policies on unsafe conditions

- How personnel-in-charge are determined

- Policies on professional conduct

- Scope of trainee responsibility

- Systems subject to routine inspections (or automatic data gathering) and list of procedures for such inspections

- Contents of procedures for routine inspections, including items to be monitored and action levels.

- Training of personnel and monitoring of implementation of routine inspections

- Definition and implementation of action levels

- Collection and analysis of data from routine inspections

- Clearance procedure or procedures

- Identification of equipment subject to Clearance

- Information available at the equipment

- Information at other locations, availability to personnel

- Tracking and handoff of clearances

- Frequency and scope of training

- Frequency and scope of monitoring

- Summary of procedure for review of work plans

- Training and monitoring of implementation

- Steps taken to assure participation by operations personnel in work orders

  - Identification and evaluation of operating issues that could require work orders

  - Initiation of such work orders

  - Monitoring of progress of such work orders

  - Availability to personnel of work order tracking system

- Policies and procedures for the retention of operations records.

- List of records to be retained.

- Equipment subject to testing and scope and frequency of tests

- General parameters of plant operation to be maintained

- Maintenance of communication with the Control Area Operator

- Emergency operations procedures

  - For various types of grid emergency

  - Actions to be taken during periods of stress and shortage

- Training in procedures: scope and frequency

- Policies on consultation with regulatory agencies; frequency and scope

- Identification of plant systems requiring special attention in emergencies

- Policies on assistance to grid operation following major disturbances

- Emergency action plan

  - Types of emergencies addressed

  - Responsibilities and actions to be taken by plant personnel

  - Procedures for back-up communications

  - Availability of plan to personnel

- Training in emergency response.

- Plant security procedures at different threat levels

- Perimeter and access control

- Lighting and intrusion detection

- Protection of operating information

- Protection of data, communications and control systems (cybersecurity)

- Contingency Plans

  - Supply of Commodities

  - Alternative delivery if possible

  - For seasonal plants, time necessary to achieve readiness after notification

  - Personnel for plant operation

- Readiness Policies

  - Number of days of supplies of consumables kept on site

  - Maintenance of cooling water supply, such as tunnel cleaning, intake channel dredging.

  - Personnel planning and vacations

  - Protection of equipment affected by weather, such as pumps, motors, FD fans, ID fans, boiler feed pumps, circulating water pumps, condensate feed pumps.

  - Access roads

  - Other preparation for severe weather

  - Alternative methods of communication

- Coverage of standard in plant documents

- Coverage of standard in plant documents

- Coverage of standard in plant documents

- Coverage of standard in plant documents

- Description of the plant’s flow assisted corrosion program, including the following:

  - Identity of equipment/pipes tested

  - Scheduled future testing

  - Records of completed tests

  - Recommendation for replacement or further testing

  - Trends

- For each major system relevant to the unit (see guidelines for Standard 28), summarize and reference:

  - Procedures

    - Startup and shutdown

    - Normal

    - Reasonably expected abnormal conditions

    - During system emergencies, if appropriate.

  - Critical parameters and action levels

  - Procedures for operation during periods of stress or shortage

  - Training and qualifications for operation

# Footnotes

The Committee specifically recommends the contents of the “Operations Plan,” which is to summarize the GAO’s compliance program and which is to be submitted regularly to the Commission.  The Commission’s decision and GO 167 call this document the “Operations Plan Summary.”   The Operations Plan, as described in the GO, is to be retained at the plant and is expected to be much more voluminous.

# Text boxes

Chapter 1 -- Standard 1-- Safety

The protection of life and limb for the work force is paramount.  GAOs have a comprehensive safety program in place at each site.  The company behavior ensures that personnel at all levels of the organization consider safety as the overriding priority.  This is manifested in decisions and actions based on this priority. The work environment and the policies and procedures foster such a safety culture, and the attitudes and behaviors of personnel are consistent with the policies and procedures.

Chapter 2 -- Standard 2 - Organizational Structure and Responsibilities

The organization with responsibility and accountability for establishing and implementing an operation strategy to support company objectives for reliable plant operation is clearly defined, communicated, understood and is effectively implemented.  Reporting relationships, control of resources, and individual authorities support and are clearly defined and commensurate with responsibilities

Chapter 3 -- Standard 3 - Operations Management and Leadership

Operations management establishes high standards of performance and aligns the operations organization to effectively implement and control operations activities.

Chapter 4-- Standard 4 - Problem Resolution and Continuing Improvement

The GAO values and fosters an environment of continuous improvement and timely and effective problem resolution.

Chapter 5  --  Standard 5 - Operations Personnel Knowledge and Skills

Operations personnel are trained and qualified to possess and apply the knowledge and skills needed to perform operations activities that support safe and reliable plant operation.

Chapter 6 --Standard 6 - Training Support

A systematic approach to training is used to achieve, improve, and maintain a high level of personnel knowledge, skill, and performance.  Each GAO provides a site-specific training program including on-the-job training, covering operations, including reasonably anticipated abnormal and emergency operations.  Personnel are trained commensurate with their duties.

Chapter 7 -- Standard 7 - Operation Procedures and Documentation

Operation procedures exist for critical systems and states of those systems necessary for the operation of the unit including startup, shutdown, normal operation, and reasonably anticipated abnormal and emergency conditions.  Operation procedures and documents are clear and technically accurate, provide appropriate direction, and are used to support safe and reliable plant operation.  Procedures are current to the actual methods being employed to accomplish the task and are comprehensive to ensure reliable energy delivery to the transmission grid.

Chapter 8  -- Standard 8 - Plant Status and Configuration

Station activities are effectively managed so plant status and configuration are maintained to support safe, reliable and efficient operation.

Chapter 9 -- Standard 9 - Engineering and Technical Support

Engineering activities are conducted such that equipment performance supports reliable plant operation.  Engineering provides the technical information necessary for the plant to be operated and maintained within the operating parameters defined by plant design.  Engineering provides support, when needed, to operations and maintenance groups to resolve operations and maintenance problems.

Chapter 10 -- Standard 10 - Environmental Regulatory Requirements

Environmental regulatory compliance is paramount in the operation of the generating asset.  Each regulatory event is identified, reported and appropriate action taken to prevent recurrence.

Chapter 11 --Standard 11 - Operations Facilities, Tools and Equipment

Facilities and equipment are adequate to effectively support operations activities.

Chapter 12 --Standard 12 - Operations Conduct

To ensure safety, and optimize plant availability, the GAO conducts operations systematically, professionally, and in accordance with approved policies and procedures.  The GAO takes responsibility for personnel actions, assigns personnel to tasks for which they are trained, and requires personnel to follow plant and operation procedures and instructions while taking responsibility for safety.

Among other things:

- All personnel follow approved policies and procedures.  Procedures are current, and include a course of action to be employed when an adopted procedure is found to be deficient.

- All operations are performed in a professional manner.  Basic rules of conduct apply throughout the plant at all times.

- All personnel on-duty are trained, qualified, and capable of performing their job functions.  Personnel are assigned only to duties for which they are properly trained and qualified.

- Personnel take immediate actions to prevent or correct unsafe situations.

Chapter 13 --Standard 13 - Routine Inspections

Routine inspections by plant personnel ensure that all areas and critical parameters of plant operations are continually monitored, equipment is operating normally, and that routine maintenance is being performed.  Results of data collection and monitoring of parameters during routine inspections are utilized to identify and resolve problems, to improve plant operations, and to identify the need for maintenance.  All personnel are trained in the routine inspections procedures relevant to their responsibilities.

Among other things, the GAO creates, maintains, and implements routine inspections by:

- Identifying systems and components critical to system operation (such as those identified in the guidelines to Standard 28).

- Establishing procedures for routine inspections that define critical parameters of these systems, describe how those parameters are monitored, and delineate what action is taken when parameters meet alert or action levels.

- Training personnel to conduct routine inspections.

- Monitoring routine inspections.

Chapter 14 -- Standard 14 - Clearances

Work is performed on equipment only when safe.  When necessary, equipment is taken out of service, de-energized, controlled, and tagged in accordance with a clearance procedure.    Personnel are trained in the clearance procedure and its use, and always verify that equipment is safe before any work proceeds.  Among other things:

A.	The GAO prepares and maintains a clearance procedure.  The clearance procedure contains requirements for removing a component from service and/or placing a component back into service.

B.	The GAO ensures that personnel are trained in and follow the clearance procedure.

Chapter 15 -- Standard 15 - Communications and Work Order Meetings

The availability of the generating asset and safety of personnel is ensured during the execution of work orders by adequate communications and meetings, which may be scheduled or as needed, to review work plans with all affected personnel before work begins.  Clear lines of communication exist between personnel responsible for operations, maintenance and engineering groups.

Among other things:

- The GAO prepares and maintains a procedure for review of work plans through communications and work order meetings at the facility.

- Work is analyzed to determine what personnel, components, and systems are affected.

- Affected personnel meet before work begins to define the work, identify safety issues, to minimize the impact on plant operation, and to determine the need for further meetings.

- Personnel are trained in and follow the procedure.

Chapter 16 – Standard 16 -- Participation by Operations Personnel in Work Orders

Operations personnel identify potential system and equipment problems and initiate work orders necessary to correct system or equipment problems that may inhibit or prevent plant operations.  Operations personnel monitor the progress of work orders affecting operations to ensure timely completion and closeout of the work orders, so that the components and systems are returned to service.

Among other things:

- Operations personnel identify problems requiring work orders, and initiate work orders to correct those problems

- The operations manager or other appropriate operating personnel periodically review work orders that affect operations to ensure timely completion and closeout of the work orders, so that components and systems are returned to service.

- Personnel responsible for prioritizing work orders consult operations personnel to assure that work orders affecting the operations of the plant are properly prioritized.

- Appropriate personnel are trained in and follow procedures applicable to work orders.

Chapter 17 --Standard 17 - Records of Operation

The GAO assures that data, reports and other records reasonably necessary for ensuring proper operation and monitoring of the generating asset are collected by trained personnel and retained for at least five years, and longer if appropriate.

Chapter 18 --  Standard 18 - Unit Performance Testing

The GAO conducts periodic performance tests as appropriate to identify trends and possible improvements in unit operation.  The GAO responds to test results with changes to equipment, policies, routines, or procedures necessary to maintaining unit availability and the unit’s ability to support grid operations consistent with the Unit Plan.

Chapter 19 -- Standard 19 - Emergency Grid Operations

The GAO prepares for conditions that may be reasonably anticipated to occur during periods of stress or shortage on the state’s electric grid.  During such periods of stress or shortage, the GAO makes operational decisions to maximize each unit’s availability and ability to support grid operations.

Among other things the GAO:

- Takes reasonable steps to maintain the ability to communicate with the Control Area Operator at all times.

- In preparing for periods of stress or shortage, takes steps to clarify the regulatory requirements, such as emissions, water discharge temperature, etc., which will apply during emergencies.

- When emergencies appear imminent, seeks regulatory relief from those regulatory requirements that reduce output.

- Assists the Control Area Operator in responding to the various kinds of possible problems on the electrical grid, including restoration of service after a disturbance.

- When practical, during periods of stress or shortage, consults with the Control Area Operator before derating a unit or taking a unit off line and defers outages and derates at the Control Area Operator’s request when continued operation is

1.	Possible and practical,

2.	Safe to plant personnel and to the public,

3.	In accordance with applicable law and regulations, and

4.	Will not cause major damage to the plant.

Chapter 20 --  Standard 20 –  Preparedness for On-Site and Off-Site Emergencies

The GAO plans for, prepares for, and responds to reasonably anticipated emergencies on and off the plant site, primarily to protect plant personnel and the public, and secondarily to minimize damage to maintain the reliability and availability of the plant.

Among other things, the GAO:

- Plans for the continuity of management and communications during emergencies, both within and outside the plant,

- Trains personnel in the emergency plan periodically, and

- Ensures provision of emergency information and materials to personnel.

Chapter 21 -- Standard 21 - Plant Security

To ensure safe and continued operations, each GAO provides a prudent level of security for the plant, its personnel, operating information and communications, stepping up security measures when necessary.

Chapter 22 -- Standard 22 - Readiness

Until a change in a unit’s long-term status, except during necessary maintenance or forced outages, the GAO is prepared to operate the unit at full available power if the Control Area Operator so requests, after reasonable notice, when such operation is permitted by law and regulation.

Among other things, the GAO:

- Maintains contingency plans to secure necessary personnel, fuel, and supplies, and

- Prepares facilities for reasonably anticipated severe weather conditions.

Chapter 23 --  Standard 23 - Notification of Changes in Long-Term Status of a Unit

The GAO notifies the Commission and the Control Area Operator in writing at least 90 days prior to a change in the long-term status of a unit.  The notification includes a description of the planned change.

Chapter 24 -- Standard 24 - Approval of Changes in Long-Term Status of a Unit

The GAO maintains a unit in readiness for service in conformance with Standard 22 unless the Commission, after consultation with the Control Area Operator, affirmatively declares that a generation facility is unneeded during a specified period of time.  This standard is applicable only to the extent that the regulatory body with relevant ratemaking authority has instituted a mechanism to compensate the GAO for readiness services provided.

Chapter 25 -- Standard 25 - Transfer of Ownership

The GAO notifies the Commission and the Control Area Operator in writing at least 90 days prior to any change in ownership.

Chapter 26 -- Standard 26 - Planning for Long-Term Unit Storage

At least 90 days before a change in the long-term status of an electric generation unit, other than permanent shutdown and/or decommissioning, the GAO shall submit to the Commission plans and procedures for storage, reliable restart, and operation of the unit.

Chapter 27 -- Standard 27 - Flow Assisted Corrosion.

Where circumstances require it, the GAO has a flow-assisted corrosion program, which identifies vulnerable equipment, provides for regular testing of that equipment, and responds appropriately to prevent high energy pipe failures.

Chapter 28 -- Standard 28 – Equipment and Systems.

GAO complies with these Operation Standards (1-27) considering the design bases (as defined in the Appendix) of plant equipment and critical systems.  The GAO considers the design basis of power plant equipment when as required by other standards it, among other things:

### Establishes procedures for the operation of critical systems at each unit (Ref. Standard No. 7).

### For each system, identifies critical parameters that require monitoring (Ref. Standard No. 8 and 13).

### For each critical parameter, establishes values at which to increase observation of the system or take actions to protect it (Ref. Standard No. 8 and 13).

### Assures that systems are monitored and actions are taken. (Ref. Standard 8 and 13)

### Establishes parameters for operation during periods of stress or shortage on the state’s electric grid (Ref. Standard No. 9 and 19).

### Assures that personnel operating critical systems are trained and qualified (Ref. Standard No. 6).

The unit plan is a brief summary of the business plant for the unit, and is intended to put the Operations Plan and Operations Plan Summary in context, particularly when a unit is expected to be retired within a few months or years.