## Sheet1
Non-Pipeline Alternatives - Lithium Ion Battery Storage Scenarios
System Capacity Analysis:
Operated As | Standalone | Standalone | Standalone Total | System | System | System Total | Standalone | Standalone | Standalone Total | System | System | System Total | System | System | System Total
Line | 3010 | 1600 | 3010+1600 | 3010 | 1600 | 3010+1600 | 3010 | 1600 | 3010+1600 | 3010 | 1600 | 3010+1600 | 3010 | 1600 | 3010+1600
Pressure (psig) | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 512 | 640 & 512 | 640 | 512 | 640 & 512 | 640 | 320 | 640 & 320
Capacity MMCFD) | 570 | 150 | 720 | 530 | 100 | 630 | 570 | 115 | 685 | 530 | 65 | 595 | 530 | 40 | 570
References: (1) A.15-09-013, SDGE -12, Supplemental Testimony of SDGE and SoCal Gas (2) ED_DR_04
Remark:
1. L3010 operating at 640 psig and L1600 operating at 320 psig and both operating as a system provide a system capacity of 570 MMCFD
2. L3010 operating as a standalone pipeline without L1600 also has a capacity of 570 MMCFD
Battery storage requirement: | [5 empty] | 8-HOUR SERVICE NEEDS | [5 empty] | 4-HOUR SERVICE NEEDS
Base MMCFD Available | MMCFD Required | Addl MMCFD required | Additional MMBtuD required | MWh for 24 hours | MWh for 8hrs | MWh need for 8-Hr (w/ Turbine Gen eff. 0.6) | Energy rate (MW) required | # of Tesla 50KW/ 210KWH pack reqd. | Sq Ft Reqd (per Pack approx. 72 sq ft) | Total Sq Ft w/ 25% extra for Rd /Bldgs/park | Approx Acres | MWh need for 4-Hr (w/ Turbine Gen eff. 0.6) | Energy rate (MW) required | # of 50KW/ 210KWH pack reqd. | Approx Acres | Notes
570 | 570 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0
570 | 572 | 2 | 2040 | 597.865 | 199.2883 | 119.573 | 14.9466 | 569.3953 | 40757.2351 | 50946.5438 | 1.1696 | 59.7865 | 14.9466 | 284.6976 | 0.58479 | Scenario 2
570 | 574 | 4 | 4080 | 1195.7301 | 398.5767 | 239.146 | 29.8933 | 1138.7906 | 81514.4701 | 101893.0876 | 2.3391 | 119.573 | 29.8933 | 569.3953 | 1.1696
570 | 576 | 6 | 6120 | 1793.5951 | 597.865 | 358.719 | 44.8399 | 1708.1858 | 122271.7052 | 152839.6315 | 3.5087 | 179.3595 | 44.8399 | 854.0929 | 1.7544
570 | 578 | 8 | 8160 | 2391.4602 | 797.1534 | 478.292 | 59.7865 | 2277.5811 | 163028.9402 | 203786.1753 | 4.6783 | 239.146 | 59.7865 | 1138.7906 | 2.3391
570 | 580 | 10 | 10200 | 2989.3252 | 996.4417 | 597.865 | 74.7331 | 2846.9764 | 203786.1753 | 254732.7191 | 5.8479 | 298.9325 | 74.7331 | 1423.4882 | 2.9239
570 | 582 | 12 | 12240 | 3587.1903 | 1195.7301 | 717.4381 | 89.6798 | 3416.3717 | 244543.4104 | 305679.2629 | 7.0174 | 358.719 | 89.6798 | 1708.1858 | 3.5087
570 | 584 | 14 | 14280 | 4185.0553 | 1395.0184 | 837.0111 | 104.6264 | 3985.767 | 285300.6454 | 356625.8068 | 8.187 | 418.5055 | 104.6264 | 1992.8835 | 4.0935
570 | 586 | 16 | 16320 | 4782.9204 | 1594.3068 | 956.5841 | 119.573 | 4555.1622 | 326057.8805 | 407572.3506 | 9.3566 | 478.292 | 119.573 | 2277.5811 | 4.6783
570 | 588 | 18 | 18360 | 5380.7854 | 1793.5951 | 1076.1571 | 134.5196 | 5124.5575 | 366815.1155 | 458518.8944 | 10.5261 | 538.0785 | 134.5196 | 2562.2788 | 5.2631
570 | 590 | 20 | 20400 | 5978.6504 | 1992.8835 | 1195.7301 | 149.4663 | 5693.9528 | 407572.3506 | 509465.4382 | 11.6957 | 597.865 | 149.4663 | 2846.9764 | 5.8479 | Scenario 1
570 | 595 | 25 | 25500 | 7473.313 | 2491.1044 | 1494.6626 | 186.8328 | 7117.441 | 509465.4382 | 636831.7978 | 14.6196 | 747.3313 | 186.8328 | 3558.7205 | 7.3098 | Scenario 3
NOTE: MWh needed, number of Tesla pack required, and space required for 4-hr service will be half of what is required for 8-hr service, MW will remain same
25MMCFD Case ==>> |  | 25 | 25500 | 7473.313 | 2491.1044 | 1494.6626 | 186.8328 | 7117.441 | 509465.4382 | 636831.7978 | 14.6196 | 747.3313 | 186.8328 | 3558.7205 | 7.3098
NOTE: 25 MMCFD is the SDG&E System wide reduction in flow when L1600 pressure is reduced from 512 psig to 320 psig.
44.5MMCFD Case ==>> |  | 44.51 | 45400.2 | 13305.4866 | 4435.1622 | 2661.0973 | 332.6372 | 12671.892 | 907052.2663 | 1133815.3328 | 26.0288 | 1330.5487 | 332.6372 | 6335.946 | 13.0144 | Scenario 4
NOTE: 44.5 MMCFD is the reduction in flow when L1600 operated as a standalone pipeline and L1600 pressure is reduced from 512 psig to 320 psig.
Conversion Factors used |  |  |  | GENERAL REMARK:
Btu/cf = | 1020 |  |  | Pg. 13, R.15-03-011, Table 1: SDG&E Energy Storage procurement target = 165 MW
1MMBtu = | 0.29307 | MWh |  | Pg. 17, R.15-03-011, Table 2: SDG&E Energy Storage procurement t date = 96.65 MW, remaining obligation = 68.35 MW
1 acre = | 43560 | Sq. Ft |  | Pg. 26, R.15-03-011, Table 6:SDG&E Long Term energy storage obligation = 331 MW
Pg. 2, SDG&E Long-Term Gas demand forecast, 1-in-10 yr cold day: 2018/19 = 589 MMCFD, 2022/23 = 572 MMCFD
The energy storage market continues to change rapidly. For this analysis, publicly available Tesla battery specifications were applied, but many other lithium-ion battery products could also have been used.
TESLA SPEC: | * Net Energy delivered at 25°C (77°F) ambient temperature including thermal control
Overall System Specs
AC Voltage380 to 480V, 3 phases |  |  |  | Dimensions and Foot Print per Tesla Pack
Energy Capacity210 kWh (AC) per Powerpack
CommunicationsModbus TCP/IP; DNP3 |  |  |  | Powerpack |  |  | Estimated Area per Tesla pack
Operating Temperature-22°F to 122°F / -30°C to 50°C |  |  |  | Length: 1,308 mm (51.5")
Power50kW (AC) per Powerpack |  |  |  | Width: 822 mm (32.4") |  |  | Longest L= | 4.2917 | ft
EnclosuresPods: IP67 |  |  |  | Height: 2,185 mm (86") |  |  | W1+W2 = | 6.8167 | ft
Powerpack: IP35/NEMA 3R |  |  |  | Weight: 1622 kg (3575 lbs) |  |  | + 1.5' all around to give 3' between packs
Inverter: IP66/NEMA 4 |  |  |  | Industrial Inverter |  |  | Total L = | 7.2917 | ft
Scalable Inverter Powerfrom 50kVA to 625kVA (at 480V) |  |  |  | Length: 1,014 mm (39.9") |  |  | Total W = | 9.8167 | ft
System Efficiency (AC) *88% round-trip (2 hour system) |  |  |  | Width: 1254 mm (49.4") |  |  | Area/pack | 71.5799 | sq. ft
89% round-trip (4 hour system) |  |  |  | Height: 2192 mm (86.3")
Depth of Discharge100% |  |  |  | Weight: 1200 kg (2650 lbs)
CertificationsNationally accredited certifications to
international safety, EMC, utility and env. legislation.