## Sheet1
PG&E Upcoming 2012 Hydrotests with Spike Tests Unadvisable - March 16, 2012
Test Pressure is Limited by Valve and Insulating Flange Ratings
Ref Number | Test Number | Test Date | Line | OD | WT | Grade | Long seam | Class Location | Test Multiplier | MAOP | Min. Test P | Max. Test P | % SMYS @ min. test | % SMYS @ max test | Test Footage | Limiting Factor
1 | T-122-12 | 2012-03-22 | 300B | 34 | 0.5 | 52000 | DSAW | 1 | 1.5 | 700 | 1050 | 1100 | 68.85 | 71.92 | 163 | This test includes a valve and an insulating flange assembly with an ANSI 300 rating which limits the maximum test pressure to 1110 psig.
[14 empty] | Total | 163 | feet