## One Class Out Details
Color Fill Key | Pressure Reduction previously taken due to a non-One-Class-Out issue |  |  |  |  | Note, all lines previously reduced are NOT operating one-class-out.
Pressure Reduction taken due to One-Class-Out issue
|  | Total | 9.3065 | miles
General Information |  |  |  |  | Pipe Specs |  |  |  | Install/Test Specs | [6 empty] | MAOP Calcs
Route | Approx GIS Segment | Feature Type | Feature Length | Class Location Value | OD (in) | WT (in) | SYMS (psi) | LSF | Install date | Test Year | Duration (hr) | Pressure (min test pressure, psig) | Test Factor (per 192.611) | Established MAOP (per Test) | STPR or Uprate | MAOP of Record (Pre-Reduction) | % SMYS @ Current MAOP | % SYMS (per 192.111) | % SMYS (allowable per One-Class-Out)
101 | 167.2 | Pipe | 2 | 3 | 20 | 0.25 | 33000 | 0.8 | 1947-11-09 | 1989 | 8.6 | 650 | 0.66667 | 433.3333 | Uprate | 365 | 55.3% | 50% | 60%
101 | 167.2 | Pipe | 200.3 | 3 | 20 | 0.25 | 33000 | 0.8 | 1947-11-09 | 1989 | 8.6 | 650 | 0.66667 | 433.3333 | Uprate | 365 | 55.3% | 50% | 60%
101 | 167.2 | Pipe | 2 | 3 | 20 | 0.25 | 33000 | 0.8 | 1947-11-09 | 1989 | 8.6 | 650 | 0.66667 | 433.3333 | Uprate | 365 | 55.3% | 50% | 60%
101 | 167.2 | Pipe | 394.2 | 3 | 20 | 0.25 | 33000 | 0.8 | 1947-11-09 | 1989 | 8.6 | 650 | 0.66667 | 433.3333 | Uprate | 365 | 55.3% | 50% | 60%
101 | 167.2 | Pipe | 90 | 3 | 20 | 0.25 | 33000 | 0.8 | 1947-11-09 | 1989 | 8.6 | 650 | 0.66667 | 433.3333 | Uprate | 365 | 55.3% | 50% | 60%
101 | 167.2 | Pipe | 12 | 3 | 20 | 0.25 | 33000 | 0.8 | 1947-11-09 | 1989 | 8.6 | 650 | 0.66667 | 433.3333 | Uprate | 365 | 55.3% | 50% | 60%
101 | 167.2 | Pipe | 6 | 3 | 20 | 0.25 | 33000 | 0.8 | 1947-11-09 | 1989 | 8.6 | 650 | 0.66667 | 433.3333 | Uprate | 365 | 55.3% | 50% | 60%
101 | 167.2 | Pipe | 7 | 3 | 20 | 0.25 | 33000 | 0.8 | 1947-11-09 | 1989 | 8.6 | 650 | 0.66667 | 433.3333 | Uprate | 365 | 55.3% | 50% | 60%
101 | 167.2 | Pipe | 990.5 | 3 | 20 | 0.25 | 33000 | 0.8 | 1947-11-09 | 1989 | 8.6 | 650 | 0.66667 | 433.3333 | Uprate | 365 | 55.3% | 50% | 60%
101 | 167.2 | Pipe | 9 | 3 | 20 | 0.25 | 33000 | 0.8 | 1947-11-09 | 1989 | 8.6 | 650 | 0.66667 | 433.3333 | Uprate | 365 | 55.3% | 50% | 60%
101 | 167.2 | Pipe | 422 | 3 | 20 | 0.25 | 33000 | 0.8 | 1947-11-09 | 1989 | 8.6 | 650 | 0.66667 | 433.3333 | Uprate | 365 | 55.3% | 50% | 60%
101 | 167.2 | Pipe | 9.2 | 3 | 20 | 0.25 | 33000 | 0.8 | 1947-11-09 | 1989 | 8.6 | 650 | 0.66667 | 433.3333 | Uprate | 365 | 55.3% | 50% | 60%
101 | 167.2 | Pipe | 56.6 | 3 | 20 | 0.25 | 33000 | 0.8 | 1947-11-09 | 1989 | 8.6 | 650 | 0.66667 | 433.3333 | Uprate | 365 | 55.3% | 50% | 60%
101 | 167.2 | Pipe | 113.8 | 3 | 20 | 0.25 | 33000 | 0.8 | 1947-11-09 | 1989 | 8.6 | 650 | 0.66667 | 433.3333 | Uprate | 365 | 55.3% | 50% | 60%
101 | 168 | Pipe | 235.8 | 3 | 20 | 0.25 | 33000 | 0.8 | 1947-11-09 | 1989 | 8.6 | 650 | 0.66667 | 433.3333 | Uprate | 365 | 55.3% | 50% | 60%
101 | 168 | Pipe | 10 | 3 | 20 | 0.25 | 33000 | 0.8 | 1947-11-09 | 1989 | 8.6 | 650 | 0.66667 | 433.3333 | Uprate | 365 | 55.3% | 50% | 60%
101 | 169 | Pipe | 61 | 3 | 20 | 0.25 | 33000 | 0.8 | 1947-11-09 | 1989 | 8.6 | 650 | 0.66667 | 433.3333 | Uprate | 365 | 55.3% | 50% | 60%
021F | 128.3 | Pipe | 2.4 | 3 | 12.75 | 0.203 | 30000 | 1 | 12/15/1952 | 1983 | 8.2 | 835 | 0.66667 | 556.6667 | Uprate | 500 | 52.34% | 50% | 60%
021F | 128.3 | Pipe | 3.8 | 3 | 12.75 | 0.203 | 30000 | 1 | 12/15/1952 | 1983 | 8.2 | 835 | 0.66667 | 556.6667 | Uprate | 500 | 52.34% | 50% | 60%
021F | 128.3 | Pipe | 18.8 | 3 | 12.75 | 0.203 | 30000 | 1 | 12/15/1952 | 1983 | 8.2 | 835 | 0.66667 | 556.6667 | Uprate | 500 | 52.34% | 50% | 60%
021F | 128.3 | Pipe | 4.8 | 3 | 12.75 | 0.203 | 30000 | 1 | 12/15/1952 | 1983 | 8.2 | 835 | 0.66667 | 556.6667 | Uprate | 500 | 52.34% | 50% | 60%
021F | 128.3 | Pipe | 2.4 | 3 | 12.75 | 0.203 | 30000 | 1 | 12/15/1952 | 1983 | 8.2 | 835 | 0.66667 | 556.6667 | Uprate | 500 | 52.34% | 50% | 60%
021F | 150.2 | Pipe | 10.1 | 3 | 16 | 0.25 | 30000 | 1 | 7/1/1960 | 2012 | 8.3 | 871 | 0.66667 | 580.6667 | Uprate | 500 | 53.33% | 50% | 60%
021F | 150.4 | Pipe | 135.2 | 3 | 16 | 0.25 | 30000 | 1 | 7/1/1960 | 2012 | 8.3 | 871 | 0.66667 | 580.6667 | Uprate | 500 | 53.33% | 50% | 60%
021F | 150.4 | Pipe | 89.3 | 3 | 16 | 0.25 | 30000 | 1 | 7/1/1960 | 2012 | 8.3 | 871 | 0.66667 | 580.6667 | Uprate | 500 | 53.33% | 50% | 60%
021F | 150.4 | Pipe | 213.3 | 3 | 16 | 0.25 | 30000 | 1 | 7/1/1960 | 2012 | 8.3 | 871 | 0.66667 | 580.6667 | Uprate | 500 | 53.33% | 50% | 60%
021F | 150.4 | Pipe | 196.2 | 3 | 16 | 0.25 | 30000 | 1 | 7/1/1960 | 2012 | 8.3 | 871 | 0.66667 | 580.6667 | Uprate | 500 | 53.33% | 50% | 60%
021F | 150.5 | Pipe | 58.7 | 3 | 16 | 0.25 | 30000 | 1 | 7/1/1960 | 2012 | 8.3 | 871 | 0.66667 | 580.6667 | Uprate | 500 | 53.33% | 50% | 60%
021F | 150.7 | Pipe | 2 | 3 | 16 | 0.25 | 30000 | 1 | 7/1/1960 | 1985 | 8.3 | 920 | 0.66667 | 613.3333 | Uprate | 500 | 53.33% | 50% | 60%
021F | 150.7 | Pipe | 100 | 3 | 16 | 0.25 | 30000 | 1 | 7/1/1960 | 1985 | 8.3 | 920 | 0.66667 | 613.3333 | Uprate | 500 | 53.33% | 50% | 60%
021F | 150.7 | Pipe | 220.4 | 3 | 16 | 0.25 | 30000 | 1 | 7/1/1960 | 1985 | 8.3 | 920 | 0.66667 | 613.3333 | Uprate | 500 | 53.33% | 50% | 60%
021F | 150.7 | Pipe | 20 | 3 | 16 | 0.25 | 30000 | 1 | 7/1/1960 | 2012 | 8.3 | 871 | 0.66667 | 580.6667 | Uprate | 500 | 53.33% | 50% | 60%
021F | 151.6 | Pipe | 1.2 | 3 | 16 | 0.25 | 30000 | 1 | 10/28/1960 | 1985 | 8.3 | 920 | 0.66667 | 613.3333 | Uprate | 500 | 53.33% | 50% | 60%
021F | 151.6 | Pipe | 4.4 | 3 | 16 | 0.25 | 30000 | 1 | 10/28/1960 | 1985 | 8.3 | 920 | 0.66667 | 613.3333 | Uprate | 500 | 53.33% | 50% | 60%
021F | 151.6 | Pipe | 193.4 | 3 | 16 | 0.25 | 30000 | 1 | 10/28/1960 | 1985 | 8.3 | 920 | 0.66667 | 613.3333 | Uprate | 500 | 53.33% | 50% | 60%
021F | 151.6 | Pipe | 3.4 | 3 | 16 | 0.25 | 30000 | 1 | 10/28/1960 | 1985 | 8.3 | 920 | 0.66667 | 613.3333 | Uprate | 500 | 53.33% | 50% | 60%
021F | 151.6 | Pipe | 1.2 | 3 | 16 | 0.25 | 30000 | 1 | 10/28/1960 | 1985 | 8.3 | 920 | 0.66667 | 613.3333 | Uprate | 500 | 53.33% | 50% | 60%
021F | 151.6 | Pipe | 1.2 | 3 | 16 | 0.25 | 30000 | 1 | 10/28/1960 | 1985 | 8.3 | 920 | 0.66667 | 613.3333 | Uprate | 500 | 53.33% | 50% | 60%
107 | 162 | Mfg Bend | 1.4 | 3 | 24 | 0.375 | 30000 | 1 | 10/20/1954 | 1977 | 8.5 | 755 | 0.66667 | 503.3333 | STPR | 477 | 50.88% | 50% | 60%
107 | 162 | Mfg Bend | 1.4 | 3 | 24 | 0.375 | 30000 | 1 | 10/20/1954 | 1977 | 8.5 | 755 | 0.66667 | 503.3333 | STPR | 477 | 50.88% | 50% | 60%
107 | 162 | Mfg Bend | 1.4 | 3 | 24 | 0.375 | 30000 | 1 | 10/20/1954 | 1977 | 8.5 | 755 | 0.66667 | 503.3333 | STPR | 477 | 50.88% | 50% | 60%
107 | 162 | Mfg Bend | 1.4 | 3 | 24 | 0.375 | 30000 | 1 | 10/20/1954 | 1977 | 8.5 | 755 | 0.66667 | 503.3333 | STPR | 477 | 50.88% | 50% | 60%
147 | 103.1 | Pipe | 420 | 3 | 24 | 0.313 | 33000 | 0.8 | 11/1/1947 | 2011 | 8.2 | 765 | 0.66667 | 510 | STPR | 365 | 53.01% | 50% | 60%
147 | 103.1 | Pipe | 93 | 3 | 24 | 0.313 | 33000 | 0.8 | 11/1/1947 | 2011 | 8.2 | 765 | 0.66667 | 510 | STPR | 365 | 53.01% | 50% | 60%
147 | 103.1 | Pipe | 4 | 3 | 24 | 0.313 | 33000 | 0.8 | 11/1/1947 | 2011 | 8.2 | 765 | 0.66667 | 510 | STPR | 365 | 53.01% | 50% | 60%
147 | 103.1 | Pipe | 4 | 3 | 24 | 0.313 | 33000 | 0.8 | 11/1/1947 | 2011 | 8.2 | 765 | 0.66667 | 510 | STPR | 365 | 53.01% | 50% | 60%
147 | 103.1 | Pipe | 51 | 3 | 24 | 0.313 | 33000 | 0.8 | 11/1/1947 | 2011 | 8.2 | 765 | 0.66667 | 510 | STPR | 365 | 53.01% | 50% | 60%
147 | 103.1 | Pipe | 10 | 3 | 24 | 0.313 | 33000 | 0.8 | 11/1/1947 | 2011 | 8.2 | 765 | 0.66667 | 510 | STPR | 365 | 53.01% | 50% | 60%
147 | 103.1 | Pipe | 455 | 3 | 24 | 0.313 | 33000 | 0.8 | 11/1/1947 | 2011 | 8.2 | 765 | 0.66667 | 510 | STPR | 365 | 53.01% | 50% | 60%
147 | 103.1 | Pipe | 355 | 3 | 24 | 0.313 | 33000 | 0.8 | 11/1/1947 | 2011 | 8.2 | 765 | 0.66667 | 510 | STPR | 365 | 53.01% | 50% | 60%
147 | 103.6 | Pipe | 90 | 3 | 24 | 0.313 | 33000 | 0.8 | 11/1/1947 | 2011 | 8.2 | 765 | 0.66667 | 510 | STPR | 365 | 53.01% | 50% | 60%
057A-MD1 | 103.05 | Pipe | 75 | 3 | 10.75 | 0.5 | 42000 | 1 | 10/20/1961 | 1981 | 8.3 | 3272 | 0.66667 | 2181.3333 | STPR | 2160 | 55.29% | 50% | 60%
057A-MD1 | 103.1 | Pipe | 146 | 3 | 10.75 | 0.5 | 42000 | 1 | 10/20/1961 | 1981 | 8.3 | 3272 | 0.66667 | 2181.3333 | STPR | 2160 | 55.29% | 50% | 60%
057A-MD1 | 103.1 | Pipe | 55 | 3 | 10.75 | 0.5 | 42000 | 1 | 10/20/1961 | 1981 | 8.3 | 3272 | 0.66667 | 2181.3333 | STPR | 2160 | 55.29% | 50% | 60%
057A-MD1 | 103.1 | Pipe | 2 | 3 | 10.75 | 0.5 | 42000 | 1 | 10/20/1961 | 1981 | 8.3 | 3272 | 0.66667 | 2181.3333 | STPR | 2160 | 55.29% | 50% | 60%
057A-MD1 | 103.1 | Pipe | 35 | 3 | 10.75 | 0.5 | 42000 | 1 | 10/20/1961 | 1981 | 8.3 | 3272 | 0.66667 | 2181.3333 | STPR | 2160 | 55.29% | 50% | 60%
057A-MD1 | 103.1 | Pipe | 2 | 3 | 10.75 | 0.5 | 42000 | 1 | 10/20/1961 | 1981 | 8.3 | 3272 | 0.66667 | 2181.3333 | STPR | 2160 | 55.29% | 50% | 60%
057A-MD1 | 103.1 | Pipe | 14 | 3 | 10.75 | 0.5 | 42000 | 1 | 10/20/1961 | 1981 | 8.3 | 3272 | 0.66667 | 2181.3333 | STPR | 2160 | 55.29% | 50% | 60%
057A-MD1 | 103.1 | Pipe | 37 | 3 | 10.75 | 0.5 | 42000 | 1 | 10/20/1961 | 1981 | 8.3 | 3272 | 0.66667 | 2181.3333 | STPR | 2160 | 55.29% | 50% | 60%
057A-MD1 | 103.1 | Pipe | 315 | 3 | 10.75 | 0.5 | 42000 | 1 | 10/20/1961 | 1981 | 8.3 | 3272 | 0.66667 | 2181.3333 | STPR | 2160 | 55.29% | 50% | 60%
057A-MD1 | 103.1 | Pipe | 58 | 3 | 10.75 | 0.5 | 42000 | 1 | 10/20/1961 | 1981 | 8.3 | 3272 | 0.66667 | 2181.3333 | STPR | 2160 | 55.29% | 50% | 60%
057A-MD1 | 103.1 | Pipe | 48 | 3 | 10.75 | 0.5 | 42000 | 1 | 10/20/1961 | 1981 | 8.3 | 3272 | 0.66667 | 2181.3333 | STPR | 2160 | 55.29% | 50% | 60%
057A-MD1 | 103.1 | Pipe | 3 | 3 | 10.75 | 0.5 | 42000 | 1 | 10/20/1961 | 1981 | 8.3 | 3272 | 0.66667 | 2181.3333 | STPR | 2160 | 55.29% | 50% | 60%
057A-MD1 | 103.1 | Pipe | 1 | 3 | 10.75 | 0.5 | 42000 | 1 | 10/20/1961 | 1981 | 8.3 | 3272 | 0.66667 | 2181.3333 | STPR | 2160 | 55.29% | 50% | 60%
057A-MD1 | 103.1 | Pipe | 23.7 | 3 | 10.75 | 0.5 | 42000 | 1 | 10/20/1961 | 1981 | 8.3 | 3272 | 0.66667 | 2181.3333 | STPR | 2160 | 55.29% | 50% | 60%
057A-MD1 | 103.1 | Pipe | 12 | 3 | 10.75 | 0.5 | 42000 | 1 | 10/20/1961 | 1981 | 8.3 | 3272 | 0.66667 | 2181.3333 | STPR | 2160 | 55.29% | 50% | 60%
057A-MD1 | 103.1 | Pipe | 8 | 3 | 10.75 | 0.5 | 42000 | 1 | 10/20/1961 | 1981 | 8.3 | 3272 | 0.66667 | 2181.3333 | STPR | 2160 | 55.29% | 50% | 60%
057A-MD1 | 103.1 | Pipe | 63 | 3 | 10.75 | 0.5 | 42000 | 1 | 10/20/1961 | 1981 | 8.3 | 3272 | 0.66667 | 2181.3333 | STPR | 2160 | 55.29% | 50% | 60%
057A-MD1 | 103.1 | Pipe | 526.5 | 3 | 10.75 | 0.5 | 42000 | 1 | 10/20/1961 | 1981 | 8.3 | 3272 | 0.66667 | 2181.3333 | STPR | 2160 | 55.29% | 50% | 60%
057A-MD1 | 103.4 | Pipe | 32 | 3 | 10.75 | 0.5 | 42000 | 1 | 10/20/1961 | 1981 | 8.3 | 3272 | 0.66667 | 2181.3333 | STPR | 2160 | 55.29% | 50% | 60%
057A-MD1 | 103.8 | Pipe | 20 | 3 | 10.75 | 0.5 | 42000 | 1 | 10/20/1961 | 1981 | 8.3 | 3272 | 0.66667 | 2181.3333 | STPR | 2160 | 55.29% | 50% | 60%
057A-MD1 | 103.8 | Pipe | 166.5 | 3 | 10.75 | 0.5 | 42000 | 1 | 10/20/1961 | 1981 | 8.3 | 3272 | 0.66667 | 2181.3333 | STPR | 2160 | 55.29% | 50% | 60%
200A-3 | 104 | Pipe | 781 | 2 | 16 | 0.281 | 35000 | 1 | 11/30/1953 | 1988 | 8.8 | 1202 | 0.8 | 961.6 | STPR | 800 | 65.07% | 60% | 72%
200A-3 | 104 | Pipe | 3.1 | 2 | 16 | 0.281 | 35000 | 1 | 11/30/1953 | 1988 | 8.8 | 1202 | 0.8 | 961.6 | STPR | 800 | 65.07% | 60% | 72%
200A-3 | 104 | Mfg Bend | 1.6 | 2 | 16 | 0.312 | 30000 | 1 | 11/30/1953 | 1988 | 8.8 | 1202 | 0.8 | 961.6 | STPR | 800 | 68.38% | 60% | 72%
200A-3 | 104 | Pipe | 54.2 | 2 | 16 | 0.281 | 35000 | 1 | 11/30/1953 | 1988 | 8.8 | 1202 | 0.8 | 961.6 | STPR | 800 | 65.07% | 60% | 72%
200A-3 | 104 | Tee | 2 | 2 | 16 | 0.312 | 30000 | 1 | 11/30/1953 | 1988 | 8.8 | 1202 | 0.8 | 961.6 | STPR | 800 | 68.38% | 60% | 72%
200A-3 | 104 | Pipe | 1 | 2 | 16 | 0.281 | 35000 | 1 | 11/30/1953 | 1988 | 8.8 | 1202 | 0.8 | 961.6 | STPR | 800 | 65.07% | 60% | 72%
200A-3 | 104 | Mfg Bend | 27536.6 | 2 | 16 | 0.3125 | 30000 | 1 | 11/30/1953 | 1988 | 8.8 | 1202 | 0.8 | 961.6 | STPR | 800 | 68.27% | 60% | 72%
300A | 154 | Pipe | 1500 | 2 | 34 | 0.3125 | 52000 | 1 | 12/26/1950 | 2001 | 8 | 895 | 0.8 | 716 | Uprate | 688 | 71.98% | 60% | 72%
300A | 156 | Pipe | 1963 | 2 | 34 | 0.3125 | 52000 | 1 | 12/26/1950 | 2001 | 8 | 895 | 0.8 | 716 | Uprate | 688 | 71.98% | 60% | 72%
300B | 253 | Pipe | 87.6 | 2 | 34 | 0.375 | 52000 | 1 | 12/26/1950 | 2011 | 8.2 | 1031 | 0.8 | 824.8 | STPR | 803 | 70.01% | 60% | 72%
300B | 253 | Pipe | 436.5 | 2 | 34 | 0.375 | 52000 | 1 | 12/26/1950 | 2011 | 8.2 | 1031 | 0.8 | 824.8 | STPR | 803 | 70.01% | 60% | 72%
300B | 253 | Pipe | 734.6 | 2 | 34 | 0.375 | 52000 | 1 | 12/26/1950 | 2011 | 8.2 | 1031 | 0.8 | 824.8 | STPR | 803 | 70.01% | 60% | 72%
300B | 253 | Pipe | 63.7 | 2 | 34 | 0.375 | 52000 | 1 | 12/26/1950 | 2011 | 8.2 | 1031 | 0.8 | 824.8 | STPR | 803 | 70.01% | 60% | 72%
300B | 253 | Pipe | 230.8 | 2 | 34 | 0.375 | 52000 | 1 | 12/26/1950 | 2011 | 8.2 | 1031 | 0.8 | 824.8 | STPR | 803 | 70.01% | 60% | 72%
300B | 253 | Pipe | 53.9 | 2 | 34 | 0.375 | 52000 | 1 | 12/26/1950 | 2011 | 8.2 | 1031 | 0.8 | 824.8 | STPR | 803 | 70.01% | 60% | 72%
300B | 253 | Pipe | 842.3 | 2 | 34 | 0.375 | 52000 | 1 | 12/26/1950 | 2011 | 8.2 | 1031 | 0.8 | 824.8 | STPR | 803 | 70.01% | 60% | 72%
300B | 253 | Pipe | 58.2 | 2 | 34 | 0.375 | 52000 | 1 | 12/26/1950 | 2011 | 8.2 | 1031 | 0.8 | 824.8 | STPR | 803 | 70.01% | 60% | 72%
300B | 253 | Pipe | 147.7 | 2 | 34 | 0.375 | 52000 | 1 | 12/26/1950 | 2011 | 8.2 | 1031 | 0.8 | 824.8 | STPR | 803 | 70.01% | 60% | 72%
300B | 253 | Pipe | 436.4 | 2 | 34 | 0.375 | 52000 | 1 | 12/26/1950 | 2011 | 8.2 | 1031 | 0.8 | 824.8 | STPR | 803 | 70.01% | 60% | 72%
300B | 253 | Pipe | 86 | 2 | 34 | 0.375 | 52000 | 1 | 12/26/1950 | 2011 | 8.2 | 1031 | 0.8 | 824.8 | STPR | 803 | 70.01% | 60% | 72%
300B | 253 | Pipe | 356.3 | 2 | 34 | 0.375 | 52000 | 1 | 12/26/1950 | 2011 | 8.2 | 1031 | 0.8 | 824.8 | STPR | 803 | 70.01% | 60% | 72%
300B | 253 | Pipe | 48.9 | 2 | 34 | 0.375 | 52000 | 1 | 12/26/1950 | 2011 | 8.2 | 1031 | 0.8 | 824.8 | STPR | 803 | 70.01% | 60% | 72%
300B | 253 | Pipe | 185 | 2 | 34 | 0.375 | 52000 | 1 | 12/26/1950 | 2011 | 8.2 | 1031 | 0.8 | 824.8 | STPR | 803 | 70.01% | 60% | 72%
300B | 253 | Pipe | 316 | 2 | 34 | 0.375 | 52000 | 1 | 12/26/1950 | 2011 | 8.2 | 1031 | 0.8 | 824.8 | STPR | 803 | 70.01% | 60% | 72%
300B | 253 | Pipe | 115 | 2 | 34 | 0.375 | 52000 | 1 | 1/1/1966 | 2011 | 8.2 | 1031 | 0.8 | 824.8 | STPR | 803 | 70.01% | 60% | 72%
131 | 172.25 | Reducer | 2 | 3 | 34 | 0.5 | 35000 | 1 | 10/20/1954 | 2011 | 8.4 | 914 | 0.66667 | 609.3333 | STPR | 590 | 57.31% | 50% | 60%
167 | 129 | Pipe | 151 | 3 | 16 | 0.281 | 42000 | 0.8 | 6/11/1954 | 1992 | 8.1 | 1375 | 0.66667 | 916.6667 | STPR | 708 | 59.99% | 50% | 60%
167 | 129 | Pipe | 10 | 3 | 16 | 0.281 | 42000 | 0.8 | 6/11/1954 | 1992 | 8.1 | 1375 | 0.66667 | 916.6667 | STPR | 708 | 59.99% | 50% | 60%
167 | 129 | Pipe | 119 | 3 | 16 | 0.281 | 42000 | 0.8 | 6/11/1954 | 1992 | 8.1 | 1375 | 0.66667 | 916.6667 | STPR | 708 | 59.99% | 50% | 60%
167 | 129 | Pipe | 2 | 3 | 16 | 0.281 | 42000 | 0.8 | 6/11/1954 | 1992 | 8.1 | 1375 | 0.66667 | 916.6667 | STPR | 708 | 59.99% | 50% | 60%
167 | 129 | Pipe | 57 | 3 | 16 | 0.281 | 42000 | 0.8 | 6/11/1954 | 1992 | 8.1 | 1375 | 0.66667 | 916.6667 | STPR | 708 | 59.99% | 50% | 60%
167 | 129 | Pipe | 11 | 3 | 16 | 0.281 | 42000 | 0.8 | 6/11/1954 | 1992 | 8.1 | 1375 | 0.66667 | 916.6667 | STPR | 708 | 59.99% | 50% | 60%
167 | 129 | Pipe | 4 | 3 | 16 | 0.281 | 42000 | 0.8 | 6/11/1954 | 1992 | 8.1 | 1375 | 0.66667 | 916.6667 | STPR | 708 | 59.99% | 50% | 60%
167 | 129 | Pipe | 13 | 3 | 16 | 0.281 | 42000 | 0.8 | 6/11/1954 | 1992 | 8.1 | 1375 | 0.66667 | 916.6667 | STPR | 708 | 59.99% | 50% | 60%
167 | 129 | Pipe | 4 | 3 | 16 | 0.281 | 42000 | 0.8 | 6/11/1954 | 1992 | 8.1 | 1375 | 0.66667 | 916.6667 | STPR | 708 | 59.99% | 50% | 60%
167 | 129 | Pipe | 8 | 3 | 16 | 0.281 | 42000 | 0.8 | 6/11/1954 | 1992 | 8.1 | 1375 | 0.66667 | 916.6667 | STPR | 708 | 59.99% | 50% | 60%
167 | 129 | Pipe | 55 | 3 | 16 | 0.281 | 42000 | 0.8 | 6/11/1954 | 1992 | 8.1 | 1375 | 0.66667 | 916.6667 | STPR | 708 | 59.99% | 50% | 60%
167 | 129 | Pipe | 37 | 3 | 16 | 0.281 | 42000 | 0.8 | 6/11/1954 | 1992 | 8.1 | 1375 | 0.66667 | 916.6667 | STPR | 708 | 59.99% | 50% | 60%
167 | 129 | Pipe | 115 | 3 | 16 | 0.281 | 42000 | 0.8 | 6/11/1954 | 1992 | 8.1 | 1375 | 0.66667 | 916.6667 | STPR | 708 | 59.99% | 50% | 60%
167 | 130 | Pipe | 216 | 3 | 16 | 0.281 | 42000 | 0.8 | 6/11/1954 | 1992 | 8.1 | 1375 | 0.66667 | 916.6667 | STPR | 708 | 59.99% | 50% | 60%
167 | 130 | Pipe | 11 | 3 | 16 | 0.281 | 42000 | 0.8 | 6/11/1954 | 1992 | 8.1 | 1375 | 0.66667 | 916.6667 | STPR | 708 | 59.99% | 50% | 60%
300A | 228.7 | Pipe | 50 | 2 | 34 | 0.375 | 52000 | 1 | 6/18/1954 | 2011 | 8.2 | 970 | 0.8 | 776 | STPR | 757 | 65.99% | 60% | 72%
300A | 228.7 | Pipe | 654 | 2 | 34 | 0.375 | 52000 | 1 | 6/18/1954 | 2011 | 8.2 | 970 | 0.8 | 776 | STPR | 757 | 65.99% | 60% | 72%
300A | 228.7 | Pipe | 553.3 | 2 | 34 | 0.375 | 52000 | 1 | 6/18/1954 | 2011 | 8.2 | 970 | 0.8 | 776 | STPR | 757 | 65.99% | 60% | 72%
300A | 233 | Pipe | 100 | 2 | 34 | 0.375 | 52000 | 1 | 6/18/1954 | 2011 | 8.1 | 970 | 0.8 | 776 | STPR | 757 | 65.99% | 60% | 72%
300A | 233 | Pipe | 576 | 2 | 34 | 0.375 | 52000 | 1 | 6/18/1954 | 2011 | 8.1 | 970 | 0.8 | 776 | STPR | 757 | 65.99% | 60% | 72%
300A | 395.6 | Pipe | 8.7 | 3 | 34 | 0.344 | 52000 | 1 | 12/29/1950 | 1977 | 8.2 | 1048 | 0.66667 | 698.6667 | STPR | 631 | 59.97% | 50% | 60%
300A | 395.6 | Pipe | 92.3 | 3 | 34 | 0.344 | 52000 | 1 | 12/29/1950 | 1977 | 8.2 | 1048 | 0.66667 | 698.6667 | STPR | 631 | 59.97% | 50% | 60%
300A | 395.6 | Pipe | 174.7 | 3 | 34 | 0.344 | 52000 | 1 | 12/29/1950 | 1977 | 8.2 | 1048 | 0.66667 | 698.6667 | STPR | 631 | 59.97% | 50% | 60%
300A | 395.6 | Pipe | 335.7 | 3 | 34 | 0.344 | 52000 | 1 | 12/29/1950 | 1977 | 8.2 | 1048 | 0.66667 | 698.6667 | STPR | 631 | 59.97% | 50% | 60%
300A | 395.6 | Pipe | 2.3 | 3 | 34 | 0.344 | 52000 | 1 | 12/29/1950 | 1977 | 8.2 | 1048 | 0.66667 | 698.6667 | STPR | 631 | 59.97% | 50% | 60%
300A | 395.6 | Pipe | 50 | 3 | 34 | 0.344 | 52000 | 1 | 12/29/1950 | 1977 | 8.2 | 1048 | 0.66667 | 698.6667 | STPR | 631 | 59.97% | 50% | 60%
300A | 395.6 | Pipe | 29.7 | 3 | 34 | 0.344 | 52000 | 1 | 12/29/1950 | 1977 | 8.2 | 1048 | 0.66667 | 698.6667 | STPR | 631 | 59.97% | 50% | 60%
300A | 395.6 | Pipe | 137.9 | 3 | 34 | 0.344 | 52000 | 1 | 12/29/1950 | 1977 | 8.2 | 1048 | 0.66667 | 698.6667 | STPR | 631 | 59.97% | 50% | 60%
300A | 395.6 | Pipe | 22.1 | 3 | 34 | 0.344 | 52000 | 1 | 12/29/1950 | 1977 | 8.2 | 1048 | 0.66667 | 698.6667 | STPR | 631 | 59.97% | 50% | 60%
300A | 395.6 | Pipe | 50 | 3 | 34 | 0.344 | 52000 | 1 | 12/29/1950 | 1977 | 8.2 | 1048 | 0.66667 | 698.6667 | STPR | 631 | 59.97% | 50% | 60%
300A | 395.6 | Pipe | 340 | 3 | 34 | 0.344 | 52000 | 1 | 12/29/1950 | 1977 | 8.2 | 1048 | 0.66667 | 698.6667 | STPR | 631 | 59.97% | 50% | 60%
300A | 395.6 | Pipe | 50 | 3 | 34 | 0.344 | 52000 | 1 | 12/29/1950 | 1977 | 8.2 | 1048 | 0.66667 | 698.6667 | STPR | 631 | 59.97% | 50% | 60%
300A | 395.7 | Pipe | 30 | 3 | 34 | 0.344 | 52000 | 1 | 12/29/1950 | 2011 | 9.8 | 970 | 0.66667 | 646.6667 | STPR | 631 | 59.97% | 50% | 60%
300A | 395.7 | Pipe | 60 | 3 | 34 | 0.344 | 52000 | 1 | 12/29/1950 | 2011 | 9.8 | 970 | 0.66667 | 646.6667 | STPR | 631 | 59.97% | 50% | 60%
300A | 395.7 | Pipe | 13 | 3 | 34 | 0.344 | 52000 | 1 | 12/29/1950 | 2011 | 9.8 | 970 | 0.66667 | 646.6667 | STPR | 631 | 59.97% | 50% | 60%
300A | 395.7 | Pipe | 79 | 3 | 34 | 0.344 | 52000 | 1 | 12/29/1950 | 2011 | 9.8 | 970 | 0.66667 | 646.6667 | STPR | 631 | 59.97% | 50% | 60%
300A | 395.7 | Pipe | 125.2 | 3 | 34 | 0.344 | 52000 | 1 | 12/29/1950 | 2011 | 9.8 | 970 | 0.66667 | 646.6667 | STPR | 631 | 59.97% | 50% | 60%
300A | 395.7 | Pipe | 342.8 | 3 | 34 | 0.344 | 52000 | 1 | 12/29/1950 | 2011 | 9.8 | 970 | 0.66667 | 646.6667 | STPR | 631 | 59.97% | 50% | 60%
300A | 396.6 | Mfg Bend | 0.6 | 3 | 34 | 0.4063 | 50000 | 1 | 12/29/1950 | 2001 | 8.4 | 1198 | 0.66667 | 798.6667 | STPR | 631 | 52.8% | 50% | 60%
400 | 209 | Pipe | 1137.8 | 2 | 36 | 0.453 | 52000 | 1 | 12/7/1961 | 1980 | 8.2 | 1189 | 0.8 | 951.2 | STPR | 915 | 69.92% | 60% | 72%
SP3 | 160.36 | Pipe | 8 | 3 | 16 | 0.25 | 28000 | 0.8 | 1/1/1930 | 1995 | 9 | 630 | 0.66667 | 420 | STPR | 380 | 54.29% | 50% | 60%
SP3 | 160.36 | Pipe | 25.7 | 3 | 16 | 0.25 | 28000 | 0.8 | 1/1/1930 | 1995 | 9 | 630 | 0.66667 | 420 | STPR | 380 | 54.29% | 50% | 60%
SP3 | 160.36 | Pipe | 1 | 3 | 16 | 0.25 | 28000 | 0.8 | 1/1/1930 | 1995 | 9 | 630 | 0.66667 | 420 | STPR | 380 | 54.29% | 50% | 60%
SP3 | 160.4 | Pipe | 1 | 3 | 16 | 0.25 | 28000 | 0.8 | 1/1/1930 | 1995 | 9 | 630 | 0.66667 | 420 | STPR | 420 | 60% | 50% | 60%
SP3 | 160.4 | Pipe | 0.6 | 3 | 16 | 0.25 | 28000 | 0.8 | 1/1/1930 | 1995 | 9 | 630 | 0.66667 | 420 | STPR | 420 | 60% | 50% | 60%
SP3 | 160.4 | Pipe | 0.5 | 3 | 16 | 0.25 | 28000 | 0.8 | 1/1/1930 | 1995 | 9 | 630 | 0.66667 | 420 | STPR | 420 | 60% | 50% | 60%
SP3 | 160.5 | Pipe | 1 | 3 | 16 | 0.25 | 28000 | 0.8 | 1/1/1930 | 1995 | 9 | 630 | 0.66667 | 420 | STPR | 420 | 60% | 50% | 60%
SP3 | 160.5 | Pipe | 101.2 | 3 | 16 | 0.25 | 28000 | 0.8 | 1/1/1930 | 1995 | 9 | 630 | 0.66667 | 420 | STPR | 420 | 60% | 50% | 60%
SP3 | 160.6 | Pipe | 94 | 3 | 16 | 0.25 | 28000 | 0.8 | 1/1/1930 | 1995 | 9 | 630 | 0.66667 | 420 | STPR | 420 | 60% | 50% | 60%