## Wood Pole Inspections
TABLE A-1
2002 GENERAL ORDER 165 ANNUAL REPORT
Reporting Period: 01/01/02 - 12/31/02
PacifiCorp Wood Pole Inspections
DISTRICT | NO. OF FACILITIES |  | INSPECTION TYPE
| Distribution Poles | Transmission Poles | O/H Safety (Patrol) | % Comp. | O/H Detail | % Comp. | O/H Test & Treat (Intrusive) | % Comp.
Inspection Cycle |  |  | 2 Yrs | 50% | 5 Yrs | 20% | 10 Yrs | 10%
Tulelake | 13485 | 1713 | 7143 | 47% | 1332 | 8.764% | 1332 | 8.764%
Alturas | 3826 | 1123 | 2882 | 58.23% | 1329 | 26.85% | 1329 | 26.85%
Crescent City | 9533 | 460 | 3770 | 37.73% | 2144 | 21.46% | 653 | 6.535%
Yreka/Mt. Shasta | 33745 | 1620 | 23396 | 69.33% | 6940 | 19.62% | 3151 | 8.91%
Main Grid |  | 2317 | 1472 | 63.53% | 1472 | 63.53% | 0 | 0%
California Totals | 60589 | 7233 | 38663 | 57.01% | 13217 | 19.49% | 6465 | 9.532%
Note on F8: Mike D Strickler: FP24 Report: OHDIST OHTRANS IT DETAIL IT DTLTRT IT CLIMBING
Note on H8: Mike D Strickler: FP24 Report: OHDIST OHTRANS IT TSTRT IT DTLTRT
Note on D8: Mike D Strickler: FP24 Report: OHDIST OHTRANS IT SAFETY IT DETAIL IT DTLTRT
Note on F11: Jack G Vranish: includes detail test and treats miscoded to test and treat only

## Line Equpment Inspections
TABLE A-2
2002 GENERAL ORDER 165 ANNUAL REPORT
Reporting Period: 01/01/02- 12/31/02
PacifiCorp Line Equipment Inspections
District/Equipment | Type | QTY | Safety (Patrol) Rural (1) |  |  | Detailed Rural (1)
|  |  | Plan (2) | Actual | % Complete | Plan (2) | Actual | % Complete
|  |  | 2 Yrs |  | 50% | 4 or 5 Yrs |  | 20-25%
Tulelake
Transformers | Overhead | 2589 | 1294.5 | 1533.5971 | 47% | 517.8 | 285.9795 | 8.764%
Switch/Protect Device | Overhead | 596 | 298 |  |  | 119.2
Regs/Caps | Overhead | 78 | 39 |  |  | 15.6
All | Pad Mounted | 216 |  |  |  | 54 | 0 | 0%
Total |  |  | 1631.5 | 1533.5971 |  | 706.6 | 285.9795 | 8.22%
Alturas
Transformers | Overhead | 1033 | 516.5 | 1013.2714 | 58.23% | 206.6 | 467.258 | 26.85%
Switch/Protect Device | Overhead | 706 | 353 |  |  | 141.2
Regs/Caps | Overhead | 1 | 0.5 |  |  | 0.2
All | Pad Mounted | 177 |  |  |  | 44.25 | 0 | 0%
Total |  |  | 870 | 1013.2714 |  | 392.25 | 467.258 | 24.37%
Crescent City
Transformers | Overhead | 3461 | 1730.5 | 1573.1912 | 37.73% | 692.2 | 894.6743 | 21.46%
Switch/Protect Device | Overhead | 706 | 353 |  |  | 141.2
Regs/Caps | Overhead | 3 | 1.5 |  |  | 0.6
All | Pad Mounted | 2739 |  |  |  | 684.75 | 37 | 1.351%
Total |  |  | 2085 | 1573.1912 |  | 1518.75 | 931.6743 | 13.48%
Yreka/Mt. Shasta
Transformers | Overhead | 7172 | 3586 | 5329.5318 | 69.33% | 1434.4 | 1508.4909 | 19.62%
Switch/Protect Device | Overhead | 485 | 242.5 |  |  | 97
Regs/Caps | Overhead | 30 | 15 |  |  | 6
All | Pad Mounted | 1898 |  |  |  | 474.5 | 520 | 27.4%
Total |  |  | 3843.5 | 5329.5318 |  | 2011.9 | 2028.4909 | 21.16%
California Totals
Transformers | Overhead | 14255 | 7127.5 | 9449.5916 | 56.05% | 2851 | 3156.4027 | 18.72%
Switch/Protect Device | Overhead | 2493 | 1246.5 |  |  | 498.6
Regs/Caps | Overhead | 112 | 56 |  |  | 22.4
All | Pad Mounted | 5030 |  |  |  | 1257.5 | 557 | 11.07%
NOTES:
1. PacifiCorp has no Urban area in its California service territory.
Urban is defined as those areas with a population of more than 1,000 persons per square mile and Rural as those
with a population less than 1,000 persons per square mile as determined by the U.S. Bureau of the Census.
2001 results are:
7.0 persons/sq.mi. | Siskiyou County (Tulelake, Yreka, Mt. Shasta)
27.3 persons/sq.mi. | Del Norte County (Crescent City)
2.4 persons/sq.mi. | Modoc County (Alturas)
2. Planned inspection cycles: | Patrol |  | Detailed
Overhead | 2 years |  | 5 years
Pad Mounted |  |  | 4 years
3. Due to calendar year reporting vs. fiscal year operations, some variances to plan are artifacts of timing differences.
4. Device counts for overhead equipment are from mapping records, with the exception of Yreka where digitized maps are not yet available. Line inspections include an inspection of all equipment on the line, therefore inspection percentages for overhead equipment is calculated at the same percentage as poles inspected.
Note on E8: Mike D Strickler: Value is calculated from percentage of poles detailed in the district times quantity of equipment in column B
Note on H8: Mike D Strickler: FP24 Report: OHDIST IT DETAIL and UGDIST IT DETAIL
Note on B14: Jack G Vranish: incl vaults & equipment
Note on B20: Jack G Vranish: incl vaults & equipment
Note on B26: Jack G Vranish: incl vaults & equipment
Note on B32: Jack G Vranish: incl vaults & equipment
Note on B38: Jack G Vranish: incl vaults & equipment
Note on C7: Jack G Vranish: OH quantities from Mapping except for Yreka - these are from FPI. Padmount qty from FpiI - total facility count

## Wood Pole-St Light Conditions
TABLE B-1
2002 GENERAL ORDER 165 ANNUAL REPORT
Reporting Period: 01/01/02 - 12/31/02
PacifiCorp Wood Pole Conditions
DISTRICT | CONDITIONS FOUND |  | CONDITIONS CORRECTED |  | CONDITIONS OUTSTANDING |  | REASON WHY CORRECTION IS OUTSTANDING | DATE CORRECTION WILL BE COMPLETED BY
| A | B | A | B | A | B
Tulelake | 19 | 37 | 3 | 114 | 16 | 27 | Scheduled in next calendar year | 2003-12-31
Alturas | 36 | 58 | 9 | 25 | 11 | 47 | Scheduled in next calendar year | 2003-12-31
Crescent City | 0 | 90 | 1 | 14 | 0 | 83 | Scheduled in next calendar year | 2003-12-31
Yreka/Mt. Shasta | 98 | 231 | 57 | 138 | 87 | 217 | Scheduled in next calendar year | 2003-12-31
California Total | 153 | 416 | 70 | 291 | 114 | 374
PacifiCorp Street Light Conditions
DISTRICT | CONDITIONS FOUND |  | CONDITIONS CORRECTED |  | CONDITIONS OUTSTANDING |  | REASON WHY CORRECTION IS OUTSTANDING | DATE CORRECTION WILL BE COMPLETED BY
| A | B | A | B | A | B
Tulelake | 0 | 0 | 0 | 1 | 0 | 23 | Scheduled in next calendar year. | 2003-12-31
Alturas | 0 | 0 |  | 0 | 0 | 10 | Scheduled in next calendar year. | 2003-12-31
Crescent City | 0 | 0 | 0 | 2 | 0 | 0
Yreka/Mt. Shasta | 0 | 0 | 0 | 20 | 0 | 0
California Total | 0 | 0 | 0 | 23 | 0 | 33
Note on B7: Mike D Strickler: FP24 Report: CO BOPOLE _ I
Note on D7: Mike D Strickler: FP24 Report: CO BOPOLE _ C
Note on F7: Mike D Strickler: FP24 Report: CO BOPOLE _ O
Note on B20: Mike D Strickler: FP24 Report: CO BOLIGHT _ I
Note on D20: Mike D Strickler: FP24 Report: CO BOLIGHT _ C
Note on F20: Mike D Strickler: FP24 Report: CO BOLIGHT _ O

## Equipment Conditions
TABLE B-2
2002 GENERAL ORDER 165 ANNUAL REPORT
Reporting Period: 01/01/02 - 12/31/02
PacifiCorp Equipment Conditions
DISTRICT | Type | CONDITION RATING FOUND |  | CORRECTIVE ACTIONS COMPLETED |  | CONDITIONS OUTSTANDING |  | REASON WHY CORRECTION IS OUTSTANDING | DATE CORRECTION WILL BE COMPLETED BY
|  | A | B | A | B | A | B
Tulelake
Transformers | Overhead | 0 | 0 | 0 | 1 | 0 | 0
Switch/Protect Device | Overhead | 0 | 1 | 0 | 0 | 0 | 4 | Scheduled next calendar year. | 2003-12-31
Regs/Caps | Overhead | 0 | 0 | 0 | 0 | 0 | 0
All | Padmounted | 0 | 0 | 0 | 0 | 0 | 0
Alturas
Transformers | Overhead | 0 | 2 | 0 | 0 | 0 | 2 | Scheduled next calendar year | 2003-12-31
Switch/Protect Device | Overhead | 0 | 1 | 0 | 1 | 0 | 0
Regs/Caps | Overhead | 0 | 0 | 0 | 0 | 0 | 0
All | Padmounted | 0 | 0 | 0 | 0 | 0 | 0
Crescent City
Transformers | Overhead | 0 | 1 | 0 | 1 | 0 | 0
Switch/Protect Device | Overhead | 0 | 5 | 0 | 1 | 0 | 5 | Scheduled next calendar year | 2003-12-31
Regs/Caps | Overhead | 0 | 0 | 0 | 0 | 0 | 0
All | Padmounted | 0 | 6 | 0 | 3 | 0 | 6 | Scheduled next calendar year | 2003-12-31
Yreka/Mt. Shasta
Transformers | Overhead | 1 | 3 | 0 | 13 | 0 | 2 | Scheduled next calendar year | 2003-12-30
Switch/Protect Device | Overhead | 2 | 31 | 2 | 42 | 0 | 7 | Scheduled next calendar year | 2003-12-31
Regs/Caps | Overhead | 0 | 0 | 1 | 0 | 0 | 0
All | Padmounted | 0 | 5 | 0 | 4 | 0 | 1 | Scheduled next calendar year | 2003-12-31
CA Total
Transformers | Overhead | 1 | 6 | 0 | 15 | 0 | 4
Switch/Protect Device | Overhead | 2 | 38 | 2 | 44 | 0 | 16
Regs/Caps | Overhead | 0 | 0 | 1 | 0 | 0 | 0
All | Padmounted | 0 | 11 | 0 | 7 | 0 | 7
California Totals |  | 3 | 55 | 3 | 66 | 0 | 27