## A-1 Wood Pole Inspections
TABLE A-1
2004 GENERAL ORDER 165 ANNUAL REPORT
Reporting Period: 01/01/04 - 12/31/04
PacifiCorp Wood Pole Inspections
DISTRICT | NO. OF FACILITIES |  | INSPECTION TYPE
| Distribution Poles | Transmission Poles | O/H Safety (Patrol) | % Comp. | O/H Detail | % Comp. | O/H Test & Treat (Intrusive) | % Comp.
Inspection Cycle |  |  | 2 Yrs | 50% | 5 Yrs | 20% | 15 Yrs | 7%
Tulelake | 13450 | 1714 | 12832 | 84.62% | 3668 | 24.19% | 1046 | 6.898%
Alturas | 4558 | 1126 | 4930 | 86.73% | 1478 | 26% | 0 | 0%
Crescent City | 9538 | 696 | 7739 | 75.62% | 2041 | 19.94% | 543 | 5.306%
Yreka/Mt. Shasta | 33779 | 1777 | 34195 | 96.17% | 4700 | 13.22% | 3574 | 10.05%
Main Grid | 0 | 3726 | 8615 | 231.2% | 2672 | 71.71% | 0 | 0%
California Totals | 61325 | 9039 | 68311 | 97.08% | 14559 | 20.69% | 5163 | 7.338%
Note on D8: Patience Kerchinsky: FP24 Report: OHDIST OHTRANS IT SAFETY IT DETAIL IT DTLTRT
Note on F8: Patience Kerchinsky: FP24 Report: OHDIST OHTRANS IT DETAIL IT DTLTRT IT CLIMBING
Note on H8: Patience Kerchinsky: FP24 Report: OHDIST OHTRANS IT TSTTRT IT DTLTRT
Note on F11: Patience Kerchinsky: includes detail test and treats miscoded to test and treat only
Note on B8: Patience Kerchinsky: Counts sourced from FPI web page report dated 3/11/2004
Note on C8: Patience Kerchinsky: Counts sourced from FPI web page report dated 3/11/2004
Note on C19: Patience Kerchinsky: Data sourced from FPI Database 6/15/05 - Counts from 2004 are not available

## A-2 Line Equpment Inspections
TABLE A-2
2004 GENERAL ORDER 165 ANNUAL REPORT
Reporting Period: 01/01/04- 12/31/04
PacifiCorp Line Equipment Inspections
District/Equipment | Type | QTY | Safety (Patrol) Rural (1) |  |  | Detailed Rural (1)
|  |  | Plan (2) | Actual | % Complete | Plan (2) | Actual | % Complete
|  |  | 2 Yrs |  | 50% | 4 or 5 Yrs |  | 20-25%
Tulelake
Transformers | Overhead | 2581 | 1290.5 | 2695.1939 | 84.62% | 516.2 | 770.4155 | 24.19%
Switch/Protect Device | Overhead | 558 | 279 |  |  | 111.6
Regs/Caps | Overhead | 46 | 23 |  |  | 9.2
All | Pad Mounted | 75 |  |  |  | 18.75 | 22.028 | 29.37%
Total |  |  | 1592.5 | 2695.1939 |  | 655.75 | 792.4434 | 24.31%
Alturas
Transformers | Overhead | 1035 | 517.5 | 1022.602 | 86.73% | 207 | 306.5732 | 26%
Switch/Protect Device | Overhead | 143 | 71.5 |  |  | 28.6
Regs/Caps | Overhead | 1 | 0.5 |  |  | 0.2
All | Pad Mounted | 44 |  |  |  | 11 | 3.25 | 7.386%
Total |  |  | 589.5 | 1022.602 |  | 246.8 | 309.8232 | 25.33%
Crescent City
Transformers | Overhead | 3477 | 1738.5 | 3267.561 | 75.62% | 695.4 | 861.7511 | 19.94%
Switch/Protect Device | Overhead | 843 | 421.5 |  |  | 168.6
Regs/Caps | Overhead | 1 | 0.5 |  |  | 0.2
All | Pad Mounted | 1100 |  |  |  | 275 | 85.5734 | 7.779%
Total |  |  | 2160.5 | 3267.561 |  | 1139.2 | 947.3245 | 17.48%
Yreka/Mt. Shasta
Transformers | Overhead | 9191 | 4595.5 | 11127.1276 | 96.17% | 1838.2 | 1529.3903 | 13.22%
Switch/Protect Device | Overhead | 2339 | 1169.5 |  |  | 467.8
Regs/Caps | Overhead | 40 | 20 |  |  | 8
All | Pad Mounted | 3226 |  |  |  | 806.5 | 1303.186 | 40.4%
Total |  |  | 5785 | 11127.1276 |  | 3120.5 | 2832.5762 | 19.14%
California Totals
Transformers | Overhead | 16284 | 8142 | 18112.4845 | 89.42% | 3256.8 | 3468.13 | 17.12%
Switch/Protect Device | Overhead | 3883 | 1941.5 |  |  | 776.6
Regs/Caps | Overhead | 88 | 44 |  |  | 17.6
All | Pad Mounted | 4445 |  |  |  | 1111.25 | 1414.0374 | 31.81%
NOTES:
1. PacifiCorp has no Urban area in its California service territory.
Urban is defined as those areas with a population of more than 1,000 persons per square mile and Rural as those
with a population less than 1,000 persons per square mile as determined by the U.S. Bureau of the Census.
U. S. Bureau of the Census reports the population densities below (using 2000 Census data)
Each of these counties is reported to have a reducing population
7.0 persons/sq.mi. | Siskiyou County (Tulelake, Yreka, Mt. Shasta)
27.3 persons/sq.mi. | Del Norte County (Crescent City)
2.4 persons/sq.mi. | Modoc County (Alturas)
2. Planned inspection cycles: | Patrol |  | Detailed
Overhead | 2 years |  | 5 years
Pad Mounted |  |  | 4 years
3. Due to calendar year reporting vs. fiscal year operations, some variances to plan are artifacts of timing differences.
Note on C7: Patience Kerchinsky: OH quantities from Mapping
Note on E8: Patience Kerchinsky: Value is calculated from percentage of poles detailed in the district times quantity of equipment in column B
Note on H8: Patience Kerchinsky: FP24 Report: OHDIST IT DETAIL and UGDIST IT DETAIL

## B-1 Wood Pole-St Light Cond
TABLE B-1
2004 GENERAL ORDER 165 ANNUAL REPORT
Reporting Period: 01/01/04 - 12/31/04
PacifiCorp Wood Pole Conditions
DISTRICT | CONDITIONS FOUND |  | CONDITIONS CORRECTED |  | REMOVED FROM SYSTEM |  | CONDITIONS OUTSTANDING |  | REASON WHY CORRECTION IS OUTSTANDING | DATE CORRECTION WILL BE COMPLETED BY
| A | B | A | B | A | B | A | B
Tulelake | 2 | 178 | 18 | 75 | 0 | 3 | 11 | 186 | A's planned to be completed by end of 2005; B's planned to be corrected by end of 2006 | Per note
Alturas | 2 | 7 | 5 | 43 | 1 | 1 | 1 | 6 | A's planned to be completed by end of 2005; B's planned to be corrected by end of 2006 | Per note
Crescent City | 17 | 130 | 33 | 69 | 0 | 2 | 15 | 143 | A's planned to be completed by end of 2005; B's planned to be corrected by end of 2006 | Per note
Yreka/Mt. Shasta | 175 | 467 | 155 | 243 | 9 | 47 | 170 | 1006 | A's planned to be completed by end of 2005; B's planned to be corrected by end of 2006 | Per note
California Total | 196 | 782 | 211 | 430 | 10 | 53 | 197 | 1341
PacifiCorp Street Light Conditions
DISTRICT | CONDITIONS FOUND |  | CONDITIONS CORRECTED |  | REMOVED FROM SYSTEM |  | CONDITIONS OUTSTANDING |  | REASON WHY CORRECTION IS OUTSTANDING | DATE CORRECTION WILL BE COMPLETED BY
| A | B | A | B | A | B | A | B
Tulelake | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0
Alturas | 0 | 84 | 0 | 12 | 0 | 0 | 0 | 84 | B's planned to be corrected by end of 2006 | 2006-12-31
Crescent City | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | B's planned to be corrected by end of 2006 | 2006-12-31
Yreka/Mt. Shasta | 0 | 44 | 0 | 0 | 0 | 0 | 1 | 78 | A's planned to be completed by end of 2005; B's planned to be corrected by end of 2006 | Per note
California Total | 0 | 129 | 0 | 28 | 0 | 0 | 1 | 163
Note on B7: Patience Kerchinsky: FP24 Report: CO BOPOLE _ I
Note on D7: Patience Kerchinsky: FP24 Report: CO BOPOLE _ C
Note on F7: Patience Kerchinsky: FP24 Report: CO BOPOLE _ R
Note on H7: Patience Kerchinsky: FP24 Report: CO BOPOLE _ O I_CO_BOPOLE_C I_CO_BOPOLE_R
Note on B22: Patience Kerchinsky: FP24 Report: CO BOLIGHT _ I
Note on D22: Patience Kerchinsky: FP24 Report: CO BOLIGHT _ C
Note on F22: Patience Kerchinsky: FP24 Report: CO BOLIGHT _ R
Note on H22: Patience Kerchinsky: FP24 Report: CO BOLIGHT _ O I_CO_BOLIGHT_C I_CO_BOLIGHT_R

## B-2 Equipment Conditions
TABLE B-2
2004 GENERAL ORDER 165 ANNUAL REPORT
Reporting Period: 01/01/04 - 12/31/04
PacifiCorp Equipment Conditions
DISTRICT | Type | CONDITION RATING FOUND |  | CORRECTIVE ACTIONS COMPLETED |  | REMOVED FROM SYSTEM |  | CONDITIONS OUTSTANDING |  | REASON WHY CORRECTION IS OUTSTANDING | DATE CORRECTION WILL BE COMPLETED BY
|  | A | B | A | B | A | B | A | B
Tulelake
Transformers | Overhead | 1 | 1 | 0 | 20 | 0 | 0 | 1 | 5 | A's Scheduled next calendar year, B's scheduled for 2006 calendar year. | Per note
Switch/Protect Device | Overhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Regs/Caps | Overhead | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
All | Padmounted | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alturas
Transformers | Overhead | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | Scheduled for 2006 calendar year | 2006-12-31
Switch/Protect Device | Overhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Regs/Caps | Overhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All | Padmounted | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Crescent City
Transformers | Overhead | 0 | 3 | 0 | 3 | 0 | 1 | 0 | 8 | Scheduled for 2006 calendar year | 2006-12-31
Switch/Protect Device | Overhead | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 4 | Scheduled for 2006 calendar year | 2006-12-31
Regs/Caps | Overhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All | Padmounted | 1 | 0 | 1 | 4 | 0 | 0 | 0 | 0
Yreka
Transformers | Overhead | 6 | 13 | 0 | 2 | 0 | 0 | 6 | 15 | A's Scheduled next calendar year, B's scheduled for 2006 calendar year. | Per note
Switch/Protect Device | Overhead | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8
Regs/Caps | Overhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All | Padmounted | 2 | 5 | 0 | 0 | 0 | 0 | 2 | 5 | A's Scheduled next calendar year, B's scheduled for 2006 calendar year. | Per note
Mt. Shasta
Transformers | Overhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Switch/Protect Device | Overhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Regs/Caps | Overhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All | Padmounted | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CA Total
Transformers | Overhead | 7 | 18 | 0 | 25 | 0 | 1 | 7 | 30
Switch/Protect Device | Overhead | 0 | 6 | 0 | 1 | 0 | 0 | 0 | 12
Regs/Caps | Overhead | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
All | Padmounted | 3 | 5 | 1 | 4 | 0 | 0 | 2 | 5
California Totals |  | 10 | 29 | 1 | 31 | 0 | 1 | 9 | 47
Note on C7: Fpi Trans: co_boxfrmr_i Sw/pr: co_borecl_i + co_boptsw_i reg/cap: co_boreg_i + co_bocap_i pad: co_bopadvlt_i
Note on E7: Fpi Trans:co_boxfrmr_c Sw/pr: co_borecl_c + co_boptsw_c reg/cap:co_boreg_c + co_bocap_c pad: co_bopadvlt_c
Note on I7: Patience Kerchinsky: Fpi (must use ignore corrected and removed, leave start date blank) Trans: co_boxfrmr_o i_co_boxfrmr_c i_co_boxfrmr_r Sw/pr: co_borecl_o i_co_borecl_c i_co_borecl_r + co_boptsw_o i_co_boptsw_c i_co_boptsw_r reg/cap:co_boreg_o i_co_boreg_c i_co_boreg_r + co_bocap_o i_co_bocap_c i_co_bocap_r pad: co_bopadvlt_o i_co_bopadvlt_c i_co_bopadvlt_r

## don't print FPI Data
| OH DIST |  |  |  | OHTRANS |  |  |  | UGDIST
District | SAFETY | DETAIL | DTLTRT | TSTTRT | SAFETY | DETAIL | DTLTRT | TSTTRT | DETAIL
Klamath Falls 650 | 6706 | 1882 | 873 | 0 | 2458 | 740 | 173 | 0 | 42
Alturas 651 | 1857 | 829 | 0 | 0 | 1595 | 649 | 0 | 0 | 13
Crescent City 654 | 5453 | 1055 | 543 | 0 | 245 | 443 | 0 | 0 | 213
Yreka 655 | 25812 | 848 | 2959 | 0 | 3683 | 278 | 615 | 0 | 1855
Mt. Shasta 656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Main Grid 960 |  |  |  |  | 8615 | 2672 | 0 | 0 | 0
UG Totals | Total UG Count |  | % Complete
Klamath Falls 650 | 143 |  | 29.37%
Alturas 651 | 176 |  | 7.386%
Crescent City 654 | 2738 |  | 7.779%
Yreka 655 | 4592 |  | 40.4%
Mt. Shasta 656 | 0 |  | N/A
Main Grid 960 | 0 |  | N/A
Note on E4: Patience Kerchinsky: Added to DTLTRT Totals was 485
Note on I4: Patience Kerchinsky: Added to DTLTRT Totals Was 173
Note on B1: Patience Kerchinsky: Sourced from FPI
Note on F1: Patience Kerchinsky: Sourced from FPI
Note on J1: Patience Kerchinsky: Sourced from FPI
Note on B17: Patience Kerchinsky: Counts sourced from FPI web page report dated 3/11/2004