## A-1 Wood Pole Inspections
TABLE A-1
GENERAL ORDER 165 ANNUAL REPORT - 2006
Reporting Period: 01/01/06 - 12/31/06
PacifiCorp Wood Pole Inspections
Visual Assurance & Detail Inspections
DISTRICT | NO. OF FACILITIES |  | INSPECTION TYPE
| Distribution Poles | Transmission Poles | O/H Safety (Patrol) | % Compliance Distribution | % Compliance Transmission | % Compliance (Dist. & Trans.) | % Comp. per Inspections Done | O/H Detail | % Compliance Distribution | % Compliance Transmission | % Compliance (Dist. & Trans.) | % Comp. per Inspections Done
Inspection Cycle |  |  | 2 Yrs |  |  |  | 50% | 5 Yrs |  |  |  | 20%
Tulelake | 13488 | 1719 | 7502 | 66.75% | 91.51% | 69.55% | 49.33% | 3536 | 95.57% | 80.45% | 93.86% | 23.25%
Alturas | 4567 | 1127 | 2935 | 63.3% | 100% | 70.57% | 51.55% | 697 | 92.4% | 100% | 93.91% | 12.24%
Crescent City | 9458 | 909 | 9938 | 73.38% | 92.3% | 75.04% | 95.86% | 3933 | 89.3% | 100% | 90.24% | 37.94%
Yreka/Mt. Shasta | 34328 | 2846 | 29876 | 85.39% | 97.65% | 86.33% | 80.37% | 11468 | 82.91% | 100% | 84.22% | 30.85%
Main Grid | 0 | 3702 | 8815 | n/a | 99.08% | 99.08% | 238.1% | 1571 | n/a | 100% | 100% | 42.44%
California Totals | 61841 | 10303 | 59066 |  |  | 80.62% | 81.87% | 21205 |  |  | 88.69% | 29.39%
1. Percentage of Compliance for the 2006 General Order 165 Annual Report for Visual Assurance and Detail Inspections is based on a point by point analysis of each facility’s inspection records comparing the last inspection date for each inspection type (visual assurance or detail inspection) through December 31, 2006.
2. If a facility point has not undergone a visual assurance inspection in the previous two calendar years from 1/1/2007, or a detail inspection in the previous five calendar years from 1/1/2007, the facility point is out of compliance.
a. As of January 1, 2007, Pacificorp has initiated a project to identify all out of compliance facility points for visual assurance and detail inspections.
b. If a facility point is out of compliance for either inspection type (visual assurance or detail inspection) on January 1, 2007, the facility will be inspected and in compliance by December 31, 2007.
Test and Treat (Intrusive) Inspections
DISTRICT | NO. OF FACILITIES |  | O/H Test & Treat (Intrusive) | % Intrusive Inspections Completed
| Distribution Poles | Transmission Poles
Inspection Cycle |  |  | 10 Yrs | 7%
Tulelake | 13488 | 1719 | 1321 | 8.687%
Alturas | 4567 | 1127 | 334 | 5.866%
Crescent City | 9458 | 909 | 1316 | 12.69%
Yreka/Mt. Shasta | 34328 | 2846 | 3185 | 8.568%
Main Grid | 0 | 3702 | 0 | 0%
California Totals | 61841 | 10303 | 6156 | 8.533%
1. Percentage of Compliance for the 2006 General Order 165 Annual Report for Test and Treat (intrusive) inspections is based on a systemwide average of the number of inspections performed on the total population of facility points in each District. Effective with the company's 2007 Annual Report, the Percentage of Compliance for the Test and Treat (intrusive) inspections will be based on a point by point analysis.

## A-2 Line Equpment Inspections
TABLE A-2
GENERAL ORDER 165 ANNUAL REPORT - 2006
Reporting Period: 01/01/06- 12/31/06
PacifiCorp Line Equipment Inspections
District/Equipment | Type | QTY | Safety (Patrol) Rural (1) |  |  | Detailed Rural (1)
|  |  | Plan (2) | Actual | % Complete | Plan (2) | Actual | % Complete
|  |  | 2 Yrs |  | 50% | 4 or 5 Yrs |  | 20-25%
Tulelake
Transformers | Overhead | 2590 | 1295 | 1685.1997 | 49.33% | 518 | 794.3037 | 23.25%
Switch/Protect Device | Overhead | 778 | 389 |  |  | 155.6
Regs/Caps | Overhead | 48 | 24 |  |  | 9.6
All | Pad Mounted | 81 |  |  |  | 20.25 | 22.2838 | 27.51%
Total |  |  | 1708 | 1685.1997 | 49.33% | 703.45 | 816.5875 | 23.35%
Alturas
Transformers | Overhead | 1056 | 528 | 629.8858 | 51.55% | 211.2 | 149.5845 | 12.24%
Switch/Protect Device | Overhead | 165 | 82.5 |  |  | 33
Regs/Caps | Overhead | 1 | 0.5 |  |  | 0.2
All | Pad Mounted | 45 |  |  |  | 11.25 | 19.6875 | 43.75%
Total |  |  | 611 | 629.8858 | 51.55% | 255.65 | 169.272 | 13.36%
Crescent City
Transformers | Overhead | 3488 | 1744 | 5208.1754 | 95.86% | 697.6 | 2061.1545 | 37.94%
Switch/Protect Device | Overhead | 1943 | 971.5 |  |  | 388.6
Regs/Caps | Overhead | 2 | 1 |  |  | 0.4
All | Pad Mounted | 1166 |  |  |  | 291.5 | 145.5409 | 12.48%
Total |  |  | 2716.5 | 5208.1754 | 95.86% | 1378.1 | 2206.6954 | 33.44%
Yreka/Mt. Shasta
Transformers | Overhead | 9214 | 4607 | 12645.101 | 80.37% | 1842.8 | 4853.8632 | 30.85%
Switch/Protect Device | Overhead | 6419 | 3209.5 |  |  | 1283.8
Regs/Caps | Overhead | 101 | 50.5 |  |  | 20.2
All | Pad Mounted | 3370 |  |  |  | 842.5 | 442.3599 | 13.13%
Total |  |  | 7867 | 12645.101 | 80.37% | 3989.3 | 5296.2231 | 27.72%
California Totals
Transformers | Overhead | 16348 | 8174 | 20168.3619 | 81.87% | 3269.6 | 7858.9059 | 29.39%
Switch/Protect Device | Overhead | 9305 | 4652.5 |  |  | 1861
Regs/Caps | Overhead | 152 | 76 |  |  | 30.4
All | Pad Mounted | 4662 |  |  |  | 1165.5 | 629.8721 | 13.51%
Total |  |  | 12902.5 | 20168.3619 | 81.87% | 6326.5 | 8488.7781 | 27.86%
NOTES:
1. PacifiCorp has no Urban area in its California service territory.
Urban is defined as those areas with a population of more than 1,000 persons per square mile and Rural as those with a population less than 1,000 persons per square
mile as determined by the U.S. Bureau of the Census. U. S. Bureau of the Census reports the population densities below (using 2006 Estimated Census data)
7.1 persons/sq.mi. | Siskiyou County (Tulelake, Yreka, Mt. Shasta)
28.7 persons/sq.mi. | Del Norte County (Crescent City)
2.4 persons/sq.mi. | Modoc County (Alturas)
2. Planned inspection cycles: | Patrol |  | Detailed
Overhead | 2 years |  | 5 years
Pad Mounted |  |  | 4 years
3. Due to calendar year reporting vs. fiscal year operations, some variances to plan are artifacts of these timing differences.
4. Percentage Complete for Visual Assurance and Detail Inspections are based on a systemwide average of inspections performed on the total population of facility
points in each District.

## B-1 Wood Pole-St Light Cond
TABLE B-1
GENERAL ORDER 165 ANNUAL REPORT - 2006
Reporting Period: 01/01/06 - 12/31/06
PacifiCorp Wood Pole Conditions
DISTRICT | CONDITIONS FOUND |  | CONDITIONS CORRECTED |  | REMOVED FROM SYSTEM |  | CONDITIONS OUTSTANDING |  | REASON WHY CORRECTION IS OUTSTANDING | DATE CORRECTION WILL BE COMPLETED BY
| A | B | A | B | A | B | A | B
Tulelake | 25 | 41 | 26 | 71 | 0 | 2 | 9 | 44 | A conditions planned to be completed by end of 2007; B conditions planned to be completed consistent with company policy | Per note
Alturas | 5 | 14 | 5 | 0 | 0 | 0 | 0 | 14 | A conditions planned to be completed by end of 2007; B conditions planned to be completed consistent with company policy | Per note
Crescent City | 75 | 98 | 56 | 30 | 6 | 6 | 20 | 97 | A conditions planned to be completed by end of 2007; B conditions planned to be completed consistent with company policy | Per note
Yreka/Mt. Shasta | 46 | 197 | 80 | 439 | 10 | 37 | 15 | 579 | A conditions planned to be completed by end of 2007; B conditions planned to be completed consistent with company policy | Per note
California Total | 151 | 350 | 167 | 540 | 16 | 45 | 44 | 734
PacifiCorp Street Light Conditions
DISTRICT | CONDITIONS FOUND |  | CONDITIONS CORRECTED |  | REMOVED FROM SYSTEM |  | CONDITIONS OUTSTANDING |  | REASON WHY CORRECTION IS OUTSTANDING | DATE CORRECTION WILL BE COMPLETED BY
| A | B | A | B | A | B | A | B
Tulelake | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 7 | B conditions planned to be completed consistent with company policy | Per note
Alturas | 0 | 18 | 0 | 14 | 0 | 0 | 0 | 20 | B conditions planned to be completed consistent with company policy | Per note
Crescent City | 0 | 20 | 0 | 3 | 0 | 0 | 0 | 18 | B conditions planned to be completed consistent with company policy | Per note
Yreka/Mt. Shasta | 0 | 116 | 1 | 31 | 0 | 18 | 0 | 157 | A conditions planned to be completed by end of 2007; B conditions planned to be completed consistent with company policy | Per note
California Total | 0 | 160 | 1 | 48 | 0 | 18 | 0 | 202
Effective 1/1/2007, 'C' Priority Conditions will be identified and tracked separately from 'B' priority conditions.

## B-2 Equipment Conditions
TABLE B-2
GENERAL ORDER 165 ANNUAL REPORT - 2006
Reporting Period: 01/01/06 - 12/31/06
PacifiCorp Equipment Conditions
DISTRICT | Type | CONDITION RATING FOUND |  | CORRECTIVE ACTIONS COMPLETED |  | REMOVED FROM SYSTEM |  | CONDITIONS OUTSTANDING |  | REASON WHY CORRECTION IS OUTSTANDING | DATE CORRECTION WILL BE COMPLETED BY
|  | A | B | A | B | A | B | A | B
Tulelake
Transformers | Overhead | 0 | 25 | 0 | 1 | 0 | 0 | 0 | 27 | B conditions planned to be completed consistent with company policy | Per note
Switch/Protect Device | Overhead | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | A conditions planned to be completed by end of 2007; B conditions planned to be completed consistent with company policy | Per note
Regs/Caps | Overhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All | Padmounted | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | B conditions planned to be completed consistent with company policy | Per note
Alturas
Transformers | Overhead | 0 | 4 | 0 | 1 | 0 | 0 | 0 | 4 | B conditions planned to be completed consistent with company policy | Per note
Switch/Protect Device | Overhead | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | A conditions planned to be completed by end of 2007 | 2007-12-31
Regs/Caps | Overhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All | Padmounted | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Crescent City
Transformers | Overhead | 0 | 25 | 2 | 2 | 0 | 0 | 0 | 28 | A conditions planned to be completed by end of 2007; B conditions planned to be completed consistent with company policy | Per note
Switch/Protect Device | Overhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Regs/Caps | Overhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All | Padmounted | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | B conditions planned to be completed consistent with company policy | Per note
Yreka
Transformers | Overhead | 2 | 381 | 10 | 75 | 1 | 16 | 0 | 390 | A conditions planned to be completed by end of 2007; B conditions planned to be completed consistent with company policy | Per note
Switch/Protect Device | Overhead | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 7 | B conditions planned to be completed consistent with company policy | Per note
Regs/Caps | Overhead | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | B conditions planned to be completed consistent with company policy | Per note
All | Padmounted | 8 | 7 | 10 | 0 | 0 | 0 | 1 | 19 | A conditions planned to be completed by end of 2007; B conditions planned to be completed consistent with company policy | Per note
Mt. Shasta
Transformers | Overhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Switch/Protect Device | Overhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Regs/Caps | Overhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All | Padmounted | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CA Total
Transformers | Overhead | 2 | 435 | 12 | 79 | 1 | 16 | 0 | 449
Switch/Protect Device | Overhead | 0 | 1 | 2 | 2 | 1 | 0 | 0 | 7
Regs/Caps | Overhead | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2
All | Padmounted | 8 | 8 | 10 | 0 | 0 | 0 | 1 | 21
California Totals |  | 10 | 446 | 24 | 81 | 2 | 16 | 1 | 479
Effective 1/1/2007, 'C' Priority Conditions will be identified and tracked separately from 'B' priority conditions.