## Historical
Southern California Edison
Historical System Reliability Data
1993 - 2002
(New Sustained Outage Definition)
|  | All Interruptions Included |  |  |  | Major Events Excluded
YEAR | SAIDI1 | SAIFI | MAIFI |  | SAIDI1 | SAIFI | MAIFI
1993 | 62.0265 | 0.91617 | 1.0941 |  | 62.0265 | 0.91617 | 1.0941
1994 | 124.132 | 0.853 | 1.2416 |  | 44.2816 | 0.68527 | 1.1497
1995 | 66.8662 | 0.87004 | 1.096 |  | 66.8662 | 0.87004 | 1.096
1996 | 125.9625 | 1.4178 | 1.4033 |  | 62.7579 | 0.98322 | 1.3911
1997 | 77.0214 | 1.0996 | 1.3382 |  | 77.0214 | 1.0996 | 1.3382
1998 | 78.4768 | 1.3073 | 1.3874 |  | 78.4768 | 1.3073 | 1.3874
1999 | 49.0461 | 1.044 | 1.226 |  | 49.0461 | 1.044 | 1.226
2000 | 46.8684 | 1.1163 | 1.2334 |  | 46.8684 | 1.1163 | 1.2334
2001 | 51.589 | 1.0478 | 1.1602 |  | 51.589 | 1.0478 | 1.1602
2002 | 52.6172 | 1.2665 | 1.1488 |  | 50.4686 | 1.1191 | 1.1471
1 Normalized to reflect the variance introduced by Southern California Edison's convention of declaring All Load Up (ALU) when power had been restored
up to the last residential transformer - an estimate was added to the annual CMI base to arrive at the normalized SAIDIs.

## List >12 Sustained
NEW SUSTAINED OUTAGE DEFINITION
Year | Circuit | Circuit Name | Number of customers experiencing > 12 sustained outages
1993 | 9205 | JENKS LAKE | 137
| 12190 | MORITZ | 700
| 18540 | VALLEY OF THE MOON | 330
| 6924 | GALAHAD | 124
1994 | 4635 | DANBY | 25
| 3130 | CASTLE | 713
1995 | 3485 | CHINA RANCH | 4
| 7657 | GRIMSHAW | 69
| 8735 | HOT WATER | 32
| 14926 | REVERSE PEAK | 8
| 15282 | ROBINSON CREEK | 140
| 16600 | SODA SPRINGS | 47
| 17955 | TOLL | 75
| 15415 | ROSEBUD | 536
1996 | 14955 | RHINEDOLLAR | 14
1997 | 11448 | MCCLENNY | 57
| 14349 | POSO PARK | 49
| 17190 | SUGARLOAF | 114
| 1640 | BIG PINES | 242
| 9320 | JORDAN | 698
| 11270 | MARSH | 848
| 12190 | MORITZ | 502
| 17063 | STONEMAN | 80
1998 | 3890 | CONCEPCION | 126
| 16600 | SODA SPRINGS | 53
| 14652 | RAMAC | 7
| 17663 | TENNECO | 307
| 19150 | WELLS | 123
1999 | 3170 | CATTLE | 296
| 15475 | ROWCO | 849
2000 | 5085 | DINKEY CREEK | 37
| 8702 | HOSSACK | 100
| 10945 | MAHOGANY | 6
| 12910 | NOVAC | 272
| 13959 | PERIMETER | 7
| 17672 | TERMINUS | 137
2001 | 1626 | BIGFOOT | 47
| 2664 | CALCADIA | 5
| 3890 | CONCEPCION | 68
| 5018 | DEVINE | 8
| 5146 | DOGWOOD | 1890
| 12722 | NIPTON | 27
| 15680 | SALT CREEK | 118
| 19134 | WEINING | 64
2002 | 1630 | BIG ROCK | 469
| 4635 | DANBY | 57
| 9060 | IVERSON | 124

## No Service by Hourly Interval
NEW SUSTAINED OUTAGE DEFINITION
| Landers Earthquake | Northridge Earthquake | WSCC Pacific Intertie | Mira Loma RAS | ïDescription of event
Time | 06/28/1992 | 01/17/1994 | 08/10/1996 | 2002-06-26 | ïDate of event
0 | 0 | 2637 | 2640 | 1973
1 | 5748 | 3171 | 2851 | 1995
2 | 1119 | 195 | 211 | 22
3 | 74 | 195 | 211 | 0
4 | 1187853 | 903390 | 3065 | 0
5 | 568943 | 541461 | 704 | 0
6 | 415267 | 532081 | 266 | 469
7 | 335012 | 576456 | 610 | 0
8 | 317182 | 477808 | 588 | 131
9 | 192925 | 448021 | 293 | 0
10 | 150768 | 439365 | 12 | 412
11 | 111974 | 427073 | 2812 | 114
12 | 83392 | 420299 | 12 | 1053
13 | 57105 | 415879 | 72036 | 622
14 | 59119 | 316889 | 72033 | 622
15 | 31818 | 224531 | 1725167 | 0
16 | 24659 | 158073 | 1819090 | 0
17 | 13948 | 127152 | 1610131 | 0
18 | 16102 | 117840 | 1299530 | 664331
19 | 9863 | 107412 | 31614 | 112065
20 | 9465 | 100287 | 20946 | 6960
21 | 6791 | 97352 | 17018 | 3244
22 | 5628 | 78803 | 5492 | 459
23 | 4943 | 69910 | 9331 | 2827

## No Service by Duration
NEW SUSTAINED OUTAGE DEFINITION
| Landers Earthquake | Northridge Earthquake | WSCC Pacific Intertie | Mira Loma RAS | ïDescription of event
Outage Duration | 06/28/1992 | 01/17/1994 | 08/10/1996 | 2002-06-26 | ïDate of event
0 to 1 hour | 844880 | 416201 | 58188 | 629136
1 to 5 hours | 253052 | 113315 | 1801902 | 44522
5 to 10 hours | 169156 | 280389 | 19352 | 1096
10 to 15 hours | 87420 | 143152 | 6377 | 1203
15 to 20 hours | 30198 | 78136 | - | 267
20 to 24 hours | 21457 | 41360 | - | -
1 to 2 days | 18133 | 5160 | - | -
2 to 3 days | - | - | - | 8
3 to 4 days | - | - | - | -
4 to 5 days | - | - | - | -
5 to 6 days | - | - | - | -
6 to 7 days | - | - | - | -
> 7 days | - | - | - | -
Total | 1424296 | 1077713 | 1885819 | 676232

## Top 10 SAIDI each year
1993 | NEW SUSTAINED OUTAGE DEFINITION
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption | Number of people used to restore service | CPUC major event?
1 | Wind Storm | 1993-10-27 | 2.1757 |  |  |  | N
2 | Wind Storm | 1993-01-06 | 2.1604 |  |  |  | N
3 | Lightning Storm | 1993-01-30 | 2.0072 |  |  |  | N
4 | Lightning Storm | 1993-11-14 | 1.8832 |  |  |  | N
5 | Wind Storm | 1993-12-11 | 1.6011 |  |  |  | N
6 | Lightning Storm | 1993-01-18 | 1.4744 |  |  |  | N
7 | Lightning Storm | 1993-05-15 | 1.1464 |  |  |  | N
8 | Flood | 1993-02-07 | 1.1419 |  |  |  | N
9 | Equipment Failure | 1993-06-05 | 1.0721 |  |  |  | N
10 | Wind Storm | 1993-10-11 | 0.91182 |  |  |  | N
1994 | NEW SUSTAINED OUTAGE DEFINITION
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption | Number of people used to restore service | CPUC major event?
1 | Northridge Earthquake | 1994-01-17 | 79.8504 | 1077713 | 2270 | N/A | Y
2 | Rain Storm | 1994-10-04 | 0.89114 |  |  |  | N
3 | Lightning Storm | 1994-08-13 | 0.70297 |  |  |  | N
4 | Lightning Storm | 1994-04-26 | 0.69375 |  |  |  | N
5 | Wind Storm | 1994-02-07 | 0.66839 |  |  |  | N
6 | Equipment Failure | 1994-03-24 | 0.61868 |  |  |  | N
7 | Heavy Fog | 1994-11-10 | 0.59503 |  |  |  | N
8 | Wind Storm | 1994-11-16 | 0.58207 |  |  |  | N
9 | Lightning Storm | 1994-08-12 | 0.53937 |  |  |  | N
10 | Wind Storm | 1994-11-26 | 0.52845 |  |  |  | N
1995 | NEW SUSTAINED OUTAGE DEFINITION
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption | Number of people used to restore service | CPUC major event?
1 | Wind Storm | 1995-12-31 | 6.584 |  |  |  | N
2 | Snow Storm | 1995-01-04 | 4.1573 |  |  |  | N
3 | Snow Storm | 1995-03-10 | 3.88 |  |  |  | N
4 | Wind Storm | 1995-01-10 | 1.5011 |  |  |  | N
5 | Snow Storm | 1995-01-05 | 1.4371 |  |  |  | N
6 | Wind Storm | 1995-03-11 | 1.0955 |  |  |  | N
7 | Wind Storm | 1995-09-02 | 1.0094 |  |  |  | N
8 | Wind Storm | 1995-03-23 | 0.83806 |  |  |  | N
9 | Wind Storm | 1995-12-12 | 0.78277 |  |  |  | N
10 | Vehicle Hit Pole | 1995-02-14 | 0.69805 |  |  |  | N
1996 | NEW SUSTAINED OUTAGE DEFINITION
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption | Number of people used to restore service | CPUC major event?
1 | WSCC Intertie Disturbance | 1996-08-10 | 63.2047 | 1885819 | 842 | 300 | Y
2 | Wind Storm | 1996-12-22 | 3.0236 |  |  |  | N
3 | Wind Storm | 1996-12-15 | 2.9425 |  |  |  | N
4 | Wind Storm | 1996-01-01 | 2.8298 |  |  |  | N
5 | Wind Storm | 1996-12-14 | 2.1172 |  |  |  | N
6 | Wind Storm | 1996-10-30 | 1.96 |  |  |  | N
7 | Wind Storm | 1996-10-25 | 1.5081 |  |  |  | N
8 | Wind Storm | 1996-10-21 | 1.4034 |  |  |  | N
9 | Wind Storm | 1996-11-27 | 1.0157 |  |  |  | N
10 | Wind Storm | 1996-10-29 | 0.80286 |  |  |  | N
1997 | NEW SUSTAINED OUTAGE DEFINITION
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption | Number of people used to restore service | CPUC major event?
1 | Rain Storm | 1997-01-06 | 12.7006 |  |  |  | N
2 | Rain Storm | 1997-01-07 | 8.9336 |  |  |  | N
3 | Rain Storm | 1997-01-13 | 1.9715 |  |  |  | N
4 | Plane Crash | 1997-08-05 | 1.7605 |  |  |  | N
5 | Wind Storm | 1997-12-11 | 1.4818 |  |  |  | N
6 | Wind Storm | 1997-12-06 | 1.221 |  |  |  | N
7 | Rain Storm | 1997-09-25 | 1.2155 |  |  |  | N
8 | Wind Storm | 1997-11-10 | 1.2062 |  |  |  | N
9 | Rain Storm | 1997-11-26 | 1.1881 |  |  |  | N
10 | Lightning Storm | 1997-09-02 | 0.78466 |  |  |  | N
1998 | NEW SUSTAINED OUTAGE DEFINITION
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption | Number of people used to restore service | CPUC major event?
1 | Rain Storm | 1998-02-03 | 8.4764 |  |  |  | N
2 | Wind Storm | 1998-12-09 | 5.5171 |  |  |  | N
3 | Heat Storm | 1998-09-02 | 3.5752 |  |  |  | N
4 | Heat Storm | 1998-08-31 | 3.1617 |  |  |  | N
5 | Wind Storm | 1998-12-06 | 2.6246 |  |  |  | N
6 | Rain Storm | 1998-02-23 | 1.6497 |  |  |  | N
7 | Rain Storm | 1998-03-24 | 1.1831 |  |  |  | N
8 | Rain Storm | 1998-11-08 | 1.119 |  |  |  | N
9 | Rain Storm | 1998-02-06 | 1.0561 |  |  |  | N
10 | Heat Storm | 1998-08-29 | 0.97176 |  |  |  | N
1999 | NEW SUSTAINED OUTAGE DEFINITION
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption | Number of people used to restore service | CPUC major event?
1 | Hector Mines Earthquake | 1999-10-16 | 3.314 |  |  |  | N
2 | Rain/Wind Storm | 1999-01-25 | 2.0993 |  |  |  | N
3 | Rain Storm | 1999-11-08 | 1.6926 |  |  |  | N
4 | Rain/Wind Storm | 1999-04-03 | 1.0897 |  |  |  | N
5 | Rain Storm | 1999-04-06 | 0.99027 |  |  |  | N
6 | Laguna Bell A-Bank | 1999-07-07 | 0.73652 |  |  |  | N
7 | Rain/Wind Storm | 1999-02-09 | 0.67476 |  |  |  | N
8 | La Cienega A-Bank | 1999-01-07 | 0.66321 |  |  |  | N
9 | Wind Storm | 1999-02-11 | 0.65328 |  |  |  | N
10 | Heat/Lightning Storm | 1999-07-11 | 0.62073 |  |  |  | N
2000 | NEW SUSTAINED OUTAGE DEFINITION
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption | Number of people used to restore service | CPUC major event?
1 | Equipment Failure | 2000-10-26 | 1.5705 |  |  |  | N
2 | Rain/Wind Storm | 2000-04-18 | 1.2847 |  |  |  | N
3 | Rain/Wind Storm | 2000-02-20 | 0.94447 |  |  |  | N
4 | Rain/Wind Storm | 2000-02-21 | 0.8196 |  |  |  | N
5 | Car Hit Transmission Pole | 2000-04-03 | 0.80443 |  |  |  | N
6 | Wind Storm | 2000-03-21 | 0.77422 |  |  |  | N
7 | Rain/Wind Storm | 2000-03-05 | 0.63785 |  |  |  | N
8 | Rain Storm | 2000-09-22 | 0.6329 |  |  |  | N
9 | Rain/Wind Storm | 2000-04-17 | 0.57183 |  |  |  | N
10 | Equipment Failure | 2000-05-13 | 0.55115 |  |  |  | N
2001 | NEW SUSTAINED OUTAGE DEFINITION
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption | Number of people used to restore service | CPUC major event?
1 | Rain/Snow/Wind Storm | 2001-02-13 | 3.106 |  |  |  | N
2 | Wind Storm | 2001-01-11 | 1.7288 |  |  |  | N
3 | Rain/Wind Storm | 2001-11-24 | 1.6705 |  |  |  | N
4 | Rain/Wind Storm | 2001-11-12 | 1.1803 |  |  |  | N
5 | Wind Storm | 2001-01-10 | 0.91992 |  |  |  | N
6 | Wind Storm | 2001-09-30 | 0.59811 |  |  |  | N
7 | Rain Storm | 2001-10-30 | 0.59 |  |  |  | N
8 | Lightning Storm | 2001-07-06 | 0.56447 |  |  |  | N
9 | Structure Fire | 2001-06-21 | 0.56441 |  |  |  | N
10 | Rain/Snow/Wind Storm | 2001-02-12 | 0.55418 |  |  |  | N
2002 | NEW SUSTAINED OUTAGE DEFINITION
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption | Number of people used to restore service | CPUC major event?
1 | Rain/Wind Storm | 2002-12-16 | 2.7805 |  |  |  | N
2 | Rain/Wind Storm | 2002-11-08 | 2.4152 |  |  |  | N
3 | Mira Loma RAS, Louisiana Fire | 2002-06-26 | 2.1486 | 676232 | 3996 | 50 | Y
4 | Rain/Wind Storm | 2002-11-09 | 1.0429 |  |  |  | N
5 | Rain Storm | 2002-11-25 | 1.0143 |  |  |  | N
6 | Wind Storm | 2002-02-09 | 0.85849 |  |  |  | N
7 | Car Hit Pole | 2002-10-04 | 0.84707 |  |  |  | N
8 | Rain/Wind Storm | 2002-11-07 | 0.70412 |  |  |  | N
9 | Heat Storm | 2002-09-01 | 0.66042 |  |  |  | N
10 | Rain Storm | 2002-02-17 | 0.64036 |  |  |  | N