## READ ME
This dashboard provides an overview of busbar mapping results for the CPUC IRP Proceeding
Resource-to-busbar mapping (“busbar mapping”) is the process of refining the geographically coarse portfolios produced in the California Public Utilities Commission’s (CPUC) Integrated Resource Plan (IRP) proceeding, into plausible network modeling locations for electrical analysis in the California Independent System Operator’s (CAISO) annual Transmission Planning Process (TPP).
The purpose of this workbook is to communicate the results of the busbar mapping process for the 2021-22 TPP performed by the CPUC, CAISO and California Energy Commission (CEC).
Tabs shaded blue are authored by CEC: busbar allocation results
Tabs shaded purple are authored by CPUC: these tabs show busbar mapping criteria and results
Tabs shaded green are authored by CPUC: these tabs show the underlying calculations used to review busbar mapping results against mapping criteria
See Methodology for more detail, available at:
https://www.cpuc.ca.gov/General.aspx?id=6442466555

## VERSIONS
Version # | Mapping Rounds Performed | Description | Changes to Prior Version
n/a | 0 | 38MMT_20201015_2045_RSP_2019IEPR | Not applicable
n/a | 0 | Portfolio sent to CEC for mapping Thu 11/5/2020 7:33 PM. | 2021-22 TPP Sensitivity #1 RESOLVE resources added with baseline reconciliation
1 | 1 | Imported busbar allocations received from CEC for criteria evaluation Wednesday, November 18, 2020 1:41 PM. Source data file name "2021 IRP Portfolios_CEC BusBar Assignment_WORKING_11182020.xlsx" | Added results from Round 1 of mapping of renewable resources
2 | 2 | Dashboard following round 2 of mapping: 12/14/2020 | Added results and dashboard for Round 2 of mapping including storage resources, battery and pumped hydro.
2.1 | 2 | Final workbook for portfolio: 12/22/2020 | Few minor corrections based on CEC and CAISO guidiance

## CITATIONS
This tab provides the information, details, and notes on sources of data used in this dashboard
Reference No. | Locations Cited | Reference Source | Notes
1 | Dashboard 38MMT (Round 0): Cell C5 | RESOLVE Portfolio Analytics Tab ("2020-10-29-All_Portfolios_For_Busbar_Mapping.xlsx"; tab "Portfolio Analytics_Sens 1"; Row 466 "Selected Renewables by Location (Fully Deliverable)" and Row 539 "Selected Renewables by Location (Energy Only)"). | Fully Deliverable amounts have been adjusted to account for new baseline resources, contracted since the time of the 2019 CAISO transmission capability whitepaper. This baseline adjustment is done in the NewBaselineSumByRESOLVEResource tab.
2 | 2_TxCapability: Cells B5 | CAISO Transmission Capability Whitepaper May 20, 2019 | http://www.caiso.com/Documents/WhitePaper-TransmissionCapabilityEstimates-InputtoCPUCIntegratedResourcePlanPortfolioDevelopment.pdf
3 | 2_TxCapability: Cells O6 & P6 | Workbook received through email communciation from ISO staff: Feb2020_Resolve_tx_zones
4 | 5b_ComparToPrevYr | Modeling Assumptions for the 2020-2021 Transmission Planning Process | Busbar mapping for 20-21 TPP base case and sensitivity #1 portfolios
5 | 4d_CommercialInterest_LSEPlans | Source: LSE Plans, summarized in resource data template. Filter for contract status = online or development. Removed those that are already captured in RESOLVE baseline "Genlist." Identified zone for all those for which information was available.
6 | 2_TxCapability: Cell B15 | Inputs & Assumptions: 2019-2020 Integrated Resource Planning | The Westlands subzone identified by CAISO is split between two zones in RESOLVE: 1) Kern and Greater Carrizo and 2) Central Valley North & Los Banos
7 | NewBaselineSumByRESOLVEResource: Cell I2 | 2020 IRP Baseline Reconciliation (for non-battery and battery mapped resources) workbook | Reconiciliation of new resources added since RESOLVE baseline genlist was set

## Dashboard 38MMT (Round 1)
IRP Busbar Mapping Dashboard
Purpose: Quickly communicate compliance of portfolio mapping with the criteria per the Methodology. Highlight MW amounts by zone that breach criteria, if any, and identify next steps as part of the iterative process.
38MMT_20201015_2045_RSP_2019IEPR
Round 1 |  |  |  | Prior Year Portfolio | Compliance with Criteria
|  | Resource Selection¹ |  |  | [1=Yes, 2=Possible/Moderate, 3=Materially in Breach] | [11 empty] | Actions
Resource | Tx Deliv. Zone | 2031 FCDS MW | 2031 EO MW | Total MW (2019 RSP adj) | 1. Distance to Trans. of Appropriate Voltage | EO Inner Zone | EO Outer zone | FD inner zone | FD outer zone | 2. Trans. Capability | 3a. Available Land Area | 3b. High Environmental Implications | 4. Commercial Interest | 5. Consistency with Prior Year's Mapping | Sum of flagged criteria | Low-Effort Adjustment Available? | Further Round of Mapping Needed? | Comment; Potential Solutions for Consideration | Include in display?
InState_Biomass | N/A | 0 | 0 | 0 |  |  |  | N/A | N/A |  |  |  |  | 1 |  |  |  |  | 0
Greater_Imperial_Geothermal | Greater_Imperial-SCADSNV | 0 | 0 | 0 | none selected |  |  | ok | breach | none selected | none selected | none selected | 1 | 1 | 2 |  |  | 5. Greater Imperial Geothermal was not selected by RESOLVE this year, due to updated cost assumptions, no longer competitive. | 0
Inyokern_North_Kramer_Geothermal | Greater_Kramer-Inyokern_North_Kramer | 0 | 0 | 0 | 1 |  |  | ok | ok | 1 |  |  | 1 | 1 |  |  |  |  | 0 | #NAME?
Northern_California_Ex_Geothermal | Northern_California_Ex | 0 | 0 | 0 | none selected |  |  | N/A | N/A | none selected | none selected | none selected | 1 | 1 | 2 |  |  |  | 0
Pacific_Northwest_Geothermal | N/A | 0 | 0 | 0 |  |  |  | #N/A | #N/A | #N/A |  |  |  | 1 |  |  |  |  | 0
Riverside_Palm_Springs_Geothermal | SCADSNV-Riverside_Palm_Springs | 0 | 0 | 0 | 1 |  |  | ok | breach | 3 |  |  | 1 | 1 |  |  |  |  | 0
Solano_Geothermal | Solano-Sacramento_River | 57 | 48 | 0 | 1 | ok | breach | ok | ok | 3 | info not available | info not available | 1 | 1 | 3 |  |  | 2. Northern CA outer zone limit exceeded. | 1
Southern_Nevada_Geothermal | SCADSNV-Mountain_Pass_El_Dorado | 0 | 0 | 0 | 1 |  |  | ok | breach | 3 |  |  | 1 | 1 |  |  |  |  | 0
Carrizo_Solar | SPGE-Kern_Greater_Carrizo-Carrizo | 0 | 0 | 0 | 1 |  |  | ok | breach | 3 | none selected | none selected | 1 | 1 | 6 |  |  | 2. SPGE outer zone exceeded by non-battery resources. 5. Carrizo_Solar not selected in latest RESOLVE portfolio. | 0
Carrizo_Wind | SPGE-Kern_Greater_Carrizo-Carrizo | 287 | 0 | 287 | 1 | ok | ok | ok | breach | 3 | 2 | 2 | 1 | 1 | 7 |  |  | 2. SPGE outer zone exceeded by non-battery resources. 3a. Carrizo wind is flagged for exceeding 75% of project candidate land 3b. Project acres exceeds total low-value acres available | 1
Central_Valley_North_Los_Banos_Solar | Central_Valley_North_Los_Banos-SPGE | 0 | 0 | 0 | 1 |  |  | ok | breach | 3 | none selected | none selected | 1 | 1 |  |  |  |  | 0
Central_Valley_North_Los_Banos_Wind | Central_Valley_North_Los_Banos-SPGE | 173 | 0 | 173 | 2 | ok | ok | ok | breach | 3 | 3 | 2 | 1 | 1 | 10 | Yes |  | 1. Central Valley North Los Banos Wind is flagged for distance to transmission, because there is a closer substation in the Westlands Tx Zone. 2. SPGE outer zone exceeded by non-battery resources. 3a. Central Valley N Los BAnos wind wind is flagged for exceeding project candidate land 3b. Project area requires 43% of low value land. | 1
Distributed_Solar | N/A | 0 | 0 | 0 | none selected |  |  | none selected | none selected | none selected | none selected | none selected | none selected | 1 |  |  |  |  | 0
Distributed_Wind | N/A | 0 | 0 | 0 | none selected |  |  | none selected | none selected | none selected | none selected | none selected | none selected | 1 |  |  |  |  | 0
Greater_Imperial_Solar | Greater_Imperial-SCADSNV | 0 | 548 | 548 | 1 | ok | ok | ok | breach | 1 | 1 | 1 | 1 | 1 | 0 |  |  |  | 1
Greater_Imperial_Wind | Greater_Imperial-SCADSNV | 0 | 0 | 0 | 1 |  |  | ok | breach | 3 | none selected | none selected | 1 | 1 |  |  |  |  | 0
Greater_Kramer_Wind | Greater_Kramer | 0 | 0 | 0 | 1 |  |  | ok | ok | 1 | none selected | none selected | 1 | 1 |  |  |  |  | 0
Humboldt_Wind | Sacramento_River-Humboldt | 0 | 34 | 34 | 1 | ok | breach | ok | ok | 3 | 1 | 2 | 1 | 1 | 5 |  |  | 2. Northern CA outer zone limit exceeded. 3b. Humboldt Wind has no low-value land area. | 1
Inyokern_North_Kramer_Solar | Greater_Kramer-Inyokern_North_Kramer | 0 | 0 | 97 | 1 | ok | ok | ok | ok | 1 | none selected | none selected | 1 | 2 | 2 |  |  | 5. Inyokern_North_Kramer_Solar not selected in latest RESOLVE portfolio. | 1
Kern_Greater_Carrizo_Solar | SPGE-Kern_Greater_Carrizo | 101.32 | 700 | 242 | 1 | ok | ok | ok | breach | 3 | 1 | 1 | 1 | 1 | 3 |  |  | 2. SPGE outer zone exceeded by non-battery resources. | 1
Kern_Greater_Carrizo_Wind | SPGE-Kern_Greater_Carrizo | 20 | 0 | 60 | 1 | ok | ok | ok | breach | 3 | 1 | 1 | 1 | 2 | 5 |  |  | 2. SPGE outer zone exceeded by non-battery resources. 5. Less allocated compared with prior year's 2019 RSP adj. portfolio | 1
Kramer_Inyokern_Ex_Solar | Kramer_Inyokern_Ex | 0 | 0 | 0 | 1 |  |  | ok | ok | 1 | none selected | none selected | 1 | 1 | 4 | Yes |  |  | 0
Kramer_Inyokern_Ex_Wind | Kramer_Inyokern_Ex | 0 | 0 | 0 | 3 |  |  | ok | ok | 1 | none selected | none selected | 1 | 1 |  |  |  |  | 0
Mountain_Pass_El_Dorado_Solar | Mountain_Pass_El_Dorado | 248 | 0 | 248 | 2 | ok | ok | ok | breach | 3 | 1 | 1 | 1 | 1 | 5 |  |  | 1. Solar mapped to 500kV sub. 2. SCADSNV outer zone limit exceeded by non-battery resources. | 1
North_Victor_Solar | North_Victor-Greater_Kramer | 300 | 0 | 300 | 1 | ok | ok | ok | ok | 1 | 1 | 1 | 1 | 1 | 0 |  |  |  | 1
Northern_California_Ex_Solar | Northern_California_Ex | 397 | 0 | 0 | 1 | ok | ok | ok | ok | 1 | 1 | 1 | 3 | 1 | 3 |  |  | 4. No commercial interest. | 1
Northern_California_Ex_Wind | Sacramento_River | 767 | 0 | 866 | 1 | ok | breach | ok | ok | 1 | info not available | info not available | 1 | 1 | 0 | Yes |  |  | 1
NW_Ext_Tx_Wind | Sacramento_River | 530 | 970 | 0 | 1 | ok | breach | ok | ok | 3 | info not available | info not available | 1 | 1 | 3 |  |  | 2. The amount mapped at Round Mountain exceeds the 500 MW transmission capability estimate for the zone. CAISO is in the process of further assessment | 1
Riverside_Palm_Springs_Solar | SCADSNV-Riverside_Palm_Springs | 0 | 0 | 0 | 1 |  |  | ok | breach | 3 | none selected | none selected | 3 | 1 | 8 |  |  | 2. SCADSNV outer zone limit exceeded by non-battery resources. 4. Not selected by RESOLVE, despite signifcant commercial interest: 4610 MW 5. Riverside Palm Springs not selected in latest RESOLVE portfolio. | 0
Sacramento_River_Solar | Sacramento_River | 0 | 896 | 0 | 1 | ok | breach | ok | ok | 3 | 1 | 1 | 1 | 1 | 3 |  |  | 2. Northern CA outer zone limit exceeded. | 1
Sacramento_River_Wind | N/A | 0 | 0 | 0 | 1 |  |  | ok | ok | 1 | none selected | none selected | 1 | 1 |  |  |  |  | 0
SCADSNV_Solar | SCADSNV | 0 | 330 | 330 | 2 | ok | ok | breach | breach | 1 | 1 | 1 | 1 | 1 | 2 |  |  | 1. Solar mapped to 500kV sub. | 1
SCADSNV_Wind | SCADSNV | 0 | 0 | 0 | 1 |  |  | breach | breach | 3 | none selected | none selected | 1 | 1 | 6 |  |  |  | 0
Solano_Solar | Solano-Sacramento_River | 0 | 622 | 0 | 2 | ok | breach | ok | ok | 3 | 1 | 1 | 1 | 1 | 5 |  |  | 1. Solar mapped to 500kV sub. 2. Northern CA outer zone limit exceeded. | 1
Solano_subzone_Solar | Solano-Sacramento_River-Solano_subzone | 0 | 0 | 0 | 1 |  |  | ok | ok | 1 | none selected | none selected | 1 | 1 |  |  |  |  | 0
Solano_subzone_Wind | Solano-Sacramento_River-Solano_subzone | 0 | 0 | 0 | 1 |  |  | ok | ok | 1 | none selected | none selected | 1 | 1 |  |  |  |  | 0
Solano_Wind | Solano-Sacramento_River | 462 | 0 | 542 | 1 | ok | breach | ok | ok | 1 | 1 | 3 | 1 | 1 | 3 |  |  | 3b. Solano Wind has one wind polygon that exceeds level 3 non-compliance at Lakeville substation. Substation has other polygons w/ enough room for the resource | 1
Southern_California_Desert_Ex_Solar | Southern_California_Desert_Ex | 862 | 0 | 0 | 2 | ok | ok | ok | ok | 1 | 1 | 1 | 1 | 1 | 2 |  |  | 1. Solar mapped to 500kV sub. | 1
Southern_California_Desert_Ex_Wind | Southern_California_Desert_Ex | 0 | 0 | 0 | 1 |  |  | ok | ok | 1 | none selected | none selected | 1 | 1 |  |  |  |  | 0
Southern_Nevada_Solar | SCADSNV-GLW_VEA | 0 | 0 | 862 | 1 | ok | ok | ok | breach | 1 | 1 | 1 | 2 | 2 | 4 |  |  | 4. Not selected by RESOLVE, despite signifcant commercial interest: 2,325 MW. 5. SNV solar not selected by RESOLVE despite being selected in previous portfolio. However, RESOLVE did select a significant amount of other solar resources allocated to the same SNV substations (Innovation, Gamebird, Crazy Eyes, Eldorado, Mohave) | 1
Southern_Nevada_Wind | SCADSNV-GLW_VEA | 442 | 0 | 0 | 1 | ok | ok | ok | breach | 3 | info not available | info not available | 1 | 1 | 3 |  |  | 2. SCADSNV outer zone limit exceeded by non-battery resources. | 1
SW_Ext_Tx_Wind | SCADSNV-Riverside_Palm_Springs | 0 | 500 | 0 | 1 | ok | ok | ok | breach | 1 | info not available | info not available | 3 | 1 | 3 |  |  | 4. No commercial interest found in queue or LSE plans, but stakeholder comments indiciate that there is commercial interest in New Mexico Wind (new transmission). RESOLVE definitions of this resource "SW_Ext_Tx_Wind" is Southwest wind on existing transmission | 1
Tehachapi_Solar | Tehachapi | 3856 | 800 | 4202 | 2 | ok | ok | ok | ok | 1 | 1 | 1 | 1 | 1 | 2 |  |  | 1. Solar mapped to 500kV sub. | 1
Tehachapi_Ex_Solar | Tehachapi_Ex | 0 | 0 | 0 | 1 |  |  | ok | ok | 1 | none selected | none selected | 1 | 1 | 4 |  |  |  | 0
Tehachapi_Wind | Tehachapi | 275 | 0 | 275 | 1 | ok | ok | ok | ok | 1 | 2 | 1 | 1 | 1 | 2 | Yes |  | 3a. Tehachapi_Wind is flagged for exceeding 75% of project candidate land | 1
Westlands_Ex_Solar | Westlands_Ex | 1779 | 0 | 0 | 2 | ok | ok | ok | ok | 1 | 1 | 1 | 3 | 1 | 5 |  |  | 4. Selected by RESOLVE despite absence of commercial interest. However, Westlands Solar proper has significant commercial interest (4779 MW). In previous portfolio, resources were shifted to Westlands | 1
Westlands_Ex_Wind | N/A | 0 | 0 | 0 | 1 |  |  | ok | ok | 1 | none selected | none selected | 1 | 1 |  |  |  |  | 0
Westlands_Solar | Central_Valley_North_Los_Banos-SPGE | 468 | 0 | 1836 | 1 | ok | ok | ok | breach | 3 | 1 | 1 | 1 | 3 | 6 |  |  | 2. SPGE outer zone limit exceeded by non-battery resources. 5. Westlands_Ex solar was adjusted to be in Westlands solar in 2019 RSP adj portfolio | 1
Cape_Mendocino_Offshore_Wind | N/A | 0 | 0 | 0 |  |  |  | #N/A | #N/A | #N/A | none selected | none selected |  | 1 |  |  |  |  | 0
Del_Norte_Offshore_Wind | N/A | 0 | 0 | 0 |  |  |  | #N/A | #N/A | #N/A | none selected | none selected |  | 1 |  |  |  |  | 0
Diablo_Canyon_Offshore_Wind_Ext_Tx | N/A | 0 | 0 | 0 |  |  |  | #N/A | #N/A | #N/A | none selected | none selected |  | 1 |  |  |  |  | 0
Diablo_Canyon_Offshore_Wind | N/A | 0 | 0 | 0 |  |  |  | #N/A | #N/A | #N/A | info not available | info not available |  | 1 |  |  |  |  | 0
Humboldt_Bay_Offshore_Wind | N/A | 0 | 0 | 0 |  |  |  | ok | ok | 1 | info not available | info not available |  | 1 |  |  |  |  | 0
Morro_Bay_Offshore_Wind | N/A | 0 | 0 | 0 |  |  |  | #N/A | #N/A | #N/A | info not available | info not available |  | 1 |  |  |  |  | 0
Utah_Solar | N/A | 0 | 0 | 0 |  |  |  | #N/A | #N/A | #N/A | none selected | none selected |  | 1 |  |  |  |  | 0
Arizona_Solar | SCADSNV-Riverside_Palm_Springs | 447 | 1463 | 2352 | 2 | ok | ok | ok | breach | 3 | info not available | info not available | 1 | 1 | 5 |  |  | 1. Solar mapped to 500kV sub. 2. SCADSNV outer zone limit exceeded by non-battery resources. | 1
New_Mexico_Solar | N/A | 0 | 0 | 0 |  |  |  | #N/A | #N/A | #N/A | none selected | none selected |  | 1 | #N/A |  |  |  | 0
Baja_California_Solar | N/A | 0 | 0 | 0 |  |  |  | #N/A | #N/A | #N/A | none selected | none selected |  | 1 |  |  |  |  | 0
Baja_California_Wind | Greater_Imperial-SCADSNV | 495 | 0 | 600 | 1 | ok | ok | ok | breach | 3 | info not available | info not available | 1 | 1 | 3 |  |  | 2. SCADSNV outer zone limit exceeded by non-battery resources. | 1
Pacific_Northwest_Wind | N/A | 0 | 0 | 0 |  |  |  | #N/A | #N/A | #N/A |  |  |  | 1 | #N/A |  |  |  | 0
Idaho_Wind | N/A | 0 | 0 | 0 |  |  |  | #N/A | #N/A | #N/A |  |  |  | 1 |  |  |  |  | 0
Utah_Wind | N/A | 0 | 0 | 0 |  |  |  | #N/A | #N/A | #N/A |  |  |  | 1 |  |  |  |  | 0
Wyoming_Wind | SCADSNV-Mountain_Pass_El_Dorado | 0 | 1500 | 1500 | info not available | ok | ok | breach | breach | 1 | info not available | info not available | 1 | 1 | 0 |  |  |  | 1
Arizona_Wind | N/A | 0 | 0 | 0 |  |  |  | #N/A | #N/A | #N/A |  |  |  | 1 |  |  |  |  | 0
New_Mexico_Wind | SCADSNV-Riverside_Palm_Springs | 945 | 555 | 606 | info not available | ok | ok | ok | breach | 3 | info not available | info not available | 1 | 1 | 3 |  |  | 2. SCADSNV outer zone limit exceeded by non-battery resources. | 1
Pumped Storage Hydro_GreaterImpOutsideTxConstraintZones | GreaterImpOutsideTxConstraintZones | 0 | 0 | 0 |  |  |  | N/A | N/A |  |  |  | 1 | 1 |  |  |  |  | 0
Pumped Storage Hydro_GreaterImpOutsideTxConstraintZones | GreaterImpOutsideTxConstraintZones | 0 | 0 | 0 |  |  |  | N/A | N/A |  |  |  | 1 | 1 |  |  |  |  | 0
Pumped Storage Hydro_SCADSNV_Z4_RiversideAndPalmSprings | SCADSNV_Z4_RiversideAndPalmSprings | 0 | 0 | 0 |  |  |  | N/A | N/A |  |  |  | 1 | 1 |  |  |  |  | 0
Sub Total - Renewables |  | 12911.32 | 8966 | 15960 | [14 empty] | 1
Battery |  | 9448 | 0 | 8873 | [14 empty] | 1
Pumped Hydro Storage |  | 1843 | 0 | 974 | [14 empty] | 1
Sub Total - Energy Storage |  | 11291 | 0 | 9847 | [14 empty] | 1
0

## Dashboard 38MMT (Round 2)
IRP Busbar Mapping Dashboard
Purpose: Quickly communicate compliance of portfolio mapping with the criteria per the Methodology. Highlight MW amounts by zone that breach criteria, if any, and identify next steps as part of the iterative process.
38MMT_20201015_2045_RSP_2019IEPR_adj
Post Round 1 |  | Resource Selection |  | Prior Year Portfolio | Compliance with Criteria
[1=Yes, 2=Possible/Moderate, 3=Materially in Breach]
Resource | Tx Deliv. Zone | 2031 FCDS MW adj | 2031 EO MW adj | Total MW (2019 RSP adj) | 1. Distance to Trans. of Appropriate Voltage | EO Inner Zone | EO outer zone | inner zone | outer zone | 2. Trans. Capability | 3a. Available Land Area | 3b. High Environmental Implications | 4. Comm. Interest | 5. Consistency with Prior Year's Mapping | Notes | Include in display?
Solano_Geothermal | Solano-Sacramento_River | 57 | 48 | 0 | 1 | ok | ok | ok | ok | 1 | info not available | info not available | 1 | 1 |  | 1
Carrizo_Wind | SPGE-Kern_Greater_Carrizo-Carrizo | 287 | 0 | 287 | 1 | ok | ok | ok | breach | 3 | 2 | 2 | 1 | 1 | 2. SPGE outer zone Tx capability exceeded, addressed by proposed upgrade. 3a. Carrizo wind is flagged for exceeding 75% of project candidate land 3b. Project acres exceeds total low-value acres available | 1
Central_Valley_North_Los_Banos_Wind | Central_Valley_North_Los_Banos-SPGE | 173 | 0 | 173 | 1 | breach | ok | breach | breach | 3 | 3 | 2 | 1 | 1 | 2. SPGE outer zone Tx capability exceeded, addressed by proposed upgrade. 3a. Central Valley N Los Banos wind wind is flagged for exceeding project candidate land. 3b. Project area requires 43% of low value land | 1
Greater_Imperial_Solar | Greater_Imperial-SCADSNV | 600 | 548 | 548 | 1 | ok | ok | ok | breach | 3 | 1 | 1 | 1 | 1 | 2. SCADSNV outer zone Tx capability exceeded, addressed by ISO staff guidance of higher limit and proposed upgrade. | 1
Humboldt_Wind | Sacramento_River-Humboldt | 0 | 34 | 34 | 1 | ok | ok | ok | ok | 1 | 1 | 2 | 1 | 1 | 3b. Humboldt Wind has no low-value land area. | 1
Inyokern_North_Kramer_Solar | Greater_Kramer-Inyokern_North_Kramer | 0 | 0 | 97 | 1 | ok | ok | ok | ok | 1 | none selected | none selected | 1 | 2 | 5. Inyokern_North_Kramer_Solar not selected in latest RESOLVE portfolio, despite being selected in previous TPP 2019 RSP adj portfolio. | 1
Kern_Greater_Carrizo_Solar | SPGE-Kern_Greater_Carrizo | 101.32 | 700 | 242 | 1 | ok | ok | ok | breach | 3 | 1 | 1 | 1 | 1 | 2. SPGE outer zone Tx capability exceeded, addressed by proposed upgrade. | 1
Kern_Greater_Carrizo_Wind | SPGE-Kern_Greater_Carrizo | 20 | 0 | 60 | 1 | ok | ok | ok | breach | 3 | 1 | 1 | 1 | 2 | 2. SPGE outer zone Tx capability exceeded, addressed by proposed upgrade. 5. Less allocated than prior year's 2019 RSP portfolio. | 1
Mountain_Pass_El_Dorado_Solar | Mountain_Pass_El_Dorado | 248 | 0 | 248 | 2 | ok | ok | ok | breach | 3 | 1 | 1 | 1 | 1 | 1. Solar mapped to 500kV sub. 2. SCADSNV outer zone Tx capability exceeded, addressed by ISO staff guidance of updated higher limit for SCADSNV. | 1
North_Victor_Solar | North_Victor-Greater_Kramer | 300 | 0 | 300 | 1 | ok | ok | ok | ok | 1 | 1 | 1 | 1 | 1 |  | 1
Northern_California_Ex_Solar | Northern_California_Ex | 0 | 0 | 0 | 1 | ok | ok | ok | breach | 1 | 1 | 1 | 1 | 1 |  | 0
Northern_California_Ex_Wind | Sacramento_River | 767 | 0 | 866 | 1 | ok | ok | ok | ok | 1 | info not available | info not available | 1 | 1 |  | 1
NW_Ext_Tx_Wind | Sacramento_River | 530 | 970 | 0 | 1 | ok | ok | ok | ok | 1 | info not available | info not available | 1 | 1 |  | 1
Sacramento_River_Solar | Sacramento_River | 0 | 896 | 0 | 1 | ok | ok | ok | ok | 1 | 1 | 1 | 1 | 1 |  | 1
SCADSNV_Solar | SCADSNV | 410 | 330 | 330 | 2 | ok | ok | breach | breach | 3 | 1 | 1 | 1 | 1 | 1. Solar mapped to 500kV sub. 2. SCADSNV outer zone Tx capability exceeded, addressed by ISO staff guidance of higher limit and proposed upgrade. | 1
Solano_Solar | Solano-Sacramento_River | 0 | 622 | 0 | 1 | ok | ok | ok | ok | 1 | 1 | 1 | 1 | 1 |  | 1
Solano_Wind | Solano-Sacramento_River | 462 | 0 | 542 | 1 | ok | ok | ok | ok | 1 | 1 | 3 | 1 | 1 | 3b. Solano Wind has one wind tract that exceeds level 3 non-compliance at Lakeville substation. Substation has other wind tracts that can accomodate resources assigned. | 1
Southern_California_Desert_Ex_Solar | Southern_California_Desert_Ex | 0 | 0 | 0 | 2 | ok | ok | ok | breach | 1 | none selected | none selected | 1 | 1 |  | 0
Southern_Nevada_Solar | SCADSNV-GLW_VEA | 182 | 0 | 862 | 1 | ok | ok | ok | breach | 3 | 1 | 1 | 2 | 2 | 2. SCADSNV outer zone Tx capability exceeded, addressed by ISO staff guidance of higher limit and proposed upgrade. 4. & 5. Signficant commercial interest and more selected in previous portfolio, but Tx limits prevent more resources mapped here | 1
Southern_Nevada_Wind | SCADSNV-GLW_VEA | 442 | 0 | 0 | 1 | ok | ok | ok | breach | 3 | info not available | info not available | 1 | 1 | 2. SCADSNV outer zone Tx capability exceeded, addressed by ISO staff guidance of higher limit and proposed upgrade. | 1
SW_Ext_Tx_Wind | SCADSNV-Riverside_Palm_Springs | 0 | 500 | 0 | 1 | breach | ok | breach | breach | 3 | info not available | info not available | 1 | 1 | 2. SCADSNV outer zone Tx capability exceeded, addressed by ISO staff guidance of higher limit and proposed upgrade. | 1
Tehachapi_Solar | Tehachapi | 4876 | 800 | 4202 | 1 | ok | ok | breach | breach | 3 | 1 | 1 | 1 | 1 | 2. Tehachapi zone Tx capability exceeded, addressed by proposed upgrade. | 1
Tehachapi_Wind | Tehachapi | 275 | 0 | 275 | 1 | ok | ok | breach | breach | 3 | 2 | 1 | 1 | 1 | 2. Tehachapi zone Tx capability exceeded, addressed by proposed upgrade. 3a. Tehachapi_Wind is flagged for exceeding 75% of project candidate land. | 1
Westlands_Ex_Solar | Westlands_Ex | 0 | 0 | 0 | 2 | ok | ok | ok | breach | 1 | 1 | 1 | 1 | 1 |  | 0
Westlands_Solar | Central_Valley_North_Los_Banos-SPGE | 1423 | 0 | 1836 | 2 | breach | ok | breach | breach | 3 | 1 | 1 | 1 | 1 | 1. Solar mapped to 500kV sub. 2. SPGE outer zone Tx capability exceeded, addressed by proposed upgrade. | 1
Arizona_Solar | SCADSNV-Riverside_Palm_Springs | 117 | 1463 | 2352 | 2 | breach | ok | breach | breach | 3 | info not available | info not available | 1 | 1 | 1. Solar mapped to 500kV sub. 2. SCADSNV outer zone Tx capability exceeded, addressed by ISO staff guidance of updated higher limit for SCADSNV. | 1
Baja_California_Wind | Greater_Imperial-SCADSNV | 495 | 0 | 600 | 1 | ok | ok | ok | breach | 3 | info not available | info not available | 1 | 1 | 2. SCADSNV outer zone Tx capability exceeded, addressed by ISO staff guidance of higher limit and proposed upgrade. | 1
Wyoming_Wind | SCADSNV-Mountain_Pass_El_Dorado | 1500 | 1500 | 1500 | 1 | ok | ok | breach | breach | 3 | info not available | info not available | 1 | 1 | 2. SCADSNV outer zone Tx capability exceeded, addressed by ISO staff guidance of higher limit and proposed upgrade. | 1
New_Mexico_Wind | SCADSNV-Riverside_Palm_Springs | 945 | 555 | 606 | info not available | breach | ok | breach | breach | 3 | info not available | info not available | 1 | 1 | 2. SCADSNV outer zone Tx capability exceeded, addressed by ISO staff guidance of higher limit and proposed upgrade. | 1
Pisgah_Solar | GK_Z4_Pisgah | 200.5 | 0 | 0 | 1 | ok | ok | ok | ok | 1 | 1 | 1 | 1 | 1 |  | 1
Sub Total - Renewables |  | 14410.82 | 8966 | 15960 | [11 empty] | 1
BatteryStorage_GK_Z2_InyokernAndNorthOfKramer | GK_Z2_InyokernAndNorthOfKramer | 0 |  |  | not applicable |  |  | ok | ok | 1 | not applicable | not applicable | 1 | not applicable |  | 0
BatteryStorage_GK_Z3_NorthOfVictor | GK_Z3_NorthOfVictor | 50 |  |  | not applicable |  |  | ok | ok | 1 | not applicable | not applicable | 1 | not applicable |  | 1
BatteryStorage_GK_Z4_Pisgah | GK_Z4_Pisgah | 126 |  |  | not applicable |  |  | ok | ok | 1 | not applicable | not applicable | 1 | not applicable |  | 1
BatteryStorage_GreaterImpOutsideTxConstraintZones | GreaterImpOutsideTxConstraintZones | 560 |  |  | not applicable |  |  | breach | breach | 3 | not applicable | not applicable | 1 | not applicable | 2. Outside Tx constraints | 1
BatteryStorage_KramerInyoOutsideTxConstraintZones | KramerInyoOutsideTxConstraintZones | 101 |  |  | not applicable |  |  | breach | breach | 3 | not applicable | not applicable | 1 | not applicable | 2. Outside Tx constraints | 1
BatteryStorage_Norcal_Z2_Humboldt | Norcal_Z2_Humboldt | 0 |  |  | not applicable |  |  | ok | ok | 1 | not applicable | not applicable | 1 | not applicable |  | 0
BatteryStorage_Norcal_Z3_SacramentoRiver | Norcal_Z3_SacramentoRiver | 0 |  |  | not applicable |  |  | ok | ok | 1 | not applicable | not applicable | 1 | not applicable |  | 0
BatteryStorage_Norcal_Z4_Solano | Norcal_Z4_Solano | 0 |  |  | not applicable |  |  | ok | ok | 1 | not applicable | not applicable | 1 | not applicable |  | 0
BatteryStorage_Norcal_Z4_Solano_subzone | Norcal_Z4_Solano_subzone | 0 |  |  | not applicable |  |  | ok | ok | 1 | not applicable | not applicable | 1 | not applicable |  | 0
BatteryStorage_NorCalOutsideTxConstraintZones | NorCalOutsideTxConstraintZones | 309 |  |  | not applicable |  |  | ok | breach | 3 | not applicable | not applicable | 1 | not applicable | 2. Outside Tx constraints | 1
BatteryStorage_SCADOutsideTxConstraintZones | SCADOutsideTxConstraintZones | 0 |  |  | not applicable |  |  | ok | breach | 3 | not applicable | not applicable | 1 | not applicable |  | 0
BatteryStorage_SCADSNV_Z2_GLW_VEA | SCADSNV_Z2_GLW_VEA | 100 |  |  | not applicable |  |  | ok | breach | 3 | not applicable | not applicable | 1 | not applicable | 2. SCADSNV outer zone Tx capability exceeded, addressed by ISO staff guidance of higher limit and proposed upgrade. | 1
BatteryStorage_SCADSNV_Z3_GreaterImperial | SCADSNV_Z3_GreaterImperial | 53 |  |  | not applicable |  |  | ok | breach | 3 | not applicable | not applicable | 2 | not applicable | 2. SCADSNV outer zone Tx capability exceeded, addressed by ISO staff guidance of higher limit and proposed upgrade. 4. Battery storage mapped signficantly less than commercial interest. | 1
BatteryStorage_SCADSNV_Z4_RiversideAndPalmSprings | SCADSNV_Z4_RiversideAndPalmSprings | 1313 |  |  | not applicable |  |  | breach | breach | 3 | not applicable | not applicable | 3 | not applicable | 2. SCADSNV outer zone Tx capability exceeded, addressed by ISO staff guidance of higher limit and proposed upgrade. 4. Battery storage mapped signficantly less than commercial interest. | 1
BatteryStorage_SCADSNV_Z5_SCADSNV | SCADSNV_Z5_SCADSNV | 629 |  |  | not applicable |  |  | breach | breach | 3 | not applicable | not applicable | 1 | not applicable | 2. SCADSNV outer zone Tx capability exceeded, addressed by ISO staff guidance of higher limit and proposed upgrade. | 1
BatteryStorage_SPGE_Z1_Westlands | SPGE_Z1_Westlands | 825 |  |  | not applicable |  |  | breach | breach | 3 | not applicable | not applicable | 1 | not applicable | 2. SPGE outer zone Tx capability exceeded, addressed by proposed upgrade. | 1
BatteryStorage_SPGE_Z2_KernAndGreaterCarrizo | SPGE_Z2_KernAndGreaterCarrizo | 53 |  |  | not applicable |  |  | ok | breach | 3 | not applicable | not applicable | 1 | not applicable | 2. SPGE outer zone Tx capability exceeded, addressed by proposed upgrade. | 1
BatteryStorage_SPGE_Z3_Carrizo | SPGE_Z3_Carrizo | 0 |  |  | not applicable |  |  | ok | breach | 3 | not applicable | not applicable | 1 | not applicable |  | 0
BatteryStorage_SPGE_Z4_CentralValleyAndLosBanos | SPGE_Z4_CentralValleyAndLosBanos | 0 |  |  | not applicable |  |  | breach | breach | 3 | not applicable | not applicable | 1 | not applicable |  | 0
BatteryStorage_Tehachapi | Tehachapi | 3121 |  |  | not applicable |  |  | breach | breach | 3 | not applicable | not applicable | 2 | not applicable | 2. Tehachapi zone Tx capability exceeded, addressed by proposed upgrade. 4. Battery storage mapped signficantly less than commercial interest. | 1
BatteryStorage_TehachapiOutsideTxConstraintZones | TehachapiOutsideTxConstraintZones | 2208 |  |  | not applicable |  |  | breach | breach | 3 | not applicable | not applicable | 1 | not applicable | 2. Outside Tx constraints | 1
BatteryStorage_WestlandsOutsideTxConstraintZones | WestlandsOutsideTxConstraintZones | 0 |  |  | not applicable |  |  | ok | breach | 3 | not applicable | not applicable | 1 | not applicable |  | 0
Sub Total - Battery Storage |  | 9448 | 0 | 8873 | [11 empty] | 1
Pumped Storage Hydro_GreaterImpOutsideTxConstraintZones | GreaterImpOutsideTxConstraintZones | 500 |  | 487 | info not available | ok | ok | breach | breach | info not available | not applicable | info not available | 1 | 1 |  | 1
Pumped Storage Hydro_SCADSNV_Z4_RiversideAndPalmSprings | SCADSNV_Z4_RiversideAndPalmSprings | 1343 |  | 0 | info not available | breach | ok | breach | breach | 3 | not applicable | info not available | 1 | 1 | 2. SCADSNV outer zone Tx capability exceeded, addressed by ISO staff guidance of higher limit and proposed upgrade. | 1
Sub Total - Pumped Storage Hydro |  | 1843 |  | 974 | [11 empty] | 1
Sub Total - Energy Storage |  | 11291 | 0 | 9847 | [11 empty] | 1
Total |  | 25701.82 | 8966 | 25807 | [11 empty] | 1

## proposedAdjustments
| Proposed Adjustments | FD | EO
1 | Westlands_Ex_Solar | -1779 |  | Move 1779 from Westlands_Ex solar to Westlands, Tehachapi, and Pisgah solar (due to overlap in the tx capability estimates between “Ex” zone and core tx constraint zones – the estimates for the core zones have greater confidence and should probably supersede)
| Tehachapi_Solar | 623 |  | Allocate 623 MW to Tehachapi to reduce amount of resources to be mapped to Gates 500 kV system where there is little commercial interest
| Pisgah_Solar | 200.5 |  | Allocate 201 MW to Pisgah to reduce amount of resources to be mapped to Gates 500 kV system where there is little commercial interest
| Westlands_Solar | 955 |  | Allocate 576 MW across Westlands substations and allocate excess to Gates 500 kV system, per ISO guidance
2 | Tehachapi_Solar | 0 |  | Change occurs at substation level within zone. Reassign to Vincent 230kV bus
3 | Arizona_Solar | 0 |  | Change occurs at substation level within zone. Reassign 993 MW from Hoodoo bus to Delaney and Hassayampa
4 | Pumped Storage Hydro | 0 |  | Add pumped storage hydro to busbar mapping. No change to RESOLVE selection, simply new to busbar mapping
5 | Arizona_Solar | -330 |  | Move this amount to SCADSNV_Solar to alleviate Tx exceedance in Riverside inner Tx zone created by mapping pumped hydro to Red Bluff
| SCADSNV_Solar | 330 |  | Amount from Arizona solar due to Riverside Tx exceedance. Map to Mohave 500kV
6 | Southern_California_Desert_Ex_Solar | -862 |  | Move 862 MW from Southern California Desert Ex Solar to SNV solar (same rationale as for Westlands_Ex), excess is moved to Riverside and Imperial
| Southern_Nevada_Solar | 182 |  | Amount that can fit without violating tx limit (map to Innovation, Desert View, and Crazy Eyes)
| Greater_Imperial_Solar | 600 |  | Allocate Southern Nevada Solar to Imperial up to inner Tx zone limit
| SCADSNV_Solar | 80 |  | Allocate excess SNV Solar to Mohave 500kV
7 | Sacramento_River_Solar |  | -665 | EO Tx exceedance in outer northern CA zone by 443 MW
| Westlands_Solar |  | 665 | Amount of exceedance of Tx zone for Sacramento River Solar
8 | Northern_California_Ex_Solar | -397 |  | No commercial interest and in Ex zone so move to Tehachapi
| Tehachapi_Solar | 397 |  | Amount of solar from Northen CA Ex zone, Tehachapi has Tx headroom with Tx build out selected by RESOLVE.
9 | Wyoming_Wind | 1500 | -1500 | Convert 1,500 MW of Wyoming Wind from EO to FD

## SelectedPortfolio_38MMT
Portfolio: | 38MMT_20201015_2045_RSP_2019IEPR
Portfolio Analytics
| FCDS Renewable Resource Summary by Location (MW) |  |  |  |  | EO Renewable Resource Summary by Location (MW)
| RESOLVE Resource | Tx Zone | 2031 FD | Proposed Adjustment | Adjusted Value (FD) | RESOLVE Resource | Tx Zone | 2031 EO | Proposed Adjustment | Adjusted Value (EO) | FD + EO | Adjusted (FD + EO)
| InState_Biomass | None | 0 | 0 | 0 | InState_Biomass | None |  | 0 | 0 | 0 | 0
| Greater_Imperial_Geothermal | Greater_Imperial-SCADSNV | 0 | 0 | 0 | Greater_Imperial_Geothermal | Greater_Imperial-SCADSNV |  | 0 | 0 | 0 | 0
| Inyokern_North_Kramer_Geothermal | Greater_Kramer-Inyokern_North_Kramer | 0 | 0 | 0 | Inyokern_North_Kramer_Geothermal | Greater_Kramer-Inyokern_North_Kramer |  | 0 | 0 | 0 | 0
| Northern_California_Ex_Geothermal | Northern_California_Ex | 0 | 0 | 0 | Northern_California_Ex_Geothermal | Northern_California_Ex |  | 0 | 0 | 0 | 0
| Pacific_Northwest_Geothermal | N/A | 0 | 0 | 0 | Pacific_Northwest_Geothermal | N/A |  | 0 | 0 | 0 | 0
| Riverside_Palm_Springs_Geothermal | SCADSNV-Riverside_Palm_Springs | 0 | 0 | 0 | Riverside_Palm_Springs_Geothermal | SCADSNV-Riverside_Palm_Springs |  | 0 | 0 | 0 | 0
| Solano_Geothermal | Solano-Sacramento_River | 57 | 0 | 57 | Solano_Geothermal | Solano-Sacramento_River | 48 | 0 | 48 | 105 | 105
| Southern_Nevada_Geothermal | SCADSNV-Mountain_Pass_El_Dorado | 0 | 0 | 0 | Southern_Nevada_Geothermal | SCADSNV-Mountain_Pass_El_Dorado |  | 0 | 0 | 0 | 0
| Carrizo_Solar | SPGE-Kern_Greater_Carrizo-Carrizo | 0 | 0 | 0 | Carrizo_Solar | SPGE-Kern_Greater_Carrizo-Carrizo |  | 0 | 0 | 0 | 0
| Carrizo_Wind | SPGE-Kern_Greater_Carrizo-Carrizo | 287 | 0 | 287 | Carrizo_Wind | SPGE-Kern_Greater_Carrizo-Carrizo |  | 0 | 0 | 287 | 287
| Central_Valley_North_Los_Banos_Solar | Central_Valley_North_Los_Banos-SPGE | 0 | 0 | 0 | Central_Valley_North_Los_Banos_Solar | Central_Valley_North_Los_Banos-SPGE |  | 0 | 0 | 0 | 0
| Central_Valley_North_Los_Banos_Wind | Central_Valley_North_Los_Banos-SPGE | 173 | 0 | 173 | Central_Valley_North_Los_Banos_Wind | Central_Valley_North_Los_Banos-SPGE |  | 0 | 0 | 173 | 173
| Distributed_Solar | None | 0 | 0 | 0 | Distributed_Solar | None |  | 0 | 0 | 0 | 0
| Distributed_Wind | #N/A | 0 | 0 | 0 | Distributed_Wind | #N/A |  | 0 | 0 | 0 | 0
| Greater_Imperial_Solar | Greater_Imperial-SCADSNV | 0 | 600 | 600 | Greater_Imperial_Solar | Greater_Imperial-SCADSNV | 548 | 0 | 548 | 548 | 1148
| Greater_Imperial_Wind | Greater_Imperial-SCADSNV | 0 | 0 | 0 | Greater_Imperial_Wind | Greater_Imperial-SCADSNV |  | 0 | 0 | 0 | 0
| Greater_Kramer_Wind | Greater_Kramer | 0 | 0 | 0 | Greater_Kramer_Wind | Greater_Kramer |  | 0 | 0 | 0 | 0
| Humboldt_Wind | Sacramento_River-Humboldt | 0 | 0 | 0 | Humboldt_Wind | Sacramento_River-Humboldt | 34 | 0 | 34 | 34 | 34
| Inyokern_North_Kramer_Solar | Greater_Kramer-Inyokern_North_Kramer | 0 | 0 | 0 | Inyokern_North_Kramer_Solar | Greater_Kramer-Inyokern_North_Kramer |  | 0 | 0 | 0 | 0
| Kern_Greater_Carrizo_Solar | SPGE-Kern_Greater_Carrizo | 101.32 | 0 | 101.32 | Kern_Greater_Carrizo_Solar | SPGE-Kern_Greater_Carrizo | 700 | 0 | 700 | 801.32 | 801.32
| Kern_Greater_Carrizo_Wind | SPGE-Kern_Greater_Carrizo | 20 | 0 | 20 | Kern_Greater_Carrizo_Wind | SPGE-Kern_Greater_Carrizo |  | 0 | 0 | 20 | 20
| Kramer_Inyokern_Ex_Solar | Kramer_Inyokern_Ex | 0 | 0 | 0 | Kramer_Inyokern_Ex_Solar | Kramer_Inyokern_Ex |  | 0 | 0 | 0 | 0
| Kramer_Inyokern_Ex_Wind | Kramer_Inyokern_Ex | 0 | 0 | 0 | Kramer_Inyokern_Ex_Wind | Kramer_Inyokern_Ex |  | 0 | 0 | 0 | 0
| Mountain_Pass_El_Dorado_Solar | Mountain_Pass_El_Dorado | 248 | 0 | 248 | Mountain_Pass_El_Dorado_Solar | Mountain_Pass_El_Dorado |  | 0 | 0 | 248 | 248
| North_Victor_Solar | North_Victor-Greater_Kramer | 300 | 0 | 300 | North_Victor_Solar | North_Victor-Greater_Kramer |  | 0 | 0 | 300 | 300
| Northern_California_Ex_Solar | Northern_California_Ex | 397 | -397 | 0 | Northern_California_Ex_Solar | Northern_California_Ex |  | 0 | 0 | 397 | 0
| Northern_California_Ex_Wind | Sacramento_River | 767 | 0 | 767 | Northern_California_Ex_Wind | Sacramento_River |  | 0 | 0 | 767 | 767
| NW_Ext_Tx_Wind | Sacramento_River | 530 | 0 | 530 | NW_Ext_Tx_Wind | Sacramento_River | 970 | 0 | 970 | 1500 | 1500
| Riverside_Palm_Springs_Solar | SCADSNV-Riverside_Palm_Springs | 0 | 0 | 0 | Riverside_Palm_Springs_Solar | SCADSNV-Riverside_Palm_Springs |  | 0 | 0 | 0 | 0
| Sacramento_River_Solar | Sacramento_River | 0 | 0 | 0 | Sacramento_River_Solar | Sacramento_River | 896 | -665 | 231 | 896 | 231
| Sacramento_River_Wind | N/A | 0 | 0 | 0 | Sacramento_River_Wind | N/A |  | 0 | 0 | 0 | 0
| SCADSNV_Solar | SCADSNV | 0 | 410 | 410 | SCADSNV_Solar | SCADSNV | 330 | 0 | 330 | 330 | 740
| SCADSNV_Wind | SCADSNV | 0 | 0 | 0 | SCADSNV_Wind | SCADSNV |  | 0 | 0 | 0 | 0
| Solano_Solar | Solano-Sacramento_River | 0 | 0 | 0 | Solano_Solar | Solano-Sacramento_River | 622 | 0 | 622 | 622 | 622
| Solano_subzone_Solar | Solano-Sacramento_River-Solano_subzone | 0 | 0 | 0 | Solano_subzone_Solar | Solano-Sacramento_River-Solano_subzone |  | 0 | 0 | 0 | 0
| Solano_subzone_Wind | Solano-Sacramento_River-Solano_subzone | 0 | 0 | 0 | Solano_subzone_Wind | Solano-Sacramento_River-Solano_subzone |  | 0 | 0 | 0 | 0
| Solano_Wind | Solano-Sacramento_River | 462 | 0 | 462 | Solano_Wind | Solano-Sacramento_River |  | 0 | 0 | 462 | 462
| Southern_California_Desert_Ex_Solar | Southern_California_Desert_Ex | 862 | -862 | 0 | Southern_California_Desert_Ex_Solar | Southern_California_Desert_Ex |  | 0 | 0 | 862 | 0
| Southern_California_Desert_Ex_Wind | Southern_California_Desert_Ex | 0 | 0 | 0 | Southern_California_Desert_Ex_Wind | Southern_California_Desert_Ex |  | 0 | 0 | 0 | 0
| Southern_Nevada_Solar | SCADSNV-GLW_VEA | 0 | 182 | 182 | Southern_Nevada_Solar | SCADSNV-GLW_VEA |  | 0 | 0 | 0 | 182
| Southern_Nevada_Wind | SCADSNV-GLW_VEA | 442 | 0 | 442 | Southern_Nevada_Wind | SCADSNV-GLW_VEA |  | 0 | 0 | 442 | 442
| SW_Ext_Tx_Wind | SCADSNV-Riverside_Palm_Springs | 0 | 0 | 0 | SW_Ext_Tx_Wind | SCADSNV-Riverside_Palm_Springs | 500 | 0 | 500 | 500 | 500
| Tehachapi_Solar | Tehachapi | 3856 | 1020 | 4876 | Tehachapi_Solar | Tehachapi | 800 | 0 | 800 | 4656 | 5676
| Tehachapi_Ex_Solar | Tehachapi_Ex | 0 | 0 | 0 | Tehachapi_Ex_Solar | Tehachapi_Ex |  | 0 | 0 | 0 | 0
| Tehachapi_Wind | Tehachapi | 275 | 0 | 275 | Tehachapi_Wind | Tehachapi |  | 0 | 0 | 275 | 275
| Westlands_Ex_Solar | Westlands_Ex | 1779 | -1779 | 0 | Westlands_Ex_Solar | Westlands_Ex |  | 0 | 0 | 1779 | 0
| Westlands_Ex_Wind | N/A | 0 | 0 | 0 | Westlands_Ex_Wind | N/A |  | 0 | 0 | 0 | 0
| Westlands_Solar | Central_Valley_North_Los_Banos-SPGE | 468 | 955 | 1423 | Westlands_Solar | Central_Valley_North_Los_Banos-SPGE |  | 665 | 665 | 468 | 2088
| Cape_Mendocino_Offshore_Wind | N/A | 0 | 0 | 0 | Cape_Mendocino_Offshore_Wind | N/A |  | 0 | 0 | 0 | 0
| Del_Norte_Offshore_Wind | N/A | 0 | 0 | 0 | Del_Norte_Offshore_Wind | N/A |  | 0 | 0 | 0 | 0
| Diablo_Canyon_Offshore_Wind_Ext_Tx | N/A | 0 | 0 | 0 | Diablo_Canyon_Offshore_Wind_Ext_Tx | N/A |  | 0 | 0 | 0 | 0
| Diablo_Canyon_Offshore_Wind | N/A | 0 | 0 | 0 | Diablo_Canyon_Offshore_Wind | N/A |  | 0 | 0 | 0 | 0
| Humboldt_Bay_Offshore_Wind | N/A | 0 | 0 | 0 | Humboldt_Bay_Offshore_Wind | N/A |  | 0 | 0 | 0 | 0
| Morro_Bay_Offshore_Wind | N/A | 0 | 0 | 0 | Morro_Bay_Offshore_Wind | N/A |  | 0 | 0 | 0 | 0
| Utah_Solar | N/A | 0 | 0 | 0 | Utah_Solar | N/A |  | 0 | 0 | 0 | 0
| Arizona_Solar | SCADSNV-Riverside_Palm_Springs | 447 | -330 | 117 | Arizona_Solar | SCADSNV-Riverside_Palm_Springs | 1463 | 0 | 1463 | 1910 | 1580
| New_Mexico_Solar | N/A | 0 | 0 | 0 | New_Mexico_Solar | N/A |  | 0 | 0 | 0 | 0
| Baja_California_Solar | N/A | 0 | 0 | 0 | Baja_California_Solar | N/A |  | 0 | 0 | 0 | 0
| Baja_California_Wind | Greater_Imperial-SCADSNV | 495 | 0 | 495 | Baja_California_Wind | Greater_Imperial-SCADSNV |  | 0 | 0 | 495 | 495
| Pacific_Northwest_Wind | N/A | 0 | 0 | 0 | Pacific_Northwest_Wind | N/A |  | 0 | 0 | 0 | 0
| Idaho_Wind | N/A | 0 | 0 | 0 | Idaho_Wind | N/A |  | 0 | 0 | 0 | 0
| Utah_Wind | N/A | 0 | 0 | 0 | Utah_Wind | N/A |  | 0 | 0 | 0 | 0
| Wyoming_Wind | SCADSNV-Mountain_Pass_El_Dorado | 0 | 1500 | 1500 | Wyoming_Wind | SCADSNV-Mountain_Pass_El_Dorado | 1500 | -1500 | 0 | 1500 | 1500
| Arizona_Wind | N/A | 0 | 0 | 0 | Arizona_Wind | N/A |  | 0 | 0 | 0 | 0
| New_Mexico_Wind | SCADSNV-Riverside_Palm_Springs | 945 | 0 | 945 | New_Mexico_Wind | SCADSNV-Riverside_Palm_Springs | 555 | 0 | 555 | 1500 | 1500
| Pisgah_Solar | GK_Z4_Pisgah |  | 200.5 | 200.5 | Pisgah_Solar | GK_Z4_Pisgah | 0 | 0 | 0 | 0 | 200.5
| Pumped Storage Hydro_GreaterImpOutsideTxConstraintZones | GreaterImpOutsideTxConstraintZones |  | 500 | 500 | Pumped Storage Hydro_GreaterImpOutsideTxConstraintZones | GreaterImpOutsideTxConstraintZones |  | 0 |  | 0 | 500
| Pumped Storage Hydro_SCADSNV_Z4_RiversideAndPalmSprings | SCADSNV_Z4_RiversideAndPalmSprings |  | 1343 | 1343 | Pumped Storage Hydro_SCADSNV_Z4_RiversideAndPalmSprings | SCADSNV_Z4_RiversideAndPalmSprings |  | 0 |  | 0 | 1343
| BatteryStorage_GK_Z2_InyokernAndNorthOfKramer | GK_Z2_InyokernAndNorthOfKramer |  | 0 | 0 | BatteryStorage_GK_Z2_InyokernAndNorthOfKramer | GK_Z2_InyokernAndNorthOfKramer | 0 | 0 | 0 | 0 | 0
| BatteryStorage_GK_Z3_NorthOfVictor | GK_Z3_NorthOfVictor |  | 50 | 50 | BatteryStorage_GK_Z3_NorthOfVictor | GK_Z3_NorthOfVictor | 0 | 0 | 0 | 0 | 50
| BatteryStorage_GK_Z4_Pisgah | GK_Z4_Pisgah |  | 126 | 126 | BatteryStorage_GK_Z4_Pisgah | GK_Z4_Pisgah | 0 | 0 | 0 | 0 | 126
| BatteryStorage_GreaterImpOutsideTxConstraintZones | GreaterImpOutsideTxConstraintZones |  | 560 | 560 | BatteryStorage_GreaterImpOutsideTxConstraintZones | GreaterImpOutsideTxConstraintZones | 0 | 0 | 0 | 0 | 560
| BatteryStorage_KramerInyoOutsideTxConstraintZones | KramerInyoOutsideTxConstraintZones |  | 101 | 101 | BatteryStorage_KramerInyoOutsideTxConstraintZones | KramerInyoOutsideTxConstraintZones | 0 | 0 | 0 | 0 | 101
| BatteryStorage_Norcal_Z2_Humboldt | Norcal_Z2_Humboldt |  | 0 | 0 | BatteryStorage_Norcal_Z2_Humboldt | Norcal_Z2_Humboldt | 0 | 0 | 0 | 0 | 0
| BatteryStorage_Norcal_Z3_SacramentoRiver | Norcal_Z3_SacramentoRiver |  | 0 | 0 | BatteryStorage_Norcal_Z3_SacramentoRiver | Norcal_Z3_SacramentoRiver | 0 | 0 | 0 | 0 | 0
| BatteryStorage_Norcal_Z4_Solano | Norcal_Z4_Solano |  | 0 | 0 | BatteryStorage_Norcal_Z4_Solano | Norcal_Z4_Solano | 0 | 0 | 0 | 0 | 0
| BatteryStorage_Norcal_Z4_Solano_subzone | Norcal_Z4_Solano_subzone |  | 0 | 0 | BatteryStorage_Norcal_Z4_Solano_subzone | Norcal_Z4_Solano_subzone | 0 | 0 | 0 | 0 | 0
| BatteryStorage_NorCalOutsideTxConstraintZones | NorCalOutsideTxConstraintZones |  | 309 | 309 | BatteryStorage_NorCalOutsideTxConstraintZones | NorCalOutsideTxConstraintZones | 0 | 0 | 0 | 0 | 309
| BatteryStorage_SCADOutsideTxConstraintZones | SCADOutsideTxConstraintZones |  | 0 | 0 | BatteryStorage_SCADOutsideTxConstraintZones | SCADOutsideTxConstraintZones | 0 | 0 | 0 | 0 | 0
| BatteryStorage_SCADSNV_Z2_GLW_VEA | SCADSNV_Z2_GLW_VEA |  | 100 | 100 | BatteryStorage_SCADSNV_Z2_GLW_VEA | SCADSNV_Z2_GLW_VEA | 0 | 0 | 0 | 0 | 100
| BatteryStorage_SCADSNV_Z3_GreaterImperial | SCADSNV_Z3_GreaterImperial |  | 53 | 53 | BatteryStorage_SCADSNV_Z3_GreaterImperial | SCADSNV_Z3_GreaterImperial | 0 | 0 | 0 | 0 | 53
| BatteryStorage_SCADSNV_Z4_RiversideAndPalmSprings | SCADSNV_Z4_RiversideAndPalmSprings |  | 1313 | 1313 | BatteryStorage_SCADSNV_Z4_RiversideAndPalmSprings | SCADSNV_Z4_RiversideAndPalmSprings | 0 | 0 | 0 | 0 | 1313
| BatteryStorage_SCADSNV_Z5_SCADSNV | SCADSNV_Z5_SCADSNV |  | 629 | 629 | BatteryStorage_SCADSNV_Z5_SCADSNV | SCADSNV_Z5_SCADSNV | 0 | 0 | 0 | 0 | 629
| BatteryStorage_SouthernPGE | SouthernPGE |  | 0 | 0 | BatteryStorage_SouthernPGE | SouthernPGE | 0 | 0 | 0 | 0 | 0
| BatteryStorage_SPGE_Z1_Westlands | SPGE_Z1_Westlands |  | 825 | 825 | BatteryStorage_SPGE_Z1_Westlands | SPGE_Z1_Westlands | 0 | 0 | 0 | 0 | 825
| BatteryStorage_SPGE_Z2_KernAndGreaterCarrizo | SPGE_Z2_KernAndGreaterCarrizo |  | 53 | 53 | BatteryStorage_SPGE_Z2_KernAndGreaterCarrizo | SPGE_Z2_KernAndGreaterCarrizo | 0 | 0 | 0 | 0 | 53
| BatteryStorage_SPGE_Z3_Carrizo | SPGE_Z3_Carrizo |  | 0 | 0 | BatteryStorage_SPGE_Z3_Carrizo | SPGE_Z3_Carrizo | 0 | 0 | 0 | 0 | 0
| BatteryStorage_SPGE_Z4_CentralValleyAndLosBanos | SPGE_Z4_CentralValleyAndLosBanos |  | 0 | 0 | BatteryStorage_SPGE_Z4_CentralValleyAndLosBanos | SPGE_Z4_CentralValleyAndLosBanos | 0 | 0 | 0 | 0 | 0
| BatteryStorage_Tehachapi | Tehachapi |  | 3121 | 3121 | BatteryStorage_Tehachapi | Tehachapi | 0 | 0 | 0 | 0 | 3121
| BatteryStorage_TehachapiOutsideTxConstraintZones | TehachapiOutsideTxConstraintZones |  | 2208 | 2208 | BatteryStorage_TehachapiOutsideTxConstraintZones | TehachapiOutsideTxConstraintZones | 0 | 0 | 0 | 0 | 2208
| BatteryStorage_WestlandsOutsideTxConstraintZones | WestlandsOutsideTxConstraintZones |  | 0 | 0 | BatteryStorage_WestlandsOutsideTxConstraintZones | WestlandsOutsideTxConstraintZones | 0 | 0 | 0 | 0 | 0

## 2_TxCapability
What constitutes level 3 criteria flag? |  | Selected resource exceeds transmission capability (Full deliverability or energy only)
1. Applied first to all sub-zones
2. Applied next to all outer-zones
| Transmission Capability Estimated for IRP (CAISO Transmission Capability Whitepaper May 20, 2019)² | [13 empty] | RESOLVE Selected Portfolio | [17 empty] | RESOLVE Selected Portfolio Aggregated and Compared to Tx Constraint Zone Limits
| Transmission Zones | Estimated FCDS Capability (MW) | [5 empty] | Incremental Upgrade Cost Estimate ($million) |  |  |  | Estimated EODS Capability (MW) | New EO Values - level I³ | New EO Values - level II³ | Resource | Inner Zone | Outer Zone | Selected by RESOLVE | Selected by RESOLVE (FD) | FD tx limit check | Selected by RESOLVE (EO) | EO tx limit check | FD + EO tx limit check | Outer Zone EO tx limit Check | Outer Zone FD tx limit Check | Adjusted Selected resources (FD) | FD tx limit check | Adjusted Selected resources (EO) | EO tx limit check | FD + EO tx limit check | Outer Zone EO tx limit Check | Outer Zone FD tx limit Check | Zone | Portfolio | [7 empty] | Adjusted portfolio
|  | Existing System | Post-2018 COD Capacity in Baseline | Fully Deliverable New Tx Limit Net of "NEW" Baseline Contracts | Minor Upgrades | Major Upgrade #1 | Major Upgrade #2 | Existing System | Minor Upgrades | Major Upgrade #1 | Major Upgrade #2 | Existing System |  |  | InState_Biomass | N/A |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Zone Name in RESOLVE | Selected Resource (FD MW) | Selected Resource (EO MW) | Remaining Tx Capability (FD) | Exceeds Tx Capability (FD)? | Remaining Tx Capability (EO) | Exceeds Tx Capability (EO)? | Exceeds Outer Zone Tx Capability (FD)? | Exceeds Outer Zone Tx Capability (EO)? | Selected Resource (FD MW Adj) | Selected Resource (EO MW Adj) | Remaining Tx Capability (FD Adj) | Exceeds Tx Capability (FD adj)? | Remaining Tx Capability (EO adj) | Exceeds Tx Capability (EO adj)? | Exceeds Outer Zone Tx Capability (FD)? | Exceeds Outer Zone Tx Capability (EO)?
11000 | Northern CA | 2000 | 0 | 1821 |  | 2000 |  |  |  | 285 |  | 3900 | 3900 | 3900 | Greater_Imperial_Geothermal | SCADSNV_Z3_GreaterImperial | Southern CA Desert and Southern NV | 0 | 0 | ok | 0 | ok | ok | ok | breach | 0 | ok | 0 | ok | ok | ok | breach
| Round Mountain | 500 | 0 | 500 | [7 empty] | 2100 | 2100 | 2100 | Inyokern_North_Kramer_Geothermal | GK_Z2_InyokernAndNorthOfKramer | Greater Kramer (North of Lugo) | 0 | 0 | ok | 0 | ok | ok | ok | ok | 0 | ok | 0 | ok | ok | ok | ok | Northern CA |  |  | 5 |  | -665 |  | 0 | 1 |  |  | 5 | 0 | 0 | 0 | 0 | 0
| Humboldt | 0 | 0 | 0 | [7 empty] | 100 | 100 | 100 | Northern_California_Geothermal | NorCalOutsideTxConstraintZones | Ex Zones | 0 | 0 | ok | 0 | ok | ok | ok | ok | 0 | ok | 0 | ok | ok | ok | breach | Norcal_Z2_Humboldt | 0 | 34 | 0 | 0 | 66 | 0 |  |  | 0 | 34 | 0 | 0 | 66 | 0
| Sacramento River | 2000 | 99 | 1901 | [7 empty] | 4600 | 4600 | 4600 | Pacific_Northwest_Geothermal | N/A |  | #N/A | 0 | #N/A | 0 |  | #N/A | #N/A | #N/A | 0 |  | 0 |  | breach | #N/A | #N/A | Norcal_Z3_SacramentoRiver | 1297 | 1866 | 604 | 0 | 1338 | 0 |  |  | 1297 | 1201 | 604 | 0 | 2003 | 0
| Solano | 600 | 80 | 520 |  | 2000 |  |  |  | 322 |  | 1300 | 1300 | 1300 | Riverside_Palm_Springs_Geothermal | SCADSNV_Z4_RiversideAndPalmSprings | Southern CA Desert and Southern NV | 0 | 0 | ok | 0 | ok | ok | ok | breach | 0 | breach | 0 | breach | breach | ok | breach | Norcal_Z4_Solano | 519 | 670 | 1 | 0 | 31 | 0 |  |  | 519 | 670 | 1 | 0 | 31 | 0
[15 empty] | Solano_Geothermal | Norcal_Z4_Solano | Northern CA | 105 | 57 | ok | 48 | ok | ok | breach | ok | 57 | ok | 48 | ok | ok | ok | ok | Norcal_Z4_Solano_subzone | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Southern PG&E | 1100 | 0 | 394.32 |  | 1000 |  |  |  | 55 |  | 1800 | 4180 | 5180 | Southern_Nevada_Geothermal | SCADSNV_Z1_EldoradoAndMtnPass | Southern CA Desert and Southern NV | 0 | 0 | ok | 0 | ok | ok | ok | breach | 0 | ok | 0 | ok | ok | ok | breach | Southern PG&E |  |  | -655 |  | 2725 |  | 1 | 0 |  |  | -1783 | 1 | 932 | 0 | 1 | 0
| Westlands⁶ |  | 0 | 0 |  | 1000 |  |  |  | 55 |  | TBD | 2200 | 3200 | Carrizo_Solar | SPGE_Z3_Carrizo | Southern PG&E | 0 | 0 | ok | 0 | ok | ok | ok | breach | 0 | ok | 0 | ok | ok | ok | breach | SPGE_Z1_Westlands | 0 | 0 | 0 | 0 | 3200 | 0 |  |  | 173 | 0 | -173 | 1 | 3027 | 0
| Kern and Greater Carrizo | 1000 | 375.68 | 624.32 |  | 1500 |  |  |  | 241 |  | 1700 | 4180 | 4180 | Carrizo_Wind | SPGE_Z3_Carrizo | Southern PG&E | 287 | 287 | ok | 0 | ok | ok | ok | breach | 287 | ok | 0 | ok | ok | ok | breach | SPGE_Z2_KernAndGreaterCarrizo | 121.32 | 700 | 503 | 0 | 2983 | 0 |  |  | 121.32 | 700 | 503 | 0 | 2983 | 0
| Carrizo | 400 | 0 | 400 |  | 700 |  |  |  | 53 |  | 400 | 400 | 1100 | Central_Valley_North_Los_Banos_Solar | SPGE_Z4_CentralValleyAndLosBanos | Southern PG&E | 0 | 0 | ok | 0 | ok | ok | ok | breach | 0 | breach | 0 | breach | breach | ok | breach | SPGE_Z3_Carrizo | 287 | 0 | 113 | 0 | 813 | 0 |  |  | 287 | 0 | 113 | 0 | 813 | 0
| Central Valley North & Los Banos | 1000 | 330 | 670 |  | 1000 |  |  |  | 274 |  | 1000 | 1000 | 1000 | Central_Valley_North_Los_Banos_Wind | SPGE_Z4_CentralValleyAndLosBanos | Southern PG&E | 173 | 173 | ok | 0 | ok | ok | ok | breach | 173 | breach | 0 | breach | breach | ok | breach | SPGE_Z4_CentralValleyAndLosBanos | 641 | 0 | 29 | 0 | 29 | 0 |  |  | 1596 | 665 | -926 | 1 | -1591 | 1
[15 empty] | Distributed_Solar | N/A |  | #N/A | 0 | #N/A | 0 |  | #N/A | #N/A | #N/A | 0 |  | 0 |  | breach | #N/A | #N/A
| Tehachapi | 4300 | 145 | 4155 | 1000 |  |  |  | 100 |  |  | 5100 | 6100 | 6100 | Distributed_Wind | N/A |  | #N/A | 0 | #N/A | 0 |  | #N/A | #N/A | #N/A | 0 |  | 0 |  | breach | #N/A | #N/A | Tehachapi | 4131 | 800 | 24 | 0 | 1024 | 0 | 0 | 0 | 5151 | 800 | -996 | 1 | 149 | 0 | 1 | 0
[15 empty] | Greater_Imperial_Solar | SCADSNV_Z3_GreaterImperial | Southern CA Desert and Southern NV | 548 | 0 | ok | 548 | ok | ok | ok | breach | 600 | ok | 548 | ok | ok | ok | breach | Greater Kramer (North of Lugo) |  |  | 200.5 |  | 200.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Greater Kramer (North of Lugo) | 600 | 0 | 500.5 |  | 400 |  |  |  | 146 |  | 600 | 600 | 600 | Greater_Imperial_Wind | SCADSNV_Z3_GreaterImperial | Southern CA Desert and Southern NV | 0 | 0 | ok | 0 | ok | ok | ok | breach | 0 | ok | 0 | ok | ok | ok | breach | GK_Z1_GreaterKramer | 0 | 0 | 500.5 | 0 | 200.5 | 0 |  |  | 0 | 0 | 500.5 | 0 | 0 | 0
| North of Victor | 300 | 0 | 300 |  | 400 |  |  |  | 485 |  | 300 | 300 | 300 | Greater_Kramer_Wind | GK_Z1_GreaterKramer | Greater Kramer (North of Lugo) | 0 | 0 | ok | 0 | ok | ok | ok | ok | 0 | ok | 0 | ok | ok | ok | ok | GK_Z3_NorthOfVictor | 300 | 0 | 0 | 0 | 0 | 0 |  |  | 300 | 0 | 0 | 0 | 0 | 0
| Inyokern and North of Kramer | 100 | 99.5 | 0.5 |  | 400 |  |  |  | 485 |  | 100 | 100 | 100 | Humboldt_Wind | Norcal_Z2_Humboldt | Northern CA | 34 | 0 | ok | 34 | ok | ok | breach | ok | 0 | ok | 34 | ok | ok | ok | ok | GK_Z2_InyokernAndNorthOfKramer | 0 | 0 | 0.5 | 0 | 0.5 | 0 |  |  | 0 | 0 | 0.5 | 0 | 0.5 | 0
| Pisgah | 400 | 0 | 400 |  | 400 |  |  |  | 261 |  | 400 | 400 | 400 | Inyokern_North_Kramer_Solar | GK_Z2_InyokernAndNorthOfKramer | Greater Kramer (North of Lugo) | 0 | 0 | ok | 0 | ok | ok | ok | ok | 0 | ok | 0 | ok | ok | ok | ok | GK_Z4_Pisgah | 0 | 0 | 400 | 0 | 400 | 0 |  |  | 200.5 | 0 | 199.5 | 0 | 199.5 | 0
[15 empty] | Kern_Greater_Carrizo_Solar | SPGE_Z2_KernAndGreaterCarrizo | Southern PG&E | 801.32 | 101.32 | ok | 700 | ok | ok | ok | breach | 101.32 | ok | 700 | ok | ok | ok | breach | Southern CA Desert and Southern NV |  |  | -303.5 |  | 5060.5 |  | 1 | 0 |  |  | -5268.5 | 1 | 1595.5 | 0 | 1 | 0
| Southern CA Desert and Southern NV | 3000 | 0 | 2273.5 |  | 2800 |  |  |  | 2156 |  | 9600 | 10460 | 13260 | Kern_Greater_Carrizo_Wind | SPGE_Z2_KernAndGreaterCarrizo | Southern PG&E | 20 | 20 | ok | 0 | ok | ok | ok | breach | 20 | ok | 0 | ok | ok | ok | breach | SCADSNV_Z5_SCADSNV | 0 | 1830 | -303.5 | 1 | 5060.5 | 0 |  |  | 1910 | 330 | -5268.5 | 1 | 2322 | 0
| El Dorado and Mountain Pass 230 kV | 250 | 0 | 250 |  | 1400 |  |  |  | 76 |  | 2400 | 2640 | 4040 | Kramer_Inyokern_Ex_Solar | KramerInyoOutsideTxConstraintZones | Ex Zones | 0 | 0 | ok | 0 | ok | ok | ok | ok | 0 | breach | 0 | ok | breach | ok | breach | SCADSNV_Z1_EldoradoAndMtnPass | 248 | 0 | 2 | 0 | 3792 | 0 |  |  | 248 | 0 | 2 | 0 | 3792 | 0
| Southern NV (GLW-VEA) | 700 | 76 | 624 |  | 1400 |  |  |  | 150 |  | 700 | 770 | 2170 | Kramer_Inyokern_Ex_Wind | KramerInyoOutsideTxConstraintZones | Ex Zones | 0 | 0 | ok | 0 | ok | ok | ok | ok | 0 | breach | 0 | ok | breach | ok | breach | SCADSNV_Z2_GLW_VEA | 442 | 0 | 182 | 0 | 1652 | 0 |  |  | 624 | 0 | 0 | 0 | 1470 | 0
| Greater Imperial* | 1200 | 105 | 1095 |  | 1400 |  |  |  | 2334 |  | 3100 | 3100 | 3100 | Mountain_Pass_El_Dorado_Solar | SCADSNV_Z1_EldoradoAndMtnPass | Southern CA Desert and Southern NV | 248 | 248 | ok | 0 | ok | ok | ok | breach | 248 | ok | 0 | ok | ok | ok | breach | SCADSNV_Z3_GreaterImperial | 495 | 548 | 600 | 0 | 1952 | 0 |  |  | 1095 | 548 | 0 | 0 | 1352 | 0
| Riverside East & Palm Springs | 2950 | 545.5 | 2404.5 |  | 1500 |  |  |  | 2156 |  | 5500 | 6050 | 6050 | North_Victor_Solar | GK_Z3_NorthOfVictor | Greater Kramer (North of Lugo) | 300 | 300 | ok | 0 | ok | ok | ok | ok | 300 | ok | 0 | ok | ok | ok | ok | SCADSNV_Z4_RiversideAndPalmSprings | 1392 | 2518 | 1012.5 | 0 | 1594.5 | 0 |  |  | 3665 | 2518 | -1260.5 | 1 | -678.5 | 1
| Ex Zones | [13 empty] | Northern_California_Ex_Solar | NorCalOutsideTxConstraintZones | Ex Zones | 397 | 397 | ok | 0 | ok | ok | ok | ok | 0 | ok | 0 | ok | ok | ok | breach | Ex Zones |  |  | 469 |  |  |  | 0 | 0 |  |  | -171 | 1 | 0 | 0 | 1 | 0
| GreaterImpOutsideTxConstraintZones | 0 | 0 | 0 | [10 empty] | Northern_California_Ex_Wind | Norcal_Z3_SacramentoRiver | Northern CA | 767 | 767 | ok | 0 | ok | ok | breach | ok | 767 | ok | 0 | ok | ok | ok | ok | GreaterImpOutsideTxConstraintZones | 0 | 0 | 0 | 0 |  | 0 |  |  | 1060 | 0 | -1060 | 1 |  | 0
| KramerInyoOutsideTxConstraintZones | 0 | 162 | 0 | [10 empty] | NW_Ext_Tx_Wind | Norcal_Z3_SacramentoRiver | Northern CA | 1500 | 530 | ok | 970 | ok | ok | breach | ok | 530 | ok | 970 | ok | ok | ok | ok | KramerInyoOutsideTxConstraintZones | 0 | 0 | 0 | 0 |  | 0 |  |  | 101 | 0 | -101 | 1 |  | 0
| NorCalOutsideTxConstraintZones | 866 | 0 | 866 | [10 empty] | Riverside_Palm_Springs_Solar | SCADSNV_Z4_RiversideAndPalmSprings | Southern CA Desert and Southern NV | 0 | 0 | ok | 0 | ok | ok | ok | breach | 0 | breach | 0 | breach | breach | ok | breach | NorCalOutsideTxConstraintZones | 397 | 0 | 469 | 0 |  | 0 |  |  | 309 | 0 | 557 | 0 |  | 0
| TehachapiOutsideTxConstraintZones | 0 | 0 | 0 | [10 empty] | Riverside_Palm_Springs_Wind | SCADSNV_Z4_RiversideAndPalmSprings | Southern CA Desert and Southern NV | 0 | 0 | ok | 0 | ok | ok | ok | breach | 0 | breach | 0 | breach | breach | ok | breach | TehachapiOutsideTxConstraintZones | 0 | 0 | 0 | 0 |  | 0 |  |  | 2208 | 0 | -2208 | 1 |  | 0
| WestlandsOutsideTxConstraintZones | 1779 | 0 | 1779 | [10 empty] | Sacramento_River_Solar | Norcal_Z3_SacramentoRiver | Northern CA | 896 | 0 | ok | 896 | ok | ok | breach | ok | 0 | ok | 231 | ok | ok | ok | ok | WestlandsOutsideTxConstraintZones | 1779 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 1779 | 0 |  | 0
| SCADOutsideTxConstraintZones | 862 | 0 | 862 | [10 empty] | Sacramento_River_Wind | Norcal_Z3_SacramentoRiver | Northern CA | 0 | 0 | ok | 0 | ok | ok | breach | ok | 0 | ok | 0 | ok | ok | ok | ok | SCADOutsideTxConstraintZones | 862 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 862 | 0 |  | 0
[15 empty] | SCADSNV_Solar | SCADSNV_Z5_SCADSNV | Southern CA Desert and Southern NV | 330 | 0 | breach | 330 | ok | breach | ok | breach | 410 | breach | 330 | ok | breach | ok | breach | Total | 12911.32 | 8966 | [6 empty] | 20864.82 | 7466
[15 empty] | SCADSNV_Wind | SCADSNV_Z5_SCADSNV | Southern CA Desert and Southern NV | 0 | 0 | breach | 0 | ok | breach | ok | breach | 0 | breach | 0 | ok | breach | ok | breach
[15 empty] | Solano_Solar | Norcal_Z4_Solano | Northern CA | 622 | 0 | ok | 622 | ok | ok | breach | ok | 0 | ok | 622 | ok | ok | ok | ok
[15 empty] | Solano_subzone_Solar | Norcal_Z4_Solano_subzone | Northern CA | 0 | 0 | ok | 0 | ok | ok | breach | ok | 0 | ok | 0 | ok | ok | ok | ok |  |  |  |  | 1 |  | 1
[15 empty] | Solano_subzone_Wind | Norcal_Z4_Solano_subzone | Northern CA | 0 | 0 | ok | 0 | ok | ok | breach | ok | 0 | ok | 0 | ok | ok | ok | ok
[15 empty] | Solano_Wind | Norcal_Z4_Solano | Northern CA | 462 | 462 | ok | 0 | ok | ok | breach | ok | 462 | ok | 0 | ok | ok | ok | ok
[15 empty] | Southern_California_Desert_Ex_Solar | SCADOutsideTxConstraintZones | Ex Zones | 862 | 862 | ok | 0 | ok | ok | ok | ok | 0 | ok | 0 | ok | ok | ok | breach
[15 empty] | Southern_California_Desert_Ex_Wind | SCADOutsideTxConstraintZones | Ex Zones | 0 | 0 | ok | 0 | ok | ok | ok | ok | 0 | ok | 0 | ok | ok | ok | breach
[15 empty] | Southern_Nevada_Solar | SCADSNV_Z2_GLW_VEA | Southern CA Desert and Southern NV | 0 | 0 | ok | 0 | ok | ok | ok | breach | 182 | ok | 0 | ok | ok | ok | breach
[15 empty] | Southern_Nevada_Wind | SCADSNV_Z2_GLW_VEA | Southern CA Desert and Southern NV | 442 | 442 | ok | 0 | ok | ok | ok | breach | 442 | ok | 0 | ok | ok | ok | breach
[15 empty] | SW_Ext_Tx_Wind | SCADSNV_Z4_RiversideAndPalmSprings | Southern CA Desert and Southern NV | 500 | 0 | ok | 500 | ok | ok | ok | breach | 0 | breach | 500 | breach | breach | ok | breach
[15 empty] | Tehachapi_Solar | Tehachapi | Tehachapi | 4656 | 3856 | ok | 800 | ok | ok | ok | ok | 4876 | breach | 800 | ok | breach | ok | breach
[15 empty] | Tehachapi_Ex_Solar | TehachapiOutsideTxConstraintZones | Ex Zones | 0 | 0 | ok | 0 | ok | ok | ok | ok | 0 | breach | 0 | ok | breach | ok | breach
[15 empty] | Tehachapi_Wind | Tehachapi | Tehachapi | 275 | 275 | ok | 0 | ok | ok | ok | ok | 275 | breach | 0 | ok | breach | ok | breach
[15 empty] | Westlands_Ex_Solar | WestlandsOutsideTxConstraintZones | Ex Zones | 1779 | 1779 | ok | 0 | ok | ok | ok | ok | 0 | ok | 0 | ok | ok | ok | breach
[15 empty] | Westlands_Ex_Wind | WestlandsOutsideTxConstraintZones | Ex Zones | 0 | 0 | ok | 0 | ok | ok | ok | ok | 0 | ok | 0 | ok | ok | ok | breach
[15 empty] | Westlands_Solar | SPGE_Z4_CentralValleyAndLosBanos | Southern PG&E | 468 | 468 | ok | 0 | ok | ok | ok | breach | 1423 | breach | 665 | breach | breach | ok | breach
[15 empty] | Cape_Mendocino_Offshore_Wind | N/A |  | #N/A | 0 | #N/A | 0 |  | #N/A | #N/A | #N/A | 0 |  | 0 |  | breach | #N/A | #N/A
[15 empty] | Del_Norte_Offshore_Wind | N/A |  | #N/A | 0 | #N/A | 0 |  | #N/A | #N/A | #N/A | 0 |  | 0 |  | breach | #N/A | #N/A
[15 empty] | Diablo_Canyon_Offshore_Wind_Ext_Tx | N/A |  | #N/A | 0 | #N/A | 0 |  | #N/A | #N/A | #N/A | 0 |  | 0 |  | breach | #N/A | #N/A
[15 empty] | Diablo_Canyon_Offshore_Wind | N/A |  | #N/A | 0 | #N/A | 0 |  | #N/A | #N/A | #N/A | 0 |  | 0 |  | breach | #N/A | #N/A
[15 empty] | Humboldt_Bay_Offshore_Wind | Norcal_Z2_Humboldt | Northern CA | 0 | 0 | ok | 0 | ok | ok | breach | ok | 0 | ok | 0 | ok | ok | ok | ok
[15 empty] | Morro_Bay_Offshore_Wind | N/A |  | #N/A | 0 | #N/A | 0 |  | #N/A | #N/A | #N/A | 0 |  | 0 |  | breach | #N/A | #N/A
[15 empty] | Utah_Solar | N/A |  | #N/A | 0 | #N/A | 0 |  | #N/A | #N/A | #N/A | 0 |  | 0 |  | breach | #N/A | #N/A
[15 empty] | Arizona_Solar | SCADSNV_Z4_RiversideAndPalmSprings | Southern CA Desert and Southern NV | 1910 | 447 | ok | 1463 | ok | ok | ok | breach | 117 | breach | 1463 | breach | breach | ok | breach
[15 empty] | New_Mexico_Solar | N/A |  | #N/A | 0 | #N/A | 0 |  | #N/A | #N/A | #N/A | 0 |  | 0 |  | breach | #N/A | #N/A
[15 empty] | Baja_California_Solar | N/A |  | #N/A | 0 | #N/A | 0 |  | #N/A | #N/A | #N/A | 0 |  | 0 |  | breach | #N/A | #N/A
[15 empty] | Baja_California_Wind | SCADSNV_Z3_GreaterImperial | Southern CA Desert and Southern NV | 495 | 495 | ok | 0 | ok | ok | ok | breach | 495 | ok | 0 | ok | ok | ok | breach
[15 empty] | Pacific_Northwest_Wind | N/A |  | #N/A | 0 | #N/A | 0 |  | #N/A | #N/A | #N/A | 0 |  | 0 |  | breach | #N/A | #N/A
[15 empty] | Idaho_Wind | N/A |  | #N/A | 0 | #N/A | 0 |  | #N/A | #N/A | #N/A | 0 |  | 0 |  | breach | #N/A | #N/A
[15 empty] | Utah_Wind | N/A |  | #N/A | 0 | #N/A | 0 |  | #N/A | #N/A | #N/A | 0 |  | 0 |  | breach | #N/A | #N/A
[15 empty] | Wyoming_Wind | SCADSNV_Z5_SCADSNV | Southern CA Desert and Southern NV | 1500 | 0 | breach | 1500 | ok | breach | ok | breach | 1500 | breach | 0 | ok | breach | ok | breach
[15 empty] | Arizona_Wind | N/A |  | #N/A | 0 | #N/A | 0 |  | #N/A | #N/A | #N/A | 0 |  | 0 |  | breach | #N/A | #N/A
[15 empty] | New_Mexico_Wind | SCADSNV_Z4_RiversideAndPalmSprings | Southern CA Desert and Southern NV | 1500 | 945 | ok | 555 | ok | ok | ok | breach | 945 | breach | 555 | breach | breach | ok | breach
[15 empty] | Pisgah_Solar | GK_Z4_Pisgah | Greater Kramer (North of Lugo) |  |  | ok |  | ok | ok | ok | ok | 200.5 | ok | 0 | ok | ok | ok | ok
[15 empty] | Pumped Storage Hydro_GreaterImpOutsideTxConstraintZones | GreaterImpOutsideTxConstraintZones | Ex Zones | 0 | 0 | ok | 0 | ok | ok | ok | ok | 500 | breach | 0 | ok | breach | ok | breach
[15 empty] | Pumped Storage Hydro_SCADSNV_Z4_RiversideAndPalmSprings | SCADSNV_Z4_RiversideAndPalmSprings | Southern CA Desert and Southern NV | 0 | 0 | ok | 0 | ok | ok | ok | breach | 1343 | breach | 0 | breach | breach | ok | breach
[15 empty] | BatteryStorage_GK_Z2_InyokernAndNorthOfKramer | GK_Z2_InyokernAndNorthOfKramer | Greater Kramer (North of Lugo) |  |  | ok | 0 | ok | ok |  | ok | 0 | ok | 0 | ok | ok |  | ok
[15 empty] | BatteryStorage_GK_Z3_NorthOfVictor | GK_Z3_NorthOfVictor | Greater Kramer (North of Lugo) |  |  | ok | 0 | ok | ok |  | ok | 0 | ok | 0 | ok | ok |  | ok
[15 empty] | BatteryStorage_GK_Z4_Pisgah | GK_Z4_Pisgah | Greater Kramer (North of Lugo) |  |  | ok | 0 | ok | ok |  | ok | 0 | ok | 0 | ok | ok |  | ok
[15 empty] | BatteryStorage_GreaterImpOutsideTxConstraintZones | GreaterImpOutsideTxConstraintZones | Ex Zones |  |  | ok | 0 | ok | ok |  | ok | 560 | breach | 0 | ok | breach |  | breach
[15 empty] | BatteryStorage_KramerInyoOutsideTxConstraintZones | KramerInyoOutsideTxConstraintZones | Ex Zones |  |  | ok | 0 | ok | ok |  | ok | 101 | breach | 0 | ok | breach |  | breach
[15 empty] | BatteryStorage_Norcal_Z2_Humboldt | Norcal_Z2_Humboldt | Northern CA |  |  | ok | 0 | ok | ok |  | ok | 0 | ok | 0 | ok | ok |  | ok
[15 empty] | BatteryStorage_Norcal_Z3_SacramentoRiver | Norcal_Z3_SacramentoRiver | Northern CA |  |  | ok | 0 | ok | ok |  | ok | 0 | ok | 0 | ok | ok |  | ok
[15 empty] | BatteryStorage_Norcal_Z4_Solano | Norcal_Z4_Solano | Northern CA |  |  | ok | 0 | ok | ok |  | ok | 0 | ok | 0 | ok | ok |  | ok
[15 empty] | BatteryStorage_Norcal_Z4_Solano_subzone | Norcal_Z4_Solano_subzone | Northern CA |  |  | ok | 0 | ok | ok |  | ok | 0 | ok | 0 | ok | ok |  | ok
[15 empty] | BatteryStorage_NorCalOutsideTxConstraintZones | NorCalOutsideTxConstraintZones | Ex Zones |  |  | ok | 0 | ok | ok |  | ok | 309 | ok | 0 | ok | ok |  | breach
[15 empty] | BatteryStorage_SCADOutsideTxConstraintZones | SCADOutsideTxConstraintZones | Ex Zones |  |  | ok | 0 | ok | ok |  | ok | 0 | ok | 0 | ok | ok |  | breach
[15 empty] | BatteryStorage_SCADSNV_Z2_GLW_VEA | SCADSNV_Z2_GLW_VEA | Southern CA Desert and Southern NV |  |  | ok | 0 | ok | ok |  | breach | 0 | ok | 0 | ok | ok |  | breach
[15 empty] | BatteryStorage_SCADSNV_Z3_GreaterImperial | SCADSNV_Z3_GreaterImperial | Southern CA Desert and Southern NV |  |  | ok | 0 | ok | ok |  | breach | 0 | ok | 0 | ok | ok |  | breach
[15 empty] | BatteryStorage_SCADSNV_Z4_RiversideAndPalmSprings | SCADSNV_Z4_RiversideAndPalmSprings | Southern CA Desert and Southern NV |  |  | ok | 0 | ok | ok |  | breach | 1260 | breach | 0 | breach | breach |  | breach
[15 empty] | BatteryStorage_SCADSNV_Z5_SCADSNV | SCADSNV_Z5_SCADSNV | Southern CA Desert and Southern NV |  |  | breach | 0 | ok | breach |  | breach | 0 | breach | 0 | ok | breach |  | breach
[15 empty] | BatteryStorage_SouthernPGE | SouthernPGE |  |  |  | #N/A | 0 |  | #N/A |  | #N/A | 0 |  | 0 |  | breach |  | #N/A
[15 empty] | BatteryStorage_SPGE_Z1_Westlands | SPGE_Z1_Westlands | Southern PG&E |  |  | ok | 0 | ok | ok |  | breach | 173 | breach | 0 | ok | breach |  | breach
[15 empty] | BatteryStorage_SPGE_Z2_KernAndGreaterCarrizo | SPGE_Z2_KernAndGreaterCarrizo | Southern PG&E |  |  | ok | 0 | ok | ok |  | breach | 0 | ok | 0 | ok | ok |  | breach
[15 empty] | BatteryStorage_SPGE_Z3_Carrizo | SPGE_Z3_Carrizo | Southern PG&E |  |  | ok | 0 | ok | ok |  | breach | 0 | ok | 0 | ok | ok |  | breach
[15 empty] | BatteryStorage_SPGE_Z4_CentralValleyAndLosBanos | SPGE_Z4_CentralValleyAndLosBanos | Southern PG&E |  |  | ok | 0 | ok | ok |  | breach | 0 | breach | 0 | breach | breach |  | breach
[15 empty] | BatteryStorage_Tehachapi | Tehachapi | Tehachapi |  |  | ok | 0 | ok | ok |  | ok | 0 | breach | 0 | ok | breach |  | breach
[15 empty] | BatteryStorage_TehachapiOutsideTxConstraintZones | TehachapiOutsideTxConstraintZones | Ex Zones |  |  | ok | 0 | ok | ok |  | ok | 2208 | breach | 0 | ok | breach |  | breach
[15 empty] | BatteryStorage_WestlandsOutsideTxConstraintZones | WestlandsOutsideTxConstraintZones | Ex Zones |  |  | ok | 0 | ok | ok |  | ok | 0 | ok | 0 | ok | ok |  | breach
#N/A

## 2_CheckTab
Analysis of compliance of Round 1 mapping with criterion 2 (transmission limits), to inform changes needed in Round 2 of mapping | [5 empty] | Adjusted Amounts
| Zone Name in RESOLVE | Selected Resource (FD MW) | Estimated FCDS Capacity (MW) Existing System | Remaining FCDS tx capacity (inner zone) | Remaining FCDS tx capacity (outer zone) | Selected Resource Adj (FD MW) | Remaining tx capability (FD MW) (inner zone) | Remaining tx capability (FD MW) (outer zone)
| Northern CA |  | 2000 |  | 184 |  |  | 184
| Norcal_Z2_Humboldt | 0 | 0 | 0 |  | 0 | 0
| Norcal_Z3_SacramentoRiver | 1297 | 2000 | 703 |  | 1297 | 703
| Norcal_Z4_Solano | 519 | 600 | 81 |  | 519 | 81
| Norcal_Z4_Solano_subzone | 0 | 0 | 0 |  | 0 | 0
| Southern PG&E | 0 | 1100 |  | 50.68 |  |  | -1077.32
| SPGE_Z1_Westlands | 0 | 0 | 0 |  | 173 | -173
| SPGE_Z2_KernAndGreaterCarrizo | 121.32 | 1000 | 878.68 |  | 121.32 | 878.68
| SPGE_Z3_Carrizo | 287 | 400 | 113 |  | 287 | 113
| SPGE_Z4_CentralValleyAndLosBanos | 641 | 1000 | 359 |  | 1596 | -596
| Tehachapi | 4131 | 4300 |  | 169 | 5151 |  | -851
| Greater Kramer (North of Lugo) | 0 | 600 |  | 300 |  |  | 99.5
| GK_Z1_GreaterKramer | 0 | 600 | 600 |  | 0 | 600
| GK_Z3_NorthOfVictor | 300 | 300 | 0 |  | 300 | 0
| GK_Z2_InyokernAndNorthOfKramer | 0 | 100 | 100 |  | 0 | 100
| GK_Z4_Pisgah | 0 | 400 | 400 |  | 200.5 | 199.5
| Southern CA Desert and Southern NV | 0 | 3000 |  | 423 |  |  | -4542
| SCADSNV_Z5_SCADSNV | 0 | 3000 |  |  | 1910
| SCADSNV_Z1_EldoradoAndMtnPass | 248 | 250 | 2 |  | 248 | 2
| SCADSNV_Z2_GLW_VEA | 442 | 700 | 258 |  | 624 | 76
| SCADSNV_Z3_GreaterImperial | 495 | 1200 | 705 |  | 1095 | 105
| SCADSNV_Z4_RiversideAndPalmSprings | 1392 | 2950 | 1558 |  | 3665 | -715
| Ex Zones |  | 3507 |  | 469 | 0 |  | -171
| GreaterImpOutsideTxConstraintZones | 0 | 0 | 0 |  | 1060 | -1060
| KramerInyoOutsideTxConstraintZones | 0 | 0 | 0 |  | 101 | -101
| NorCalOutsideTxConstraintZones | 397 | 866 | 469 |  | 309 | 557
| TehachapiOutsideTxConstraintZones | 0 | 0 | 0 |  | 2208 | -2208
| WestlandsOutsideTxConstraintZones | 1779 | 1779 | 0 |  | 0 | 1779
| SCADOutsideTxConstraintZones | 862 | 862 | 0 |  | 0 | 862
| Total | 12911.32 | 0

## 2_BatteryStorageSumByZone
Substation Name | Tx Deliv. Zone | Battery Mapping - Stand-alone LCR + System (MW) | Battery Mapping - Stand-alone System Only (MW) | Battery Mapping - Co-located (MW) | Total Battery Mapping Without Tx Upgrades | Battery Mapping Stand Alone Triggering Tx Upgrade (MW) | Total Battery Mapping (MW) | Tx Deliv. Zone | Sum of Total Battery Mapping (MW) | Sum of Battery Mapping - Co-located (MW)
ANTELOPE | Tehachapi | - | - | 575 | 575 |  | 575 | GK_Z2_InyokernAndNorthOfKramer | 0 | 0
CORCORAN | SPGE_Z1_Westlands | - | - | - | - |  | - | GK_Z3_NorthOfVictor | 50 | 50
HENRIETTA | SPGE_Z1_Westlands | - | - | - | - |  | - | GK_Z4_Pisgah | 126 | 126
WEBER | SPGE_Z4_CentralValleyAndLosBanos | - | - | - | - |  | - | GreaterImpOutsideTxConstraintZones | 560 | 0
SCHINDLER | SPGE_Z1_Westlands | - | - | - | - |  | - | KramerInyoOutsideTxConstraintZones | 101 | 0
PANOCHE | SPGE_Z1_Westlands | - | - | 52 | 52 |  | 52 | Norcal_Z2_Humboldt | 0 | 0
WHEELER RIDGE | SPGE_Z2_KernAndGreaterCarrizo | - | - | 16 | 16 |  | 16 | Norcal_Z3_SacramentoRiver | 0 | 0
MIDWAY 500KV | SPGE_Z2_KernAndGreaterCarrizo | - | - | - | - |  | - | Norcal_Z4_Solano | 0 | 0
ARCO | SPGE_Z2_KernAndGreaterCarrizo | - | - | 19 | 19 |  | 19 | Norcal_Z4_Solano_subzone | 0 | 0
MIDWAY 230KV | SPGE_Z2_KernAndGreaterCarrizo | - | - | 18 | 18 |  | 18 | NorCalOutsideTxConstraintZones | 309 | 0
MCCALL | SPGE_Z4_CentralValleyAndLosBanos | - | - | - | - |  | - | SCADOutsideTxConstraintZones | 0 | 0
MCMULLIN | SPGE_Z4_CentralValleyAndLosBanos | - | - | - | - |  | - | SCADSNV_Z2_GLW_VEA | 100 | 100
HELM | SPGE_Z4_CentralValleyAndLosBanos | - | - | - | - |  | - | SCADSNV_Z3_GreaterImperial | 53 | 53
RIPON | SPGE_Z4_CentralValleyAndLosBanos | - | - | - | - |  | - | SCADSNV_Z4_RiversideAndPalmSprings | 1313 | 53
LOS BANOS 230KV | SPGE_Z4_CentralValleyAndLosBanos | - | - | - | - |  | - | SCADSNV_Z5_SCADSNV | 629 | 629
BOULEVARD | SCADSNV_Z3_GreaterImperial | - | - | - | - |  | - | SouthernPGE | 0 | 0
ROADWAY | GK_Z3_NorthOfVictor | - | - | - | - |  | - | SPGE_Z1_Westlands | 825 | 652
CONTRA COSTA | Norcal_Z4_Solano | - | - | - | - |  | - | SPGE_Z2_KernAndGreaterCarrizo | 53 | 53
WOODLAND | Norcal_Z3_SacramentoRiver | - | - | - | - |  | - | SPGE_Z3_Carrizo | 0 | 0
BIRDS LANDING | Norcal_Z4_Solano | - | - | - | - |  | - | SPGE_Z4_CentralValleyAndLosBanos | 0 | 0
CHRISTIE | Norcal_Z4_Solano_subzone | - | - | - | - |  | - | Tehachapi | 3121 | 3121
CAYETANO | Norcal_Z4_Solano | - | - | - | - |  | - | TehachapiOutsideTxConstraintZones | 2208 | 0
GRANT | Norcal_Z4_Solano_subzone | - | - | - | - |  | - | WestlandsOutsideTxConstraintZones | 0 | 0
EAST COUNTY | SCADSNV_Z3_GreaterImperial | - | - | - | - |  | - | Grand Total | 9448 | 4837
PISGAH | GK_Z4_Pisgah | - | - | - | - |  | -
COOLWATER | GK_Z3_NorthOfVictor | - | - | - | - |  | -
GATES 230KV | SPGE_Z1_Westlands | - | - | 51 | 51 |  | 51
FULTON | Norcal_Z4_Solano | - | - | - | - |  | -
THERMALITO | Norcal_Z3_SacramentoRiver | - | - | - | - |  | -
DESERT VIEW | SCADSNV_Z5_SCADSNV | - | - | - | - |  | -
CALDWELL | SCADSNV_Z5_SCADSNV | - | - | - | - |  | -
RENFRO | SPGE_Z2_KernAndGreaterCarrizo | - | - | - | - |  | -
DELANEY | SCADSNV_Z4_RiversideAndPalmSprings | - | - | 53 | 53 | 420 | 473
VINCENT | Tehachapi | - | - | 743 | 743 |  | 743
PALO VERDE | SCADSNV_Z4_RiversideAndPalmSprings | - | - | - | - |  | -
PEARBLOSSOM | Tehachapi | - | - | - | - |  | -
WINDHUB | Tehachapi | - | - | 855 | 855 |  | 855
MOSS LANDING | SPGE_Z3_Carrizo | - | - | - | - |  | -
WHIRLWIND | Tehachapi | - | - | 948 | 948 |  | 948
HIGHWIND | Tehachapi | - | - | - | - |  | -
COLORADO POWERSTATION | SCADSNV_Z4_RiversideAndPalmSprings | - | - | - | - |  | -
SHILO I | Norcal_Z4_Solano | - | - | - | - |  | -
MILLER | SPGE_Z4_CentralValleyAndLosBanos | - | - | - | - |  | -
LAKEVILLE | Norcal_Z4_Solano | - | - | - | - |  | -
RIO OSO | Norcal_Z3_SacramentoRiver | - | - | - | - |  | -
MILLER | SPGE_Z4_CentralValleyAndLosBanos | - | - | - | - |  | -
IMPERIAL VALLEY | SCADSNV_Z3_GreaterImperial | - | - | - | - |  | -
GATES 500KV | SPGE_Z1_Westlands | - | - | 549 | 549 | 173 | 722
VICTOR | GK_Z3_NorthOfVictor | - | - | 50 | 50 |  | 50
LONE TREE | Norcal_Z4_Solano | - | - | - | - |  | -
HASSAYAMPA | SCADSNV_Z3_GreaterImperial | - | - | 53 | 53 |  | 53
VACA-DIXON | Norcal_Z4_Solano | - | - | - | - |  | -
TULUCAY | Norcal_Z4_Solano | - | - | - | - |  | -
KRAMER | GK_Z2_InyokernAndNorthOfKramer | - | - | - | - |  | -
VALLEY | SCADSNV_Z3_GreaterImperial | - | - | - | - |  | -
MOHAVE 500KV | SCADSNV_Z5_SCADSNV | - | - | 369 | 369 |  | 369
VALLEY | SCADSNV_Z3_GreaterImperial | - | - | - | - |  | -
CALCITE | GK_Z4_Pisgah | - | - | 126 | 126 |  | 126
INNOVATION | SCADSNV_Z5_SCADSNV | - | - | 36 | 36 |  | 36
ELDORADO 230KV | SCADSNV_Z5_SCADSNV | - | - | 75 | 75 |  | 75
ELDORADO 500KV | SCADSNV_Z5_SCADSNV | - | - | 149 | 149 |  | 149
GAMEBIRD | SCADSNV_Z5_SCADSNV | - | - | - | - |  | -
OCOTILLO | SCADSNV_Z3_GreaterImperial | - | - | - | - |  | -
RED BLUFF | SCADSNV_Z4_RiversideAndPalmSprings | - | - | - | - | 420 | 420
COLORADO RIVER | SCADSNV_Z4_RiversideAndPalmSprings | - | - | - | - | 420 | 420
MORRO BAY | SPGE_Z3_Carrizo | - | - | - | - |  | -
CHOLAME | SPGE_Z2_KernAndGreaterCarrizo | - | - | - | - |  | -
CRAZY EYES | SCADSNV_Z2_GLW_VEA | - | - | 100 | 100 |  | 100
CORTINA | Norcal_Z4_Solano | - | - | - | - |  | -
INYOKERN | GK_Z2_InyokernAndNorthOfKramer | - | - | - | - |  | -
GLENN | Norcal_Z3_SacramentoRiver | - | - | - | - |  | -
BRIDGEVILLE | Norcal_Z2_Humboldt | - | - | - | - |  | -
ROUND MOUNTAIN | Norcal_Z3_SacramentoRiver | - | - | - | - |  | -
DELEVAN | Norcal_Z3_SacramentoRiver | - | - | - | - |  | -
TEMPLETON | SouthernPGE | - | - | - | - |  | -
HOODOO | SCADSNV_Z3_GreaterImperial | - | - | - | - |  | -
STOCKDALE | SPGE_Z2_KernAndGreaterCarrizo | - | - | - | - |  | -
COOLEY LANDING | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
HUNT-WESSON | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
GOLD HILL | NorCalOutsideTxConstraintZones | - | 59 | - | 59 |  | 59
STATION D | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
MARTIN | NorCalOutsideTxConstraintZones | 250 | - | - | 250 |  | 250
STATION A | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
WIRE-48TH | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
POWER INN-ELDER CREEK | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
UNITED COGEN TAP | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
MARTIN LUTHER KING | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
JAMESTOWN | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
HEDGE | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
EAST GRANDE | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
SAN FRANCISCO AIRPORT | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
SHAW ROAD | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
POWER INN | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
NORTH CITY | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
SOUTH CITY | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
POCKET | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
UNITED COGEN INC | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
BAY MEADOWS | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
SAN MATEO | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
ELK GROVE | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
S.L.A.C. | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
CIMA | SCADOutsideTxConstraintZones | - | - | - | - |  | -
BAKER | SCADOutsideTxConstraintZones | - | - | - | - |  | -
COSUMNES | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
CANYONLANDS | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
DALY CITY | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
FOLSOM | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
CARMICHAEL | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
SHREDDER TAP | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
S.L.A.C. TAP | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
SAN CARLOS | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
MOUNTAIN PASS | SCADOutsideTxConstraintZones | - | - | - | - |  | -
HI DESERT | SCADOutsideTxConstraintZones | - | - | - | - |  | -
NIMBUS | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
RMC LONESTAR | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
JEFFERSON | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
MILLBRAE | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
HURLEY | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
TAP305164 | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
TAP305465 | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
BURLINGAME | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
CARODEAN | SCADOutsideTxConstraintZones | - | - | - | - |  | -
MID CITY | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
SACRAMENTO | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
LAWNDALE | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
SAN MATEO | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
LAKE | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
BAIR | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
JEFFERSON | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
MA | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
BELMONT | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
SANTA PAULA | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
RANCHO SECO | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
GRAND ISLAND | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
SHREDDER | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
LAKE FOREST | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
LEATHERNECK | SCADOutsideTxConstraintZones | - | - | - | - |  | -
SERRAMONTE | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
REDWOOD CITY | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
ORANGEVALE | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
CAVITT | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
STATION B | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
EAST CITY | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
IVANPAH | SCADOutsideTxConstraintZones | - | - | - | - |  | -
TWENTY NINE PALMS | SCADOutsideTxConstraintZones | - | - | - | - |  | -
DALY CITY TAP | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
DAVIS CREEK | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
FOOTHILL | WestlandsOutsideTxConstraintZones | - | - | - | - |  | -
FOOTHILL | WestlandsOutsideTxConstraintZones | - | - | - | - |  | -
SURF | WestlandsOutsideTxConstraintZones | - | - | - | - |  | -
LEAVITT | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
PRUNEDALE | WestlandsOutsideTxConstraintZones | - | - | - | - |  | -
SALINAS | WestlandsOutsideTxConstraintZones | - | - | - | - |  | -
FORT ORD | WestlandsOutsideTxConstraintZones | - | - | - | - |  | -
LEAVITT | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
MANVILLE | WestlandsOutsideTxConstraintZones | - | - | - | - |  | -
ORACLE | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
DEL MONTE | WestlandsOutsideTxConstraintZones | - | - | - | - |  | -
BO RONDA | WestlandsOutsideTxConstraintZones | - | - | - | - |  | -
CALPELLA | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
OCEANO | WestlandsOutsideTxConstraintZones | - | - | - | - |  | -
HILLTOP | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
SOLEDAD | WestlandsOutsideTxConstraintZones | - | - | - | - |  | -
GOLETA | WestlandsOutsideTxConstraintZones | - | - | - | - |  | -
HILLTOP TAP | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
MANZANITA | WestlandsOutsideTxConstraintZones | - | - | - | - |  | -
WARNER | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
ALTRUS | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
LOGAN CREEK | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
DIABLO CANYON | WestlandsOutsideTxConstraintZones | - | - | - | - |  | -
UKIAH | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
COBURN | WestlandsOutsideTxConstraintZones | - | - | - | - |  | -
HILLTOP | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
CALLENDER | WestlandsOutsideTxConstraintZones | - | - | - | - |  | -
CANBY 1 | NorCalOutsideTxConstraintZones | - | - | - | - |  | -
PECHO VALLEY | WestlandsOutsideTxConstraintZones | - | - | - | - |  | -
UNION OIL | WestlandsOutsideTxConstraintZones | - | - | - | - |  | -
CASTROVILLE | WestlandsOutsideTxConstraintZones | - | - | - | - |  | -
WALNUT | TehachapiOutsideTxConstraintZones | 200 | - | - | 200 |  | 200
HINSON | TehachapiOutsideTxConstraintZones | 200 | - | - | 200 |  | 200
ETIWANDA | KramerInyoOutsideTxConstraintZones | 101 | - | - | 101 |  | 101
RIO HONDO | TehachapiOutsideTxConstraintZones | 569 | 39 | - | 608 |  | 608
LAGUNA BELL | TehachapiOutsideTxConstraintZones | - | 500 | - | 500 |  | 500
WALNUT | TehachapiOutsideTxConstraintZones | - | 200 | - | 200 |  | 200
SILVERGATE | GreaterImpOutsideTxConstraintZones | 200 | - | - | 200 |  | 200
MOORPARK | TehachapiOutsideTxConstraintZones | 128 | 372 | - | 500 |  | 500
ESCONDIDO | GreaterImpOutsideTxConstraintZones | 50 | - | - | 50 |  | 50
SYCAMORE CANYON | GreaterImpOutsideTxConstraintZones | 300 | - | - | 300 |  | 300
KEARNY | GreaterImpOutsideTxConstraintZones | 10 | - | - | 10 |  | 10

## NestedTxZoneList
Outer Zone | Inner Zone
Northern CA | Norcal_Z2_Humboldt
Northern CA | Norcal_Z3_SacramentoRiver
Northern CA | Norcal_Z4_Solano
Northern CA | Norcal_Z4_Solano_subzone
Southern PG&E | SPGE_Z1_Westlands
Southern PG&E | SPGE_Z2_KernAndGreaterCarrizo
Southern PG&E | SPGE_Z3_Carrizo
Southern PG&E | SPGE_Z4_CentralValleyAndLosBanos
Tehachapi | Tehachapi
Greater Kramer (North of Lugo) | GK_Z1_GreaterKramer
Greater Kramer (North of Lugo) | GK_Z3_NorthOfVictor
Greater Kramer (North of Lugo) | GK_Z2_InyokernAndNorthOfKramer
Greater Kramer (North of Lugo) | GK_Z4_Pisgah
Southern CA Desert and Southern NV | SCADSNV_Z5_SCADSNV
Southern CA Desert and Southern NV | SCADSNV_Z1_EldoradoAndMtnPass
Southern CA Desert and Southern NV | SCADSNV_Z2_GLW_VEA
Southern CA Desert and Southern NV | SCADSNV_Z3_GreaterImperial
Southern CA Desert and Southern NV | SCADSNV_Z4_RiversideAndPalmSprings
Ex Zones | GreaterImpOutsideTxConstraintZones
Ex Zones | KramerInyoOutsideTxConstraintZones
Ex Zones | NorCalOutsideTxConstraintZones
Ex Zones | TehachapiOutsideTxConstraintZones
Ex Zones | WestlandsOutsideTxConstraintZones
Ex Zones | SCADOutsideTxConstraintZones

## 3_SUM OF SOLAR RESOURCE ACRES
Source: IRP 2021 Solar Allocation and ECO Value_v.4_SUMMARIES.xlsx
3a. What constitutes level 3 flag? |  | 100% | Exceeds 100% of candidate project area land within the standard radius
3a. What constitutes level 2 flag? |  | 75% | Exceeds 75% of candidate project area land within the standard radius
3a. What constitutes level 1 flag? |  | All other
3b. What constitutes level 3 flag? |  | 75% | More than 75% of the candidate project area occurs on four or more of the sensitive area types
4
3b. What constitutes level 2 flag? |  | 20% | Exceeds 20% of the low-environmental-implication land area within the standard radius
4
3b. What constitutes level 1 flag? |  | All other
[6 empty] | SELECTED | [12 empty] | SUMMARY |  |  |  | INTACTNESS | NLB | CONNECTIVITY | BIO | RARE | NATIVE | IRREPLACIBILITY | 3b. Level 3 Non-compliance Flag | [7 empty] | 3b. Level 2 | 3a. Non-compliance Flag |  | Source data for main dashboard tab Criteria 3.b. and 3.a.
| Tx Zone/Substation | ACRES_15_LOW | ACRES_15_HIGH | TOTAL ACRES_15 | Filter flag | Tx Zone/Substation | ACRES_15_LOW | ACRES_15_HIGH | TOTAL ACRES_15 | Porportion of Total Acres | Potential MW | Potential MW Low | Potential MW High | MW Allocation | Percent Total ACRES | Percent ACRES Low | RESOLVE MW | RESOLVE Resource | SUBSTATION | 4 | 5 | Total Acres | % of Area | % of Area | % of Area | % of Area | % of Area | % of Area | % of Area | INTACTNESS | NLB | CONNECTIVITY | BIO | RARE | NATIVE | IRREPLACIBILITY | 3b. Level 3 | 3b. Level 2 | 3a Level 3 | 3a Level 2 | Row Labels | Sum of 3b. Level 3 | Sum of 3b. Level 2 | Sum of 3a Level 3 | Sum of 3a Level 2 | Criteria 3a | Criteria 3b
| GK_Z2_InyokernAndNorthOfKramer |  |  |  | 0 | [36 empty] | 0 | 0 | 0 | 0
| Kramer | 22292 | 108531 | 130823 | 0
| Randsburg | 32006 | 132828 | 164834 | 0 | [35 empty] | Greater_Imperial_Solar | 0 | 0 | 0 | 0 | 1 | 1
[5 empty] | 0 | [35 empty] | Kern_Greater_Carrizo_Solar | 0 | 0 | 0 | 0 | 1 | 1
| GK_Z3_NorthOfVictor |  |  |  | 1 | GK_Z3_NorthOfVictor | [34 empty] | North_Victor_Solar | 0 | 0 | 0 | 0 | 1 | 1
| Caldwell | 202590 | 157849 | 360439 | 1 | Caldwell | [10 empty] | 300 | [23 empty] | Northern_California_Ex_Solar | 0 | 0 | 0 | 0 | 1 | 1
| Cool Water | 37474 | 118138 | 155612 | 1 | Cool Water | 37474 | 118138 | 155612 | 0.28 | 22230 | 5353 | 16877 | 85 | 0.11% | 1.59% |  |  | Cool Water | 27109.5302 | 18042.6093 | 159843 | 28% | 8% | 16% | 74% | 58% | 94% | 11% | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | Sacramento_River_Solar | 0 | 0 | 0 | 0 | 1 | 1
| Victor | 226644 | 167494 | 394138 | 1 | Victor | 226644 | 167494 | 394138 | 0.72 | 56305 | 32378 | 23928 | 215 | 0.27% | 0.66% |  |  | Victor | 52753.358 | 19113.8778 | 428829 | 17% | 2% | 3% | 92% | 56% | 98% | 8% | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | Solano_Solar | 0 | 0 | 0 | 0 | 1 | 1
| GK_Z4_Pisgah |  |  |  | 1 | Total | 264117 | 285633 | 549750 |  | 78536 | 37731 | 40805 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tehachapi_Solar | 0 | 0 | 0 | 0 | 1 | 1
| Calcite | 263893 | 637139 | 901032 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Westlands_Ex_Solar | 0 | 0 | 0 | 0 | 1 | 1
| Lugo | 172374 | 130196 | 302570 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Westlands_Solar | 0 | 0 | 0 | 0 | 1 | 1
| Pisgah | 33413 | 60109 | 93523 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (blank) |  |  | 0 | 0 | 1 | 1
[5 empty] | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mountain_Pass_El_Dorado_Solar |  |  | 0 | 0 | 1 | 1
| GreaterImpOutsideTxConstraintZones |  |  |  | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Southern_Nevada_Solar |  |  | 0 | 0 | 1 | 1
| Batiquitos | 157633 | 47688 | 205321 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SCADSNV_Solar |  |  | 0 | 0 | 1 | 1
| Calpeak Power Enterprise 7 | 202401 | 121913 | 324314 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Southern_California_Desert_Ex_Solar |  |  | 0 | 0 | 1 | 1
| Doublett | 80436 | 44592 | 125028 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Grand Total | 0 | 0 | 0 | 0
| Elliott | 45307 | 46729 | 92036 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Encina | 126454 | 24920 | 151374 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Escondido | 203431 | 121928 | 325359 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fashion Valley | 28282 | 16983 | 45265 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Friars | 30269 | 20371 | 50640 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Main St. | 8747 | 7667 | 16414 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mesa Rim | 74254 | 55527 | 129781 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mission | 32441 | 23993 | 56434 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| North City West | 96479 | 49202 | 145681 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Old Town | 25583 | 12290 | 37873 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Palomar Airport | 143556 | 37740 | 181296 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Penasquitos | 81522 | 44598 | 126120 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| San Luis Rey | 133893 | 33714 | 167606 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| San Onofre | 23573 | 62718 | 86290 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Shadowridge | 174758 | 56678 | 231437 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Silvergate | 8282 | 7914 | 16196 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sycamore Canyon | 81712 | 110788 | 192500 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KramerInyoOutsideTxConstraintZones |  |  |  | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chino | 115236 | 34278 | 149514 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Etiwanda | 119521 | 34144 | 153665 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mira Loma | 153868 | 44777 | 198645 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Padua | 103281 | 37944 | 141225 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rancho Vista | 117869 | 35516 | 153385 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| San Bernardino | 109190 | 93582 | 202772 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Soquel | 112556 | 38097 | 150654 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Vista | 154339 | 71821 | 226161 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Norcal_Z3_SacramentoRiver |  |  |  | 1 | Norcal_Z3_SacramentoRiver | [10 empty] | 926 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Carberry | 63074 | 243738 | 306812 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Delevan | 226931 | 151233 | 378165 | 1 | Delevan | 226931 | 151233 | 378165 | 0.19 | 54024 | 32419 | 21605 | 173 | 0.06% | 0.53% |  | Sacramento_River_Solar | Delevan | 51195.299 | 81012.1767 | 390084 | 34% | 33% | 10% | 40% | 17% | 27% | 16% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Glenn | 312380 | 98005 | 410385 | 1 | Glenn | 312380 | 98005 | 410385 | 0.2 | 58626 | 44626 | 14001 | 187 | 0.06% | 0.42% |  | Sacramento_River_Solar | Glenn | 44210.1698 | 12672.6095 | 422866 | 13% | 14% | 14% | 13% | 15% | 19% | 11% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hat Creek 2 | 136010 | 217546 | 353557 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Palermo | 214738 | 187412 | 402150 | 1 | Palermo | 214738 | 187412 | 402150 | 0.2 | 57450 | 30677 | 26773 | 184 | 0.06% | 0.6% |  | Sacramento_River_Solar | Palermo | 88571.0985 | 38264.9217 | 469932 | 27% | 23% | 25% | 41% | 24% | 52% | 27% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pit 1 | 141777 | 214370 | 356147 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pit 1 Ph | 141555 | 215093 | 356648 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rio Oso | 390291 | 40334 | 430625 | 1 | Rio Oso | 390291 | 40334 | 430625 | 0.21 | 61518 | 55756 | 5762 | 197 | 0.07% | 0.35% |  | Sacramento_River_Solar | Rio Oso | 14098.6045 | 8689.4185 | 453203 | 5% | 3% | 3% | 33% | 8% | 30% | 2% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Table Mt. | 240287 | 158423 | 398711 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Thermalito | 249280 | 157779 | 407058 | 1 | Thermalito | 249280 | 157779 | 407058 | 0.2 | 58151 | 35611 | 22540 | 186 | 0.06% | 0.52% |  | Sacramento_River_Solar | Thermalito | 65448.8538 | 33637.056 | 480893 | 21% | 18% | 20% | 56% | 30% | 46% | 32% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 |  |  |  | 2028383 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Norcal_Z4_Solano |  |  |  | 1 | Norcal_Z4_Solano | [10 empty] | 622 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Amerigas | 260414 | 114395 | 374808 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bear Canyon | 117353 | 203394 | 320747 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Big Geysers | 130673 | 197242 | 327915 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Calistoga 19 | 139609 | 188704 | 328314 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Calpeak Power Vaca Dixon 1 | 262551 | 111983 | 374534 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Castro Valley | 46179 | 79407 | 125586 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cayetano | 116508 | 230435 | 346943 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cobb Creek | 146233 | 181413 | 327646 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Contra Costa | 200922 | 142150 | 343072 | 1 | Contra Costa | 200922 | 142150 | 343072 | 0.25 | 49010 | 28703 | 20307 | 156 | 0.08% | 0.54% |  |  | Contra Costa | 44886.2518 | 8693.2269 | 577525 | 9% | 30% | 1% | 57% | 80% | 44% | 46% | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
| Contra Costa Power | 210000 | 136983 | 346983 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fulton | 167498 | 182136 | 349634 | 1 | Fulton | 167498 | 182136 | 349634 | 0.26 | 49948 | 23928 | 26019 | 159 | 0.08% | 0.66% |  |  | Fulton | 113420.2788 | 51698.6453 | 492897 | 33% | 2% | 7% | 79% | 70% | 23% | 75% | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fumarole | 143276 | 186187 | 329463 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Geysers Unit 3 | 143689 | 184448 | 328137 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Grant 20 | 139259 | 192919 | 332177 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lake View | 156924 | 171486 | 328410 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lakeville | 154619 | 185621 | 340241 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lambie Energy | 239213 | 117481 | 356694 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lone Tree | 189538 | 155954 | 345491 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mccabe | 143114 | 185477 | 328591 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N.N. | 449207 | 549785 | 998991 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ncpa 1 & 2 | 123947 | 205474 | 329421 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ncpa 3 & 4 | 121200 | 206076 | 327276 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Oakmont North | 172006 | 168015 | 340021 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Oakmont South | 178163 | 164286 | 342449 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Peabody | 208221 | 151124 | 359345 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Quicksilver | 124619 | 201651 | 326270 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| San Ramon | 59665 | 164537 | 224202 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| San Ramon Research Cntr. | 58453 | 139042 | 197495 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Shiloh II | 225035 | 123667 | 348702 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Shiloh III | 223956 | 124121 | 348077 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Socrates 18 | 135800 | 198058 | 333858 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sonoma 3 | 141347 | 188617 | 329964 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sulphur Springs | 139885 | 191618 | 331503 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tassajara | 84879 | 164187 | 249066 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Technical Ecological Services | 58453 | 138968 | 197421 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Trans Bay Cable | 169698 | 134040 | 303738 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tulucay | 167011 | 134030 | 301040 | 1 | Tulucay | 167011 | 134030 | 301040 | 0.22 | 43006 | 23859 | 19147 | 137 | 0.07% | 0.57% |  |  | Tulucay | 69006.0487 | 47352.8037 | 401927 | 29% | 13% | 17% | 36% | 41% | 15% | 70% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Vaca-Dixon & Gc Yard | 259968 | 113943 | 373910 | 1 | Vaca-Dixon & Gc Yard | 259968 | 113943 | 373910 | 0.27 | 53416 | 37138 | 16278 | 170 | 0.09% | 0.46% |  |  | Vaca-Dixon & Gc Yard | 51167.8064 | 30002.4215 | 486714 | 17% | 15% | 7% | 38% | 39% | 49% | 37% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| West Ford Flat | 132006 | 192813 | 324820 | 0 |  |  |  | 1367657 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Norcal_Z4_Solano_subzone |  |  |  | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bahia | 89718 | 122146 | 211863 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Embarcadero (Sf Z) | 11282 | 9587 | 20869 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ignacio | 97444 | 129759 | 227203 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Moraga | 39757 | 50910 | 90667 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Parkway | 130355 | 119288 | 249643 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pittsburg | 142317 | 145504 | 287821 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rossmoor | 57401 | 90527 | 147928 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sobrante | 34876 | 49389 | 84265 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tidewater | 69223 | 127137 | 196360 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unocal | 88845 | 87790 | 176635 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NorCalOutsideTxConstraintZones |  |  |  | 1 | NorCalOutsideTxConstraintZones | [10 empty] | 397 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Brighton | 191632 | 60092 | 251724 | 1 | Brighton | 191632 | 60092 | 251724 | 0.39 | 35961 | 27376 | 8585 | 156 | 0.28% | 0.57% |  |  | Brighton | 12542.1839 | 6656.611 | 270547 | 7% | 13% | 6% | 53% | 44% | 58% | 18% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Gold Hill | 129525 | 192148 | 321673 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Jefferson | 7654 | 89704 | 97358 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Logan Creek | 250598 | 139780 | 390378 | 1 | Logan Creek | 250598 | 139780 | 390378 | 0.61 | 55768 | 35800 | 19969 | 241 | 0.26% | 0.67% |  |  | Logan Creek | 69148.2162 | 65087.8819 | 410633 | 33% | 33% | 14% | 15% | 12% | 14% | 4% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Martin | 5970 | 14050 | 20020 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| San Mateo | 9079 | 37974 | 47053 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 |  |  |  | 642102 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SCADOutsideTxConstraintZones |  |  |  | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cima | - | 8101 | 8101 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SCADSNV_Z1_EldoradoAndMtnPass |  |  |  | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ElDorado | - | - | - | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SCADSNV_Z3_GreaterImperial |  |  |  | 1 | SCADSNV_Z3_GreaterImperial | [10 empty] | 548 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| East County | 11025 | 96156 | 107180 | 1 | East County | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Imperial Valley | 207772 | 25483 | 233255 | 1 | Imperial Valley | 207772 | 25483 | 233255 | 0.61 | 33322 | 29682 | 3640 | 333 | 0.61% | 1.12% |  |  | Imperial Valley | 16371.6201 | 21146.4397 | 239781 | 16% | 4% | 4% | 22% | 22% | 72% | 7% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ocotillo Express | 38327 | 112107 | 150434 | 1 | Ocotillo Express | 38327 | 112107 | 150434 | 0.39 | 21491 | 5475 | 16015 | 215 | 0.39% | 3.92% |  |  | Ocotillo Express | 50579.2763 | 41549.0601 | 158933 | 58% | 34% | 42% | 25% | 39% | 16% | 34% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Suncrest | 14209 | 224326 | 238534 | 1 | Suncrest | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 1 | Total |  |  | 383689 |  | 54813 | 35157 | 19656 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SCADSNV_Z4_RiversideAndPalmSprings |  |  |  | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Colorado River | 121669 | 200351 | 322021 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Red Bluff | 51720 | 112348 | 164067 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SCADSNV_Z5_SCADSNV |  |  |  | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capacitor | 18968 | 48995 | 67963 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Eagle Mt. | 47355 | 84479 | 131834 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Iron Mt. | 32233 | 161416 | 193650 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Julian Hinds | 9794 | 39712 | 49506 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Los Coches | 45300 | 141878 | 187178 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Miguel | 11515 | 58209 | 69725 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mohave | 252 | 5823 | 6075 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Otay Mesa | 7815 | 59710 | 67525 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| South Bay | 7192 | 12577 | 19769 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SPGE_Z1_Westlands |  |  |  | 1 | SPGE_Z1_Westlands | [10 empty] | 468 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ashlan Ave. | 339742 | 55626 | 395368 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fig Garden | 325840 | 67856 | 393696 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Gates | 244790 | 61943 | 306734 | 1 | Gates | 244790 | 61943 |  | - | - | 34970 | 8849 | - | 0% | 0% |  |  | Gates | 19172.7969 | 6084.4336 | 316899 | 8% | 10% | 12% | 26% | 28% | 11% | 14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Gregg | 317053 | 74590 | 391644 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Helm | 351333 | 7887 | 359220 | 1 | Helm | 351333 | 7887 |  | - | - | 50190 | 1127 | - | 0% | 0% |  |  | Helm | 247.1054 | 0 | 409866 | 0% | 1% | 0% | 22% | 15% | 27% | 15% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Henrietta | 332147 | - | 332147 | 1 | Henrietta | 332147 | - |  | - | - | 47450 | - | - | 0% | 0% |  |  | Henrietta | 0 | 0 | 345015 | 0% | 0% | 0% | 12% | 8% | 17% | 3% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Herndon | 323716 | 66266 | 389982 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kearney (New) | 371486 | 61 | 371547 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Los Banos | 114226 | 174190 | 288416 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mc Call | 409347 | 5918 | 415265 | 1 | Mc Call | 409347 | 5918 | 415265 | 1 | 59324 | 58478 | 845 | 468 | 0.79% | 0.8% |  |  | Mc Call | 957.8942 | 203.4955 | 482590 | 0% | 0% | 0% | 6% | 3% | 38% | 3% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mc Mullin | 386506 | 648 | 387154 | 1 | Mc Mullin | 386506 | 648 |  | - | - | 55215 | 93 | - | 0% | 0% |  |  | Mc Mullin | 0 | 0 | 460177 | 0% | 1% | 0% | 11% | 5% | 27% | 9% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Oxford | 161974 | 150132 | 312106 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Panoche | 208837 | 117291 | 326128 | 1 | Panoche | 208837 | 117291 |  | - | - | 29834 | 16756 | - | 0% | 0% |  |  | Panoche | 41908.7178 | 54263.3679 | 354129 | 27% | 25% | 27% | 38% | 40% | 18% | 33% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| San Luis | 108749 | 201483 | 310232 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| San Luis 3 | 195956 | 128527 | 324483 | 1 | Total | 1932960 | 193688 | 415265 |  | 59324 | 276137 | 27670 | 468 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| San Luis 5 | 173321 | 138035 | 311356 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wright | 138417 | 143289 | 281706 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SPGE_Z2_KernAndGreaterCarrizo |  |  |  | 1 | SPGE_Z2_KernAndGreaterCarrizo | [10 empty] | 801 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Arco | 273895 | 115185 | 389080 | 1 | Arco | 273895 | 115185 | 389080 | 0.21 | 55583 | 39128 | 16455 | 165 | 0.06% | 0.42% |  |  | Arco | 32458.9861 | 11374.1407 | 401584 | 11% | 31% | 18% | 26% | 21% | 19% | 11% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Buena Vista Pumps | 210938 | 156404 | 367342 | 1 | Buena Vista Pumps | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kern Power | 316544 | 76164 | 392707 | 1 | Kern Power | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Midway | 275516 | 100733 | 376249 | 1 | Midway | 275516 | 100733 | 376249 | 0.2 | 53750 | 39359 | 14390 | 160 | 0.06% | 0.41% |  |  | Midway | 11830.8569 | 0 | 420674 | 3% | 13% | 7% | 72% | 72% | 22% | 61% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Renfro | 318206 | 68186 | 386392 | 1 | Renfro | 318206 | 68186 | 386392 | 0.2 | 55199 | 45458 | 9741 | 164 | 0.06% | 0.36% |  |  | Renfro | 12637.4596 | 0 | 463397 | 3% | 3% | 2% | 50% | 45% | 28% | 34% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Stockdale | 329571 | 58200 | 387771 | 1 | Stockdale | 329571 | 58200 | 387771 | 0.21 | 55396 | 47082 | 8314 | 165 | 0.06% | 0.35% |  |  | Stockdale | 10024.6916 | 0 | 471591 | 2% | 2% | 2% | 51% | 42% | 35% | 31% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wheeler Ridge | 238850 | 108140 | 346990 | 1 | Wheeler Ridge | 238850 | 108140 | 346990 | 0.18 | 49570 | 34121 | 15449 | 147 | 0.05% | 0.43% |  |  | Wheeler Ridge | 48498.2819 | 11956.8974 | 403802 | 15% | 18% | 18% | 44% | 37% | 36% | 25% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 1 | Total | 1436038 | 450445 | 1886482 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SPGE_Z3_Carrizo |  |  |  | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Caliente | 153857 | 222593 | 376449 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mesa | 183463 | 152282 | 335745 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Solar | 129613 | 260323 | 389936 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Templeton | 246398 | 178427 | 424825 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SPGE_Z4_CentralValleyAndLosBanos |  |  |  | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bellota | 255520 | 190399 | 445919 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cottle | 244115 | 184778 | 428893 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Eight Mile | 361385 | 26159 | 387544 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Stagg | 361484 | 19363 | 380846 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Storey | 293286 | 148690 | 441976 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weber | 390024 | 7132 | 397157 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wilson | 221461 | 144010 | 365471 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tehachapi |  |  |  | 1 | Tehachapi | [10 empty] | 4656 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Antelope | 283495 | 91598 | 375092 | 1 | Antelope | 283495 | 91598 | 375092 | 0.26 | 53585 | 40499 | 13085 | 1210 | 0.59% | 2.99% |  |  | Antelope | 57483.2355 | 17818.6781 | 452328 | 17% | 7% | 6% | 68% | 30% | 75% | 22% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Arbwind | 187469 | 131236 | 318705 | 1 | Arbwind | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bailey | 51085 | 172594 | 223678 | 1 | Bailey | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Highwind | 177593 | 122671 | 300264 | 1 | Highwind | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mojave 17 | 219898 | 123483 | 343381 | 1 | Mojave 17 | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N.N. | 449207 | 549785 | 998991 | 1 | N.N. | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pardee | 103541 | 134265 | 237806 | 1 | Pardee | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pearblossom | 161231 | 175860 | 337091 | 1 | Pearblossom | 161231 | 175860 | 337091 | 0.23 | 48156 | 23033 | 25123 | 1087 | 0.53% | 4.72% |  |  | Pearblossom | 84512.2937 | 38538.2188 | 358514 | 34% | 10% | 3% | 78% | 47% | 91% | 23% | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0
| Saugus | 104149 | 130389 | 234538 | 1 | Saugus | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sky River North | 42559 | 138617 | 181177 | 1 | Sky River North | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Vincent | 184409 | 117262 | 301671 | 1 | Vincent | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Warne | 33576 | 158596 | 192172 | 1 | Warne | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Westwind | 219617 | 124770 | 344387 | 1 | Westwind | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Whirlwind | 242519 | 141802 | 384321 | 1 | Whirlwind | 242519 | 141802 | 384321 | 0.27 | 54903 | 34646 | 20257 | 1240 | 0.6% | 3.58% |  |  | Whirlwind | 73010.2351 | 40426.1201 | 489686 | 23% | 12% | 10% | 73% | 30% | 89% | 21% | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
| Winderness | 224940 | 119400 | 344340 | 1 | Winderness | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Windhub | 224364 | 122565 | 346929 | 1 | Windhub | 224364 | 122565 | 346929 | 0.24 | 49561 | 32052 | 17509 | 1119 | 0.54% | 3.49% |  |  | Windhub | 81311.2708 | 31850.2971 | 461897 | 24% | 3% | 4% | 59% | 37% | 77% | 22% | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
[5 empty] | 1 | Total | 911607 | 531825 | 1443433 |  |  |  |  | 4656 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TehachapiOutsideTxConstraintZones |  |  |  | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Airchem | - | - | - | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Arcogen | - | - | - | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cameron | - | - | - | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Casitas | 105111 | 55297 | 160408 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Center | 835 | - | 835 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chevmain | - | - | - | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Del Amo | - | - | - | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Eagle Rock | 90 | 20648 | 20738 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| El Nido | - | - | - | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| El Segundo | - | 3 | 3 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Federalgen | - | - | - | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Goodrich | 90 | 23212 | 23303 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Gould | 3647 | 48488 | 52135 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Harborgen | - | - | - | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hinson | - | - | - | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kinetic | - | - | - | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| La Cienega | 60 | 3 | 64 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| La Fresa | - | - | - | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Laguna Bell | - | - | - | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lawndale | - | - | - | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lighthipe | - | - | - | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mandalay | 121908 | 24739 | 146647 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mesa | 183463 | 152282 | 335745 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Moorpark | 175850 | 76092 | 251941 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N.N. | 449207 | 549785 | 998991 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Olinda | 28973 | 12098 | 41071 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ormond Beach | 110407 | 14885 | 125292 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Redondo 1 | - | - | - | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Repro | - | - | - | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rio Hondo | 18154 | 19395 | 37550 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rosecrans | - | - | - | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Santa Clara | 176305 | 44572 | 220877 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Stadium | - | - | - | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Stanhill | - | - | - | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tahiti | 60 | 13 | 74 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Venice Hydro | 60 | 8 | 69 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Walnut | 26759 | 8356 | 35115 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Windsor Hills | - | - | - | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WestlandsOutsideTxConstraintZones |  |  |  | 1 | WestlandsOutsideTxConstraintZones | [10 empty] | 1779 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Coburn | 162721 | 218557 | 381278 | 1 | Coburn | 162721 | 218557 | 381278 | 0.62 | 54468 | 23246 | 31222 | 1100 | 1.25% | 4.73% |  |  | Coburn | 109154.4382 | 41112.0693 | 381278 | 39% | 18% | 25% | 27% | 20% | 38% | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diablo Canyon | 52516 | 78415 | 130931 | 1 | Diablo Canyon | 52516 | 78415 | 130931 | 0.21 | 18704 | 7502 | 11202 | 378 | 0.43% | 5.03% |  |  | Diablo Canyon | 40683.9006 | 19212.5757 | 140061 | 43% | 2% | 1% | 71% | 69% | 32% | 97% | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
| Goleta | 50794 | 53729 | 104523 | 1 | Goleta | 50794 | 53729 | 104523 | 0.17 | 14932 | 7256 | 7676 | 302 | 0.34% | 4.16% |  |  | Goleta | 29380.9657 | 29032.5296 | 104523 | 56% | 37% | 10% | 17% | 18% | 58% | 26% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 |  |  |  | 616732 |  |  |  |  | 1779 | [24 empty] | 0 | 0
| Grand Total | 28058029 | 21760032 | 49818061 | 0 | [33 empty] | 0 | 0
[5 empty] | 0 | [33 empty] | 0 | 0
[5 empty] | 1 | Mountain_Pass_El_Dorado _Solar | [10 empty] | 248 | [21 empty] | 0 | 0
[5 empty] | 1 | El Dorado 230kV | [7 empty] | 83 | [24 empty] | 0 | 0
[5 empty] | 1 | El Dorado 500kV | [7 empty] | 165 |  |  |  | Mountain_Pass_El_Dorado_Solar | [20 empty] | 0 | 0
[5 empty] | 1 | El Dorado |  |  | 42263 | 1 | 6038 |  |  | 248 | 4.11% |  |  | Mountain_Pass_El_Dorado_Solar | [20 empty] | 0 | 0
[5 empty] | 0 | [33 empty] | 0 | 0
[5 empty] | 1 | Southern_California Desert_Ex_Solar | [10 empty] | 862 | [21 empty] | 0 | 0
[5 empty] | 1 | Crazy Eyes |  |  | 155787 | 0.61 | 22255 |  |  | 526 | 2.36% |  |  | Southern_California_Desert_Ex_Solar | [20 empty] | 0 | 0
[5 empty] | 1 | Desert View |  |  | 42719 | 0.17 | 6103 |  |  | 147 | 2.4% |  |  | Southern_California_Desert_Ex_Solar | [20 empty] | 0 | 0
[5 empty] | 1 | Innovation |  |  | 54904 | 0.22 | 7843 |  |  | 190 | 2.42% |  |  | Southern_California_Desert_Ex_Solar | [20 empty] | 0 | 0
[5 empty] | 1 | Eldorado |  |  | 42263 | 1 | 6038 |  |  |  | 0% |  |  | Southern_California_Desert_Ex_Solar | [20 empty] | 0 | 0
[5 empty] | 1 | Mohave 500kV | [32 empty] | 0 | 0
[5 empty] | 0 | [8 empty] | 862 | [24 empty] | 0 | 0
[5 empty] | 0 | [33 empty] | 0 | 0
[5 empty] | 1 | Southern_Nevada_Solar | [32 empty] | 0 | 0
[5 empty] | 1 | Crazy Eyes |  |  | 155787 | 0.61 | 22255 |  |  |  | 0% |  |  | Southern_Nevada_Solar | [20 empty] | 0 | 0
[5 empty] | 1 | Desert View |  |  | 42719 | 0.17 | 6103 |  |  |  | 0% |  |  | Southern_Nevada_Solar | [20 empty] | 0 | 0
[5 empty] | 1 | Innovation |  |  | 54904 | 0.22 | 7843 |  |  |  | 0% |  |  | Southern_Nevada_Solar | [20 empty] | 0 | 0
[5 empty] | 1 | Eldorado |  |  | 42263 | 1 | 6038 |  |  |  | 0% |  |  | Southern_Nevada_Solar | [20 empty] | 0 | 0
[5 empty] | 1 | Mohave 500kV | [32 empty] | 0 | 0
[5 empty] | 0 | [33 empty] | 0 | 0
[5 empty] | 1 | SCADSNV_Solar | [10 empty] | 330 | [21 empty] | 0 | 0
[5 empty] | 1 | Mohave 500kV |  |  | 28764 | 1 | 4109 |  |  | 330 | 8.03% |  |  | SCADSNV_Solar | [20 empty] | 0 | 0

## 3_SUM WIND RESOURCE ACRES
Source: IRP 2021 Wind Allocation and ECO Values.xlsx
3a. What constitutes level 3 flag? | 100% | Exceeds 100% of candidate project area land within the standard radius
3a. What constitutes level 2 flag? | 75% | Exceeds 75% of candidate project area land within the standard radius
3a. What constitutes level 1 flag? | All other
3b. What constitutes level 3 flag? | 75% | More than 75% of the candidate project area occurs on four or more of the sensitive area types
4
3b. What constitutes level 2 flag? | 20% | Exceeds 20% of the low-environmental-implication land area within the standard radius
4
3b. What constitutes level 1 flag? | All other |  |  |  |  | acres/MW #1 | 107.7431 |  | acres/MW #2 | 40
|  |  | SUMMARY | [10 empty] | SUMMARY |  | INTACTNESS | NLB | CONNECTIVITY | BIO | RARE | NATIVE | IRREPLACABILITY | 3b. Level 3 Non-compliance Flag | [7 empty] | 3b. Level 2 | 3a. Non Compliance Flag |  |  | Exceeds 100% of candidate project area land within the standard radius | Exceeds 75% of candidate project area land within the standard radius
|  | Substation | Wind Project | ACRES_LOW | ACRES_HIGH | TOTAL_ACRES | Potential MW | MW Allocation | Percent of Total _MW | PROJECT ACRES | Percent of Acres_LOW | CEC Comments | RESOLVE resource | WIND AREA | Total Acres | INTACT % of Area | NLB % of Area | CONNECTIVITY % of Area | BIO % of Area | RARE % of Area | NATIVE % of Area | IRREPLACEABLE % of Area | INTACTNESS | NLB | CONNECTIVITY | BIO | RARE | NATIVE | IRREPLACIBILITY | 3b. Level 3 | 3b. Level 2 | 3a Level 3 | 3a Level 2 | RESOLVE resource | Sum of 3a Level 3 | Sum of 3a Level 2 | Sum of 3b. Level 3 | Sum of 3b. Level 2 | Criteria 3a | Criteria 3b
| Carrizo Wind | [6 empty] | 287 | [25 empty] | Carrizo_Wind | 0 | 1 | 0 | 1 | 2 | 2
|  | Templeton | Wind 124 | 6730 | 24300 | 31030 | 288 |  | 100% | 11480 | 171% | Project Acres Exceeds Total Low Value Acres | Carrizo_Wind | Wind 124 | 3093900% | 68% | 9% | 3% | 78% | 83% | 67% | 49% | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | Central_Valley_North_Los_Banos_Wind | 1 | 1 | 0 | 1 | 3 | 2
[23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Humboldt_Wind | 0 | 0 | 0 | 1 | 1 | 2
| Central Valley and North Los Banos Wind |  |  |  |  | acres/MW #1 | 335.7353 |  | acres/MW #2 | 40 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | Kern_Greater_Carrizo_Wind | 0 | 0 | 0 | 0 | 1 | 1
| 439.212 | Los Banos | Wind 112 | 16166 | 23407 | 39573 | 170 | 173 | 102% | 6920 | 43% |  | Central_Valley_North_Los_Banos_Wind | Wind 112 | 37621 | 35% | 35% | 38% | 46% | 36% | 67% | 8% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | Northern_California_Ex_Wind | 0 | 0 | 0 | 0 | 1 | 1
[23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Solano_Wind | 0 | 0 | 1 | 1 | 1 | 3
| Humboldt Wind |  |  |  |  | acres/MW #1 | 335.7353 | 34 | acres/MW #2 | 147.7059 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | Tehachapi_Wind | 0 | 1 | 0 | 0 | 2 | 1
|  | Bridgeville | Wind 7 | - | 11415 | 11415 | 34 |  |  | 5022 |  |  | Humboldt_Wind | Wind 7 | 11415 | 100% | 63% | 94% | 0% | 0% | 0% | 0% | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (blank) | 0 | 0 | 0 | 0 | 1 | 1
|  |  | Wind 8 | 0 | 11356 | 11356 | 33 |  |  | 4837 |  |  | Humboldt_Wind | Wind 8 | 10636 | 100% | 45% | 86% | 0% | 0% | 0% | 0% | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Grand Total | 1 | 3 | 1 | 4
|  |  |  | - | 22770 | 22771 | 67 |  | 50.75% | 1360 | 999999% | No Low Value ACRES | Humboldt_Wind | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
[23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kern Greater Carrizo Wind |  |  |  |  | acres/MW #1 | 298.9275 | 20 | acres/MW #2 | 40 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
|  | Cholame | Wind 207 | 11176 | 9449 | 20626 | 69 |  | 29% | 800 | 7% |  | Kern_Greater_Carrizo_Wind | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Northern_California_Ex_Wind |  |  |  |  | acres/MW #1 | 181.9917 | 767 | acres/MW #2 | 40 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
|  | Glenn | Wind 34 | 21839 | - | 21839 | 120 | [5 empty] | Northern_California_Ex_Wind | Wind 34 | 24805 | 0% | 0% | 0% | 8% | 17% | 0% | 8% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 35 | 32087 | - | 32087 | 166 | [5 empty] | Northern_California_Ex_Wind | Wind 35 | 35052 | 0% | 0% | 0% | 16% | 23% | 0% | 16% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 36 | 27505 | 1796 | 29301 | 149 | [5 empty] | Northern_California_Ex_Wind | Wind 36 | 29547 | 1% | 9% | 9% | 0% | 6% | 11% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 37 | 25022 | 3740 | 28762 | 168 | [5 empty] | Northern_California_Ex_Wind | Wind 37 | 28762 | 2% | 6% | 11% | 5% | 10% | 7% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 38 | 13114 | 16736 | 29850 | 157 | [5 empty] | Northern_California_Ex_Wind | Wind 38 | 30605 | 23% | 29% | 35% | 7% | 19% | 8% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 39 | 25914 | 7966 | 33880 | 166 | [5 empty] | Northern_California_Ex_Wind | Wind 39 | 34947 | 11% | 3% | 11% | 21% | 1% | 9% | 15% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 40 | 20909 | 8988 | 29897 | 166 | [5 empty] | Northern_California_Ex_Wind | Wind 40 | 30502 | 33% | 22% | 3% | 13% | 3% | 22% | 18% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 42 | 31675 | 1332 | 33007 | 183 | [5 empty] | Northern_California_Ex_Wind | Wind 42 | 32983 | 0% | 0% | 0% | 6% | 15% | 31% | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 43 | 21329 | 11016 | 32345 | 183 | [5 empty] | Northern_California_Ex_Wind | Wind 43 | 35716 | 24% | 22% | 22% | 27% | 17% | 63% | 3% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 50 | 17028 | 12467 | 29496 | 166 | [5 empty] | Northern_California_Ex_Wind | Wind 50 | 29495 | 17% | 34% | 24% | 36% | 47% | 55% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 51 | 33870 | 247 | 34117 | 163 | [5 empty] | Northern_California_Ex_Wind | Wind 51 | 34117 | 0% | 0% | 0% | 44% | 48% | 32% | 42% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 204 | 13663 | - | 13663 | 69 | [5 empty] | Northern_California_Ex_Wind | Wind 204 | 13663 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 283957 | 64288 | 348245 | 1856 | 354 | 19% | 14160 | 5% |  | Northern_California_Ex_Wind | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Delevan |  |  |  | acres/MW #1 | 193.8947 |  | acres/MW #1 | 40 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
|  |  | Wind 31 | 6085 | 1283 | 7368 | 38 | [5 empty] | Northern_California_Ex_Wind | Wind 31 | 7368 | 0% | 0% | 15% | 17% | 41% | 0% | 17% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 32 | 31203 | 2641 | 33844 | 175 | [5 empty] | Northern_California_Ex_Wind | Wind 32 | 33844 | 0% | 0% | 0% | 32% | 57% | 0% | 32% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 33 | 29016 | - | 29016 | 222 | [5 empty] | Northern_California_Ex_Wind | Wind 33 | 29016 | 0% | 0% | 0% | 31% | 52% | 0% | 31% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 66304 | 3924 | 70228 | 435 | 83 | 19% | 3320 | 5% |  | Northern_California_Ex_Wind | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Thermalito |  |  |  | acres/MW #1 | 179.1703 |  | acres/MW #1 | 40 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
|  |  | Wind 52 | 32609 | - | 32609 | 182 | [5 empty] | Northern_California_Ex_Wind | Wind 52 | 32609 | 0% | 0% | 0% | 67% | 53% | 0% | 67% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 53 | 29609 | - | 29609 | 172 | [5 empty] | Northern_California_Ex_Wind | Wind 53 | 29609 | 0% | 0% | 0% | 59% | 25% | 6% | 59% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 54 | 30953 | 377 | 31330 | 174 | [5 empty] | Northern_California_Ex_Wind | Wind 54 | 35340 | 0% | 0% | 0% | 64% | 16% | 12% | 64% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 55 | 23422 | - | 23422 | 138 | [5 empty] | Northern_California_Ex_Wind | Wind 55 | 25446 | 0% | 0% | 0% | 82% | 41% | 0% | 82% | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
|  |  | Wind 56 | 31229 | 634 | 31863 | 172 | [5 empty] | Northern_California_Ex_Wind | Wind 56 | 31863 | 0% | 1% | 0% | 90% | 27% | 0% | 90% | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
|  |  | Wind 202 | 16889 | - | 16889 | 96 | [5 empty] | Northern_California_Ex_Wind | Wind 202 | 18875 | 0% | 0% | 0% | 54% | 0% | 0% | 54% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 164712 | 1011 | 165722 | 934 | 178 | 19% | 7120 | 4% |  | Northern_California_Ex_Wind | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Rio Oso | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 62 | 30714 | - | 30714 | 176 | [5 empty] | Northern_California_Ex_Wind | Wind 62 | 36470 | 0% | 0% | 0% | 39% | 0% | 0% | 39% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 73 | 29002 | - | 29002 | 172 | [5 empty] | Northern_California_Ex_Wind | Wind 73 | 31279 | 0% | 0% | 0% | 68% | 0% | 0% | 68% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 77 | 35294 | - | 35294 | 181 | [5 empty] | Northern_California_Ex_Wind | Wind 77 | 35294 | 0% | 0% | 0% | 31% | 11% | 47% | 31% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 78 | 30267 | - | 30267 | 160 | [5 empty] | Northern_California_Ex_Wind | Wind 78 | 30267 | 0% | 0% | 0% | 92% | 1% | 3% | 92% | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
|  |  | Wind 79 | 20228 | - | 20228 | 107 | [5 empty] | Northern_California_Ex_Wind | Wind 79 | 20228 | 0% | 0% | 0% | 38% | 0% | 40% | 38% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 145506 | - | 145506 | 796 | 152 | 19% | 6080 | 4% |  | Northern_California_Ex_Wind | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Solano Wind | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Lakeville | Wind 198 | 2361 | 15003 | 17364 | 71 | [5 empty] | Solano_Wind | Wind 198 | 17040 | 93% | 42% | 51% | 59% | 64% | 0% | 59% | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 101 | 2393 | 29049 | 31442 | 166 | [5 empty] | Solano_Wind | Wind 101 | 28905 | 82% | 60% | 86% | 77% | 79% | 16% | 70% | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
|  |  | Wind 102 | 7207 | 8591 | 15798 | 70 | [5 empty] | Solano_Wind | Wind 102 | 15067 | 25% | 38% | 44% | 1% | 1% | 0% | 1% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 196 | 2948 | 31571 | 34519 | 146 | [5 empty] | Solano_Wind | Wind 196 | 33765 | 73% | 16% | 30% | 72% | 75% | 14% | 58% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 197 | 4626 | 26007 | 30633 | 117 | [5 empty] | Solano_Wind | Wind 197 | 26596 | 84% | 83% | 73% | 72% | 77% | 35% | 52% | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 199 | 4047 | 26316 | 30363 | 136 | [5 empty] | Solano_Wind | Wind 199 | 30012 | 91% | 37% | 34% | 49% | 52% | 0% | 49% | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 23583 | 136537 | 160119 | 706 | 194 | 27% | 7760 | 33% |  | Solano_Wind | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
[23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Tulucay | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 103 | 3479 | 13205 | 16684 | 22 | [5 empty] | Solano_Wind | Wind 103 | 16602 | 76% | 12% | 37% | 19% | 13% | 13% | 19% | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 106 | 5959 | 19351 | 25310 | 50 | [5 empty] | Solano_Wind | Wind 106 | 25278 | 36% | 41% | 50% | 79% | 45% | 0% | 81% | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
|  |  |  | 9438 | 32556 | 41994 | 72 | 20 | 28% | 800 | 8% |  | Solano_Wind | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Vaca-Dixon & GC Yard | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 80 | 11733 | 20669 | 32402 | 86 | [5 empty] | Solano_Wind | Wind 80 | 32399 | 49% | 48% | 57% | 10% | 2% | 94% | 0% | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 81 | 23098 | 11486 | 34584 | 114 | [5 empty] | Solano_Wind | Wind 81 | 33699 | 12% | 6% | 10% | 30% | 31% | 89% | 0% | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 82 | 30872 | - | 30872 | 77 | [5 empty] | Solano_Wind | Wind 82 | 29984 | 0% | 0% | 0% | 0% | 0% | 62% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 83 | 34973 | 574 | 35547 | 80 | [5 empty] | Solano_Wind | Wind 83 | 33527 | 0% | 2% | 0% | 65% | 47% | 63% | 61% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 84 | 32773 | 3679 | 36452 | 89 | [5 empty] | Solano_Wind | Wind 84 | 36452 | 0% | 2% | 2% | 63% | 47% | 32% | 40% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 85 | 29813 | 6243 | 36056 | 85 | [5 empty] | Solano_Wind | Wind 85 | 36056 | 0% | 9% | 1% | 23% | 17% | 34% | 22% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 163263 | 42650 | 205914 | 531 | 146 | 27% | 5840 | 4% |  | Solano_Wind | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Shilo III | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 91 | 28654 | 5620 | 34273 | 82 | [5 empty] | Solano_Wind | Wind 91 | 34273 | 0% | 0% | 0% | 59% | 84% | 33% | 47% | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 206 | 10021 | 4705 | 14725 | 34 | [5 empty] | Solano_Wind | Wind 206 | 14725 | 0% | 33% | 0% | 50% | 100% | 18% | 5% | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 88 | 38049 | 3368 | 41417 | 88 | [5 empty] | Solano_Wind | Wind 88 | 36096 | 0% | 12% | 0% | 36% | 75% | 39% | 15% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 90 | 22116 | 689 | 22805 | 57 | [5 empty] | Solano_Wind | Wind 90 | 22805 | 0% | 0% | 0% | 60% | 79% | 43% | 23% | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 98839 | 14382 | 113220 | 261 | 72 | 28% | 2880 | 3% |  | Solano_Wind | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Lone Tree | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 104 | 5792 | 16975 | 22767 | 35 | [5 empty] | Solano_Wind | Wind 104 | 22172 | 50% | 56% | 0% | 89% | 91% | 19% | 81% | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0
|  |  | Wind 107 | 15568 | 23209 | 38777 | 79 | [5 empty] | Solano_Wind | Wind 107 | 38776 | 26% | 32% | 29% | 74% | 89% | 45% | 66% | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 21360 | 40184 | 61544 | 114 | 30 | 26% | 1200 | 6% |  | Solano_Wind | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tehachapi Wind | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Windhub | Wind 129 | 13671 | 16117 | 29787 | 128 | [5 empty] | Tehachapi_Wind | Wind 129 | 28309 | 19% | 0% | 0% | 77% | 37% | 52% | 88% | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
|  |  | Wind 156 | 12436 | 922 | 13358 | 86 | [5 empty] | Tehachapi_Wind | Wind 156 | 13358 | 10% | 0% | 0% | 38% | 31% | 94% | 0% | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
|  |  | Wind 157 | 30642 | 1301 | 31943 | 138 | [5 empty] | Tehachapi_Wind | Wind 157 | 30279 | 5% | 0% | 0% | 60% | 36% | 96% | 3% | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
|  |  |  | 56748 | 18340 | 75088 | 352 | 275 | 78% | 11000 | 19% |  | Tehachapi_Wind | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1

## 3aSUM OF SOLAR RESOURCE ACRE R2
Source:
3a. What constitutes level 3 flag? |  | 100% | Exceeds 100% of candidate project area land within the standard radius
3a. What constitutes level 2 flag? |  | 75% | Exceeds 75% of candidate project area land within the standard radius
3a. What constitutes level 1 flag? |  | All other
3b. What constitutes level 3 flag? |  | 75% | More than 75% of the candidate project area occurs on four or more of the sensitive area types
4
3b. What constitutes level 2 flag? |  | 20% | Exceeds 20% of the low-environmental-implication land area within the standard radius
4
3b. What constitutes level 1 flag? |  | All other
[5 empty] | SELECTED | [13 empty] | SUMMARY |  |  |  | INTACTNESS | NLB | CONNECTIVITY | BIO | RARE | NATIVE | IRREPLACIBILITY | IBA Acres | Percent Total | Fire_T1 Acres | Fire_T2 Acres | Fire_T3 Acres | Total FireThreat Acres | Percent Total | 3b. Level 3 Non-compliance Flag | [7 empty] | 3b. Level 2 | 3a. Non-compliance Flag
| Tx Zone/Substation | ACRES_15_LOW | ACRES_15_HIGH | TOTAL ACRES_15 | Tx Zone/Substation | ACRES_15_LOW | ACRES_15_HIGH | TOTAL ACRES_15 | Porportion of Total Acres | Potential MW | Potential MW Low | Potential MW High | MW Allocation | Percent Total ACRES | Percent ACRES Low |  | RESOLVE MW | RESOLVE Resource | SUBSTATION | 4 | 5 | Total Acres | % of Area | % of Area | % of Area | % of Area | % of Area | % of Area | % of Area | IBA Acres | Percent Total | Fire_T1 Acres | Fire_T2 Acres | Fire_T3 Acres | Total FireThreat Acres | Area | INTACTNESS | NLB | CONNECTIVITY | BIO | RARE | NATIVE | IRREPLACIBILITY | 3b. Level 3 | 3b. Level 2 | 3a Level 3 | 3a Level 2 | RESOLVE Resource | Sum of 3a Level 3 | Sum of 3a Level 2 | Sum of 3b. Level 3 | Sum of 3b. Level 2 | Criteria 3a | Criteria 3b
| GK_Z2_InyokernAndNorthOfKramer | [46 empty] | Greater_Imperial_Solar | 0 | 0 | 0 | 0 | 1 | 1
| Kramer | 22292 | 108531 | 130823 | [43 empty] | Kern_Greater_Carrizo_Solar | 0 | 0 | 0 | 0 | 1 | 1
| Randsburg | 32006 | 132828 | 164834 | [43 empty] | Mountain_Pass_El_Dorado_Solar | 0 | 0 | 0 | 0 | 1 | 1
[48 empty] | North_Victor_Solar | 0 | 0 | 0 | 0 | 1 | 1
| GK_Z3_NorthOfVictor |  |  |  | GK_Z3_NorthOfVictor | [42 empty] | Northern_California_Ex_Solar | 0 | 0 | 0 | 0 | 1 | 1
| Caldwell | 202590 | 157849 | 360439 | Caldwell | [11 empty] | 300 | [30 empty] | Riverside_Palm_Springs_Solar | 0 | 0 | 0 | 0 | 1 | 1
| Cool Water | 37474 | 118138 | 155612 | Cool Water | 37474 | 118138 | 155612 | #DIV/0! | 22230 | 5353 | 16877 | 215 | 1.274% | 4.016% |  |  | North_Victor_Solar | Cool Water | 27109.5303 | 18042.6093 | 159843 | 28% | 8% | 16% | 74% | 58% | 94% | 11% | 1343 | 0.3% | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | Sacramento_River_Solar | 0 | 0 | 0 | 0 | 1 | 1
| Victor | 226644 | 167494 | 394138 | Victor | 226644 | 167494 | 394138 | #DIV/0! | 56305 | 32378 | 23928 | 85 | 0.3552% | 0.2625% |  |  | North_Victor_Solar | Victor | 52753.358 | 19113.8778 | 428829 | 17% | 2% | 3% | 92% | 56% | 98% | 8% | 3930 | 1% | 1 | 51364 | 36289 | 87654 | 19% | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | SCADSNV_Solar | 0 | 0 | 0 | 0 | 1 | 1
[18 empty] | North_Victor_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Solano_Solar | 0 | 0 | 0 | 0 | 1 | 1
[18 empty] | North_Victor_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Southern_Nevada_Solar | 0 | 0 | 0 | 0 | 1 | 1
| GK_Z4_Pisgah |  |  |  | GK_Z4_Pisgah | [12 empty] | North_Victor_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tehachapi_Solar | 0 | 0 | 0 | 0 | 1 | 1
| Calcite | 263893 | 637139 | 901032 | Calcite | 263893 | 637139 | 901032 | 0.69 | 128719 | 37699 | 91020 | 140 | 0.08% | 0.37% |  |  | Pisgah_Solar | Calcite | 94244.9456 | 93945.5228 | 484156 | 39% | 6% | 11% | 65% | 39% | 91% | 14% | 1165 | 0.3% | - | 52805 | - | 52805 | 12% | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | Westlands_Ex_Solar | 0 | 0 | 0 | 0 | 1 | 1
| Lugo | 172374 | 130196 | 302570 | Lugo | 172374 | 130196 | 302570 | 0.23 | 43224 | 24625 | 18599 | 47 | 0.03% | 0.19% |  |  | Pisgah_Solar | Lugo | 35425.4841 | 18985.7466 | 326644 | 17% | 8% | 10% | 88% | 56% | 91% | 22% | - | - | - | 87484 | 166228 | 253712 | 56% | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | Westlands_Solar | 0 | 0 | 0 | 0 | 1 | 1
| Pisgah | 33413 | 60109 | 93523 | Pisgah | 33413 | 60109 | 93523 | 0.07 | 13360 | 4773 | 8587 | 14 | 0.01% | 0.3% |  |  | Pisgah_Solar | Pisgah | 19965.7518 | 42547.0444 | 96744 | 65% | 8% | 15% | 43% | 43% | 38% | 2% | - | - | - | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (blank) | 2 | 2 | 0 | 2 | 3 | 2
[8 empty] | 1297125 |  |  |  |  | 201 | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pisgah_Solar | 0 | 0 | 0 | 0 | 1 | 1
| GreaterImpOutsideTxConstraintZones | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Grand Total | 2 | 2 | 0 | 2
| Batiquitos | 157633 | 47688 | 205321 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Calpeak Power Enterprise 7 | 202401 | 121913 | 324314 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Doublett | 80436 | 44592 | 125028 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Elliott | 45307 | 46729 | 92036 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Encina | 126454 | 24920 | 151374 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Escondido | 203431 | 121928 | 325359 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fashion Valley | 28282 | 16983 | 45265 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Friars | 30269 | 20371 | 50640 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Main St. | 8747 | 7667 | 16414 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mesa Rim | 74254 | 55527 | 129781 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mission | 32441 | 23993 | 56434 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| North City West | 96479 | 49202 | 145681 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Old Town | 25583 | 12290 | 37873 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Palomar Airport | 143556 | 37740 | 181296 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Penasquitos | 81522 | 44598 | 126120 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| San Luis Rey | 133893 | 33714 | 167606 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| San Onofre | 23573 | 62718 | 86290 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Shadowridge | 174758 | 56678 | 231437 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Silvergate | 8282 | 7914 | 16196 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sycamore Canyon | 81712 | 110788 | 192500 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| KramerInyoOutsideTxConstraintZones | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chino | 115236 | 34278 | 149514 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Etiwanda | 119521 | 34144 | 153665 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mira Loma | 153868 | 44777 | 198645 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Padua | 103281 | 37944 | 141225 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rancho Vista | 117869 | 35516 | 153385 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| San Bernardino | 109190 | 93582 | 202772 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Soquel | 112556 | 38097 | 150654 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Vista | 154339 | 71821 | 226161 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Norcal_Z3_SacramentoRiver |  |  |  | Norcal_Z3_SacramentoRiver | [11 empty] | 493 | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Carberry | 63074 | 243738 | 306812 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Delevan | 226931 | 151233 | 378165 | Delevan | 226931 | 151233 | 378165 | 0.19 | 54024 | 32419 | 21605 | 92 | 0.17% | 0.28% |  |  | Sacramento_River_Solar | Delevan | 51195.299 | 81012.1767 | 390084 | 34% | 33% | 10% | 40% | 17% | 27% | 16% | 51111 | 11% | 14 | 111549 | - | 111562 | 25% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Glenn | 312380 | 98005 | 410385 | Glenn | 312380 | 98005 | 410385 | 0.2 | 58626 | 44626 | 14001 | 100 | 0.17% | 0.22% |  |  | Sacramento_River_Solar | Glenn | 44210.1698 | 12672.6095 | 422866 | 13% | 14% | 14% | 13% | 15% | 19% | 11% | 17528 | 4% | 6 | 1755 | - | 1760 | 0.4% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hat Creek 2 | 136010 | 217546 | 353557 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Palermo | 214738 | 187412 | 402150 | Palermo | 214738 | 187412 | 402150 | 0.2 | 57450 | 30677 | 26773 | 98 | 0.17% | 0.32% |  |  | Sacramento_River_Solar | Palermo | 88571.0985 | 38264.9217 | 469932 | 27% | 23% | 25% | 41% | 24% | 52% | 27% |  |  | 11 | 138134 | 63268 | 201412 | 45% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pit 1 | 141777 | 214370 | 356147 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pit 1 Ph | 141555 | 215093 | 356648 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rio Oso | 390291 | 40334 | 430625 | Rio Oso | 390291 | 40334 | 430625 | 0.21 | 61518 | 55756 | 5762 | 105 | 0.17% | 0.19% |  |  | Sacramento_River_Solar | Rio Oso | 14098.6044 | 8689.4185 | 453203 | 5% | 3% | 3% | 33% | 8% | 30% | 2% | 11502 | 3% | - | 32235 | - | 32235 | 7% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Table Mt. | 240287 | 158423 | 398711 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Thermalito | 249280 | 157779 | 407058 | Thermalito | 249280 | 157779 | 407058 | 0.2 | 58151 | 35611 | 22540 | 99 | 0.17% | 0.28% |  |  | Sacramento_River_Solar | Thermalito | 65448.8538 | 33637.056 | 480893 | 21% | 18% | 20% | 56% | 30% | 46% | 32% | 11393 | 3% | 11 | 105934 | 38032 | 143977 | 32% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 2028383 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Norcal_Z4_Solano |  |  |  | Norcal_Z4_Solano | [11 empty] | 622 | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Amerigas | 260414 | 114395 | 374808 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bear Canyon | 117353 | 203394 | 320747 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Big Geysers | 130673 | 197242 | 327915 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Calistoga 19 | 139609 | 188704 | 328314 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Calpeak Power Vaca Dixon 1 | 262551 | 111983 | 374534 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Castro Valley | 46179 | 79407 | 125586 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cayetano | 116508 | 230435 | 346943 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cobb Creek | 146233 | 181413 | 327646 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Contra Costa | 200922 | 142150 | 343072 | Contra Costa | 200922 | 142150 | 343072 | 0.25 | 49010 | 28703 | 20307 | 156 | 0.08% | 0.54% |  |  | Solano_Solar | Contra Costa | 44886.2518 | 8693.227 | 577525 | 9% | 30% | 1% | 57% | 80% | 44% | 46% | 178426 | 39% | 6 | 65700 | 46540 | 112246 | 25% | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
| Contra Costa Power | 210000 | 136983 | 346983 | [13 empty] | Solano_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fulton | 167498 | 182136 | 349634 | Fulton | 167498 | 182136 | 349634 | 0.26 | 49948 | 23928 | 26019 | 159 | 0.08% | 0.66% |  |  | Solano_Solar | Fulton | 113420.279 | 51698.6453 | 492897 | 33% | 2% | 7% | 79% | 70% | 23% | 75% |  |  | 18 | 85250 | 206860 | 292127 | 65% | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fumarole | 143276 | 186187 | 329463 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Geysers Unit 3 | 143689 | 184448 | 328137 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Grant 20 | 139259 | 192919 | 332177 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lake View | 156924 | 171486 | 328410 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lakeville | 154619 | 185621 | 340241 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lambie Energy | 239213 | 117481 | 356694 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lone Tree | 189538 | 155954 | 345491 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mccabe | 143114 | 185477 | 328591 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N.N. | 449207 | 549785 | 998991 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ncpa 1 & 2 | 123947 | 205474 | 329421 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ncpa 3 & 4 | 121200 | 206076 | 327276 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Oakmont North | 172006 | 168015 | 340021 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Oakmont South | 178163 | 164286 | 342449 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Peabody | 208221 | 151124 | 359345 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Quicksilver | 124619 | 201651 | 326270 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| San Ramon | 59665 | 164537 | 224202 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| San Ramon Research Cntr. | 58453 | 139042 | 197495 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Shiloh II | 225035 | 123667 | 348702 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Shiloh III | 223956 | 124121 | 348077 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Socrates 18 | 135800 | 198058 | 333858 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sonoma 3 | 141347 | 188617 | 329964 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sulphur Springs | 139885 | 191618 | 331503 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tassajara | 84879 | 164187 | 249066 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Technical Ecological Services | 58453 | 138968 | 197421 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Trans Bay Cable | 169698 | 134040 | 303738 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tulucay | 167011 | 134030 | 301040 | Tulucay | 167011 | 134030 | 301040 | 0.22 | 43006 | 23859 | 19147 | 137 | 0.07% | 0.57% |  |  | Solano_Solar | Tulucay | 69006.0487 | 47352.8037 | 401927 | 29% | 13% | 17% | 36% | 41% | 15% | 70% | 103190 | 23% | 24 | 124783 | 28295 | 153102 | 34% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Vaca-Dixon & Gc Yard | 259968 | 113943 | 373910 | Vaca-Dixon & Gc Yard | 259968 | 113943 | 373910 | 0.27 | 53416 | 37138 | 16278 | 170 | 0.09% | 0.46% |  |  | Solano_Solar | Vaca-Dixon & Gc Yard | 51167.8064 | 30002.4215 | 486714 | 17% | 15% | 7% | 38% | 39% | 49% | 37% | 72634 | 16% | 54 | 113094 | - | 113148 | 25% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| West Ford Flat | 132006 | 192813 | 324820 |  |  |  | 1367657 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Norcal_Z4_Solano_subzone | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bahia | 89718 | 122146 | 211863 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Embarcadero (Sf Z) | 11282 | 9587 | 20869 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ignacio | 97444 | 129759 | 227203 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Moraga | 39757 | 50910 | 90667 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Parkway | 130355 | 119288 | 249643 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pittsburg | 142317 | 145504 | 287821 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rossmoor | 57401 | 90527 | 147928 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sobrante | 34876 | 49389 | 84265 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tidewater | 69223 | 127137 | 196360 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unocal | 88845 | 87790 | 176635 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NorCalOutsideTxConstraintZones |  |  |  | NorCalOutsideTxConstraintZones | [11 empty] | 397 | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Brighton | 191632 | 60092 | 251724 | Brighton | 191632 | 60092 | 251724 | 0.39 | 35961 | 27376 | 8585 | 156 | 0.28% | 0.57% |  |  | Northern_California_Ex_Solar | Brighton | 12542.1839 | 6656.611 | 270547 | 7% | 13% | 6% | 53% | 44% | 58% | 18% | 72594 | 16% | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Gold Hill | 129525 | 192148 | 321673 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Jefferson | 7654 | 89704 | 97358 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Logan Creek | 250598 | 139780 | 390378 | Logan Creek | 250598 | 139780 | 390378 | 0.61 | 55768 | 35800 | 19969 | 241 | 0.26% | 0.67% |  |  | Northern_California_Ex_Solar | Logan Creek | 69148.2162 | 65087.8819 | 410633 | 33% | 33% | 14% | 15% | 12% | 14% | 4% | 27072 | 6% | 32 | 63683 | - | 63715 | 14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Martin | 5970 | 14050 | 20020 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| San Mateo | 9079 | 37974 | 47053 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 642102 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SCADOutsideTxConstraintZones | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cima | - | 8101 | 8101 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SCADSNV_Z1_EldoradoAndMtnPass | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ElDorado | - | - | - | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SCADSNV_Z3_GreaterImperial |  |  |  | SCADSNV_Z3_GreaterImperial | [11 empty] | 1148 | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| East County | 11025 | 96156 | 107180 | East County | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Imperial Valley | 207772 | 25483 | 233255 | Imperial Valley | 207772 | 25483 | 233255 | 0.61 | 33322 | 29682 | 3640 | 698 | 1.27% | 2.35% |  |  | Greater_Imperial_Solar | Imperial Valley | 16371.6201 | 21146.4397 | 239781 | 16% | 4% | 4% | 22% | 22% | 72% | 7% | 168195 | 56% | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ocotillo Express | 38327 | 112107 | 150434 | Ocotillo Express | 38327 | 112107 | 150434 | 0.39 | 21491 | 5475 | 16015 | 450 | 0.82% | 8.22% |  |  | Greater_Imperial_Solar | Ocotillo Express | 50579.2763 | 41549.0601 | 158933 | 58% | 34% | 42% | 25% | 39% | 16% | 34% | 1308 | 0.3% | - | 48460 | 78 | 48538 | 11% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Suncrest | 14209 | 224326 | 238534 | Suncrest | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Total |  |  | 383689 |  | 54813 | 35157 | 19656 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SCADSNV_Z4_RiversideAndPalmSprings |  |  |  | SCADSNV_Z4_RiversideAndPalmSprings | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Colorado River | 121669 | 200351 | 322021 | Colorado River | 121669 | 200351 | 322021 | [9 empty] | Riverside_Palm_Springs_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Red Bluff | 51720 | 112348 | 164067 | Red Bluff | 51720 | 112348 | 164067 | [9 empty] | Riverside_Palm_Springs_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 486088 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SCADSNV_Z5_SCADSNV | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capacitor | 18968 | 48995 | 67963 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Eagle Mt. | 47355 | 84479 | 131834 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Iron Mt. | 32233 | 161416 | 193650 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Julian Hinds | 9794 | 39712 | 49506 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Los Coches | 45300 | 141878 | 187178 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Miguel | 11515 | 58209 | 69725 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mohave | 252 | 5823 | 6075 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Otay Mesa | 7815 | 59710 | 67525 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| South Bay | 7192 | 12577 | 19769 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SPGE_Z1_Westlands |  |  |  | SPGE_Z1_Westlands | [11 empty] | 443 | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ashlan Ave. | 339742 | 55626 | 395368 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fig Garden | 325840 | 67856 | 393696 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Gates | 244790 | 61943 | 306734 | Gates | 244790 | 61943 | 306734 | 0.14 | 43819 | 34970 | 8849 | 64 | 0.15% | 0.18% |  |  | Westlands_Solar | Gates | 19172.797 | 6084.4336 | 316899 | 8% | 10% | 12% | 26% | 28% | 11% | 14% | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Gregg | 317053 | 74590 | 391644 | [13 empty] | Westlands_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Helm | 351333 | 7887 | 359220 | Helm | 351333 | 7887 | 359220 | 0.17 | 51317 | 50190 | 1127 | 75 | 0.15% | 0.15% |  |  | Westlands_Solar | Helm | 247.1054 | 0 | 409866 | 0% | 1% | 0% | 22% | 15% | 27% | 15% | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Henrietta | 332147 | - | 332147 | Henrietta | 332147 | - | 332147 | 0.16 | 47450 | 47450 | - | 69 | 0.15% | 0.15% |  |  | Westlands_Solar | Henrietta | 0 | 0 | 345015 | 0% | 0% | 0% | 12% | 8% | 17% | 3% | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Herndon | 323716 | 66266 | 389982 | [13 empty] | Westlands_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kearney (New) | 371486 | 61 | 371547 | [13 empty] | Westlands_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Los Banos | 114226 | 174190 | 288416 | [13 empty] | Westlands_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mc Call | 409347 | 5918 | 415265 | Mc Call | 409347 | 5918 | 415265 | 0.2 | 59324 | 58478 | 845 | 87 | 0.15% | 0.15% |  |  | Westlands_Solar | Mc Call | 957.8942 | 203.4955 | 482590 | 0% | 0% | 0% | 6% | 3% | 38% | 3% | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mc Mullin | 386506 | 648 | 387154 | Mc Mullin | 386506 | 648 | 387154 | 0.18 | 55308 | 55215 | 93 | 81 | 0.15% | 0.15% |  |  | Westlands_Solar | Mc Mullin | 0 | 0 | 460177 | 0% | 1% | 0% | 11% | 5% | 27% | 9% | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Oxford | 161974 | 150132 | 312106 | [13 empty] | Westlands_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Panoche | 208837 | 117291 | 326128 | Panoche | 208837 | 117291 | 326128 | 0.15 | 46590 | 29834 | 16756 | 68 | 0.15% | 0.23% |  |  | Westlands_Solar | Panoche | 41908.7178 | 54263.3679 | 354129 | 27% | 25% | 27% | 38% | 40% | 18% | 33% |  |  | - | 4 | - | 4 | 0.001% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| San Luis | 108749 | 201483 | 310232 | [13 empty] | Westlands_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| San Luis 3 | 195956 | 128527 | 324483 | Total | 1932960 | 193688 | 2126648 |  | 303807 | 276137 | 27670 | 443 |  |  |  |  | Westlands_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| San Luis 5 | 173321 | 138035 | 311356 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wright | 138417 | 143289 | 281706 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SPGE_Z2_KernAndGreaterCarrizo |  |  |  | SPGE_Z2_KernAndGreaterCarrizo | [11 empty] | 801 | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Arco | 273895 | 115185 | 389080 | Arco | 273895 | 115185 | 389080 | 0.21 | 55583 | 39128 | 16455 | 165 | 0.06% | 0.42% |  |  | Kern_Greater_Carrizo_Solar | Arco | 32458.9861 | 11374.1407 | 401584 | 11% | 31% | 18% | 26% | 21% | 19% | 11% | 92845 | 21% | - | 11383 | - | 11383 | 3% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Buena Vista Pumps | 210938 | 156404 | 367342 | Buena Vista Pumps | [12 empty] | Kern_Greater_Carrizo_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kern Power | 316544 | 76164 | 392707 | Kern Power | [12 empty] | Kern_Greater_Carrizo_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Midway | 275516 | 100733 | 376249 | Midway | 275516 | 100733 | 376249 | 0.2 | 53750 | 39359 | 14390 | 160 | 0.06% | 0.41% |  |  | Kern_Greater_Carrizo_Solar | Midway | 11830.8569 | 0 | 420674 | 3% | 13% | 7% | 72% | 72% | 22% | 61% | 103361 | 23% | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Renfro | 318206 | 68186 | 386392 | Renfro | 318206 | 68186 | 386392 | 0.2 | 55199 | 45458 | 9741 | 164 | 0.06% | 0.36% |  |  | Kern_Greater_Carrizo_Solar | Renfro | 12637.4596 | 0 | 463397 | 3% | 3% | 2% | 50% | 45% | 28% | 34% | 63203 | 14% | - | 689 | - | 689 | 0.2% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Stockdale | 329571 | 58200 | 387771 | Stockdale | 329571 | 58200 | 387771 | 0.21 | 55396 | 47082 | 8314 | 165 | 0.06% | 0.35% |  |  | Kern_Greater_Carrizo_Solar | Stockdale | 10024.6916 | 0 | 471591 | 2% | 2% | 2% | 51% | 42% | 35% | 31% | 58531 | 13% | - | 569 | - | 569 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wheeler Ridge | 238850 | 108140 | 346990 | Wheeler Ridge | 238850 | 108140 | 346990 | 0.18 | 49570 | 34121 | 15449 | 147 | 0.05% | 0.43% |  |  | Kern_Greater_Carrizo_Solar | Wheeler Ridge | 48498.2819 | 11956.8974 | 403802 | 15% | 18% | 18% | 44% | 37% | 36% | 25% | 100625 | 22% | 34 | 42668 | - | 42702 | 9% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Total | 1436038 | 450445 | 1886482 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SPGE_Z3_Carrizo | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Caliente | 153857 | 222593 | 376449 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mesa | 183463 | 152282 | 335745 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Solar | 129613 | 260323 | 389936 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Templeton | 246398 | 178427 | 424825 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SPGE_Z4_CentralValleyAndLosBanos | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bellota | 255520 | 190399 | 445919 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cottle | 244115 | 184778 | 428893 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Eight Mile | 361385 | 26159 | 387544 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Stagg | 361484 | 19363 | 380846 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Storey | 293286 | 148690 | 441976 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Weber | 390024 | 7132 | 397157 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wilson | 221461 | 144010 | 365471 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tehachapi |  |  |  | Tehachapi | [11 empty] | 4656 | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Antelope | 283495 | 91598 | 375092 | Antelope | 283495 | 91598 | 375092 | 0.27 | 53585 | 40499 | 13085 | 1240 | 2.31% | 3.06% |  |  | Tehachapi_Solar | Antelope | 57483.2355 | 17818.6781 | 452328 | 17% | 7% | 6% | 68% | 30% | 75% | 22% | 182681 | 40% | - | 33809 | 164964 | 198774 | 44% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Arbwind | 187469 | 131236 | 318705 | Arbwind | [12 empty] | Tehachapi_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bailey | 51085 | 172594 | 223678 | Bailey | [12 empty] | Tehachapi_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Highwind | 177593 | 122671 | 300264 | Highwind | [12 empty] | Tehachapi_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mojave 17 | 219898 | 123483 | 343381 | Mojave 17 | [12 empty] | Tehachapi_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N.N. | 449207 | 549785 | 998991 | N.N. | [12 empty] | Tehachapi_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pardee | 103541 | 134265 | 237806 | Pardee | [12 empty] | Tehachapi_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pearblossom | 161231 | 175860 | 337091 | Pearblossom |  |  |  | - | - | - | - | - |  |  |  |  | Tehachapi_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Saugus | 104149 | 130389 | 234538 | Saugus | [12 empty] | Tehachapi_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sky River North | 42559 | 138617 | 181177 | Sky River North | [12 empty] | Tehachapi_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Vincent | 184409 | 117262 | 301671 | Vincent | 184409 | 117262 | 301671 | 0.21 | 43096 | 26344 | 16752 | 998 | 2.31% | 3.3% |  |  | Tehachapi_Solar | Vincent |  |  | 331801 | 30% | 19% | 8% | 54% | 37% | 64% | 23% | 18653 | 4% | 36 | 15643 | 307931 | 323610 | 72% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Warne | 33576 | 158596 | 192172 | Warne | [12 empty] | Tehachapi_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Westwind | 219617 | 124770 | 344387 | Westwind | [12 empty] | Tehachapi_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Whirlwind | 242519 | 141802 | 384321 | Whirlwind | 242519 | 141802 | 384321 | 0.27 | 54903 | 34646 | 20257 | 1271 | 2.31% | 3.67% |  |  | Tehachapi_Solar | Whirlwind | 73010.2351 | 40426.1201 | 489686 | 23% | 12% | 10% | 73% | 30% | 89% | 21% | 261700 | 58% | 17 | 212330 | 28822 | 241169 | 53% | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
| Winderness | 224940 | 119400 | 344340 | Winderness | [12 empty] | Tehachapi_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Windhub | 224364 | 122565 | 346929 | Windhub | 224364 | 122565 | 346929 | 0.25 | 49561 | 32052 | 17509 | 1147 | 2.31% | 3.58% |  |  | Tehachapi_Solar | Windhub | 81311.2708 | 31850.2971 | 461897 | 24% | 3% | 4% | 59% | 37% | 77% | 22% | 97244 | 22% | - | 157667 | 19976 | 177642 | 39% | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
[5 empty] | Total | 934786 | 473227 | 1408013 |  |  |  |  | 4656 | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TehachapiOutsideTxConstraintZones | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Airchem | - | - | - | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Arcogen | - | - | - | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cameron | - | - | - | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Casitas | 105111 | 55297 | 160408 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Center | 835 | - | 835 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chevmain | - | - | - | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Del Amo | - | - | - | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Eagle Rock | 90 | 20648 | 20738 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| El Nido | - | - | - | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| El Segundo | - | 3 | 3 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Federalgen | - | - | - | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Goodrich | 90 | 23212 | 23303 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Gould | 3647 | 48488 | 52135 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Harborgen | - | - | - | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hinson | - | - | - | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kinetic | - | - | - | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| La Cienega | 60 | 3 | 64 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| La Fresa | - | - | - | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Laguna Bell | - | - | - | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lawndale | - | - | - | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lighthipe | - | - | - | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mandalay | 121908 | 24739 | 146647 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mesa | 183463 | 152282 | 335745 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Moorpark | 175850 | 76092 | 251941 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N.N. | 449207 | 549785 | 998991 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Olinda | 28973 | 12098 | 41071 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ormond Beach | 110407 | 14885 | 125292 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Redondo 1 | - | - | - | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Repro | - | - | - | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rio Hondo | 18154 | 19395 | 37550 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rosecrans | - | - | - | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Santa Clara | 176305 | 44572 | 220877 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Stadium | - | - | - | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Stanhill | - | - | - | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tahiti | 60 | 13 | 74 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Venice Hydro | 60 | 8 | 69 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Walnut | 26759 | 8356 | 35115 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Windsor Hills | - | - | - | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WestlandsOutsideTxConstraintZones |  |  |  | WestlandsOutsideTxConstraintZones | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Coburn | 162721 | 218557 | 381278 | Coburn | 162721 | 218557 | 381278 | [9 empty] | Westlands_Ex_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Diablo Canyon | 52516 | 78415 | 130931 | Diablo Canyon | 52516 | 78415 | 130931 | [9 empty] | Westlands_Ex_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Goleta | 50794 | 53729 | 104523 | Goleta | 50794 | 53729 | 104523 | [9 empty] | Westlands_Ex_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 616732 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Grand Total | 28058029 | 21760032 | 49818061 | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Mountain_Pass_El_Dorado _Solar | [11 empty] | 248 | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | El Dorado 230kV | [7 empty] | 83 |  |  |  |  | Mountain_Pass_El_Dorado_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | El Dorado 500kV | [7 empty] | 165 |  |  |  |  | Mountain_Pass_El_Dorado_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | El Dorado |  |  | 42263 | 1 | 6038 |  |  | 248 | 4.11% |  |  |  | Mountain_Pass_El_Dorado_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Southern_Nevada_Solar | BLM Variance Lands | [9 empty] | 182 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Crazy Eyes |  |  | 155787 | 0.61 | 22255 |  |  | 111 | 0.5% | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Desert View |  |  | 42719 | 0.17 | 6103 |  |  | 31 | 0.51% | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Innovation |  |  | 54904 | 0.22 | 7843 |  |  | 40 | 0.51% | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Eldorado |  |  | 42263 | 1 | 6038 |  |  |  | 0% | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Mohave 500kV | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 182 | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Southern_Nevada_Solar | WGA CHAT | [30 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1
[5 empty] | Crazy Eyes | 76564 | 375691 | 452256 | 0.61 | 64608 |  |  | 111 | 0.17% | 1.02% |  |  | Southern_Nevada_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Desert View | 35392 | 416874 | 452266 | 0.17 | 64609 |  |  | 31 | 0.05% | 0.61% |  |  | Southern_Nevada_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Innovation | 145066 | 307201 | 452267 | 0.22 | 64610 |  |  | 40 | 0.06% | 0.19% |  |  | Southern_Nevada_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Eldorado | 3200 | 449067 | 452267 | 1 | 64610 |  |  |  | 0% | 0% |  |  | Southern_Nevada_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Mohave 500kV | 214514 | 227477 | 441990 | 1 | 63141 |  |  |  | 0% | 0% | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 182 | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SCADSNV_Solar | BLM Variance Lands | [9 empty] | 740 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Mohave 500kV |  |  | 28764 | 1 | 4109 |  |  | 740 | 18.01% |  |  |  | SCADSNV_Solar | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SCADSNV_Solar | WGA CHAT | [30 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1
[5 empty] | Mohave 500kV | 214514 | 227477 | 441990 | 1 | 63141 |  |  | 740 | 1.17% | 2.41% |  |  | SCADSNV_Solar

## 4_CommercialInterest
What constitutes level 3 criteria flag? |  | 300 | MW | Model selection 300 MW or more, in absence of any commercial interest
|  | 3000 | MW | Difference from commercial interest
What constitutes level 2 criteria flag? |  | 2000 | MW or greater | Difference from commercial interest
What constitutes level 1 criteria flag? |  | All other
| Summary of Commercial Interest (Interconnection Queue / Zones) | Row Labels | Sum of MW-1 |  | Summary of RESOLVE Selected Portfolio | Selected by RESOLVE | RESOLVE Portfolio (adj) | Zone | Technology | Commercial Interest (queue), Summarized by RESOLVE Resource | Difference (RESOLVE Portfolio) - (Commercial Interest) | Selected Portfolio, as Percent of Queue | Boolean: significant model selection in absence of commercial interest | Mapping criteria compliance flag | Difference (Adjusted Selected Portfolio) - (Commercial Interest) | Selected Portfolio, as Percent of Queue | Boolean: significant model selection in absence of commercial interest | Mapping criteria compliance flag | LSE Plans⁵
| "0" Zone | 0 | 3314.665 |  | InState_Biomass | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 | [5 empty] | 0
| "0" Zone | Photovoltaic | 485.875 |  | Greater_Imperial_Geothermal | 0 | 0 | SCADSNV_Z3_GreaterImperial | Geothermal | 102.2804 | -102.2804 | 0% | 0 | 1 | -102.2804 | 0% | 0 | 1 | 102.2804
| "0" Zone | Storage | 2090.97 |  | Inyokern_North_Kramer_Geothermal | 0 | 0 | GK_Z2_InyokernAndNorthOfKramer |  | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0
| "0" Zone | Wind Turbine | 737.82 |  | Northern_California_Ex_Geothermal | 0 | 0 | NorCalOutsideTxConstraintZones | Geothermal | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0
| Blank Zone |  | 23918.4361 |  | Pacific_Northwest_Geothermal | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0 |  | 0
| Blank Zone | Combined Cycle | 717.07 |  | Riverside_Palm_Springs_Geothermal | 0 | 0 | SCADSNV_Z4_RiversideAndPalmSprings | Geothermal | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0
| Blank Zone | Photovoltaic | 3292.3221 |  | Solano_Geothermal | 105 | 105 | Norcal_Z4_Solano | Geothermal | 0 | 105 | No commercial interest; 105 MW selected | 0 | 1 | 105 | No commercial interest; 105 MW selected | 0 | 1 | 0
| Blank Zone | Solar Thermal | 103.455 |  | Southern_Nevada_Geothermal | 0 | 0 | SCADSNV_Z1_EldoradoAndMtnPass |  | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0
| Blank Zone | Storage | 13012.3441 |  | Carrizo_Solar | 0 | 0 | SPGE_Z3_Carrizo | Photovoltaic | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0
| Blank Zone | Wind Turbine | 6793.245 |  | Carrizo_Wind | 287 | 287 | SPGE_Z3_Carrizo | Wind Turbine | 0 | 287 | No commercial interest; 287 MW selected | 0 | 1 | 287 | No commercial interest; 287 MW selected | 0 | 1 | 0
| GK_Z1_GreaterKramer | GK_Z1_GreaterKramer | 361.14 |  | Central_Valley_North_Los_Banos_Solar | 0 | 0 | SPGE_Z4_CentralValleyAndLosBanos | Photovoltaic | 248.35 | -248.35 | 0% | 0 | 1 | -248.35 | 0% | 0 | 1 | 0
| GK_Z1_GreaterKramer | Photovoltaic | 148.96 |  | Central_Valley_North_Los_Banos_Wind | 173 | 173 | SPGE_Z4_CentralValleyAndLosBanos | Wind Turbine | 0 | 173 | No commercial interest; 173 MW selected | 0 | 1 | 173 | No commercial interest; 173 MW selected | 0 | 1 | 0
| GK_Z1_GreaterKramer | Wind Turbine | 212.18 |  | Distributed_Solar | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0 |  | 3
| GK_Z2_InyokernAndNorthOfKramer | GK_Z2_InyokernAndNorthOfKramer | 1126 |  | Distributed_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0 |  | 0
| GK_Z2_InyokernAndNorthOfKramer | Photovoltaic | 852.74 |  | Greater_Imperial_Solar | 548 | 1148 | SCADSNV_Z3_GreaterImperial | Photovoltaic | 2106.66 | -1558.66 | 26.01% | 0 | 1 | -958.66 | 54.49% | 0 | 1 | 0
| GK_Z2_InyokernAndNorthOfKramer | Storage | 273.26 |  | Greater_Imperial_Wind | 0 | 0 | SCADSNV_Z3_GreaterImperial | Wind Turbine | 1502.3 | -1502.3 | 0% | 0 | 1 | -1502.3 | 0% | 0 | 1 | 17.5381
| GK_Z3_NorthOfVictor | GK_Z3_NorthOfVictor | 320.92 |  | Greater_Kramer_Wind | 0 | 0 | GK_Z1_GreaterKramer | Wind Turbine | 212.18 | -212.18 | 0% | 0 | 1 | -212.18 | 0% | 0 | 1 | 0
| GK_Z3_NorthOfVictor | Photovoltaic | 210.88 |  | Humboldt_Wind | 34 | 34 | Norcal_Z2_Humboldt | Wind Turbine | 259.125 | -225.125 | 13.12% | 0 | 1 | -225.125 | 13.12% | 0 | 1 | 116.0943
| GK_Z3_NorthOfVictor | Storage | 110.04 |  | Inyokern_North_Kramer_Solar | 0 | 0 | GK_Z2_InyokernAndNorthOfKramer | Photovoltaic | 852.74 | -852.74 | 0% | 0 | 1 | -852.74 | 0% | 0 | 1 | 23.1583
| GK_Z4_Pisgah | GK_Z4_Pisgah | 302.85 |  | Kern_Greater_Carrizo_Solar | 801.32 | 801.32 | SPGE_Z2_KernAndGreaterCarrizo | Photovoltaic | 1420.621 | -619.301 | 56.41% | 0 | 1 | -619.301 | 56.41% | 0 | 1 | 25.6
| GK_Z4_Pisgah | Photovoltaic | 302.85 |  | Kern_Greater_Carrizo_Wind | 20 | 20 | SPGE_Z2_KernAndGreaterCarrizo | Wind Turbine | 0 | 20 | No commercial interest; 20 MW selected | 0 | 1 | 20 | No commercial interest; 20 MW selected | 0 | 1 | 0
| GreaterImpOutsideTxConstraintZones | GreaterImpOutsideTxConstraintZones | 747.7 |  | Kramer_Inyokern_Ex_Solar | 0 | 0 | KramerInyoOutsideTxConstraintZones | Photovoltaic | 91 | -91 | 0% | 0 | 1 | -91 | 0% | 0 | 1 | 91
| GreaterImpOutsideTxConstraintZones | Storage | 747.7 |  | Kramer_Inyokern_Ex_Wind | 0 | 0 | KramerInyoOutsideTxConstraintZones | Wind Turbine | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0
| KramerInyoOutsideTxConstraintZones | KramerInyoOutsideTxConstraintZones | 100.98 |  | Mountain_Pass_El_Dorado_Solar | 248 | 248 | SCADSNV_Z1_EldoradoAndMtnPass | Photovoltaic | 300 | -52 | 82.67% | 0 | 1 | -52 | 82.67% | 0 | 1 | 0
| KramerInyoOutsideTxConstraintZones | Storage | 100.98 |  | North_Victor_Solar | 300 | 300 | GK_Z3_NorthOfVictor | Photovoltaic | 210.88 | 89.12 | 142.3% | 0 | 1 | 89.12 | 142.3% | 0 | 1 | 0
| None | None | 2101.66 |  | Northern_California_Ex_Solar | 397 | 0 | NorCalOutsideTxConstraintZones | Photovoltaic | 0 | 397 | No commercial interest; 397 MW selected | 1 | 3 | 0 | No commercial interest; 397 MW selected | 0 | 1 | 0
| None | Storage | 2101.66 |  | Northern_California_Ex_Wind | 767 | 767 | NorCalOutsideTxConstraintZones | Wind Turbine | 1774 | -1007 | 43.24% | 0 | 1 | -1007 | 43.24% | 0 | 1 | 140
| Norcal_Z2_Humboldt | Norcal_Z2_Humboldt | 259.125 |  | NW_Ext_Tx_Wind | 1500 | 1500 | Norcal_Z3_SacramentoRiver |  | 1500 | 0 | 100% | 0 | 1 | 0 | 100% | 0 | 1 | 0
| Norcal_Z2_Humboldt | Wind Turbine | 259.125 |  | Riverside_Palm_Springs_Solar | 0 | 0 | SCADSNV_Z4_RiversideAndPalmSprings | Photovoltaic | 4609.61 | -4609.61 | 0% | 0 | 3 | -4609.61 | 0% | 0 | 3 | 514.4848
| Norcal_Z3_SacramentoRiver | Norcal_Z3_SacramentoRiver | 522 |  | Riverside_Palm_Springs_Wind | 0 | 0 | SCADSNV_Z4_RiversideAndPalmSprings | Wind Turbine | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0
| Norcal_Z3_SacramentoRiver | Photovoltaic | 12 |  | Sacramento_River_Solar | 896 | 231 | Norcal_Z3_SacramentoRiver | Photovoltaic | 56 | 840 | 1600% | 0 | 1 | 175 | 412.5% | 0 | 1 | 56
| Norcal_Z3_SacramentoRiver | Storage | 510 |  | Sacramento_River_Wind | 0 | 0 | Norcal_Z3_SacramentoRiver | Wind Turbine | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0
| Norcal_Z4_Solano | Norcal_Z4_Solano | 1486.304 |  | SCADSNV_Solar | 330 | 740 | SCADSNV_Z5_SCADSNV | Photovoltaic | 1800.104 | -1470.104 | 18.33% | 0 | 1 | -1060.104 | 41.11% | 0 | 1 | 0
| Norcal_Z4_Solano | Photovoltaic | 275.9 |  | SCADSNV_Wind | 0 | 0 | SCADSNV_Z5_SCADSNV | Wind Turbine | 310 | -310 | 0% | 0 | 1 | -310 | 0% | 0 | 1 | 0
| Norcal_Z4_Solano | Storage | 569.5 |  | Solano_Solar | 622 | 622 | Norcal_Z4_Solano | Photovoltaic | 275.9 | 346.1 | 225.4% | 0 | 1 | 346.1 | 225.4% | 0 | 1 | 27.18
| Norcal_Z4_Solano | Wind Turbine | 640.904 |  | Solano_subzone_Solar | 0 | 0 | Norcal_Z4_Solano_subzone | Photovoltaic | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0
| Norcal_Z4_Solano_subzone | Norcal_Z4_Solano_subzone | 20 |  | Solano_subzone_Wind | 0 | 0 | Norcal_Z4_Solano_subzone | Wind Turbine | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0
| Norcal_Z4_Solano_subzone | Storage | 20 |  | Solano_Wind | 462 | 462 | Norcal_Z4_Solano | Wind Turbine | 640.904 | -178.904 | 72.09% | 0 | 1 | -178.904 | 72.09% | 0 | 1 | 25
| NorCalOutsideTxConstraintZones | NorCalOutsideTxConstraintZones | 1837.75 |  | Southern_California_Desert_Ex_Solar | 862 | 0 | SCADOutsideTxConstraintZones | Photovoltaic | 475 | 387 | 181.5% | 0 | 1 | -475 | 0% | 0 | 1 | 475
| NorCalOutsideTxConstraintZones | Hydro | 5 |  | Southern_California_Desert_Ex_Wind | 0 | 0 | SCADOutsideTxConstraintZones | Wind Turbine | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0
| NorCalOutsideTxConstraintZones | Storage | 58.75 |  | Southern_Nevada_Solar | 0 | 182 | SCADSNV_Z2_GLW_VEA | Photovoltaic | 2325 | -2325 | 0% | 0 | 2 | -2143 | 7.828% | 0 | 2 | 0
| NorCalOutsideTxConstraintZones | Wind Turbine | 1774 |  | Southern_Nevada_Wind | 442 | 442 | SCADSNV_Z2_GLW_VEA |  | 2000 | -1558 | 22.1% | 0 | 1 | -1558 | 22.1% | 0 | 1 | 2000
| Outside | Outside | 1482.6 |  | SW_Ext_Tx_Wind | 500 | 500 | SCADSNV_Z4_RiversideAndPalmSprings |  | 0 | 500 | No commercial interest; 500 MW selected | 1 | 3 | 500 | No commercial interest; 500 MW selected | 1 | 3 | 0
| Outside | Storage | 1482.6 |  | Tehachapi_Solar | 4656 | 5676 | Tehachapi | Photovoltaic | 4116.798 | 539.202 | 113.1% | 0 | 1 | 1559.202 | 137.9% | 0 | 1 | 0
| SCADSNV_Z1_EldoradoAndMtnPass | SCADSNV_Z1_EldoradoAndMtnPass | 300 |  | Tehachapi_Ex_Solar | 0 | 0 | TehachapiOutsideTxConstraintZones | Photovoltaic | 388 | -388 | 0% | 0 | 1 | -388 | 0% | 0 | 1 | 388
| SCADSNV_Z1_EldoradoAndMtnPass | Photovoltaic | 300 |  | Tehachapi_Wind | 275 | 275 | Tehachapi | Wind Turbine | 1086.26 | -811.26 | 25.32% | 0 | 1 | -811.26 | 25.32% | 0 | 1 | 0
| SCADSNV_Z3_GreaterImperial | SCADSNV_Z3_GreaterImperial | 5750.49 |  | Westlands_Ex_Solar | 1779 | 0 | WestlandsOutsideTxConstraintZones | Photovoltaic | 0 | 1779 | No commercial interest; 1779 MW selected | 1 | 3 | 0 | No commercial interest; 1779 MW selected | 0 | 1 | 0
| SCADSNV_Z3_GreaterImperial | Photovoltaic | 2106.66 |  | Westlands_Ex_Wind | 0 | 0 | WestlandsOutsideTxConstraintZones | Wind Turbine | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0
| SCADSNV_Z3_GreaterImperial | Storage | 2141.53 |  | Westlands_Solar | 468 | 2088 | SPGE_Z4_CentralValleyAndLosBanos | Photovoltaic | 248.35 | 219.65 | 188.4% | 0 | 1 | 1839.65 | 840.7% | 0 | 1 | 0
| SCADSNV_Z3_GreaterImperial | Wind Turbine | 1502.3 |  | Cape_Mendocino_Offshore_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0 |  | 0
| SCADSNV_Z4_RiversideAndPalmSprings | SCADSNV_Z4_RiversideAndPalmSprings | 9897.4429 |  | Del_Norte_Offshore_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0 |  | 0
| SCADSNV_Z4_RiversideAndPalmSprings | Photovoltaic | 4609.61 |  | Diablo_Canyon_Offshore_Wind_Ext_Tx | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0 |  | 0
| SCADSNV_Z4_RiversideAndPalmSprings | Steam Turbine | 549.5 |  | Diablo_Canyon_Offshore_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0 |  | 0
| SCADSNV_Z4_RiversideAndPalmSprings | Storage | 4738.3329 |  | Humboldt_Bay_Offshore_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0 |  | 120
| SCADSNV_Z5_SCADSNV | SCADSNV_Z5_SCADSNV | 4736.144 |  | Morro_Bay_Offshore_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0 |  | 0
| SCADSNV_Z5_SCADSNV | Photovoltaic | 1800.104 |  | Utah_Solar | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0 |  | 0
| SCADSNV_Z5_SCADSNV | Storage | 2626.04 |  | Arizona_Solar | 1910 | 1580 | SCADSNV_Z4_RiversideAndPalmSprings | Photovoltaic | 3059 | -1149 | 62.44% | 0 | 1 | -1479 | 51.65% | 0 | 1 | 118.33
| SCADSNV_Z5_SCADSNV | Wind Turbine | 310 |  | New_Mexico_Solar | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0 |  | 0
| SPGE_Z1_Westlands | SPGE_Z1_Westlands | 6315.775 |  | Baja_California_Solar | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0 |  | 0
| SPGE_Z1_Westlands | Gas Turbine | 63 |  | Baja_California_Wind | 495 | 495 | SCADSNV_Z3_GreaterImperial | Wind Turbine | 1828 | -1333 | 27.08% | 0 | 1 | -1333 | 27.08% | 0 | 1 | 0
| SPGE_Z1_Westlands | Photovoltaic | 4778.535 |  | Pacific_Northwest_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0 |  | 18
| SPGE_Z1_Westlands | Storage | 1394.24 |  | Idaho_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0 |  | 0
| SPGE_Z1_Westlands | Wind Turbine | 80 |  | Utah_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0 |  | 0
| SPGE_Z2_KernAndGreaterCarrizo | SPGE_Z2_KernAndGreaterCarrizo | 2925.291 |  | Wyoming_Wind | 1500 | 1500 | SCADSNV_Z1_EldoradoAndMtnPass |  | 1500 | 0 | 100% | 0 | 1 | 0 | 100% | 0 | 1 | 0
| SPGE_Z2_KernAndGreaterCarrizo | Photovoltaic | 1420.621 |  | Arizona_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0 |  | 0
| SPGE_Z2_KernAndGreaterCarrizo | Storage | 1504.67 |  | New_Mexico_Wind | 1500 | 1500 | SCADSNV_Z4_RiversideAndPalmSprings | Wind Turbine | 1000 | 500 | 150% | 0 | 1 | 500 | 150% | 0 | 1 | 0
| SPGE_Z3_Carrizo | SPGE_Z3_Carrizo | 1855.99 |  | Pisgah_Solar | 0 | 200.5 | GK_Z4_Pisgah | Photovoltaic | 302.85 | -302.85 | 0% | 0 | 1 | -102.35 | 66.2% | 0 | 1 | 0
| SPGE_Z3_Carrizo | Storage | 1855.99 |  | Pumped Storage Hydro_GreaterImpOutsideTxConstraintZones | 0 | 500 | GreaterImpOutsideTxConstraintZones | Storage | 500 | -500 | 0% | 0 | 1 | 0 | 100% | 0 | 1 | 0
| SPGE_Z4_CentralValleyAndLosBanos | SPGE_Z4_CentralValleyAndLosBanos | 1064.986 |  | Pumped Storage Hydro_GreaterImpOutsideTxConstraintZones | 0 | 500 | GreaterImpOutsideTxConstraintZones | Storage | 500 | -500 | 0% | 0 | 1 | 0 | 100% | 0 | 1 | 0
| SPGE_Z4_CentralValleyAndLosBanos | Photovoltaic | 248.35 |  | Pumped Storage Hydro_SCADSNV_Z4_RiversideAndPalmSprings | 0 | 1343 | SCADSNV_Z4_RiversideAndPalmSprings | Storage | 1407 | -1407 | 0% | 0 | 1 | -64 | 95.45% | 0 | 1 | 0
| SPGE_Z4_CentralValleyAndLosBanos | Storage | 816.636 |  | BatteryStorage_GK_Z2_InyokernAndNorthOfKramer | 0 | 0 | GK_Z2_InyokernAndNorthOfKramer | Storage | 273.26 | -273.26 | 0% | 0 | 1 | -273.26 | 0% | 0 | 1 | 0
| Tehachapi | Tehachapi | 10409.6394 |  | BatteryStorage_GK_Z3_NorthOfVictor | 0 | 50 | GK_Z3_NorthOfVictor | Storage | 110.04 | -110.04 | 0% | 0 | 1 | -60.04 | 45.44% | 0 | 1 | 0
| Tehachapi | Photovoltaic | 4116.798 |  | BatteryStorage_GK_Z4_Pisgah | 0 | 126 | GK_Z4_Pisgah | Storage | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 126 | No commercial interest; 0 MW selected | 0 | 1 | 0
| Tehachapi | Storage | 5206.5814 |  | BatteryStorage_GreaterImpOutsideTxConstraintZones | 0 | 560 | GreaterImpOutsideTxConstraintZones | Storage | 747.7 | -747.7 | 0% | 0 | 1 | -187.7 | 74.9% | 0 | 1 | 0
| Tehachapi | Wind Turbine | 1086.26 |  | BatteryStorage_KramerInyoOutsideTxConstraintZones | 0 | 101 | KramerInyoOutsideTxConstraintZones | Storage | 100.98 | -100.98 | 0% | 0 | 1 | 0.02 | 100% | 0 | 1 | 0
| TehachapiOutsideTxConstraintZones | TehachapiOutsideTxConstraintZones | 2008.07 |  | BatteryStorage_Norcal_Z2_Humboldt | 0 | 0 | Norcal_Z2_Humboldt | Storage | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0
| TehachapiOutsideTxConstraintZones | Storage | 2008.07 |  | BatteryStorage_Norcal_Z3_SacramentoRiver | 0 | 0 | Norcal_Z3_SacramentoRiver | Storage | 510 | -510 | 0% | 0 | 1 | -510 | 0% | 0 | 1 | 0
[5 empty] | BatteryStorage_Norcal_Z4_Solano | 0 | 0 | Norcal_Z4_Solano | Storage | 569.5 | -569.5 | 0% | 0 | 1 | -569.5 | 0% | 0 | 1 | 0
[5 empty] | BatteryStorage_Norcal_Z4_Solano_subzone | 0 | 0 | Norcal_Z4_Solano_subzone | Storage | 20 | -20 | 0% | 0 | 1 | -20 | 0% | 0 | 1 | 0
[5 empty] | BatteryStorage_NorCalOutsideTxConstraintZones | 0 | 309 | NorCalOutsideTxConstraintZones | Storage | 58.75 | -58.75 | 0% | 0 | 1 | 250.25 | 526% | 0 | 1 | 0
[5 empty] | BatteryStorage_SCADOutsideTxConstraintZones | 0 | 0 | SCADOutsideTxConstraintZones | Storage | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0
[5 empty] | BatteryStorage_SCADSNV_Z2_GLW_VEA | 0 | 100 | SCADSNV_Z2_GLW_VEA | Storage | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 100 | No commercial interest; 0 MW selected | 0 | 1 | 0
[5 empty] | BatteryStorage_SCADSNV_Z3_GreaterImperial | 0 | 53 | SCADSNV_Z3_GreaterImperial | Storage | 2141.53 | -2141.53 | 0% | 0 | 2 | -2088.53 | 2.475% | 0 | 2 | 0
[5 empty] | BatteryStorage_SCADSNV_Z4_RiversideAndPalmSprings | 0 | 1313 | SCADSNV_Z4_RiversideAndPalmSprings | Storage | 4738.3329 | -4738.3329 | 0% | 0 | 3 | -3425.3329 | 27.71% | 0 | 3 | 0
[5 empty] | BatteryStorage_SCADSNV_Z5_SCADSNV | 0 | 629 | SCADSNV_Z5_SCADSNV | Storage | 2626.04 | -2626.04 | 0% | 0 | 2 | -1997.04 | 23.95% | 0 | 1 | 0
[5 empty] | BatteryStorage_SouthernPGE | 0 | 0 | SouthernPGE | Storage | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0
[5 empty] | BatteryStorage_SPGE_Z1_Westlands | 0 | 825 | SPGE_Z1_Westlands | Storage | 1394.24 | -1394.24 | 0% | 0 | 1 | -569.24 | 59.17% | 0 | 1 | 0
[5 empty] | BatteryStorage_SPGE_Z2_KernAndGreaterCarrizo | 0 | 53 | SPGE_Z2_KernAndGreaterCarrizo | Storage | 1504.67 | -1504.67 | 0% | 0 | 1 | -1451.67 | 3.522% | 0 | 1 | 0
[5 empty] | BatteryStorage_SPGE_Z3_Carrizo | 0 | 0 | SPGE_Z3_Carrizo | Storage | 1855.99 | -1855.99 | 0% | 0 | 1 | -1855.99 | 0% | 0 | 1 | 0
[5 empty] | BatteryStorage_SPGE_Z4_CentralValleyAndLosBanos | 0 | 0 | SPGE_Z4_CentralValleyAndLosBanos | Storage | 816.636 | -816.636 | 0% | 0 | 1 | -816.636 | 0% | 0 | 1 | 0
[5 empty] | BatteryStorage_Tehachapi | 0 | 3121 | Tehachapi | Storage | 5206.5814 | -5206.5814 | 0% | 0 | 3 | -2085.5814 | 59.94% | 0 | 2 | 0
[5 empty] | BatteryStorage_TehachapiOutsideTxConstraintZones | 0 | 2208 | TehachapiOutsideTxConstraintZones | Storage | 2008.07 | -2008.07 | 0% | 0 | 2 | 199.93 | 110% | 0 | 1 | 0
[5 empty] | BatteryStorage_WestlandsOutsideTxConstraintZones | 0 | 0 | WestlandsOutsideTxConstraintZones | Storage | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0

## 4b_QueuePivotTable_20201123
Row Labels | Sum of MW-1 | Summary of Commercial Interest (Interconnection Queue / Zones) | Row Labels | Sum of MW-1
0 | 3314.665 | "0" Zone | 0 | 3314.665
Photovoltaic | 485.875 | "0" Zone | Photovoltaic | 485.875
Storage | 2090.97 | "0" Zone | Storage | 2090.97
Wind Turbine | 737.82 | "0" Zone | Wind Turbine | 737.82
| 23918.4361 | Blank Zone |  | 23918.4361
Combined Cycle | 717.07 | Blank Zone | Combined Cycle | 717.07
Photovoltaic | 3292.3221 | Blank Zone | Photovoltaic | 3292.3221
Solar Thermal | 103.455 | Blank Zone | Solar Thermal | 103.455
Storage | 13012.3441 | Blank Zone | Storage | 13012.3441
Wind Turbine | 6793.245 | Blank Zone | Wind Turbine | 6793.245
GK_Z1_GreaterKramer | 361.14 | GK_Z1_GreaterKramer | GK_Z1_GreaterKramer | 361.14
Photovoltaic | 148.96 | GK_Z1_GreaterKramer | Photovoltaic | 148.96
Wind Turbine | 212.18 | GK_Z1_GreaterKramer | Wind Turbine | 212.18
GK_Z2_InyokernAndNorthOfKramer | 1126 | GK_Z2_InyokernAndNorthOfKramer | GK_Z2_InyokernAndNorthOfKramer | 1126
Photovoltaic | 852.74 | GK_Z2_InyokernAndNorthOfKramer | Photovoltaic | 852.74
Storage | 273.26 | GK_Z2_InyokernAndNorthOfKramer | Storage | 273.26
GK_Z3_NorthOfVictor | 320.92 | GK_Z3_NorthOfVictor | GK_Z3_NorthOfVictor | 320.92
Photovoltaic | 210.88 | GK_Z3_NorthOfVictor | Photovoltaic | 210.88
Storage | 110.04 | GK_Z3_NorthOfVictor | Storage | 110.04
GK_Z4_Pisgah | 302.85 | GK_Z4_Pisgah | GK_Z4_Pisgah | 302.85
Photovoltaic | 302.85 | GK_Z4_Pisgah | Photovoltaic | 302.85
GreaterImpOutsideTxConstraintZones | 747.7 | GreaterImpOutsideTxConstraintZones | GreaterImpOutsideTxConstraintZones | 747.7
Storage | 747.7 | GreaterImpOutsideTxConstraintZones | Storage | 747.7
KramerInyoOutsideTxConstraintZones | 100.98 | KramerInyoOutsideTxConstraintZones | KramerInyoOutsideTxConstraintZones | 100.98
Storage | 100.98 | KramerInyoOutsideTxConstraintZones | Storage | 100.98
None | 2101.66 | None | None | 2101.66
Storage | 2101.66 | None | Storage | 2101.66
Norcal_Z2_Humboldt | 259.125 | Norcal_Z2_Humboldt | Norcal_Z2_Humboldt | 259.125
Wind Turbine | 259.125 | Norcal_Z2_Humboldt | Wind Turbine | 259.125
Norcal_Z3_SacramentoRiver | 522 | Norcal_Z3_SacramentoRiver | Norcal_Z3_SacramentoRiver | 522
Photovoltaic | 12 | Norcal_Z3_SacramentoRiver | Photovoltaic | 12
Storage | 510 | Norcal_Z3_SacramentoRiver | Storage | 510
Norcal_Z4_Solano | 1486.304 | Norcal_Z4_Solano | Norcal_Z4_Solano | 1486.304
Photovoltaic | 275.9 | Norcal_Z4_Solano | Photovoltaic | 275.9
Storage | 569.5 | Norcal_Z4_Solano | Storage | 569.5
Wind Turbine | 640.904 | Norcal_Z4_Solano | Wind Turbine | 640.904
Norcal_Z4_Solano_subzone | 20 | Norcal_Z4_Solano_subzone | Norcal_Z4_Solano_subzone | 20
Storage | 20 | Norcal_Z4_Solano_subzone | Storage | 20
NorCalOutsideTxConstraintZones | 1837.75 | NorCalOutsideTxConstraintZones | NorCalOutsideTxConstraintZones | 1837.75
Hydro | 5 | NorCalOutsideTxConstraintZones | Hydro | 5
Storage | 58.75 | NorCalOutsideTxConstraintZones | Storage | 58.75
Wind Turbine | 1774 | NorCalOutsideTxConstraintZones | Wind Turbine | 1774
Outside | 1482.6 | Outside | Outside | 1482.6
Storage | 1482.6 | Outside | Storage | 1482.6
SCADSNV_Z1_EldoradoAndMtnPass | 300 | SCADSNV_Z1_EldoradoAndMtnPass | SCADSNV_Z1_EldoradoAndMtnPass | 300
Photovoltaic | 300 | SCADSNV_Z1_EldoradoAndMtnPass | Photovoltaic | 300
SCADSNV_Z3_GreaterImperial | 5750.49 | SCADSNV_Z3_GreaterImperial | SCADSNV_Z3_GreaterImperial | 5750.49
Photovoltaic | 2106.66 | SCADSNV_Z3_GreaterImperial | Photovoltaic | 2106.66
Storage | 2141.53 | SCADSNV_Z3_GreaterImperial | Storage | 2141.53
Wind Turbine | 1502.3 | SCADSNV_Z3_GreaterImperial | Wind Turbine | 1502.3
SCADSNV_Z4_RiversideAndPalmSprings | 9897.4429 | SCADSNV_Z4_RiversideAndPalmSprings | SCADSNV_Z4_RiversideAndPalmSprings | 9897.4429
Photovoltaic | 4609.61 | SCADSNV_Z4_RiversideAndPalmSprings | Photovoltaic | 4609.61
Steam Turbine | 549.5 | SCADSNV_Z4_RiversideAndPalmSprings | Steam Turbine | 549.5
Storage | 4738.3329 | SCADSNV_Z4_RiversideAndPalmSprings | Storage | 4738.3329
SCADSNV_Z5_SCADSNV | 4736.144 | SCADSNV_Z5_SCADSNV | SCADSNV_Z5_SCADSNV | 4736.144
Photovoltaic | 1800.104 | SCADSNV_Z5_SCADSNV | Photovoltaic | 1800.104
Storage | 2626.04 | SCADSNV_Z5_SCADSNV | Storage | 2626.04
Wind Turbine | 310 | SCADSNV_Z5_SCADSNV | Wind Turbine | 310
SPGE_Z1_Westlands | 6315.775 | SPGE_Z1_Westlands | SPGE_Z1_Westlands | 6315.775
Gas Turbine | 63 | SPGE_Z1_Westlands | Gas Turbine | 63
Photovoltaic | 4778.535 | SPGE_Z1_Westlands | Photovoltaic | 4778.535
Storage | 1394.24 | SPGE_Z1_Westlands | Storage | 1394.24
Wind Turbine | 80 | SPGE_Z1_Westlands | Wind Turbine | 80
SPGE_Z2_KernAndGreaterCarrizo | 2925.291 | SPGE_Z2_KernAndGreaterCarrizo | SPGE_Z2_KernAndGreaterCarrizo | 2925.291
Photovoltaic | 1420.621 | SPGE_Z2_KernAndGreaterCarrizo | Photovoltaic | 1420.621
Storage | 1504.67 | SPGE_Z2_KernAndGreaterCarrizo | Storage | 1504.67
SPGE_Z3_Carrizo | 1855.99 | SPGE_Z3_Carrizo | SPGE_Z3_Carrizo | 1855.99
Storage | 1855.99 | SPGE_Z3_Carrizo | Storage | 1855.99
SPGE_Z4_CentralValleyAndLosBanos | 1064.986 | SPGE_Z4_CentralValleyAndLosBanos | SPGE_Z4_CentralValleyAndLosBanos | 1064.986
Photovoltaic | 248.35 | SPGE_Z4_CentralValleyAndLosBanos | Photovoltaic | 248.35
Storage | 816.636 | SPGE_Z4_CentralValleyAndLosBanos | Storage | 816.636
Tehachapi | 10409.6394 | Tehachapi | Tehachapi | 10409.6394
Photovoltaic | 4116.798 | Tehachapi | Photovoltaic | 4116.798
Storage | 5206.5814 | Tehachapi | Storage | 5206.5814
Wind Turbine | 1086.26 | Tehachapi | Wind Turbine | 1086.26
TehachapiOutsideTxConstraintZones | 2008.07 | TehachapiOutsideTxConstraintZones | TehachapiOutsideTxConstraintZones | 2008.07
Storage | 2008.07 | TehachapiOutsideTxConstraintZones | Storage | 2008.07
Grand Total | 83165.9585

## 4c_Grid GenerationQueue wZones
Date: 11/23/2020 | [26 empty] | Report Run Date: 11/23/2020
The California ISO Controlled Grid Generation Queue for All: Active
[6 empty] | Generating Facility |  |  |  | Net MWs |  |  | Deliverability |  | Location |  | Point of Interconnection | [6 empty] | Study Availability
Status
Project Name | Queue Position | Interconnection Request | Queue Date | Application Status | Study | Type-1 | Type-2 | Fuel-1 | Fuel-2 | MW-1 | MW-2 | MW Total | Full Capacity, Partial or Energy Only (FC/P/EO) | Off-Peak Deliverability and Economic Only | County | State | Utility | Station or Transmission Line | Simplified Substation Name | Index in substation list | Zone | Proposed | Current | Feasibility Study or Supplemental Review | System Impact Study or | Facilities Study (FAS) or | Optional Study | Interconnection Agreement
|  | Receive Date |  |  | Process | [16 empty] | On-line Date | On-line Date |  | Phase I Cluster Study | Phase II Cluster Study | (OS) | Status
(as filed with IR)
TULE WIND | 32 | 2004-05-12 | 2004-05-24 | ACTIVE | Serial LGIP | Wind Turbine |  | Wind Turbine |  | 193.8 |  | 193.8 | Partial Capacity |  | SAN DIEGO | CA | SDGE | Boulevard East Substation 138kV | Boulevard | 2 | SCADSNV_Z3_GreaterImperial | 2007-09-01 | 2022-12-31 | Waived | Complete | Complete | None | Executed
LAKE ELSINORE ADVANCED PUMPED STORAGE PROJECT | 72 | 2005-04-26 | 2005-06-21 | ACTIVE | Serial LGIP | Storage |  | Pumped-Storage hydro |  | 500 |  | 500 | Full Capacity |  | RIVERSIDE | CA | SDGE | Proposed Lee Lake Substation 500kV | Lee | 3 | SPGE_Z4_CentralValleyAndLosBanos | 2008-12-31 | 2021-12-31 | Waived | Complete | Re-Study | None | Executed
VOYAGER WIND | 93 | 2006-02-15 | 2006-03-01 | ACTIVE | Serial LGIP | Wind Turbine |  | Wind Turbine |  | 220 |  | 220 | Full Capacity |  | KERN | CA | SCE | Windhub Substation 220kV bus | Windhub | 5 | Tehachapi | 2008-12-31 | 2020-12-31 | Waived | Complete | Complete | None | Executed
VOYAGER WIND 2 | 119 | 2006-08-08 | 2006-08-08 | ACTIVE | Serial LGIP | Wind Turbine |  | Wind Turbine |  | 500 |  | 500 | Full Capacity |  | KERN | CA | SCE | Windhub Sub 230kV Bus | Windhub | 6 | Tehachapi | 2013-12-31 | 2020-12-31 | Required | Complete | Complete | None | Executed
SANDSTORM WIND POWER | 138 | 2006-10-23 | 2006-10-23 | ACTIVE | Serial LGIP | Wind Turbine |  | Wind Turbine |  | 150 |  | 150 | Full Capacity |  | RIVERSIDE | CA | SCE | Devers-Vista #1 230kV | Devers | 8 | 0 | 2008-12-31 | 2021-12-31 | Waived | Complete | Complete | None | Executed
DESERT SUNLIGHT PV I (FKA EAGLE MOUNTAIN PV I) | 146 | 2006-11-16 | 2006-11-16 | ACTIVE | Serial LGIP | Photovoltaic | Storage | Solar | Battery | 250 | 250 | 250 | Partial Capacity |  | RIVERSIDE | CA | SCE | Red Bluff Substation 230kV | Red Bluff | 12 | SCADSNV_Z4_RiversideAndPalmSprings | 2008-12-01 | 2014-12-05 | Required | Complete | Complete | None | Executed
ENERGIA SIERRA JUAREZ WIND | 159A | 2006-12-06 | 2006-12-22 | ACTIVE | Serial LGIP | Wind Turbine |  | Wind Turbine |  | 256 |  | 256 | Full Capacity |  | BAJA CALIFORNIA | MX | SDGE | East County (ECO) Substation 230kV | East County | 9 | SCADSNV_Z3_GreaterImperial | 2009-06-01 | 2022-01-15 | Required | Complete | Complete | None | Executed
GENESIS MCCOY | 193 | 2007-03-19 | 2007-04-04 | ACTIVE | TC | Steam Turbine | Storage | Solar | Battery | 500 | 230 | 500 | Partial Capacity |  | RIVERSIDE | CA | SCE | Colorado River Substation 500kV | Colorado River | 11 | SCADSNV_Z4_RiversideAndPalmSprings | 2010-12-31 | 2016-06-14 | NA | Complete | Complete | NA | Executed
AMERICAN KINGS SOLAR | 272 | 2007-11-01 | 2007-11-01 | ACTIVE | TC | Photovoltaic |  | Solar |  | 123 |  | 123 | Full Capacity |  | KINGS | CA | PGAE | Henrietta Substation 70kV bus | Henrietta | 10 | SPGE_Z1_Westlands | 2012-06-01 | 2020-12-01 | NA | Complete | Complete | NA | Executed
DRACKER SOLAR | 294 | 2008-01-15 | 2008-01-16 | ACTIVE | TC | Photovoltaic | Storage | Solar | Battery | 485 | 392.83 | 485 | Partial Capacity |  | RIVERSIDE | CA | SCE | Colorado River Substation 500kV | Colorado River | 11 | SCADSNV_Z4_RiversideAndPalmSprings | 2012-06-01 | 2022-08-31 | NA | Complete | Complete | NA | Executed
ALMASOL | 365 | 2008-05-06 | 2008-05-12 | ACTIVE | TC | Photovoltaic | Storage | Solar | Battery | 500 | 500 | 500 | Partial Capacity |  | RIVERSIDE | CA | SCE | Red Bluff Substation 230kV | Red Bluff | 12 | SCADSNV_Z4_RiversideAndPalmSprings | 2013-12-28 | 2022-08-31 | NA | Complete | Complete | NA | Executed
SLOTH | 421 | 2008-05-30 | 2008-05-30 | ACTIVE | TC | Steam Turbine |  | Solar |  | 49.5 |  | 49.5 | Energy Only |  | RIVERSIDE | CA | SCE | Red Bluff Substation 220kV | Red Bluff | 13 | SCADSNV_Z4_RiversideAndPalmSprings | 2012-02-01 | 2024-07-31 | NA | Complete | Complete | NA | Executed
ROSAMOND WEST SOLAR | 506 | 2009-07-30 | 2009-07-31 | ACTIVE | C01 | Photovoltaic | Storage | Solar | Battery | 300 | 147.7 | 299.6 | Full Capacity |  | KERN | CA | SCE | Whirlwind Substation 230kV | Whirlwind | 14 | Tehachapi | 2015-07-31 | 2020-12-30 | NA | Complete | Complete | NA | Executed
ORD MOUNTAIN | 552 | 2009-10-02 | 2010-02-01 | ACTIVE | C02 | Photovoltaic | Storage | Solar | Battery | 60 | 60 | 60 | Energy Only |  | SAN BERNARDINO | CA | SCE | Calcite Substation 220kV | Calcite | 15 |  | 2012-03-01 | 2022-09-06 | NA | Complete | Complete | NA | Executed
BLYTHE MESA SOLAR | 576 | 2010-01-29 | 2010-02-01 | ACTIVE | C02 | Photovoltaic | Storage | Solar | Battery | 224 | 223.6 | 224 | Partial Capacity |  | RIVERSIDE | CA | SCE | Colorado River Sub 230kV Bus | Colorado River | 16 | SCADSNV_Z4_RiversideAndPalmSprings | 2013-12-31 | 2022-08-31 | NA | Complete | Complete | NA | Executed
CATALINA SOLAR | 602 | 2010-01-30 | 2010-02-01 | ACTIVE | C02 | Photovoltaic |  | Solar |  | 150 |  | 150 | Full Capacity |  | KERN | CA | SCE | Whirlwind Substation 230kV | Whirlwind | 14 | Tehachapi | 2013-07-01 | 2021-12-01 | NA | Complete | Complete | NA | Executed
DESERT HARVEST | 643AE | 2010-07-30 | 2010-07-31 | ACTIVE | C03 | Photovoltaic | Storage | Solar | Battery | 150 | 150 | 150 | Partial Capacity |  | RIVERSIDE | CA | SCE | Red Bluff Sub 230kV Bus | Red Bluff | 17 | SCADSNV_Z4_RiversideAndPalmSprings | 2014-01-01 | 2020-12-01 | NA | Complete | Complete | NA | Executed
APPARENT FIRST HYBRID | 653F | 2010-10-07 | 2010-10-13 | ACTIVE | SGIP-TC | Photovoltaic | Storage | Solar | Battery | 12 | 12.1 | 12 | Full Capacity |  | YOLO | CA | PGAE | Woodland-Davis 115 kV | Woodland | 18 | Norcal_Z3_SacramentoRiver | 2012-05-01 | 2020-12-30 | NA | Complete | Complete | NA | Executed
LASSEN LODGE HYDROELECTRIC | 720 | 2011-03-31 | 2011-03-31 | ACTIVE | C04 | Hydro |  | Water |  | 4.5 |  | 4.5 | Energy Only |  | TEHAMA | CA | PGAE | Vota - South 60 KV | Vota | 19 | NorCalOutsideTxConstraintZones | 2012-12-15 | 2022-10-15 | NA | Complete | Complete | NA | Executed
REDWOOD SOLAR FARM | 744 | 2011-03-31 | 2011-03-31 | ACTIVE | C04 | Photovoltaic |  | Solar |  | 90 |  | 90 | Full Capacity |  | KERN | CA | PGAE | Lamont Sub 115 KV Bus | Lamont | 21 | SPGE_Z1_Westlands | 2014-07-01 | 2020-12-01 | NA | Complete | Complete | NA | Executed
BIG SKY SOLAR | 768 | 2011-03-31 | 2011-03-31 | ACTIVE | C04 | Photovoltaic | Storage | Solar | Battery | 320 | 163.4 | 320 | Partial Capacity |  | LOS ANGELES | CA | SCE | Antelope Substation 230kV bus |  |  |  | 2014-12-31 | 2019-09-14 | NA | Complete | Complete | NA | Executed
WRIGHT SOLAR | 779 | 2011-03-31 | 2011-03-31 | ACTIVE | C04 | Photovoltaic |  | Solar |  | 200 |  | 200 | Full Capacity |  | MERCED | CA | PGAE | Los Banos-Panoche #1 230kV | Panoche | 22 | SPGE_Z1_Westlands | 2014-01-06 | 2019-12-31 | NA | Complete | Complete | NA | Executed
RUGGED SOLAR FARM | 789 | 2011-03-30 | 2011-03-31 | ACTIVE | C04 | Photovoltaic |  | Solar |  | 71.88 |  | 71.88 | Energy Only |  | SAN DIEGO | CA | SDGE | Boulevard East Substation 69 kV | Boulevard | 23 | SCADSNV_Z3_GreaterImperial | 2015-07-31 | 2021-11-01 | NA | Complete | Complete | NA | Executed
BLUE HORNET SOLAR | 838 | 2011-03-31 | 2011-03-31 | ACTIVE | C04 | Photovoltaic |  | Solar |  | 100 |  | 100 | Full Capacity |  | IMPERIAL | CA | SDGE | Imperial Valley Substation 230kV | Imperial | 7 | SCADSNV_Z3_GreaterImperial | 2015-12-31 | 2021-12-01 | NA | Complete | Complete | NA | Executed
CALIFORNIA FLATS SOLAR | 877 | 2012-03-23 | 2012-04-02 | ACTIVE | C05 | Photovoltaic | Storage | Solar | Battery | 280 | 60 | 280 | Full Capacity |  | MONTEREY | CA | PGAE | Morro-Gates 230kV line |  |  |  | 2015-10-30 | 2018-09-30 | NA | Complete | Complete | NA | Executed
STAGE COACH SOLAR | 897 | 2012-04-02 | 2012-04-02 | ACTIVE | C05 | Photovoltaic | Storage | Solar | Battery | 200 | 50 | 200 | Partial Capacity |  | SAN BERNARDINO | CA | SCE | Calcite Substation 220kV bus | Calcite | 24 |  | 2016-12-01 | 2022-08-01 | NA | Complete | Complete | NA | Executed
NORTHERN ORCHARD SOLAR | 946 | 2013-04-23 | 2013-04-30 | ACTIVE | C06 | Photovoltaic | Storage | Solar | Battery | 100 | 92 | 100 | Partial Capacity |  | KERN | CA | PGAE | Midway- Wheeler Ridge #2 - 230 kV Line | Midway | 25 | SPGE_Z2_KernAndGreaterCarrizo | 2015-12-01 | 2021-12-31 | NA | Complete | Complete | NA | Executed
FIFTH STANDARD SOLAR | 954 | 2013-04-29 | 2013-04-30 | ACTIVE | C06 | Photovoltaic | Storage | Solar | Battery | 150 | 117 | 150 | Partial Capacity |  | FRESNO | CA | PGAE | Gates Substation 230 kV | Gates | 26 | SPGE_Z1_Westlands | 2016-07-01 | 2021-12-31 | NA | Complete | Complete | NA | Executed
JAVA SOLAR | 965 | 2013-04-30 | 2013-04-30 | ACTIVE | C06 | Photovoltaic |  | Solar |  | 13.5 |  | 13.5 | Full Capacity |  | KINGS | CA | PGAE | Henrietta-GWF 115 kV Line | Henrietta | 28 | SPGE_Z1_Westlands | 2016-10-01 | 2024-05-30 | NA | Complete | Complete | NA | Executed
PALOMAR ENERGY CENTER 2 | 968 | 2013-04-30 | 2013-04-30 | ACTIVE | C06 | Combined Cycle |  | Natural Gas |  | 35 |  | 35 | Full Capacity |  | SAN DIEGO | CA | SDGE | Palomar Energy Substation 230kV | Palomar | 29 |  | 2015-03-01 | 2021-04-15 | NA | Complete | Complete | NA | Executed
GARLAND (FKA: RE GARLAND) | 971 | 2013-04-30 | 2013-04-30 | ACTIVE | C06 | Photovoltaic | Storage | Solar | Battery | 200 | 88.7 | 200 | Full Capacity |  | KERN | CA | SCE | Whirlwind Substation 220kV |  |  |  | 2016-05-30 | 2016-09-30 | NA | Complete | Complete | NA | Executed
SUNSHINE VALLEY SOLAR 1 | 993 | 2013-04-30 | 2013-04-30 | ACTIVE | C06 | Photovoltaic | Storage | Solar | Battery | 50 | 40 | 50 | Full Capacity |  | NYE | NV | VEA | Valley Substation 138kV | Valley | 30 | SCADSNV_Z5_SCADSNV | 2016-12-31 | 2019-12-18 | NA | Complete | Complete | NA | Executed
LASSEN LODGE HYDROELECTRIC 2 | 1002 | 2013-05-01 | 2013-04-30 | ACTIVE | C06 | Hydro |  | Water |  | 0.5 |  | 0.5 | Energy Only |  | TEHAMA | CA | PGAE | Volta-South 60 kV Line | Volta | 32 | NorCalOutsideTxConstraintZones | 2015-11-15 | 2022-10-15 | NA | Complete | Complete | NA | Executed
DYER SUMMIT WIND REPOWER | 1010 | 2014-04-28 | 2014-04-30 | ACTIVE | C07 | Wind Turbine |  | Wind Turbine |  | 46.1 |  | 44.8 | Full Capacity |  | SAN JOAQUIN | CA | PGAE | Vasco-Herdlyn 60kV line | Vasco | 33 | 0 | 2015-12-01 | 2020-12-15 | NA | Complete | Complete | NA | Executed
COLINAS DE ORO | 1011 | 2014-04-28 | 2014-04-30 | ACTIVE | C07 | Storage |  | Battery |  | 30 |  | 30 | Full Capacity |  | ALAMEDA | CA | PGAE | Tesla Substation 115kV | Tesla | 34 | 0 | 2016-12-01 | 2021-03-01 | NA | Complete | Complete | NA | Executed
BLACKBRIAR | 1027 | 2014-05-01 | 2014-04-30 | ACTIVE | C07 | Storage |  | Battery |  | 20 |  | 20 | Full Capacity |  | FRESNO | CA | PGAE | Gates Substation 230kV | Gates | 35 | SPGE_Z1_Westlands | 2016-06-01 | 2021-12-31 | NA | Complete | Complete | NA | Executed
LITTLE BEAR SOLAR 1 | 1028 | 2014-04-30 | 2014-04-30 | ACTIVE | C07 | Photovoltaic |  | Solar |  | 20 |  | 20 | Full Capacity |  | FRESNO | CA | PGAE | Mendota Substation 115 kV | Mendota | 36 | SPGE_Z1_Westlands | 2016-12-01 | 2020-12-31 | NA | Complete | Complete | NA | Executed
LITTLE BEAR SOLAR 2 | 1029 | 2014-04-30 | 2014-04-30 | ACTIVE | C07 | Photovoltaic |  | Solar |  | 20 |  | 20 | Full Capacity |  | FRESNO | CA | PGAE | Mendota Substation 115 kV | Mendota | 36 | SPGE_Z1_Westlands | 2018-09-01 | 2020-12-31 | NA | Complete | Complete | NA | Executed
MUSTANG 2 | 1036 | 2014-04-30 | 2014-04-30 | ACTIVE | C07 | Photovoltaic |  | Solar |  | 153.4 |  | 153.4 | Full Capacity |  | KINGS | CA | PGAE | Mustang Switchyard 230 kV | Mustang | 38 | SPGE_Z1_Westlands | 2016-09-30 | 2020-10-01 | NA | Complete | Complete | NA | Executed
CHULA VISTA ENERGY CENTER 2 | 1045 | 2014-04-30 | 2014-04-30 | ACTIVE | C07 | Storage |  | Battery |  | 50 |  | 50 | Energy Only |  | SAN DIEGO | CA | SDGE | Otay Substation 69 kV | Otay | 39 | SCADSNV_Z5_SCADSNV | 2019-11-01 | 2021-03-15 | NA | Complete | Complete | NA | In Progress
NORTH JOHNSON ENERGY CENTER | 1047 | 2014-04-30 | 2014-04-30 | ACTIVE | C07 | Storage |  | Battery |  | 50 |  | 50 | Full Capacity |  | SAN DIEGO | CA | SDGE | El Cajon Substation 69kV | El Cajon | 40 | SCADSNV_Z5_SCADSNV | 2019-11-01 | 2021-12-08 | NA | Complete | Complete | NA | In Progress
ESCONDIDO ENERGY CENTER 2 | 1048 | 2014-04-30 | 2014-04-30 | ACTIVE | C07 | Storage |  | Battery |  | 50 |  | 50 | Full Capacity |  | SAN DIEGO | CA | SDGE | Escondido Substation 69 kV | Escondido | 41 | GreaterImpOutsideTxConstraintZones | 2019-11-01 | 2022-01-12 | NA | Complete | Complete | NA | In Progress
WHITE WING RANCH SOLAR | 1062 | 2014-04-30 | 2014-04-30 | ACTIVE | C07 | Photovoltaic | Storage | Solar | Battery | 200 | 200 | 200 | Energy Only |  | YUMA | AZ | SDGE | Hoodoo Wash Switchyard 500 kV | Hoodoo | 42 | SCADSNV_Z3_GreaterImperial | 2018-12-31 | 2022-12-31 | NA | Complete | Complete | NA | In Progress
ARES NEVADA | 1064 | 2014-04-30 | 2014-04-30 | ACTIVE | C07 | Storage |  | Gravity via Rail |  | 44 |  | 44 | Full Capacity |  | NYE | NV | GLW | Gamebird Switchyard 230kV | Gamebird | 43 | SCADSNV_Z5_SCADSNV | 2017-01-01 | 2022-06-28 | NA | Complete | Complete | NA | Executed
GASKELL WEST | 1074 | 2014-04-30 | 2014-04-30 | ACTIVE | C07 | Photovoltaic | Storage | Solar | Battery | 128.1 | 125 | 128.07 | Partial Capacity |  | KERN | CA | SCE | Whirlwind Substation 220 kV | Whirlwind | 44 | Tehachapi | 2016-06-30 | 2022-07-01 | NA | Complete | Complete | NA | Executed
WILLOW SPRINGS SOLAR 3 | 1076 | 2014-04-30 | 2014-04-30 | ACTIVE | C07 | Photovoltaic | Storage | Solar | Battery | 50 | 50 | 50 | Partial Capacity |  | KERN | CA | SCE | Whirlwind Substation 230 kV | Whirlwind | 45 | Tehachapi | 2017-06-30 | 2022-04-30 | NA | Complete | Complete | NA | Executed
ALTAMONT MIDWAY LTD | 1096 | 2015-02-24 | 2015-04-13 | ACTIVE | FT | Wind Turbine |  | Wind Turbine |  | 5 |  | 5 | Energy Only |  | ALAMEDA | CA | PGAE | Altamont Midway Substation 230 kV | Altamont | 46 | 0 | 2015-08-31 | 2020-08-01 | None | NA | NA | NA | Executed
BEAR CANYON ENERGY STORAGE | 1097 | 2015-04-29 | 2015-04-30 | ACTIVE | C08 | Storage |  | Battery |  | 13.25 |  | 13 | Full Capacity |  | LAKE | CA | PGAE | Geysers #12-Fulton 230kV line | Geysers | 47 | Norcal_Z4_Solano | 2018-01-01 | 2021-09-01 | NA | Complete | Complete | NA | Executed
CENTRAL 40 | 1103 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Photovoltaic |  | Solar |  | 40 |  | 40 | Full Capacity |  | STANISLAUS | CA | PGAE | Miller #1 115 kV line | Miller | 48 | SPGE_Z1_Westlands | 2017-08-01 | 2020-11-30 | NA | Complete | Complete | NA | Executed
FOUNTAIN WIND | 1106 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Wind Turbine |  | Wind Turbine |  | 206 |  | 200 | Full Capacity |  | SHASTA | CA | PGAE | Pit1-Cottonwood 230kV line | Pit1 | 49 | NorCalOutsideTxConstraintZones | 2020-10-15 | 2024-03-15 | NA | Complete | Complete | NA | Executed
NORTH CENTRAL VALLEY | 1109 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Storage |  | Battery |  | 150 |  | 132 | Full Capacity |  | SAN JOAQUIN | CA | PGAE | Belotta Substation 115 kV | Belotta | 50 | SPGE_Z4_CentralValleyAndLosBanos | 2021-06-01 | 2022-04-01 | NA | Complete | Complete | NA | Executed
BLACK DIAMOND ENERGY STORAGE | 1111 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Storage |  | Battery |  | 200 |  | 200 | Full Capacity |  | CONTRA COSTA | CA | PGAE | Pittsburgh Substation 230kV | Pittsburgh | 51 | None | 2018-06-01 | 2021-05-01 | NA | Complete | Complete | NA | Executed
ULTRAPOWER CHINESE STATION BESS | 1116 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Storage |  | Battery |  | 10 |  | 10 | Full Capacity |  | TUOLUMNE | CA | PGAE | Melones-Curtis 115kV line | Melones | 52 | 0 | 2017-03-31 | 2020-08-31 | NA | Complete | Complete | NA | Executed
AQUAMARINE WESTSIDE | 1117 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Photovoltaic |  | Solar |  | 254 |  | 250 | Full Capacity |  | KINGS | CA | PGAE | Gates Substation 230 kV | Gates | 26 | SPGE_Z1_Westlands | 2019-06-18 | 2020-11-06 | NA | Complete | Complete | NA | Executed
CHESTNUT WESTSIDE | 1120 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Photovoltaic |  | Solar |  | 152 |  | 150 | Full Capacity |  | KINGS | CA | PGAE | Gates Substation 230kV | Gates | 35 | SPGE_Z1_Westlands | 2021-04-19 | 2022-04-29 | NA | Complete | Complete | NA | Executed
LITTLE BEAR 3 | 1127 | 2015-04-28 | 2015-04-30 | ACTIVE | C08 | Photovoltaic |  | Solar |  | 20.44 |  | 20 | Full Capacity |  | FRESNO | CA | PGAE | Mendota Substation 115kV | Mendota | 53 | SPGE_Z1_Westlands | 2020-08-01 | 2020-11-15 | NA | Complete | Complete | NA | Executed
LITTLE BEAR 4 | 1128 | 2015-04-28 | 2015-04-30 | ACTIVE | C08 | Photovoltaic |  | Solar |  | 103.1 |  | 100 | Full Capacity |  | FRESNO | CA | PGAE | Mendota Substation 115kV | Mendota | 53 | SPGE_Z1_Westlands | 2020-12-01 | 2020-12-15 | NA | Complete | Complete | NA | Executed
LUNA VALLEY SOLAR | 1129 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Photovoltaic |  | Solar |  | 204 |  | 200 | Full Capacity |  | FRESNO | CA | PGAE | Tranquility Substation 230kV | Tranquility | 54 | SPGE_Z1_Westlands | 2018-12-31 | 2022-04-29 | NA | Complete | Complete | NA | Executed
SCARLET | 1135 | 2015-04-29 | 2015-04-30 | ACTIVE | C08 | Photovoltaic | Storage | Solar | Battery | 417.9 | 420 | 400 | Full Capacity |  | FRESNO | CA | PGAE | Tranquillity Switching Station 230kV | Tranquility | 55 | SPGE_Z1_Westlands | 2018-12-31 | 2022-12-31 | NA | Complete | Complete | NA | Executed
WESTLANDS ALMOND | 1136 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Photovoltaic |  | Solar |  | 20 |  | 20 | Energy Only |  | KINGS | CA | PGAE | Kent SW STA 70 kV | Kent | 56 | SPGE_Z1_Westlands | 2016-11-14 | 2022-02-15 | NA | Complete | Complete | NA | Executed
WESTLANDS SOLAR BLUE | 1139 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Photovoltaic |  | Solar |  | 252 |  | 250 | Full Capacity |  | KINGS | CA | PGAE | Gates Substation 230kV | Gates | 35 | SPGE_Z1_Westlands | 2020-04-20 | 2022-03-30 | NA | Complete | Complete | NA | Executed
ALAMO SPRINGS SOLAR 1 | 1141 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Photovoltaic | Storage | Solar | Battery | 80 | 73.6 | 80 | Partial Capacity |  | KERN | CA | PGAE | Arco Substation 70kV | Arco | 57 | SPGE_Z2_KernAndGreaterCarrizo | 2018-12-31 | 2022-04-28 | NA | Complete | Complete | NA | Executed
LAKE ALPAUGH BATTERY STORAGE | 1143 | 2015-04-29 | 2015-04-30 | ACTIVE | C08 | Storage |  | Battery |  | 10 |  | 10 | Full Capacity |  | TULARE | CA | PGAE | Corcoran-Olive Switching Station 115 kV | Corcoran | 58 | SPGE_Z1_Westlands | 2017-12-31 | 2021-12-31 | NA | Complete | Complete | NA | Executed
ALAMO SPRINGS SOLAR 2 | 1157 | 2015-04-22 | 2015-04-30 | ACTIVE | C08 | Photovoltaic | Storage | Solar | Battery | 50 | 46 | 50 | Partial Capacity |  | KERN | CA | PGAE | Arco Substation 70kV | Arco | 57 | SPGE_Z2_KernAndGreaterCarrizo | 2018-12-31 | 2022-04-28 | NA | Complete | Complete | NA | Executed
SLATE | 1158 | 2015-04-29 | 2015-04-30 | ACTIVE | C08 | Photovoltaic | Storage | Solar | Battery | 308.5 | 308.7 | 300 | Full Capacity |  | KINGS | CA | PGAE | Mustang Switching Station 230kV | Mustang | 59 | SPGE_Z1_Westlands | 2018-12-31 | 2021-04-15 | NA | Complete | Complete | NA | Executed
BIG ROCK SOLAR FARM | 1166 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Photovoltaic | Storage | Solar | Battery | 200 | 200 | 200 | Partial Capacity |  | IMPERIAL | CA | SDGE | Imperial Valley Substation 230 kV | Imperial | 60 | SCADSNV_Z3_GreaterImperial | 2020-06-01 | 2022-09-01 | NA | Complete | Complete | NA | Executed
FALLBROOK ENERGY STORAGE | 1169 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Storage |  | Battery |  | 69.6 |  | 69.6 | Full Capacity |  | SAN DIEGO | CA | SDGE | Avocado Substation 69kV | Avocado | 61 | GreaterImpOutsideTxConstraintZones | 2020-02-01 | 2021-03-24 | NA | Complete | Complete | NA | Executed
GATEWAY ENERGY STORAGE | 1170 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Storage |  | Battery |  | 250 |  | 250 | Full Capacity |  | SAN DIEGO | CA | SDGE | Otay Mesa Switchyard 230 kV | Otay | 62 | Outside | 2018-09-01 | 2021-08-01 | NA | Complete | Complete | NA | Executed
MCFARLAND SOLAR | 1171 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Photovoltaic | Storage | Solar | Battery | 500 | 435 | 500 | Partial Capacity |  | YUMA | AZ | SDGE | Hoodoo Wash Switchyard 500 kV | Hoodoo | 42 | SCADSNV_Z3_GreaterImperial | 2018-12-31 | 2021-06-01 | NA | Complete | Complete | NA | In Progress
LECONTE ENERGY STORAGE | 1175 | 2015-04-29 | 2015-04-30 | ACTIVE | C08 | Storage |  | Battery |  | 125 |  | 125 | Partial Capacity |  | IMPERIAL | CA | SDGE | Imperial Valley Substation 230 kV | Imperial | 60 | SCADSNV_Z3_GreaterImperial | 2018-09-01 | 2021-06-01 | NA | Complete | Complete | NA | Executed
SUN STREAMS SOLAR 2 | 1189 | 2015-04-28 | 2015-04-30 | ACTIVE | C08 | Photovoltaic |  | Solar |  | 150 |  | 150 | Full Capacity |  | MARICOPA | AZ | SDGE | Hassayampa Switchyard 500 kV common bus | Hassayampa | 63 | SCADSNV_Z3_GreaterImperial | 2020-01-31 | 2021-07-01 | NA | Complete | Complete | NA | Executed
VALLEY CENTER ENERGY STORAGE | 1191 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Photovoltaic | Storage | Solar | Battery | 6 | 114 | 120 | Partial Capacity |  | SAN DIEGO | CA | SDGE | Valley Center Substation 69kV | Valley | 64 | SCADSNV_Z3_GreaterImperial | 2018-10-01 | 2021-12-15 | NA | Complete | Complete | NA | Executed
CRIMSON | 1192 | 2015-04-29 | 2015-04-30 | ACTIVE | C08 | Photovoltaic | Storage | Solar | Battery | 359.6 | 365 | 350 | Full Capacity |  | RIVERSIDE | CA | SCE | Colorado River Substation 230kV | Colorado River | 65 | SCADSNV_Z4_RiversideAndPalmSprings | 2020-12-31 | 2021-09-30 | NA | Complete | Complete | NA | Executed
ARLINGTON | 1196 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Photovoltaic | Storage | Solar | Battery | 409.9 | 242.6 | 409.9 | Partial Capacity |  | RIVERSIDE | CA | SCE | Colorado River Substation 230kV | Colorado River | 65 | SCADSNV_Z4_RiversideAndPalmSprings | 2021-07-01 | 2023-07-01 | NA | Complete | Complete | NA | Executed
QUARTZITE SOLAR 8 | 1198 | 2015-04-28 | 2015-04-30 | ACTIVE | C08 | Photovoltaic | Storage | Solar | Battery | 150 | 150 | 150 | Partial Capacity |  | RIVERSIDE | CA | SCE | Colorado River Substation 220kV | Colorado River | 66 | SCADSNV_Z4_RiversideAndPalmSprings | 2020-12-01 | 2022-04-28 | NA | Complete | Complete | NA | Executed
VICTORY PASS SOLAR | 1200 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Photovoltaic | Storage | Solar | Battery | 200 | 186 | 200 | Partial Capacity |  | RIVERSIDE | CA | SCE | Red Bluff Substation 230kV | Red Bluff | 12 | SCADSNV_Z4_RiversideAndPalmSprings | 2018-12-31 | 2024-07-31 | NA | Complete | Complete | NA | Executed
ARATINA SOLAR CENTER 1 | 1204 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Photovoltaic | Storage | Solar | Battery | 200 | 200 | 200 | Partial Capacity |  | SAN BERNARDINO | CA | SCE | Kramer Substation 230kV | Kramer | 67 | GK_Z2_InyokernAndNorthOfKramer | 2020-06-01 | 2022-12-30 | NA | Complete | Complete | NA | Executed
SIENNA SOLAR FARM | 1207 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Photovoltaic | Storage | Solar | Battery | 200 | 200 | 200 | Partial Capacity |  | SAN BERNARDINO | CA | SCE | Calcite Substation 230kV | Calcite | 68 | GK_Z4_Pisgah | 2020-06-01 | 2023-03-31 | NA | Complete | Complete | NA | Executed
ANTELOPE SOLAR 2 | 1208 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Storage | Photovoltaic | Battery | Solar | 200 | 450 | 650 | Full Capacity |  | LOS ANGELES | CA | SCE | Antelope Substation 220kV | Antelope | 69 | Tehachapi | 2018-12-31 | 2021-03-31 | NA | Complete | Complete | NA | Executed
ROSAMOND SOUTH EAST | 1211 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Photovoltaic | Storage | Solar | Battery | 101.7 | 94 | 101.7 | Full Capacity |  | KERN | CA | SCE | Whirlwind Substation 230kV | Whirlwind | 14 | Tehachapi | 2018-06-30 | 2022-04-30 | NA | Complete | Complete | NA | Executed
GOLDEN FIELDS SOLAR | 1212 | 2015-04-30 | 2015-04-30 | ACTIVE | C08 | Photovoltaic |  | Solar |  | 101.7 |  | 101.7 | Full Capacity |  | KERN | CA | SCE | Whirlwind Substation 230kV | Whirlwind | 70 | Tehachapi | 2018-06-30 | 2022-04-30 | NA | Complete | Complete | NA | Executed
RABBITBRUSH SOLAR | 1215 | 2015-04-28 | 2015-04-30 | ACTIVE | C08 | Photovoltaic | Storage | Solar | Battery | 153.7 | 150 | 153.73 | Partial Capacity |  | KERN | CA | SCE | Whirlwind Substation 230kV | Whirlwind | 14 | Tehachapi | 2019-12-31 | 2022-04-30 | NA | Complete | Complete | NA | Executed
WILLOW SPRINGS SOLAR 4 | 1217 | 2015-04-28 | 2015-04-30 | ACTIVE | C08 | Photovoltaic | Storage | Solar | Battery | 102 | 75 | 75 | Partial Capacity |  | KERN | CA | SCE | Whirlwind Substation 230kV | Whirlwind | 14 | Tehachapi | 2019-12-31 | 2022-04-30 | NA | Complete | Complete | NA | Executed
NEVADA MOHAVE SOLAR | 1218 | 2015-04-28 | 2015-04-30 | ACTIVE | C08 | Photovoltaic |  | Solar |  | 400 |  | 400 | Energy Only |  | CLARK | NV | SCE | Jointly-owned Mohave Switchyard 500kV | Mohave | 71 | SCADSNV_Z5_SCADSNV | 2019-12-01 | 2024-06-15 | NA | Complete | Complete | NA | In Progress
AGUA CALIENTE SOLAR 2 | 1222 | 2016-03-01 | 2016-03-08 | ACTIVE | ISP | Photovoltaic |  | Solar |  | 20 |  | 20 | Energy Only |  | MARICOPA | AZ | SDGE | Hoodoo Wash Switchyard 500kV | Hoodoo | 72 | SCADSNV_Z3_GreaterImperial | 2016-12-01 | 2016-12-01 | NA |  |  | NA
AMERICAN KINGS 9 | 1223 | 2016-04-22 | 2016-05-02 | ACTIVE | C09 | Photovoltaic | Storage | Solar | Battery | 310.7 | 300 | 300 | Energy Only |  | KINGS | CA | PGAE | Mustang Switching Station 230kV | Mustang | 59 | SPGE_Z1_Westlands | 2020-12-31 | 2024-04-30 | NA | Complete | Complete | NA | In Progress
CINCO | 1225 | 2016-04-27 | 2016-05-02 | ACTIVE | C09 | Storage | Photovoltaic | Battery | Solar | 10.45 | 53.2 | 60 | Energy Only |  | FRESNO | CA | PGAE | Five Points Substation 70 kV | Five Points | 73 |  | 2019-06-01 | 2021-12-31 | NA | Complete | Complete | NA | In Progress
HUDSON SOLAR 1 | 1235 | 2016-04-21 | 2016-05-02 | ACTIVE | C09 | Photovoltaic | Storage | Solar | Battery | 86.64 | 99 | 85 | Energy Only |  | FRESNO | CA | PGAE | Panoche Substation 115 kV | Panoche | 74 | SPGE_Z1_Westlands | 2019-12-31 | 2024-12-31 | NA | Complete | Complete | NA | Executed
MEDEIROS SOLAR | 1239 | 2016-05-03 | 2016-05-02 | ACTIVE | C09 | Photovoltaic |  | Solar |  | 28.35 |  | 26.5 | Energy Only |  | MERCED | CA | PGAE | Los Banos - O'Neil PGP 70 kV Line | O'Neil | 75 | SPGE_Z4_CentralValleyAndLosBanos | 2019-08-01 | 2019-08-01 | NA | Complete | Complete | NA | In Progress
PLUOT | 1242 | 2016-05-03 | 2016-05-02 | ACTIVE | C09 | Photovoltaic |  | Solar |  | 254 |  | 246.4 | Energy Only |  | KINGS | CA | PGAE | Gates 230 kV. | Gates | 76 | SPGE_Z1_Westlands | 2023-04-05 | 2023-04-05 | NA | Complete | Complete | NA | Executed
POMEGRANATE | 1243 | 2016-05-03 | 2016-05-02 | ACTIVE | C09 | Photovoltaic |  | Solar |  | 254 |  | 249.7 | Full Capacity |  | KINGS | CA | PGAE | Gates Substation 230kV | Gates | 35 | SPGE_Z1_Westlands | 2022-04-06 | 2023-04-05 | NA | Complete | Complete | NA | Executed
PROXIMA SOLAR | 1244 | 2016-04-30 | 2016-05-02 | ACTIVE | C09 | Photovoltaic | Storage | Solar | Battery | 220 | 154.5 | 300 | Full Capacity |  | STANISLAUS | CA | PGAE | Quinto-Westley 230 kV line | Quinto | 77 | SPGE_Z4_CentralValleyAndLosBanos | 2020-03-10 | 2023-06-01 | NA | Complete | Complete | NA | Executed
NORTHERN ORCHARD SOLAR 2 | 1259 | 2016-04-27 | 2016-05-02 | ACTIVE | C09 | Photovoltaic |  | Solar |  | 133.6 |  | 130 | Energy Only |  | KERN | CA | PGAE | Midway - Wheeler Ridge 230kV #2 line | Midway | 78 | SPGE_Z2_KernAndGreaterCarrizo | 2020-12-16 | 2021-12-31 | NA | Complete | Complete | NA | In Progress
NORTHERN ORCHARD SOLAR 3 | 1260 | 2016-04-27 | 2016-05-02 | ACTIVE | C09 | Photovoltaic |  | Solar |  | 102 |  | 100 | Energy Only |  | KERN | CA | PGAE | Midway - Wheeler Ridge 230kV #2 line | Midway | 78 | SPGE_Z2_KernAndGreaterCarrizo | 2020-10-14 | 2021-12-31 | NA | Complete | Complete | NA | In Progress
CORBY | 1270 | 2016-04-27 | 2016-05-02 | ACTIVE | C09 | Storage |  | Battery |  | 313.5 |  | 300 | Full Capacity |  | SOLANO | CA | PGAE | Vaca-Dixon Substation 230kV | Vaca-Dixon | 80 |  | 2020-12-01 | 2023-06-30 | NA | Complete | Complete | NA | In Progress
CASCADE ENERGY STORAGE | 1272 | 2016-05-02 | 2016-05-02 | ACTIVE | C09 | Storage |  | Battery |  | 25.2 |  | 25 | Full Capacity |  | SAN JOAQUIN | CA | PGAE | Weber Substation 60kV | Weber | 81 | SPGE_Z4_CentralValleyAndLosBanos | 2018-05-31 | 2021-12-31 | NA | Complete | Complete | NA | Executed
KOLA | 1275 | 2016-04-26 | 2016-05-02 | ACTIVE | C09 | Storage |  | Battery |  | 418 |  | 418 | Full Capacity |  | ALAMEDA | CA | PGAE | Tesla Substation 230kV | Tesla | 82 | 0 | 2020-12-01 | 2023-04-10 | NA | Complete | Complete | NA | Executed
MULQUEENEY RANCH WIND | 1277 | 2016-05-02 | 2016-05-02 | ACTIVE | C09 | Wind Turbine |  | Wind Turbine |  | 114 |  | 20 | Full Capacity |  | ALAMEDA | CA | PGAE | Tesla 230 kV Bus "C" | Tesla | 83 | 0 | 2020-03-01 | 2021-12-15 | NA | Complete | Complete | NA | Executed
WALKER RIDGE | 1284 | 2016-05-23 | 2016-05-02 | ACTIVE | C09 | Wind Turbine |  | Wind Turbine |  | 144.9 |  | 140.9 | Partial Capacity |  | LAKE | CA | PGAE | Cortina-Mendocino and Cortina-Eagle Rock 115kV Lines | Cortina | 85 | Norcal_Z4_Solano | 2019-02-01 | 2021-10-16 | NA | Complete | Complete | NA | Executed
MESQUITE SOLAR 5 | 1291 | 2016-04-28 | 2016-05-02 | ACTIVE | C09 | Storage | Photovoltaic | Battery | Solar | 20 | 300 | 300 | Full Capacity |  | MARICOPA | AZ | SDGE | Hassayampa Switchyard 500kV common bus | Hassayampa | 86 | SCADSNV_Z3_GreaterImperial | 2023-04-28 | 2023-04-28 | NA | Complete | Complete | NA | Executed
MARVEL | 1295 | 2016-04-26 | 2016-05-02 | ACTIVE | C09 | Storage |  | Battery |  | 405.9 |  | 400 | Full Capacity |  | RIVERSIDE | CA | SCE | Devers Substation 230kV | Devers | 87 | 0 | 2022-04-01 | 2023-01-01 | NA | Complete | Complete | NA | Executed
SOL CATCHER BESS | 1302 | 2016-05-03 | 2016-05-02 | ACTIVE | C09 | Storage |  | Battery |  | 220 |  | 213.5 | Energy Only |  | RIVERSIDE | CA | SCE | Red Bluff 220 kV | Red Bluff | 88 | SCADSNV_Z4_RiversideAndPalmSprings | 2019-05-31 | 2024-07-31 | NA | Complete | Complete | NA | In Progress
CALCITE SOLAR 1 | 1305 | 2016-04-22 | 2016-05-02 | ACTIVE | C09 | Photovoltaic | Storage | Solar | Battery | 102.9 | 20.7 | 100 | Energy Only |  | SAN BERNARDINO | CA | SCE | Calcite 230 kV Line | Calcite | 89 | GK_Z4_Pisgah | 2020-08-01 | 2021-12-31 | NA | Complete | Complete | NA | In Progress
DAGGETT SOLAR 1 | 1312 | 2016-04-28 | 2016-05-02 | ACTIVE | C09 | Photovoltaic | Storage | Solar | Battery | 149 | 100 | 144 | Full Capacity |  | SAN BERNARDINO | CA | SCE | Coolwater Substation 115kV | Coolwater | 90 | GK_Z1_GreaterKramer | 2020-06-30 | 2024-12-15 | NA | Complete | Complete | NA | Executed
DAGGETT SOLAR 2 | 1313 | 2016-04-28 | 2016-05-02 | ACTIVE | C09 | Photovoltaic | Storage | Solar | Battery | 188.9 | 126 | 182 | Full Capacity |  | SAN BERNARDINO | CA | SCE | Kramer Substation 230kV | Kramer | 67 | GK_Z2_InyokernAndNorthOfKramer | 2020-06-30 | 2023-04-15 | NA | Complete | Complete | NA | Executed
DAGGETT SOLAR 3 | 1314 | 2016-04-28 | 2016-05-02 | ACTIVE | C09 | Photovoltaic | Storage | Solar | Battery | 313.9 | 208 | 300 | Full Capacity |  | SAN BERNARDINO | CA | SCE | Kramer Substation 230kV | Kramer | 67 | GK_Z2_InyokernAndNorthOfKramer | 2020-06-30 | 2023-04-15 | NA | Complete | Complete | NA | Executed
WILLY 9 | 1319 | 2016-04-25 | 2016-05-02 | ACTIVE | C09 | Photovoltaic | Storage | Solar | Battery | 259.8 | 250 | 250 | Partial Capacity |  | KERN | CA | SCE | Whirlwind Substation 230kV | Whirlwind | 14 | Tehachapi | 2020-12-31 | 2023-01-31 | NA | Complete | Complete | NA | Executed
SOLAR STAR 3 | 1322 | 2016-04-25 | 2016-05-02 | ACTIVE | C09 | Storage | Photovoltaic | Battery | Solar | 24.95 | 25 | 24 | Full Capacity |  | KERN | CA | SCE | Whirlwind Substation 230kV | Whirlwind | 14 | Tehachapi | 2021-12-31 | 2023-04-24 | NA | Complete | Complete | NA | Executed
SOLAR STAR 4 | 1323 | 2016-04-25 | 2016-05-02 | ACTIVE | C09 | Storage | Photovoltaic | Battery | Solar | 24.95 | 25.05 | 24 | Full Capacity |  | KERN | CA | SCE | Whirlwind Substation 230kV | Whirlwind | 14 | Tehachapi | 2021-12-31 | 2023-04-24 | NA | Complete | Complete | NA | Executed
EDSAN 1 | 1324 | 2016-04-27 | 2016-05-02 | ACTIVE | C09 | Photovoltaic |  | Solar |  | 311.4 |  | 300 | Full Capacity |  | KERN | CA | SCE | Windhub Substation 230kV | Windhub | 91 | Tehachapi | 2019-12-31 | 2022-06-01 | NA | Complete | Complete | NA | Executed
SAGEBRUSH SOLAR 2 | 1325 | 2016-04-27 | 2016-05-02 | ACTIVE | C09 | Photovoltaic | Storage | Solar | Battery | 100 | 100 | 200 | Energy Only |  | KERN | CA | SCE | Vincent Substation 230kV | Vincent | 92 | Tehachapi | 2019-12-31 | 2022-06-01 | NA | Complete | Complete | NA | Executed
CYCLONE SOLAR | 1327 | 2016-04-29 | 2016-05-02 | ACTIVE | C09 | Photovoltaic | Storage | Solar | Battery | 57.95 | 52 | 56.87 | Partial Capacity |  | KERN | CA | SCE | Whirlwind Substation 230kV | Whirlwind | 14 | Tehachapi | 2019-07-01 | 2022-04-30 | NA | Complete | Complete | NA | In Progress
TROPICO SOLAR | 1329 | 2016-04-29 | 2016-05-02 | ACTIVE | C09 | Photovoltaic | Storage | Solar | Battery | 112.3 | 110 | 110 | Partial Capacity |  | KERN | CA | SCE | Whirlwind Substation 230 kV | Whirlwind | 93 | Tehachapi | 2021-12-01 | 2022-04-30 | NA | Complete | Complete | NA | Executed
PASTORIA SOLAR | 1335 | 2016-05-02 | 2016-05-02 | ACTIVE | C09 | Photovoltaic | Storage | Solar | Battery | 106.9 | 80 | 105.2 | Partial Capacity |  | KERN | CA | SCE | Pastoria Substation 230kV | Pastoria | 95 | 0 | 2019-09-01 | 2022-04-30 | NA | Complete | Complete | NA | Executed
SOUTHLAND | 1336 | 2016-04-27 | 2016-05-02 | ACTIVE | C09 | Photovoltaic |  | Solar |  | 380.1 |  | 375 | Full Capacity |  | CLARK | NV | SCE | Mohave Substation 500kV | Mohave | 96 | SCADSNV_Z5_SCADSNV | 2019-12-01 | 2023-04-26 | NA | Complete | Complete | NA | In Progress
TECHREN SOLAR | 1339 | 2016-04-29 | 2016-05-02 | ACTIVE | C09 | Photovoltaic | Storage | Solar | Battery | 300 | 279 | 300 | Partial Capacity |  | CLARK | NV | SCE | SCE owned Eldorado Bus 230kV | Eldorado | 97 | SCADSNV_Z1_EldoradoAndMtnPass | 2019-07-31 | 2022-04-30 | NA | Complete | Complete | NA | Executed
YELLOW PINE 2 | 1341 | 2016-04-26 | 2016-05-02 | ACTIVE | C09 | Photovoltaic | Storage | Solar | Battery | 254.1 | 125 | 250 | Full Capacity |  | CLARK | NV | GLW | Crazy Eyes Substation 230kV | Crazy Eyes | 98 | SCADSNV_Z5_SCADSNV | 2019-12-01 | 2022-12-01 | NA | Complete | Complete | NA | Executed
CRESCENT PEAK | 1347 | 2016-05-02 | 2016-05-02 | ACTIVE | C09 | Wind Turbine |  | Wind Turbine |  | 310 |  | 303 | Partial Capacity |  | CLARK | NV | GLW | Sloan Canyon Switching Station 230kV | Sloan | 99 | SCADSNV_Z5_SCADSNV | 2019-07-31 | 2021-11-30 | NA | Complete | Complete | NA | Executed
ARAMIS POWER PLANT | 1349 | 2017-04-28 | 2017-05-01 | ACTIVE | C10 | Photovoltaic | Storage | Solar | Battery | 101.4 | 101.3 | 100 | Full Capacity |  | ALAMEDA | CA | PGAE | Cayetano Substation 230kV | Cayetano | 100 | Norcal_Z4_Solano | 2020-12-31 | 2023-06-30 | NA | Complete | Complete | NA | Executed
PAULSELL SOLAR ENERGY CENTER | 1350 | 2017-05-01 | 2017-05-01 | ACTIVE | C10 | Photovoltaic | Storage | Solar | Battery | 20.32 | 15 | 20 | Partial Capacity |  | STANISLAUS | CA | PGAE | Crow Creek Switching Station 60kV | Crow Creek | 101 |  | 2019-12-31 | 2023-05-01 | NA | Complete | Complete | NA | In Progress
EAST-BAY-WIND | 1354 | 2017-04-25 | 2017-05-01 | ACTIVE | C10 | Wind Turbine |  | Wind Turbine |  | 153 |  | 150 | Full Capacity |  | ALAMEDA | CA | PGAE | Tesla Substation 230kV | Tesla | 82 | 0 | 2020-12-01 | 2023-02-14 | NA | Complete | Complete | NA | In Progress
SAND HILL C | 1363 | 2017-04-29 | 2017-05-01 | ACTIVE | C10 | Wind Turbine |  | Wind Turbine |  | 84.25 |  | 80.8 | Full Capacity |  | ALAMEDA | CA | PGAE | Delta Switching Yard-Tesla 230kV line | Delta | 102 | Norcal_Z4_Solano | 2019-12-31 | 2021-04-17 | NA | Complete | Complete | NA | Executed
WEST FORD FLAT ENERGY STORAGE | 1367 | 2017-04-28 | 2017-05-01 | ACTIVE | C10 | Storage |  | Battery |  | 26.25 |  | 25 | Full Capacity |  | LAKE | CA | PGAE | Fulton Substation 230kV | Fulton | 103 | Norcal_Z4_Solano | 2020-01-01 | 2021-05-18 | NA | Complete | Complete | NA | In Progress
ELKHORN ENERGY STORAGE | 1374 | 2017-05-01 | 2017-05-01 | ACTIVE | C10 | Storage |  | Battery |  | 189 |  | 182.5 | Full Capacity |  | MONTEREY | CA | PGAE | Moss Landing Substation 115kV | Moss Landing | 105 | None | 2020-10-31 | 2020-12-31 | NA | Complete | Complete | NA | Filed Unexecuted
GONZAGA WIND FARM | 1378 | 2017-04-27 | 2017-05-01 | ACTIVE | C10 | Wind Turbine |  | Wind Turbine |  | 80 |  | 76.35 | Full Capacity |  | MERCED | CA | PGAE | Los Banos Substation 70kV | Los Banos | 106 | SPGE_Z1_Westlands | 2020-10-09 | 2023-10-16 | NA | Complete | Complete | NA | Executed
HEARTLAND 1 | 1379 | 2017-04-26 | 2017-05-01 | ACTIVE | C10 | Photovoltaic |  | Solar |  | 156 |  | 150 | Energy Only |  | FRESNO | CA | PGAE | Tranquility Switching Station 230kV | Tranquility | 107 | SPGE_Z1_Westlands | 2021-09-01 | 2023-12-31 | NA | Complete | Complete | NA | In Progress
HEARTLAND 2 | 1380 | 2017-04-26 | 2017-05-01 | ACTIVE | C10 | Photovoltaic |  | Solar |  | 156.1 |  | 150 | Energy Only |  | FRESNO | CA | PGAE | Tranquility Switching Station 230kV | Tranquility | 107 | SPGE_Z1_Westlands | 2021-09-01 | 2021-09-01 | NA | Complete | Complete | NA | In Progress
LAS CAMAS 1 | 1382 | 2017-04-29 | 2017-05-01 | ACTIVE | C10 | Photovoltaic |  | Solar |  | 102.5 |  | 100 | Full Capacity |  | MERCED | CA | PGAE | Los Banos Substation 230kV | Los Banos | 108 | SPGE_Z1_Westlands | 2021-11-30 | 2021-11-30 | NA | Complete | Complete | NA
REDUX SOLAR | 1389 | 2017-05-01 | 2017-05-01 | ACTIVE | C10 | Photovoltaic |  | Solar |  | 128.2 |  | 125 | Full Capacity |  | FRESNO | CA | PGAE | Gates Substation 230kV | Gates | 35 | SPGE_Z1_Westlands | 2020-12-30 | 2023-10-15 | NA | Complete | Complete | NA
SONRISA | 1391 | 2017-04-29 | 2017-05-01 | ACTIVE | C10 | Photovoltaic |  | Solar |  | 205.1 |  | 200 | Full Capacity |  | FRESNO | CA | PGAE | Tranquility Switching Station 230kV | Tranquility | 107 | SPGE_Z1_Westlands | 2021-11-30 | 2024-02-28 | NA | Complete | Complete | NA | Executed
DRIFTWOOD STELLA | 1394 | 2017-04-29 | 2017-05-01 | ACTIVE | C10 | Photovoltaic | Storage | Solar | Battery | 207.4 | 184 | 200 | Partial Capacity |  | KERN | CA | PGAE | Midway Substation 115kV | Midway | 111 | SPGE_Z2_KernAndGreaterCarrizo | 2021-11-30 | 2024-01-16 | NA | Complete | Complete | NA | In Progress
SANDRINI SOL 1 | 1397 | 2017-04-29 | 2017-05-01 | ACTIVE | C10 | Photovoltaic | Storage | Solar | Battery | 104.2 | 92 | 100 | Partial Capacity |  | KERN | CA | PGAE | Wheeler Ridge Substation 70kV | Wheeler Ridge | 112 | SPGE_Z2_KernAndGreaterCarrizo | 2021-11-30 | 2023-03-01 | NA | Complete | Complete | NA | Executed
SANDRINI SOL 2 | 1398 | 2017-04-29 | 2017-05-01 | ACTIVE | C10 | Photovoltaic |  | Solar |  | 205.1 |  | 200 | Full Capacity |  | KERN | CA | PGAE | Wheeler Ridge Substation 230kV | Wheeler Ridge | 113 | SPGE_Z2_KernAndGreaterCarrizo | 2021-11-30 | 2023-03-01 | NA | Complete | Complete | NA | Executed
ATLAS SOLAR | 1402 | 2017-04-28 | 2017-05-01 | ACTIVE | C10 | Storage | Photovoltaic | Battery | Solar | 1920 | 3200 | 3200 | Partial Capacity |  | LA PAZ | AZ | DCRT | Delaney-Colorado River 500kV | Colorado River | 114 | SCADSNV_Z4_RiversideAndPalmSprings | 2020-12-31 | 2023-12-31 | NA | Complete | Complete | NA
ATHOS POWER PLANT | 1405 | 2017-04-28 | 2017-05-01 | ACTIVE | C10 | Photovoltaic |  | Solar |  | 458 |  | 450 | Full Capacity |  | RIVERSIDE | CA | SCE | Red Bluff Substation 230kV | Red Bluff | 12 | SCADSNV_Z4_RiversideAndPalmSprings | 2020-12-31 | 2021-12-15 | NA | Complete | Complete | NA | Executed
BALDY MESA | 1413 | 2017-04-29 | 2017-05-01 | ACTIVE | C10 | Storage | Photovoltaic | Battery | Solar | 110 | 110.04 | 100 | Full Capacity |  | SAN BERNARDINO | CA | SCE | Roadway Substation 115kV bus | Roadway | 117 | GK_Z3_NorthOfVictor | 2020-12-31 | 2022-07-31 | NA | Complete | Complete | NA | Executed
HIGH 5 SOLAR | 1414 | 2017-04-28 | 2017-05-01 | ACTIVE | C10 | Photovoltaic | Storage | Solar | Battery | 100 | 50 | 100 | Full Capacity |  | SAN BERNARDINO | CA | SCE | Victor Substation 230kV | Victor | 118 | GK_Z3_NorthOfVictor | 2019-12-29 | 2022-04-30 | NA | Complete | Complete | NA | Executed
CAMINO SOLAR | 1419 | 2017-04-27 | 2017-05-01 | ACTIVE | C10 | Photovoltaic | Storage | Solar | Battery | 44.88 | 22.44 | 54.28 | Partial Capacity |  | KERN | CA | SCE | Whirlwind Substation 230kV | Whirlwind | 14 | Tehachapi | 2020-08-15 | 2021-12-15 | NA | Complete | Complete | NA | Executed
EDSAN 2 | 1424 | 2017-04-28 | 2017-05-01 | ACTIVE | C10 | Photovoltaic |  | Solar |  | 524 |  | 500 | Full Capacity |  | KERN | CA | SCE | Windhub Substation 230kV | Windhub | 91 | Tehachapi | 2020-12-31 | 2022-11-01 | NA | Complete | Complete | NA | Executed
MAVERICK | 1428 | 2017-04-27 | 2017-05-01 | ACTIVE | C10 | Storage |  | Battery |  | 10 |  | 10 | Full Capacity |  | SAN DIEGO | CA | SDGE | Miramar GT Switchyard 69kV |  |  |  | 2021-12-31 | 2021-12-31 | NA | Complete | Complete | NA
MOUNT LAGUNA WIND 2 | 1429 | 2017-04-28 | 2017-05-01 | ACTIVE | C10 | Wind Turbine |  | Wind Turbine |  | 400 |  | 400 | Energy Only |  | SAN DIEGO | CA | SDGE | Suncrest-Ocotillo 500 kV Line | Suncrest | 122 | SCADSNV_Z3_GreaterImperial | 2020-06-01 | 2020-12-31 | NA | Complete | Complete | NA | In Progress
ROSEBUD | 1431 | 2017-04-27 | 2017-05-01 | ACTIVE | C10 | Storage |  | Battery |  | 10 |  | 10 | Full Capacity |  | SAN DIEGO | CA | SDGE | Kearny West Substation 69kV |  |  |  | 2021-12-31 | 2021-12-31 | NA | Complete | Complete | NA
STARLIGHT SOLAR | 1432 | 2017-05-01 | 2017-05-01 | ACTIVE | C10 | Photovoltaic | Storage | Solar | Battery | 20 | 17.4 | 20 | Partial Capacity |  | SAN DIEGO | CA | SDGE | Boulevard East Substation 69kV |  |  |  | 2020-06-01 | 2022-12-15 | NA | Complete | Complete | NA
TOP GUN ENERGY STORAGE | 1434 | 2017-04-28 | 2017-05-01 | ACTIVE | C10 | Storage |  | Battery |  | 30 |  | 30 | Full Capacity |  | SAN DIEGO | CA | SDGE | Miramar GT Switchyard 69kV |  |  |  | 2019-12-31 | 2021-02-16 | NA | Complete | Complete | NA | Executed
VIKTORIA SOLAR | 1435 | 2017-04-24 | 2017-05-01 | ACTIVE | C10 | Photovoltaic | Storage | Solar | Battery | 250 | 112.5 | 250 | Full Capacity |  | YUMA | AZ | SDGE | Hoodoo Wash Switchyard 500kV | Hoodoo | 72 | SCADSNV_Z3_GreaterImperial | 2020-12-31 | 2022-12-23 | NA | Complete | Complete | NA
WIND WALL MONOLITH 1 | 1439 | 2018-04-30 | 2018-04-17 | ACTIVE | FT | Wind Turbine |  | Wind Turbine |  | 4.96 |  | 4.96 | Energy Only |  | KERN | CA | SCE | Vincent Substation 220kV | Vincent | 127 | Tehachapi | 2019-12-15 | 2020-08-31 | Offered | NA | NA | NA | Executed
WIND WALL MONOLITH 2 | 1440 | 2018-04-30 | 2018-04-17 | ACTIVE | FT | Wind Turbine |  | Wind Turbine |  | 3.7 |  | 3.7 | Energy Only |  | KERN | CA | SCE | Vincent Substation 220kV | Vincent | 127 | Tehachapi | 2019-12-15 | 2020-08-31 | Offered | NA | NA | NA | Executed
AJO POWER BANK | 1442 | 2018-04-05 | 2018-04-16 | ACTIVE | C11 | Storage |  | Battery |  | 124.3 |  | 120 | Full Capacity |  | SANTA CLARA | CA | PGAE | Llagas-Gilroy Foods 115 kV line | Llagas Gilroy | 129 | None | 2020-12-01 | 2025-04-01 | NA | Complete | Complete | NA | In Progress
ANGELA | 1443 | 2018-04-13 | 2018-04-16 | ACTIVE | C11 | Photovoltaic |  | Solar |  | 141.1 |  | 40 | Full Capacity |  | TULARE | CA | PGAE | Olive Switching Station 115kV | Olive | 130 | Tehachapi | 2021-11-30 | 2021-11-30 | NA | Complete | Complete | NA | Executed
BEAUCHAMP SOLAR | 1444 | 2018-04-04 | 2018-04-16 | ACTIVE | C11 | Photovoltaic | Storage | Solar | Battery | 150 | 150 | 150 | Partial Capacity |  | COLUSA | CA | PGAE | Cortina Substation 115kV | Cortina | 131 | Norcal_Z4_Solano | 2022-12-01 | 2024-02-01 | NA | Complete | Complete | NA
HUMMINGBIRD ENERGY STORAGE | 1454 | 2018-04-09 | 2018-04-16 | ACTIVE | C11 | Storage |  | Battery |  | 75 |  | 75 | Full Capacity |  | SANTA CLARA | CA | PGAE | Metcalf 115kV | Metcalf | 132 | None | 2020-12-31 | 2022-01-30 | NA | Complete | Complete | NA
JANUS | 1455 | 2018-04-12 | 2018-04-16 | ACTIVE | C11 | Storage | Photovoltaic | Battery | Solar | 80 | 83.54 | 80 | Partial Capacity |  | COLUSA | CA | PGAE | Cortina Substation 60kV | Cortina | 133 | Norcal_Z4_Solano | 2021-12-31 | 2024-02-01 | NA | Complete | Complete | NA | Executed
LAS CAMAS 3 | 1456 | 2018-04-10 | 2018-04-16 | ACTIVE | C11 | Photovoltaic |  | Solar |  | 102.5 |  | 100 | Full Capacity |  | MERCED | CA | PGAE | Los Banos 230kV | Los Banos | 134 | SPGE_Z1_Westlands | 2022-11-30 | 2025-02-07 | NA | Complete | Complete | NA
MILPA POWER BANK | 1457 | 2018-04-09 | 2018-04-16 | ACTIVE | C11 | Storage |  | Battery |  | 3 |  | 3 | Full Capacity |  | SANTA CLARA | CA | PGAE | Los Esteros Substation 115kV | Los Esteros | 135 | None | 2020-12-01 | 2022-05-01 | NA | Complete | Complete | NA
MULQUEENEY RANCH WIND 2 | 1459 | 2018-04-12 | 2018-04-16 | ACTIVE | C11 | Wind Turbine |  | Wind Turbine |  | 62.5 |  | 60 | Full Capacity |  | ALAMEDA | CA | PGAE | Tesla Substation 230kV | Tesla | 82 | 0 | 2021-12-15 | 2021-12-15 | NA | Complete | Complete | NA | In Progress
PINTO PASS | 1460 | 2018-04-12 | 2018-04-16 | ACTIVE | C11 | Storage |  | Battery |  | 20 |  | 20 | Full Capacity |  | CONTRA COSTA | CA | PGAE | Christie Substation 60kV | Christie | 136 | Norcal_Z4_Solano_subzone | 2021-12-31 | 2023-12-31 | NA | Complete | Complete | NA | Executed
RECLAIMED WIND | 1461 | 2018-04-04 | 2018-04-16 | ACTIVE | C11 | Wind Turbine |  | Wind Turbine |  | 112.2 |  | 90.7 | Full Capacity |  | ALAMEDA | CA | PGAE | Kelso - Tesla Tap 230kV | Kelso | 137 | Norcal_Z4_Solano | 2020-12-31 | 2022-12-22 | NA | Complete | Complete | NA | In Progress
SOLANO 4 WIND | 1463 | 2018-04-04 | 2018-04-16 | ACTIVE | C11 | Wind Turbine |  | Wind Turbine |  | 92.35 |  | 90.8 | Full Capacity |  | SOLANO | CA | PGAE | Birds Landing Switching Station 230kV | Birds Landing | 138 | Norcal_Z4_Solano | 2023-03-31 | 2022-03-31 | NA | Complete | Complete | NA | In Progress
CABALLERO STORAGE | 1470 | 2018-04-13 | 2018-04-16 | ACTIVE | C11 | Storage |  | Battery |  | 106.2 |  | 99.7 | Full Capacity |  | SAN LUIS OBISPO | CA | PGAE | Mesa Substation 230kV | Mesa Substation | 139 | SPGE_Z3_Carrizo | 2021-12-01 | 2024-01-06 | NA | Complete | Complete | NA
DALLAS ENERGY STORAGE | 1472 | 2018-04-11 | 2018-04-18 | ACTIVE | C11 | Storage |  | Battery |  | 500 |  | 400 | Full Capacity |  | MONTEREY | CA | PGAE | Moss Landing Substation 500kV | Moss Landing | 140 | SPGE_Z3_Carrizo | 2020-12-01 | 2020-12-01 | NA | Complete | Complete | NA | Executed
KEY STORAGE 1 | 1479 | 2018-04-11 | 2018-04-16 | ACTIVE | C11 | Storage |  | Battery |  | 309.3 |  | 300.1 | Full Capacity |  | FRESNO | CA | PGAE | Gates Sub 500kV | Gates | 141 | SPGE_Z1_Westlands | 2022-12-01 | 2024-12-24 | NA | Complete |  | NA | In Progress
PANOCHE ENERGY CENTER C11 | 1484 | 2018-04-10 | 2018-04-16 | ACTIVE | C11 | Gas Turbine |  | Natural Gas |  | 63 |  | 63 | Full Capacity |  | FRESNO | CA | PGAE | Panoche Substation 230kV | Panoche | 142 | SPGE_Z1_Westlands | 2020-07-01 | 2021-11-07 | NA | Complete | Complete | NA
TEPONA OFF-SHORE WIND | 1491 | 2018-04-14 | 2018-04-16 | ACTIVE | C11 | Wind Turbine |  | Wind Turbine |  | 161.9 |  | 156 | Full Capacity |  | HUMBOLDT | CA | PGAE | Humboldt Substation 115kV | Humboldt | 143 | Norcal_Z2_Humboldt | 2024-10-01 | 2026-03-01 | NA | Complete | Complete | NA
WINDCHARGER ESS | 1492 | 2018-04-12 | 2018-04-16 | ACTIVE | C11 | Storage |  | Battery |  | 150 |  | 150 | Full Capacity |  | SOLANO | CA | PGAE | Birds Landing Substation 230kV | Birds Landing | 144 | Norcal_Z4_Solano | 2021-12-01 | 2021-12-01 | NA | Complete | Complete | NA
AZALEA | 1493 | 2018-04-16 | 2018-04-16 | ACTIVE | C11 | Photovoltaic | Storage | Solar | Battery | 61.3 | 55.2 | 60 | Partial Capacity |  | KERN | CA | PGAE | Arco Substation 70kV | Arco | 145 | SPGE_Z2_KernAndGreaterCarrizo | 2022-11-01 | 2025-03-09 | NA | Complete | Complete | NA | Executed
CHALAN SOLAR | 1495 | 2018-04-13 | 2018-04-16 | ACTIVE | C11 | Storage | Photovoltaic | Battery | Solar | 25.2 | 66.6 | 64.9 | Full Capacity |  | KERN | CA | PGAE | Arco Substation 230kV | Arco | 146 | SPGE_Z2_KernAndGreaterCarrizo | 2021-12-01 | 2021-12-01 | NA | Complete | Complete | NA
DESCENDANT RANCH 1 | 1496 | 2018-04-11 | 2018-04-16 | ACTIVE | C11 | Storage | Photovoltaic | Battery | Solar | 510 | 513.5 | 500 | Full Capacity |  | COLUSA | CA | PGAE | Delevan Sub 230kV | Delevan | 147 | Norcal_Z3_SacramentoRiver | 2023-12-01 | 2024-05-08 | NA | Complete | Complete | NA | In Progress
JASMINE | 1499 | 2018-04-16 | 2018-04-16 | ACTIVE | C11 | Photovoltaic | Storage | Solar | Battery | 71.16 | 70 | 70 | Partial Capacity |  | KERN | CA | PGAE | Lakeview Substation 70kV | Lakeview | 148 | SPGE_Z2_KernAndGreaterCarrizo | 2022-11-01 | 2025-02-14 | NA | Complete | Complete | NA | Executed
PROSPECT ENERGY STORAGE | 1507 | 2018-04-16 | 2018-04-16 | ACTIVE | C11 | Storage |  | Battery |  | 58.75 |  | 49.9 | Full Capacity |  | SACRAMENTO | CA | PGAE | Gold Hill Substation 60kV | Gold Hill | 149 | NorCalOutsideTxConstraintZones | 2022-06-01 | 2023-09-06 | NA | Complete | Complete | NA | In Progress
BELLEFIELD SOLAR FARM | 1510 | 2018-04-16 | 2018-04-16 | ACTIVE | C11 | Photovoltaic | Storage | Solar | Battery | 500 | 500 | 500 | Full Capacity |  | KERN | CA | SCE | Windhub Substation 230kV | Windhub | 91 | Tehachapi | 2022-10-01 | 2023-02-15 | NA | Complete |  | NA | Executed
REXFORD SOLAR FARM | 1516 | 2018-04-16 | 2018-04-16 | ACTIVE | C11 | Photovoltaic | Storage | Solar | Battery | 300 | 300 | 300 | Full Capacity |  | TULARE | CA | SCE | Vestal Substation 230kV | Vestal | 150 | 0 | 2022-10-01 | 2023-02-15 | NA | Complete |  | NA | Executed
SANBORN SOLAR 2 | 1518 | 2018-04-13 | 2018-04-16 | ACTIVE | C11 | Photovoltaic | Storage | Solar | Battery | 268 | 250 | 500 | Full Capacity |  | KERN | CA | SCE | Windhub Substation 230kV | Windhub | 91 | Tehachapi | 2022-12-31 | 2023-01-31 | NA | Complete |  | NA | Executed
BALDY MESA 2 | 1519 | 2018-04-15 | 2018-04-16 | ACTIVE | C11 | Photovoltaic | Storage | Solar | Battery | 110.9 | 49.9 | 100 | Full Capacity |  | SAN BERNARDINO | CA | SCE | Roadway Substation 115kV | Roadway | 151 | GK_Z3_NorthOfVictor | 2021-12-15 | 2023-01-31 | NA | Complete |  | NA | Executed
ARIDA SOLAR FARM | 1522 | 2018-04-16 | 2018-04-16 | ACTIVE | C11 | Storage | Photovoltaic | Battery | Solar | 370 | 370 | 370 | Full Capacity |  | CLARK | NV | SCE | Mohave Substation 500kV | Mohave | 96 | SCADSNV_Z5_SCADSNV | 2022-10-01 | 2022-10-01 | NA | Complete |  | NA
QUARTZITE SOLAR 11 | 1526 | 2018-04-11 | 2018-04-16 | ACTIVE | C11 | Storage | Photovoltaic | Battery | Solar | 151.1 | 155.43 | 150 | Full Capacity |  | RIVERSIDE | CA | SCE | Colorado River Substation 230kV | Colorado River | 65 | SCADSNV_Z4_RiversideAndPalmSprings | 2022-12-30 | 2023-03-15 | NA | Complete |  | NA
WINDY WASH SOLAR | 1528 | 2018-04-13 | 2018-04-16 | ACTIVE | C11 | Photovoltaic |  | Solar |  | 79 |  | 79 | Full Capacity |  | RIVERSIDE | CA | SCE | Devers Substation 220kV | Devers | 153 | 0 | 2021-06-30 | 2022-12-31 | NA | Complete |  | NA
CENTENNIAL FLATS | 1529 | 2018-04-17 | 2018-04-16 | ACTIVE | C11 | Photovoltaic | Storage | Solar | Battery | 514.6 | 257.28 | 500 | Full Capacity |  | LA PAZ | AZ | DCRT | Delaney-Colorado River 500kV line | Colorado River | 154 | SCADSNV_Z4_RiversideAndPalmSprings | 2022-12-15 | 2023-08-15 | NA | Complete |  | NA
BATERIA DEL SUR | 1531 | 2018-04-16 | 2018-04-16 | ACTIVE | C11 | Storage |  | Battery |  | 350 |  | 350 | Full Capacity |  | TBD | MX | SDGE | Imperial Valley 230kV | Imperial | 155 | SCADSNV_Z3_GreaterImperial | 2022-05-01 | 2023-06-01 | NA | Complete | Complete | NA
KETTLE SOLAR ONE | 1532 | 2018-04-16 | 2018-04-16 | ACTIVE | C11 | Photovoltaic | Storage | Solar | Battery | 90 | 20 | 90 | Full Capacity |  | SAN DIEGO | CA | SDGE | New Switchyard with East County-Boulevard East 138 kV line looped-in | East County | 156 | SCADSNV_Z3_GreaterImperial | 2020-12-01 | 2021-12-01 | NA | Complete | Complete | NA | Executed
VULCAN | 1534 | 2018-04-11 | 2018-04-16 | ACTIVE | C11 | Storage | Photovoltaic | Battery | Solar | 28.8 | 225 | 250 | Full Capacity |  | MARICOPA | AZ | SDGE | Hassayampa Switchyard 500kV Common Bus | Hassayampa | 86 | SCADSNV_Z3_GreaterImperial | 2021-05-01 | 2023-12-15 | NA | Complete | Complete | NA
IRVING STORAGE | 1539 | 2019-03-05 | 2019-05-07 | ACTIVE | ISP | Storage |  | Battery |  | 782.8 |  | 750 | Full Capacity |  | MONTEREY | CA | PGAE | Moss Landing Substation 500kV | Moss Landing | 140 | SPGE_Z3_Carrizo | 2022-12-01 | 2022-12-01 | NA | Complete | Complete | NA | In Progress
PLANO STORAGE | 1540 | 2019-03-05 | 2019-05-07 | ACTIVE | ISP | Storage |  | Battery |  | 365 |  | 350 | Full Capacity |  | MONTEREY | CA | PGAE | Moss Landing Substation 500kV | Moss Landing | 140 | SPGE_Z3_Carrizo | 2021-12-01 | 2021-12-01 | NA | Complete | Complete | NA | Executed
LORINER STORAGE | 1548 | 2019-04-06 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 30.48 |  | 30 | Full Capacity |  | SANTA CLARA | CA | PGAE | Morgan Hill Substation 115kV | Morgan Hill | 163 | None | 2022-11-30 | 2022-11-30 | NA |  |  | NA
TANAGER STORAGE | 1550 | 2019-04-02 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 200 |  | 200 | Full Capacity |  | SANTA CLARA | CA | PGAE | Los Esteros Substation 230kV | Los Esteros | 164 | None | 2023-06-30 | 2023-06-30 | NA | Complete |  | NA
CORMORANT STORAGE | 1552 | 2019-04-02 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 250 |  | 250 | Full Capacity |  | SAN FRANCISCO | CA | PGAE | Martin Substation 115kV | Martin | 165 | None | 2023-06-30 | 2023-06-30 | NA | Complete |  | NA
JEWELFLOWER STORAGE | 1553 | 2019-04-05 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 354.9 |  | 350 | Full Capacity |  | SANTA CLARA | CA | PGAE | Metcalf Substation 230kV | 0 | 166 | None | 2022-12-31 | 2022-12-31 | NA | Complete |  | NA
NOOSA ENERGY STORAGE | 1557 | 2019-04-15 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 100 |  | 99 | Full Capacity |  | SAN JOAQUIN | CA | PGAE | Ripon Substation 115kV | Ripon | 170 | SPGE_Z4_CentralValleyAndLosBanos | 2022-12-16 | 2022-12-16 | NA | Complete |  | NA
HYDASPES | 1558 | 2019-04-04 | 2018-04-15 | ACTIVE | C12 | Storage | Photovoltaic | Battery | Solar | 41.44 | 40.562 | 40 | Energy Only |  | STANISLAUS | CA | PGAE | Miller #1 Tap 115 kV | Mille | 171 | SPGE_Z4_CentralValleyAndLosBanos | 2022-12-31 | 2022-12-31 | NA | Complete |  | NA
DYNAMO SOLAR | 1565 | 2019-04-08 | 2019-04-15 | ACTIVE | C12 | Photovoltaic |  | Solar |  | 24.5 |  | 24.5 | Full Capacity |  | NAPA | CA | PGAE | Tulucay Substation 60kV | Tulucay | 175 | Norcal_Z4_Solano | 2023-06-30 | 2023-06-30 | NA | Complete |  | NA
AIR STATION 1 | 1568 | 2019-04-16 | 2019-04-15 | ACTIVE | C12 | Photovoltaic | Storage | Solar | Battery | 21.05 | 21.05 | 40 | Full Capacity |  | KINGS | CA | PGAE | Henrietta-Lemoore NAS 70 kV | 0 | 177 | SPGE_Z1_Westlands | 2021-12-31 | 2021-12-31 | NA | Complete |  | NA
ARCTURUS | 1586 | 2019-04-04 | 2019-04-15 | ACTIVE | C12 | Storage | Photovoltaic | Battery | Solar | 152.3 | 151.794 | 150 | Full Capacity |  | KERN | CA | PGAE | Arco Substation 230kV | Arco | 146 | SPGE_Z2_KernAndGreaterCarrizo | 2022-12-30 | 2022-12-30 | NA |  |  | NA
KINGSROAD HYBRID SOLAR | 1587 | 2019-04-16 | 2019-04-15 | ACTIVE | C12 | Storage | Photovoltaic | Battery | Solar | 101.8 | 101.78 | 100 | Full Capacity |  | KERN | CA | PGAE | Arco Substation 230kV | Arco | 146 | SPGE_Z2_KernAndGreaterCarrizo | 2023-11-30 | 2023-11-30 | NA | Complete |  | NA
CARTHAGE | 1591 | 2019-04-04 | 2019-04-15 | ACTIVE | C12 | Photovoltaic | Storage | Solar | Battery | 55.9 | 55.8 | 55 | Energy Only |  | KERN | CA | PGAE | Midway-Tupman-Rio Bravo-Renfro 115 kV | Midway | 184 | SPGE_Z2_KernAndGreaterCarrizo | 2022-12-31 | 2022-12-31 | NA | Complete |  | NA
PELICANS JAW HYBRID SOLAR | 1593 | 2019-04-09 | 2019-04-15 | ACTIVE | C12 | Storage | Photovoltaic | Battery | Solar | 500 | 500 | 500 | Full Capacity |  | KINGS | CA | PGAE | Gates-Midway 230 kV | Gates | 186 | SPGE_Z1_Westlands | 2022-11-30 | 2022-11-30 | NA | Complete |  | NA
GRAND LAKE HYBRID SOLAR | 1594 | 2019-04-15 | 2019-04-15 | ACTIVE | C12 | Storage | Photovoltaic | Battery | Solar | 250 | 254 | 250 | Full Capacity |  | KINGS | CA | PGAE | Gates-Midway 230kV | Gates | 187 | SPGE_Z1_Westlands | 2023-11-30 | 2023-11-30 | NA | Complete |  | NA
BUTTONBUSH SOLAR HYBRID ENERGY CENTER | 1596 | 2019-04-01 | 2019-04-15 | ACTIVE | C12 | Storage | Photovoltaic | Battery | Solar | 818 | 818 | 800 | Full Capacity |  | KERN | CA | PGAE | Midway Substation 500kV | Midway | 189 | SPGE_Z2_KernAndGreaterCarrizo | 2025-11-01 | 2025-11-01 | NA | Complete |  | NA
ARATINA SOLAR CENTER 2 | 1604 | 2019-04-01 | 2019-04-15 | ACTIVE | C12 | Storage | Photovoltaic | Battery | Solar | 200 | 200 | 200 | Full Capacity |  | KERN | CA | SCE | Kramer Substation 230kV | Kramer | 67 | GK_Z2_InyokernAndNorthOfKramer | 2022-06-01 | 2023-06-01 | NA | Complete |  | NA
AVOCET STORAGE | 1608 | 2019-04-01 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 200 |  | 200 | Full Capacity |  | LOS ANGELES | CA | SCE | Hinson Substation 230kV | Hinson | 197 | TehachapiOutsideTxConstraintZones | 2023-06-30 | 2023-06-30 | NA | Complete |  | NA
COMMERCE ENERGY STORAGE | 1611 | 2019-04-09 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 250 |  | 250 | Full Capacity |  | LOS ANGELES | CA | SCE | Laguna Bell Substation 230kV | Laguna Bell | 200 | TehachapiOutsideTxConstraintZones | 2023-01-01 | 2023-01-01 | NA | Complete |  | NA
SPEEDWAY ESS | 1612 | 2019-04-05 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 200 |  | 200 | Full Capacity |  | LOS ANGELES | CA | SCE | Rio Hondo Substation 230kV | Rio Hondo | 201 | TehachapiOutsideTxConstraintZones | 2023-12-01 | 2023-12-01 | NA | Complete |  | NA
KESTREL STORAGE | 1615 | 2019-04-01 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 200 |  | 200 | Full Capacity |  | LOS ANGELES | CA | SCE | Walnut Substation 220kV | Walnut | 203 | TehachapiOutsideTxConstraintZones | 2023-06-30 | 2023-06-30 | NA | Complete |  | NA
SEGS EXPANSION HYBRID | 1617 | 2019-04-05 | 2019-04-15 | ACTIVE | C12 | Storage | Photovoltaic | Battery | Solar | 73.26 | 82.4342 | 150 | Full Capacity |  | SAN BERNARDINO | CA | SCE | Kramer Substation 230kV | Kramer | 67 | GK_Z2_InyokernAndNorthOfKramer | 2022-12-01 | 2022-12-01 | NA | Complete |  | NA
GOLDBACK SOLAR CENTER | 1619 | 2019-04-12 | 2019-04-15 | ACTIVE | C12 | Storage | Photovoltaic | Battery | Solar | 500 | 500 | 500 | Full Capacity |  | VENTURA | CA | SCE | Moorpark Substation 230 kV | Moorpark | 206 | TehachapiOutsideTxConstraintZones | 2023-06-01 | 2024-04-01 | NA | Complete |  | NA
ANGELENO SOLAR FARM | 1625 | 2019-03-31 | 2019-04-15 | ACTIVE | C12 | Storage | Photovoltaic | Battery | Solar | 1150 | 1150 | 1150 | Full Capacity |  | LOS ANGELES | CA | SCE | Vincent Substation 500kV | Vincent | 210 | Tehachapi | 2023-06-01 | 2025-10-01 | NA | Complete |  | NA
FORT TEJON SOLAR | 1628 | 2019-04-05 | 2019-04-15 | ACTIVE | C12 | Photovoltaic | Storage | Solar | Battery | 310.2 | 306.26 | 300 | Full Capacity |  | LOS ANGELES | CA | SCE | Vincent Substation 230kV | Vincent | 92 | Tehachapi | 2023-12-31 | 2023-12-30 | NA | Complete |  | NA
HUMIDOR STORAGE 1 | 1629 | 2019-04-11 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 305 |  | 300 | Full Capacity |  | LOS ANGELES | CA | SCE | Vincent Substation 230 kV | Vincent | 211 | Tehachapi | 2021-12-01 | 2021-12-01 | NA | Complete |  | NA
GLENFELIZ SOLAR FARM | 1631 | 2019-04-01 | 2019-04-15 | ACTIVE | C12 | Storage | Photovoltaic | Battery | Solar | 500 | 500 | 500 | Full Capacity |  | KERN | CA | SCE | Windhub Substation 220kV | Windhub | 212 | Tehachapi | 2022-10-01 | 2023-06-01 | NA | Complete |  | NA
SANBORN HYBRID 3 | 1632 | 2019-04-05 | 2019-04-15 | ACTIVE | C12 | Storage | Photovoltaic | Battery | Solar | 671.6 | 778.546 | 1400 | Full Capacity |  | KERN | CA | SCE | Windhub Substation 500kV | Windhub | 213 | Tehachapi | 2023-12-01 | 2023-12-01 | NA | Complete |  | NA
CALYPSO SOLAR | 1636 | 2019-04-04 | 2019-04-15 | ACTIVE | C12 | Storage | Photovoltaic | Battery | Solar | 200 | 400 | 400 | Full Capacity |  | RIVERSIDE | CA | SCE | Colorado River Substation 230kV | Colorado River | 65 | SCADSNV_Z4_RiversideAndPalmSprings | 2023-12-01 | 2023-12-01 | NA | Complete |  | NA
RAMPA | 1641 | 2019-04-05 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 101 |  | 100 | Full Capacity |  | SAN BERNARDINO | CA | SCE | Etiwanda Substation 230kV | Etiwanda | 215 | KramerInyoOutsideTxConstraintZones | 2022-12-31 | 2022-12-31 | NA | Complete |  | NA
OBERON | 1642 | 2019-04-02 | 2019-04-15 | ACTIVE | C12 | Storage | Photovoltaic | Battery | Solar | 518.4 | 518.4 | 500 | Full Capacity |  | RIVERSIDE | CA | SCE | Red Bluff Substation 500kV | Red Bluff | 216 | SCADSNV_Z4_RiversideAndPalmSprings | 2022-12-31 | 2023-09-30 | NA | Complete |  | NA
LYCAN SOLAR | 1643 | 2019-04-04 | 2019-04-15 | ACTIVE | C12 | Photovoltaic | Storage | Solar | Battery | 400 | 200 | 400 | Full Capacity |  | RIVERSIDE | CA | SCE | Red Bluff Substation 500kV | Red Bluff | 216 | SCADSNV_Z4_RiversideAndPalmSprings | 2023-12-01 | 2023-12-01 | NA | Complete |  | NA
MENIFEE POWER BANK | 1645 | 2019-04-10 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 725 |  | 705 | Full Capacity |  | RIVERSIDE | CA | SCE | Valley Substation 500kV | Valley | 218 | Outside | 2022-12-01 | 2023-08-01 | NA | Complete |  | NA
DOUBLE BUTTE STORAGE | 1646 | 2019-04-05 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 507.6 |  | 500 | Full Capacity |  | RIVERSIDE | CA | SCE | Valley Substation 500 kV | Valley | 219 | Outside | 2022-12-31 | 2023-12-30 | NA | Complete |  | NA
ANGORA SOLAR FARM | 1647 | 2019-04-02 | 2019-04-15 | ACTIVE | C12 | Storage | Photovoltaic | Battery | Solar | 700 | 700 | 700 | Full Capacity |  | CLARK | NV | SCE | Mohave Substation 500kV | Mohave | 96 | SCADSNV_Z5_SCADSNV | 2022-10-01 | 2025-04-01 | NA | Complete |  | NA
BONANZA SOLAR | 1649 | 2019-04-05 | 2019-04-15 | ACTIVE | C12 | Storage | Photovoltaic | Battery | Solar | 150 | 300 | 300 | Full Capacity |  | CLARK/NYE | NV | GLW | Innovation 230kV Sub | Innovation | 220 | SCADSNV_Z5_SCADSNV | 2023-12-01 | 2023-12-01 | NA | Complete |  | NA
ROUGH HAT HYBRID SOLAR | 1650 | 2019-04-15 | 2019-04-15 | ACTIVE | C12 | Photovoltaic | Storage | Solar | Battery | 204 | 200 | 200 | Full Capacity |  | NYE | NV | GLW | Trout Canyon Switching Station 230kV | Trout Canyon | 221 | SCADSNV_Z5_SCADSNV | 2022-11-30 | 2022-11-30 | NA | Complete |  | NA
YELLOW PINE 3 | 1654 | 2019-04-09 | 2019-04-15 | ACTIVE | C12 | Photovoltaic | Storage | Solar | Battery | 262 | 254.98 | 250 | Full Capacity |  | CLARK | NV | GLW | Trout Canyon Substation 230kV | Trout Canyon | 222 | SCADSNV_Z5_SCADSNV | 2025-12-31 | 2025-12-31 | NA | Complete |  | NA
BONANZA PEAK SOLAR FARM | 1655 | 2019-04-12 | 2019-04-12 | ACTIVE | C12 | Storage | Photovoltaic | Battery | Solar | 200 | 441 | 400 | Full Capacity |  | CLARK AND NYE | NV | GLW | Trout Canyon Switching Station 230kV | Trout Canyon | 221 | SCADSNV_Z5_SCADSNV | 2022-12-16 | 2022-12-16 | NA | Complete |  | NA
GYPSY ESS | 1656 | 2019-04-04 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 200 |  | 200 | Full Capacity |  | SAN DIEGO | CA | SDGE | Bay-Boulevard 230kV | Bay | 223 |  | 2023-12-01 | 2023-12-01 | NA | Complete |  | NA
SANDPIPER STORAGE | 1657 | 2019-04-02 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 200 |  | 200 | Full Capacity |  | ORANGE | CA | SDGE | Talega 138kV |  |  |  | 2023-06-30 | 2023-06-30 | NA | Complete |  | NA
CARDINAL STORAGE | 1658 | 2019-04-01 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 200 |  | 200 | Full Capacity |  | IMPERIAL | CA | SDGE | Imperial Valley Substation 230kV | Imperial | 7 | SCADSNV_Z3_GreaterImperial | 2023-06-30 | 2023-06-30 | NA | Complete |  | NA
CIMARRON WIND | 1660 | 2019-03-29 | 2019-04-15 | ACTIVE | C12 | Wind Turbine |  | Wind Turbine |  | 352.5 |  | 300 | Full Capacity |  | TIJUANA | MX | SDGE | ECO Substation 230kV | East County | 225 | SCADSNV_Z3_GreaterImperial | 2023-12-31 | 2024-12-31 | NA | Complete |  | NA
OBSIDIAN WIND | 1661 | 2019-04-05 | 2019-04-15 | ACTIVE | C12 | Wind Turbine |  | Wind Turbine |  | 300 |  | 300 | Full Capacity |  | BAJA CALIFORNIA | MX | SDGE | ECO Substation 230kV | East County | 225 | SCADSNV_Z3_GreaterImperial | 2024-12-01 | 2024-12-01 | NA | Complete |  | NA
VENTASSO ENERGY STORAGE | 1662 | 2019-04-06 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 50.77 |  | 50 | Full Capacity |  | SAN DIEGO | CA | SDGE | EI Cajon Substation 69kV | EI Cajon | 226 |  | 2022-11-30 | 2022-11-30 | NA | Complete |  | NA
HOODINI | 1663 | 2019-04-13 | 2019-04-15 | ACTIVE | C12 | Storage | Photovoltaic | Battery | Solar | 112.6 | 459.54 | 450 | Full Capacity |  | YUMA COUNTY | AZ | SDGE | Hoodoo Wash Substation 500kV | Hoodoo | 126 | SCADSNV_Z3_GreaterImperial | 2023-05-31 | 2023-05-31 | NA | Complete |  | NA
CUCAPA ENERGIA | 1664 | 2019-03-29 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 500 |  | 500 | Full Capacity |  | SONORA | MX | SDGE | Imperial Valley Substation 230kV | Imperial | 7 | SCADSNV_Z3_GreaterImperial | 2021-12-31 | 2021-12-31 | NA | Complete |  | NA
KINGSLEY SOLAR FARM | 1665 | 2019-04-01 | 2019-04-15 | ACTIVE | C12 | Storage | Photovoltaic | Battery | Solar | 360 | 360 | 360 | Full Capacity |  | IMPERIAL | CA | SDGE | Imperial Valley Substation 230kV | Imperial | 7 | SCADSNV_Z3_GreaterImperial | 2023-06-01 | 2023-06-01 | NA | Complete |  | NA
WISTARIA RANCH SOLAR 2 | 1667 | 2019-04-12 | 2019-04-15 | ACTIVE | C12 | Photovoltaic | Storage | Solar | Battery | 153.7 | 52.13 | 150 | Full Capacity |  | IMPERIAL | CA | SDGE | Imperial Valley Substation 230kV | Imperial | 7 | SCADSNV_Z3_GreaterImperial | 2022-12-31 | 2022-12-31 | NA |  |  | NA
POME BESS | 1669 | 2019-04-13 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 101.5 |  | 100 | Full Capacity |  | SAN DIEGO | CA | SDGE | Pomerado Substation 69kV | Pomerado | 228 | GreaterImpOutsideTxConstraintZones | 2023-05-31 | 2023-05-31 | NA | Complete |  | NA
PEREGRINE STORAGE | 1670 | 2019-04-01 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 200 |  | 200 | Full Capacity |  | SAN DIEGO | CA | SDGE | Silvergate Substation 230kV | Silvergate | 229 | GreaterImpOutsideTxConstraintZones | 2023-06-30 | 2023-06-30 | NA | Complete |  | NA
MARINE DEPOT | 1671 | 2019-04-16 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 26.6 |  | 25 | Full Capacity |  | SAN DEIGO | CA | SDGE | Point Loma Substation 69kV | Point Loma | 230 | GreaterImpOutsideTxConstraintZones | 2021-12-31 | 2021-12-31 | NA | Complete |  | NA
NIGHTHAWK STORAGE | 1673 | 2019-04-02 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 300 |  | 300 | Full Capacity |  | SAN DIEGO | CA | SDGE | Sycamore Canyon Substation 138kV | Sycamore Canyon | 232 | GreaterImpOutsideTxConstraintZones | 2023-06-30 | 2023-06-30 | NA | Complete |  | NA
RESAVA ENERGY STORAGE | 1675 | 2019-04-05 | 2019-04-15 | ACTIVE | C12 | Storage |  | Battery |  | 20 |  | 20 | Energy Only |  | SAN DIEGO | CA | SDGE | Valley Center 69kV | Valley | 234 | SCADSNV_Z3_GreaterImperial | 2021-12-31 | 2021-12-31 | NA | Complete |  | NA
HARQUAHALA SUNRISE | 1678 | 2020-03-13 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 308.9 | 308.926 | 300 | Full Capacity |  | MARICOPA | AZ | DCRT | Delaney |  |  |  | 2022-04-01 | 2022-04-01 | NA |  |  | NA
POINT WIND FAST TRACK | 1679 | 2020-03-30 | 2020-04-14 | ACTIVE | FT | Wind Turbine |  | Wind Turbine |  | 1.62 |  | 1.5374 | Energy Only | Economic Only | KERN | CA | SCE | Vincent Sub |  |  |  | 2020-11-01 | 2020-11-01 |  | NA | NA | NA
RE GARLAND LLC | 1680 | 2020-01-29 | 2020-05-13 | ACTIVE | FT | Photovoltaic |  | Solar |  | 5 |  | 5 | Energy Only |  | KERN | CA | SCE | Whirlwind Substation |  |  |  | 2019-08-03 | 2019-08-03 |  | NA | NA | NA
BRISBANE ENERGY STORAGE | 1682 | 2020-04-10 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 253.7 |  | 250 | Full Capacity |  | SAN MATEO | CA | PGAE | Martin |  |  |  | 2023-10-15 | 2023-10-15 | NA |  |  | NA
BUENA VISTA EXPANSION | 1683 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Wind Turbine |  | Wind Turbine |  | 102 |  | 100 | Full Capacity | Off-Peak Deliverability | CONTRA COSTA | CA | PGAE | Contra Costa-Delta Switchyard 230 kV Line |  |  |  | 2023-12-31 | 2023-12-31 | NA |  |  | NA
CAPETOWN 3 HYBRID | 1684 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Wind Turbine | Storage | Wind Turbine | Battery | 97.2 | 61.0139 | 150 | Full Capacity | Off-Peak Deliverability | HUMBOLDT | CA | PGAE | Bridgeville Substation 115kV | Bridgeville | 160 | Norcal_Z2_Humboldt | 2023-12-01 | 2023-12-01 | NA |  |  | NA
CHIA ESS | 1685 | 2020-04-07 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 300 |  | 300 | Full Capacity |  | ALAMEDA | CA | PGAE | Cayetano Substation 230kV | Cayetano | 100 | Norcal_Z4_Solano | 2025-12-01 | 2025-12-01 | NA |  |  | NA
CHICKAREE HYBRID SOLAR | 1686 | 2020-04-01 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 86.7 | 86.7 | 85 | Full Capacity | Off-Peak Deliverability | BUTTE | CA | PGAE | Table Mountain Substation 115kV |  |  |  | 2023-12-31 | 2023-12-31 | NA |  |  | NA
CONAWAY HYBRID POWER PLANT | 1687 | 2020-04-08 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 84.81 | 84.9957 | 80 | Full Capacity | Off-Peak Deliverability | YOLO | CA | PGAE | Woodland - Davis 115 kV |  |  |  | 2023-01-01 | 2023-01-01 | NA |  |  | NA
CROSSROADS STORAGE | 1688 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 313 |  | 299.99 | Full Capacity |  | SHASTA | CA | PGAE | Round Mountain Substation 230kV |  |  |  | 2024-11-30 | 2024-11-30 | NA |  |  | NA
CROWSWEST | 1689 | 2020-04-07 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 20.2 | 10 | 20 | Full Capacity | Off-Peak Deliverability | STANISLAUS | CA | PGAE | Crow Creek Switching Station 60kV | Crow Creek | 101 |  | 2023-12-30 | 2023-12-30 | NA |  |  | NA
DENALI ENERGY STORAGE | 1690 | 2020-04-14 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 102 |  | 101.2 | Full Capacity |  | SAN JAUQUIN | CA | PGAE | Vierra Substation 115kV |  |  |  | 2023-06-15 | 2023-06-15 | NA |  |  | NA
FORTIS | 1691 | 2020-04-09 | 2020-04-15 | ACTIVE | C13 | Wind Turbine | Storage | Wind Turbine | Battery | 207.2 | 203.94 | 200 | Full Capacity | Off-Peak Deliverability | SOLANO | CA | PGAE | BIRDS LANDING SWITCHING STATION 230kV | Birds Landing | 138 | Norcal_Z4_Solano | 2024-12-15 | 2024-12-15 | NA |  |  | NA
INTREPID ENERGY | 1692 | 2020-04-12 | 2020-04-15 | ACTIVE | C13 | Wind Turbine | Storage | Wind Turbine | Battery | 1568 | 319.356 | 1500.12 | Full Capacity | Off-Peak Deliverability | HUMBOLDT | CA | PGAE | Round Mountain Substation 500kV | Round | 172 | NorCalOutsideTxConstraintZones | 2027-04-15 | 2027-04-15 | NA |  |  | NA
MAYA | 1694 | 2020-04-14 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 102.8 |  | 100 | Full Capacity |  | CONTRA COSTA | CA | PGAE | Pittsburg Substation 60kV |  |  |  | 2023-12-31 | 2023-12-31 | NA |  |  | NA
MEADOWS ENERGY STORAGE | 1695 | 2020-04-14 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 102 |  | 101.2 | Full Capacity |  | PLACER | CA | PGAE | Atlantic Substation 60kV |  |  |  | 2023-06-15 | 2023-06-15 | NA |  |  | NA
MENARD ENERGY STORAGE | 1696 | 2020-04-14 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 950.4 |  | 900 | Full Capacity |  | SOLANO | CA | PGAE | Vaca-Dixon Substation 500kV |  |  |  | 2023-08-01 | 2023-08-01 | NA |  |  | NA
NORTH BAY ENERGY STORAGE | 1700 | 2020-04-14 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 102.8 |  | 100 | Full Capacity |  | NAPA COUNTY | CA | PGAE | Lakeville Substation 60kV |  |  |  | 2023-06-01 | 2023-06-01 | NA |  |  | NA
POTENTIA-VIRDI | 1702 | 2020-04-13 | 2020-04-15 | ACTIVE | C13 | Wind Turbine | Photovoltaic | Wind Turbine | Solar | 408.8 | 410.04 | 400 | Full Capacity | Off-Peak Deliverability | SAN JOAQUIN | CA | PGAE | Tesla Substation 500 kV |  |  |  | 2024-12-15 | 2024-12-15 | NA |  |  | NA
RAILYARD ENERGY STORAGE | 1703 | 2020-04-10 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 150.9 |  | 150 | Full Capacity |  | SANTA CLARA | CA | PGAE | New Switchyard on Los Esteros-Trimble Line 115kV |  |  |  | 2023-10-15 | 2023-10-15 | NA |  |  | NA
STEEL CITY BATTERY STORAGE | 1705 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 675 |  | 220 | Full Capacity |  | CONTRA COSTA | CA | PGAE | Pittsburg Substation 230kV | 0 | 168 | None | 2025-06-30 | 2025-06-30 | NA |  |  | NA
ROSEMARY | 1709 | 2020-04-10 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 36.17 | 36.1746 | 35 | Full Capacity | Off-Peak Deliverability | FRESNO | CA | PGAE | Crescent Switching Station 70kV | Crescent | 110 |  | 2023-12-01 | 2023-12-01 | NA |  |  | NA
ALBA | 1710 | 2020-04-03 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 154.8 | 77.638 | 150 | Full Capacity | Off-Peak Deliverability | FRESNO | CA | PGAE | Mendota Substation 115kV | Mendota | 53 | SPGE_Z1_Westlands | 2023-10-31 | 2023-10-31 | NA |  |  | NA
ALLIUM | 1711 | 2020-04-10 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 114.6 | 114.553 | 110 | Full Capacity | Off-Peak Deliverability | SAN BENITO | CA | PGAE | Hollister Substation 115kV |  |  |  | 2023-12-01 | 2023-12-01 | NA |  |  | NA
APRICOT ENERGY STORAGE | 1712 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 30.6 |  | 30 | Full Capacity |  | FRESNO | CA | PGAE | Cheney #1 Tap 115kV Line |  |  |  | 2023-07-01 | 2023-07-01 | NA |  |  | NA
BIA BESS 1 | 1713 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 33.32 |  | 32 | Full Capacity |  | KINGS | CA | PGAE | GWF Switching Station 115 kV |  |  |  | 2023-08-01 | 2023-08-01 | NA |  |  | NA
COMAL FLATS 1 | 1714 | 2020-04-02 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 202.5 | 202.5 | 200 | Full Capacity | Off-Peak Deliverability | FRESNO | CA | PGAE | Gates Substation 230kV | Gates | 35 | SPGE_Z1_Westlands | 2024-09-30 | 2024-09-30 | NA |  |  | NA
EDGEWOOD SOLAR HYBRID | 1715 | 2020-04-02 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 1700 | 1700 | 1700 | Full Capacity | Off-Peak Deliverability | FRESNO | CA | PGAE | Los Banos - Gates #1 500kV line |  |  |  | 2024-11-01 | 2024-11-01 | NA |  |  | NA
FOXGLOVE HYBRID SOLAR | 1717 | 2020-04-01 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 102.5 | 102.5 | 100 | Full Capacity | Off-Peak Deliverability | MADERA | CA | PGAE | Borden Substation 70kV |  |  |  | 2023-12-31 | 2023-12-31 | NA |  |  | NA
GONZAGA HYBRID | 1718 | 2020-04-14 | 2020-04-15 | ACTIVE | C13 | Storage | Wind Turbine | Battery | Wind Turbine | 54.94 | 60.45 | 103.65 | Full Capacity | Off-Peak Deliverability | MERCED | CA | PGAE | Los Banos Substation 70kV | Los Banos | 106 | SPGE_Z1_Westlands | 2024-07-01 | 2024-07-01 | NA |  |  | NA
MILKY WAY HYBRID SOLAR | 1721 | 2020-04-10 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 175 | 355.2 | 350 | Full Capacity | Off-Peak Deliverability | KINGS | CA | PGAE | Gates- Templeton 230kV line |  |  |  | 2023-11-30 | 2023-11-30 | NA |  |  | NA
MORTIMER SOLAR HYBRID | 1722 | 2020-04-01 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 250 | 250 | 250 | Full Capacity | Off-Peak Deliverability | KINGS | CA | PGAE | Mustang Switching Station 230kV | Mustang | 59 | SPGE_Z1_Westlands | 2024-04-01 | 2024-04-01 | NA |  |  | NA
ROCK DOVE 1 ENERGY CENTER | 1724 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 387.9 | 312.96 | 300 | Full Capacity | Off-Peak Deliverability | KERN | CA | PGAE | Arco - Midway 230kV line |  |  |  | 2024-11-30 | 2024-11-30 | NA |  |  | NA
TORANA HYBRID SOLAR | 1726 | 2020-04-01 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 102.5 | 102.5 | 100 | Full Capacity | Off-Peak Deliverability | MERCED | CA | PGAE | Los Banos Substation 70kV | Los Banos | 106 | SPGE_Z1_Westlands | 2023-12-31 | 2023-12-31 | NA |  |  | NA
ZETA | 1728 | 2020-04-10 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 77.48 | 77.4774 | 75 | Full Capacity | Off-Peak Deliverability | MERCED | CA | PGAE | Mercy Springs Switching Station 70kV |  |  |  | 2023-12-01 | 2023-12-01 | NA |  |  | NA
ANACAPA | 1729 | 2020-04-03 | 2020-04-15 | ACTIVE | C13 | Storage | Solar Thermal | Battery | Solar | 103.2 | 206.2 | 200 | Full Capacity | Off-Peak Deliverability | SANTA BARBARA | CA | PGAE | Sisquoc Substation 115kV |  |  |  | 2023-10-31 | 2023-10-31 | NA |  |  | NA
AUSTIN ES | 1730 | 2019-10-15 | 2020-04-15 | ACTIVE | ISP | Storage |  | Battery |  | 203.6 |  | 200 | Full Capacity |  | SAN LUIS OBISPO | CA | PGAE | Morro Bay Substation 230kV | Morro Bay | 192 | SPGE_Z2_KernAndGreaterCarrizo | 2024-12-01 | 2024-12-01 | NA |  |  | NA
BLACK BEAR ENERGY STORAGE 1 | 1731 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 102 |  | 100 | Full Capacity |  | SAN LUIS OBISPO | CA | PGAE | Mesa Substation 115kV |  |  |  | 2023-02-01 | 2023-02-01 | NA |  |  | NA
BLACK BEAR ENERGY STORAGE 2 | 1732 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 102 |  | 100 | Full Capacity |  | SAN LUIS OBISPO | CA | PGAE | Mesa Substation 230kV | Mesa Substation | 139 | SPGE_Z3_Carrizo | 2023-02-01 | 2023-02-01 | NA |  |  | NA
BLUFF TRAIL STORAGE | 1733 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 632.4 |  | 500 | Full Capacity |  | SAN LUIS OBISPO | CA | PGAE | MesaSubstation 230kV |  |  |  | 2024-11-30 | 2024-11-30 | NA |  |  | NA
HAWKINS SOLAR HYBRID | 1736 | 2020-04-01 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 250 | 250 | 250 | Full Capacity | Off-Peak Deliverability | KERN | CA | PGAE | ARCO Substation 230kV | Arco | 146 | SPGE_Z2_KernAndGreaterCarrizo | 2024-04-01 | 2024-04-01 | NA |  |  | NA
KAIROS HYBRID | 1737 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 179.4 | 359.352 | 350 | Full Capacity | Off-Peak Deliverability | KERN | CA | PGAE | Midway Substation 230kV |  |  |  | 2025-10-30 | 2025-10-30 | NA |  |  | NA
LIGHTHOUSE WIND | 1738 | 2020-04-01 | 2020-04-15 | ACTIVE | C13 | Wind Turbine |  | Wind Turbine |  | 1456 |  | 1400 | Full Capacity | Off-Peak Deliverability | SAN LUIS OBISPO | NN | PGAE | Diablo Canyon Switching Station 500kV |  |  |  | 2027-03-01 | 2027-03-01 | NA |  |  | NA
PECHO ENERGY STORAGE | 1739 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Storage | Other | Battery | Other | 108 | 520 | 500 | Full Capacity |  | SAN LUIS OBISPO | CA | PGAE | Morro Bay Switching Station 230kV |  |  |  | 2023-06-01 | 2023-06-01 | NA |  |  | NA
PUFF HYBRID SOLAR | 1740 | 2020-04-14 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 101.8 | 101.8 | 100 | Full Capacity | Off-Peak Deliverability | KERN | CA | PGAE | Arco Substation 230kV | Arco | 146 | SPGE_Z2_KernAndGreaterCarrizo | 2024-11-30 | 2024-11-30 | NA |  |  | NA
ROBIN 2 | 1741 | 2020-04-08 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 104 | 204.12 | 200 | Full Capacity | Off-Peak Deliverability | SAN LUIS OBISPO | CA | PGAE | Morro Bay Solar Sw Sta #2 230kV |  |  |  | 2023-12-01 | 2023-12-01 | NA |  |  | NA
ROBIN 3 | 1742 | 2020-04-08 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 79.2 | 155.925 | 150 | Full Capacity | Off-Peak Deliverability | SAN LUIS OBISPO | CA | PGAE | Temblor - San Luis Obispo 115kV line |  |  |  | 2023-12-01 | 2023-12-01 | NA |  |  | NA
SAGRARIO | 1743 | 2020-04-02 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 51.4 | 103.456 | 100 | Full Capacity | Off-Peak Deliverability | KERN | CA | PGAE | Old River Substation 70kV |  |  |  | 2023-10-31 | 2023-10-31 | NA |  |  | NA
SECOND FIDDLE | 1744 | 2020-04-02 | 2020-04-15 | ACTIVE | C13 | Solar Thermal | Storage | Solar | Battery | 103.5 | 51.401 | 100 | Full Capacity | Off-Peak Deliverability | KERN | CA | PGAE | Lamont Substation 115kV |  |  |  | 2023-10-31 | 2023-10-31 | NA |  |  | NA
SUNRISE POWER IMPROVEMENT | 1745 | 2020-04-06 | 2020-04-15 | ACTIVE | C13 | Combined Cycle |  | Natural Gas |  | 655.7 |  | 635 | Full Capacity |  | KERN | NN | PGAE | Midway Substation 230kV |  |  |  | 2023-06-01 | 2023-06-01 | NA |  |  | NA
VERBENA | 1746 | 2020-04-10 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 123.6 | 123.597 | 120 | Full Capacity | Off-Peak Deliverability | KERN | CA | PGAE | Tupman Substation 115kV |  |  |  | 2023-12-01 | 2023-12-01 | NA |  |  | NA
VINSON ENERGY | 1747 | 2020-04-08 | 2020-04-15 | ACTIVE | C13 | Wind Turbine | Storage | Wind Turbine | Battery | 1568 | 319.35 | 1499.94 | Full Capacity | Off-Peak Deliverability | SAN LUIS OBISPO | CA | PGAE | Diablo-Gates 500kV line |  |  |  | 2027-04-13 | 2027-04-13 | NA |  |  | NA
WESTERN COAST WIND 1 | 1748 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Wind Turbine |  | Wind Turbine |  | 1021 |  | 1000 | Full Capacity | Off-Peak Deliverability | SAN LUIS OBISPO | CA | PGAE | Diablo Canyon Substation 230kV |  |  |  | 2027-04-07 | 2027-04-07 | NA |  |  | NA
WHALE ROCK ENERGY | 1749 | 2020-04-13 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 100.6 | 53.68 | 299.93 | Full Capacity | Off-Peak Deliverability | SAN LUIS OBISPO | CA | PGAE | Caliente Switching Station 230kV |  |  |  | 2024-12-31 | 2024-12-31 | NA |  |  | NA
WINDWALKER OFFSHORE | 1750 | 2020-04-11 | 2020-04-15 | ACTIVE | C13 | Wind Turbine |  | Wind Turbine |  | 1029 |  | 1000 | Full Capacity | Off-Peak Deliverability | SAN LUIS OBISPO | CA | PGAE | Diablo Canyon Switching Station 500kV |  |  |  | 2027-03-31 | 2027-03-31 | NA |  |  | NA
WINSTON HYBRID PV AND BESS | 1751 | 2020-04-08 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 102 | 204 | 200 | Full Capacity | Off-Peak Deliverability | KERN | CA | PGAE | Midway Substation 115kV | Midway | 111 | SPGE_Z2_KernAndGreaterCarrizo | 2025-03-01 | 2025-03-01 | NA |  |  | NA
ARIZONA A1 | 1752 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 1572 | 2072.52 | 2000 | Full Capacity | Off-Peak Deliverability | MARICOPA | AZ | DCRT | Delaney Substation 500kV |  |  |  | 2025-02-05 | 2025-02-05 | NA |  |  | NA
LA PAZ | 1753 | 2020-04-02 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 526.7 | 415.96 | 500 | Full Capacity | Off-Peak Deliverability | MARICOPA | AZ | DCRT | Delaney - Colorado River 500kV line |  |  |  | 2024-12-01 | 2024-12-01 | NA |  |  | NA
PAPAGO | 1754 | 2020-04-11 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 307.2 | 306.18 | 300 | Full Capacity | Off-Peak Deliverability | MARICOPA | AZ | DCRT | Delaney Substation 500kV |  |  |  | 2023-10-31 | 2023-10-31 | NA |  |  | NA
ASTRA | 1756 | 2020-04-09 | 2020-04-15 | ACTIVE | C13 | Storage | Wind Turbine | Battery | Wind Turbine | 205.9 | 207.2 | 200 | Full Capacity | Off-Peak Deliverability | RIVERSIDE | CA | SCE | BLYTHE SUBSTATION 161kV |  |  |  | 2024-12-15 | 2024-12-15 | NA |  |  | NA
COBALT | 1757 | 2020-04-11 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 256.2 | 256.41 | 250 | Full Capacity | Off-Peak Deliverability | RIVERSIDE | CA | SCE | Colorado River Substation 220kV | Colorado River | 66 | SCADSNV_Z4_RiversideAndPalmSprings | 2023-10-31 | 2023-10-31 | NA |  |  | NA
DESERT SANDS | 1758 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 313 | 312.96 | 300 | Full Capacity | Off-Peak Deliverability | RIVERSIDE | CA | SCE | Devers Substation 230kV | Devers | 87 | 0 | 2024-11-30 | 2024-11-30 | NA |  |  | NA
ETERNAL PUMPED STORAGE | 1759 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Storage |  | Pumped-Storage hydro |  | 1407 |  | 1400 | Full Capacity |  | RIVERSIDE | CA | SCE | Red Bluff Substation 500kV | Red Bluff | 216 | SCADSNV_Z4_RiversideAndPalmSprings | 2026-12-01 | 2026-12-01 | NA |  |  | NA
FORTUNA | 1760 | 2020-04-11 | 2020-04-15 | ACTIVE | C13 | Wind Turbine | Storage | Wind Turbine | Battery | 207.2 | 205.92 | 200 | Full Capacity | Off-Peak Deliverability | RIVERSIDE | CA | SCE | DEVERS SUBSTATION 220kV | Devers | 153 | 0 | 2024-12-15 | 2024-12-15 | NA |  |  | NA
GRACE ENERGY CENTER | 1761 | 2020-04-14 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 508.6 | 508.56 | 500 | Full Capacity | Off-Peak Deliverability | RIVERSIDE | CA | SCE | Colorado River Substation 230kV | Colorado River | 65 | SCADSNV_Z4_RiversideAndPalmSprings | 2024-11-30 | 2024-11-30 | NA |  |  | NA
GRISEDALE STORAGE 1 | 1762 | 2020-04-13 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 510 |  | 500 | Full Capacity |  | RIVERSIDE | CA | SCE | Devers Substation 230kV | Devers | 87 | 0 | 2022-11-15 | 2022-11-15 | NA |  |  | NA
PORTA | 1763 | 2020-04-09 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 204.2 | 203.76 | 200 | Full Capacity | Off-Peak Deliverability | RIVERSIDE | CA | SCE | DEVERS SUBSTATION 220kV | Devers | 153 | 0 | 2024-12-15 | 2024-12-15 | NA |  |  | NA
SAPPHIRE SOLAR | 1764 | 2020-04-07 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 65.68 | 126.291 | 117 | Full Capacity | Off-Peak Deliverability | RIVERSIDE | CA | SCE | Red Bluff Substation 230kV | Red Bluff | 12 | SCADSNV_Z4_RiversideAndPalmSprings | 2024-12-01 | 2024-12-01 | NA |  |  | NA
BULLDOG ENERGY STORAGE | 1765 | 2020-04-14 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 408.1 |  | 400 | Full Capacity |  | LOS ANGELES | CA | SCE | Rio Hondo Substation 220kV | Rio Hondo | 202 | TehachapiOutsideTxConstraintZones | 2023-06-01 | 2023-06-01 | NA |  |  | NA
COMMERCE ENERGY STORAGE 2 | 1766 | 2020-04-14 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 250 |  | 250 | Full Capacity |  | LOS ANGELES | CA | SCE | Laguna Bell Substation 230kV | Laguna Bell | 200 | TehachapiOutsideTxConstraintZones | 2023-12-01 | 2023-12-01 | NA |  |  | NA
ROADHOUSE STORAGE | 1768 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 313 |  | 300 | Full Capacity |  | SAN BERNARDINO | CA | SCE | Mira Loma Substation 230kV |  |  |  | 2024-11-30 | 2024-11-30 | NA |  |  | NA
SWAN ESS | 1770 | 2020-04-07 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 300 |  | 300 | Full Capacity |  | SAN BERNARDINO | CA | SCE | Mira Loma Substation 230kV |  |  |  | 2025-12-01 | 2025-12-01 | NA |  |  | NA
OVERNIGHT SOLAR | 1774 | 2020-04-09 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 150 | 150 | 150 | Full Capacity | Off-Peak Deliverability | SAN BERNARDINO | CA | SCE | Kramer Substation 230kV | Kramer | 67 | GK_Z2_InyokernAndNorthOfKramer | 2024-10-31 | 2024-10-31 | NA |  |  | NA
SEGS EXPANSION 2 HYBRID | 1775 | 2020-04-11 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 54.59 | 54.5914 | 100 | Full Capacity | Off-Peak Deliverability | SAN BERNARDINO | CA | SCE | Kramer Junction Substation 230kV |  |  |  | 2023-12-15 | 2023-12-15 | NA |  |  | NA
VENTOSO | 1776 | 2020-04-11 | 2020-04-15 | ACTIVE | C13 | Wind Turbine | Photovoltaic | Wind Turbine | Solar | 212.2 | 206.59 | 200 | Full Capacity | Off-Peak Deliverability | SAN BERNARDINO | CA | SCE | COOLWATER SUBSTATION 115kV | Coolwater | 90 | GK_Z1_GreaterKramer | 2024-12-15 | 2024-12-15 | NA |  |  | NA
ALTA 20 WIND | 1778 | 2020-04-14 | 2020-04-15 | ACTIVE | C13 | Wind Turbine |  | Wind Turbine |  | 257.6 |  | 250 | Full Capacity | Off-Peak Deliverability | KERN | CA | SCE | Windhub Substation 230kV | Windhub | 91 | Tehachapi | 2023-10-15 | 2023-10-15 | NA |  |  | NA
BELLEFIELD 3 SOLAR FARM | 1779 | 2020-04-01 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 150 | 150 | 150 | Full Capacity | Off-Peak Deliverability | KERN | CA | SCE | Windhub Substation 230kV | Windhub | 91 | Tehachapi | 2023-04-01 | 2023-04-01 | NA |  |  | NA
BOBCAT ENERGY STORAGE | 1780 | 2020-04-10 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 75 |  | 75 | Full Capacity |  | LOS ANGELES | CA | SCE | Antelope Substation 66kV | Antelope | 94 | Tehachapi | 2022-07-01 | 2022-07-01 | NA |  |  | NA
GEM ENERGY STORAGE | 1782 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Storage | Other | Battery | Other | 108 | 512 | 500 | Full Capacity |  | KERN | CA | SCE | Whirlwind Substation 230kV | Whirlwind | 14 | Tehachapi | 2023-06-01 | 2023-06-01 | NA |  |  | NA
HARBOR ENERGY STORAGE | 1783 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 560 |  | 560 | Full Capacity |  | VENTURA | CA | SCE | Mandalay Switchyard 220kV |  |  |  | 2023-07-01 | 2023-07-01 | NA |  |  | NA
KEYHOLE WIND | 1784 | 2020-04-06 | 2020-04-15 | ACTIVE | C13 | Wind Turbine |  | Wind Turbine |  | 100 |  | 100 | Full Capacity | Off-Peak Deliverability | KERN | CA | SCE | Whirlwind Substation 230kV | Whirlwind | 14 | Tehachapi | 2024-12-01 | 2024-12-01 | NA |  |  | NA
LONGHORN 1 | 1786 | 2020-04-02 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 405.8 | 405.8 | 400 | Full Capacity | Off-Peak Deliverability | KERN | CA | SCE | Windhub Substation 500kV | Windhub | 213 | Tehachapi | 2024-09-30 | 2024-09-30 | NA |  |  | NA
LYCKA SOLAR | 1787 | 2020-04-11 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 122.5 | 464.42 | 460 | Full Capacity | Off-Peak Deliverability | TULARE | CA | SCE | Springville Substation 230kV |  |  |  | 2024-04-15 | 2024-04-15 | NA |  |  | NA
METEORITE SOLAR | 1788 | 2020-04-06 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 400 | 200 | 400 | Full Capacity | Off-Peak Deliverability | KERN | CA | SCE | Whirlwind Substation 230 kV | Whirlwind | 45 | Tehachapi | 2024-12-01 | 2024-12-01 | NA |  |  | NA
REXFORD 2 SOLAR FARM | 1789 | 2020-04-01 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 200 | 200 | 200 | Full Capacity | Off-Peak Deliverability | TULARE | CA | SCE | Vestal Substation 230kV | Vestal | 150 | 0 | 2023-04-01 | 2023-04-01 | NA |  |  | NA
SANBORN HYBRID 4 | 1790 | 2020-04-10 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 54.59 | 54.5914 | 100 | Full Capacity | Off-Peak Deliverability | KERN | CA | SCE | Windhub Substation 230kV | Windhub | 91 | Tehachapi | 2022-12-15 | 2022-12-15 | NA |  |  | NA
SANBORN 5 HYBRID | 1791 | 2020-04-10 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 1028 |  | 1000 | Full Capacity |  | KERN | CA | SCE | Windhub Substation 230kV | Windhub | 91 | Tehachapi | 2024-12-15 | 2024-12-15 | NA |  |  | NA
SEQUOIA | 1792 | 2020-04-03 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 103 | 206.13 | 200 | Full Capacity | Off-Peak Deliverability | TULARE | CA | SCE | Vestal Substation 230 kV |  |  |  | 2023-10-31 | 2023-10-31 | NA |  |  | NA
VALOREM | 1793 | 2020-04-11 | 2020-04-15 | ACTIVE | C13 | Storage | Wind Turbine | Battery | Wind Turbine | 203.9 | 207.2 | 200 | Full Capacity | Off-Peak Deliverability | KERN | CA | SCE | HIGHWIND SUBSTATION 230kV | Highwind | 204 | Tehachapi | 2024-12-15 | 2024-12-15 | NA |  |  | NA
VENADO VALLEY 1 | 1794 | 2020-04-02 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 305.2 | 305.2 | 300 | Full Capacity | Off-Peak Deliverability | ROSAMOND | CA | SCE | WhirlWind Substation 230kV | Whirlwind | 14 | Tehachapi | 2024-09-30 | 2024-09-30 | NA |  |  | NA
ARIDA 3 SOLAR FARM | 1795 | 2020-04-01 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 450 | 450 | 450 | Full Capacity | Off-Peak Deliverability | CLARK | NV | SCE | Mohave Substation 500kV | Mohave | 96 | SCADSNV_Z5_SCADSNV | 2025-04-01 | 2025-04-01 | NA |  |  | NA
DELAMAR ENERGY STORAGE | 1796 | 2020-04-14 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 256.3 |  | 250 | Full Capacity |  | CLARK | NV | SCE | Eldorado Substation 230kV |  |  |  | 2024-08-01 | 2024-08-01 | NA |  |  | NA
BONANZA SOLAR 2 | 1797 | 2020-04-06 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 300 | 150 | 300 | Full Capacity | Off-Peak Deliverability | CLARK/NYE | NV | GLW | Innovation Substation 230kV | Innovation |  | SCADSNV_Z5_SCADSNV | 2024-12-01 | 2024-12-01 | NA |  |  | NA
CALVADA SPRINGS SOLAR | 1798 | 2020-04-08 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 250 | 250 | 250 | Full Capacity | Off-Peak Deliverability | INYO | CA | GLW | Trout Canyon Switching Station 230kV | Trout Canyon | 221 | SCADSNV_Z5_SCADSNV | 2022-12-16 | 2022-12-16 | NA |  |  | NA
ROUGH HAT 2 | 1799 | 2020-04-02 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 203.8 | 203.8 | 200 | Full Capacity | Off-Peak Deliverability | CLARK | NV | GLW | Trout Canyon Substation 230kV | Trout Canyon | 222 | SCADSNV_Z5_SCADSNV | 2024-09-30 | 2024-09-30 | NA |  |  | NA
SAGITTARIUS HYBRID | 1800 | 2020-03-31 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 408.2 | 409.2 | 400 | Full Capacity | Off-Peak Deliverability | CLARK | NV | GLW | Trout Canyon Switching Station 230kV | Trout Canyon | 221 | SCADSNV_Z5_SCADSNV | 2024-12-31 | 2024-12-31 | NA |  |  | NA
WATER ROCK | 1801 | 2020-04-02 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 210.2 | 210.23 | 200 | Full Capacity | Off-Peak Deliverability | NYE | NV | GLW | Gamebird Substation 230kV | Gamebird |  | SCADSNV_Z5_SCADSNV | 2025-12-01 | 2025-12-01 | NA |  |  | NA
AMPCHAMP STORAGE | 1802 | 2020-04-02 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 20.8 |  | 20 | Full Capacity |  | SAN DIEGO | CA | SDGE | Otay Substation 69kV |  |  |  | 2023-12-31 | 2023-12-31 | NA |  |  | NA
BLUEGILL STORAGE | 1803 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 81.38 |  | 80 | Full Capacity |  | SAN DIEGO | CA | SDGE | Loop Loveland - Los Coches 69kV line |  |  |  | 2025-10-30 | 2025-10-30 | NA |  |  | NA
BOULDER OAKS HYBRID 2 | 1804 | 2020-04-13 | 2020-04-15 | ACTIVE | C13 | Wind Turbine | Storage | Wind Turbine | Battery | 205.8 | 205 | 400 | Full Capacity | Off-Peak Deliverability | SAN DIEGO | CA | SDGE | New Switchyard to loop the ECO-Miguel 500 kV Line |  |  |  | 2023-12-01 | 2023-12-01 | NA |  |  | NA
BRADSHAW ENERGY STORAGE | 1805 | 2020-04-14 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 75 |  | 75 | Full Capacity |  | SAN DIEGO | CA | SDGE | Miramar-Scripps 69kV line |  |  |  | 2022-06-01 | 2022-06-01 | NA |  |  | NA
CAPTIVA ENERGY STORAGE | 1806 | 2020-04-14 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 256.9 |  | 250 | Full Capacity |  | ORANGE | CA | SDGE | Trabuco - Capistrano 138kV line |  |  |  | 2024-06-01 | 2024-06-01 | NA |  |  | NA
CARROLL CANYON ENERGY STORAGE | 1807 | 2020-04-10 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 154.1 |  | 150 | Full Capacity |  | SAN DIEGO | CA | SDGE | Eastgate Substation 69kV |  |  |  | 2023-10-15 | 2023-10-15 | NA |  |  | NA
COASTWOOD ENERGY STORAGE | 1808 | 2020-04-14 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 101.9 |  | 101.1 | Full Capacity |  | SAN DIEGO | CA | SDGE | Shadowridge Substation 138kV |  |  |  | 2023-07-15 | 2023-07-15 | NA |  |  | NA
DROP ZONE STORAGE | 1810 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 313 |  | 300.01 | Full Capacity |  | SAN DIEGO | CA | SDGE | Otay Mesa Substation 230kV |  |  |  | 2024-11-30 | 2024-11-30 | NA |  |  | NA
DUCK PILOT STORAGE | 1811 | 2020-04-02 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 101.9 |  | 100 | Full Capacity |  | SAN DIEGO | CA | SDGE | Los Coches Substation 138kV |  |  |  | 2023-12-31 | 2023-12-31 | NA |  |  | NA
ELISABETH | 1812 | 2020-04-01 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 365.1 | 310.52 | 350 | Full Capacity | Off-Peak Deliverability | YUMA | AZ | SDGE | Hoodoo Wash Substation 500kV | Hoodoo | 126 | SCADSNV_Z3_GreaterImperial | 2024-12-01 | 2024-12-01 | NA |  |  | NA
HEDIONDA ENERGY STORAGE | 1814 | 2020-04-01 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 160 |  | 160 | Full Capacity |  | SAN DIEGO | CA | SDGE | Encina Substation 138kV |  |  |  | 2023-03-31 | 2023-03-31 | NA |  |  | NA
HINTON ENERGY STORAGE | 1815 | 2020-03-31 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 103.3 |  | 100 | Full Capacity |  | SAN DIEGO | CA | SDGE | Creelman Substation 69kV |  |  |  | 2023-06-01 | 2023-06-01 | NA |  |  | NA
OTAY MESA ENERGY CENTER EXPANSION | 1816 | 2020-04-09 | 2020-04-15 | ACTIVE | C13 | Combined Cycle |  | Natural Gas |  | 26.37 |  | 26.37 | Full Capacity |  | SAN DIEGO | CA | SDGE | Otay Mesa Substation 230kV |  |  |  | 2022-05-01 | 2022-05-01 | NA |  |  | NA
POWWOW | 1817 | 2020-04-01 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 33.5 | 202.23 | 200 | Full Capacity | Off-Peak Deliverability | SAN DIEGO | CA | SDGE | Oceanside Tap - Stuart Tap 69kV (TL690C ) |  |  |  | 2022-06-20 | 2022-06-20 | NA |  |  | NA
SADDLE MOUNTAIN SOLAR | 1818 | 2020-04-06 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 62.1 | 126.9 | 125 | Full Capacity | Off-Peak Deliverability | MARICOPA | AZ | SDGE | Hassayampa Substation 500kV |  |  |  | 2023-02-10 | 2023-02-10 | NA |  |  | NA
SCAFELL STORAGE | 1820 | 2020-04-12 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 52 |  | 50 | Full Capacity |  | SAN DIEGO | CA | SDGE | Creelman Substaton 69kV |  |  |  | 2022-11-15 | 2022-11-15 | NA |  |  | NA
SEGURO STORAGE | 1821 | 2020-04-15 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 407 |  | 400 | Full Capacity |  | SAN DIEGO | CA | SDGE | Escondido Substation 230kV |  |  |  | 2025-10-30 | 2025-10-30 | NA |  |  | NA
SUN STREAMS 4 | 1822 | 2020-04-02 | 2020-04-15 | ACTIVE | C13 | Photovoltaic | Storage | Solar | Battery | 225 | 225.04 | 215 | Full Capacity | Off-Peak Deliverability | MARICOPA | AZ | SDGE | Hassayampa Substation 500kV |  |  |  | 2021-12-31 | 2021-12-31 | NA |  |  | NA
SUN STREAMS 5 | 1823 | 2020-04-02 | 2020-04-15 | ACTIVE | C13 | Storage | Photovoltaic | Battery | Solar | 473.8 | 473.76 | 450 | Full Capacity | Off-Peak Deliverability | MARICOPA | AZ | SDGE | Hassayampa Substation 500kV |  |  |  | 2023-06-30 | 2023-06-30 | NA |  |  | NA
VIENTO FRONTERIZO | 1824 | 2020-04-11 | 2020-04-15 | ACTIVE | C13 | Wind Turbine |  | Wind Turbine |  | 1001 |  | 972.82 | Full Capacity | Off-Peak Deliverability | MUNICIPALITY OF TECATE | MX | SDGE | East County Substation 500kV |  |  |  | 2024-09-30 | 2024-09-30 | NA |  |  | NA
VIKING ENERGY STORAGE | 1825 | 2020-04-14 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 101.9 |  | 101.1 | Full Capacity |  | SAN DIEGO | CA | SDGE | Ocean Ranch Substation 69kV |  |  |  | 2023-07-15 | 2023-07-15 | NA |  |  | NA
BIG HORN ENERGY STORAGE | 1827 | 2020-04-05 | 2020-04-15 | ACTIVE | C13 | Storage |  | Battery |  | 425.1 |  | 400 | Full Capacity |  | IMPERIAL | CA | SDGE | Imperial Valley Substation 230kV | Imperial | 7 | SCADSNV_Z3_GreaterImperial | 2024-07-01 | 2024-07-01 | NA |  |  | NA
|  | Legend: | ● Study Process Key: Active=project is in study through Construction phases; Complete=project is in Commercial Operation, Withdrawn=project is withdrawn
● Study Process Key: A39=Amendment 39 Procedures (Appendix W), Serial=Standard Large Generator Interconnection Procedures (Appendix U), SGIP=Small Generator Interconnection Procedure (Appendix S), Numbered Clusters=Large Generator Interconnection Procedures in a Queue Cluster Window (Appendix Y), TC=Transition Cluster (Appendix 2 to Appendix Y), ISP=Independent Study Process (Appendix Y), FT=Fast Track (Appendix Y)
● Generating Facility Type Key: CC=Combined Cycle, CT=Combustion Turbine, FC=Fuel Cell, H=Hydro, PS=Pump Storage, PV=Photovoltaic, RE=Reciprocating Engine, ST= Steam Turbine, STH=Solar Thermal, STR=Storage, WT=Wind Turbine
● Generating Facility Fuel Key: B=Biofuel, BAT=Battery, C=Coal, G=Geothermal, FW=Flywheel, HR=Heat Recovery, NG=Natural Gas, NU=Nuclear, O=Fuel Oil, S=Solar, W=Wind, WTR=Water
The contents of these pages are subject to change without notice. Decisions based on information contained within the California ISO's web site are the visitor's sole responsibility.

## 4d_CommercialInterest_LSEPlans
Source: LSE Plans, summarized in Resource Data Template (5)
resource | Sum of max_mw
ARIZONA_SOLAR | 118.33
DISTRIBUTED_SOLAR | 3
GREATER_IMPERIAL_GEOTHERMAL | 102.2804
GREATER_IMPERIAL_WIND | 17.5381
HUMBOLDT_BAY_OFFSHORE_WIND | 120
HUMBOLDT_WIND | 116.0943
INYOKERN_NORTH_KRAMER_SOLAR | 23.1583
KERN_GREATER_CARRIZO_SOLAR | 25.6
KRAMER_INYOKERN_EX_SOLAR | 91
NEW_BTM_DR | 5.5
NEW_GENERIC_BATTERY_STORAGE | 1905.5
NEW_GENERIC_BIOMASS/WOOD | 83.07
NEW_GENERIC_DR | 52.4
NEW_GENERIC_GEOTHERMAL | 105
NEW_GENERIC_SOLAR_1AXIS | 671.76
NEW_HYBRID | 9577.5
NORTHERN_CALIFORNIA_EX_WIND | 140
PACIFIC_NORTHWEST_WIND | 18
RIVERSIDE_PALM_SPRINGS_SOLAR | 514.4848
SACRAMENTO_RIVER_SOLAR | 56
SOLANO_SOLAR | 27.18
SOLANO_WIND | 25
SOUTHERN_CA_DESERT_SOUTHERN_NV_SOLAR | 607.3235
SOUTHERN_CALIFORNIA_DESERT_EX_SOLAR | 475
SOUTHERN_NEVADA_WIND | 2000
TEHACHAPI_EX_SOLAR | 388
Grand Total | 17268.7195
Sum battery storage | 11483

## 38MMT_CEC BusBar Assignment
Portfolio: 38MMT_20201015_2045_RSP_2019IEPR
Source: RESOLVE Portfolio Analytics Tab ("2020-10-29-All_Portfolios_For_Busbar_Mapping.xlsx"; tab "Portfolio Analytics_Sens 1"; Row 466 "Selected Renewables by Location (Fully Deliverable)" and Row 539 "Selected Renewables by Location (Energy Only)")
RESOLVE Resource | Resource Type | kV | 500 kV plus Solar | RESOLVE Resource | Tx Deliv. Zone | FCDS Renewable Resource Summary by Location (MW) | EO Renewable Resource Summary by Location (MW) | Total MW | SUBSTATION | MW ASSIGNED | CEC NOTES
|  |  |  | InState_Biomass | None | 0 | 0 | 0
|  |  |  | Greater_Imperial_Geothermal | Greater_Imperial-SCADSNV | 0 | 0 | 0
|  |  |  | Inyokern_North_Kramer_Geothermal | Greater_Kramer-Inyokern_North_Kramer | 0 | 0 | 0
|  |  |  | Northern_California_Ex_Geothermal | Northern_California_Ex | 0 | 0 | 0
|  |  |  | Pacific_Northwest_Geothermal | N/A | 0 | 0 | 0
|  |  |  | Riverside_Palm_Springs_Geothermal | SCADSNV-Riverside_Palm_Springs | 0 | 0 | 0
|  |  |  | Solano_Geothermal | Solano-Sacramento_River | 57 | 48 | 105
Solano_Geothermal | Geothermal | 230 | no flag | [5 empty] | Sonoma 3 230kV | 105 | PG&E 230kV
|  |  |  | Southern_Nevada_Geothermal | SCADSNV-Mountain_Pass_El_Dorado | 0 | 0 | 0
|  |  |  | Carrizo_Solar | SPGE-Kern_Greater_Carrizo-Carrizo | 0 | 0 | 0
|  |  |  | Carrizo_Wind | SPGE-Kern_Greater_Carrizo-Carrizo | 287 | 0 | 287
Carrizo_Wind | Wind | 230 | no flag | [5 empty] | Templeton 230kV | 287
|  |  |  | Central_Valley_North_Los_Banos_Solar | Central_Valley_North_Los_Banos-SPGE | 0 | 0 | 0
|  |  |  | Central_Valley_North_Los_Banos_Wind | Central_Valley_North_Los_Banos-SPGE | 173 | 0 | 173
Central_Valley_North_Los_Banos_Wind | Wind | 230 | no flag | [5 empty] | Los Banos 230kV | 173 | Assign this Wind Resource and MW to Westlands Tx Zone
|  |  |  | Distributed_Solar | None | 0 | 0 | 0
|  |  |  | Distributed_Wind | #N/A | 0 | 0 | 0
|  |  |  | Greater_Imperial_Solar | Greater_Imperial-SCADSNV | 0 | 547.9 | 547.9
Greater_Imperial_Solar | Solar | 230 | 1 | [5 empty] | Imperial Valley 230kV | 332
Greater_Imperial_Solar | Solar | 230 | 1 | [5 empty] | Ocotillo Express 230kV | 216
|  |  |  | Greater_Imperial_Wind | Greater_Imperial-SCADSNV | 0 | 0 | 0
|  |  |  | Greater_Kramer_Wind | Greater_Kramer | 0 | 0 | 0
|  |  |  | Humboldt_Wind | Sacramento_River-Humboldt | 0 | 34 | 34
Humboldt_Wind | Wind | 115 | no flag | [5 empty] | Bridgeville 115kV | 34
|  |  |  | Inyokern_North_Kramer_Solar | Greater_Kramer-Inyokern_North_Kramer | 0 | 0 | 0
|  |  |  | Kern_Greater_Carrizo_Solar | SPGE-Kern_Greater_Carrizo | 101.32 | 700 | 801.32
Kern_Greater_Carrizo_Solar | Solar | 230 | 1 | [5 empty] | Arco 230kV | 165
Kern_Greater_Carrizo_Solar | Solar | 230 | 1 | [5 empty] | Midway 230kV | 159.7554
Kern_Greater_Carrizo_Solar | Solar | 115 | 1 | [5 empty] | Renfro 115 kV | 164.062
Kern_Greater_Carrizo_Solar | Solar | 230 | 1 | [5 empty] | Stockdale 230kV | 164.6475
Kern_Greater_Carrizo_Solar | Solar | 230 | 1 | [5 empty] | Wheeler Ridge 230kV | 147.332
|  |  |  | Kern_Greater_Carrizo_Wind | SPGE-Kern_Greater_Carrizo | 20 | 0 | 20
Kern_Greater_Carrizo_Wind | Wind | 70 | no flag | [5 empty] | Cholame 70 kV | 20 | Assign to Cholame Sub to reduce gentie distance. May require local upgrade to connect project(s)
|  |  |  | Kramer_Inyokern_Ex_Solar | Kramer_Inyokern_Ex | 0 | 0 | 0
|  |  |  | Kramer_Inyokern_Ex_Wind | Kramer_Inyokern_Ex | 0 | 0 | 0
|  |  |  | Mountain_Pass_El_Dorado_Solar | Mountain_Pass_El_Dorado | 248 | 0 | 248
Mountain_Pass_El_Dorado_Solar | Solar | 230 | 1 | [5 empty] | El Dorado 230kV | 83
Mountain_Pass_El_Dorado_Solar | Solar | 500 | 2 | [5 empty] | EL Dorado 500kV | 165
|  |  |  | North_Victor_Solar | North_Victor-Greater_Kramer | 300 | 0 | 300
North_Victor_Solar | Solar | 230 | 1 | [5 empty] | Victor 230kV | 215
North_Victor_Solar | Solar | 230 | 1 | [5 empty] | Cool water 230kV | 85
|  |  |  | Northern_California_Ex_Solar | Northern_California_Ex | 396.9 | 0 | 396.9
Northern_California_Ex_Solar | Solar | 230 | 1 | [5 empty] | Brighton 230kV | 156
Northern_California_Ex_Solar | Solar | 230 | 1 | [5 empty] | Logan Creek 230kV | 241
|  |  |  | Northern_California_Ex_Wind | Sacramento_River | 766.9 | 0 | 766.9
Northern_California_Ex_Wind | Wind | 230 | no flag | [5 empty] | Glenn 230kV | 354
Northern_California_Ex_Wind | Wind | 230 | no flag | [5 empty] | Delevan 230kV | 83
Northern_California_Ex_Wind | Wind | 230 | no flag | [5 empty] | Thermalito 230kV | 178
Northern_California_Ex_Wind | Wind | 230 | no flag | [5 empty] | Rio Oso 230kV | 152
|  |  |  | NW_Ext_Tx_Wind | Sacramento_River | 559.54 | 940.46 | 1500 | Round Mountain 500kV | 1500
|  |  |  | Riverside_Palm_Springs_Solar | SCADSNV-Riverside_Palm_Springs | 0 | 0 | 0
|  |  |  | Sacramento_River_Solar | Sacramento_River | 0 | 925.54 | 925.54
Sacramento_River_Solar | Solar | 230 | 1 | [5 empty] | Delevan 230kV | 172
Sacramento_River_Solar | Solar | 230 | 1 | [5 empty] | Glenn 230kV | 187
Sacramento_River_Solar | Solar | 230 | 1 | [5 empty] | Palermo 230kV | 184
Sacramento_River_Solar | Solar | 230 | 1 | [5 empty] | Rio Oso 230kV | 197
Sacramento_River_Solar | Solar | 230 | 1 | [5 empty] | Thermalito 230kV | 186
|  |  |  | Sacramento_River_Wind | N/A | 0 | 0 | 0
|  |  |  | SCADSNV_Solar | SCADSNV | 0 | 330 | 330
SCADSNV_Solar | Solar | 500 | 2 | [5 empty] | Mohave 500kV | 330
|  |  |  | SCADSNV_Wind | SCADSNV | 0 | 0 | 0
|  |  |  | Solano_Solar | Solano-Sacramento_River | 0 | 622 | 622
Solano_Solar | Solar | 230 | 1 | [5 empty] | Fulton 230kV | 159
Solano_Solar | Solar | 230 | 1 | [5 empty] | Contra Costa 230kV | 156
Solano_Solar | Solar | 230 | 1 | [5 empty] | Tulucay 230kV | 137
Solano_Solar | Solar | 500 | 2 | [5 empty] | Vaca-Dixon & GC Yard 500kV | 170
|  |  |  | Solano_subzone_Solar | Solano-Sacramento_River-Solano_subzone | 0 | 0 | 0
|  |  |  | Solano_subzone_Wind | Solano-Sacramento_River-Solano_subzone | 0 | 0 | 0
|  |  |  | Solano_Wind | Solano-Sacramento_River | 462 | 0 | 462
Solano_Wind | Wind | 230 | no flag | [5 empty] | Lakeville 230kV | 194
Solano_Wind | Wind | 230 | no flag | [5 empty] | Tulucay 230kV | 20
Solano_Wind | Wind | 500 | no flag | [5 empty] | Vaca-Dixon & GC Yard 500kV | 146
Solano_Wind | Wind | 230 | no flag | [5 empty] | Shilo III 230kV | 72
Solano_Wind | Wind | 230 | no flag | [5 empty] | Lone Tree 230kV | 30
|  |  |  | Southern_California_Desert_Ex_Solar | Southern_California_Desert_Ex | 862 | 0 | 862
Southern_California_Desert_Ex_Solar | Solar | 230 | 1 | [5 empty] | Innovation 230kV | 154
Southern_California_Desert_Ex_Solar | Solar | 230 | 1 | [5 empty] | Desert View 230kV | 119
Southern_California_Desert_Ex_Solar | Solar | 230 | 1 | [5 empty] | Crazy Eyes 230kV | 427
Southern_California_Desert_Ex_Solar | Solar | 230 | 1 | [5 empty] | El Dorado 230kV | 54
Southern_California_Desert_Ex_Solar | Solar | 500 | 2 | [5 empty] | El Dorado 500kV | 108
Mohave 500kV
|  |  |  | Southern_California_Desert_Ex_Wind | Southern_California_Desert_Ex | 0 | 0 | 0
|  |  |  | Southern_Nevada_Solar | SCADSNV-GLW_VEA | 0 | 0 | 0
|  |  |  | Southern_Nevada_Wind | SCADSNV-GLW_VEA | 442.03 | 0 | 442.03
Southern_Nevada_Wind | Wind | 230 | no flag | [5 empty] | Innovation 230kV | 97
Southern_Nevada_Wind | Wind | 230 | no flag | [5 empty] | Desert View 230kV | 75
Southern_Nevada_Wind | Wind | 230 | no flag | [5 empty] | Crazy Eyes 230kV | 270
|  |  |  | SW_Ext_Tx_Wind | SCADSNV-Riverside_Palm_Springs | 0 | 500 | 500
SW_Ext_Tx_Wind | Wind | 500 | no flag | [5 empty] | Palo Verde 500kV | 500 | SunZia/Devers-Palo Verde 500kV
|  |  |  | Tehachapi_Solar | Tehachapi | 3856 | 800 | 4656
Tehachapi_Solar | Solar | 500 | 2 | [5 empty] | WindHub 500kV | 1119
Tehachapi_Solar | Solar | 500 | 2 | [5 empty] | Whirlwind 500kV | 1240
Tehachapi_Solar | Solar | 500 | 2 | [5 empty] | Antelope 500kV | 1210
Tehachapi_Solar | Solar | 230 | 1 | [5 empty] | Pearblossom 230kV | 1087
|  |  |  | Tehachapi_Ex_Solar | Tehachapi_Ex | 0 | 0 | 0
|  |  |  | Tehachapi_Wind | Tehachapi | 275 | 0 | 275
Tehachapi_Wind | Wind | 500 | no flag | [5 empty] | WindHub 500kV | 275
|  |  |  | Westlands_Ex_Solar | Westlands_Ex | 1778.57 | 0 | 1778.57
Westlands_Ex_Solar | Solar | 230 | 1 | [5 empty] | Coburn 230kV | 1099.8182
Westlands_Ex_Solar | Solar | 500 | 2 | [5 empty] | Diablo Canyon 500kV | 377.679
Westlands_Ex_Solar | Solar | 230 | 1 | [5 empty] | Goleta 230kV | 301.5028
|  |  |  | Westlands_Ex_Wind | N/A | 0 | 0 | 0
|  |  |  | Westlands_Solar | Central_Valley_North_Los_Banos-SPGE | 467.94 | 0 | 467.94
Westlands_Solar | Solar | 230 | 1 | [5 empty] | Mc Call 230kV | 468
|  |  |  | Cape_Mendocino_Offshore_Wind | N/A | 0 | 0 | 0
|  |  |  | Del_Norte_Offshore_Wind | N/A | 0 | 0 | 0
|  |  |  | Diablo_Canyon_Offshore_Wind_Ext_Tx | N/A | 0 | 0 | 0
|  |  |  | Diablo_Canyon_Offshore_Wind | N/A | 0 | 0 | 0
|  |  |  | Humboldt_Bay_Offshore_Wind | N/A | 0 | 0 | 0
|  |  |  | Morro_Bay_Offshore_Wind | N/A | 0 | 0 | 0
|  |  |  | Utah_Solar | N/A | 0 | 0 | 0
|  |  |  | Arizona_Solar | SCADSNV-Riverside_Palm_Springs | 475.03 | 1435.02 | 1910.05
Arizona_Solar | Solar | 500 | 2 | [5 empty] | Hassayampa 500kV | 210
Arizona_Solar | Solar | 500 | 2 | [5 empty] | Hoodoo Wash Switchyard 500kV | 993
Arizona_Solar | Solar | 500 | 2 | [5 empty] | Delaney-Colorado 500kV | 707
|  |  |  | New_Mexico_Solar | N/A | 0 | 0 | 0
|  |  |  | Baja_California_Solar | N/A | 0 | 0 | 0
|  |  |  | Baja_California_Wind | Greater_Imperial-SCADSNV | 495 | 0 | 495
Baja_California_Wind | Wind | 500 | no flag | [5 empty] | East County 500kV | 495
|  |  |  | Pacific_Northwest_Wind | N/A | 0 | 0 | 0
|  |  |  | Idaho_Wind | N/A | 0 | 0 | 0
|  |  |  | Utah_Wind | N/A | 0 | 0 | 0
|  |  |  | Wyoming_Wind | SCADSNV-Mountain_Pass_El_Dorado | 0 | 1500 | 1500
Wyoming_Wind | Wind | 500 | no flag | [5 empty] | El Dorado 500kV | 1500
|  |  |  | Arizona_Wind | N/A | 0 | 0 | 0
|  |  |  | New_Mexico_Wind | SCADSNV-Riverside_Palm_Springs | 917.02 | 582.98 | 1500
New_Mexico_Wind | Wind | 500 | no flag | [5 empty] | Palo Verde 500kV | 1500 | SunZia/Devers-Palo Verde 500kV

## 38MMT_CEC BusBar Assignment_R2
Portfolio: 38MMT_20201015_2045_RSP_2019IEPR
Source: RESOLVE Portfolio Analytics Tab ("2020-10-29-All_Portfolios_For_Busbar_Mapping.xlsx"; tab "Portfolio Analytics_Sens 1"; Row 466 "Selected Renewables by Location (Fully Deliverable)" and Row 539 "Selected Renewables by Location (Energy Only)")
Tech | kV | 500 kV plus flag for solar | RESOLVE Resource | New FCDS MW 2020-12-04-All_Portfolios_For_Busbar_Mapping.xlsx | EO Renewable Resource Summary by Location (MW) | Total MW | SUBSTATION | FCDS MW ASSIGNED | EO MW ASSIGNED | Total MW Assigned | CEC NOTES
Biomass | no flag | no flag | InState_Biomass | 0 | - | -
Geothermal | no flag | no flag | Greater_Imperial_Geothermal | 0 | - | -
Geothermal | no flag | no flag | Inyokern_North_Kramer_Geothermal | 0 | - | -
Geothermal | no flag | no flag | Northern_California_Ex_Geothermal | 0 | - | -
Geothermal | no flag | no flag | Pacific_Northwest_Geothermal | 0 | - | -
Geothermal | no flag | no flag | Riverside_Palm_Springs_Geothermal | 0 | - | -
Geothermal | no flag | no flag | Solano_Geothermal | 57 | - | 57
Geothermal | 230 | no flag | Solano_Geothermal | 0 |  | - | Sonoma 3 230kV | 57 | - | 57 | PG&E 230kV
| no flag | no flag |  | 0 |  | -
| no flag | no flag | Southern_Nevada_Geothermal | 0 | - | -
| no flag | no flag | Carrizo_Solar | 0 | - | - |  |  | - | -
Wind | no flag | no flag | Carrizo_Wind | 287 | - | 287
Wind | 230 | no flag | Carrizo_Wind | 0 |  | - | Templeton 230kV | 287 | - | 287
| no flag | no flag |  | 0 |  | -
| no flag | no flag | Central_Valley_North_Los_Banos_Solar | 0 | - | - |  |  | - | -
| no flag | no flag | Central_Valley_North_Los_Banos_Wind | 173 | - | 173
Wind | 230 | no flag | Central_Valley_North_Los_Banos_Wind | 0 |  | - | Los Banos 230kV | 173 | - | 173 | Assign this Wind Resource and MW to Westlands Tx Zone
| no flag | no flag |  | 0 |  | -
| no flag | no flag | Distributed_Solar | 0 | - | -
| no flag | no flag | Distributed_Wind | 0 | - | -
Solar | no flag | 1 | Greater_Imperial_Solar | 0 | 548 | 548 | [5 empty] | Adjustment 6b
Solar | 230 | 1 | Greater_Imperial_Solar | 0 |  | - | Imperial Valley 230kV | 365 | 332 | 697 |  | Allocate part of excess of Southern Nevada Solar to Imperial proportional to commercial interests
Solar | 230 | 1 | Greater_Imperial_Solar | 0 |  | - | Ocotillo Express 230kV | 235 | 216 | 451 |  | 600
| no flag | no flag |  | 0 |  | -
| no flag | no flag | Greater_Imperial_Wind | 0 | - | -
| no flag | no flag | Greater_Kramer_Wind | 0 | - | -
Wind | no flag | no flag | Humboldt_Wind | 0 | 34 | 34
Wind | no flag | no flag | Humboldt_Wind | 0 |  | - | Bridgeville 115kV | - | 34 | 34
| no flag | no flag |  | 0 |  | -
| no flag | no flag | Inyokern_North_Kramer_Solar | 0 | - | -
Solar | no flag | 1 | Kern_Greater_Carrizo_Solar | 101 | 700 | 801
Solar | 230 | 1 | Kern_Greater_Carrizo_Solar | 0 |  | - | Arco 230kV | 21 | 144 | 165
Solar | 230 | 1 | Kern_Greater_Carrizo_Solar | 0 |  | - | Midway 230kV | 20 | 140 | 160
Solar | no flag | 1 | Kern_Greater_Carrizo_Solar | 0 |  | - | Renfro 115kV | 21 | 143 | 164
Solar | 230 | 1 | Kern_Greater_Carrizo_Solar | 0 |  | - | Stockdale 230kV | 21 | 144 | 165
Solar | 230 | 1 | Kern_Greater_Carrizo_Solar | 0 |  | - | Wheeler Ridge 230kV | 18 | 129 | 147
| no flag | no flag |  | 0 |  | -
Wind | no flag | no flag | Kern_Greater_Carrizo_Wind | 20 | - | 20
Wind | no flag | no flag | Kern_Greater_Carrizo_Wind | 0 |  | - | Cholame 70 kV | 20 | - | 20 | Assign to Cholame Sub to reduce gentie distance. May require local upgrade to connect project(s)
| no flag | no flag |  | 0 |  | -
| no flag | no flag | Kramer_Inyokern_Ex_Solar | 0 | - | -
| no flag | no flag | Kramer_Inyokern_Ex_Wind | 0 | - | -
Solar | no flag | 1 | Mountain_Pass_El_Dorado_Solar | 248 | - | 248
Solar | 230 | 1 | Mountain_Pass_El_Dorado_Solar | 0 |  | - | El Dorado 230kV | 83 | - | 83
Solar | 500 | 2 | Mountain_Pass_El_Dorado_Solar | 0 |  | - | El Dorado 500kV | 165 | - | 165
| no flag | no flag |  | 0 |  | -
Solar | no flag | 1 | North_Victor_Solar | 300 | - | 300
Solar | 230 | 1 | North_Victor_Solar | 0 |  | - | Victor 230kV | 215 | - | 215
Solar | 230 | 1 | North_Victor_Solar | 0 |  | - | Coolwater 230kV | 85 | - | 85
| no flag | no flag |  | 0 |  | -
Wind | no flag | no flag | Northern_California_Ex_Solar | 396.9 | - | 397
Wind | 230 | no flag | Northern_California_Ex_Solar | 0 |  | - | Brighton 230kV | 156 | - | 156
Wind | 230 | no flag | Northern_California_Ex_Solar | 0 |  | - | Logan Creek 230kV | 241 | - | 241
Wind | no flag | no flag |  | 0 |  | -
Wind | no flag | no flag | Northern_California_Ex_Wind | 766.9 | - | 767
Wind | 230 | no flag | Northern_California_Ex_Wind | 0 |  | - | Glenn 230kV | 354 | - | 354
Wind | 230 | no flag | Northern_California_Ex_Wind | 0 |  | - | Delevan 230kV | 83 | - | 83
Wind | 230 | no flag | Northern_California_Ex_Wind | 0 |  | - | Thermalito 230kV | 178 | - | 178
| 230 | no flag | Northern_California_Ex_Wind | 0 |  | - | Rio Oso 230kV | 152 | - | 152
| no flag | no flag |  | 0 |  | -
Wind | 500 | no flag | NW_Ext_Tx_Wind | 530.12 | 940 | 1471 | Round Mountain 500kV | 530 | 940 | 1470
| no flag | no flag | Riverside_Palm_Springs_Solar | 0 | - | -
Solar | no flag | 1 | Sacramento_River_Solar | 0 | 926 | 926 | [5 empty] | Adjustment 7
Solar | 230 | 1 | Sacramento_River_Solar | 0 |  | - | Delevan 230kV | - | 39 | 39 |  | EO Tx exceedance in outer northern CA zone by 443 MW
Solar | 230 | 1 | Sacramento_River_Solar | 0 |  | - | Glenn 230kV | - | 54 | 54 |  | -665 EO
Solar | 230 | 1 | Sacramento_River_Solar | 0 |  | - | Palmero 230kV | - | 51 | 51
Solar | 230 | 1 | Sacramento_River_Solar | 0 |  | - | Rio Oso 230kV | - | 64 | 64
Solar | 230 | 1 | Sacramento_River_Solar | 0 |  | - | Thermalito 230kV | - | 53 | 53
Solar | no flag | 1 |  | 0 |  | -
| no flag | no flag | Sacramento_River_Wind | 0 | - | -
Solar | no flag | 1 | SCADSNV_Solar | 0 | 330 | 330 | [5 empty] | Adjustment 5
Solar | 500 | 2 | SCADSNV_Solar | 0 |  | - | Mohave 500kV | 410 | 330 | 740 |  | Move 330 MW from Arizona Solar to SCADSNV_Solar to alleviate Tx exceedance created by mapping pumped hydro to Red Bluff
| no flag | no flag |  | 0 |  | - | [5 empty] | 330
| no flag | no flag | SCADSNV_Wind | 0 | - | - | [5 empty] | Adjustment 6c: Allocate excess SNV Solar to Mohave 500kV
Solar | no flag | 1 | Solano_Solar | 0 | 622 | 622 | [5 empty] | 80
Solar | 230 | 1 | Solano_Solar | 0 |  | - | Fulton 230kV | - | 159 | 159
Solar | 230 | 1 | Solano_Solar | 0 |  | - | Contra Costa 230kV | - | 156 | 156
Solar | 230 | 1 | Solano_Solar | 0 |  | - | Tulucay 230kV | - | 137 | 137
Solar | 230 | 1 | Solano_Solar | 0 |  | - | Vaca-Dixon & GC Yard 230kV | - | 170 | 170
| no flag | no flag |  | 0 |  | -
| no flag | no flag | Solano_subzone_Solar | 0 | - | -
| no flag | no flag | Solano_subzone_Wind | 0 | - | -
Wind | no flag | no flag | Solano_Wind | 462 | - | 462
Wind | 230 | no flag | Solano_Wind | 0 |  | - | Lakeville 230kV | 194 | - | 194
Wind | 230 | no flag | Solano_Wind | 0 |  | - | Tulucay 230kV | 20 | - | 20
Wind | 230 | no flag | Solano_Wind | 0 |  | - | Vaca-Dixon & GC Yard 230kV | 146 | - | 146
Wind | 230 | no flag | Solano_Wind | 0 |  | - | Shilo III 230kV | 72 | - | 72
| 230 | no flag | Solano_Wind | 0 |  | - | Lone Tree 230kV | 30 | - | 30
| no flag | no flag |  | 0 |  | -
Solar | no flag | 1 | Southern_California_Desert_Ex_Solar | 862 | - | 862
Solar | 230 | 1 | Southern_California_Desert_Ex_Solar | 0 |  | - | Innovation 230kV | - | - | - |  | Adjustment 6
Solar | 230 | 1 | Southern_California_Desert_Ex_Solar | 0 |  | - | Desert View 230kV | - | - | - |  | Move 862 MW from Southern California Desert Ex Solar
Solar | 230 | 1 | Southern_California_Desert_Ex_Solar | 0 |  | - | Crazy Eyes 230kV | - | - | - |  | to SNV solar (same rationale as for Westlands_Ex),
Solar | 230 | 1 | Southern_California_Desert_Ex_Solar | 0 |  | - | El Dorado 230kV | - | - | - |  | excess is moved to Riverside and Imperial
Solar | 500 | 2 | Southern_California_Desert_Ex_Solar | 0 |  | - | El Dorado 500kV | - | - | - |  | -862
Solar | 500 | 2 | Southern_California_Desert_Ex_Solar | 0 |  | - | Mohave 500kV
| no flag | no flag |  | 0 |  | -
| no flag | no flag | Southern_California_Desert_Ex_Wind | 0 | - | -
Solar | 230 | 1 | Southern_Nevada_Solar | 0 | - | - | Innovation 230kV | 40 |  |  |  | Adjustment 6a
Solar | 230 | 1 | Southern_Nevada_Solar |  |  | - | Desert View 230kV | 31 |  |  |  | Moved from SCAD Ex solar. Amount that can fit without violating tx limit (map to Innovation, Desert View, and Crazy Eyes)
Solar | 230 | 1 | Southern_Nevada_Solar |  |  | - | Crazy Eyes 230kV | 111 |  |  |  | 182
| no flag | no flag |  |  |  | -
| no flag | no flag |  |  |  | -
| no flag | no flag | Southern_Nevada_Wind | 442.03 | - | 442
| 230 | no flag | Southern_Nevada_Wind | 0 |  | - | Innovation 230kV | 97 | - | 97
| 230 | no flag | Southern_Nevada_Wind | 0 |  | - | Desert View 230kV | 75 | - | 75
| 230 | no flag | Southern_Nevada_Wind | 0 |  | - | Crazy Eyes 230kV | 270 | - | 270
| no flag | no flag |  | 0 |  | -
| no flag | no flag | SW_Ext_Tx_Wind | 0 | 500 | 500
| 500 | no flag | SW_Ext_Tx_Wind | 0 |  | - | Palo Verde 500kV |  | 500 | 500 | SunZia/Devers-Palo Verde 500kV
| no flag | no flag |  | 0 |  | - |  |  | - | -
Solar | no flag | 1 | Tehachapi_Solar | 3856 | 800 | 4656 |  |  | - | -
Solar | 230 | 1 | Tehachapi_Solar | 0 |  | - | WindHub 230kV | 950 | 197 | 1147 |  | Adjustment 1a
Solar | 230 | 1 | Tehachapi_Solar | 0 |  | - | Whirlwind 230kV | 1053 | 218 | 1271 |  | Move 623 MW overflow from Gates 500kV to Tehachapi
Solar | 230 | 1 | Tehachapi_Solar | 0 |  | - | Antelope 230kV | 1027 | 213 | 1240 |  | spread evenly across 4 subs
Solar | 230 | 1 | Tehachapi_Solar | 0 |  | - | Vincent 230kV | 826 | 172 | 998 | Replaced Pearblossom 230kV with Vincent 230kV | Adjustment 2: Reassign from Pearblossom to Vincent 230kV bus
| no flag | no flag |  | 0 |  | -
| no flag | no flag | Tehachapi_Ex_Solar | 0 | - | -
Wind | no flag | no flag | Tehachapi_Wind | 275 | - | 275
Wind | 230 | no flag | Tehachapi_Wind | 0 |  | - | WindHub 230kV | 275 | - | 275
| no flag | no flag |  | 0 |  | -
Solar | no flag | 1 | Westlands_Ex_Solar | 1778.57 | - | 1779
Solar | 230 | 1 | Westlands_Ex_Solar | 0 |  | - | Coburn 230kV | - | - | - |  | Adjustment 1c
Solar | 500 | 2 | Westlands_Ex_Solar | 0 |  | - | Diablo Canyon 500kV | - | - | - |  | Move westlands_ex solar to westlands
Solar | 230 | 1 | Westlands_Ex_Solar | 0 |  | - | Goleta 230kV | - | - | - |  | -1779
| no flag | no flag |  | 0 |  | -
| no flag | no flag | Westlands_Ex_Wind | 0 | - | -
Solar | no flag | 1 | Westlands_Solar | 467.94 | - | 468 |  |  |  |  | Re-allocated MW to additional subatations per previous year | Adjustment 1c
Solar | 230 | 1 | Westlands_Solar | 0 |  | - | Gates 230kV | 57 | 100 | 157 |  | Westlands solar
Solar | 230 | 1 | Westlands_Solar | 0 |  | - | Helm 230kV | 57 | 112 | 169 |  | 955
Solar | 230 | 1 | Westlands_Solar | 0 |  | - | Henrietta 230kV | 57 | 106 | 163 |  | spread evenly up to the transmission zone limit,
Solar | 230 | 1 | Westlands_Solar | 0 |  | - | Mc Call 230kV | 526 | 124 | 650 |  | with overflow allocated to the gates 500 kV system
Solar | 230 | 1 | Westlands_Solar | 0 |  | - | Mc Mullin 230kV | 58 | 118 | 176
Solar | 230 | 1 | Westlands_Solar | 0 |  | - | Panoche 230kV | 58 | 105 | 163 |  | Adjustment 7a
Solar | 500 | 2 | Westlands_Solar | 0 |  | - | Gates 500kV | 610 |  | 610 |  | Amount in exceedance of Tx zone for Sacramento River Solar
| no flag | no flag | Cape_Mendocino_Offshore_Wind | 0 | - | - | [5 empty] | +665 (EO)
| no flag | no flag | Del_Norte_Offshore_Wind | 0 | - | -
| no flag | no flag | Diablo_Canyon_Offshore_Wind_Ext_Tx | 0 | - | -
| no flag | no flag | Diablo_Canyon_Offshore_Wind | 0 | - | -
| no flag | no flag | Humboldt_Bay_Offshore_Wind | 0 | - | -
| no flag | no flag | Morro_Bay_Offshore_Wind | 0 | - | -
| no flag | no flag | Utah_Solar | 0 | - | -
Solar | no flag | 1 | Arizona_Solar | 446.89 | 1463 | 1909.89 | [5 empty] | Adjustment 3
Solar | 500 | 2 | Arizona_Solar | 0 |  | - | Hassayampa 500kV | 58.5 | 463 | 521.5 |  | Reassign from Hoodoo bus to Delaney and Hassayampa
Solar | 500 | 2 | Arizona_Solar | 0 |  | - | Hoodoo Wash Switchyard 500kV |  |  | 0 |  | Adjustment 5
Solar | 500 | 2 | Arizona_Solar | 0 |  | - | Delaney-Colorado 500kV | 58.5 | 1000 | 1058.5 |  | Move 330 MW to SCADSNV_Solar to alleviate Tx exceedance created by mapping pumped hydro to Red Bluff
| no flag | no flag |  | 0 |  | - | [5 empty] | -330
| no flag | no flag | New_Mexico_Solar | 0 | - | -
| no flag | no flag | Baja_California_Solar | 0 | - | -
Wind | no flag | no flag | Baja_California_Wind | 495 | - | 495
Wind | 500 | no flag | Baja_California_Wind | 0 |  | - | East County 500kV | 495 | - | 495
| no flag | no flag |  | 0 |  | -
| no flag | no flag | Pacific_Northwest_Wind | 0 | - | -
| no flag | no flag | Idaho_Wind | 0 | - | -
| no flag | no flag | Utah_Wind | 0 | - | -
Wind | no flag | no flag | Wyoming_Wind | 0 | 1500 | 1500
Wind | 500 | no flag | Wyoming_Wind | 0 |  | - | El Dorado 500kV | 1500 |  | 1500 |  | Adjustment 9
| no flag | no flag |  | 0 |  | -
Wind | no flag | no flag | Arizona_Wind | 0 | - | -
Wind | no flag | no flag | New_Mexico_Wind | 945.16 | 583 | 1528
| 500 | no flag | New_Mexico_Wind | 0 |  | - | Palo Verde 500kV | 945 | 583 | 1528 | SunZia/Devers-Palo Verde 500kV
Solar | no flag | 1 | Pisgah_Solar |  |  | - | [5 empty] | Adjustment 1b
Solar | no flag | 1 | Pisgah_Solar |  |  | - | Calcite | 140 |  |  |  | Allocate 201 MW to Pisgah to reduce amount of resources to be mapped to Gates 500 kV system where there is little commercial interest
Solar | no flag | 1 | Pisgah_Solar |  |  |  | Lugo | 47
Solar | 230 | 1 | Pisgah_Solar |  |  |  | Pisgah 230kV | 14
Pumped Hydro | no flag | no flag | Pumped Hydro Storage | 1843 |  | 1843
Pumped Hydro | 500 | no flag | Pumped Hydro Storage |  |  | - | Lee Lake 500kV | 500 |  |  |  | Adjustment 4: Add pumped hydro
Pumped Hydro | no flag | no flag | Pumped Hydro Storage |  |  | - | Red Bluff | 1343

## 5a_PrevYear
Resource | Tx Zone | Total MW (2019 RSP) | Total MW (2019 RSP adj)
Greater_Imperial_Geothermal | SCADSNV-Greater_Imperial | 0 | 0
Carrizo_Wind | Carrizo-Kern_Greater_Carrizo-SPGE | 287 | 287
Central_Valley_North_Los_Banos_Wind | Central_Valley_North_Los_Banos-SPGE | 173 | 173
Greater_Imperial_Solar | SCADSNV-Greater_Imperial | 548 | 548
Humboldt_Wind | Humboldt-Sacramento_River | 34 | 34
Inyokern_North_Kramer_Solar | Inyokern_North_Kramer-Greater_Kramer | 97 | 97
Kern_Greater_Carrizo_Solar | Kern_Greater_Carrizo-SPGE | 242 | 242
Kern_Greater_Carrizo_Wind | Kern_Greater_Carrizo-SPGE | 60 | 60
Mountain_Pass_El_Dorado_Solar | N/A | 248 | 248
North_Victor_Solar | North_Victor-Greater_Kramer | 300 | 300
Northern_California_Ex_Wind | Sacramento_River | 866 | 866
Riverside_Palm_Springs_Solar | SCADSNV-Riverside_Palm_Springs | 0 | 0
SCADSNV_Solar | SCADSNV | 330 | 330
Solano_Wind | Sacramento_River-Solano | 542 | 542
Southern_California_Desert_Ex_Solar | Southern_California_Desert_Ex | 862 | 0
Southern_Nevada_Solar | SCADSNV-GLW_VEA | 0 | 862
Tehachapi_Solar | Tehachapi | 4202 | 4202
Tehachapi_Wind | Tehachapi | 275 | 275
Westlands_Ex_Solar | Westlands_Ex | 1779 | 0
Westlands_Solar | Central_Valley_North_Los_Banos-SPGE | 58 | 1836
Arizona_Solar | SCADSNV-Riverside_Palm_Springs | 2352 | 2352
Baja_California_Wind | SCADSNV-Greater_Imperial | 600 | 600
New_Mexico_Wind | SCADSNV-Riverside_Palm_Springs | 606 | 606
Wyoming_Wind | Mountain_Pass_El_Dorado-SCADSNV | 1500 | 1500
Sub Total - Renewables |  | 15961 | 15960
Pumped Storage Hydro |  | 973 | 974

## 5b_ComparToPrevYr
What constitutes level 3 criteria flag? | -1000 | or greater | Reduction from prior year
What constitutes level 2 criteria flag? | -0.6 | or greater | Reduction from prior year
What constitutes level 1 criteria flag?
| FD + EO |  |  |  |  | Adjusted values
RESOLVE Resource | Prior Year: 2019 RSP adj Portfolio⁴ | 38MMT_20201015_2045_RSP_2019IEPR | Delta | Reduction > 1000 MW? | Dashboard value | pfolio name | Delta | Difference > 1000 MW? | Dashboard value | Prev Year Base Case⁴ | 2018 PSP | Delta | Reduction > 1000 MW? | Non-compliance flag
InState_Biomass | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | InState_Biomass | 0 | 0% | 0 | 1
Greater_Imperial_Geothermal | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Greater_Imperial_Geothermal | 1276 | -100% | 1 | 3
Inyokern_North_Kramer_Geothermal | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Inyokern_North_Kramer_Geothermal | 0 | 0% | 0 | 1
Northern_California_Ex_Geothermal | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Northern_California_Ex_Geothermal | 424 | -100% | 0 | 2
Pacific_Northwest_Geothermal | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Pacific_Northwest_Geothermal | 0 | 0% | 0 | 1
Riverside_Palm_Springs_Geothermal | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Riverside_Palm_Springs_Geothermal | 0 | 0% | 0 | 1
Solano_Geothermal | 0 | 105 | 10500% | 0 | 1 | 105 | 10500% | 0 | 1 | Solano_Geothermal | 0 | 10500% | 0 | 1
Southern_Nevada_Geothermal | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Southern_Nevada_Geothermal | 0 | 0% | 0 | 1
Carrizo_Solar | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Carrizo_Solar | 0 | 0% | 0 | 1
Carrizo_Wind | 287 | 287 | 0% | 0 | 1 | 287 | 0% | 0 | 1 | Carrizo_Wind | 160 | 79.38% | 0 | 1
Central_Valley_North_Los_Banos_Solar | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Central_Valley_North_Los_Banos_Solar | 0 | 0% | 0 | 1
Central_Valley_North_Los_Banos_Wind | 173 | 173 | 0% | 0 | 1 | 173 | 0% | 0 | 1 | Central_Valley_North_Los_Banos_Wind | 146 | 18.49% | 0 | 1
Distributed_Solar | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Distributed_Solar | 0 | 0% | 0 | 1
Distributed_Wind | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Distributed_Wind | 0 | 0% | 0 | 1
Greater_Imperial_Solar | 548 | 548 | 0% | 0 | 1 | 1148 | 109.5% | 0 | 1 | Greater_Imperial_Solar | 0 | 54800% | 0 | 1
Greater_Imperial_Wind | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Greater_Imperial_Wind | 0 | 0% | 0 | 1
Greater_Kramer_Wind | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Greater_Kramer_Wind | 0 | 0% | 0 | 1
Humboldt_Wind | 34 | 34 | 0% | 0 | 1 | 34 | 0% | 0 | 1 | Humboldt_Wind | 0 | 3400% | 0 | 1
Inyokern_North_Kramer_Solar | 97 | 0 | -100% | 0 | 2 | 0 | -100% | 0 | 2 | Inyokern_North_Kramer_Solar | 577 | -100% | 0 | 2
Kern_Greater_Carrizo_Solar | 242 | 801.32 | 231.1% | 0 | 1 | 801.32 | 231.1% | 0 | 1 | Kern_Greater_Carrizo_Solar | 0 | 80132% | 0 | 1
Kern_Greater_Carrizo_Wind | 60 | 20 | -66.67% | 0 | 2 | 20 | -66.67% | 0 | 2 | Kern_Greater_Carrizo_Wind | 0 | 2000% | 0 | 1
Kramer_Inyokern_Ex_Solar | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Kramer_Inyokern_Ex_Solar | 0 | 0% | 0 | 1
Kramer_Inyokern_Ex_Wind | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Kramer_Inyokern_Ex_Wind | 0 | 0% | 0 | 1
Mountain_Pass_El_Dorado_Solar | 248 | 248 | 0% | 0 | 1 | 248 | 0% | 0 | 1 | Mountain_Pass_El_Dorado_Solar | 0 | 24800% | 0 | 1
North_Victor_Solar | 300 | 300 | 0% | 0 | 1 | 300 | 0% | 0 | 1 | North_Victor_Solar | 0 | 30000% | 0 | 1
Northern_California_Ex_Solar | 0 | 397 | 39700% | 0 | 1 | 0 | 0% | 0 | 1 | Northern_California_Ex_Solar | 0 | 39700% | 0 | 1
Northern_California_Ex_Wind | 866 | 767 | -11.43% | 0 | 1 | 767 | -11.43% | 0 | 1 | Northern_California_Ex_Wind | 0 | 76700% | 0 | 1
NW_Ext_Tx_Wind | 0 | 1500 | 150000% | 0 | 1 | 1500 | 150000% | 0 | 1 | NW_Ext_Tx_Wind | 0 | 150000% | 0 | 1
Riverside_Palm_Springs_Solar | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Riverside_Palm_Springs_Solar | 1320 | -100% | 1 | 3
Sacramento_River_Solar | 0 | 896 | 89600% | 0 | 1 | 231 | 23100% | 0 | 1 | Sacramento_River_Solar | 0 | 89600% | 0 | 1
Sacramento_River_Wind | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Sacramento_River_Wind | 0 | 0% | 0 | 1
SCADSNV_Solar | 330 | 330 | 0% | 0 | 1 | 740 | 124.2% | 0 | 1 | SCADSNV_Solar | 0 | 33000% | 0 | 1
SCADSNV_Wind | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | SCADSNV_Wind | 0 | 0% | 0 | 1
Solano_Solar | 0 | 622 | 62200% | 0 | 1 | 622 | 62200% | 0 | 1 | Solano_Solar | 0 | 62200% | 0 | 1
Solano_subzone_Solar | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Solano_subzone_Solar | 0 | 0% | 0 | 1
Solano_subzone_Wind | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Solano_subzone_Wind | 0 | 0% | 0 | 1
Solano_Wind | 542 | 462 | -14.76% | 0 | 1 | 462 | -14.76% | 0 | 1 | Solano_Wind | 643 | -28.15% | 0 | 1
Southern_California_Desert_Ex_Solar | 0 | 862 | 86200% | 0 | 1 | 0 | 0% | 0 | 1 | Southern_California_Desert_Ex_Solar | 0 | 86200% | 0 | 1
Southern_California_Desert_Ex_Wind | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Southern_California_Desert_Ex_Wind | 0 | 0% | 0 | 1
Southern_Nevada_Solar | 862 | 0 | -100% | 0 | 2 | 182 | -78.89% | 0 | 2 | Southern_Nevada_Solar | 3006 | -100% | 1 | 3
Southern_Nevada_Wind | 0 | 442 | 44200% | 0 | 1 | 442 | 44200% | 0 | 1 | Southern_Nevada_Wind | 0 | 44200% | 0 | 1
SW_Ext_Tx_Wind | 0 | 500 | 50000% | 0 | 1 | 500 | 50000% | 0 | 1 | SW_Ext_Tx_Wind | 0 | 50000% | 0 | 1
Tehachapi_Solar | 4202 | 4656 | 10.8% | 0 | 1 | 5676 | 35.08% | 0 | 1 | Tehachapi_Solar | 1013 | 359.6% | 0 | 1
Tehachapi_Ex_Solar | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Tehachapi_Ex_Solar | 0 | 0% | 0 | 1
Tehachapi_Wind | 275 | 275 | 0% | 0 | 1 | 275 | 0% | 0 | 1 | Tehachapi_Wind | 153 | 79.74% | 0 | 1
Westlands_Ex_Solar | 0 | 1779 | 177900% | 0 | 1 | 0 | 0% | 0 | 1 | Westlands_Ex_Solar | 0 | 177900% | 0 | 1
Westlands_Ex_Wind | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Westlands_Ex_Wind | 0 | 0% | 0 | 1
Westlands_Solar | 1836 | 468 | -74.51% | 1 | 3 | 2088 | 13.73% | 0 | 1 | Westlands_Solar | 0 | 46800% | 0 | 1
Cape_Mendocino_Offshore_Wind | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Cape_Mendocino_Offshore_Wind | 0 | 0% | 0 | 1
Del_Norte_Offshore_Wind | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Del_Norte_Offshore_Wind | 0 | 0% | 0 | 1
Diablo_Canyon_Offshore_Wind_Ext_Tx | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Diablo_Canyon_Offshore_Wind_Ext_Tx | 0 | 0% | 0 | 1
Diablo_Canyon_Offshore_Wind | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Diablo_Canyon_Offshore_Wind | 0 | 0% | 0 | 1
Humboldt_Bay_Offshore_Wind | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Humboldt_Bay_Offshore_Wind | 0 | 0% | 0 | 1
Morro_Bay_Offshore_Wind | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Morro_Bay_Offshore_Wind | 0 | 0% | 0 | 1
Utah_Solar | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Utah_Solar | 0 | 0% | 0 | 1
Arizona_Solar | 2352 | 1910 | -18.79% | 0 | 1 | 1580 | -32.82% | 0 | 1 | Arizona_Solar | 0 | 191000% | 0 | 1
New_Mexico_Solar | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | New_Mexico_Solar | 0 | 0% | 0 | 1
Baja_California_Solar | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Baja_California_Solar | 0 | 0% | 0 | 1
Baja_California_Wind | 600 | 495 | -17.5% | 0 | 1 | 495 | -17.5% | 0 | 1 | Baja_California_Wind | 0 | 49500% | 0 | 1
Pacific_Northwest_Wind | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Pacific_Northwest_Wind | 0 | 0% | 0 | 1
Idaho_Wind | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Idaho_Wind | 0 | 0% | 0 | 1
Utah_Wind | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Utah_Wind | 0 | 0% | 0 | 1
Wyoming_Wind | 1500 | 1500 | 0% | 0 | 1 | 1500 | 0% | 0 | 1 | Wyoming_Wind | 0 | 150000% | 0 | 1
Arizona_Wind | 0 | 0 | 0% | 0 | 1 | 0 | 0% | 0 | 1 | Arizona_Wind | 0 | 0% | 0 | 1
New_Mexico_Wind | 606 | 1500 | 147.5% | 0 | 1 | 1500 | 147.5% | 0 | 1 | New_Mexico_Wind | 0 | 150000% | 0 | 1
Pumped Storage Hydro | 974 | 0 | -100% | 0 | 2 | 1843 | 89.22% | 0 | 1 | Pumped Storage Hydro | 0 | 0% | 0 | 1
Pisgah_Solar | 0 | 0 |  |  | 1 | 200.5 | 20050% | 0 | 1 | Pisgah_Solar | 1 | -100% | 0 | 2

## NewBaselineSumByRESOLVEResource
| Additions to Baseline since 5-27-20 RESOLVE | 2031 Selected Resources, 38 MMT portfolio as at November 2020 | 2031 Selected Resources, 38 MMT portfolio, post Baseline Rec at November 2020
RESOLVE Resource | MW | MW | MW | Display_filter | Flag new commercial resources online where RESOLVE selected none | Notes | New Baseline Resources⁷ | Tx Zone |  | Extract from: | RESOLVE_Results_Viewer_2020-09-10_LLT_tests_2_SK | 38MMT_20201015_2045_RSP_2019IEPR
InState_Biomass | 0 | 0 | 0 | 0 | 0 |  | RESOLVE Resource |  | New contracts, online by 2022 | FCDS Renewable Resource Summary by Location (MW)
Greater_Imperial_Geothermal | 0 | 0 | 0 | 0 | 0 |  | Row Labels |  | Sum of max_mw | RESOLVE Resource | Tx Zone | 2031
Inyokern_North_Kramer_Geothermal | 0 | 0 | 0 | 0 | 0 |  | Arizona_Wind | N/A | 300 | InState_Biomass | None
Northern_California_Ex_Geothermal | 0 | 0 | 0 | 0 | 0 |  | Baja_California_Wind | SCADSNV_Z3_GreaterImperial | 105 | Greater_Imperial_Geothermal | Greater_Imperial-SCADSNV
Pacific_Northwest_Geothermal | 0 | 0 | 0 | 0 | 0 |  | Central_Valley_North_Los_Banos_Solar | SPGE_Z4_CentralValleyAndLosBanos | 180 | Inyokern_North_Kramer_Geothermal | Greater_Kramer-Inyokern_North_Kramer
Riverside_Palm_Springs_Geothermal | 0 | 0 | 0 | 0 | 0 |  | Humboldt_Solar | N/A | 2.2 | Northern_California_Ex_Geothermal | Northern_California_Ex
Solano_Geothermal | 0 | 57 | 57 | 1 | 0 |  | Inyokern_North_Kramer_Solar | GK_Z2_InyokernAndNorthOfKramer | 99.5 | Pacific_Northwest_Geothermal | N/A
Southern_Nevada_Geothermal | 0 | 0 | 0 | 0 | 0 |  | Kern_Greater_Carrizo_Solar | SPGE_Z2_KernAndGreaterCarrizo | 335.68 | Riverside_Palm_Springs_Geothermal | SCADSNV-Riverside_Palm_Springs
Carrizo_Solar | 0 | 0 | 0 | 0 | 0 |  | Kern_Greater_Carrizo_Wind | SPGE_Z2_KernAndGreaterCarrizo | 40 | Solano_Geothermal | Solano-Sacramento_River | 57
Carrizo_Wind | 0 | 287 | 287 | 1 | 0 |  | Kramer_Inyokern_Ex_Solar | KramerInyoOutsideTxConstraintZones | 162 | Southern_Nevada_Geothermal | SCADSNV-Mountain_Pass_El_Dorado
Central_Valley_North_Los_Banos_Solar | 180 | 0 | 0 | 1 | 1 | Note contracting activity in location not selected by RESOLVE | Northern_California_Ex_Wind | Norcal_Z3_SacramentoRiver | 99 | Carrizo_Solar | SPGE-Kern_Greater_Carrizo-Carrizo
Central_Valley_North_Los_Banos_Wind | 0 | 173 | 173 | 1 | 0 |  | Riverside_Palm_Springs_Solar | SCADSNV_Z4_RiversideAndPalmSprings | 545.5 | Carrizo_Wind | SPGE-Kern_Greater_Carrizo-Carrizo | 287
Distributed_Solar | 0 | 0 | 0 | 0 | 0 |  | Solano_Wind | Norcal_Z4_Solano | 80 | Central_Valley_North_Los_Banos_Solar | Central_Valley_North_Los_Banos-SPGE
Distributed_Wind | 0 | 0 | 0 | 0 | 0 |  | Southern_Nevada_Solar | SCADSNV_Z2_GLW_VEA | 76 | Central_Valley_North_Los_Banos_Wind | Central_Valley_North_Los_Banos-SPGE | 173
Greater_Imperial_Solar | 0 | 0 | 0 | 0 | 0 |  | Tehachapi_Solar | Tehachapi | 145 | Distributed_Solar | None
Greater_Imperial_Wind | 0 | 0 | 0 | 0 | 0 |  | Westlands_Solar | SPGE_Z4_CentralValleyAndLosBanos | 150 | Distributed_Wind | #N/A
Greater_Kramer_Wind | 0 | 0 | 0 | 0 | 0 |  | #N/A |  | 1086.743 | Greater_Imperial_Solar | Greater_Imperial-SCADSNV
Humboldt_Wind | 0 | 0 | 0 | 0 | 0 |  | Grand Total |  | 3406.623 | Greater_Imperial_Wind | Greater_Imperial-SCADSNV
Inyokern_North_Kramer_Solar | 99.5 | 97 | 0 | 1 | 1 |  | Battery Total |  | 1216 | Greater_Kramer_Wind | Greater_Kramer
Kern_Greater_Carrizo_Solar | 335.68 | 437 | 101.32 | 1 | 0 |  |  |  |  | Humboldt_Wind | Sacramento_River-Humboldt
Kern_Greater_Carrizo_Wind | 40 | 60 | 20 | 1 | 0 |  |  |  |  | Inyokern_North_Kramer_Solar | Greater_Kramer-Inyokern_North_Kramer | 97
Kramer_Inyokern_Ex_Solar | 162 | 0 | 0 | 1 | 1 | Note contracting activity in location not selected by RESOLVE |  |  |  | Kern_Greater_Carrizo_Solar | SPGE-Kern_Greater_Carrizo | 437
Kramer_Inyokern_Ex_Wind | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Kern_Greater_Carrizo_Wind | SPGE-Kern_Greater_Carrizo | 60
Mountain_Pass_El_Dorado_Solar | 0 | 248 | 248 | [6 empty] | Kramer_Inyokern_Ex_Solar | Kramer_Inyokern_Ex
North_Victor_Solar | 0 | 300 | 300 | 1 | 0 |  |  |  |  | Kramer_Inyokern_Ex_Wind | Kramer_Inyokern_Ex
Northern_California_Ex_Solar | 0 | 397 | 397 | 1 | 0 | Note Ex zone |  |  |  | Mountain_Pass_El_Dorado_Solar | Mountain_Pass_El_Dorado | 248
Northern_California_Ex_Wind | 99 | 866 | 767 | 1 | 0 | Note Ex zone |  |  |  | North_Victor_Solar | North_Victor-Greater_Kramer | 300
NW_Ext_Tx_Wind | 0 | 530 | 530 | 1 | 0 |  |  |  |  | Northern_California_Ex_Solar | Northern_California_Ex | 397
Riverside_Palm_Springs_Solar | 545.5 | 0 | 0 | 1 | 1 | Note contracting activity in location not selected by RESOLVE |  |  |  | Northern_California_Ex_Wind | Sacramento_River | 866
Sacramento_River_Solar | 0 | 0 | 0 | 0 | 0 |  |  |  |  | NW_Ext_Tx_Wind | Sacramento_River | 530
Sacramento_River_Wind | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Riverside_Palm_Springs_Solar | SCADSNV-Riverside_Palm_Springs
SCADSNV_Solar | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Sacramento_River_Solar | Sacramento_River
SCADSNV_Wind | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Sacramento_River_Wind | N/A
Solano_Solar | 0 | 0 | 0 | 0 | 0 |  |  |  |  | SCADSNV_Solar | SCADSNV
Solano_subzone_Solar | 0 | 0 | 0 | 0 | 0 |  |  |  |  | SCADSNV_Wind | SCADSNV
Solano_subzone_Wind | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Solano_Solar | Solano-Sacramento_River
Solano_Wind | 80 | 542 | 462 | 1 | 0 |  |  |  |  | Solano_subzone_Solar | Solano-Sacramento_River-Solano_subzone
Southern_California_Desert_Ex_Solar | 0 | 862 | 862 | 1 | 0 | Note Ex zone |  |  |  | Solano_subzone_Wind | Solano-Sacramento_River-Solano_subzone
Southern_California_Desert_Ex_Wind | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Solano_Wind | Solano-Sacramento_River | 542
Southern_Nevada_Solar | 76 | 0 | 0 | 1 | 1 | Note contracting activity in location not selected by RESOLVE |  |  |  | Southern_California_Desert_Ex_Solar | Southern_California_Desert_Ex | 862
Southern_Nevada_Wind | 0 | 442 | 442 | 1 | 0 |  |  |  |  | Southern_California_Desert_Ex_Wind | Southern_California_Desert_Ex
SW_Ext_Tx_Wind | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Southern_Nevada_Solar | SCADSNV-GLW_VEA
Tehachapi_Solar | 145 | 4001 | 3856 | 1 | 0 |  |  |  |  | Southern_Nevada_Wind | SCADSNV-GLW_VEA | 442
Tehachapi_Ex_Solar | 0 | 0 | 0 | 0 | 0 |  |  |  |  | SW_Ext_Tx_Wind | SCADSNV-Riverside_Palm_Springs
Tehachapi_Wind | 0 | 275 | 275 | 1 | 0 |  |  |  |  | Tehachapi_Solar | Tehachapi | 4001
Westlands_Ex_Solar | 0 | 1779 | 1779 | 1 | 0 | Note Ex zone |  |  |  | Tehachapi_Ex_Solar | Tehachapi_Ex
Westlands_Ex_Wind | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Tehachapi_Wind | Tehachapi | 275
Westlands_Solar | 150 | 618 | 468 | 1 | 0 |  |  |  |  | Westlands_Ex_Solar | Westlands_Ex | 1779
Cape_Mendocino_Offshore_Wind | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Westlands_Ex_Wind | N/A
Del_Norte_Offshore_Wind | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Westlands_Solar | Central_Valley_North_Los_Banos-SPGE | 618
Diablo_Canyon_Offshore_Wind_Ext_Tx | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Cape_Mendocino_Offshore_Wind | N/A
Diablo_Canyon_Offshore_Wind | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Del_Norte_Offshore_Wind | N/A
Humboldt_Bay_Offshore_Wind | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Diablo_Canyon_Offshore_Wind_Ext_Tx | N/A
Morro_Bay_Offshore_Wind | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Diablo_Canyon_Offshore_Wind | N/A
Utah_Solar | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Humboldt_Bay_Offshore_Wind | N/A
Arizona_Solar | 0 | 447 | 447 | 1 | 0 |  |  |  |  | Morro_Bay_Offshore_Wind | N/A
New_Mexico_Solar | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Utah_Solar | N/A
Baja_California_Solar | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Arizona_Solar | SCADSNV-Riverside_Palm_Springs | 447
Baja_California_Wind | 105 | 600 | 495 | 1 | 0 |  |  |  |  | New_Mexico_Solar | N/A
Pacific_Northwest_Wind | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Baja_California_Solar | N/A
Idaho_Wind | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Baja_California_Wind | Greater_Imperial-SCADSNV | 600
Utah_Wind | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Pacific_Northwest_Wind | N/A
Wyoming_Wind | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Idaho_Wind | N/A
Arizona_Wind | 300 | 0 | 0 | 1 | 1 | Note contracting activity in location not selected by RESOLVE |  |  |  | Utah_Wind | N/A
New_Mexico_Wind | 0 | 945 | 945 | 1 | 0 |  |  |  |  | Wyoming_Wind | SCADSNV-Mountain_Pass_El_Dorado
Total | 2317.68 | 13963 | 12911.32 | 1 | 1363 |  |  |  |  | Arizona_Wind | N/A
Battery Total | 1216 | 10663.38 | 9447.38 | 1 | [5 empty] | New_Mexico_Wind | SCADSNV-Riverside_Palm_Springs | 945
[10 empty] | In-State |  | 13017
[10 empty] | Out-Of-State |  | 945
[10 empty] | Battery Total |  | 10663.38
Note: Resources with #N/A as transmission zone were not made available to the model for this scenario