## READ ME
This dashboard provides an overview of busbar mapping results for the CPUC IRP Proceeding
Resource-to-busbar mapping (“busbar mapping”) is the process of refining the geographically coarse portfolios produced in the California Public Utilities Commission’s (CPUC) Integrated Resource Plan (IRP) proceeding, into plausible network modeling locations for electrical analysis in the California Independent System Operator’s (CAISO) annual Transmission Planning Process (TPP).
The purpose of this workbook is to communicate the results of the 2019 busbar mapping process performed by the CPUC, CAISO and California Energy Commission (CEC).
Tabs shaded blue are authored by CEC: busbar allocation results
Tabs shaded purple are authored by CPUC: these tabs show busbar mapping criteria and results
Tab "Dashboard 2018PSP (Round 0)" shows the mapping criteria for the RESOLVE portfolio (2018 PSP) after baseline reconciliation (MW amounts in column D). Busbar mapping criteria are shown in columns G-M, with working group comments in column Q. Cells in the dashboard are shaded red, orange, and green, with red cells indicating issues exceeding the busbar mapping criteria compliance thresholds.
Tabs shaded green are authored by CPUC: these tabs show the underlying calculations used to review busbar mapping results against mapping criteria
Tabs shaded yellow are authored by CPUC: these tabs summarize post-processing adjustments (addressing criteria non-compliance)
Tab shaded purple "Dashboard 2018PSP (Round 1)" shows the criteria after round 1 mapping is complete. This tab is intended to show all issues have been addressed. All resources should appear orange and green on all criteria.
See methodology for more detail. “CPUC Staff Proposal: Methodology for 2019 IRP Resource-to-Busbar Mapping, October 18, 2019”
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Emily, the file is linking to other workbooks. Please break links.

## Dashboard 2018PSP (Round 0)
IRP Busbar Mapping Dashboard
Purpose: Quickly communicate compliance of portfolio mapping with the criteria per the Methodology. Highlight MW amounts by zone that breach criteria, if any, and identify next steps as part of the iterative process.
Updated 2018 PSP
|  |  | Selected | Busbar Mapping |  |  | Compliance with Criteria
Post Baseline Reconciliation, post-Updates | Resource Selection |  | Resources |  |  | [1=Yes, 2=Possible/Moderate, 3=Materially in Breach] | [8 empty] | Actions
Resource & Zone | 2030 FCDS MW | 2030 EO MW | Total MW (Updated Baseline) | Count of Substations Allocated To | MW Allocated (Mar 2019) | 1. Distance to Transmission | 2. Transmission Capability Limits | 3a. Available Land Area | 3b. High Environmental Implications | [lookup formula] | 4. Commercial Interest | 5. Consistency with Prior Year's Mapping | Sum of criteria | Low-Effort Adjustment Available? | Further Round of Mapping Needed? | Comment; Potential Solutions for Consideration | Include in display?
InState_Biomass |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Greater_Imperial_Geothermal |  |  | 1256 | 4 | 1276 | 1 | 1 |  |  | 1 | 1 | 1 | 4 |  | No | [Commercial interest]: CAISO queue has 0MW. IID queue has 500 MW | 1 | Note: see updated IID queue amount
Inyokern_North_Kramer_Geothermal |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Northern_California_Geothermal |  |  | 424 | 1 | 424 | 3 | 1 |  |  | 3 | 3 | 1 | 8 |  | Yes | [Distance to tx]: Known Geothermal Resource Areas (KGRA) are not in close proximity to CAISO-controlled facilities. Although the Round Mt 230 kV substation is the nearest major CAISO-controlled substation, the straight-line distance to each identified resource is approximately: geo_12 384 MW 56 mi NE; geo_11 32 MW 106 mi NE; geo_10 8 MW 92.5 mi SE. [Commercial interest]: Model selecting more than commercial interest (model = 424, commercial interest = 0). [Recommendation]: Re-allocate to equivalent resource (solar + storage) in locations of known commercial interest (Riverside_Palm_Springs, Tehachapi, Arizona) | 1
Pacific_Northwest_Geothermal |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Riverside_Palm_Springs_Geothermal |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Solano_Geothermal |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Southern_Nevada_Geothermal |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Carrizo_Wind |  |  | 160 | 2 | 160 | 1 | 1 |  |  | 1 | 1 | 1 | 4 |  | No |  | 1
Central_Valley_North_Los_Banos_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Central_Valley_North_Los_Banos_Wind |  |  | 146 | 1 | 146 | 1 | 1 |  |  | 1 | 1 | 1 | 4 | Yes | No |  | 1
Distributed_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Distributed_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Greater_Imperial_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 | 2 |  |  |  | 0
Greater_Imperial_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Greater_Kramer_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Humboldt_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 | 2 |  |  |  | 0
Inyokern_North_Kramer_Solar |  |  | 554 | 5 | 577 | 1 | 1 |  |  | 1 | 1 | 1 | 4 |  | No | [Baseline reconciliation]: amount reduced by 23 MW due to new projects online | 1
Kern_Greater_Carrizo_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Kern_Greater_Carrizo_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 | 2 |  |  |  | 0
Kramer_Inyokern_Ex_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 | 2 | Yes |  |  | 0
Kramer_Inyokern_Ex_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
North_Victor_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 | 2 |  |  |  | 0
Northern_California_Ex_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Northern_California_Ex_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 | 2 | Yes |  |  | 0
NW_Ext_Tx_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Riverside_Palm_Springs_Solar |  |  | 1194.09 | 2 | 1320 | 1 | 1 |  |  | 3 | 3 | 1 | 6 |  | Yes | [Commercial interest]: Model selecting less than commercial interest (model = 1320; queue = 4777 MW.) Note queue summary for this zone includes significant AZ solar (2595 MW), with POI specified in Riverside. [Recommendation]: Amount reduced by 126 MW (baseline reconciliation) | 1
Riverside_Palm_Springs_Wind |  |  | 42 | 1 | 42 | 1 | 1 |  |  | 1 | 1 | 1 | 4 |  | No |  | 1
Sacramento_River_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Sacramento_River_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
SCADSNV_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 | 2 |  |  |  | 0
SCADSNV_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Solano_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Solano_subzone_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Solano_subzone_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Solano_Wind |  |  | 643 | 5 | 643 | 1 | 1 |  |  | 1 | 1 | 1 | 4 |  | No |  | 1
Southern_California_Desert_Ex_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Southern_California_Desert_Ex_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Southern_Nevada_Solar |  |  | 3006 | 5 | 3006 | 2 | 3 |  |  | 1 | 1 | 1 | 7 |  | Yes | [Distance to tx]: See CPUC analysis (dated 6/28/19) reviewing detailed interconnection costs and recommending changes. [Distance to tx]: There are 3 Qualifying Resource Areas (QRAs) included in this transmission zone within the RESOLVE supply assumptions; all are located 30 to 200 miles to the El Dorado substation. [Tx capability limits]: Selected amount (3,000 MW SNV solar) does not exceed total area tx limit (3000 MW for Southern CA Desert and Southern NV) but may exceed sum of nested limits (250 MW for El Dorado and Mountain Pass, 700 MW for GLW-VEA). [Recommendation]: Reallocate the ~2.2GW of S NV Solar at El Dorado to Mojave. This means assuming that the 2.2GW is from the outer nested Southern CA Desert. | 1
Southern_Nevada_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
SW_Ext_Tx_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Tehachapi_Solar |  |  | 725 | 2 | 1013 | 1 | 1 |  |  | 3 | 3 | 1 | 6 |  | Yes | [Baseline reconciliation]: portfolio selection reduced by 288 MW (new projects online) [Commercial interest]: Model selecting less than commercial interest (model = 1013; queue = 4698 MW) | 1
Tehachapi_Ex_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 | 2 | Yes |  |  | 0
Tehachapi_Wind |  |  | 0 | 1 | 153 | 1 | 1 |  |  | 1 | 1 | 1 | 4 |  | No | [Baseline reconciliation]: portfolio selection reduced by 169 MW due to new projects online | 1
Westlands_Ex_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Westlands_Ex_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Westlands_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Westlands Wind |  |  |  | 0 | 0 |  | 1 |  |  | #N/A | #N/A | 1 |  |  |  |  | 0
Utah_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Arizona_Solar |  |  | 0 | 0 | 0 |  |  |  |  | 2 | 2 | 1 | 3 |  | Yes | [Commercial interest]: Arizona solar does not appear in 2018 PSP busbar mapping results, despite significant commercial interest (2595 MW). | 1
New_Mexico_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Baja_California_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 | 2 |  |  |  | 0
Pacific_Northwest_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Idaho_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Utah_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Wyoming_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Arizona_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 | [6 empty] | 0
New_Mexico_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  | 0 |  | 1 |  |  |  |  | 0
Sub Total - Renewables |  |  | 8150.09 | 29 | 8760 | [11 empty] | 1
Battery Storage |  |  |  | 0 | 0 | [10 empty] | ~2GW of storage +/- changes due to Baseline Rec and NoCal Geo substitution: not to be mapped, but PUC instruct ISO to consider using a mitigation for transmission issues found during TPP studies. | 1
Total - Renewables & Storage | [16 empty] | 1
Note on D54: Raffan, Neil: Fix zone name

## Dashboard 2018PSP (Round 1)
IRP Busbar Mapping Dashboard
Purpose: Quickly communicate compliance of portfolio mapping with the criteria per the Methodology. Highlight MW amounts by zone that breach criteria, if any, and identify next steps as part of the iterative process.
Updated 2018 PSP
Post Baseline Rec & Updates; Post Mapping Rnd 1 | Resource Selection |  | Selected | Busbar Mapping |  |  | Compliance with Criteria | [8 empty] | Actions
|  |  | Resources |  |  | [1=Yes, 2=Possible/Moderate, 3=Materially in Breach]
Resource & Zone | 2030 FCDS MW | 2030 EO MW | Total MW (After Adjustments) | Count of Substations Allocated To | MW Allocated | 1. Distance to Transmission | 2. Transmission Capability Limits |  | 3a. Available Land Area | 3b. High Environmental Implications | [lookup formula] | 4. Commercial Interest | 5. Consistency with Prior Year's Mapping | Sum of criteria | Low-Effort Adjustment Available? | Further Round of Mapping Needed? | Comment; Potential Solutions for Consideration | Include in display?
InState_Biomass |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Greater_Imperial_Geothermal |  |  | 1256 | 4 | 1256 | 1 | 1 | 9 | 1 |  | 1 | 1 | 1 | 5 |  | No | Model selecting more than queue (model = 1256 MW; queue = 600 MW) | 1
Inyokern_North_Kramer_Geothermal |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Northern_California_Geothermal |  |  | 0 | 1 | 0 | 1 | 1 |  | 1 |  | 1 | 1 | 1 | 5 |  | No |  | 1
Pacific_Northwest_Geothermal |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Riverside_Palm_Springs_Geothermal |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Solano_Geothermal |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Southern_Nevada_Geothermal |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Carrizo_Wind |  |  | 160 | 2 | 160 | 1 | 1 | 8 | 2 |  | 1 | 1 | 1 | 6 |  | No | One allocation assumes that 86% available land area for wind would be utilized | 1
Central_Valley_North_Los_Banos_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Central_Valley_North_Los_Banos_Wind |  |  | 146 | 1 | 146 | 1 | 1 | 9 | 2 |  | 1 | 1 | 1 | 6 | Yes | No | One allocation assumes that 56% available land area for wind would be utilized | 1
Distributed_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Distributed_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Greater_Imperial_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 | 2 |  |  |  | 0
Greater_Imperial_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Greater_Kramer_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Humboldt_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 | 2 |  |  |  | 0
Inyokern_North_Kramer_Solar |  |  | 554 | 5 | 554 | 1 | 1 | 10 | 1 |  | 1 | 1 | 1 | 5 |  | No |  | 1
Kern_Greater_Carrizo_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Kern_Greater_Carrizo_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 | 2 |  |  |  | 0
Kramer_Inyokern_Ex_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 | 2 | Yes |  |  | 0
Kramer_Inyokern_Ex_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
North_Victor_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 | 2 |  |  |  | 0
Northern_California_Ex_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Northern_California_Ex_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 | 2 | Yes |  |  | 0
NW_Ext_Tx_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Riverside_Palm_Springs_Solar |  |  | 1622.3728 | 2 | 1622 | 1 | 1 | 8 | 1 |  | 2 | 2 | 1 | 6 |  | No | Model selecting less than queue (model = 1320; queue = 4777 MW.) Note queue summary for this zone includes significant AZ solar, with POI specified in Riverside. | 1
Riverside_Palm_Springs_Wind |  |  | 42 | 1 | 42 | 1 | 1 | #N/A | 1 |  | 1 | 1 | 1 | 5 |  | No |  | 1
Sacramento_River_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Sacramento_River_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
SCADSNV_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 | 2 |  |  |  | 0
SCADSNV_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Solano_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Solano_subzone_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Solano_subzone_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Solano_Wind |  |  | 643 | 5 | 644 | 1 | 1 | 7 | 1 |  | 1 | 1 | 1 | 5 |  | No |  | 1
Southern_California_Desert_Ex_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Southern_California_Desert_Ex_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Southern_Nevada_Solar |  |  | 3006 | 5 | 3006 | 1 | 1 | 11 | 1 |  | 1 | 1 | 1 | 5 |  | No |  | 1
Southern_Nevada_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
SW_Ext_Tx_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Tehachapi_Solar |  |  | 1153.2828 | 2 | 1153 | 1 | 1 | 7 | 1 |  | 2 | 2 | 1 | 6 |  | No | Model selecting less than queue (model = 1153; queue = 4698 MW) | 1
Tehachapi_Ex_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 | 2 | Yes |  |  | 0
Tehachapi_Wind |  |  | 0 | 1 | 0 | 1 | 1 | 10 | 1 |  | 1 | 1 | 1 | 5 |  | No |  | 1
Westlands_Ex_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Westlands_Ex_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Westlands_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Westlands Wind |  |  |  | 0 | 0 |  | 1 |  |  |  | #N/A | #N/A | 1 |  |  |  |  | 0
Utah_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Arizona_Solar |  |  | 428.2828 | 0 | 428 | 1 | 1 |  | 1 |  | 2 | 2 | 1 | 6 |  | No | Model selecting less than queue (model = 428; queue = 2595 MW AZ resource interconnecting to substations in Riverside Palm Springs and Greater Imperial) | 1
New_Mexico_Solar |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Baja_California_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 | 2 |  |  |  | 0
Pacific_Northwest_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Idaho_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Utah_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Wyoming_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Arizona_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 | [6 empty] | 0
New_Mexico_Wind |  |  | 0 | 0 | 0 |  | 1 |  |  |  | 0 |  | 1 |  |  |  |  | 0
Sub Total - Renewables |  |  | 9010.9385 | 29 | 9011 | [12 empty] | 1
Battery Storage |  |  |  | 0 | 0 | [12 empty] | 1
Total - Renewables & Storage | [17 empty] | 1
Note on D54: Raffan, Neil: Fix zone name

## 1_CEC_BUSBARALLOC_2018_PSP_BASE
Source: TN227311_20190311T143938_UPDATED 2019 IRP Portfolio Allocations to Substations.xlsx (from CEC Docket 17-Misc-03)
Substation MW Mapping Allocation Recommendations for Transmission Modeling
Portfolio for Reliability and Policy-Driven Base Case (IEPR version of 42 MMT Case - Adjusted to Updated Transmission Capabilities)
|  | 2710 | 3206 | 341 | 803 | 1048 | 652 | 8760
Capacity selected using RESOLVE (MW)
| Transmission Zone | Solar |  | Wind |  | Geothermal |  | MW Assignment | Substation | Notes
|  | FCDS | EO | FCDS | EO | FCDS | EO
Northern California
Northern_California_Geothermal | Geothermal 424 MW |  |  |  |  | 424 |  | 424 | Round Mountain | Geothermal FCDS. Known Geothermal Resource Areas (KGRA) are not in close proximity to CAISO-controlled facilities. Although the Round Mt 230 kV substation is the nearest major CAISO-controlled substation, the straight-line distance to each identified resource is approximately: geo_12 384 MW 56 mi NE; geo_11 32 MW 106 mi NE; geo_10 8 MW 92.5 mi SE.
Solano
Solano_Wind | Wind 643 MW |  |  |  | 643 |  |  | 281 | Tesla 230kV
Solano_Wind | [7 empty] | 42 | Contra Costa
Solano_Wind | [7 empty] | 18 | Christie
Solano_Wind | [7 empty] | 247 | Vaca-Dixon
Solano_Wind | [7 empty] | 55 | Eight-Mile
Central Valley and Los Banos
Central_Valley_North_Los_Banos_Wind | Wind 146 MW |  |  | 146 |  |  |  | 146 | Los Banos 230kV
Westlands
Greater Carrizo
Carrizo_Wind | Wind 160 MW |  |  |  | 160 |  |  | 80 | Solar 230kV | These two substations are intended to correspond to the interconnection points for Topaz Solar Farm and California Valley Solar Ranch on the two Morro Bay to Midway 230 kV lines.
Carrizo_Wind | [7 empty] | 80 | Caliente 230kV
Tehachapi
Tehachapi_Solar | Solar 1013 MW | 1013 | [5 empty] | 565 | Whirlwind
Tehachapi_Solar | [7 empty] | 448 | Windhub
Tehachapi_Wind | Wind 153 MW |  |  | 153 |  |  |  | 153 | Highwind
Kramer and Inyokern
Inyokern_North_Kramer_Solar | Solar 577 MW | 577 | [5 empty] | 63 | Pisgah 230kV | Connect Cool Water MWs at Pisgah, due to Tx constraints.
Inyokern_North_Kramer_Solar | [7 empty] | 142 | Caldwell
Inyokern_North_Kramer_Solar | [7 empty] | 191 | Calcite (Proposed)
Inyokern_North_Kramer_Solar | [7 empty] | 100 | Kramer 230kV
Inyokern_North_Kramer_Solar | [7 empty] | 81 | Victor 230kV
Mountain Pass and El Dorado
SoCal Desert
Riverside East and Palm Springs
Riverside_Palm_Springs_Solar | Solar 1320 MW | 318 | 1002 |  |  |  |  | 861 | Colorado River
Riverside_Palm_Springs_Solar | [7 empty] | 459 | Red Bluff
Riverside_Palm_Springs_Wind | Wind 42 MW |  |  | 42 |  |  |  | 42 | Devers
Greater Imperial*
Greater_Imperial_Geothermal | Geothermal 1276 MW |  |  |  |  | 624 | 652 | 1052 | Bannister | Imperial Irrigation District (IID)
Greater_Imperial_Geothermal | [7 empty] | 160 | El Centro | IID-CAISO Line S
Greater_Imperial_Geothermal | [7 empty] | 32 | Highline | IID
Greater_Imperial_Geothermal | [7 empty] | 32 | Imperial Valley | CAISO
S Nevada (in-state)
Southern_Nevada_Solar | Solar 3006 MW | 802 | 2204 |  |  |  |  | 99 | Innovation | Solar FCDS. After allocating the FCDS resources, there is not sufficient transmission capability for the energy-only resources.
Southern_Nevada_Solar | [7 empty] | 77 | Desert View
Southern_Nevada_Solar | [7 empty] | 290 | Crazy Eyes (Proposed)
Southern_Nevada_Solar | [7 empty] | 236 | Gamebird (Proposed)
Southern_Nevada_Solar | [7 empty] | 2304 | ElDorado | 100 Solar FCDS + 2204 Solar EO. All of the assumed EO transmission capabilities are at this substation so the EO resources are allocated here. There are 3 Qualifying Resource Areas (QRAs) included in this transmission zone within the RESOLVE supply assumptions: The NV_SW QRA is 1,081,369 acres and the straight line distance to the nearest portion of the QRA is approximately 30 miles and the furthest portion is approximately 120 miles to the El Dorado substation. The NV_WE QRA is 2,476,129 acres and the straight line distance to the nearest portion of the QRA is approximately 120 miles and the furthest portion is over 200 miles to the El Dorado substation. The NV_EA QRA is 2,413,066 acres and the straight line distance to the nearest portion of the QRA is approximately 100 miles and the furthest portion is over 200 miles to the El Dorado substation.
*Substation assignments made on the basis of proximity to substations rather than on which entity operates the substation, which includes Imperial Irrigation District and CAISO in this zone.

## 1a_BUSBAR ALLOC_Adjusted
2018 PSP with Baseline Reconciliation
Selected Renewables by Location
|  | Renewable Resource Summary by Location (MW) |  |  |  |  | Revised Busbar Allocation
|  | RESOLVE Resource | Tx Zone | 2030 FD | 2030 EO | TOTAL | SUBSTATION | MW ASSIGNED
|  | InState_Biomass | None
|  | Greater_Imperial_Geothermal | Greater_Imperial | 604 | 652 | 1256
Greater_Imperial_Geothermal | [6 empty] | Bannister 230kV (IID) | 628 | IID
Greater_Imperial_Geothermal | [6 empty] | Hudson Ranch 230kV (IID) | 628 | Connecting to IID Midway 230kV
Greater_Imperial_Geothermal
Greater_Imperial_Geothermal
|  | Inyokern_North_Kramer_Geothermal | Inyokern_North_Kramer
|  | Northern_California_Ex_Geothermal | Northern_California_Ex
Northern_California_Ex_Geothermal | [6 empty] | Round Mountain
Pacific_Northwest_Geothermal
|  | Riverside_Palm_Springs_Geothermal | Riverside_Palm_Springs
|  | Solano_Geothermal | Solano
|  | Southern_Nevada_Geothermal | Mountain_Pass_El_Dorado
|  | Carrizo_Wind | Carrizo |  | 160 | 160
Carrizo_Wind | [6 empty] | Templeton | 160
|  | Central_Valley_North_Los_Banos_Solar | Central_Valley_North_Los_Banos |  |  | 0
|  | Central_Valley_North_Los_Banos_Wind | Central_Valley_North_Los_Banos | 146 |  | 146
Central_Valley_North_Los_Banos_Wind | [6 empty] | Los Banos | 146
|  | Distributed_Solar | None
|  | Distributed_Wind | None
|  | Greater_Imperial_Solar | Greater_Imperial |  |  | 0
|  | Greater_Imperial_Wind | Greater_Imperial
|  | Greater_Kramer_Wind | Greater_Kramer
|  | Humboldt_Wind | Humboldt
|  | Inyokern_North_Kramer_Solar | Inyokern_North_Kramer | 554 |  | 554
Inyokern_North_Kramer_Solar | [6 empty] | Caldwell | 263 | Victor Substation alloction removed due to significant land overlap with Caldwell Substation 81 MW reassigned form Victor to Caldwell | 63 | Pisgah 230kV | Connect Cool Water MWs at Pisgah, due to Tx constraints.
Inyokern_North_Kramer_Solar | [6 empty] | Calcite (Proposed) | 191 |  | 142 | Caldwell
Inyokern_North_Kramer_Solar | [6 empty] | Kramer 230kV | 100 |  | 191 | Calcite (Proposed)
Inyokern_North_Kramer_Solar | [9 empty] | 100 | Kramer 230kV
|  | Kern_Greater_Carrizo_Solar | Kern_Greater_Carrizo |  |  | 0
|  | Kern_Greater_Carrizo_Wind | Kern_Greater_Carrizo
|  | Kramer_Inyokern_Ex_Solar | Kramer_Inyokern_Ex
|  | Kramer_Inyokern_Ex_Wind | Kramer_Inyokern_Ex
|  | North_Victor_Solar | North_Victor_Solar |  |  | 0
|  | Northern_California_Ex_Solar | Northern_California_Ex
|  | Northern_California_Ex_Wind | Northern_California_Ex
|  | NW_Ext_Tx_Wind | Sacramento_River
|  | Riverside_Palm_Springs_Solar | Riverside_Palm_Springs | 192 | 1430 | 1622
Riverside_Palm_Springs_Solar | [6 empty] | Red Bluff | 1074
Riverside_Palm_Springs_Solar | [6 empty] | Colorado River | 548
|  | Sacramento_River_Solar | Sacramento_River
Sacramento_River_Wind
|  | SCADSNV_Solar | SCADSNV
|  | SCADSNV_Wind | SCADSNV
|  | Solano_Solar | Solano
|  | Solano_subzone_Solar | Solano_subzone
|  | Solano_subzone_Wind | Solano_subzone
|  | Solano_Wind | Solano |  | 643 | 643
Solano_Wind | [6 empty] | Lakeville | 270
Solano_Wind | [6 empty] | Tulucay | 27
Solano_Wind | [6 empty] | Vaca-Dixon & GC Yard | 203
Solano_Wind | [6 empty] | Shilo II | 100
Solano_Wind | [6 empty] | Lone Tree | 44
|  | Southern_California_Desert_Ex_Solar | Southern_California_Desert_Ex
|  | Southern_California_Desert_Ex_Wind | Southern_California_Desert_Ex
|  | Southern_Nevada_Solar | Mountain_Pass_El_Dorado | 802 | 2204 | 3006
Southern_Nevada_Solar | [6 empty] | Innovation | 152 | VA 700 MW FCDS Tx Constraint Limit
Southern_Nevada_Solar | [6 empty] | Desert View | 118
Southern_Nevada_Solar | [6 empty] | Crazy Eyes | 430
Southern_Nevada_Solar | [6 empty] | El Dorado 500 kV | 645 | EO
Southern_Nevada_Solar | [6 empty] | El Dorado 230 kV | 102 | FD
Southern_Nevada_Solar | [6 empty] | El Dorado 230 kV | 323 | EO
Southern_Nevada_Solar | [6 empty] | Mohave 500 kV | 1236 | EO Only
|  | Southern_Nevada_Wind | Mountain_Pass_El_Dorado
|  | SW_Ext_Tx_Wind | Riverside_Palm_Springs
|  | Tehachapi_Solar |  | 725 | 428 | 1153
Tehachapi_Solar | [6 empty] | WindHub | 277
Tehachapi_Solar | [6 empty] | Whirlwind | 307
Tehachapi_Solar | [6 empty] | Antelope | 300
Tehachapi_Solar | [6 empty] | Pearblossom | 269
|  | Tehachapi_Ex_Solar | Tehachapi_Ex
|  | Tehachapi_Wind | Tehachapi |  |  | 0
Tehachapi_Wind | [6 empty] | WindHub
|  | Westlands_Ex_Solar | Westlands_Ex
|  | Westlands_Ex_Wind | Westlands_Ex
|  | Westlands_Solar | Westlands |  |  | 0
|  | Utah_Solar | #N/A
|  | Arizona_Solar | #N/A |  | 428 | 428 |  | 428
Arizona_Solar | [6 empty] | Hassayampa | 47.08
Arizona_Solar | [6 empty] | Hoodoo Wash Switchyard | 222.56
Arizona_Solar | [6 empty] | Delaney-Colorado 500kV | 158.36
|  | New_Mexico_Solar | #N/A
|  | Baja_California_Wind | SCADSNV-Greater_Imperial
|  | Pacific_Northwest_Wind | #N/A
|  | Idaho_Wind | #N/A
|  | Utah_Wind | #N/A
|  | Wyoming_Wind | #N/A
|  | Arizona_Wind | #N/A
|  | New_Mexico_Wind | #N/A
|  | In-State |  | 3023 | 5945 | 8968 |  | 9397
|  | Out-Of-State |  | 0 | 0 | 0

## 2_TxCapability
What constitutes level 3 criteria flag? |  |  |  | Selected portfolio exceeds tx capability (FD or EO)
What constitutes level 2 criteria flag? |  |  |  | None
What constitutes level 1 criteria flag? |  |  |  | All other
[12 empty] | 4099 | 4661 |  |  |  |  | 8760 | 4099 | 4661
| Transmission Capability Estimated for IRP (dated May 20, 2019) | [9 empty] | RESOLVE Selected Portfolio (2018 PSP) Aggregated by Tx Zone |  |  |  |  | RESOLVE Selected Portfolio (2018 PSP) | [6 empty] | Modified 2018 PSP (w/ Norcal geothermal, SNV Solar adjustments)
| Transmission Zones | Estimated FCDS Capability (MW) |  |  |  | Incremental Upgrade Cost Estimate ($million) |  |  |  | Estimated EODS Capability (MW) | Zone |  |  |  |  | Resource | Zone | Selected by RESOLVE | Selected by RESOLVE (FD) | Selected by RESOLVE (EO) | Adjusted Selected resources (baseline, norcal geo, SNV solar adjustments) |  | Zone
|  | Existing System | Minor Upgrades | Major Upgrade #1 | Major Upgrade #2 | Existing System | Minor Upgrades | Major Upgrade #1 | Major Upgrade #2 | Existing System | Zone Name in RESOLVE | Selected Resource (FD MW) | Selected Resource (EO MW) | Exceeds Tx Capability (FD)? | Exceeds Tx Capability (EO)? | InState_Biomass |  | 0 | 0 |  |  |  | Zone Name in RESOLVE | Adjustment | Notes | Exceeds Tx Capability (FD)? | Exceeds Tx Capability (EO)?
| Northern CA | 2000 |  | 2000 |  |  |  | 285 |  | 3900 | [5 empty] | Greater_Imperial_Geothermal | SCADSNV_Z3_GreaterImperial | 1276 | 624 | 652 | 1256
| Round Mountain | 500 | [7 empty] | 2100 | [5 empty] | Inyokern_North_Kramer_Geothermal |  | 0 | 0 | 0
| Humboldt | 0 | [7 empty] | 100 | Norcal_Z2_Humboldt | 0 | 0 | 0 | 0 | Northern_California_Geothermal | Norcal_Z3_SacramentoRiver | 424 | 424 | 0 | 0 |  | Norcal_Z2_Humboldt | 0
| Sacramento River | 2000 | [7 empty] | 4600 | Norcal_Z3_SacramentoRiver | 424 | 0 | 0 | 0 | Pacific_Northwest_Geothermal |  | 0 | 0 | 0 |  |  | Norcal_Z3_SacramentoRiver | -424 | Norcal geothermal re-allocated to solar in prost-rprocessing due to viability and tx concerns | 0
| Solano | 600 |  | 2000 |  |  |  | 322 |  | 1300 | Norcal_Z4_Solano | 0 | 643 | 0 | 0 | Riverside_Palm_Springs_Geothermal |  | 0 | 0 | 0 |  |  | Norcal_Z4_Solano
[11 empty] | Norcal_Z4_Solano_subzone | 0 | 0 | 0 | 0 | Solano_Geothermal |  | 0 | 0 | 0 |  |  | Norcal_Z4_Solano_subzone
| Southern PG&E | 1100 |  | 1000 |  |  |  | 55 |  | TBD | [5 empty] | Southern_Nevada_Geothermal |  | 0 | 0 | 0
| Westlands | 1100 |  | 1000 |  |  |  | 55 |  | TBD | SPGE_Z1_Westlands | 0 | 0 | 0 |  | Carrizo_Solar |  | 0 | 0 | 0 |  |  | SPGE_Z1_Westlands
| Kern and Greater Carrizo | 1000 |  | 1500 |  |  |  | 241 |  | TBD | SPGE_Z2_KernAndGreaterCarrizo | 0 | 0 | 0 |  | Carrizo_Wind | SPGE_Z3_Carrizo | 160 | 0 | 160 | 160 |  | SPGE_Z2_KernAndGreaterCarrizo
| Carrizo | 400 |  | 700 |  |  |  | 53 |  | 400 | SPGE_Z3_Carrizo | 0 | 160 | 0 | 0 | Central_Valley_North_Los_Banos_Solar |  | 0 | 0 | 0 |  |  | SPGE_Z3_Carrizo
| Central Valley North & Los Banos | 1000 |  | 1000 |  |  |  | 274 |  | TBD | SPGE_Z4_CentralValleyAndLosBanos | 146 | 0 | 0 |  | Central_Valley_North_Los_Banos_Wind | SPGE_Z4_CentralValleyAndLosBanos | 146 | 146 | 0 | 146 |  | SPGE_Z4_CentralValleyAndLosBanos
[16 empty] | Distributed_Solar |  | 0 | 0 | 0
| Tehachapi | 4300 | 1000 |  |  |  | 100 |  |  | 5100 | Tehachapi | 1166 | 0 | 0 | 0 | Distributed_Wind |  | 0 | 0 | 0 |  |  | Tehachapi | 428 | 428 MW added to Riverside Palm Springs, due to re-alloaction of Norcal geothermal. | 0
[16 empty] | Greater_Imperial_Solar |  | 0 | 0 | 0
| Greater Kramer (North of Lugo) | 600 |  | 400 |  |  |  | 146 |  | 600 | GK_Z1_GreaterKramer | 0 | 0 | 0 | 0 | Greater_Imperial_Wind |  | 0 | 0 | 0 |  |  | GK_Z1_GreaterKramer
| North of Victor | 300 |  | 400 |  |  |  | 485 |  | 300 | GK_Z3_NorthOfVictor | 0 | 0 | 0 | 0 | Greater_Kramer_Wind |  | 0 | 0 | 0 |  |  | GK_Z3_NorthOfVictor
| Inyokern and North of Kramer | 100 |  | 400 |  |  |  | 485 |  | 100 | GK_Z2_InyokernAndNorthOfKramer | 577 | 0 | 0 | 0 | Humboldt_Wind |  | 0 | 0 | 0 |  |  | GK_Z2_InyokernAndNorthOfKramer
| Pisgah | 400 |  | 400 |  |  |  | 261 |  | 400 | GK_Z4_Pisgah | 0 | 0 | 0 | 0 | Inyokern_North_Kramer_Solar | GK_Z2_InyokernAndNorthOfKramer | 577 | 577 | 0 | 554 |  | GK_Z4_Pisgah
[16 empty] | Kern_Greater_Carrizo_Solar |  | 0 | 0 | 0
| Southern CA Desert and Southern NV | 3000 |  | 2800 |  |  |  | 2156 |  | 9600 | SCADSNV_Z5_SCADSNV | 802 | 2204 | 0 | 0 | Kern_Greater_Carrizo_Wind |  | 0 | 0 | 0 |  |  | SCADSNV_Z5_SCADSNV | (modified internally within zone, checked separately and confirmed tx impact ok)
| El Dorado and Mountain Pass 230 kV | 250 |  | 1400 |  |  |  | 76 |  | 2400 | [5 empty] | Kramer_Inyokern_Ex_Solar |  | 0 | 0 | 0
| Southern NV (GLW-VEA) | 700 |  | 1400 |  |  |  | 150 |  | 700 | [5 empty] | Kramer_Inyokern_Ex_Wind |  | 0 | 0 | 0
| Greater Imperial* | 1200 |  | 1400 |  |  |  | 2334 |  | 3100 | SCADSNV_Z3_GreaterImperial | 624 | 652 | 0 | 0 | North_Victor_Solar |  | 0 | 0 | 0 |  |  | SCADSNV_Z3_GreaterImperial
| Riverside East & Palm Springs | 2950 |  | 1500 |  |  |  | 2156 |  | 5500 | SCADSNV_Z4_RiversideAndPalmSprings | 360 | 1002 | 0 | 0 | Northern_California_Ex_Solar |  | 0 | 0 | 0 |  |  | SCADSNV_Z4_RiversideAndPalmSprings | 856 | 428 MW added to Riverside Palm Springs, due to re-alloaction of Norcal geothermal. 428 MW added to AZ solar, with delivery to Riverside and Palm Springs zone, from re-allocation of Norcal geothermal. | 0
[16 empty] | Northern_California_Ex_Wind |  | 0 | 0 | 0
[11 empty] | GreaterImpOutsideTxConstraintZones | 0 | 0 | 0 | 0 | NW_Ext_Tx_Wind |  | 0 | 0 | 0
[11 empty] | KramerInyoOutsideTxConstraintZones | 0 | 0 | 0 | 0 | Riverside_Palm_Springs_Solar | SCADSNV_Z4_RiversideAndPalmSprings | 1320 | 318 | 1002 | 1622
[11 empty] | NorCalOutsideTxConstraintZones | 0 | 0 | 0 | 0 | Riverside_Palm_Springs_Wind | SCADSNV_Z4_RiversideAndPalmSprings | 42 | 42 | 0
[11 empty] | TehachapiOutsideTxConstraintZones | 0 | 0 | 0 | 0 | Sacramento_River_Solar |  | 0 | 0 | 0
[11 empty] | WestlandsOutsideTxConstraintZones | 0 | 0 | 0 | 0 | Sacramento_River_Wind |  | 0 | 0 | 0
[16 empty] | SCADSNV_Solar |  | 0 | 0 | 0
[16 empty] | SCADSNV_Wind |  | 0 | 0 | 0
[16 empty] | Solano_Solar |  | 0 | 0 | 0
[16 empty] | Solano_subzone_Solar |  | 0 | 0 | 0
[16 empty] | Solano_subzone_Wind |  | 0 | 0 | 0
[16 empty] | Solano_Wind | Norcal_Z4_Solano | 643 | 0 | 643 | 643
[16 empty] | Southern_California_Desert_Ex_Solar |  | 0 | 0 | 0
[16 empty] | Southern_California_Desert_Ex_Wind |  | 0 | 0 | 0
[16 empty] | Southern_Nevada_Solar | SCADSNV_Z5_SCADSNV | 3006 | 802 | 2204 | 3006 | 700 (FD), 2300 (EO)
[16 empty] | Southern_Nevada_Wind |  | 0 | 0 | 0
[16 empty] | SW_Ext_Tx_Wind |  | 0 | 0 | 0
[16 empty] | Tehachapi_Solar | Tehachapi | 1013 | 1013 | 0 | 1153
[16 empty] | Tehachapi_Ex_Solar |  | 0 | 0 | 0
[16 empty] | Tehachapi_Wind | Tehachapi | 153 | 153 | 0
[16 empty] | Westlands_Ex_Solar |  | 0 | 0 | 0
[16 empty] | Westlands_Ex_Wind |  | 0 | 0 | 0
[16 empty] | Westlands_Solar |  | 0 | 0 | 0
[16 empty] | Cape_Mendocino_Offshore_Wind |  | 0 | 0 | 0
[16 empty] | Del_Norte_Offshore_Wind |  | 0 | 0 | 0
[16 empty] | Diablo_Canyon_Offshore_Wind_Ext_Tx |  | 0 | 0 | 0
[16 empty] | Diablo_Canyon_Offshore_Wind |  | 0 | 0 | 0
[16 empty] | Humboldt_Bay_Offshore_Wind |  | 0 | 0 | 0
[16 empty] | Morro_Bay_Offshore_Wind |  | 0 | 0 | 0
[16 empty] | Utah_Solar |  | 0 | 0 | 0
[16 empty] | Arizona_Solar |  | 0 | 0 | 0 | 428
[16 empty] | New_Mexico_Solar |  | 0 | 0 | 0
[16 empty] | Baja_California_Solar |  | 0 | 0 | 0
[16 empty] | Baja_California_Wind |  | 0 | 0 | 0
[16 empty] | Pacific_Northwest_Wind |  | 0 | 0 | 0
[16 empty] | Idaho_Wind |  | 0 | 0 | 0
[16 empty] | Utah_Wind |  | 0 | 0 | 0
[16 empty] | Wyoming_Wind |  | 0 | 0 | 0
[16 empty] | Arizona_Wind |  | 0 | 0 | 0
[16 empty] | New_Mexico_Wind |  | 0 | 0 | 0
[16 empty] | Mountain_Pass_and_El_Dorado_Solar |  | 0 | 0 | 0

## 3a_SUMMARY OF ACRES SOLAR
What constitutes level 3 criteria flag? |  |  | None
What constitutes level 2 criteria flag? |  |  | 10% | Exceeds this percentage utilization of available land in proximity to substation
What constitutes level 1 criteria flag? |  |  | All other
Summary of Solar Resource Acre Values within 15 miles of Selected Substations
Substation | Acres_15_ LOW | Acres_15_HIGH | Total ACRES | Potential MW | Potential MW_LOW | Potential MW_HIGH | MW Allocation | Percent of Total _MW | Percent of ACRES_LOW | Exceeds 10% Total)? (1,0) | Exceeds 10% (Low)? (1,0) | RESOLVE Resource lookup | RESOLVE Resource | Aggregated RESOLVE Resource | Criteria Threshold: Exceeds 10% (Total)? | Criteria Thershold: Exceeds 10% (Low)?
Antelope | 283494.6086 | 91597.5112 | 375092.1198 | 53584.5885 | 40499.2298 | 13085.3587 | 300 | 0.5599% | 0.7408% | 0 | 0 | 76 | Tehachapi_Solar | Tehachapi_Solar | 1 | 1
Casitas | [9 empty] | 0 | 0 |  |  | Riverside_Palm_Springs_Solar | 1 | 2
Colorado River | 121669.3342 | 200319.7753 | 321989.1095 | 45998.4442 | 17381.3335 | 28617.1108 | 548 | 1.191% | 3.153% | 0 | 0 | 47 | Riverside_Palm_Springs_Solar | Greater_Imperial_Geothermal | 1 | 1
Cool Water | [9 empty] | 0 | 0 |  |  | Inyokern_North_Kramer_Solar | 1 | 1
East County | [9 empty] | 0 | 0 |  |  | Southern_Nevada_Solar | 1 | 1
Imperial Valley | [9 empty] | 0 | 0
Kramer | 22291.7169 | 108531.3471 | 130823.0641 | 18689.0092 | 3184.531 | 15504.4782 | 100 | 0.5351% | 3.14% | 0 | 0
Mandalay | [9 empty] | 0 | 0
Moorpark | [9 empty] | 0 | 0
Ocotillo Express | [9 empty] | 0 | 0
Ormond Beach | [9 empty] | 0 | 0
Pearblossom | 161230.5478 | 175860.4673 | 337091.0151 | 48155.8593 | 23032.9354 | 25122.9239 | 269 | 1% | 1.168% | 0 | 0 | 77 | Tehachapi_Solar
Rancho Vista | [9 empty] | 0 | 0
Randsburg | [9 empty] | 0 | 0
Red Bluff | 51719.5818 | 112347.5969 | 164067.1787 | 23438.1684 | 7388.5117 | 16049.6567 | 1074 | 4.582% | 14.54% | 0 | 1 | 46 | Riverside_Palm_Springs_Solar
Rio Hondo | [9 empty] | 0 | 0
Santa Clara | [9 empty] | 0 | 0
Victor | 226643.6098 | 167494.0413 | 394137.651 | 56305.3787 | 32377.6585 | 23927.7202 | 81 | 0.1439% | 0.2502% | 0 | 0
Vista | [9 empty] | 0 | 0
Whirlwind | 242518.5078 | 141802.2074 | 384320.7152 | 54902.9593 | 34645.5011 | 20257.4582 | 307 | 0.5592% | 0.8861% | 0 | 0 | 75 | Tehachapi_Solar
Windhub | 224363.6679 | 122565.196 | 346928.864 | 49561.2663 | 32051.9526 | 17509.3137 | 277 | 0.5589% | 0.8642% | 0 | 0 | 74 | Tehachapi_Solar
Crazy Eyes |  |  | 155786.7953 | 22255.2565 |  |  | 430 | 1.932% |  | 0 | 0 | 66 | Southern_Nevada_Solar
Desert View |  |  | 42718.73 | 6102.6757 |  |  | 118 | 1.934% |  | 0 | 0 | 65 | Southern_Nevada_Solar
Innovation |  |  | 54904.2824 | 7843.4689 |  |  | 152 | 1.938% |  | 0 | 0 | 64 | Southern_Nevada_Solar
Mohave |  |  | 28763.8343 | 4109.1192 |  |  | 2204 | 53.64% |  | 1 | 0
El Dorado |  |  | 42263 | 6037.5714 |  |  | 102 | 1.689% |  | 0 | 0
Caldwell | 136997 | 104549.7844 | 241546.7844 | 34506.6835 | 19571 | 14935.6835 | 182 | 0.5274% | 0.9299% | 0 | 0 | 33 | Inyokern_North_Kramer_Solar
Calcite | 25822.5839 | 75486.3569 | 101308.9408 | 14472.7058 | 3688.9406 | 10783.7653 | 191 | 1.32% | 5.178% | 0 | 0
[10 empty] | 0 | 0
[10 empty] | 0 | 0
[10 empty] | 0 | 0
[10 empty] | 0 | 0
[10 empty] | 0 | 0
Totals | 2640477.6214 | 1946617.3771 | 4587094.9985 | 655299.2855 | 213821.5941 | 185793.4691 | 6335
Summary of Geothermal Resource Acre Values within 15 miles of Selected Substations
Substation | Acres_15_ LOW | Acres_15_HIGH | Total ACRES | Potential MW | Potential MW_LOW | Potential MW_HIGH | MW Allocation | Percent of Total _MW | Percent of ACRES_LOW
Bannister
El Centro
Highline
Imperial Valley | 207772.1766 | 25278.9441 | 233051.1206 |  |  |  | 32

## 3b_SUMMARY OF ACRES WIND
What constitutes level 3 criteria flag? |  |  |  | None
What constitutes level 2 criteria flag? |  |  |  | 50% | Exceeds this percentage utilization of available land in proximity to substation
What constitutes level 1 criteria flag? |  |  |  | All other
Summary of Wind Resource Acre Values within 15 miles of Selected Substations
Substation | Acres_15_ LOW | Acres_15_HIGH | Total ACRES | Potential MW | MW Allocation | Percent of Total _MW | PROJECT ACRES | Percent of Acres_LOW | Exceeds 50% Total)? (1,0) | Exceeds 50% (Low)? (1,0) | RESOLVE Resource | RESOLVE Resource | Aggregated RESOLVE Resource | Criteria Threshold: Exceeds 5% (Total)? | Criteria Threshold: Exceeds 5% (Low)?
Bridgeville | [8 empty] | 0 | 0 |  |  | Solano_Wind | 1 | 2
Brighton | [8 empty] | 0 | 0 |  |  | Carrizo_Wind | 2 | 2
Cholame | [8 empty] | 0 | 0 |  |  | Central_Valley_North_Los_Banos_Wind | 2 | 1
Lakeville | 20011.4281 | 126111.4854 | 146122.9135 | 706 | 270 | 38.24% | 10800 | 53.97% | 0 | 1 | 56 | Solano_Wind | Tehachapi_Wind | 1 | 1
Logan Creek | [8 empty] | 0 | 0
Lone Tree | 17434.3051 | 39699.3331 | 57133.6382 | 114 | 44 | 38.6% | 1760 | 10.1% | 0 | 0 | 60 | Solano_Wind
Los Banos | 14252.8953 | 22913.1322 | 37166.0275 | 170 | 146 | 85.88% | 5840 | 40.97% | 1 | 0 | 25 | Central_Valley_North_Los_Banos_Wind
Shilo II | 69123.0372 | 9056.3857 | 78179.4229 | 261 | 100 | 38.31% | 4000 | 5.787% | 0 | 0 | 59 | Solano_Wind
Templeton | 6729.9534 | 24299.8298 | 31029.7832 | 288 | 160 | 55.56% | 6400 | 95.1% | 1 | 1 | 22 | Carrizo_Wind
Tulucay | 9437.9712 | 32556.2646 | 41994.2357 | 72 | 27 | 37.5% | 1080 | 11.44% | 0 | 0 | 57 | Solano_Wind
Vaca-Dixon & Gc Yard | 125977.0079 | 35776.8433 | 161753.8513 | 531 | 203 | 38.23% | 8120 | 6.446% | 0 | 0 | 58 | Solano_Wind
Windhub | [8 empty] | 0 | 0 | 74 | Tehachapi_Wind
East County | [8 empty] | 0 | 0
| 262966.5982 | 290413.2741 | 553379.8723 | 2142 | 950 |  | 38000

## 4_CommercialInterest
What constitutes level 3 criteria flag? |  | 300 | MW | Model selection 300 MW or more, in absence of any commercial interest
|  | 3000 | MW | Difference from commercial interest
What constitutes level 2 criteria flag? |  | 2000 | MW or greater | Difference from commercial interest
What constitutes level 1 criteria flag? |  | All other
| Summary of Commercial Interest (Interconnection Queue / Zones Intersection) |  |  |  | Summary of Selected Portfolio (2018 PSP) | Selected by RESOLVE | Zone | Technology | Commercial Interest, Summarized by RESOLVE Resource | Difference (Selected Portfolio) - (Commercial Interest) | Selected Portfolio, as Percent of Queue | Boolean: significant model selection in absence of commercial interest | Mapping criteria exceedance level |  | Summary of Selected Portfolio (2018 PSP) After Post-Processing Adjustments | Selected by RESOLVE | Zone | Technology | Difference (Selected Portfolio) - (Commercial Interest) | Selected Portfolio, as Percent of Queue | Boolean: significant model selection in absence of commercial interest | Mapping criteria exceedance level
|  | Row Labels | Sum of MW-1 |  | InState_Biomass | 0 | [8 empty] | InState_Biomass | 0
| 0 | 0 | 3204.733 |  | Greater_Imperial_Geothermal | 1276 | SCADSNV_Z3_GreaterImperial | Geothermal | 100 | 1176 | 1276% | 0 | 1 | Model selecting significant amount in absence of commercial interest (model = 1276; queue = 0 MW) | Greater_Imperial_Geothermal | 1256 | SCADSNV_Z3_GreaterImperial | Geothermal | 1156 | 1256% | 0 | 1
| 0 | Photovoltaic | 1102.265 |  | Inyokern_North_Kramer_Geothermal | 0 | [8 empty] | Inyokern_North_Kramer_Geothermal | 0
| 0 | Storage | 1571.848 |  | Northern_California_Ex_Geothermal | 424 | NorCalOutsideTxConstraintZones | Geothermal | 0 | 424 | No commercial interest; 424 MW selected | 1 | 3 | Model selecting significant amount in absence of commercial interest (model = 424; queue = 0 MW) | Northern_California_Ex_Geothermal | 0 | NorCalOutsideTxConstraintZones | Geothermal | 0 | No commercial interest; 0 MW selected | 0 | 1
| 0 | Wind Turbine | 530.62 |  | Pacific_Northwest_Geothermal | 0 | [8 empty] | Pacific_Northwest_Geothermal | 0
| GK_Z2_InyokernAndNorthOfKramer | GK_Z2_InyokernAndNorthOfKramer | 1300.5 |  | Riverside_Palm_Springs_Geothermal | 0 | [8 empty] | Riverside_Palm_Springs_Geothermal | 0
| GK_Z2_InyokernAndNorthOfKramer | Photovoltaic | 824.26 |  | Solano_Geothermal | 0 | [8 empty] | Solano_Geothermal | 0
| GK_Z2_InyokernAndNorthOfKramer | Storage | 476.24 |  | Southern_Nevada_Geothermal | 0 | [8 empty] | Southern_Nevada_Geothermal | 0
| GK_Z3_NorthOfVictor | GK_Z3_NorthOfVictor | 320.92 |  | Carrizo_Solar | 0 | [8 empty] | Carrizo_Solar | 0
| GK_Z3_NorthOfVictor | Photovoltaic | 210.88 |  | Carrizo_Wind | 160 | SPGE_Z3_Carrizo | Wind Turbine | 0 | 160 | No commercial interest; 160 MW selected | 0 | 1 |  | Carrizo_Wind | 160 | SPGE_Z3_Carrizo | Wind Turbine | 160 | No commercial interest; 160 MW selected | 0 | 1
| GK_Z3_NorthOfVictor | Storage | 110.04 |  | Central_Valley_North_Los_Banos_Solar | 0 | [8 empty] | Central_Valley_North_Los_Banos_Solar | 0
| GreaterImpOutsideTxConstraintZones | GreaterImpOutsideTxConstraintZones | 1319.1 |  | Central_Valley_North_Los_Banos_Wind | 146 | SPGE_Z4_CentralValleyAndLosBanos | Wind Turbine | 0 | 146 | No commercial interest; 146 MW selected | 0 | 1 |  | Central_Valley_North_Los_Banos_Wind | 146 | SPGE_Z4_CentralValleyAndLosBanos | Wind Turbine | 146 | No commercial interest; 146 MW selected | 0 | 1
| GreaterImpOutsideTxConstraintZones | Storage | 110.04 |  | Distributed_Solar | 0 | [8 empty] | Distributed_Solar | 0
| KramerInyoOutsideTxConstraintZones | KramerInyoOutsideTxConstraintZones | 511.18 |  | Distributed_Wind | 0 | [8 empty] | Distributed_Wind | 0
| KramerInyoOutsideTxConstraintZones | Storage | 511.18 |  | Greater_Imperial_Solar | 0 | [8 empty] | Greater_Imperial_Solar | 0
| Norcal_Z2_Humboldt | Norcal_Z2_Humboldt | 348.1 |  | Greater_Imperial_Wind | 0 | [8 empty] | Greater_Imperial_Wind | 0
| Norcal_Z2_Humboldt | Storage | 50.875 |  | Greater_Kramer_Wind | 0 | [8 empty] | Greater_Kramer_Wind | 0
| Norcal_Z2_Humboldt | Wind Turbine | 297.225 |  | Humboldt_Wind | 0 | [8 empty] | Humboldt_Wind | 0
| Norcal_Z3_SacramentoRiver | Norcal_Z3_SacramentoRiver | 522 |  | Inyokern_North_Kramer_Solar | 577 | GK_Z2_InyokernAndNorthOfKramer | Photovoltaic | 824.26 | -247.26 | 70% | 0 | 1 |  | Inyokern_North_Kramer_Solar | 554 | GK_Z2_InyokernAndNorthOfKramer | Photovoltaic | -270.26 | 67.21% | 0 | 1
| Norcal_Z3_SacramentoRiver | Photovoltaic | 12 |  | Kern_Greater_Carrizo_Solar | 0 | [8 empty] | Kern_Greater_Carrizo_Solar | 0
| Norcal_Z3_SacramentoRiver | Storage | 510 |  | Kern_Greater_Carrizo_Wind | 0 | [8 empty] | Kern_Greater_Carrizo_Wind | 0
| Norcal_Z4_Solano | Norcal_Z4_Solano | 1164.104 |  | Kramer_Inyokern_Ex_Solar | 0 | [8 empty] | Kramer_Inyokern_Ex_Solar | 0
| Norcal_Z4_Solano | Photovoltaic | 431.4 |  | Kramer_Inyokern_Ex_Wind | 0 | [8 empty] | Kramer_Inyokern_Ex_Wind | 0
| Norcal_Z4_Solano | Storage | 299 |  | North_Victor_Solar | 0 | [8 empty] | North_Victor_Solar | 0
| Norcal_Z4_Solano | Wind Turbine | 433.704 |  | Northern_California_Ex_Solar | 0 | [8 empty] | Northern_California_Ex_Solar | 0
| Norcal_Z4_Solano_subzone | Norcal_Z4_Solano_subzone | 120.4 |  | Northern_California_Ex_Wind | 0 | [8 empty] | Northern_California_Ex_Wind | 0
| Norcal_Z4_Solano_subzone | Storage | 120.4 |  | NW_Ext_Tx_Wind | 0 | [8 empty] | NW_Ext_Tx_Wind | 0
| NorCalOutsideTxConstraintZones | NorCalOutsideTxConstraintZones | 1996.155 |  | Riverside_Palm_Springs_Solar | 1320 | SCADSNV_Z4_RiversideAndPalmSprings | Photovoltaic | 4777.38 | -3457.38 | 27.63% | 0 | 3 | Model selecting less than queue (model = 1320; queue = 4777 MW.) Note queue summary for this zone includes significant AZ solar, with POI specified in Riverside. | Riverside_Palm_Springs_Solar | 1622 | SCADSNV_Z4_RiversideAndPalmSprings | Photovoltaic | -3155.38 | 33.95% | 0 | 2 | Model selecting less than queue (model = 1622; queue = 4777 MW.) Note queue summary for this zone includes significant AZ solar, with POI specified in Riverside.
| NorCalOutsideTxConstraintZones | Hydro | 5 |  | Riverside_Palm_Springs_Wind | 42 | SCADSNV_Z4_RiversideAndPalmSprings | Wind Turbine | 0 | 42 | No commercial interest; 42 MW selected | 0 | 1 |  | Riverside_Palm_Springs_Wind | 0 | SCADSNV_Z4_RiversideAndPalmSprings | Wind Turbine | 0 | No commercial interest; 0 MW selected | 0 | 1
| NorCalOutsideTxConstraintZones | Photovoltaic | 20.6 |  | Sacramento_River_Solar | 0 | [8 empty] | Sacramento_River_Solar | 0
| NorCalOutsideTxConstraintZones | Steam Turbine | 5.5 |  | Sacramento_River_Wind | 0 | [8 empty] | Sacramento_River_Wind | 0
| NorCalOutsideTxConstraintZones | Storage | 191.055 |  | SCADSNV_Solar | 0 | [8 empty] | SCADSNV_Solar | 0
| NorCalOutsideTxConstraintZones | Wind Turbine | 1774 |  | SCADSNV_Wind | 0 | [8 empty] | SCADSNV_Wind | 0
| SCADSNV_Z3_GreaterImperial | SCADSNV_Z3_GreaterImperial | 7194.91 |  | Solano_Solar | 0 | [8 empty] | Solano_Solar | 0
| SCADSNV_Z3_GreaterImperial | Photovoltaic | 3050.58 |  | Solano_subzone_Solar | 0 | [8 empty] | Solano_subzone_Solar | 0
| SCADSNV_Z3_GreaterImperial | Storage | 2429.03 |  | Solano_subzone_Wind | 0 | [8 empty] | Solano_subzone_Wind | 0
| SCADSNV_Z3_GreaterImperial | Wind Turbine | 1715.3 |  | Solano_Wind | 643 | Norcal_Z4_Solano | Wind Turbine | 433.704 | 209.296 | 148.3% | 0 | 1 |  | Solano_Wind | 644 | Norcal_Z4_Solano | Wind Turbine | 210.296 | 148.5% | 0 | 1
| SCADSNV_Z4_RiversideAndPalmSprings | SCADSNV_Z4_RiversideAndPalmSprings | 8249.732 |  | Southern_California_Desert_Ex_Solar | 0 | [8 empty] | Southern_California_Desert_Ex_Solar | 0
| SCADSNV_Z4_RiversideAndPalmSprings | Photovoltaic | 4777.38 |  | Southern_California_Desert_Ex_Wind | 0 | [8 empty] | Southern_California_Desert_Ex_Wind | 0
| SCADSNV_Z4_RiversideAndPalmSprings | Steam Turbine | 49.5 |  | Southern_Nevada_Solar | 3006 | SCADSNV_Z5_SCADSNV | Photovoltaic | 2300.104 | 705.896 | 130.7% | 0 | 1 |  | Southern_Nevada_Solar | 3006 | SCADSNV_Z5_SCADSNV | Photovoltaic | 705.896 | 130.7% | 0 | 1
| SCADSNV_Z4_RiversideAndPalmSprings | Storage | 3422.852 |  | Southern_Nevada_Wind | 0 | [8 empty] | Southern_Nevada_Wind | 0
| SCADSNV_Z5_SCADSNV | SCADSNV_Z5_SCADSNV | 4892.664 |  | SW_Ext_Tx_Wind | 0 | [8 empty] | SW_Ext_Tx_Wind | 0
| SCADSNV_Z5_SCADSNV | Photovoltaic | 2300.104 |  | Tehachapi_Solar | 1013 | Tehachapi | Photovoltaic | 4697.9116 | -3684.9116 | 21.56% | 0 | 3 | Model selecting less than queue (model = 1013; queue = 4698 MW) | Tehachapi_Solar | 1153 | Tehachapi | Photovoltaic | -3544.9116 | 24.54% | 0 | 2 | Model selecting less than queue (model = 1153; queue = 4698 MW)
| SCADSNV_Z5_SCADSNV | Storage | 2282.56 |  | Tehachapi_Ex_Solar | 0 | [8 empty] | Tehachapi_Ex_Solar | 0
| SCADSNV_Z5_SCADSNV | Wind Turbine | 310 |  | Tehachapi_Wind | 153 | Tehachapi | Wind Turbine | 728.66 | -575.66 | 21% | 0 | 1 |  | Tehachapi_Wind | 0 | Tehachapi | Wind Turbine | -728.66 | 0% | 0 | 1
| SPGE_Z1_Westlands | SPGE_Z1_Westlands | 7402.177 |  | Westlands_Ex_Solar | 0 | [8 empty] | Westlands_Ex_Solar | 0
| SPGE_Z1_Westlands | Combined Cycle | 60 |  | Westlands_Ex_Wind | 0 | [8 empty] | Westlands_Ex_Wind | 0
| SPGE_Z1_Westlands | Gas Turbine | 63 |  | Westlands_Solar | 0 | [8 empty] | Westlands_Solar | 0
| SPGE_Z1_Westlands | Photovoltaic | 5245.997 |  | Cape_Mendocino_Offshore_Wind | 0 | [8 empty] | Cape_Mendocino_Offshore_Wind | 0
| SPGE_Z1_Westlands | Storage | 1953.18 |  | Del_Norte_Offshore_Wind | 0 | [8 empty] | Del_Norte_Offshore_Wind | 0
| SPGE_Z1_Westlands | Wind Turbine | 80 |  | Diablo_Canyon_Offshore_Wind_Ext_Tx | 0 | [8 empty] | Diablo_Canyon_Offshore_Wind_Ext_Tx | 0
| SPGE_Z2_KernAndGreaterCarrizo | SPGE_Z2_KernAndGreaterCarrizo | 4025.666 |  | Diablo_Canyon_Offshore_Wind | 0 | [8 empty] | Diablo_Canyon_Offshore_Wind | 0
| SPGE_Z2_KernAndGreaterCarrizo | Photovoltaic | 1898.196 |  | Humboldt_Bay_Offshore_Wind | 0 | [8 empty] | Humboldt_Bay_Offshore_Wind | 0
| SPGE_Z2_KernAndGreaterCarrizo | Storage | 1097.27 |  | Morro_Bay_Offshore_Wind | 0 | [8 empty] | Morro_Bay_Offshore_Wind | 0
| SPGE_Z2_KernAndGreaterCarrizo | Wind Turbine | 1030.2 |  | Utah_Solar | 0 | [8 empty] | Utah_Solar | 0
| SPGE_Z4_CentralValleyAndLosBanos | SPGE_Z4_CentralValleyAndLosBanos | 1114.986 |  | Arizona_Solar | 0 |  |  | 2595 | -2595 | 0% | 0 | 2 | Model selecting less than queue (model = 0; queue = 2595 MW). Sumarized manually by state in queue spreadsheet, to distentangle AZ solar overlap with other zones (interconnecting to substations in RiversidePalm Springs and Greater Imperial) | Arizona_Solar | 428 |  |  | -2167 | 16.49% | 0 | 2 | Model selecting less than queue (model = 428; queue = 2595 MW AZ resource interconnecting to substations in Riverside Palm Springs and Greater Imperial)
| SPGE_Z4_CentralValleyAndLosBanos | Photovoltaic | 298.35 |  | New_Mexico_Solar | 0 | [8 empty] | New_Mexico_Solar | 0
| SPGE_Z4_CentralValleyAndLosBanos | Storage | 816.636 |  | Baja_California_Solar | 0 | [8 empty] | Baja_California_Solar | 0
| Tehachapi | Tehachapi | 8631.4016 |  | Baja_California_Wind | 0 | [8 empty] | Baja_California_Wind | 0
| Tehachapi | Photovoltaic | 4697.9116 |  | Pacific_Northwest_Wind | 0 | [8 empty] | Pacific_Northwest_Wind | 0
| Tehachapi | Storage | 3204.83 |  | Idaho_Wind | 0 | [8 empty] | Idaho_Wind | 0
| Tehachapi | Wind Turbine | 728.66 |  | Utah_Wind | 0 | [8 empty] | Utah_Wind | 0
| TehachapiOutsideTxConstraintZones | TehachapiOutsideTxConstraintZones | 2528.65 |  | Wyoming_Wind | 0 | [8 empty] | Wyoming_Wind | 0
| TehachapiOutsideTxConstraintZones | Storage | 2528.65 |  | Arizona_Wind | 0 | [8 empty] | Arizona_Wind | 0
| WestlandsOutsideTxConstraintZones | WestlandsOutsideTxConstraintZones | 3424.35 |  | New_Mexico_Wind | 0 | [8 empty] | New_Mexico_Wind | 0
| WestlandsOutsideTxConstraintZones | Wind Turbine | 1568 |  | Mountain_Pass_and_El_Dorado | 0 | [8 empty] | Mountain_Pass_and_El_Dorado | 0
| WestlandsOutsideTxConstraintZones | #N/A | 1379.889 |  |  | 8760
| WestlandsOutsideTxConstraintZones | Combined Cycle | 35
| WestlandsOutsideTxConstraintZones | Photovoltaic | 604.239
| WestlandsOutsideTxConstraintZones | Storage | 740.65
| SPGE_Z3_Carrizo | SPGE_Z3_Carrizo | 606.2
| SPGE_Z3_Carrizo | Storage | 606.2
| None | None | 4336.85
| None | Storage | 4336.85
| Outside | Outside | 1512.6
| Outside | Storage | 1512.6
| GK_Z4_Pisgah | GK_Z4_Pisgah | 302.85
| GK_Z4_Pisgah | Photovoltaic | 302.85
| GK_Z1_GreaterKramer | GK_Z1_GreaterKramer | 156
| GK_Z1_GreaterKramer | Photovoltaic | 156
|  | Grand Total | 66566.1176
Note on K34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Note much of this is physically located in AZ, with queue POI specified in Riverside Palm Springs zone
Note on K62: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sumarized manually by state in queue spreadsheet, to distentangle overlap with other zones (RiversidePalm Springs and Greater Imperial)

## 4b_QueuePivotTable
Source: PublicQueueReport_2019-12-04_matchedToZones_iso.xlsx
Row Labels | Sum of MW-1
0 | 3204.733
Photovoltaic | 1102.265
Storage | 1571.848
Wind Turbine | 530.62
GK_Z2_InyokernAndNorthOfKramer | 1300.5
Photovoltaic | 824.26
Storage | 476.24
GK_Z3_NorthOfVictor | 320.92
Photovoltaic | 210.88
Storage | 110.04
GreaterImpOutsideTxConstraintZones | 1319.1
Storage | 1319.1
KramerInyoOutsideTxConstraintZones | 511.18
Storage | 511.18
Norcal_Z2_Humboldt | 348.1
Storage | 50.875
Wind Turbine | 297.225
Norcal_Z3_SacramentoRiver | 522
Photovoltaic | 12
Storage | 510
Norcal_Z4_Solano | 1164.104
Photovoltaic | 431.4
Storage | 299
Wind Turbine | 433.704
Norcal_Z4_Solano_subzone | 120.4
Storage | 120.4
NorCalOutsideTxConstraintZones | 1996.155
Hydro | 5
Photovoltaic | 20.6
Steam Turbine | 5.5
Storage | 191.055
Wind Turbine | 1774
SCADSNV_Z3_GreaterImperial | 7194.91
Photovoltaic | 3050.58
Storage | 2429.03
Wind Turbine | 1715.3
SCADSNV_Z4_RiversideAndPalmSprings | 8249.732
Photovoltaic | 4777.38
Steam Turbine | 49.5
Storage | 3422.852
SCADSNV_Z5_SCADSNV | 4892.664
Photovoltaic | 2300.104
Storage | 2282.56
Wind Turbine | 310
SPGE_Z1_Westlands | 7402.177
Combined Cycle | 60
Gas Turbine | 63
Photovoltaic | 5245.997
Storage | 1953.18
Wind Turbine | 80
SPGE_Z2_KernAndGreaterCarrizo | 4025.666
Photovoltaic | 1898.196
Storage | 1097.27
Wind Turbine | 1030.2
SPGE_Z4_CentralValleyAndLosBanos | 1114.986
Photovoltaic | 298.35
Storage | 816.636
Tehachapi | 8631.4016
Photovoltaic | 4697.9116
Storage | 3204.83
Wind Turbine | 728.66
TehachapiOutsideTxConstraintZones | 2528.65
Storage | 2528.65
WestlandsOutsideTxConstraintZones | 3424.35
Storage | 1856.35
Wind Turbine | 1568
#N/A | 1379.889
Combined Cycle | 35
Photovoltaic | 604.239
Storage | 740.65
SPGE_Z3_Carrizo | 606.2
Storage | 606.2
None | 4336.85
Storage | 4336.85
Outside | 1512.6
Storage | 1512.6
GK_Z4_Pisgah | 302.85
Photovoltaic | 302.85
GK_Z1_GreaterKramer | 156
Photovoltaic | 156
Grand Total | 66566.1176

## 5_ComparToPrevYr
What constitutes level 3 criteria flag? | 1000 | or greater | Difference from prior year
What constitutes level 2 criteria flag? | 0.6 | or greater | Difference from prior year
What constitutes level 1 criteria flag?
| 032019 FD + EO | 2018
RESOLVE Resource | Base | PSP | Delta | Difference > 1000 MW? | Dashboard value
InState_Biomass | 0 | 0 | 0% | 0 | 1
Greater_Imperial_Geothermal | 1276 | 1276 | 0% | 0 | 1
Inyokern_North_Kramer_Geothermal | 0 | 0 | 0% | 0 | 1
Northern_California_Ex_Geothermal | 424 | 424 | 0% | 0 | 1
Pacific_Northwest_Geothermal | 0 | 0 | 0% | 0 | 1
Riverside_Palm_Springs_Geothermal | 0 | 0 | 0% | 0 | 1
Solano_Geothermal | 0 | 0 | 0% | 0 | 1
Southern_Nevada_Geothermal | 0 | 0 | 0% | 0 | 1
Carrizo_Solar | 0 | 0 | 0% | 0 | 1
Carrizo_Wind | 160 | 160 | 0% | 0 | 1
Central_Valley_North_Los_Banos_Solar | 0 | 0 | 0% | 0 | 1
Central_Valley_North_Los_Banos_Wind | 146 | 146 | 0% | 0 | 1
Distributed_Solar | 0 | 0 | 0% | 0 | 1
Distributed_Wind | 0 | 0 | 0% | 0 | 1
Greater_Imperial_Solar | 0 | 0 | 0% | 0 | 1
Greater_Imperial_Wind | 0 | 0 | 0% | 0 | 1
Greater_Kramer_Wind | 0 | 0 | 0% | 0 | 1
Humboldt_Wind | 0 | 0 | 0% | 0 | 1
Inyokern_North_Kramer_Solar | 577 | 577 | 0% | 0 | 1
Kern_Greater_Carrizo_Solar | 0 | 0 | 0% | 0 | 1
Kern_Greater_Carrizo_Wind | 0 | 0 | 0% | 0 | 1
Kramer_Inyokern_Ex_Solar | 0 | 0 | 0% | 0 | 1
Kramer_Inyokern_Ex_Wind | 0 | 0 | 0% | 0 | 1
North_Victor_Solar | 0 | 0 | 0% | 0 | 1
Northern_California_Ex_Solar | 0 | 0 | 0% | 0 | 1
Northern_California_Ex_Wind | 0 | 0 | 0% | 0 | 1
NW_Ext_Tx_Wind | 0 | 0 | 0% | 0 | 1
Riverside_Palm_Springs_Solar | 1320 | 1320 | 0% | 0 | 1
Riverside_Palm_Springs_Wind | 42 | 42 | 0% | 0 | 1
Sacramento_River_Solar | 0 | 0 | 0% | 0 | 1
Sacramento_River_Wind | 0 | 0 | 0% | 0 | 1
SCADSNV_Solar | 0 | 0 | 0% | 0 | 1
SCADSNV_Wind | 0 | 0 | 0% | 0 | 1
Solano_Solar | 0 | 0 | 0% | 0 | 1
Solano_subzone_Solar | 0 | 0 | 0% | 0 | 1
Solano_subzone_Wind | 0 | 0 | 0% | 0 | 1
Solano_Wind | 643 | 643 | 0% | 0 | 1
Southern_California_Desert_Ex_Solar | 0 | 0 | 0% | 0 | 1
Southern_California_Desert_Ex_Wind | 0 | 0 | 0% | 0 | 1
Southern_Nevada_Solar | 3006 | 3006 | 0% | 0 | 1
Southern_Nevada_Wind | 0 | 0 | 0% | 0 | 1
SW_Ext_Tx_Wind | 0 | 0 | 0% | 0 | 1
Tehachapi_Solar | 1013 | 1013 | 0% | 0 | 1
Tehachapi_Ex_Solar | 0 | 0 | 0% | 0 | 1
Tehachapi_Wind | 153 | 153 | 0% | 0 | 1
Westlands_Ex_Solar | 0 | 0 | 0% | 0 | 1
Westlands_Ex_Wind | 0 | 0 | 0% | 0 | 1
Westlands_Solar | 0 | 0 | 0% | 0 | 1
Cape_Mendocino_Offshore_Wind | 0 | 0 | 0% | 0 | 1
Del_Norte_Offshore_Wind | 0 | 0 | 0% | 0 | 1
Diablo_Canyon_Offshore_Wind_Ext_Tx | 0 | 0 | 0% | 0 | 1
Diablo_Canyon_Offshore_Wind | 0 | 0 | 0% | 0 | 1
Humboldt_Bay_Offshore_Wind | 0 | 0 | 0% | 0 | 1
Morro_Bay_Offshore_Wind | 0 | 0 | 0% | 0 | 1
Utah_Solar | 0 | 0 | 0% | 0 | 1
Arizona_Solar | 0 | 0 | 0% | 0 | 1
New_Mexico_Solar | 0 | 0 | 0% | 0 | 1
Baja_California_Solar | 0 | 0 | 0% | 0 | 1
Baja_California_Wind | 0 | 0 | 0% | 0 | 1
Pacific_Northwest_Wind | 0 | 0 | 0% | 0 | 1
Idaho_Wind | 0 | 0 | 0% | 0 | 1
Utah_Wind | 0 | 0 | 0% | 0 | 1
Wyoming_Wind | 0 | 0 | 0% | 0 | 1
Arizona_Wind | 0 | 0 | 0% | 0 | 1
New_Mexico_Wind | 0 | 0 | 0% | 0 | 1
Tehachapi_Solar | 0 | 0 | 0% | 0 | 1
Mountain_Pass_and_El_Dorado | 0 | 0 | 0% | 0 | 1
Note on B4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Source: Mar 2019 Busbar Allocation Filename: TN227311_20190311T143938_UPDATED 2019 IRP Portfolio Allocations to Substations.xlsx Downloaded from CEC Docket 17-Misc-03

## NoCal_Geo
| 2018 PSP as at March 2019 | 2018 PSP Updated February 2020
| Northern_California_Geothermal | Utility-scale Solar PV & Battery Storage | Utility-scale Solar PV & Battery Storage | Notes
|  | Option 1 | Option 2
Nameplate MW FCDS | 424
Capacity Factor | 90% |  |  | Source: Resource_Characteristics, RESOLVE_Resource Costs and Build.xls
Annual Energy (GWh) | 3342.816
Capacity Factor - Utility-scale Solar PV |  |  | 33% | Source: Resource_Characteristics, RESOLVE_Resource Costs and Build.xls
Solar curtailment |  |  | 10% | Source: estimate based on typical RESOLVE runs
Nameplate MW EO - Solar |  | 1284.8485 | 1284.8485 | Capacity of solar to provide the Annual Energy, allowing for curtailment
Assumed Battery : Geothermal replacement ratio (Option 1) |  | 1 |  | 1:1 replacing each MW of geothermal with 1 MW of 4 hour batteries
Alternatively: Nameplate MW Battery per Nameplate MW Solar (Option 2) |  |  | 0.80539 | Per Final RSP in 2030: Battery Storage 8,873MW Solar 11,017MW
Nameplate MW FCDS - Battery Storage |  | 424 | 1034.8063

## NewBaselineSumByRESOLVEResource
| Additions to 2019 Baseline since 2018 PSP | 2030 Selected Resources, 2018 PSP as at March 2019 | 2030 Selected Resources, post Baseline Rec at February 2020 | FOR MAPPING Post NoCal Geothermal substitution
RESOLVE Resource | MW | MW | MW | MW | Display_filter | Flag new commercial resources online where RESOLVE selected none | Notes
InState_Biomass |  | 0 | 0 |  | 0 | 0
Greater_Imperial_Geothermal | 20 | 1276 | 1256 | 1256 | 1 | 0
Inyokern_North_Kramer_Geothermal |  | 0 | 0 |  | 0 | 0
Northern_California_Geothermal |  | 424 | 424 | 0 | 1 | 0
Pacific_Northwest_Geothermal |  | 0 | 0 |  | 0 | 0
Riverside_Palm_Springs_Geothermal |  | 0 | 0 |  | 0 | 0
Solano_Geothermal |  | 0 | 0 |  | 0 | 0
Southern_Nevada_Geothermal |  | 0 | 0 |  | 0 | 0
Carrizo_Solar |  | 0 | 0 |  | 0 | 0
Carrizo_Wind |  | 160 | 160 | 160 | 1 | 0
Central_Valley_North_Los_Banos_Solar | 21.5 | 0 | 0 | 0 | 1 | 1
Central_Valley_North_Los_Banos_Wind |  | 146 | 146 | 146 | 1 | 0
Distributed_Solar |  | 0 | 0 |  | 0 | 0
Distributed_Wind |  | 0 | 0 |  | 0 | 0
Greater_Imperial_Solar | 470.81 | 0 | 0 | 0 | 1 | 1
Greater_Imperial_Wind |  | 0 | 0 |  | 0 | 0
Greater_Kramer_Wind |  | 0 | 0 |  | 0 | 0
Humboldt_Wind |  | 0 | 0 |  | 0 | 0
Inyokern_North_Kramer_Solar | 23 | 577 | 554 | 554 | 1 | 0
Kern_Greater_Carrizo_Solar | 5 | 0 | 0 | 0 | 1 | 1
Kern_Greater_Carrizo_Wind |  | 0 | 0 |  | 0 | 0
Kramer_Inyokern_Ex_Solar |  | 0 | 0 |  | 0 | 0
Kramer_Inyokern_Ex_Wind |  | 0 | 0 |  | 0 | 0
North_Victor_Solar | 13.8 | 0 | 0 | 0 | 1 | 1
Northern_California_Ex_Solar |  | 0 | 0 |  | 0 | 0
Northern_California_Ex_Wind |  | 0 | 0 |  | 0 | 0
NW_Ext_Tx_Wind |  | 0 | 0 |  | 0 | 0
Riverside_Palm_Springs_Solar | 125.91 | 1320 | 1194.09 | 1622.3728 | 1 | 0 | Includes 428MW of EO solar as partial substitution of NoCal Geothermal
Riverside_Palm_Springs_Wind |  | 42 | 42 | 42
Sacramento_River_Solar |  | 0 | 0 |  | 0 | 0
Sacramento_River_Wind |  | 0 | 0 |  | 0 | 0
SCADSNV_Solar |  | 0 | 0 |  | 0 | 0
SCADSNV_Wind |  | 0 | 0 |  | 0 | 0
Solano_Solar |  | 0 | 0 |  | 0 | 0
Solano_subzone_Solar |  | 0 | 0 |  | 0 | 0
Solano_subzone_Wind |  | 0 | 0 |  | 0 | 0
Solano_Wind |  | 643 | 643 | 643 | 1 | 0
Southern_California_Desert_Ex_Solar |  | 0 | 0 |  | 0 | 0
Southern_California_Desert_Ex_Wind |  | 0 | 0 |  | 0 | 0
Southern_Nevada_Solar |  | 2304 | 2304 | 2304 | 1 | 0
GLW-VEA_Solar |  | 702 | 702 | 702 | 1 | 0 | Included in "Southern_Nevada_Solar" elsewhere in this report
Southern_Nevada_Wind |  | 0 | 0 |  | 0 | 0
SW_Ext_Tx_Wind |  | 0 | 0 |  | 0 | 0
Tehachapi_Solar | 288 | 1013 | 725 | 1153.2828 | 1 | 0 | Includes 428MW of EO solar as partial substitution of NoCal Geothermal
Tehachapi_Ex_Solar |  | 0 | 0 |  | 0 | 0
Tehachapi_Wind | 169.1 | 153 | 0 | 0 | 1 | 0
Westlands_Ex_Solar |  | 0 | 0 |  | 0 | 0
Westlands_Ex_Wind |  | 0 | 0 |  | 0 | 0
Westlands_Solar | 290.25 | 0 | 0 | 0 | 1 | 1
Westlands_Wind |  |  |  |  | 0 | 0
Cape_Mendocino_Offshore_Wind |  | 0 | 0 |  | 0 | 0
Del_Norte_Offshore_Wind |  | 0 | 0 |  | 0 | 0
Diablo_Canyon_Offshore_Wind_Ext_Tx |  | 0 | 0 |  | 0 | 0
Diablo_Canyon_Offshore_Wind |  | 0 | 0 |  | 0 | 0
Humboldt_Bay_Offshore_Wind |  | 0 | 0 |  | 0 | 0
Morro_Bay_Offshore_Wind |  | 0 | 0 |  | 0 | 0
Utah_Solar |  | 0 | 0 |  | 0 | 0
Arizona_Solar |  | 0 | 0 | 428.2828 | 1 | 0 | Includes 428MW of EO solar as partial substitution of NoCal Geothermal. Assumed to flow through Riverside_Palm_Springs.
New_Mexico_Solar |  | 0 | 0 |  | 0 | 0
Baja_California_Solar |  | 0 | 0 |  | 0 | 0
Baja_California_Wind |  | 0 | 0 |  | 0 | 0
Pacific_Northwest_Wind |  | 0 | 0 |  | 0 | 0
Idaho_Wind |  | 0 | 0 |  | 0 | 0
Utah_Wind |  | 0 | 0 |  | 0 | 0
Wyoming_Wind |  | 0 | 0 |  | 0 | 0
Arizona_Wind |  | 0 | 0 |  | 0 | 0
New_Mexico_Wind |  | 0 | 0 |  | 0 | 0
Total | 1427.37 | 8760 | 8150.09 | 9010.9385 | 1 | 801.36
|  |  | -609.91 | 250.9385 | 1
1
Working | [7 empty] | 1
Additional EO Solar MW from NoCal Geothermal |  |  |  | 1284.8485
- allocation to Riverside_Palm_Springs | 33.33% |  |  | 428.2828
- allocation to Tehachapi Solar | 33.33% |  |  | 428.2828
- allocation to Arizona Solar | 33.33% |  |  | 428.2828