## READ ME
This dashboard provides an overview of busbar mapping results for the CPUC IRP Proceeding
Resource-to-busbar mapping (“busbar mapping”) is the process of refining the geographically coarse portfolios produced in the California Public Utilities Commission’s (CPUC) Integrated Resource Plan (IRP) proceeding, into plausible network modeling locations for electrical analysis in the California Independent System Operator’s (CAISO) annual Transmission Planning Process (TPP).
The purpose of this workbook is to communicate the results of the 2019 busbar mapping process performed by the CPUC, CAISO and California Energy Commission (CEC).
Tabs shaded blue are authored by CEC: busbar allocation results
Tabs shaded purple are authored by CPUC: these tabs show busbar mapping criteria and results
Tabs shaded green are authored by CPUC: these tabs show the underlying calculations used to review busbar mapping results against mapping criteria
See Methodology for more detail, available at:
https://www.cpuc.ca.gov/General.aspx?id=6442464144

## VERSIONS
Version # | Mapping Rounds Performed | Description | Changes to Prior Version
0.1 | 0 | 30MMT_20200207_2045_2GWPRM_NOOTCEXT_ExpandedEO | Not applicable
0.2 | 0 | Sending to CEC for mapping | Formatting
1 | 1 & 2 |  | Includes feedback from ISO and PUC staff on 3/20 check-in call
2 | 2 |  | Imported round 2 mapping results, created round 2 dashboard, updated all criteria.
Revised rounds 0 and 1 dashboards to retain criteria values prior to round 2 (hard coded from prior version)
2.1 | 2 |  | Cleaned up for public posting

## Dashboard 30MMTEO2(Round 0)
IRP Busbar Mapping Dashboard
Purpose: Quickly communicate compliance of portfolio mapping with the criteria per the Methodology. Highlight MW amounts by zone that breach criteria, if any, and identify next steps as part of the iterative process.
30 MMT EO
Pre Round 1 - RESOLVE selections |  |  | Selected | Selected |  |  | Compliance with Criteria
| Resource Selection |  | Resources | Resources | [1=Yes, 2=Possible/Moderate, 3=Materially in Breach] | [9 empty] | Actions
Resource | 2030 FCDS MW | 2030 EO MW | Total MW (2018 PSP) | Total MW (2019 EO P'folio) | 1. Distance to Transmission |  | 2. Transmission Capability Limits | 3a. Available Land Area | 3b. High Environmental Implications | [lookup formula] | 4. Commercial Interest | 5. Consistency with Prior Year's Mapping | Sum of criteria | Low-Effort Adjustment Available? | Further Round of Mapping Needed? | Comment; Potential Solutions for Consideration | Include in display?
InState_Biomass |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Greater_Imperial_Geothermal |  |  | 1256 | 716.46 |  | ok | 1 |  |  | 1 | 1 | 1 | 3 |  |  |  | 1
Inyokern_North_Kramer_Geothermal |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Northern_California_Geothermal |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 |  | 2 |  |  |  | 0
Pacific_Northwest_Geothermal |  |  | 0 | 0 |  | N/A | [5 empty] | 1 |  |  |  |  | 0
Riverside_Palm_Springs_Geothermal |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Solano_Geothermal |  |  | 0 | 135 |  | ok | 1 |  |  | 1 | 1 | 2 |  |  |  | [Prior year]: none selected previously. | 1
Southern_Nevada_Geothermal |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Carrizo_Solar |  |  | 0 | 600 |  | ok | 1 |  |  | 3 | 3 | 2 |  |  |  | [Commercial interest]: model selecting more than queue (queue = 0 MW) [Prior year]: none selected previously. | 1
Carrizo_Wind |  |  | 160 | 287 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  |  | [Commercial interest]: model selecting more than queue (queue = 0 MW) | 1
Central_Valley_North_Los_Banos_Solar |  |  | 0 | 0 |  | breach | 3 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Central_Valley_North_Los_Banos_Wind |  |  | 146 | 173 |  | breach | 1 |  |  | 1 | 1 | 1 | 3 | Yes |  |  | 1
Distributed_Solar |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Distributed_Wind |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Greater_Imperial_Solar |  |  | 0 | 866.98 |  | ok | 1 |  |  | 2 | 2 | 2 | 5 |  |  | [Commercial interest]: model selecting less than queue (queue = 3051 MW) [Prior year]: none selected previously. | 1
Greater_Imperial_Wind |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Greater_Kramer_Wind |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Humboldt_Wind |  |  | 0 | 34 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  |  | [Prior year]: none selected previously. | 1
Inyokern_North_Kramer_Solar |  |  | 554 | 97 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  |  | [Prior year]: 554 MW selected previously | 1
Kern_Greater_Carrizo_Solar |  |  | 0 | 3001.27 |  | ok | 1 |  |  | 1 | 1 | 3 |  |  |  | [Prior year]: none selected previously. | 1
Kern_Greater_Carrizo_Wind |  |  | 0 | 60 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  |  | [Prior year]: none selected previously. | 1
Kramer_Inyokern_Ex_Solar |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 | 3 | Yes |  |  | 0
Kramer_Inyokern_Ex_Wind |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Mountain_Pass_El_Dorado_Solar |  |  | 0 | 248 |  | ok | 1 |  |  | 1 | 1 | 2 |  |  |  | [Prior year]: none selected previously. | 1
North_Victor_Solar |  |  | 0 | 300 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  |  | [Prior year]: none selected previously. | 1
Northern_California_Ex_Solar |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Northern_California_Ex_Wind |  |  | 0 | 865.9 |  | ok | 2 |  |  | 1 | 1 | 2 | 5 | Yes |  | [Tx capability]: there is uncertainty in the strength of the tx capability estimates for "_Ex" zones.[Prior year]: none selected previously. | 1
NW_Ext_Tx_Wind |  |  | 0 | 1500 |  | ok | 1 |  |  | 3 |  | 3 |  |  |  | [Commercial interest]: not found in queue [Prior year]: none selected previously | 1
Riverside_Palm_Springs_Solar |  |  | 1622 | 0 |  | ok | 1 |  |  | 2 | 2 | 3 | 6 |  | Yes | [Commercial interest]: model selecting less than queue (queue = 2182 MW) [Prior year]: 1622 MW selected previously. Candidate to receive reallocation from Tehachapi | 1
Riverside_Palm_Springs_Wind |  |  | 42 | NA |  | ok | 1 |  |  | 1 | 1 |  | 2 |  |  | Resource not considered in RESOLVE in 2019 model version | 1
Sacramento_River_Solar |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Sacramento_River_Wind |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
SCADSNV_Solar |  |  | 0 | 1970 |  | ok | 1 |  |  | 1 | 1 | 3 | 5 |  |  | [Prior year]: none selected previously | 1
SCADSNV_Wind |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Solano_Solar |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Solano_subzone_Solar |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Solano_subzone_Wind |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Solano_Wind |  |  | 644 | 542 |  | ok | 1 |  |  | 1 | 1 | 1 | 3 |  |  |  | 1
Southern_California_Desert_Ex_Solar |  |  | 0 | 862 |  | ok | 2 |  |  | 3 | 3 | 2 |  |  | Yes | [Tx capability]: there is uncertainty in the strength of the tx capability estimates for "_Ex" zones. [Commercial interest]: model selecting more than queue (queue = 0 MW) [Prior year]: none selected previously. Candidate for re-allocation (see proposed adjustments tab) | 1
Southern_California_Desert_Ex_Wind |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Southern_Nevada_Solar |  |  | 3006 | 1470 |  | ok | 1 |  |  | 3 | 3 | 3 | 7 |  | Yes | [Commercial interest]: not found in queue, but this may be due to data structure, not lack of interest. Difference from prior yr ok - alleviated at the substation level. | 1
Southern_Nevada_Wind |  |  | 0 | 442.03 |  | ok | 1 |  |  | 3 | 3 | 2 |  |  |  | [Commercial interest]: not found in queue, but this may be due to data structure, not lack of interest | 1
SW_Ext_Tx_Wind |  |  | 0 | 500 |  | ok | 1 |  |  | 3 |  | 2 |  |  |  | [Commercial interest]: not found in queue | 1
Tehachapi_Solar |  |  | 1153 | 4801 |  | ok | 1 |  |  | 1 | 1 | 3 | 5 |  | Yes | [Prior year]: increased from 1153 MW. Candidate for reallocation to reallocate to Riverside. See prposed adjustments tab. | 1
Tehachapi_Ex_Solar |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 | 3 | Yes |  |  | 0
Tehachapi_Wind |  |  | 0 | 275 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  |  |  | 1
Westlands_Ex_Solar |  |  | 0 | 1778.57 |  | ok | 2 |  |  | 1 | 1 | 3 |  |  | Yes | [Tx capability]: there is uncertainty in the strength of the tx capability estimates for "_Ex" zones. [Prior year]: Increased from 0 MW. Candidate for reallocation to reduce pressure on Ex zones | 1
Westlands_Ex_Wind |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Westlands_Solar |  |  | 0 | 633.68 |  | breach | 1 |  |  | 1 | 1 | 2 |  |  | Yes | [Commercial interest]: model selecting less than queue (queue = 5246 MW) [Prior year]: none selected previously. Candidate to receive reallocation to alleviate issues at substation level (no selections applicable to substations with high commercial interest) | 1
Cape_Mendocino_Offshore_Wind |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Del_Norte_Offshore_Wind |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Diablo_Canyon_Offshore_Wind_Ext_Tx |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Diablo_Canyon_Offshore_Wind |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Humboldt_Bay_Offshore_Wind |  |  | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
Morro_Bay_Offshore_Wind |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Utah_Solar |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Arizona_Solar |  |  | 428 | 2140.97 |  | ok | 1 |  |  | 1 | 1 | 3 | 5 |  |  | [Prior year]: Increased from 856 MW | 1
New_Mexico_Solar |  |  | 0 | 0 |  | N/A | N/A |  |  |  |  | 1 |  |  |  |  | 0
Baja_California_Solar |  |  | 0 | 0 |  | N/A | N/A |  |  |  |  | 1 |  |  |  |  | 0
Baja_California_Wind |  |  | 0 | 600 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  |  |  | 1
Pacific_Northwest_Wind |  |  | 0 | 0 |  | N/A | N/A |  |  |  |  | 1 |  |  |  |  | 0
Idaho_Wind |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Utah_Wind |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Wyoming_Wind |  |  | 0 | 1500 |  | ok | 1 |  |  | 3 |  | 3 |  |  |  | [Commercial interest]: not found in queue [Prior year]: none selected previously | 1
Arizona_Wind |  |  | 0 | 0 |  | N/A | N/A |  |  |  |  | 1 |  |  |  |  | 0
New_Mexico_Wind |  |  | 0 | 1500 |  | ok | 1 |  |  | 3 |  | 3 |  |  |  | [Commercial interest]: not found in queue [Prior year]: none selected previously | 1
Sub Total - Renewables |  |  | 9011 | 27899.86 | [12 empty] | 1
Pumped Storage Hydro |  |  | 0 | 2798
Total |  |  | 9011 | 30697.86 | [12 empty] | 1

## Dashboard 30MMTEO2(Round 0 adj)
IRP Busbar Mapping Dashboard
Purpose: Quickly communicate compliance of portfolio mapping with the criteria per the Methodology. Highlight MW amounts by zone that breach criteria, if any, and identify next steps as part of the iterative process.
30 MMT EO
Pre Round 1 - Adjusted with inter-resource Reallocations |  |  | Selected | Selected | Adjusted | Compliance with Criteria
| Resource Selection |  | Resources | Resources | Resources | [1=Yes, 2=Possible/Moderate, 3=Materially in Breach] | [9 empty] | Actions
Resource | 2030 FCDS MW | 2030 EO MW | Total MW (2018 PSP) | Total MW (2019 EO P'folio) | Total MW (2019 EO P'folio adj) | 1. Distance to Trans. |  | 2. Trans. Capability | 3a. Available Land Area | 3b. High Env. Impl. | [lookup formula] | 4. Comm. Interest | 5. Consistency with Prior Year's Mapping | Sum of criteria | Low-Effort Adjustment Available? | Further Round of Mapping Needed? | Comment; Potential Solutions for Consideration | Include in display?
InState_Biomass |  |  | 0 | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Greater_Imperial_Geothermal |  |  | 1256 | 716.46 | 716.46 |  | ok | 1 |  |  | 1 | 1 | 1 | 3 |  |  |  | 1
Inyokern_North_Kramer_Geothermal |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Northern_California_Geothermal |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 |  | 2 |  |  |  | 0
Pacific_Northwest_Geothermal |  |  | 0 | 0 | 0 |  | #N/A | [5 empty] | 1 |  |  |  |  | 0
Riverside_Palm_Springs_Geothermal |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Solano_Geothermal |  |  | 0 | 135 | 135 |  | ok | 1 |  |  | 1 | 1 | 2 |  |  |  |  | 1
Southern_Nevada_Geothermal |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Carrizo_Solar |  |  | 0 | 600 | 600 |  | ok | 1 |  |  | 3 | 3 | 2 |  |  |  | [Commercial interest]: increase from prior yr ok. All zones increased with this portfolio. | 1
Carrizo_Wind |  |  | 160 | 287 | 287 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  |  |  | 1
Central_Valley_North_Los_Banos_Solar |  |  | 0 | 0 | 0 |  | breach | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 1
Central_Valley_North_Los_Banos_Wind |  |  | 146 | 173 | 173 |  | breach | 1 |  |  | 1 | 1 | 1 | 3 | Yes |  |  | 1
Distributed_Solar |  |  | 0 | 0 | 0 |  | N/A | [5 empty] | 1 |  |  |  |  | 0
Distributed_Wind |  |  | 0 | 0 | 0 |  | N/A | [5 empty] | 1 |  |  |  |  | 0
Greater_Imperial_Solar |  |  | 0 | 866.98 | 1146.98 |  | ok | 1 |  |  | 1 | 1 | 3 | 5 |  |  | Received reallocation from Southern California Desert Ex. This increased the difference from prior year, but there were few remaining zones in southern california with transmission capability to accept the reallocation. | 1
Greater_Imperial_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Greater_Kramer_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Humboldt_Wind |  |  | 0 | 34 | 34 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  |  |  | 1
Inyokern_North_Kramer_Solar |  |  | 554 | 97 | 97 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  |  |  | 1
Kern_Greater_Carrizo_Solar |  |  | 0 | 3001.27 | 3632.27 |  | ok | 3 |  |  | 1 | 1 | 3 |  |  | Yes after Round 1 | Received reallocation from Westlands Ex. This increased the difference from prior year, but there were few remaining zones in southern california with transmission capability to accept the reallocation. | 1
Kern_Greater_Carrizo_Wind |  |  | 0 | 60 | 60 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  |  |  | 1
Kramer_Inyokern_Ex_Solar |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 | 3 | Yes |  |  | 0
Kramer_Inyokern_Ex_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Mountain_Pass_El_Dorado_Solar |  |  | 0 | 248 | 248 |  | ok | 3 |  |  | 1 | 1 | 2 |  |  | Yes after Round 1 | Converted from FD to EO | 1
North_Victor_Solar |  |  | 0 | 300 | 300 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  |  |  | 1
Northern_California_Ex_Solar |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Northern_California_Ex_Wind |  |  | 0 | 865.9 | 865.9 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 | Yes |  |  | 1
NW_Ext_Tx_Wind |  |  | 0 | 1500 | 1500 |  | ok | 1 |  |  | 3 |  | 3 |  |  |  | None selected previously. Consistent with objective of this portfolio. | 1
Riverside_Palm_Springs_Solar |  |  | 1622 | 0 | 1780 |  | ok | 3 |  |  | 1 | 1 | 1 | 5 |  | Yes after Round 1 | Moved 1000 MW from Tehachapi solar to Riverside Palm Springs Solar. This improved criteria 4 (commercial interest) and 5 (delta from prior yr). See tab "proposedAdjustments", adjustment 1. However, after adjustment 1, the sum of the subzones exceeded the SCADSNV outermost zone limit. | 1
Riverside_Palm_Springs_Wind |  |  | 42 | NA | NA |  | ok | 1 |  |  | 1 | 1 |  | 2 |  |  | Resource not considered in RESOLVE in 2019 model version | 1
Sacramento_River_Solar |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Sacramento_River_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
SCADSNV_Solar |  |  | 0 | 1970 | 1970 |  | ok | 1 |  |  | 1 | 1 | 3 | 5 |  |  | None selected previously. Consistent with objective of this portfolio. | 1
SCADSNV_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Solano_Solar |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Solano_subzone_Solar |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Solano_subzone_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Solano_Wind |  |  | 644 | 542 | 542 |  | ok | 1 |  |  | 1 | 1 | 1 | 3 |  |  |  | 1
Southern_California_Desert_Ex_Solar |  |  | 0 | 862 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  | Moved 862 MW from Southern California Desert Ex Solar to SNV solar. This improved criteria 2 (tx capability), 4 (comm int) and 5 (delta from prior yr). See tab "proposedAdjustments" | 1
Southern_California_Desert_Ex_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Southern_Nevada_Solar |  |  | 3006 | 1470 | 1727 |  | ok | 3 |  |  | 3 | 3 | 3 | 9 |  | Yes after Round 1 |  | 1
Southern_Nevada_Wind |  |  | 0 | 442.03 | 442.03 |  | ok | 1 |  |  | 3 | 3 | 2 |  |  |  |  | 1
SW_Ext_Tx_Wind |  |  | 0 | 500 | 500 |  | ok | 1 |  |  | 3 | 3 | 2 |  |  |  |  | 1
Tehachapi_Solar |  |  | 1153 | 4801 | 3801 |  | ok | 1 |  |  | 1 | 1 | 3 | 5 |  |  | Moved 1000 MW from Tehachapi solar to Riverside Palm Springs Solar. This did not change any criteria. See tab "proposedAdjustments", adjustment 1 | 1
Tehachapi_Ex_Solar |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 | 3 | Yes |  |  | 0
Tehachapi_Wind |  |  | 0 | 275 | 275 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  |  |  | 1
Westlands_Ex_Solar |  |  | 0 | 1778.57 | -0.43 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  | Moved 1779 from Westlands_Ex solar to Westlands solar (same rationale as above). [Update]: a limited amount can be added to Westlands before breaching FCDS tx limit. Excess moved to Kern Greater Carrizo, FCDS. This improvied criteria 2 (tx capability) and 5 (delta from prior yr). See tab "proposedAdjustments" | 1
Westlands_Ex_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Westlands_Solar |  |  | 0 | 633.68 | 1326.68 |  | breach | 3 |  |  | 1 | 1 | 3 |  |  | Yes after Round 1 | Received reallocation from Westlands_Ex. Difference from prior year increased, but amount is still much lower than commercial interest (queue = 5246 MW) | 1
Cape_Mendocino_Offshore_Wind |  |  | 0 | 0 | 0 |  | N/A | [5 empty] | 1 |  |  |  |  | 0
Del_Norte_Offshore_Wind |  |  | 0 | 0 | 0 |  | N/A | [5 empty] | 1 |  |  |  |  | 0
Diablo_Canyon_Offshore_Wind_Ext_Tx |  |  | 0 | 0 | 0 |  | N/A | [5 empty] | 1 |  |  |  |  | 0
Diablo_Canyon_Offshore_Wind |  |  | 0 | 0 | 0 |  | N/A | [5 empty] | 1 |  |  |  |  | 0
Humboldt_Bay_Offshore_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
Morro_Bay_Offshore_Wind |  |  | 0 | 0 | 0 |  | breach | [5 empty] | 1 |  |  |  |  | 0
Utah_Solar |  |  | 0 | 0 | 0 |  | breach | [5 empty] | 1 |  |  |  |  | 0
Arizona_Solar |  |  | 428 | 2140.97 | 2140.97 |  | ok | 1 |  |  | 1 | 1 | 3 | 5 |  |  |  | 1
New_Mexico_Solar |  |  | 0 | 0 | 0 |  | N/A | [5 empty] | 1 |  |  |  |  | 0
Baja_California_Solar |  |  | 0 | 0 | 0 |  | N/A | [5 empty] | 1 |  |  |  |  | 0
Baja_California_Wind |  |  | 0 | 600 | 600 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  |  |  | 1
Pacific_Northwest_Wind |  |  | 0 | 0 | 0 |  | N/A | [5 empty] | 1 |  |  |  |  | 0
Idaho_Wind |  |  | 0 | 0 | 0 |  | N/A | [5 empty] | 1 |  |  |  |  | 0
Utah_Wind |  |  | 0 | 0 | 0 |  | N/A | [5 empty] | 1 |  |  |  |  | 0
Wyoming_Wind |  |  | 0 | 1500 | 1500 |  | ok | 1 |  |  | 3 |  | 3 |  |  |  |  | 1
Arizona_Wind |  |  | 0 | 0 | 0 |  | N/A | [5 empty] | 1 |  |  |  |  | 0
New_Mexico_Wind |  |  | 0 | 1500 | 1500 |  | ok | 1 |  |  | 3 |  | 3 |  |  |  |  | 1
Sub Total - Renewables |  |  | 9011 | 27899.86 | 27899.86 | [12 empty] | 1
Total - Renewables & Storage | [17 empty] | 1

## Dashboard 30MMTEO2(Round 1)
IRP Busbar Mapping Dashboard
Purpose: Quickly communicate compliance of portfolio mapping with the criteria per the Methodology. Highlight MW amounts by zone that breach criteria, if any, and identify next steps as part of the iterative process.
30 MMT EO
Post Round 1 | Selected | Selected | Adjusted | Compliance with Criteria
| Resources | Resources | Resources | [1=Yes, 2=Possible/Moderate, 3=Materially in Breach] | [7 empty] | Actions
Resource | Total MW (2018 PSP) | Total MW (2019 EO P'folio) | Total MW (2019 EO P'folio adj) | 1. Distance to Trans. |  | 2. Trans. Capability | 3a. Available Land Area | 3b. High Env. Impl. | [lookup formula] | 4. Comm. Interest | 5. Consistency with Prior Year's Mapping | Further Round of Mapping Needed? | Comment; Potential Solutions for Consideration | Include in display?
Greater_Imperial_Geothermal | 1256 | 716.46 | 716.46 | 1 | ok | 1 |  |  | 1 | 1 | 1 |  |  | 1
Solano_Geothermal | 0 | 135 | 135 | 1 | ok | 1 |  |  | 1 | 1 | 2 |  |  | 1
Carrizo_Solar | 0 | 600 | 600 | 1 | ok | 1 | 1 | 1 | 3 | 3 | 2 | No | [Tx capability]: Southern PG&E resource selections exceed tx capability (EO) at the child zone level, but sum of selections are ok at the parent zone level. No change recommended. [Commercial interest]: model selecting more than queue (queue = 0 MW) [Prior year]: none selected previously. | 1
Carrizo_Wind | 160 | 287 | 287 | 1 | ok | 1 | 2 | 2 | 1 | 1 | 2 | No | [Tx capability]: same comment as for Carrizo_Solar. [Available land area]: Some sites exceed available land, some sites exceed available low-value land | 1
Central_Valley_North_Los_Banos_Wind | 146 | 173 | 173 | 2 | breach | 3 | 2 | 2 | 1 | 1 | 1 | Yes after Round 1 | [Distance to Transmission]: Adjustment 8: Assign this Wind Resource and MW to Westlands Tx Zone because Westlands has closer substation. [Tx capability]: Southern PG&E resource selections exceed tx capability (EO) at the child zone level, but sum of selections are ok at the parent zone level. The flag is raised partially due to westlands solar being assigned to central valley north los banos transmission zone, despite being allocated to westlands proper at the substation level in busbar mapping. [Available land area]: Some sites exceed available land, some sites exceed available low-value land | 1
Greater_Imperial_Solar | 0 | 866.98 | 1146.98 | 1 | ok | 1 | 1 | 1 | 1 | 1 | 3 | No | [Available land area]: some sites exceed available low-impact land. [Commercial interest]: Model selecting less than queue (model = 867; queue = 3050 MW) | 1
Humboldt_Wind | 0 | 34 | 34 | 1 | ok | 1 | 2 | 2 | 1 | 1 | 2 |  | [Available land area]: Some sites exceed available land, some sites exceed available low-value land | 1
Inyokern_North_Kramer_Solar | 554 | 97 | 97 | 1 | ok | 1 | 1 | 1 | 1 | 1 | 2 |  |  | 1
Kern_Greater_Carrizo_Solar | 0 | 3001.27 | 3001.27 | 1 | ok | 1 | 1 | 1 | 1 | 1 | 3 | Yes after Round 1 | [Tx capability]: After adjustment 3, the sum of the subzones exceeded the Southern PG&E parent zone limit by 900 MW. Move this 900 MW to Gates-Diablo 500 kV system, per ISO guidance. See adjustment 5. | 1
Kern_Greater_Carrizo_Wind | 0 | 60 | 60 | 2 | ok | 1 | 2 | 2 | 1 | 1 | 2 | Yes after Round 1 | [Distance to Transmission]: Adjustment 9: Assign to Cholame Sub to reduce gentie distance. May require local upgrade to connect project(s) [Tx capability]: Southern PG&E resource selections exceed tx capability (EO) at the child zone level, but sum of selections are ok at the parent zone level. [Available land area]: some sites exceed available land, some sites exceed available low-value land | 1
Mountain_Pass_El_Dorado_Solar | 0 | 248 | 248 | 1 | ok | 1 | 1 | 1 | 1 | 1 | 2 |  | [Available land area]: some sites exceed available land | 1
North_Victor_Solar | 0 | 300 | 300 | 1 | ok | 1 | 1 | 1 | 1 | 1 | 2 |  |  | 1
Northern_California_Ex_Wind | 0 | 865.9 | 865.9 | 1 | ok | 1 | 2 | 1 | 1 | 1 | 2 |  | [Tx capability]: note this resource has been re-assigned to the Northern California core zone, within RESOLVE, to improve confidence in transmission capability | 1
NW_Ext_Tx_Wind | 0 | 1500 | 1500 |  | ok | 1 |  |  | 3 |  | 3 |  |  | 1
Riverside_Palm_Springs_Solar | 1622 | 0 | 29 | 1 | ok | 1 | 1 | 1 | 1 | 1 | 1 | Yes after Round 1 | [Tx capability]: See adjustment 6. Adjustment 1 above caused the sum of the child zones to exceed the SCADSNV parent zone limit. Reverse adjustment 1. Move that 1000 MW back from Riverside to Tehachapi. See Adjustment 7: Remaining amount exceeding parent zone transmission limit in Southern California Desert area (751 MW) can be accommodated if allocated to Mohave/Eldorado 500 kV substations. These are electrically outside the SCADSNV parent zone transmission constraint. | 1
Riverside_Palm_Springs_Wind | 42 | NA | NA | [9 empty] | Resource not considered in RESOLVE in 2019 model version
SCADSNV_Solar | 0 | 1970 | 2721 | 1 | ok | 1 | 2 | 1 | 1 | 1 | 3 | Yes after Round 1 | [Available land area]: some sites exceed available land | 1
Solano_Wind | 644 | 542 | 542 | 1 | ok | 1 | 2 | 2 | 1 | 1 | 1 |  | [Available land area]: some sites exceed available land, some sites exceed available low-value land | 1
Southern_California_Desert_Ex_Solar | 0 | 862 | 0 | 1 | ok | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1
Southern_Nevada_Solar | 3006 | 1470 | 1727 | 1 | ok | 1 | 1 | 1 | 3 | 3 | 3 | Yes after Round 1 | [Tx capability]: See adjustment 7 in "proposed adjustments" tab. Per tri-agency working group call 3/24, amount exceeding parent zone transmission limit in Southern California Desert area can be accommodated if allocated to Mohave/Eldorado 500 kV substations. These are electrically outside the SCADSNV parent zone transmission constraint. Move 751 MW from Riverside Palm Springs Solar to Mohave/Eldorado 500 kV substations (SCADSNV solar). | 1
Southern_Nevada_Wind | 0 | 442.03 | 442.03 | 1 | ok | 1 |  |  | 3 | 3 | 2 |  |  | 1
SW_Ext_Tx_Wind | 0 | 500 | 500 |  | ok | 1 |  |  | 3 | 3 | 2 |  |  | 1
Tehachapi_Solar | 1153 | 4801 | 4801 | 1 | ok | 1 | 1 | 1 | 1 | 1 | 3 | Yes after Round 1 | [Tx capability]: See adjustment 6. Adjustment 1 above caused the sum of the child zones to exceed the SCADSNV parent zone limit. Adjustment 1 was reversed and. that 1000 MW went back from Riverside to Tehachapi. | 1
Tehachapi_Wind | 0 | 275 | 275 | 1 | ok | 1 | 2 | 1 | 1 | 1 | 2 |  |  | 1
Westlands_Ex_Solar | 0 | 1778.57 | -0.43 | 1 | ok | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1
Westlands_Solar | 0 | 633.68 | 1957.68 | 1 | breach | 3 | 1 | 1 | 1 | 1 | 3 | Yes after Round 1 | [Tx capability]: See adjustment 5 in "proposed adjustments" tab. Note what looks like an exceedance of transmission capability here is in fact alleviated by adjustments to Westlands solar at the substation level. After adjustment 3, the sum of the child zones exceeded the Southern PG&E parent zone limit by 1353 MW. The excess is moved to Gates-Diablo 500 kV system, per ISO guidance. Gates-Diablo 500 kV system appears geographically in the Southern PG&E zone, but electrically it is outside the transmission constraint. | 1
Arizona_Solar | 428 | 2140.97 | 2140.97 |  | ok | 1 |  |  | 1 | 1 | 3 |  | [Prior yr]: Delta from prior year is ok. Increased more than 1000 MW from prior yr, but this brings the total up closer to commercial interest (queue = 2595 MW) | 1
Baja_California_Wind | 0 | 600 | 600 |  | ok | 1 |  |  | 1 | 1 | 2 |  |  | 1
Wyoming_Wind | 0 | 1500 | 1500 |  | ok | 1 |  |  | 3 |  | 3 |  | [Prior yr]: Delta from prior year is ok. Increased more than 1000 MW from prior yr, but this brings the total up closer to commercial interest | 1
New_Mexico_Wind | 0 | 1500 | 1500 |  | ok | 1 |  |  | 3 |  | 3 |  | [Distance to tx]: confirmed delivery point to California with commercial interest. [Comm int]: not found in queue | 1
Sub Total - Renewables | 9439 | 27899.86 | 27899.86 | [10 empty] | 1
Total - Renewables & Storage | [13 empty] | 1

## Dashboard 30MMTEO2(Round 2)
IRP Busbar Mapping Dashboard
Purpose: Quickly communicate compliance of portfolio mapping with the criteria per the Methodology. Highlight MW amounts by zone that breach criteria, if any, and identify next steps as part of the iterative process.
30 MMT EO
Post Round 2 |  | Selected | Selected | Adjusted | Compliance with Criteria
|  | Resources | Resources | Resources | [1=Yes, 2=Possible/Moderate, 3=Materially in Breach] | [7 empty] | Actions
Resource | Tx Zone | Total MW (2018 PSP) | Total MW (2019 EO P'folio) | Total MW (2019 EO P'folio adj) | 1. Distance to Trans. |  | 2. Trans. Capability | 3a. Available Land Area | 3b. High Env. Impl. | [lookup formula] | 4. Comm. Interest | 5. Consistency with Prior Year's Mapping | Further Round of Mapping Needed? | Comment; Potential Solutions for Consideration | Include in display?
Greater_Imperial_Geothermal | SCADSNV-Greater_Imperial | 1256 | 716.46 | 716.46 | 1 | ok | 1 | 1 | 1 | 1 | 1 | 1 | No |  | 1
Solano_Geothermal | Sacramento_River-Solano | 0 | 135 | 135 | 1 | ok | 1 | 1 | 1 | 1 | 1 | 2 | No |  | 1
Carrizo_Solar | Carrizo-Kern_Greater_Carrizo-SPGE | 0 | 600 | 600 | 1 | ok | 1 | 1 | 1 | 3 | 3 | 2 | No | [Comm int]: not found in queue | 1
Carrizo_Wind | Carrizo-Kern_Greater_Carrizo-SPGE | 160 | 287 | 287 | 1 | ok | 1 | 2 | 2 | 1 | 1 | 2 | No |  | 1
Central_Valley_North_Los_Banos_Wind | Central_Valley_North_Los_Banos-SPGE | 146 | 173 | 173 | 1 | breach | 3 | 2 | 2 | 1 | 1 | 1 | No | [Distance to tx]: improved with adjustment: assigned to Westlands zone (closer sub). [Tx capability]: Southern PG&E resource selections exceed tx capability (EO) at the subzone level, but sum of selections are ok at the outermost zone level. [Available land area]: some sites exceed available land | 1
Greater_Imperial_Solar | SCADSNV-Greater_Imperial | 0 | 866.98 | 355.98 | 1 | ok | 1 | 1 | 1 | 1 | 2 | 2 | No | Receive reallocation from Riverside, to make space in Riverside for pumped hydro | 1
Humboldt_Wind | Humboldt-Sacramento_River | 0 | 34 | 34 | 1 | ok | 1 | 2 | 2 | 1 | 1 | 2 | No | [High environmental imp]: no low-value land | 1
Inyokern_North_Kramer_Solar | Inyokern_North_Kramer-Greater_Kramer | 554 | 97 | 97 | 1 | ok | 1 | 1 | 1 | 1 | 1 | 2 | No |  | 1
Kern_Greater_Carrizo_Solar | Kern_Greater_Carrizo-SPGE | 0 | 3001.27 | 3001.27 | 1 | ok | 1 | 1 | 1 | 1 | 1 | 3 | No | [Tx capability]: Criteria 2 improved after adjustment 5 | 1
Kern_Greater_Carrizo_Wind | Kern_Greater_Carrizo-SPGE | 0 | 60 | 60 | 1 | ok | 1 | 2 | 2 | 1 | 1 | 2 | No | [Distance to tx]: improved with adjustment: assigned to closer substation | 1
Mountain_Pass_El_Dorado_Solar | N/A | 0 | 248 | 248 | 1 | ok | 1 | 2 | 1 | 1 | 1 | 2 | No |  | 1
North_Victor_Solar | North_Victor-Greater_Kramer | 0 | 300 | 300 | 1 | ok | 1 | 1 | 1 | 1 | 1 | 2 | No |  | 1
Northern_California_Ex_Wind | Sacramento_River | 0 | 865.9 | 865.9 | 1 | ok | 1 | 2 | 1 | 1 | 1 | 2 | No |  | 1
NW_Ext_Tx_Wind | Sacramento_River | 0 | 1500 | 1500 |  | ok | 1 |  |  | 3 | 3 | 3 | No | [Available land]: non-geographically specific resource - no land use information available. [Comm int]: not found in queue but this may be due to data structure, not lack of interest. [Prior yr]: none selected prior yr | 1
Riverside_Palm_Springs_Solar | SCADSNV-Riverside_Palm_Springs | 1622 | 0 | 29 | 1 | ok | 1 | 1 | 1 | 1 | 2 | 3 | No | [Prior yr]: SCADSNV outermost zone tx limit is causing the low FD resource selection in this zone. Adjustment 1 attempted to improve compliance with criteria 4 and 5, but was prevented by criteria 2 and was reversed. | 1
Riverside_Palm_Springs_Wind |  | 42 | #N/A | #N/A | [8 empty] | No | [Prior yr]: Resource not considered in RESOLVE in 2019 model version
SCADSNV_Solar | SCADSNV | 0 | 1970 | 4303 | 1 | ok | 1 | 2 | 1 | 1 | 2 | 3 | No | [Avail land]: some sites exceed available land. [Prior yr]: What looks like an increase from prior year is addressed at the substation level. El Dorado Mohave substations counted as part of multiple resources. Note allocation is large due to overflow from other zones, increased by adjustment 11, receive excess from Riverside to make space in Rverside for pumped hydro storage. Excess in Southern California Desert area is allocated to Mohave/Eldorado 500 kV substations. Per ISO guidance, these are electrically outside the SCADSNV parent zone transmission constraint. | 1
Solano_Wind | Sacramento_River-Solano | 644 | 542 | 542 | 1 | ok | 1 | 2 | 2 | 1 | 1 | 1 | No |  | 1
Southern_California_Desert_Ex_Solar | Southern_California_Desert_Ex | 0 | 862 | 0 | 1 | ok | 1 | 1 | 1 | 1 | 1 | 1 | No | [Tx capability]: improved with adjustment 2. | 1
Southern_Nevada_Solar | SCADSNV-GLW_VEA | 3006 | 1470 | 1727 | 1 | ok | 1 | 1 | 1 | 3 | 3 | 3 | No | [Tx capability]: affected by adjustments 7 and 11. [Commmercial interest]: not found in ISO queue, but this may be due to data structure, not lack of interest. [Prior yr]: Delta from prior year is ok. The amount at the individual substations is consistent with prior yr. Two substations (El Dorado and Mohave) receive allocations from three RESOLVE resources: SCADSNV_Solar, Mountain_Pass_El_Dorado_Solar, Southern_Nevada_Solar. | 1
Southern_Nevada_Wind | SCADSNV-GLW_VEA | 0 | 442.03 | 442.03 | 1 | ok | 1 |  |  | 3 | 3 | 2 | No | [Available land]: no land use information available. [Comm int]: not found in queue but this may be due to data structure, not lack of interest. | 1
SW_Ext_Tx_Wind | SCADSNV-Riverside_Palm_Springs | 0 | 500 | 500 |  | ok | 1 |  |  | 3 | 3 | 2 | No | [Available land]: non-geographically specific resource - no land use infomration available. [Comm int]: not found in queue but this may be due to data structure, not lack of interest. [Prior yr]: none selected prior yr | 1
Tehachapi_Solar | Tehachapi | 1153 | 4801 | 4801 | 1 | ok | 1 | 1 | 1 | 1 | 1 | 3 | No | [Prior yr]: significant increase from prior yr ok. Attempt to alleviate by moving MW to Riverside was preveted due to SCADSNV outer tx zone capability | 1
Tehachapi_Wind | Tehachapi | 0 | 275 | 275 | 1 | ok | 1 | 2 | 1 | 1 | 1 | 2 | No |  | 1
Westlands_Ex_Solar | Westlands_Ex | 0 | 1778.57 | -0.43 | 1 | ok | 1 | 1 | 1 | 1 | 1 | 1 | No |  | 1
Westlands_Solar | Central_Valley_North_Los_Banos-SPGE | 0 | 633.68 | 1957.68 | 1 | breach | 3 | 1 | 1 | 1 | 1 | 3 | No | [Tx limits]: What looks like an exceedance of transmission capability is in fact alleviated by adjustments to Westlands solar at the substation level. Some excess is allocated to Westlands proper substations (Gates, Helm, Henrietta, Mc Call, Mc Mullin, Panoche). Excess is allocated to Gates-Diablo 500 kV system. Gates-Diablo 500 kV system appears geographically in the Southern PG&E zone, but electrically it is outside the transmission constraint. | 1
Arizona_Solar | SCADSNV-Riverside_Palm_Springs | 428 | 2140.97 | 1349.97 |  | ok | 1 |  |  | 1 | 1 | 2 | No | [Prior yr]: Delta from prior year is ok. Increased more than 1000 MW from prior yr, but this brings the total up closer to commercial interest (queue = 2595 MW). Adjustment 11 moved some of this resource to SCADSNV to make space for pumped hydro in Riverside zone. | 1
Baja_California_Wind | SCADSNV-Greater_Imperial | 0 | 600 | 600 |  | ok | 1 |  |  | 1 | 1 | 2 | No |  | 1
Wyoming_Wind | Mountain_Pass_El_Dorado-SCADSNV | 0 | 1500 | 1500 |  | ok | 1 |  |  | 3 |  | 3 | No | [Prior yr]: Delta from prior year is ok. Study objectives include investigating this change. | 1
New_Mexico_Wind | SCADSNV-Riverside_Palm_Springs | 0 | 1500 | 1500 |  | ok | 1 |  |  | 3 |  | 3 | No | [Distance to tx]: confirmed delivery point to California with commercial interest. [Comm int]: not found in queue. [Prior yr]: Delta from prior year is ok. Study objectives include investigating this change. | 1
Sub Total - Renewables |  | 9011 | 27899.86 | 27899.86 | [10 empty] | 1
Pumped Storage Hydro |  | 0 | 2798 | 2798 | [6 empty] | 1 | 3 | No | [Prior yr]: signfiicant increase | 1
Total |  | 9011 | 30697.86 | 30697.86 | [10 empty] | 1

## SelectedPortfolio_30MMTEO2
Extract from: | Portfolio_zone_compare-2020-02-18.xlsx | 30MMT_20200207_2045_2GWPRM_NOOTCEXT_ExpandedEO
Portfolio Analytics
| FCDS Renewable Resource Summary by Location (MW) |  |  |  |  | EO Renewable Resource Summary by Location (MW)
| RESOLVE Resource | Tx Zone | 2030 FD | Proposed Adjustment | Adjusted Value (FD) | RESOLVE Resource | Tx Zone | 2030 EO | Proposed Adjustment | Adjusted Value (EO) | FD + EO | Adjusted (FD + EO)
| InState_Biomass | None | 0 | 0 | 0 | InState_Biomass | None | 0 | 0 | 0 | 0 | 0
| Greater_Imperial_Geothermal | SCADSNV-Greater_Imperial | 716.46 | 0 | 716.46 | Greater_Imperial_Geothermal | SCADSNV-Greater_Imperial | 0 | 0 | 0 | 716.46 | 716.46
| Inyokern_North_Kramer_Geothermal | Inyokern_North_Kramer-Greater_Kramer | 0 | 0 | 0 | Inyokern_North_Kramer_Geothermal | Inyokern_North_Kramer-Greater_Kramer | 0 | 0 | 0 | 0 | 0
| Northern_California_Ex_Geothermal | Northern_California_Ex | 0 | 0 | 0 | Northern_California_Ex_Geothermal | Northern_California_Ex | 0 | 0 | 0 | 0 | 0
| Pacific_Northwest_Geothermal | N/A | 0 | 0 | 0 | Pacific_Northwest_Geothermal | N/A | 0 | 0 | 0 | 0 | 0
| Riverside_Palm_Springs_Geothermal | SCADSNV-Riverside_Palm_Springs | 0 | 0 | 0 | Riverside_Palm_Springs_Geothermal | SCADSNV-Riverside_Palm_Springs | 0 | 0 | 0 | 0 | 0
| Solano_Geothermal | Sacramento_River-Solano | 135 | 0 | 135 | Solano_Geothermal | Sacramento_River-Solano | 0 | 0 | 0 | 135 | 135
| Southern_Nevada_Geothermal | Mountain_Pass_El_Dorado-SCADSNV | 0 | 0 | 0 | Southern_Nevada_Geothermal | Mountain_Pass_El_Dorado-SCADSNV | 0 | 0 | 0 | 0 | 0
| Carrizo_Solar | Carrizo-Kern_Greater_Carrizo-SPGE | 0 | 0 | 0 | Carrizo_Solar | Carrizo-Kern_Greater_Carrizo-SPGE | 600 | 0 | 600 | 600 | 600
| Carrizo_Wind | Carrizo-Kern_Greater_Carrizo-SPGE | 187 | 0 | 187 | Carrizo_Wind | Carrizo-Kern_Greater_Carrizo-SPGE | 100 | 0 | 100 | 287 | 287
| Central_Valley_North_Los_Banos_Solar | Central_Valley_North_Los_Banos-SPGE | 0 | 0 | 0 | Central_Valley_North_Los_Banos_Solar | Central_Valley_North_Los_Banos-SPGE | 0 | 0 | 0 | 0 | 0
| Central_Valley_North_Los_Banos_Wind | Central_Valley_North_Los_Banos-SPGE | 173 | 0 | 173 | Central_Valley_North_Los_Banos_Wind | Central_Valley_North_Los_Banos-SPGE | 0 | 0 | 0 | 173 | 173
| Distributed_Solar | None | 0 | 0 | 0 | Distributed_Solar | None | 0 | 0 | 0 | 0 | 0
| Distributed_Wind | #N/A | 0 | 0 | 0 | Distributed_Wind | #N/A | 0 | 0 | 0 | 0 | 0
| Greater_Imperial_Solar | SCADSNV-Greater_Imperial | 0 | -511 | -511 | Greater_Imperial_Solar | SCADSNV-Greater_Imperial | 866.98 | 0 | 866.98 | 866.98 | 355.98
| Greater_Imperial_Wind | SCADSNV-Greater_Imperial | 0 | 0 | 0 | Greater_Imperial_Wind | SCADSNV-Greater_Imperial | 0 | 0 | 0 | 0 | 0
| Greater_Kramer_Wind | Greater_Kramer | 0 | 0 | 0 | Greater_Kramer_Wind | Greater_Kramer | 0 | 0 | 0 | 0 | 0
| Humboldt_Wind | Humboldt-Sacramento_River | 0 | 0 | 0 | Humboldt_Wind | Humboldt-Sacramento_River | 34 | 0 | 34 | 34 | 34
| Inyokern_North_Kramer_Solar | Inyokern_North_Kramer-Greater_Kramer | 97 | 0 | 97 | Inyokern_North_Kramer_Solar | Inyokern_North_Kramer-Greater_Kramer | 0 | 0 | 0 | 97 | 97
| Kern_Greater_Carrizo_Solar | Kern_Greater_Carrizo-SPGE | 121.27 | 0 | 121.27 | Kern_Greater_Carrizo_Solar | Kern_Greater_Carrizo-SPGE | 2880 | 0 | 2880 | 3001.27 | 3001.27
| Kern_Greater_Carrizo_Wind | Kern_Greater_Carrizo-SPGE | 60 | 0 | 60 | Kern_Greater_Carrizo_Wind | Kern_Greater_Carrizo-SPGE | 0 | 0 | 0 | 60 | 60
| Kramer_Inyokern_Ex_Solar | Kramer_Inyokern_Ex | 0 | 0 | 0 | Kramer_Inyokern_Ex_Solar | Kramer_Inyokern_Ex | 0 | 0 | 0 | 0 | 0
| Kramer_Inyokern_Ex_Wind | Kramer_Inyokern_Ex | 0 | 0 | 0 | Kramer_Inyokern_Ex_Wind | Kramer_Inyokern_Ex | 0 | 0 | 0 | 0 | 0
| Mountain_Pass_El_Dorado_Solar | N/A | 248 | 0 | 248 | Mountain_Pass_El_Dorado_Solar | N/A | 0 | 0 | 0 | 248 | 248
| North_Victor_Solar | North_Victor-Greater_Kramer | 300 | 0 | 300 | North_Victor_Solar | North_Victor-Greater_Kramer | 0 | 0 | 0 | 300 | 300
| Northern_California_Ex_Solar | Northern_California_Ex | 0 | 0 | 0 | Northern_California_Ex_Solar | Northern_California_Ex | 0 | 0 | 0 | 0 | 0
| Northern_California_Ex_Wind | Sacramento_River | 865.9 | 0 | 865.9 | Northern_California_Ex_Wind | Sacramento_River | 0 | 0 | 0 | 865.9 | 865.9
| NW_Ext_Tx_Wind | Sacramento_River | 530.12 | 0 | 530.12 | NW_Ext_Tx_Wind | Sacramento_River | 969.88 | 0 | 969.88 | 1500 | 1500
| Riverside_Palm_Springs_Solar | SCADSNV-Riverside_Palm_Springs | 0 | 29 | 29 | Riverside_Palm_Springs_Solar | SCADSNV-Riverside_Palm_Springs | 0 | 0 | 0 | 0 | 29
| Sacramento_River_Solar | Sacramento_River | 0 | 0 | 0 | Sacramento_River_Solar | Sacramento_River | 0 | 0 | 0 | 0 | 0
| Sacramento_River_Wind | N/A | 0 | 0 | 0 | Sacramento_River_Wind | N/A | 0 | 0 | 0 | 0 | 0
| SCADSNV_Solar | SCADSNV | 0 | 2333 | 2333 | SCADSNV_Solar | SCADSNV | 1970 | 0 | 1970 | 1970 | 4303
| SCADSNV_Wind | SCADSNV | 0 | 0 | 0 | SCADSNV_Wind | SCADSNV | 0 | 0 | 0 | 0 | 0
| Solano_Solar | Sacramento_River-Solano | 0 | 0 | 0 | Solano_Solar | Sacramento_River-Solano | 0 | 0 | 0 | 0 | 0
| Solano_subzone_Solar | Sacramento_River-Solano-Solano_subzone | 0 | 0 | 0 | Solano_subzone_Solar | Sacramento_River-Solano-Solano_subzone | 0 | 0 | 0 | 0 | 0
| Solano_subzone_Wind | Sacramento_River-Solano-Solano_subzone | 0 | 0 | 0 | Solano_subzone_Wind | Sacramento_River-Solano-Solano_subzone | 0 | 0 | 0 | 0 | 0
| Solano_Wind | Sacramento_River-Solano | 464 | 0 | 464 | Solano_Wind | Sacramento_River-Solano | 78 | 0 | 78 | 542 | 542
| Southern_California_Desert_Ex_Solar | Southern_California_Desert_Ex | 862 | -862 | 0 | Southern_California_Desert_Ex_Solar | Southern_California_Desert_Ex | 0 | 0 | 0 | 862 | 0
| Southern_California_Desert_Ex_Wind | Southern_California_Desert_Ex | 0 | 0 | 0 | Southern_California_Desert_Ex_Wind | Southern_California_Desert_Ex | 0 | 0 | 0 | 0 | 0
| Southern_Nevada_Solar | SCADSNV-GLW_VEA | 0 | 257 | 257 | Southern_Nevada_Solar | SCADSNV-GLW_VEA | 1470 | 0 | 1470 | 1470 | 1727
| Southern_Nevada_Wind | SCADSNV-GLW_VEA | 442.03 | 0 | 442.03 | Southern_Nevada_Wind | SCADSNV-GLW_VEA | 0 | 0 | 0 | 442.03 | 442.03
| SW_Ext_Tx_Wind | SCADSNV-Riverside_Palm_Springs | 500 | 0 | 500 | SW_Ext_Tx_Wind | SCADSNV-Riverside_Palm_Springs | 0 | 0 | 0 | 500 | 500
| Tehachapi_Solar | Tehachapi | 3402 | 0 | 3402 | Tehachapi_Solar | Tehachapi | 1399 | 0 | 1399 | 4801 | 4801
| Tehachapi_Ex_Solar | Tehachapi_Ex | 0 | 0 | 0 | Tehachapi_Ex_Solar | Tehachapi_Ex | 0 | 0 | 0 | 0 | 0
| Tehachapi_Wind | Tehachapi | 275 | 0 | 275 | Tehachapi_Wind | Tehachapi | 0 | 0 | 0 | 275 | 275
| Westlands_Ex_Solar | Westlands_Ex | 1778.57 | -1779 | -0.43 | Westlands_Ex_Solar | Westlands_Ex | 0 | 0 | 0 | 1778.57 | -0.43
| Westlands_Ex_Wind | N/A | 0 | 0 | 0 | Westlands_Ex_Wind | N/A | 0 | 0 | 0 | 0 | 0
| Westlands_Solar | Central_Valley_North_Los_Banos-SPGE | 133.68 | 1324 | 1457.68 | Westlands_Solar | Central_Valley_North_Los_Banos-SPGE | 500 | 0 | 500 | 633.68 | 1957.68
| Cape_Mendocino_Offshore_Wind | N/A | 0 | 0 | 0 | Cape_Mendocino_Offshore_Wind | N/A | 0 | 0 | 0 | 0 | 0
| Del_Norte_Offshore_Wind | N/A | 0 | 0 | 0 | Del_Norte_Offshore_Wind | N/A | 0 | 0 | 0 | 0 | 0
| Diablo_Canyon_Offshore_Wind_Ext_Tx | N/A | 0 | 0 | 0 | Diablo_Canyon_Offshore_Wind_Ext_Tx | N/A | 0 | 0 | 0 | 0 | 0
| Diablo_Canyon_Offshore_Wind | N/A | 0 | 0 | 0 | Diablo_Canyon_Offshore_Wind | N/A | 0 | 0 | 0 | 0 | 0
| Humboldt_Bay_Offshore_Wind | N/A | 0 | 0 | 0 | Humboldt_Bay_Offshore_Wind | N/A | 0 | 0 | 0 | 0 | 0
| Morro_Bay_Offshore_Wind | N/A | 0 | 0 | 0 | Morro_Bay_Offshore_Wind | N/A | 0 | 0 | 0 | 0 | 0
| Utah_Solar | N/A | 0 | 0 | 0 | Utah_Solar | N/A | 0 | 0 | 0 | 0 | 0
| Arizona_Solar | SCADSNV-Riverside_Palm_Springs | 572.97 | -791 | -218.03 | Arizona_Solar | SCADSNV-Riverside_Palm_Springs | 1568 | 0 | 1568 | 2140.97 | 1349.97
| New_Mexico_Solar | N/A | 0 | 0 | 0 | New_Mexico_Solar | N/A | 0 | 0 | 0 | 0 | 0
| Baja_California_Solar | N/A | 0 | 0 | 0 | Baja_California_Solar | N/A | 0 | 0 | 0 | 0 | 0
| Baja_California_Wind | SCADSNV-Greater_Imperial | 202.62 | 0 | 202.62 | Baja_California_Wind | SCADSNV-Greater_Imperial | 397.38 | 0 | 397.38 | 600 | 600
| Pacific_Northwest_Wind | N/A | 0 | 0 | 0 | Pacific_Northwest_Wind | N/A | 0 | 0 | 0 | 0 | 0
| Idaho_Wind | N/A | 0 | 0 | 0 | Idaho_Wind | N/A | 0 | 0 | 0 | 0 | 0
| Utah_Wind | N/A | 0 | 0 | 0 | Utah_Wind | N/A | 0 | 0 | 0 | 0 | 0
| Wyoming_Wind | Mountain_Pass_El_Dorado-SCADSNV | 0 | 0 | 0 | Wyoming_Wind | Mountain_Pass_El_Dorado-SCADSNV | 1500 | 0 | 1500 | 1500 | 1500
| Arizona_Wind | N/A | 0 | 0 | 0 | Arizona_Wind | N/A | 0 | 0 | 0 | 0 | 0
| New_Mexico_Wind | SCADSNV-Riverside_Palm_Springs | 0 | 0 | 0 | New_Mexico_Wind | SCADSNV-Riverside_Palm_Springs | 1500 | 0 | 1500 | 1500 | 1500
| Pumped Storage Hydro | GreaterImpOutsideTxConstraintZones | 0 | 608 | 608 | Pumped Storage Hydro |  | 0 | 0 |  | 0 | 608
| Pumped Storage Hydro | GreaterImpOutsideTxConstraintZones | 0 | 608 | 608 | Pumped Storage Hydro |  | 0 | 0 |  | 0 | 608
| Pumped Storage Hydro | SCADSNV_Z4_RiversideAndPalmSprings | 0 | 1582 | 1582 | Pumped Storage Hydro |  |  | 0 |  | 0 | 1582
| In-State |  | 12066.62 |  | 12066.62 | In-State |  | 12833.24 |  | 15833.24 | 24899.86 | 24899.86
| Out-Of-State |  | 0 |  |  | Out-Of-State |  | 3000 |  |  | 3000 | 3000

## proposedAdjustments
| Proposed Adjustments | FD | EO
1 | Tehachapi_Solar | -1000 |  | Move 1000 MW from Tehachapi solar to Riverside Palm Springs Solar (Tehachapi model selection increased a lot, and Riverside Palm Springs model selection decreased a lot, for reasons which are not well understood)
| Riverside_Palm_Springs_Solar | 1000 |  | Reverse this adjustment. Doesn't meet SCADSNV parent zone transmission limits.
2 | Southern_California_Desert_Ex_Solar | -862 |  | Move 862 MW from Southern California Desert Ex Solar to SNV solar (due to overlap in the tx capability estimates between “Ex” zone and core tx constraint zones – the estimates for the core zones have greater confidence and should probably supersede)
| Southern_Nevada_Solar | 257 |  | Amount that can fit without violating tx limits (note overflow to Greater_Imperial)
| Greater_Imperial_Solar | 280 |  | Amount that can fit without violating tx limits (note overflow to Riverside_Palm_Springs)
| Riverside_Palm_Springs_Solar | 325
3 | Westlands_Ex_Solar | -1779 |  | Move 1779 from Westlands_Ex solar to Westlands solar (same rationale as above)
| Westlands_Solar | 693 |  | Amount that can fit without violating tx limit (note overflow to Kern_Greater_Carrizo, to bring up closer to commercial interest)
| Kern_Greater_Carrizo_Solar | 631 |  | Amount that can fit without violating tx limit (note overflow to Riverside_Palm_Springs_Solar)
| Riverside_Palm_Springs_Solar | 455
4 | Mountain_Pass_El_Dorado_Solar | -248 | 248 | Convert Mountain_Pass_El_Dorado_Solar from FD to EO per E3 guidance
5 | Kern_Greater_Carrizo_Solar | -631 |  | After adjustment 3, the sum of the subzones exceeded the Southern PG&E parent zone limit by 900 MW. Move this 900 MW to Gates-Diablo 500 kV system, per ISO guidance.
| Westlands_Solar | -269 |  | This and the prior row add up to 900 MW
| Westlands_Solar | 900 |  | Allocate to Gates-Diablo 500 kV system. This area appears geographically in the Southern PG&E zone, but electrically outside the transmission constraint.
6 | Tehachapi_Solar | 1000 |  | Adjustment 1 above caused the sum of the child zones to exceed the SCADSNV parent zone limit. Reverse adjustment 1
| Riverside_Palm_Springs_Solar | -1000
7 | Riverside_Palm_Springs_Solar | -751 |  | Per tri-agency working group call 3/24, Remaining amount exceeding transmission limit in Southern California Desert area can be accommodated if allocated to Mohave/Eldorado 500 kV substations. These are electrically outside the SCADSNV parent zone transmission constraint.
| SCADSNV_Solar | 751 |  | Allocate to Mohave/Eldorado 500 kV substations.
8 | Central_Valley_North_Los_Banos_Wind | 0 |  | Adjust tx zone assignment: Assign this wind resource and MW to Westlands Tx Zone because Westlands has closer substation.
9 | Kern_Greater_Carrizo_Wind | 0 |  | Assign to Cholame Sub to reduce gentie distance. May require local upgrade to connect project(s)
10 | Mountain_Pass_El_Dorado_Solar | 248 | -248 | Per E3 guidance 3/23, we can remove the FCDS/EO conversion. We confirmed that the El Dorado/Mphave substations are not overloaded as we had feared they might be.
11 | Arizona_Solar | -791 |  | Adding pumped hydro results in exceeding SCADSNV parent zone limit. Move excess solar from SCADSNV child zones to mohave/el dorado substations
| Greater_Imperial_Solar | -791
| SCADSNV_Solar | 1582 |  | Allocate to Mohave/Eldorado 500 kV substations because they are outside of Southern California Desert area constraint

## 2_TxCapability
What constitutes level 3 criteria flag? |  |  |  | Selected portfolio exceeds tx capability (FD or EO)
What constitutes level 2 criteria flag? |  |  |  | None
What constitutes level 1 criteria flag? |  |  |  | All other
| Transmission Capability Estimated for IRP (CAISO Transmission Capability Whitepaper May 20, 2019) | [11 empty] | RESOLVE Selected Portfolio (30 MMT EO2) | [12 empty] | RESOLVE Selected Portfolio (new RSP) Aggregated and Compared to Tx Constraint Zone Limits
| Transmission Zones | Estimated FCDS Capability (MW) |  |  |  | Incremental Upgrade Cost Estimate ($million) |  |  |  | Estimated EODS Capability (MW) | New EO Values - level I | New EO Values - level II | Resource | Zone | Selected by RESOLVE | Selected by RESOLVE (FD) | FD tx limit check | Selected by RESOLVE (EO) | EO tx limit check | FD + EO tx limit check | Adjusted Selected resources (FD) | FD tx limit check | Adjusted Selected resources (EO) | EO tx limit check | FD + EO tx limit check | Zone | 30 MMT EO2 | [5 empty] | 30 MMT EO2 (Adjusted)
|  | Existing System | Minor Upgrades | Major Upgrade #1 | Major Upgrade #2 | Existing System | Minor Upgrades | Major Upgrade #1 | Major Upgrade #2 | Existing System |  |  | InState_Biomass | None | 0 | 0 |  | 0 |  |  | 0 |  | 0 |  |  | Zone Name in RESOLVE | Selected Resource (FD MW) | Selected Resource (EO MW) | Remaining Tx Capability (FD) | Exceeds Tx Capability (FD)? | Remaining Tx Capability (EO) | Exceeds Tx Capability (EO)? | Selected Resource (FD MW Adj) | Selected Resource (EO MW Adj) | Remaining Tx Capability (FD Adj) | Exceeds Tx Capability (FD adj)? | Remaining Tx Capability (EO adj) | Exceeds Tx Capability (EO adj)?
11000 | Northern CA | 2000 |  | 2000 |  |  |  | 285 |  | 3900 | 3900 | 3900 | Greater_Imperial_Geothermal | SCADSNV_Z3_GreaterImperial | 716.46 | 716.46 | ok | 0 | ok | ok | 716.46 | ok | 0 | ok | ok
| Round Mountain | 500 | [7 empty] | 2100 | 2100 | 2100 | Inyokern_North_Kramer_Geothermal | GK_Z2_InyokernAndNorthOfKramer | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | Northern CA |  |  | 4.98 |  | 818.12 |  |  |  | 4.98 |  | 818.12
| Humboldt | 0 | [7 empty] | 100 | 100 | 100 | Northern_California_Geothermal | NorCalOutsideTxConstraintZones | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | Norcal_Z2_Humboldt | 0 | 34 | 0 | 0 | 66 | 0 | 0 | 34 | 0 | 0 | 66 | 0
| Sacramento River | 2000 | [7 empty] | 4600 | 4600 | 4600 | Pacific_Northwest_Geothermal | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Norcal_Z3_SacramentoRiver | 1396.02 | 969.88 | 603.98 | 0 | 1630.12 | 0 | 1396.02 | 969.88 | 603.98 | 0 | 1630.12 | 0
| Solano | 600 |  | 2000 |  |  |  | 322 |  | 1300 | 1300 | 1300 | Riverside_Palm_Springs_Geothermal | SCADSNV_Z4_RiversideAndPalmSprings | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | Norcal_Z4_Solano | 599 | 78 | 1 | 0 | 622 | 0 | 599 | 78 | 1 | 0 | 622 | 0
[13 empty] | Solano_Geothermal | Norcal_Z4_Solano | 135 | 135 | ok | 0 | ok | ok | 135 | ok | 0 | ok | ok | Norcal_Z4_Solano_subzone | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Southern PG&E | 1100 |  | 1000 |  |  |  | 55 |  | TBD | 4180 | 5180 | Southern_Nevada_Geothermal | SCADSNV_Z1_EldoradoAndMtnPass | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | Southern PG&E |  |  | 425.05 |  | 0 |  |  |  | -898.95 |  | 0
| Westlands |  |  | 1000 |  |  |  | 55 |  | TBD | 2200 | 3200 | Carrizo_Solar | SPGE_Z3_Carrizo | 600 | 0 | ok | 600 | ok | ok | 0 | ok | 600 | ok | ok | SPGE_Z1_Westlands | 0 | 0 | 0 | 0 | 3200 | 0 | 0 | 0 | 0 | 0 | 3200 | 0
| Kern and Greater Carrizo | 1000 |  | 1500 |  |  |  | 241 |  | TBD | 4180 | 4180 | Carrizo_Wind | SPGE_Z3_Carrizo | 287 | 187 | ok | 100 | ok | ok | 187 | ok | 100 | ok | ok | SPGE_Z2_KernAndGreaterCarrizo | 181.27 | 2880 | 818.73 | 0 | 300 | 0 | 181.27 | 2880 | 818.73 | 0 | 300 | 0
| Carrizo | 400 |  | 700 |  |  |  | 53 |  | 400 | 400 | 1100 | Central_Valley_North_Los_Banos_Solar | SPGE_Z4_CentralValleyAndLosBanos | 0 | 0 | ok | 0 | breach | breach | 0 | breach | 0 | breach | breach | SPGE_Z3_Carrizo | 187 | 700 | 213 | 0 | 0 | 0 | 187 | 700 | 213 | 0 | 0 | 0
| Central Valley North & Los Banos | 1000 |  | 1000 |  |  |  | 274 |  | TBD | 1000 | 1000 | Central_Valley_North_Los_Banos_Wind | SPGE_Z4_CentralValleyAndLosBanos | 173 | 173 | ok | 0 | breach | breach | 173 | breach | 0 | breach | breach | SPGE_Z4_CentralValleyAndLosBanos | 306.68 | 500 | 693.32 | 0 | -500 | 1 | 1630.68 | 500 | -630.68 | 1 | -500 | 1
[13 empty] | Distributed_Solar |  | 0 | 0 |  | 0 |  | breach | 0 |  | 0 |  | breach
| Tehachapi | 4300 | 1000 |  |  |  | 100 |  |  | 5100 | 6100 | 6100 | Distributed_Wind |  | 0 | 0 |  | 0 |  | breach | 0 |  | 0 |  | breach | Tehachapi | 3677 | 1399 | 623 | 0 | 401 | 0 | 3677 | 1399 | 623 | 0 | 401 | 0
[13 empty] | Greater_Imperial_Solar | SCADSNV_Z3_GreaterImperial | 866.98 | 0 | ok | 866.98 | ok | ok | -511 | ok | 866.98 | ok | ok | Greater Kramer (North of Lugo) |  |  | 203 |  | 0 |  | 0 | 0 | 203 | 0 | 0 | 0
| Greater Kramer (North of Lugo) | 600 |  | 400 |  |  |  | 146 |  | 600 | 600 | 600 | Greater_Imperial_Wind | SCADSNV_Z3_GreaterImperial | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | GK_Z1_GreaterKramer | 0 | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 0 | 0
| North of Victor | 300 |  | 400 |  |  |  | 485 |  | 300 | 300 | 300 | Greater_Kramer_Wind | GK_Z1_GreaterKramer | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | GK_Z3_NorthOfVictor | 300 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0
| Inyokern and North of Kramer | 100 |  | 400 |  |  |  | 485 |  | 100 | 100 | 100 | Humboldt_Wind | Norcal_Z2_Humboldt | 34 | 0 | ok | 34 | ok | ok | 0 | ok | 34 | ok | ok | GK_Z2_InyokernAndNorthOfKramer | 97 | 0 | 3 | 0 | 0 | 0 | 97 | 0 | 3 | 0 | 0 | 0
| Pisgah | 400 |  | 400 |  |  |  | 261 |  | 400 | 400 | 400 | Inyokern_North_Kramer_Solar | GK_Z2_InyokernAndNorthOfKramer | 97 | 97 | ok | 0 | ok | ok | 97 | ok | 0 | ok | ok | GK_Z4_Pisgah | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0
[13 empty] | Kern_Greater_Carrizo_Solar | SPGE_Z2_KernAndGreaterCarrizo | 3001.27 | 121.27 | ok | 2880 | ok | ok | 121.27 | ok | 2880 | ok | ok | Southern CA Desert and Southern NV |  |  | 317.92 |  | 987.64 |  |  |  | -999.08 |  | 987.64
| Southern CA Desert and Southern NV | 3000 |  | 2800 |  |  |  | 2156 |  | 9600 | 10460 | 13260 | Kern_Greater_Carrizo_Wind | SPGE_Z2_KernAndGreaterCarrizo | 60 | 60 | ok | 0 | ok | ok | 60 | ok | 0 | ok | ok | SCADSNV_Z5_SCADSNV | 0 | 1970 | 3000 | 0 | 8290 | 0 | 2333 | 1970 | 667 | 0 | 8290 | 0
| El Dorado and Mountain Pass 230 kV | 250 |  | 1400 |  |  |  | 76 |  | 2400 | 2640 | 4040 | Kramer_Inyokern_Ex_Solar | KramerInyoOutsideTxConstraintZones | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | SCADSNV_Z1_EldoradoAndMtnPass | 248 | 1500 | 2 | 0 | 2290 | 0 | 248 | 1500 | 2 | 0 | 2290 | 0
| Southern NV (GLW-VEA) | 700 |  | 1400 |  |  |  | 150 |  | 700 | 770 | 2170 | Kramer_Inyokern_Ex_Wind | KramerInyoOutsideTxConstraintZones | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | SCADSNV_Z2_GLW_VEA | 442.03 | 1470 | 257.97 | 0 | 0 | 0 | 699.03 | 1470 | 0.97 | 0 | 0 | 0
| Greater Imperial* | 1200 |  | 1400 |  |  |  | 2334 |  | 3100 | 3100 | 3100 | Mountain_Pass_El_Dorado_Solar | SCADSNV_Z1_EldoradoAndMtnPass | 248 | 248 | ok | 0 | ok | ok | 248 | ok | 0 | ok | ok | SCADSNV_Z3_GreaterImperial | 919.08 | 1264.36 | 280.92 | 0 | 635.64 | 0 | 408.08 | 1264.36 | 791.92 | 0 | 635.64 | 0
| Riverside East & Palm Springs | 2950 |  | 1500 |  |  |  | 2156 |  | 5500 | 6050 | 6050 | North_Victor_Solar | GK_Z3_NorthOfVictor | 300 | 300 | ok | 0 | ok | ok | 300 | ok | 0 | ok | ok | SCADSNV_Z4_RiversideAndPalmSprings | 1072.97 | 3068 | 1877.03 | 0 | 32 | 0 | 310.97 | 3068 | 2639.03 | 0 | 32 | 0
[13 empty] | Northern_California_Ex_Solar | NorCalOutsideTxConstraintZones | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | Ex Zones |  |  | 866.43 | [5 empty] | 3507.43
| GreaterImpOutsideTxConstraintZones | 0 | [10 empty] | Northern_California_Ex_Wind | Norcal_Z3_SacramentoRiver | 865.9 | 865.9 | ok | 0 | ok | ok | 865.9 | ok | 0 | ok | ok | GreaterImpOutsideTxConstraintZones | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0
| KramerInyoOutsideTxConstraintZones | 0 | 0 | 0 | [8 empty] | NW_Ext_Tx_Wind | Norcal_Z3_SacramentoRiver | 1500 | 530.12 | ok | 969.88 | ok | ok | 530.12 | ok | 969.88 | ok | ok | KramerInyoOutsideTxConstraintZones | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0
| NorCalOutsideTxConstraintZones | 866 | 0 | 0 | [8 empty] | Riverside_Palm_Springs_Solar | SCADSNV_Z4_RiversideAndPalmSprings | 0 | 0 | ok | 0 | ok | ok | 29 | ok | 0 | ok | ok | NorCalOutsideTxConstraintZones | 0 | 0 | 866 | 0 |  | 0 | 0 | 0 | 866 | 0 |  | 0
| TehachapiOutsideTxConstraintZones | 0 | 0 | 0 | [8 empty] | Riverside_Palm_Springs_Wind | SCADSNV_Z4_RiversideAndPalmSprings | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | TehachapiOutsideTxConstraintZones | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0
| WestlandsOutsideTxConstraintZones | 1779 | 0 | 0 | [8 empty] | Sacramento_River_Solar | Norcal_Z3_SacramentoRiver | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | WestlandsOutsideTxConstraintZones | 1778.57 | 0 | 0.43 | 0 |  | 0 | -0.43 | 0 | 1779.43 | 0 |  | 0
| SCADOutsideTxConstraintZones | 862 | 0 | 0 | [8 empty] | Sacramento_River_Wind | Norcal_Z3_SacramentoRiver | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | SCADOutsideTxConstraintZones | 862 | 0 | 0 | 0 |  | 0 | 0 | 0 | 862 | 0 |  | 0
[13 empty] | SCADSNV_Solar | SCADSNV_Z5_SCADSNV | 1970 | 0 | ok | 1970 | ok | ok | 2333 | ok | 1970 | ok | ok | Total | 12066.62 | 15833.24 |  |  |  |  | 12066.62 | 15833.24
[13 empty] | SCADSNV_Wind | SCADSNV_Z5_SCADSNV | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[13 empty] | Solano_Solar | Norcal_Z4_Solano | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[13 empty] | Solano_subzone_Solar | Norcal_Z4_Solano_subzone | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[13 empty] | Solano_subzone_Wind | Norcal_Z4_Solano_subzone | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[13 empty] | Solano_Wind | Norcal_Z4_Solano | 542 | 464 | ok | 78 | ok | ok | 464 | ok | 78 | ok | ok
[13 empty] | Southern_California_Desert_Ex_Solar | SCADOutsideTxConstraintZones | 862 | 862 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[13 empty] | Southern_California_Desert_Ex_Wind | SCADOutsideTxConstraintZones | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[13 empty] | Southern_Nevada_Solar | SCADSNV_Z2_GLW_VEA | 1470 | 0 | ok | 1470 | ok | ok | 257 | ok | 1470 | ok | ok
[13 empty] | Southern_Nevada_Wind | SCADSNV_Z2_GLW_VEA | 442.03 | 442.03 | ok | 0 | ok | ok | 442.03 | ok | 0 | ok | ok
[13 empty] | SW_Ext_Tx_Wind | SCADSNV_Z4_RiversideAndPalmSprings | 500 | 500 | ok | 0 | ok | ok | 500 | ok | 0 | ok | ok
[13 empty] | Tehachapi_Solar | Tehachapi | 4801 | 3402 | ok | 1399 | ok | ok | 3402 | ok | 1399 | ok | ok
[13 empty] | Tehachapi_Ex_Solar | TehachapiOutsideTxConstraintZones | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[13 empty] | Tehachapi_Wind | Tehachapi | 275 | 275 | ok | 0 | ok | ok | 275 | ok | 0 | ok | ok
[13 empty] | Westlands_Ex_Solar | WestlandsOutsideTxConstraintZones | 1778.57 | 1778.57 | ok | 0 | ok | ok | -0.43 | ok | 0 | ok | ok
[13 empty] | Westlands_Ex_Wind | WestlandsOutsideTxConstraintZones | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[13 empty] | Westlands_Solar | SPGE_Z4_CentralValleyAndLosBanos | 633.68 | 133.68 | ok | 500 | breach | breach | 1457.68 | breach | 500 | breach | breach
[13 empty] | Cape_Mendocino_Offshore_Wind | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A
[13 empty] | Del_Norte_Offshore_Wind | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A
[13 empty] | Diablo_Canyon_Offshore_Wind_Ext_Tx | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A
[13 empty] | Diablo_Canyon_Offshore_Wind | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A
[13 empty] | Humboldt_Bay_Offshore_Wind | Norcal_Z2_Humboldt | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[13 empty] | Morro_Bay_Offshore_Wind |  | 0 | 0 |  | 0 |  | breach | 0 |  | 0 |  | breach
[13 empty] | Utah_Solar |  | 0 | 0 |  | 0 |  | breach | 0 |  | 0 |  | breach
[13 empty] | Arizona_Solar | SCADSNV_Z4_RiversideAndPalmSprings | 2140.97 | 572.97 | ok | 1568 | ok | ok | -218.03 | ok | 1568 | ok | ok
[13 empty] | New_Mexico_Solar | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A
[13 empty] | Baja_California_Solar | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A
[13 empty] | Baja_California_Wind | SCADSNV_Z3_GreaterImperial | 600 | 202.62 | ok | 397.38 | ok | ok | 202.62 | ok | 397.38 | ok | ok
[13 empty] | Pacific_Northwest_Wind | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A
[13 empty] | Idaho_Wind | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A
[13 empty] | Utah_Wind | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A
[13 empty] | Wyoming_Wind | SCADSNV_Z1_EldoradoAndMtnPass | 1500 | 0 | ok | 1500 | ok | ok | 0 | ok | 1500 | ok | ok
[13 empty] | Arizona_Wind | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A
[13 empty] | New_Mexico_Wind | SCADSNV_Z4_RiversideAndPalmSprings | 1500 | 0 | ok | 1500 | ok | ok | 0 | ok | 1500 | ok | ok
[13 empty] | Pumped_Hydro_12 | GreaterImpOutsideTxConstraintZones | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[13 empty] | Pumped_Hydro_8 | GreaterImpOutsideTxConstraintZones | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[13 empty] | Pumped_Hydro_18 | SCADSNV_Z4_RiversideAndPalmSprings | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[13 empty] | Total |  | 27899.86 | 12066.62 |  | 15833.24 |  |  | 12066.62 |  | 15833.24
Note on M6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Source: Feb2020_Resolve_tx_zones
Note on N6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Source: Feb2020_Resolve_tx_zones
Note on D15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Split Westlands polygon between CentralValleyLosBanos, Carrizo, and KernAndGreaterCarrizo - Westlands is not modeled individually but limits should be adhered to via the other zones. Upgrade cost and capacity for Southern PG&E is the same as Westlands.
Note on M15: Barave, Sushant: 1100 FC + 900 MW conventional gen + 10% increase
Note on M16: Barave, Sushant: 1000 FC + 2800 MW conventional gen + 10% increase
Note on M18: Barave, Sushant: 1000 FC + 0 MW conventional gen
Note on M27: Barave, Sushant: EO number increased based on the total sub-zonal increase
Note on N27: Barave, Sushant: EO number increased based on the total sub-zonal increase
Note on M28: Barave, Sushant: EO number increased by 10%
Note on M29: Barave, Sushant: EO number increased by 10%
Note on M31: Barave, Sushant: EO number increased by 10%

## CheckTab
Analysis of compliance of Round 1 mapping with criterion 2 (transmission limits), to inform changes needed in Round 2 of mapping | [5 empty] | Adjusted Amounts
| Zone Name in RESOLVE | Selected Resource (FD MW) | Estimated FCDS Capacity (MW) Existing System | Remaining tx capacity (child zone) | Remaining tx capacity (parent zone) | Selected Resource Adj (FD MW) | Remaining tx capability (FD MW) (child zone) | Remaining tx capability (FD MW) (parent zone)
| Northern CA |  | 2000 |  | 4.98 |  |  | 4.98
| Norcal_Z2_Humboldt | 0 | 0 | 0 |  | 0 | 0
| Norcal_Z3_SacramentoRiver | 1396.02 | 2000 | 603.98 |  | 1396.02 | 603.98
| Norcal_Z4_Solano | 599 | 600 | 1 |  | 599 | 1
| Norcal_Z4_Solano_subzone | 0 | 0 | 0 |  | 0 | 0
| Southern PG&E | 0 | 1100 |  | 425.05 |  |  | -898.95 | Adjustment 3: Move 1779 from Westlands_Ex solar to Westlands and other core zones, up to the amount possible within child tx limits, to increase confidence in tx capability estimate.
| SPGE_Z1_Westlands | 0 | 0 | 0 |  | 0 | 0 |  | Note overflow to Kern Creater Carrizo, and to Riverside Palm Springs
| SPGE_Z2_KernAndGreaterCarrizo | 181.27 | 1000 | 818.73 |  | 181.27 | 818.73 |  | Note the Southern PG&E parent zone tx capability is exceeded with this change.
| SPGE_Z3_Carrizo | 187 | 400 | 213 |  | 187 | 213 |  | Adjustment 5: Move this 900 MW to Gates-Diablo 500 kV system, per ISO guidance.
| SPGE_Z4_CentralValleyAndLosBanos | 306.68 | 1000 | 693.32 |  | 1630.68 | -630.68
| Tehachapi | 3677 | 4300 |  | 623 | 3677 |  | 623 | Reverse the move from tehachapi to riverside palm springs, to alleviate SCADSNV parent zone exceedance
| Greater Kramer (North of Lugo) | 0 | 600 |  | 203 |  |  | 203
| GK_Z1_GreaterKramer | 0 | 600 | 600 |  | 0 | 600
| GK_Z3_NorthOfVictor | 300 | 300 | 0 |  | 300 | 0
| GK_Z2_InyokernAndNorthOfKramer | 97 | 100 | 3 |  | 97 | 3
| GK_Z4_Pisgah | 0 | 400 | 400 |  | 0 | 400
| Southern CA Desert and Southern NV | 0 | 3000 |  | 317.92 |  |  | -999.08 | Adjustment2: Move 862 MW from Southern California Desert Ex Solar to SNV solar (to increase confidence in core zone tx capability)
| SCADSNV_Z5_SCADSNV | 0 | 3000 |  |  | 2333 |  |  | Note overflow to Greater Imperial and Riverside Palm Springs
| SCADSNV_Z1_EldoradoAndMtnPass | 248 | 250 | 2 |  | 248 | 2 |  | Note the SCADSNV parent zone tx capability is exceeded with this change.
| SCADSNV_Z2_GLW_VEA | 442.03 | 700 | 257.97 |  | 699.03 | 0.97 |  | Adjustment 6: Reverse the move from tehchapi to riverside palm springs
| SCADSNV_Z3_GreaterImperial | 919.08 | 1200 | 280.92 |  | 408.08 | 791.92 |  | Adjustment 7: Remaining amount exceeding transmission limit in Southern California Desert area can be accommodated if allocated to Mohave/Eldorado 500 kV substations. These are electrically outside the SCADSNV parent zone transmission constraint.
| SCADSNV_Z4_RiversideAndPalmSprings | 1072.97 | 2950 | 1877.03 |  | 310.97 | 2639.03
| Ex Zones |  | 3507 |  | 866.43 | 0 |  | 3507.43
| GreaterImpOutsideTxConstraintZones | 0 | 0 | 0 |  | 0 | 0
| KramerInyoOutsideTxConstraintZones | 0 | 0 | 0 |  | 0 | 0
| NorCalOutsideTxConstraintZones | 0 | 866 | 866 |  | 0 | 866
| TehachapiOutsideTxConstraintZones | 0 | 0 | 0 |  | 0 | 0
| WestlandsOutsideTxConstraintZones | 1778.57 | 1779 | 0.43 |  | -0.43 | 1779.43
| SCADOutsideTxConstraintZones | 862 | 862 | 0 |  | 0 | 862
| Total | 12066.62 | 0

## expandedEOSummaryTable
Purpose: review zones with expanded EO limits, and highlight where the expanded EO limit is highly utilized, to guide additional study.
| Tx Zones | 2030 FD | 2030 EO | Utilization of Expanded EO Tx Capability | Zone highly utilized >80%)
| Southern PG&E |  | 4080 | 100% | 1 | Study
| Westlands |  |  | N/A
| Kern_Greater_Carrizo-SPGE | 181.27 | 2880 | 91% | 1 | Study
| Carrizo-Kern_Greater_Carrizo-SPGE | 187 | 700 | 100% | 1 | Study
| Central_Valley_North_Los_Banos-SPGE | 306.68 | 500 | N/A |  | Study
| Tehachapi | 3677 | 1399 | 77.72% | 0 | Study
| Southern CA Desert and Southern NV | 0 | 9272.36 | 90.37% | 1 | Study
| Mountain_Pass_El_Dorado-SCADSNV | 248 | 1500 | 40% | 0
| SCADSNV-GLW_VEA | 442.03 | 1470 | 100% | 1 | Study
| SCADSNV-Greater_Imperial | 919.08 | 1264.36 | 67% | 0
| SCADSNV-Riverside_Palm_Springs | 1072.97 | 3068 | 99% | 1 | Study

## 3.1_SUM OF SOLAR RESOURCE ACRES
Source: CEC BUSBAR ALLOCATION_IRP 2020_SENSITIVITY2_v2.xlsx received from CEC 3/20/2020
What constitutes level 3 criteria flag? |  | None
What constitutes level 2 criteria flag? |  | 20% | Exceeds this percentage utilization of available land in proximity to substation
What constitutes level 1 criteria flag? |  | All other |  |  |  | SELECTED
| Tx Zone/Substation | ACRES_15_LOW | ACRES_15_HIGH | TOTAL ACRES_15 |  | Tx Zone/Substation | ACRES_15_LOW | ACRES_15_HIGH | TOTAL ACRES_15 | Porportion of Total Acres | Potential MW | Potential MW Low | Potential MW High | MW Allocation | Percent Total ACRES | Percent ACRES Low | RESOLVE Resource | RESOLVE MW | Exceeds 0.2 Total? | Exceeds 0.2 Low? | Aggregated RESOLVE Resource | Criteria Threshold: Exceeds 0.1 (Total)? | Criteria Threshold: Exceeds 0.1 (Low)?
| GK_Z2_InyokernAndNorthOfKramer |  |  |  | 1 | GK_Z2_InyokernAndNorthOfKramer | [11 empty] | 97 | 0 | 0 | Inyokern_North_Kramer_Solar | 1 | 1
| Kramer | 22291.7169 | 108531.3471 | 130823.0641 | 1 | Kramer | 22291.7169 | 108531.3471 | 130823.0641 | 0.44248 | 18689.0092 | 3184.531 | 15504.4782 | 42.9208 | 0.1016% | 1.348% | Inyokern_North_Kramer_Solar |  | 0 | 0 | North_Victor_Solar | 1 | 1
| Randsburg | 32006.017 | 132827.725 | 164833.7421 | 1 | Randsburg | 32006.017 | 132827.725 | 164833.7421 | 0.55752 | 23547.6774 | 4572.2881 | 18975.3893 | 54.0792 | 0.128% | 1.183% | Inyokern_North_Kramer_Solar |  | 0 | 0 | Greater_Imperial_Solar | 1 | 1
[5 empty] | 1 | Total | 54297.734 | 241359.0722 | 295656.8061 |  | 42236.6866 | 7756.8191 | 34479.8675 | [5 empty] | 0 | 0 | Riverside_Palm_Springs_Solar | 1 | 1
| GK_Z3_NorthOfVictor |  |  |  | 1 | GK_Z3_NorthOfVictor | [12 empty] | 0 | 0 | Westlands_Solar | 1 | 1
| Caldwell | 202589.8284 | 157848.9787 | 360438.8071 | 1 | Caldwell | [11 empty] | 300 | 0 | 0 | Kern_Greater_Carrizo_Solar | 1 | 1
[21 empty] | Carrizo_Solar | 1 | 1
| Cool Water | 37473.5686 | 118138.4948 | 155612.0633 | 1 | Coolwater | 37473.5686 | 118138.4948 | 155612.0633 | 0.28306 | 22230.2948 | 5353.3669 | 16876.9278 | 84.918 | 0.1081% | 1.586% | North_Victor_Solar |  | 0 | 0 | Tehachapi_Solar | 1 | 1
[21 empty] | SCADSNV_Solar | 2 | 1
[21 empty] | Mountain_Pass_El_Dorado_Solar | 1 | 1
| Victor | 226643.6098 | 167494.0413 | 394137.651 | 1 | Victor | 226643.6098 | 167494.0413 | 394137.651 | 0.71694 | 56305.3787 | 32377.6585 | 23927.7202 | 215.082 | 0.2739% | 0.6643% | North_Victor_Solar |  | 0 | 0 | Southern_Nevada_Solar | 1 | 1
| GK_Z4_Pisgah |  |  |  | 1 | Total | 264117.1784 | 285632.536 | 549749.7144 |  | 78535.6735 | 37731.0255 | 40804.648 | [5 empty] | 0 | 0
| Calcite | 263892.9909 | 637139.2422 | 901032.2331 | 0 | [15 empty] | SCADSNV_Solar | 1 | 1
| Lugo | 172373.9318 | 130196.009 | 302569.9407 | 0
| Pisgah | 33413.4063 | 60109.1333 | 93522.5395 | 0
0
| GreaterImpOutsideTxConstraintZones |  |  |  | 0
| Batiquitos | 157633.2279 | 47687.7448 | 205320.9727 | 0
| Calpeak Power Enterprise 7 | 202401.0742 | 121913.0151 | 324314.0893 | 0
| Doublett | 80436.4119 | 44591.8086 | 125028.2206 | 0
| Elliott | 45306.7779 | 46729.0408 | 92035.8187 | 0
| Encina | 126453.5357 | 24920.1506 | 151373.6864 | 0
| Escondido | 203431.2316 | 121928.098 | 325359.3296 | 0
| Fashion Valley | 28282.4774 | 16982.609 | 45265.0864 | 0
| Friars | 30269.0864 | 20371.3117 | 50640.398 | 0
| Main St. | 8746.7355 | 7666.9279 | 16413.6634 | 0
| Mesa Rim | 74254.3006 | 55526.6452 | 129780.9458 | 0
| Mission | 32441.3434 | 23992.6928 | 56434.0363 | 0
| North City West | 96479.2733 | 49201.9852 | 145681.2584 | 0
| Old Town | 25582.5134 | 12290.2734 | 37872.7868 | 0
| Palomar Airport | 143556.2751 | 37740.1784 | 181296.4536 | 0
| Penasquitos | 81522.3916 | 44597.6923 | 126120.084 | 0
| San Luis Rey | 133892.5768 | 33713.6815 | 167606.2584 | 0
| San Onofre | 23572.9517 | 62717.5171 | 86290.4688 | 0
| Shadowridge | 174758.176 | 56678.4514 | 231436.6275 | 0
| Silvergate | 8282.4579 | 7914.0333 | 16196.4912 | 0
| Sycamore Canyon | 81712.499 | 110787.768 | 192500.267 | 0
0
| KramerInyoOutsideTxConstraintZones |  |  |  | 0
| Chino | 115236.3359 | 34277.8753 | 149514.2112 | 0
| Etiwanda | 119521.0822 | 34143.9662 | 153665.0484 | 0
| Mira Loma | 153868.1406 | 44776.7507 | 198644.8913 | 0
| Padua | 103281.4096 | 37943.9349 | 141225.3445 | 0
| Rancho Vista | 117868.9942 | 35516.3754 | 153385.3696 | 0
| San Bernardino | 109189.6264 | 93582.3238 | 202771.9502 | 0
| Soquel | 112556.4999 | 38097.3188 | 150653.8187 | 0
| Vista | 154339.3024 | 71821.2363 | 226160.5387 | 0
0
| Norcal_Z3_SacramentoRiver |  |  |  | 0
| Carberry | 63074.3128 | 243737.7267 | 306812.0395 | 0
| Delevan | 226931.429 | 151233.1065 | 378164.5356 | 0
| Glenn | 312380.3423 | 98004.73 | 410385.0723 | 0
| Hat Creek 2 | 136010.3823 | 217546.2146 | 353556.5969 | 0
| Palermo | 214738.2962 | 187411.8637 | 402150.1599 | 0
| Pit 1 | 141777.2142 | 214369.5514 | 356146.7657 | 0
| Pit 1 Ph | 141554.7552 | 215092.9619 | 356647.7171 | 0
| Rio Oso | 390290.7861 | 40333.9026 | 430624.6887 | 0
| Table Mt. | 240287.3948 | 158423.4159 | 398710.8107 | 0
| Thermalito | 249279.7572 | 157778.7081 | 407058.4653 | 0
0
| Norcal_Z4_Solano |  |  |  | 0
| Amerigas | 260413.6709 | 114394.6488 | 374808.3196 | 0
| Bear Canyon | 117353.1805 | 203393.727 | 320746.9075 | 0
| Big Geysers | 130672.7993 | 197241.7972 | 327914.5965 | 0
| Calistoga 19 | 139609.4804 | 188704.0246 | 328313.5051 | 0
| Calpeak Power Vaca Dixon 1 | 262551.2185 | 111982.5397 | 374533.7582 | 0
| Castro Valley | 46178.7025 | 79406.8554 | 125585.5579 | 0
| Cayetano | 116507.784 | 230435.0267 | 346942.8107 | 0
| Cobb Creek | 146233.0272 | 181413.1069 | 327646.1341 | 0
| Contra Costa | 200921.8609 | 142150.3168 | 343072.1777 | 0
| Contra Costa Power | 210000.4144 | 136982.7775 | 346983.1919 | 0
| Fulton | 167498.4994 | 182135.9074 | 349634.4069 | 0
| Fumarole | 143276.331 | 186186.9032 | 329463.2343 | 0
| Geysers Unit 3 | 143689.1321 | 184447.8953 | 328137.0274 | 0
| Grant 20 | 139258.9193 | 192918.5383 | 332177.4576 | 0
| Lake View | 156924.1896 | 171485.9075 | 328410.0971 | 0
| Lakeville | 154619.4171 | 185621.2358 | 340240.6529 | 0
| Lambie Energy | 239213.1528 | 117480.771 | 356693.9238 | 0
| Lone Tree | 189537.5436 | 155953.7273 | 345491.2709 | 0
| Mccabe | 143113.7335 | 185477.3419 | 328591.0754 | 0
| N.N. | 449206.5858 | 549784.8816 | 998991.4674 | 0
| Ncpa 1 & 2 | 123947.0021 | 205474.0457 | 329421.0479 | 0
| Ncpa 3 & 4 | 121199.8005 | 206076.1177 | 327275.9182 | 0
| Oakmont North | 172006.2238 | 168014.5395 | 340020.7633 | 0
| Oakmont South | 178163.2055 | 164286.0515 | 342449.2571 | 0
| Peabody | 208220.5506 | 151124.4904 | 359345.0409 | 0
| Quicksilver | 124619.0788 | 201651.3827 | 326270.4615 | 0
| San Ramon | 59665.4883 | 164536.9464 | 224202.4347 | 0
| San Ramon Research Cntr. | 58453.2899 | 139042.1832 | 197495.4731 | 0
| Shiloh II | 225035.404 | 123666.5318 | 348701.9359 | 0
| Shiloh III | 223955.7302 | 124121.0506 | 348076.7808 | 0
| Socrates 18 | 135799.7582 | 198058.0195 | 333857.7776 | 0
| Sonoma 3 | 141347.4875 | 188616.9857 | 329964.4732 | 0
| Sulphur Springs | 139885.3262 | 191618.038 | 331503.3642 | 0
| Tassajara | 84879.4268 | 164186.7603 | 249066.1871 | 0
| Technical Ecological Services | 58453.2899 | 138967.763 | 197421.0529 | 0
| Trans Bay Cable | 169698.3246 | 134040.0136 | 303738.3382 | 0
| Tulucay | 167010.6069 | 134029.5226 | 301040.1295 | 0
| Vaca-Dixon & Gc Yard | 259967.5594 | 113942.9106 | 373910.47 | 0
| West Ford Flat | 132006.477 | 192813.0644 | 324819.5414 | 0
0
| Norcal_Z4_Solano_subzone |  |  |  | 0
| Bahia | 89717.6016 | 122145.7596 | 211863.3612 | 0
| Embarcadero (Sf Z) | 11281.9223 | 9586.7575 | 20868.6798 | 0
| Ignacio | 97444.3114 | 129758.5219 | 227202.8334 | 0
| Moraga | 39756.753 | 50910.0988 | 90666.8518 | 0
| Parkway | 130355.1143 | 119287.6411 | 249642.7555 | 0
| Pittsburg | 142317.3105 | 145503.8206 | 287821.131 | 0
| Rossmoor | 57400.5593 | 90527.015 | 147927.5743 | 0
| Sobrante | 34876.0698 | 49388.9096 | 84264.9794 | 0
| Tidewater | 69222.6397 | 127137.4364 | 196360.0761 | 0
| Unocal | 88845.2603 | 87790.2136 | 176635.474 | 0
0
| NorCalOutsideTxConstraintZones |  |  |  | 0
| Brighton | 191632.1015 | 60091.9943 | 251724.0959 | 0
| Gold Hill | 129525.3865 | 192147.9308 | 321673.3173 | 0
| Jefferson | 7653.7133 | 89704.2996 | 97358.0129 | 0
| Logan Creek | 250598.194 | 139780.0319 | 390378.2259 | 0
| Martin | 5969.6971 | 14049.8915 | 20019.5886 | 0
| San Mateo | 9079.2625 | 37973.8466 | 47053.1091 | 0
0
| SCADOutsideTxConstraintZones |  |  |  | 0
| Cima | 0 | 8101.2618 | 8101.2618 | 0
0
| SCADSNV_Z1_EldoradoAndMtnPass |  |  |  | 0
| ElDorado | 0 | 0 | 0 | 0
0
| SCADSNV_Z3_GreaterImperial |  |  |  | 1 | SCADSNV_Z3_GreaterImperial | [11 empty] | 1147 | 0 | 0
| East County | 11024.5372 | 96155.6295 | 107180.1666 | 1 | East County | 11024.5372 | 96155.6295 | 107180.1666 | 0.21835 | 15311.4524 | 1574.9339 | 13736.5185 | 250.4448 | 0.3571% | 15.9% | Greater_Imperial_Solar |  | 0 | 0
| Imperial Valley | 207772.1766 | 25482.8984 | 233255.075 | 1 | Imperial Valley | 207772.1766 | 25482.8984 | 233255.075 | 0.47519 | 33322.1536 | 29681.7395 | 3640.4141 | 545.0403 | 0.7773% | 1.836% | Greater_Imperial_Solar |  | 0 | 0
| Ocotillo Express | 38327.3915 | 112106.6951 | 150434.0866 | 1 | Ocotillo Express | 38327.3915 | 112106.6951 | 150434.0866 | 0.30646 | 21490.5838 | 5475.3416 | 16015.2422 | 351.5149 | 0.5013% | 6.42% | Greater_Imperial_Solar |  | 0 | 0
| Suncrest | 14208.8214 | 224325.5091 | 238534.3305 | 1 | Suncrest | [12 empty] | 0 | 0
[5 empty] | 1 | Total |  |  | 490869.3282 |  | 54812.7374 | 35157.0812 | 19655.6562 | 1147 |  |  |  |  | 0 | 0
0
| SCADSNV_Z4_RiversideAndPalmSprings |  |  |  | 1 | SCADSNV_Z4_RiversideAndPalmSprings | [12 empty] | 0 | 0
| Colorado River | 121669.3342 | 200351.3694 | 322020.7036 | 1 | Colorado River | 121669.3342 | 200351.3694 | 322020.7036 | 0.66247 | 46002.9577 | 17381.3335 | 28621.6242 | 1179.2042 | 1.698% | 6.784% | Riverside_Palm_Springs_Solar | 1780 | 0 | 0
| Red Bluff | 51719.5818 | 112347.5969 | 164067.1787 | 1 | Red Bluff | 51719.5818 | 112347.5969 | 164067.1787 | 0.33753 | 23438.1684 | 7388.5117 | 16049.6567 | 600.7958 | 0.8652% | 8.131% | Riverside_Palm_Springs_Solar |  | 0 | 0
[5 empty] | 1 | Total |  |  | 486087.8823 |  | 69441.126 | 24769.8451 | 44671.2809 | [5 empty] | 0 | 0
| SCADSNV_Z5_SCADSNV |  |  |  | 0
| Capacitor | 18967.9466 | 48994.843 | 67962.7896 | 0
| Eagle Mt. | 47355.3448 | 84478.5763 | 131833.9211 | 0
| Iron Mt. | 32233.3948 | 161416.1964 | 193649.5912 | 0
| Julian Hinds | 9794.171 | 39712.1997 | 49506.3708 | 0
| Los Coches | 45299.875 | 141878.3741 | 187178.2491 | 0
| Miguel | 11515.3357 | 58209.2263 | 69724.562 | 0
| Mohave | 252.3457 | 5822.8718 | 6075.2175 | 0
| Otay Mesa | 7815.131 | 59710.2948 | 67525.4258 | 0
| South Bay | 7191.9922 | 12576.9679 | 19768.9601 | 0
0
| SPGE_Z1_Westlands |  |  |  | 1 | SPGE_Z1_Westlands | [11 empty] | 1327 | 0 | 0
| Ashlan Ave. | 339741.7717 | 55625.8303 | 395367.602 | 0
| Fig Garden | 325839.8294 | 67855.9079 | 393695.7373 | 0
| Gates | 244790.1476 | 61943.4468 | 306733.5943 | 1 | Gates | 244790.1476 | 61943.4468 | 306733.5943 | 0.14423 | 43819.0849 | 34970.0211 | 8849.0638 | 191.3977 | 0.063% | 0.5473% | Westlands_Solar |  | 0 | 0
| Gregg | 317053.4155 | 74590.2185 | 391643.6339 | 0
| Helm | 351333.2811 | 7886.9101 | 359220.1912 | 1 | Helm | 351333.2811 | 7886.9101 | 359220.1912 | 0.16891 | 51317.1702 | 50190.4687 | 1126.7014 | 224.1486 | 0.07378% | 0.4466% | Westlands_Solar |  | 0 | 0
| Henrietta | 332147.2882 | 0 | 332147.2882 | 1 | Henrietta | 332147.2882 | 0 | 332147.2882 | 0.15618 | 47449.6126 | 47449.6126 | 0 | 207.2555 | 0.06822% | 0.4368% | Westlands_Solar |  | 0 | 0
| Herndon | 323716.0747 | 66266.3941 | 389982.4687 | 0
| Kearney (New) | 371486.0414 | 60.7305 | 371546.7719 | 0
| Los Banos | 114225.5629 | 174190.3625 | 288415.9254 | 0
| Mc Call | 409347.0596 | 5918.4196 | 415265.4792 | 1 | Mc Call | 409347.0596 | 5918.4196 | 415265.4792 | 0.19527 | 59323.6399 | 58478.1514 | 845.4885 | 259.1201 | 0.08529% | 0.4431% | Westlands_Solar |  | 0 | 0
| Mc Mullin | 386505.5976 | 648.197 | 387153.7946 | 1 | Mc Mullin | 386505.5976 | 648.197 | 387153.7946 | 0.18205 | 55307.6849 | 55215.0854 | 92.5996 | 241.5788 | 0.07952% | 0.4375% | Westlands_Solar |  | 0 | 0
| Oxford | 161974.2756 | 150132.069 | 312106.3446 | 0
| Panoche | 208836.716 | 117290.9153 | 326127.6313 | 1 | Panoche | 208836.716 | 117290.9153 | 326127.6313 | 0.15335 | 46589.6616 | 29833.8166 | 16755.845 | 203.4993 | 0.06698% | 0.6821% | Westlands_Solar |  | 0 | 0
| San Luis | 108748.8872 | 201483.0001 | 310231.8873 | 0
| San Luis 3 | 195956.321 | 128527.0548 | 324483.3759 | 1 | Total | 1932960.0901 | 193687.8887 | 2126647.9788 |  | 303806.8541 | 276137.1557 | 27669.6984 | 1327 |  |  |  |  | 0 | 0
| San Luis 5 | 173321.3842 | 138034.6142 | 311355.9984 | 0
| Wright | 138416.5448 | 143289.1497 | 281705.6945 | 0
0
| SPGE_Z2_KernAndGreaterCarrizo |  |  |  | 1 | SPGE_Z2_KernAndGreaterCarrizo | [11 empty] | 3632 | 0 | 0
| Arco | 273894.9336 | 115184.61 | 389079.5436 | 1 | Arco | 273894.9336 | 115184.61 | 389079.5436 | 0.20625 | 55582.7919 | 39127.8477 | 16454.9443 | 749.0857 | 0.278% | 1.914% | Kern_Greater_Carrizo_Solar |  | 0 | 0
| Buena Vista Pumps | 210937.6669 | 156404.3615 | 367342.0284 | 1 | Buena Vista Pumps | [12 empty] | 0 | 0
| Kern Power | 316543.5343 | 76163.7254 | 392707.2597 | 1 | Kern Power | [12 empty] | 0 | 0
| Midway | 275515.9004 | 100733.5 | 376249.4004 | 1 | Midway | 275515.9004 | 100733.5 | 376249.4004 | 0.19944 | 53749.9143 | 39359.4143 | 14390.5 | 724.3841 | 0.2688% | 1.84% | Kern_Greater_Carrizo_Solar |  | 0 | 0
| Renfro | 318206.2071 | 68185.7886 | 386391.9958 | 1 | Renfro | 318206.2071 | 68185.7886 | 386391.9958 | 0.20482 | 55198.8565 | 45458.0296 | 9740.8269 | 743.9114 | 0.276% | 1.636% | Kern_Greater_Carrizo_Solar |  | 0 | 0
| Stockdale | 329570.6643 | 58200.378 | 387771.0423 | 1 | Stockdale | 329570.6643 | 58200.378 | 387771.0423 | 0.20555 | 55395.8632 | 47081.5235 | 8314.3397 | 746.5665 | 0.277% | 1.586% | Kern_Greater_Carrizo_Solar |  | 0 | 0
| Wheeler Ridge | 238849.923 | 108140.4149 | 346990.3379 | 1 | Wheeler Ridge | 238849.923 | 108140.4149 | 346990.3379 | 0.18394 | 49570.0483 | 34121.4176 | 15448.6307 | 668.0523 | 0.2479% | 1.958% | Kern_Greater_Carrizo_Solar |  | 0 | 0
[5 empty] | 1 | Total | 1436037.6285 | 450444.6914 | 1886482.3199 | [9 empty] | 0 | 0
| SPGE_Z3_Carrizo |  |  |  | 1 | SPGE_Z3_Carrizo | [11 empty] | 600 | 0 | 0
| Caliente | 153856.6636 | 222592.8349 | 376449.4985 | 1 | Caliente | 153856.6636 | 222592.8349 | 376449.4985 | 0.33108 | 53778.4998 | 21979.5234 | 31798.9764 | 198.6507 | 0.3694% | 0.9038% | Carrizo_Solar |  | 0 | 0
| Mesa | 183463.2714 | 152282.0231 | 335745.2944 | 1 | Mesa | 183463.2714 | 152282.0231 | 335745.2944 | 0.29529 | 47963.6135 | 26209.0388 | 21754.5747 | 177.1713 | 0.3694% | 0.676% | Carrizo_Solar |  | 0 | 0
| Solar | 129612.6335 | 260323.1903 | 389935.8237 | 0
| Templeton | 246398.0105 | 178426.6302 | 424824.6408 | 1 | Templeton | 246398.0105 | 178426.6302 | 424824.6408 | 0.37363 | 60689.2344 | 35199.7158 | 25489.5186 | 224.178 | 0.3694% | 0.6369% | Carrizo_Solar |  | 0 | 0
[5 empty] | 0 |  | 583717.9455 | 553301.4881 | 1137019.4337
| SPGE_Z4_CentralValleyAndLosBanos |  |  |  | 0 | [12 empty] | 1327
| Bellota | 255519.9564 | 190398.795 | 445918.7514 | 0
| Cottle | 244115.4368 | 184777.5408 | 428892.9777 | 0
| Eight Mile | 361384.9129 | 26159.0407 | 387543.9536 | 0
| Stagg | 361483.7987 | 19362.6578 | 380846.4565 | 0
| Storey | 293286.0857 | 148690.1618 | 441976.2475 | 0
| Weber | 390024.4437 | 7132.1547 | 397156.5984 | 0
| Wilson | 221460.6649 | 144010.4955 | 365471.1604 | 0
0
| Tehachapi |  |  |  | 1 | Tehachapi | [11 empty] | 3801 | 0 | 0
| Antelope | 283494.6086 | 91597.5112 | 375092.1198 | 1 | Antelope | 283494.6086 | 91597.5112 | 375092.1198 | 0.25986 | 53584.5885 | 40499.2298 | 13085.3587 | 987.7323 | 0.479% | 2.439% | Tehachapi_Solar |  | 0 | 0
| Arbwind | 187469.0637 | 131236.3051 | 318705.3688 | 1 | Arbwind | [8 empty] | 0 |  |  |  | 0 | 0
| Bailey | 51084.6647 | 172593.7956 | 223678.4603 | 1 | Bailey | [8 empty] | 0 |  |  |  | 0 | 0
| Highwind | 177593.1111 | 122671.0948 | 300264.2058 | 1 | Highwind | [8 empty] | 0 |  |  |  | 0 | 0
| Mojave 17 | 219898.1683 | 123482.8752 | 343381.0436 | 1 | Mojave 17 | [8 empty] | 0 |  |  |  | 0 | 0
| N.N. | 449206.5858 | 549784.8816 | 998991.4674 | 1 | N.N. | [8 empty] | 0 |  |  |  | 0 | 0
| Pardee | 103540.6965 | 134265.1503 | 237805.8468 | 1 | Pardee | [8 empty] | 0 |  |  |  | 0 | 0
| Pearblossom | 161230.5478 | 175860.4673 | 337091.0151 | 1 | Pearblossom | 161230.5478 | 175860.4673 | 337091.0151 | 0.23353 | 48155.8593 | 23032.9354 | 25122.9239 | 887.6638 | 0.4305% | 3.854% | Tehachapi_Solar |  | 0 | 0
| Saugus | 104148.9977 | 130389.4178 | 234538.4155 | 1 | Saugus | [8 empty] | 0 |  |  |  | 0 | 0
| Sky River North | 42559.4625 | 138617.3388 | 181176.8013 | 1 | Sky River North | [8 empty] | 0 |  |  |  | 0 | 0
| Vincent | 184408.9052 | 117262.3318 | 301671.237 | 1 | Vincent | [8 empty] | 0 |  |  |  | 0 | 0
| Warne | 33576.2089 | 158595.9827 | 192172.1916 | 1 | Warne | [8 empty] | 0 |  |  |  | 0 | 0
| Westwind | 219616.5744 | 124770.4984 | 344387.0727 | 1 | Westwind | [8 empty] | 0 |  |  |  | 0 | 0
| Whirlwind | 242518.5078 | 141802.2074 | 384320.7152 | 1 | Whirlwind | 242518.5078 | 141802.2074 | 384320.7152 | 0.26625 | 54902.9593 | 34645.5011 | 20257.4582 | 1012.034 | 0.4908% | 2.921% | Tehachapi_Solar |  | 0 | 0
| Winderness | 224940.2791 | 119399.7675 | 344340.0466 | 1 | Winderness | [8 empty] | 0 |  |  |  | 0 | 0
| Windhub | 224363.6679 | 122565.196 | 346928.864 | 1 | Windhub | 224363.6679 | 122565.196 | 346928.864 | 0.24035 | 49561.2663 | 32051.9526 | 17509.3137 | 913.5699 | 0.443% | 2.85% | Tehachapi_Solar |  | 0 | 0
[5 empty] | 1 | Total | 911607.3321 | 531825.382 | 1443432.7141 |  |  |  |  | 15158 |  |  |  | 14011 | 0 | 0
| TehachapiOutsideTxConstraintZones |  |  |  | 0
| Airchem | 0 | 0 | 0 | 1 | Mountain Pass and El Dorado/Southern_Nevada_Solar | [12 empty] | 0 | 0
| Arcogen | 0 | 0 | 0 | 1 | Crazy Eyes |  |  | 155787 | 0.61 | 22255.2857 |  |  | 1231 | 5.531% |  | SCADSNV_Solar |  | 0 | 0
| Cameron | 0 | 0 | 0 | 1 | Desert View |  |  | 42719 | 0.17 | 6102.7143 |  |  | 343 | 5.62% |  | SCADSNV_Solar |  | 0 | 0
| Casitas | 105110.5747 | 55297.4168 | 160407.9915 | 1 | Innovation |  |  | 54904 | 0.22 | 7843.4286 |  |  | 444 | 5.661% |  | SCADSNV_Solar |  | 0 | 0
| Center | 834.8357 | 0 | 834.8357 | 1 | El Dorado 230kV |  |  | 42263 | 1 | 6037.5714 |  |  | 986 | 16.33% |  | Mountain_Pass_El_Dorado_Solar |  | 0 | 0
| Chevmain | 0 | 0 | 0 | 0
| Del Amo | 0 | 0 | 0 | 1 | SCADSNV_Solar | [12 empty] | 0 | 0
| Eagle Rock | 89.8475 | 20648.2167 | 20738.0643 | 1 | Mohave 500kV |  |  | 28764 | 1 | 4109.1429 |  |  | 942 | 22.92% |  | SCADSNV_Solar |  | 1 | 0
| El Nido | 0 | 0 | 0 | 0
| El Segundo | 0 | 3.37 | 3.37 | 0
| Federalgen | 0 | 0 | 0 | 0
| Goodrich | 90.2923 | 23212.4228 | 23302.7151 | 0
| Gould | 3646.5285 | 48488.1105 | 52134.639 | 0
| Harborgen | 0 | 0 | 0 | 0
| Hinson | 0 | 0 | 0 | 0
| Kinetic | 0 | 0 | 0 | 0
| La Cienega | 60.4448 | 3.37 | 63.8147 | 0
| La Fresa | 0 | 0 | 0 | 0
| Laguna Bell | 0 | 0 | 0 | 0
| Lawndale | 0 | 0 | 0 | 0
| Lighthipe | 0 | 0 | 0 | 0
| Mandalay | 121907.7341 | 24738.7736 | 146646.5076 | 0
| Mesa | 183463.2714 | 152282.0231 | 335745.2944 | 0
| Moorpark | 175849.823 | 76091.5603 | 251941.3833 | 0
| N.N. | 449206.5858 | 549784.8816 | 998991.4674 | 0
| Olinda | 28973.3032 | 12098.187 | 41071.4902 | 0
| Ormond Beach | 110407.0725 | 14884.7 | 125291.7726 | 0
| Redondo 1 | 0 | 0 | 0 | 0
| Repro | 0 | 0 | 0 | 0
| Rio Hondo | 18154.1772 | 19395.3754 | 37549.5526 | 0
| Rosecrans | 0 | 0 | 0 | 0
| Santa Clara | 176304.6776 | 44572.428 | 220877.1056 | 0
| Stadium | 0 | 0 | 0 | 0
| Stanhill | 0 | 0 | 0 | 0
| Tahiti | 60.4448 | 13.3854 | 73.8302 | 0
| Venice Hydro | 60.4448 | 8.0744 | 68.5191 | 0
| Walnut | 26759.3165 | 8355.5954 | 35114.9118 | 0
| Windsor Hills | 0 | 0 | 0 | 0
0
| WestlandsOutsideTxConstraintZones |  |  |  | 0
| Coburn | 162720.8122 | 218556.7929 | 381277.605 | 0
| Diablo Canyon | 52516.4306 | 78414.7828 | 130931.2133 | 0
| Goleta | 50794.101 | 53728.8796 | 104522.9806 | 0
0
| Grand Total | 28058029.0728 | 21760032.2769 | 49818061.3496 | 0

## 3.1_SUM WIND RESOURCE ACRES
Source: CEC BUSBAR ALLOCATION_IRP 2020_SENSITIVITY2_v2.xlsx received from CEC 3/20/2020
What constitutes level 3 criteria flag? |  |  | None
What constitutes level 2 criteria flag? |  |  | 20%
What constitutes level 1 criteria flag? |  |  | All other
|  |  | Wind Project | ACRES_LOW | ACRES_HIGH | TOTAL_ACRES | Potential MW | MW Allocation | Percent of Total _MW | PROJECT ACRES | Percent of Acres_LOW |  | Criteria Threshold: Exceeds 20% (Total)? | Criteria Threshold: Exceeds 20% (Low)? | RESOLVE Resource | Aggregated RESOLVE Resource | Criteria Threshold: Exceeds 20% (Total)? | Criteria Threshold: Exceeds 20% (Low)?
| Carrizo Wind | [6 empty] | 287 |  |  |  |  | 0 | 0 | Carrizo_Wind | Carrizo_Wind | 2 | 2
|  | Templeton | Wind 124 | 6729.9534 | 24299.8298 | 31029.7832 | 288 |  | 99.65% | 11480 | 170.6% |  | 1 | 1 | Carrizo_Wind | Central_Valley_North_Los_Banos_Wind | 2 | 2
[13 empty] | 0 | 0 |  | Humboldt_Wind | 2 | 2
| Central Valley and North Los Banos Wind | [6 empty] | 173 |  |  |  |  | 0 | 0 | Central_Valley_North_Los_Banos_Wind | Kern_Greater_Carrizo_Wind | 2 | 2
|  | Los Banos | Wind 112 | 16166.129 | 23407.3429 | 39573.472 | 170 |  | 101.8% | 6920 | 42.81% |  | 1 | 1 | Central_Valley_North_Los_Banos_Wind | Northern_California_Ex_Wind | 2 | 1
[13 empty] | 0 | 0 |  | Solano_Wind | 2 | 2
| Humboldt Wind | [6 empty] | 34 |  |  |  |  | 0 | 0 | Humboldt_Wind | Tehachapi_Wind | 2 | 1
|  | Bridgeville | Wind 7 | 0 | 11414.6331 | 11414.6331 | 34 |  | 50.75% | 5022.2 |  |  | 1 | 0 | Humboldt_Wind
|  |  | Wind 8 | 0 | 11355.8557 | 11356.3005 | 33 |  | 49.25% | 4837.3 |  |  | 1 | 0 | Humboldt_Wind
|  |  |  | 0 | 22770.4889 | 22770.9337 | 67 |  |  | 1360 | #DIV/0! | No Low Value ACRES | 0 | #DIV/0! | Humboldt_Wind
[13 empty] | 0 | 0
| Kern Greater Carrizo Wind | [6 empty] | 60 |  |  |  |  | 0 | 0 | Kern_Greater_Carrizo_Wind
|  | Cholame | Wind 207 | 11176.1755 | 9449.3403 | 20625.5157 | 69 |  | 86.96% | 2400 | 21.47% |  | 1 | 1 | Kern_Greater_Carrizo_Wind
[13 empty] | 0 | 0
| Sacramento Valley Wind | [6 empty] | 866 |  |  |  |  | 0 | 0 | Northern_California_Ex_Wind
|  | Glenn | Wind 34 | 21839.4351 | 0 | 21839.4351 | 120 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 35 | 32087.1942 | 0 | 32087.1942 | 166 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 36 | 27505.3046 | 1796.0503 | 29301.3548 | 149 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 37 | 25021.9988 | 3740.2999 | 28762.2988 | 168 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 38 | 13114.3746 | 16735.7764 | 29850.1511 | 157 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 39 | 25914.2428 | 7966.2534 | 33880.4961 | 166 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 40 | 20908.7046 | 8987.8427 | 29896.5473 | 166 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 42 | 31674.5459 | 1332.0413 | 33006.5872 | 183 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 43 | 21329.2313 | 11015.7038 | 32344.9351 | 183 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 50 | 17028.3306 | 12467.3163 | 29495.647 | 166 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 51 | 33870.1339 | 247.1054 | 34117.2393 | 163 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 204 | 13663.4689 | 0 | 13663.4689 | 69 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  |  | 283956.9655 | 64288.3895 | 348245.355 | 1856 | 400 | 21.55% | 16000 | 5.635% |  | 1 | 0 | Northern_California_Ex_Wind
|  | Delevan | [10 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 31 | 6084.8094 | 1282.7612 | 7367.5707 | 38 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 32 | 31202.9317 | 2641.358 | 33844.2897 | 175 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 33 | 29015.8768 | 0 | 29015.8768 | 222 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  |  | 66303.6179 | 3924.1192 | 70227.7371 | 435 | 94 | 21.61% | 3760 | 5.671% |  | 1 | 0 | Northern_California_Ex_Wind
|  | Thermalito | [10 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 52 | 32608.7529 | 0 | 32608.7529 | 182 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 53 | 29609.2617 | 0 | 29609.2617 | 172 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 54 | 30953.4561 | 377.0251 | 31330.4812 | 174 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 55 | 23422.0305 | 0 | 23422.0305 | 138 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 56 | 31228.9783 | 633.892 | 31862.8703 | 172 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 202 | 16889.0583 | 0 | 16889.0583 | 96 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  |  | 164711.5378 | 1010.9171 | 165722.4549 | 934 | 201 | 21.52% | 8040 | 4.881% |  | 1 | 0 | Northern_California_Ex_Wind
|  | Rio Oso | [10 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 62 | 30714.3441 | 0 | 30714.3441 | 176 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 73 | 29002.0732 | 0 | 29002.0732 | 172 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 77 | 35294.3904 | 0 | 35294.3904 | 181 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 78 | 30267.3127 | 0 | 30267.3127 | 160 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 79 | 20227.9346 | 0 | 20227.9346 | 107 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  |  | 145506.0551 | 0 | 145506.0551 | 796 | 171 | 21.48% | 6840 | 4.701% |  | 1 | 0 | Northern_California_Ex_Wind
[13 empty] | 0 | 0
| Solano Wind | [11 empty] | 0 | 0 | Solano_Wind
|  | Lakeville | Wind 198 | 2361.3656 | 15002.7991 | 17364.1647 | 71 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 101 | 2393.1548 | 29048.7635 | 31441.9184 | 166 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 102 | 7207.3104 | 8590.8881 | 15798.1985 | 70 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 196 | 2948.0119 | 31570.5233 | 34518.5353 | 146 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 197 | 4625.9771 | 26007.4994 | 30633.4765 | 117 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 199 | 4046.7783 | 26316.1556 | 30362.9339 | 136 | [5 empty] | 0 | 0 | Solano_Wind
|  |  |  | 23582.5981 | 136536.6291 | 160119.2272 | 706 | 227 | 32.15% | 9080 | 38.5% |  | 1 | 1 | Solano_Wind
|  | Tulucay | [10 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 103 | 3479.2106 | 13204.9372 | 16684.1477 | 22 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 106 | 5958.7606 | 19351.3274 | 25310.088 | 50 | [5 empty] | 0 | 0 | Solano_Wind
|  |  |  | 9437.9712 | 32556.2646 | 41994.2357 | 72 | 23 | 31.94% | 920 | 9.748% |  | 1 | 0 | Solano_Wind
|  | Vaca-Dixon & GC Yard | [10 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 80 | 11733.2651 | 20668.7168 | 32401.9819 | 86 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 81 | 23098.3902 | 11485.509 | 34583.8992 | 114 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 82 | 30872.3849 | 0 | 30872.3849 | 77 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 83 | 34973.0826 | 573.8062 | 35546.8888 | 80 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 84 | 32773.4554 | 3679.007 | 36452.4624 | 89 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 85 | 29812.5532 | 6243.4009 | 36055.9541 | 85 | [5 empty] | 0 | 0 | Solano_Wind
|  |  |  | 163263.1314 | 42650.4398 | 205913.5713 | 531 | 171 | 32.2% | 6840 | 4.19% |  | 1 | 0 | Solano_Wind
|  | Shilo III | [10 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 91 | 28653.8156 | 5619.5354 | 34273.3509 | 82 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 206 | 10020.747 | 4704.6326 | 14725.3796 | 34 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 88 | 38048.726 | 3368.0093 | 41416.7354 | 88 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 90 | 22115.5238 | 689.4769 | 22805.0007 | 57 | [5 empty] | 0 | 0 | Solano_Wind
|  |  |  | 98838.8124 | 14381.6542 | 113220.4666 | 261 | 84 | 32.18% | 3360 | 3.399% |  | 1 | 0 | Solano_Wind
|  | Lone Tree | [10 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 104 | 5792.3906 | 16974.6621 | 22767.0528 | 35 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 107 | 15567.8983 | 23209.4731 | 38777.3714 | 79 | [5 empty] | 0 | 0 | Solano_Wind
|  |  |  | 21360.289 | 40184.1352 | 61544.4242 | 114 | 37 | 32.46% | 1480 | 6.929% |  | 1 | 0 | Solano_Wind
[13 empty] | 0 | 0
| Tehachapi Wind | [11 empty] | 0 | 0 | Tehachapi_Wind
|  | Windhub | Wind 129 | 13670.7998 | 16116.6015 | 29787.4013 | 128 | [5 empty] | 0 | 0 | Tehachapi_Wind
|  |  | Wind 156 | 12435.83 | 922.2979 | 13358.1279 | 86 | [5 empty] | 0 | 0 | Tehachapi_Wind
|  |  | Wind 157 | 30641.6782 | 1300.9199 | 31942.5981 | 138 | [5 empty] | 0 | 0 | Tehachapi_Wind
|  |  |  | 56748.308 | 18339.8193 | 75088.1273 | 352 | 275 | 78.12% | 11000 | 19.38% |  | 1 | 0 | Tehachapi_Wind

## 3.2_SUM OF SOLAR RESOURCE ACRE2
Source: received CEC BUSBAR ALLOCATION_IRP 2020_SENSITIVITY2_v3.xlsx received 3/26
What constitutes level 3 criteria flag? |  | None
What constitutes level 2 criteria flag? |  | 20% | Exceeds this percentage utilization of available land in proximity to substation
What constitutes level 1 criteria flag? |  | All other
SELECTED
| Tx Zone/Substation | ACRES_15_LOW | ACRES_15_HIGH | TOTAL ACRES_15 | Tx Zone/Substation | ACRES_15_LOW | ACRES_15_HIGH | TOTAL ACRES_15 | Porportion of Total Acres | Potential MW | Potential MW Low | Potential MW High | MW Allocation | Percent Total ACRES | Percent ACRES Low | RESOLVE Resource | RESOLVE MW | Exceeds 0.2 Total? | Exceeds 0.2 Low? | Aggregated RESOLVE Resource | Exceeds 0.2 Total? | Exceeds 0.2 Low?
| GK_Z2_InyokernAndNorthOfKramer |  |  |  | GK_Z2_InyokernAndNorthOfKramer | [11 empty] | 97 | 0 | 0 | Inyokern_North_Kramer_Solar | 1 | 1
| Kramer | 22291.7169 | 108531.3471 | 130823.0641 | Kramer | 22291.7169 | 108531.3471 | 130823.0641 | 0.44248 | 18689.0092 | 3184.531 | 15504.4782 | 42.9208 | 0.1016% | 1.348% | Inyokern_North_Kramer_Solar |  | 0 | 0 | North_Victor_Solar | 1 | 1
| Randsburg | 32006.017 | 132827.725 | 164833.7421 | Randsburg | 32006.017 | 132827.725 | 164833.7421 | 0.55752 | 23547.6774 | 4572.2881 | 18975.3893 | 54.0792 | 0.128% | 1.183% | Inyokern_North_Kramer_Solar |  | 0 | 0 | Greater_Imperial_Solar | 1 | 1
[5 empty] | Total | 54297.734 | 241359.0722 | 295656.8061 |  | 42236.6866 | 7756.8191 | 34479.8675 | [5 empty] | 0 | 0 | Riverside_Palm_Springs_Solar | 1 | 1
| GK_Z3_NorthOfVictor |  |  |  | GK_Z3_NorthOfVictor | [12 empty] | 0 | 0 | Westlands_Solar | 1 | 1
| Caldwell | 202589.8284 | 157848.9787 | 360438.8071 | Caldwell | [11 empty] | 300 | 0 | 0 | Kern_Greater_Carrizo_Solar | 1 | 1
| Cool Water | 37473.5686 | 118138.4948 | 155612.0633 | Coolwater | 37473.5686 | 118138.4948 | 155612.0633 | 0.28306 | 22230.2948 | 5353.3669 | 16876.9278 | 84.918 | 0.1081% | 1.586% | North_Victor_Solar |  | 0 | 0 | Carrizo_Solar | 1 | 1
| Victor | 226643.6098 | 167494.0413 | 394137.651 | Victor | 226643.6098 | 167494.0413 | 394137.651 | 0.71694 | 56305.3787 | 32377.6585 | 23927.7202 | 215.082 | 0.2739% | 0.6643% | North_Victor_Solar |  | 0 | 0 | Tehachapi_Solar | 1 | 1
| GK_Z4_Pisgah |  |  |  | Total | 264117.1784 | 285632.536 | 549749.7144 |  | 78535.6735 | 37731.0255 | 40804.648 | [5 empty] | 0 | 0 | SCADSNV_Solar | 2 | 1
| Calcite | 263892.9909 | 637139.2422 | 901032.2331 | [13 empty] | 0 | 0 | Mountain_Pass_El_Dorado_Solar | 2 | 1
| Lugo | 172373.9318 | 130196.009 | 302569.9407 | [13 empty] | 0 | 0 | Southern_Nevada_Solar | 1 | 1
| Pisgah | 33413.4063 | 60109.1333 | 93522.5395 | [13 empty] | 0 | 0 | SCADSNV_Solar | 1 | 1
[18 empty] | 0 | 0 | Southern_California_Desert_Ex_Solar | 1 | 1
| GreaterImpOutsideTxConstraintZones | [16 empty] | 0 | 0 | Westlands_Ex_Solar | 1 | 1
| Batiquitos | 157633.2279 | 47687.7448 | 205320.9727 | [13 empty] | 0 | 0
| Calpeak Power Enterprise 7 | 202401.0742 | 121913.0151 | 324314.0893 | [13 empty] | 0 | 0
| Doublett | 80436.4119 | 44591.8086 | 125028.2206 | [13 empty] | 0 | 0
| Elliott | 45306.7779 | 46729.0408 | 92035.8187 | [13 empty] | 0 | 0
| Encina | 126453.5357 | 24920.1506 | 151373.6864 | [13 empty] | 0 | 0
| Escondido | 203431.2316 | 121928.098 | 325359.3296 | [13 empty] | 0 | 0
| Fashion Valley | 28282.4774 | 16982.609 | 45265.0864 | [13 empty] | 0 | 0
| Friars | 30269.0864 | 20371.3117 | 50640.398 | [13 empty] | 0 | 0
| Main St. | 8746.7355 | 7666.9279 | 16413.6634 | [13 empty] | 0 | 0
| Mesa Rim | 74254.3006 | 55526.6452 | 129780.9458 | [13 empty] | 0 | 0
| Mission | 32441.3434 | 23992.6928 | 56434.0363 | [13 empty] | 0 | 0
| North City West | 96479.2733 | 49201.9852 | 145681.2584 | [13 empty] | 0 | 0
| Old Town | 25582.5134 | 12290.2734 | 37872.7868 | [13 empty] | 0 | 0
| Palomar Airport | 143556.2751 | 37740.1784 | 181296.4536 | [13 empty] | 0 | 0
| Penasquitos | 81522.3916 | 44597.6923 | 126120.084 | [13 empty] | 0 | 0
| San Luis Rey | 133892.5768 | 33713.6815 | 167606.2584 | [13 empty] | 0 | 0
| San Onofre | 23572.9517 | 62717.5171 | 86290.4688 | [13 empty] | 0 | 0
| Shadowridge | 174758.176 | 56678.4514 | 231436.6275 | [13 empty] | 0 | 0
| Silvergate | 8282.4579 | 7914.0333 | 16196.4912 | [13 empty] | 0 | 0
| Sycamore Canyon | 81712.499 | 110787.768 | 192500.267 | [13 empty] | 0 | 0
[18 empty] | 0 | 0
| KramerInyoOutsideTxConstraintZones | [16 empty] | 0 | 0
| Chino | 115236.3359 | 34277.8753 | 149514.2112 | [13 empty] | 0 | 0
| Etiwanda | 119521.0822 | 34143.9662 | 153665.0484 | [13 empty] | 0 | 0
| Mira Loma | 153868.1406 | 44776.7507 | 198644.8913 | [13 empty] | 0 | 0
| Padua | 103281.4096 | 37943.9349 | 141225.3445 | [13 empty] | 0 | 0
| Rancho Vista | 117868.9942 | 35516.3754 | 153385.3696 | [13 empty] | 0 | 0
| San Bernardino | 109189.6264 | 93582.3238 | 202771.9502 | [13 empty] | 0 | 0
| Soquel | 112556.4999 | 38097.3188 | 150653.8187 | [13 empty] | 0 | 0
| Vista | 154339.3024 | 71821.2363 | 226160.5387 | [13 empty] | 0 | 0
[18 empty] | 0 | 0
| Norcal_Z3_SacramentoRiver | [16 empty] | 0 | 0
| Carberry | 63074.3128 | 243737.7267 | 306812.0395 | [13 empty] | 0 | 0
| Delevan | 226931.429 | 151233.1065 | 378164.5356 | [13 empty] | 0 | 0
| Glenn | 312380.3423 | 98004.73 | 410385.0723 | [13 empty] | 0 | 0
| Hat Creek 2 | 136010.3823 | 217546.2146 | 353556.5969 | [13 empty] | 0 | 0
| Palermo | 214738.2962 | 187411.8637 | 402150.1599 | [13 empty] | 0 | 0
| Pit 1 | 141777.2142 | 214369.5514 | 356146.7657 | [13 empty] | 0 | 0
| Pit 1 Ph | 141554.7552 | 215092.9619 | 356647.7171 | [13 empty] | 0 | 0
| Rio Oso | 390290.7861 | 40333.9026 | 430624.6887 | [13 empty] | 0 | 0
| Table Mt. | 240287.3948 | 158423.4159 | 398710.8107 | [13 empty] | 0 | 0
| Thermalito | 249279.7572 | 157778.7081 | 407058.4653 | [13 empty] | 0 | 0
[18 empty] | 0 | 0
| Norcal_Z4_Solano | [16 empty] | 0 | 0
| Amerigas | 260413.6709 | 114394.6488 | 374808.3196 | [13 empty] | 0 | 0
| Bear Canyon | 117353.1805 | 203393.727 | 320746.9075 | [13 empty] | 0 | 0
| Big Geysers | 130672.7993 | 197241.7972 | 327914.5965 | [13 empty] | 0 | 0
| Calistoga 19 | 139609.4804 | 188704.0246 | 328313.5051 | [13 empty] | 0 | 0
| Calpeak Power Vaca Dixon 1 | 262551.2185 | 111982.5397 | 374533.7582 | [13 empty] | 0 | 0
| Castro Valley | 46178.7025 | 79406.8554 | 125585.5579 | [13 empty] | 0 | 0
| Cayetano | 116507.784 | 230435.0267 | 346942.8107 | [13 empty] | 0 | 0
| Cobb Creek | 146233.0272 | 181413.1069 | 327646.1341 | [13 empty] | 0 | 0
| Contra Costa | 200921.8609 | 142150.3168 | 343072.1777 | [13 empty] | 0 | 0
| Contra Costa Power | 210000.4144 | 136982.7775 | 346983.1919 | [13 empty] | 0 | 0
| Fulton | 167498.4994 | 182135.9074 | 349634.4069 | [13 empty] | 0 | 0
| Fumarole | 143276.331 | 186186.9032 | 329463.2343 | [13 empty] | 0 | 0
| Geysers Unit 3 | 143689.1321 | 184447.8953 | 328137.0274 | [13 empty] | 0 | 0
| Grant 20 | 139258.9193 | 192918.5383 | 332177.4576 | [13 empty] | 0 | 0
| Lake View | 156924.1896 | 171485.9075 | 328410.0971 | [13 empty] | 0 | 0
| Lakeville | 154619.4171 | 185621.2358 | 340240.6529 | [13 empty] | 0 | 0
| Lambie Energy | 239213.1528 | 117480.771 | 356693.9238 | [13 empty] | 0 | 0
| Lone Tree | 189537.5436 | 155953.7273 | 345491.2709 | [13 empty] | 0 | 0
| Mccabe | 143113.7335 | 185477.3419 | 328591.0754 | [13 empty] | 0 | 0
| N.N. | 449206.5858 | 549784.8816 | 998991.4674 | [13 empty] | 0 | 0
| Ncpa 1 & 2 | 123947.0021 | 205474.0457 | 329421.0479 | [13 empty] | 0 | 0
| Ncpa 3 & 4 | 121199.8005 | 206076.1177 | 327275.9182 | [13 empty] | 0 | 0
| Oakmont North | 172006.2238 | 168014.5395 | 340020.7633 | [13 empty] | 0 | 0
| Oakmont South | 178163.2055 | 164286.0515 | 342449.2571 | [13 empty] | 0 | 0
| Peabody | 208220.5506 | 151124.4904 | 359345.0409 | [13 empty] | 0 | 0
| Quicksilver | 124619.0788 | 201651.3827 | 326270.4615 | [13 empty] | 0 | 0
| San Ramon | 59665.4883 | 164536.9464 | 224202.4347 | [13 empty] | 0 | 0
| San Ramon Research Cntr. | 58453.2899 | 139042.1832 | 197495.4731 | [13 empty] | 0 | 0
| Shiloh II | 225035.404 | 123666.5318 | 348701.9359 | [13 empty] | 0 | 0
| Shiloh III | 223955.7302 | 124121.0506 | 348076.7808 | [13 empty] | 0 | 0
| Socrates 18 | 135799.7582 | 198058.0195 | 333857.7776 | [13 empty] | 0 | 0
| Sonoma 3 | 141347.4875 | 188616.9857 | 329964.4732 | [13 empty] | 0 | 0
| Sulphur Springs | 139885.3262 | 191618.038 | 331503.3642 | [13 empty] | 0 | 0
| Tassajara | 84879.4268 | 164186.7603 | 249066.1871 | [13 empty] | 0 | 0
| Technical Ecological Services | 58453.2899 | 138967.763 | 197421.0529 | [13 empty] | 0 | 0
| Trans Bay Cable | 169698.3246 | 134040.0136 | 303738.3382 | [13 empty] | 0 | 0
| Tulucay | 167010.6069 | 134029.5226 | 301040.1295 | [13 empty] | 0 | 0
| Vaca-Dixon & Gc Yard | 259967.5594 | 113942.9106 | 373910.47 | [13 empty] | 0 | 0
| West Ford Flat | 132006.477 | 192813.0644 | 324819.5414 | [13 empty] | 0 | 0
[18 empty] | 0 | 0
| Norcal_Z4_Solano_subzone | [16 empty] | 0 | 0
| Bahia | 89717.6016 | 122145.7596 | 211863.3612 | [13 empty] | 0 | 0
| Embarcadero (Sf Z) | 11281.9223 | 9586.7575 | 20868.6798 | [13 empty] | 0 | 0
| Ignacio | 97444.3114 | 129758.5219 | 227202.8334 | [13 empty] | 0 | 0
| Moraga | 39756.753 | 50910.0988 | 90666.8518 | [13 empty] | 0 | 0
| Parkway | 130355.1143 | 119287.6411 | 249642.7555 | [13 empty] | 0 | 0
| Pittsburg | 142317.3105 | 145503.8206 | 287821.131 | [13 empty] | 0 | 0
| Rossmoor | 57400.5593 | 90527.015 | 147927.5743 | [13 empty] | 0 | 0
| Sobrante | 34876.0698 | 49388.9096 | 84264.9794 | [13 empty] | 0 | 0
| Tidewater | 69222.6397 | 127137.4364 | 196360.0761 | [13 empty] | 0 | 0
| Unocal | 88845.2603 | 87790.2136 | 176635.474 | [13 empty] | 0 | 0
[18 empty] | 0 | 0
| NorCalOutsideTxConstraintZones | [16 empty] | 0 | 0
| Brighton | 191632.1015 | 60091.9943 | 251724.0959 | [13 empty] | 0 | 0
| Gold Hill | 129525.3865 | 192147.9308 | 321673.3173 | [13 empty] | 0 | 0
| Jefferson | 7653.7133 | 89704.2996 | 97358.0129 | [13 empty] | 0 | 0
| Logan Creek | 250598.194 | 139780.0319 | 390378.2259 | [13 empty] | 0 | 0
| Martin | 5969.6971 | 14049.8915 | 20019.5886 | [13 empty] | 0 | 0
| San Mateo | 9079.2625 | 37973.8466 | 47053.1091 | [13 empty] | 0 | 0
[18 empty] | 0 | 0
| SCADOutsideTxConstraintZones | [16 empty] | 0 | 0
| Cima | 0 | 8101.2618 | 8101.2618 | [13 empty] | 0 | 0
[18 empty] | 0 | 0
| SCADSNV_Z1_EldoradoAndMtnPass | [16 empty] | 0 | 0
| ElDorado | 0 | 0 | 0 | [13 empty] | 0 | 0
[18 empty] | 0 | 0
| SCADSNV_Z3_GreaterImperial |  |  |  | SCADSNV_Z3_GreaterImperial | [11 empty] | 356 | 0 | 0
| East County | 11024.5372 | 96155.6295 | 107180.1666 | East County | 11024.5372 | 96155.6295 |  | 0 | 0 | 1574.9339 | 13736.5185 | 0 | 0% | 0% | Greater_Imperial_Solar |  | 0 | 0
| Imperial Valley | 207772.1766 | 25482.8984 | 233255.075 | Imperial Valley | 207772.1766 | 25482.8984 | 233255.075 | 0.60793 | 33322.1536 | 29681.7395 | 3640.4141 | 216.4221 | 0.3948% | 0.7291% | Greater_Imperial_Solar |  | 0 | 0
| Ocotillo Express | 38327.3915 | 112106.6951 | 150434.0866 | Ocotillo Express | 38327.3915 | 112106.6951 | 150434.0866 | 0.39207 | 21490.5838 | 5475.3416 | 16015.2422 | 139.5779 | 0.2546% | 2.549% | Greater_Imperial_Solar |  | 0 | 0
| Suncrest | 14208.8214 | 224325.5091 | 238534.3305 | Suncrest | [12 empty] | 0 | 0
[5 empty] | Total |  |  | 383689.1616 |  | 54812.7374 | 35157.0812 | 19655.6562 | 356 |  |  |  |  | 0 | 0
[18 empty] | 0 | 0
| SCADSNV_Z4_RiversideAndPalmSprings |  |  |  | SCADSNV_Z4_RiversideAndPalmSprings | [12 empty] | 0 | 0
| Colorado River | 121669.3342 | 200351.3694 | 322020.7036 | Colorado River | 121669.3342 | 200351.3694 | 322020.7036 | 0.66247 | 46002.9577 | 17381.3335 | 28621.6242 | 0 | 0% | 0% | Riverside_Palm_Springs_Solar | 0 | 0 | 0
| Red Bluff | 51719.5818 | 112347.5969 | 164067.1787 | Red Bluff | 51719.5818 | 112347.5969 | 164067.1787 | 0.33753 | 23438.1684 | 7388.5117 | 16049.6567 | 0 | 0% | 0% | Riverside_Palm_Springs_Solar |  | 0 | 0
[5 empty] | Total |  |  | 486087.8823 |  | 69441.126 | 24769.8451 | 44671.2809 | [5 empty] | 0 | 0
| SCADSNV_Z5_SCADSNV | [16 empty] | 0 | 0
| Capacitor | 18967.9466 | 48994.843 | 67962.7896 | [13 empty] | 0 | 0
| Eagle Mt. | 47355.3448 | 84478.5763 | 131833.9211 | [13 empty] | 0 | 0
| Iron Mt. | 32233.3948 | 161416.1964 | 193649.5912 | [13 empty] | 0 | 0
| Julian Hinds | 9794.171 | 39712.1997 | 49506.3708 | [13 empty] | 0 | 0
| Los Coches | 45299.875 | 141878.3741 | 187178.2491 | [13 empty] | 0 | 0
| Miguel | 11515.3357 | 58209.2263 | 69724.562 | [13 empty] | 0 | 0
| Mohave | 252.3457 | 5822.8718 | 6075.2175 | [13 empty] | 0 | 0
| Otay Mesa | 7815.131 | 59710.2948 | 67525.4258 | [13 empty] | 0 | 0
| South Bay | 7191.9922 | 12576.9679 | 19768.9601 | [13 empty] | 0 | 0
[18 empty] | 0 | 0
| SPGE_Z1_Westlands |  |  |  | SPGE_Z1_Westlands | [11 empty] | 483 | 0 | 0
| Ashlan Ave. | 339741.7717 | 55625.8303 | 395367.602 | [13 empty] | 0 | 0
| Fig Garden | 325839.8294 | 67855.9079 | 393695.7373 | [13 empty] | 0 | 0
| Gates | 244790.1476 | 61943.4468 | 306733.5943 | Gates | 244790.1476 | 61943.4468 | 306733.5943 | 0.14423 | 43819.0849 | 34970.0211 | 8849.0638 | 69.6647 | 0.02293% | 0.1992% | Westlands_Solar |  | 0 | 0
| Gregg | 317053.4155 | 74590.2185 | 391643.6339 | [13 empty] | 0 | 0
| Helm | 351333.2811 | 7886.9101 | 359220.1912 | Helm | 351333.2811 | 7886.9101 | 359220.1912 | 0.16891 | 51317.1702 | 50190.4687 | 1126.7014 | 81.5854 | 0.02685% | 0.1626% | Westlands_Solar |  | 0 | 0
| Henrietta | 332147.2882 | 0 | 332147.2882 | Henrietta | 332147.2882 | 0 | 332147.2882 | 0.15618 | 47449.6126 | 47449.6126 | 0 | 75.4366 | 0.02483% | 0.159% | Westlands_Solar |  | 0 | 0
| Herndon | 323716.0747 | 66266.3941 | 389982.4687 | [13 empty] | 0 | 0
| Kearney (New) | 371486.0414 | 60.7305 | 371546.7719 | [13 empty] | 0 | 0
| Los Banos | 114225.5629 | 174190.3625 | 288415.9254 | [13 empty] | 0 | 0
| Mc Call | 409347.0596 | 5918.4196 | 415265.4792 | Mc Call | 409347.0596 | 5918.4196 | 415265.4792 | 0.19527 | 59323.6399 | 58478.1514 | 845.4885 | 94.3143 | 0.03104% | 0.1613% | Westlands_Solar |  | 0 | 0
| Mc Mullin | 386505.5976 | 648.197 | 387153.7946 | Mc Mullin | 386505.5976 | 648.197 | 387153.7946 | 0.18205 | 55307.6849 | 55215.0854 | 92.5996 | 87.9296 | 0.02894% | 0.1592% | Westlands_Solar |  | 0 | 0
| Oxford | 161974.2756 | 150132.069 | 312106.3446 | [13 empty] | 0 | 0
| Panoche | 208836.716 | 117290.9153 | 326127.6313 | Panoche | 208836.716 | 117290.9153 | 326127.6313 | 0.15335 | 46589.6616 | 29833.8166 | 16755.845 | 74.0694 | 0.02438% | 0.2483% | Westlands_Solar |  | 0 | 0
| San Luis | 108748.8872 | 201483.0001 | 310231.8873 | [13 empty] | 0 | 0
| San Luis 3 | 195956.321 | 128527.0548 | 324483.3759 | Total | 1932960.0901 | 193687.8887 | 2126647.9788 |  | 303806.8541 | 276137.1557 | 27669.6984 | 483 |  |  |  |  | 0 | 0
| San Luis 5 | 173321.3842 | 138034.6142 | 311355.9984 | [13 empty] | 0 | 0
| Wright | 138416.5448 | 143289.1497 | 281705.6945 | [13 empty] | 0 | 0
[18 empty] | 0 | 0
| SPGE_Z2_KernAndGreaterCarrizo |  |  |  | SPGE_Z2_KernAndGreaterCarrizo | [11 empty] | 3001 | 0 | 0
| Arco | 273894.9336 | 115184.61 | 389079.5436 | Arco | 273894.9336 | 115184.61 | 389079.5436 | 0.20625 | 55582.7919 | 39127.8477 | 16454.9443 | 618.9444 | 0.2297% | 1.582% | Kern_Greater_Carrizo_Solar |  | 0 | 0
| Buena Vista Pumps | 210937.6669 | 156404.3615 | 367342.0284 | Buena Vista Pumps | [12 empty] | 0 | 0
| Kern Power | 316543.5343 | 76163.7254 | 392707.2597 | Kern Power | [12 empty] | 0 | 0
| Midway | 275515.9004 | 100733.5 | 376249.4004 | Midway | 275515.9004 | 100733.5 | 376249.4004 | 0.19944 | 53749.9143 | 39359.4143 | 14390.5 | 598.5343 | 0.2221% | 1.521% | Kern_Greater_Carrizo_Solar |  | 0 | 0
| Renfro | 318206.2071 | 68185.7886 | 386391.9958 | Renfro | 318206.2071 | 68185.7886 | 386391.9958 | 0.20482 | 55198.8565 | 45458.0296 | 9740.8269 | 614.6691 | 0.2281% | 1.352% | Kern_Greater_Carrizo_Solar |  | 0 | 0
| Stockdale | 329570.6643 | 58200.378 | 387771.0423 | Stockdale | 329570.6643 | 58200.378 | 387771.0423 | 0.20555 | 55395.8632 | 47081.5235 | 8314.3397 | 616.8629 | 0.2289% | 1.31% | Kern_Greater_Carrizo_Solar |  | 0 | 0
| Wheeler Ridge | 238849.923 | 108140.4149 | 346990.3379 | Wheeler Ridge | 238849.923 | 108140.4149 | 346990.3379 | 0.18394 | 49570.0483 | 34121.4176 | 15448.6307 | 551.9893 | 0.2048% | 1.618% | Kern_Greater_Carrizo_Solar |  | 0 | 0
[5 empty] | Total | 1436037.6285 | 450444.6914 | 1886482.3199 |  |  |  |  | 3001 |  |  |  |  | 0 | 0
| SPGE_Z3_Carrizo |  |  |  | SPGE_Z3_Carrizo | [11 empty] | 600 | 0 | 0
| Caliente | 153856.6636 | 222592.8349 | 376449.4985 | Caliente | 153856.6636 | 222592.8349 | 376449.4985 | 0.33108 | 53778.4998 | 21979.5234 | 31798.9764 | 198.6507 | 0.3694% | 0.9038% | Carrizo_Solar |  | 0 | 0
| Mesa | 183463.2714 | 152282.0231 | 335745.2944 | Mesa | 183463.2714 | 152282.0231 | 335745.2944 | 0.29529 | 47963.6135 | 26209.0388 | 21754.5747 | 177.1713 | 0.3694% | 0.676% | Carrizo_Solar |  | 0 | 0
| Solar | 129612.6335 | 260323.1903 | 389935.8237 | [13 empty] | 0 | 0
| Templeton | 246398.0105 | 178426.6302 | 424824.6408 | Templeton | 246398.0105 | 178426.6302 | 424824.6408 | 0.37363 | 60689.2344 | 35199.7158 | 25489.5186 | 224.178 | 0.3694% | 0.6369% | Carrizo_Solar |  | 0 | 0
[6 empty] | 583717.9455 | 553301.4881 | 1137019.4337 | [9 empty] | 0 | 0
| SPGE_Z4_CentralValleyAndLosBanos | [15 empty] | 1327 | 0 | 0
| Bellota | 255519.9564 | 190398.795 | 445918.7514 | [13 empty] | 0 | 0
| Cottle | 244115.4368 | 184777.5408 | 428892.9777 | [13 empty] | 0 | 0
| Eight Mile | 361384.9129 | 26159.0407 | 387543.9536 | [13 empty] | 0 | 0
| Stagg | 361483.7987 | 19362.6578 | 380846.4565 | [13 empty] | 0 | 0
| Storey | 293286.0857 | 148690.1618 | 441976.2475 | [13 empty] | 0 | 0
| Weber | 390024.4437 | 7132.1547 | 397156.5984 | [13 empty] | 0 | 0
| Wilson | 221460.6649 | 144010.4955 | 365471.1604 | [13 empty] | 0 | 0
[18 empty] | 0 | 0
| Tehachapi |  |  |  | Tehachapi | [11 empty] | 4801 | 0 | 0
| Antelope | 283494.6086 | 91597.5112 | 375092.1198 | Antelope | 283494.6086 | 91597.5112 | 375092.1198 | 0.25986 | 53584.5885 | 40499.2298 | 13085.3587 | 1247.5935 | 0.605% | 3.081% | Tehachapi_Solar |  | 0 | 0
| Arbwind | 187469.0637 | 131236.3051 | 318705.3688 | Arbwind | [8 empty] | 0 |  |  |  | 0 | 0
| Bailey | 51084.6647 | 172593.7956 | 223678.4603 | Bailey | [8 empty] | 0 |  |  |  | 0 | 0
| Highwind | 177593.1111 | 122671.0948 | 300264.2058 | Highwind | [8 empty] | 0 |  |  |  | 0 | 0
| Mojave 17 | 219898.1683 | 123482.8752 | 343381.0436 | Mojave 17 | [8 empty] | 0 |  |  |  | 0 | 0
| N.N. | 449206.5858 | 549784.8816 | 998991.4674 | N.N. | [8 empty] | 0 |  |  |  | 0 | 0
| Pardee | 103540.6965 | 134265.1503 | 237805.8468 | Pardee | [8 empty] | 0 |  |  |  | 0 | 0
| Pearblossom | 161230.5478 | 175860.4673 | 337091.0151 | Pearblossom | 161230.5478 | 175860.4673 | 337091.0151 | 0.23353 | 48155.8593 | 23032.9354 | 25122.9239 | 1121.1981 | 0.5437% | 4.868% | Tehachapi_Solar |  | 0 | 0
| Saugus | 104148.9977 | 130389.4178 | 234538.4155 | Saugus | [8 empty] | 0 |  |  |  | 0 | 0
| Sky River North | 42559.4625 | 138617.3388 | 181176.8013 | Sky River North | [8 empty] | 0 |  |  |  | 0 | 0
| Vincent | 184408.9052 | 117262.3318 | 301671.237 | Vincent | [8 empty] | 0 |  |  |  | 0 | 0
| Warne | 33576.2089 | 158595.9827 | 192172.1916 | Warne | [8 empty] | 0 |  |  |  | 0 | 0
| Westwind | 219616.5744 | 124770.4984 | 344387.0727 | Westwind | [8 empty] | 0 |  |  |  | 0 | 0
| Whirlwind | 242518.5078 | 141802.2074 | 384320.7152 | Whirlwind | 242518.5078 | 141802.2074 | 384320.7152 | 0.26625 | 54902.9593 | 34645.5011 | 20257.4582 | 1278.2887 | 0.6199% | 3.69% | Tehachapi_Solar |  | 0 | 0
| Winderness | 224940.2791 | 119399.7675 | 344340.0466 | Winderness | [8 empty] | 0 |  |  |  | 0 | 0
| Windhub | 224363.6679 | 122565.196 | 346928.864 | Windhub | 224363.6679 | 122565.196 | 346928.864 | 0.24035 | 49561.2663 | 32051.9526 | 17509.3137 | 1153.9197 | 0.5596% | 3.6% | Tehachapi_Solar |  | 0 | 0
[5 empty] | Total | 911607.3321 | 531825.382 | 1443432.7141 |  |  |  |  | 13478 |  |  |  | 10965 | 0 | 0
| TehachapiOutsideTxConstraintZones | [16 empty] | 0 | 0
| Airchem | 0 | 0 | 0 | Mountain Pass and El Dorado/Southern_Nevada_Solar | [12 empty] | 0 | 0
| Arcogen | 0 | 0 | 0 | Crazy Eyes |  |  | 155787 | 0.61 | 22255.2857 |  |  | 1231 | 5.531% |  | SCADSNV_Solar |  | 0 | 0
| Cameron | 0 | 0 | 0 | Desert View |  |  | 42719 | 0.17 | 6102.7143 |  |  | 343 | 5.62% |  | SCADSNV_Solar |  | 0 | 0
| Casitas | 105110.5747 | 55297.4168 | 160407.9915 | Innovation |  |  | 54904 | 0.22 | 7843.4286 |  |  | 444 | 5.661% |  | SCADSNV_Solar |  | 0 | 0
| Center | 834.8357 | 0 | 834.8357 | El Dorado 230kV |  |  | 42263 | 1 | 6037.5714 |  |  | 1786 | 29.58% |  | Mountain_Pass_El_Dorado_Solar |  | 1 | 0
| Chevmain | 0 | 0 | 0 | [13 empty] | 0 | 0
| Del Amo | 0 | 0 | 0 | SCADSNV_Solar | [12 empty] | 0 | 0
| Eagle Rock | 89.8475 | 20648.2167 | 20738.0643 | Mohave 500kV |  |  | 28764 | 1 | 4109.1429 |  |  | 2475 | 60.23% |  | SCADSNV_Solar |  | 1 | 0
| El Nido | 0 | 0 | 0 | [13 empty] | 0 | 0
| El Segundo | 0 | 3.37 | 3.37 | [13 empty] | 0 | 0
| Federalgen | 0 | 0 | 0 | [13 empty] | 0 | 0
| Goodrich | 90.2923 | 23212.4228 | 23302.7151
| Gould | 3646.5285 | 48488.1105 | 52134.639
| Harborgen | 0 | 0 | 0
| Hinson | 0 | 0 | 0
| Kinetic | 0 | 0 | 0
| La Cienega | 60.4448 | 3.37 | 63.8147
| La Fresa | 0 | 0 | 0
| Laguna Bell | 0 | 0 | 0
| Lawndale | 0 | 0 | 0
| Lighthipe | 0 | 0 | 0
| Mandalay | 121907.7341 | 24738.7736 | 146646.5076
| Mesa | 183463.2714 | 152282.0231 | 335745.2944
| Moorpark | 175849.823 | 76091.5603 | 251941.3833
| N.N. | 449206.5858 | 549784.8816 | 998991.4674
| Olinda | 28973.3032 | 12098.187 | 41071.4902
| Ormond Beach | 110407.0725 | 14884.7 | 125291.7726
| Redondo 1 | 0 | 0 | 0
| Repro | 0 | 0 | 0
| Rio Hondo | 18154.1772 | 19395.3754 | 37549.5526
| Rosecrans | 0 | 0 | 0
| Santa Clara | 176304.6776 | 44572.428 | 220877.1056
| Stadium | 0 | 0 | 0
| Stanhill | 0 | 0 | 0
| Tahiti | 60.4448 | 13.3854 | 73.8302
| Venice Hydro | 60.4448 | 8.0744 | 68.5191
| Walnut | 26759.3165 | 8355.5954 | 35114.9118
| Windsor Hills | 0 | 0 | 0
WestlandsOutsideTxConstraintZones
| Coburn | 162720.8122 | 218556.7929 | 381277.605
| Diablo Canyon | 52516.4306 | 78414.7828 | 130931.2133
| Goleta | 50794.101 | 53728.8796 | 104522.9806
| Grand Total | 28058029.0728 | 21760032.2769 | 49818061.3496

## 3.2_SUM WIND RESOURCE ACRES2
Source: received CEC BUSBAR ALLOCATION_IRP 2020_SENSITIVITY2_v3.xlsx received 3/26
What constitutes level 3 criteria flag? |  |  | None
What constitutes level 2 criteria flag? |  |  | 20% |  | Exceeds this percentage utilization of available land in proximity to substation
What constitutes level 1 criteria flag? |  |  | All other
|  |  | Wind Project | ACRES_LOW | ACRES_HIGH | TOTAL_ACRES | Potential MW | MW Allocation | Percent of Total _MW | PROJECT ACRES | Percent of Acres_LOW |  | Criteria Threshold: Exceeds 20% (Total)? | Criteria Threshold: Exceeds 20% (Low)? | RESOLVE Resource | Aggregated RESOLVE Resource | Criteria Threshold: Exceeds 20% (Total)? | Criteria Threshold: Exceeds 20% (Low)?
| Carrizo Wind | [6 empty] | 287 |  |  |  |  | 0 | 0 | Carrizo_Wind | Carrizo_Wind | 2 | 2
|  | Templeton | Wind 124 | 6729.9534 | 24299.8298 | 31029.7832 | 288 |  | 99.65% | 11480 | 170.6% |  | 1 | 1 | Carrizo_Wind | Central_Valley_North_Los_Banos_Wind | 2 | 2
[13 empty] | 0 | 0 |  | Humboldt_Wind | 2 | 2 | No low value land
| Central Valley and North Los Banos Wind | [6 empty] | 173 |  |  |  |  | 0 | 0 | Central_Valley_North_Los_Banos_Wind | Kern_Greater_Carrizo_Wind | 2 | 2
|  | Los Banos | Wind 112 | 16166.129 | 23407.3429 | 39573.472 | 170 |  | 101.8% | 6920 | 42.81% |  | 1 | 1 | Central_Valley_North_Los_Banos_Wind | Northern_California_Ex_Wind | 2 | 1
[13 empty] | 0 | 0 |  | Solano_Wind | 2 | 2
| Humboldt Wind | [6 empty] | 34 |  |  |  |  | 0 | 0 | Humboldt_Wind | Tehachapi_Wind | 2 | 1
|  | Bridgeville | Wind 7 | 0 | 11414.6331 | 11414.6331 | 34 |  | 50.75% | 5022.2 |  |  | 1 | 0 | Humboldt_Wind
|  |  | Wind 8 | 0 | 11355.8557 | 11356.3005 | 33 |  | 49.25% | 4837.3 |  |  | 1 | 0 | Humboldt_Wind
|  |  |  | 0 | 22770.4889 | 22770.9337 | 67 |  |  | 1360 | #DIV/0! | No Low Value ACRES | 0 | #DIV/0! | Humboldt_Wind
[13 empty] | 0 | 0
| Kern Greater Carrizo Wind | [6 empty] | 60 |  |  |  |  | 0 | 0 | Kern_Greater_Carrizo_Wind
|  | Cholame | Wind 207 | 11176.1755 | 9449.3403 | 20625.5157 | 69 |  | 86.96% | 2400 | 21.47% |  | 1 | 1 | Kern_Greater_Carrizo_Wind
[13 empty] | 0 | 0
| Sacramento Valley Wind | [6 empty] | 866 |  |  |  |  | 0 | 0 | Northern_California_Ex_Wind
|  | Glenn | Wind 34 | 21839.4351 | 0 | 21839.4351 | 120 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 35 | 32087.1942 | 0 | 32087.1942 | 166 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 36 | 27505.3046 | 1796.0503 | 29301.3548 | 149 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 37 | 25021.9988 | 3740.2999 | 28762.2988 | 168 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 38 | 13114.3746 | 16735.7764 | 29850.1511 | 157 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 39 | 25914.2428 | 7966.2534 | 33880.4961 | 166 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 40 | 20908.7046 | 8987.8427 | 29896.5473 | 166 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 42 | 31674.5459 | 1332.0413 | 33006.5872 | 183 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 43 | 21329.2313 | 11015.7038 | 32344.9351 | 183 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 50 | 17028.3306 | 12467.3163 | 29495.647 | 166 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 51 | 33870.1339 | 247.1054 | 34117.2393 | 163 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 204 | 13663.4689 | 0 | 13663.4689 | 69 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  |  | 283956.9655 | 64288.3895 | 348245.355 | 1856 | 400 | 21.55% | 16000 | 5.635% |  | 1 | 0 | Northern_California_Ex_Wind
|  | Delevan | [10 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 31 | 6084.8094 | 1282.7612 | 7367.5707 | 38 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 32 | 31202.9317 | 2641.358 | 33844.2897 | 175 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 33 | 29015.8768 | 0 | 29015.8768 | 222 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  |  | 66303.6179 | 3924.1192 | 70227.7371 | 435 | 94 | 21.61% | 3760 | 5.671% |  | 1 | 0 | Northern_California_Ex_Wind
|  | Thermalito | [10 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 52 | 32608.7529 | 0 | 32608.7529 | 182 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 53 | 29609.2617 | 0 | 29609.2617 | 172 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 54 | 30953.4561 | 377.0251 | 31330.4812 | 174 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 55 | 23422.0305 | 0 | 23422.0305 | 138 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 56 | 31228.9783 | 633.892 | 31862.8703 | 172 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 202 | 16889.0583 | 0 | 16889.0583 | 96 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  |  | 164711.5378 | 1010.9171 | 165722.4549 | 934 | 201 | 21.52% | 8040 | 4.881% |  | 1 | 0 | Northern_California_Ex_Wind
|  | Rio Oso | [10 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 62 | 30714.3441 | 0 | 30714.3441 | 176 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 73 | 29002.0732 | 0 | 29002.0732 | 172 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 77 | 35294.3904 | 0 | 35294.3904 | 181 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 78 | 30267.3127 | 0 | 30267.3127 | 160 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 79 | 20227.9346 | 0 | 20227.9346 | 107 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  |  | 145506.0551 | 0 | 145506.0551 | 796 | 171 | 21.48% | 6840 | 4.701% |  | 1 | 0 | Northern_California_Ex_Wind
[13 empty] | 0 | 0
| Solano Wind | [11 empty] | 0 | 0 | Solano_Wind
|  | Lakeville | Wind 198 | 2361.3656 | 15002.7991 | 17364.1647 | 71 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 101 | 2393.1548 | 29048.7635 | 31441.9184 | 166 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 102 | 7207.3104 | 8590.8881 | 15798.1985 | 70 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 196 | 2948.0119 | 31570.5233 | 34518.5353 | 146 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 197 | 4625.9771 | 26007.4994 | 30633.4765 | 117 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 199 | 4046.7783 | 26316.1556 | 30362.9339 | 136 | [5 empty] | 0 | 0 | Solano_Wind
|  |  |  | 23582.5981 | 136536.6291 | 160119.2272 | 706 | 227 | 32.15% | 9080 | 38.5% |  | 1 | 1 | Solano_Wind
|  | Tulucay | [10 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 103 | 3479.2106 | 13204.9372 | 16684.1477 | 22 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 106 | 5958.7606 | 19351.3274 | 25310.088 | 50 | [5 empty] | 0 | 0 | Solano_Wind
|  |  |  | 9437.9712 | 32556.2646 | 41994.2357 | 72 | 23 | 31.94% | 920 | 9.748% |  | 1 | 0 | Solano_Wind
|  | Vaca-Dixon & GC Yard | [10 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 80 | 11733.2651 | 20668.7168 | 32401.9819 | 86 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 81 | 23098.3902 | 11485.509 | 34583.8992 | 114 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 82 | 30872.3849 | 0 | 30872.3849 | 77 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 83 | 34973.0826 | 573.8062 | 35546.8888 | 80 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 84 | 32773.4554 | 3679.007 | 36452.4624 | 89 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 85 | 29812.5532 | 6243.4009 | 36055.9541 | 85 | [5 empty] | 0 | 0 | Solano_Wind
|  |  |  | 163263.1314 | 42650.4398 | 205913.5713 | 531 | 171 | 32.2% | 6840 | 4.19% |  | 1 | 0 | Solano_Wind
|  | Shilo III | [10 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 91 | 28653.8156 | 5619.5354 | 34273.3509 | 82 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 206 | 10020.747 | 4704.6326 | 14725.3796 | 34 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 88 | 38048.726 | 3368.0093 | 41416.7354 | 88 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 90 | 22115.5238 | 689.4769 | 22805.0007 | 57 | [5 empty] | 0 | 0 | Solano_Wind
|  |  |  | 98838.8124 | 14381.6542 | 113220.4666 | 261 | 84 | 32.18% | 3360 | 3.399% |  | 1 | 0 | Solano_Wind
|  | Lone Tree | [10 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 104 | 5792.3906 | 16974.6621 | 22767.0528 | 35 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 107 | 15567.8983 | 23209.4731 | 38777.3714 | 79 | [5 empty] | 0 | 0 | Solano_Wind
|  |  |  | 21360.289 | 40184.1352 | 61544.4242 | 114 | 37 | 32.46% | 1480 | 6.929% |  | 1 | 0 | Solano_Wind
[13 empty] | 0 | 0
| Tehachapi Wind | [11 empty] | 0 | 0 | Tehachapi_Wind
|  | Windhub | Wind 129 | 13670.7998 | 16116.6015 | 29787.4013 | 128 | [5 empty] | 0 | 0 | Tehachapi_Wind
|  |  | Wind 156 | 12435.83 | 922.2979 | 13358.1279 | 86 | [5 empty] | 0 | 0 | Tehachapi_Wind
|  |  | Wind 157 | 30641.6782 | 1300.9199 | 31942.5981 | 138 | [5 empty] | 0 | 0 | Tehachapi_Wind
|  |  |  | 56748.308 | 18339.8193 | 75088.1273 | 352 | 275 | 78.12% | 11000 | 19.38% |  | 1 | 0 | Tehachapi_Wind

## 4_CommercialInterest
What constitutes level 3 criteria flag? |  | 300 | MW | Model selection 300 MW or more, in absence of any commercial interest
|  | 3000 | MW | Difference from commercial interest
What constitutes level 2 criteria flag? |  | 2000 | MW or greater | Difference from commercial interest
What constitutes level 1 criteria flag? |  | All other
| Summary of Commercial Interest (Interconnection Queue / Zones Intersection) |  |  |  | Summary of Selected Portfolio (new RSP) | Selected by RESOLVE (30MMTEO2) | Selected by RESOLVE (30MMTEO2 adj) | Zone | Technology | Commercial Interest, Summarized by RESOLVE Resource | Difference (Selected Portfolio) - (Commercial Interest) | Selected Portfolio, as Percent of Queue | Boolean: significant model selection in absence of commercial interest | Mapping criteria compliance level | Difference (Adjusted Selected Portfolio) - (Commercial Interest) | Selected Portfolio, as Percent of Queue | Boolean: significant model selection in absence of commercial interest | Mapping criteria compliance level
|  | Row Labels | Sum of MW-1 |  | InState_Biomass | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| 0 | 0 | 3204.733 |  | Greater_Imperial_Geothermal | 716.46 | 716.46 | SCADSNV_Z3_GreaterImperial | Geothermal | 100 | 616.46 | 716.5% | 0 | 1 | 616.46 | 716.5% | 0 | 1
| 0 | Photovoltaic | 1102.265 |  | Inyokern_North_Kramer_Geothermal | 0 | 0 | GK_Z2_InyokernAndNorthOfKramer |  | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1
| 0 | Storage | 1571.848 |  | Northern_California_Ex_Geothermal | 0 | 0 | NorCalOutsideTxConstraintZones | Geothermal | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1
| 0 | Wind Turbine | 530.62 |  | Pacific_Northwest_Geothermal | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0
| GK_Z2_InyokernAndNorthOfKramer | GK_Z2_InyokernAndNorthOfKramer | 1300.5 |  | Riverside_Palm_Springs_Geothermal | 0 | 0 | SCADSNV_Z4_RiversideAndPalmSprings | Geothermal | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1
| GK_Z2_InyokernAndNorthOfKramer | Photovoltaic | 824.26 |  | Solano_Geothermal | 135 | 135 | Norcal_Z4_Solano | Geothermal | 0 | 135 | No commercial interest; 135 MW selected | 0 | 1 | 135 | No commercial interest; 135 MW selected | 0 | 1
| GK_Z2_InyokernAndNorthOfKramer | Storage | 476.24 |  | Southern_Nevada_Geothermal | 0 | 0 | SCADSNV_Z1_EldoradoAndMtnPass |  | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1
| GK_Z3_NorthOfVictor | GK_Z3_NorthOfVictor | 320.92 |  | Carrizo_Solar | 600 | 600 | SPGE_Z3_Carrizo | Photovoltaic | 0 | 600 | No commercial interest; 600 MW selected | 1 | 3 | 600 | No commercial interest; 600 MW selected | 1 | 3
| GK_Z3_NorthOfVictor | Photovoltaic | 210.88 |  | Carrizo_Wind | 287 | 287 | SPGE_Z3_Carrizo | Wind Turbine | 0 | 287 | No commercial interest; 287 MW selected | 0 | 1 | 287 | No commercial interest; 287 MW selected | 0 | 1
| GK_Z3_NorthOfVictor | Storage | 110.04 |  | Central_Valley_North_Los_Banos_Solar | 0 | 0 | SPGE_Z4_CentralValleyAndLosBanos | Photovoltaic | 298.35 | -298.35 | 0% | 0 | 1 | -298.35 | 0% | 0 | 1
| GreaterImpOutsideTxConstraintZones | GreaterImpOutsideTxConstraintZones | 1319.1 |  | Central_Valley_North_Los_Banos_Wind | 173 | 173 | SPGE_Z4_CentralValleyAndLosBanos | Wind Turbine | 0 | 173 | No commercial interest; 173 MW selected | 0 | 1 | 173 | No commercial interest; 173 MW selected | 0 | 1
| GreaterImpOutsideTxConstraintZones | Storage | 1319.1 |  | Distributed_Solar | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0
| KramerInyoOutsideTxConstraintZones | KramerInyoOutsideTxConstraintZones | 511.18 |  | Distributed_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0
| KramerInyoOutsideTxConstraintZones | Storage | 511.18 |  | Greater_Imperial_Solar | 866.98 | 355.98 | SCADSNV_Z3_GreaterImperial | Photovoltaic | 3050.58 | -2183.6 | 28.42% | 0 | 2 | -2694.6 | 11.67% | 0 | 2
| Norcal_Z2_Humboldt | Norcal_Z2_Humboldt | 348.1 |  | Greater_Imperial_Wind | 0 | 0 | SCADSNV_Z3_GreaterImperial | Wind Turbine | 1715.3 | -1715.3 | 0% | 0 | 1 | -1715.3 | 0% | 0 | 1
| Norcal_Z2_Humboldt | Storage | 50.875 |  | Greater_Kramer_Wind | 0 | 0 | GK_Z1_GreaterKramer | Wind Turbine | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1
| Norcal_Z2_Humboldt | Wind Turbine | 297.225 |  | Humboldt_Wind | 34 | 34 | Norcal_Z2_Humboldt | Wind Turbine | 297.225 | -263.225 | 11.44% | 0 | 1 | -263.225 | 11.44% | 0 | 1
| Norcal_Z3_SacramentoRiver | Norcal_Z3_SacramentoRiver | 522 |  | Inyokern_North_Kramer_Solar | 97 | 97 | GK_Z2_InyokernAndNorthOfKramer | Photovoltaic | 824.26 | -727.26 | 11.77% | 0 | 1 | -727.26 | 11.77% | 0 | 1
| Norcal_Z3_SacramentoRiver | Photovoltaic | 12 |  | Kern_Greater_Carrizo_Solar | 3001.27 | 3001.27 | SPGE_Z2_KernAndGreaterCarrizo | Photovoltaic | 1898.196 | 1103.074 | 158.1% | 0 | 1 | 1103.074 | 158.1% | 0 | 1
| Norcal_Z3_SacramentoRiver | Storage | 510 |  | Kern_Greater_Carrizo_Wind | 60 | 60 | SPGE_Z2_KernAndGreaterCarrizo | Wind Turbine | 1030.2 | -970.2 | 5.824% | 0 | 1 | -970.2 | 5.824% | 0 | 1
| Norcal_Z4_Solano | Norcal_Z4_Solano | 1164.104 |  | Kramer_Inyokern_Ex_Solar | 0 | 0 | KramerInyoOutsideTxConstraintZones | Photovoltaic | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1
| Norcal_Z4_Solano | Photovoltaic | 431.4 |  | Kramer_Inyokern_Ex_Wind | 0 | 0 | KramerInyoOutsideTxConstraintZones | Wind Turbine | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1
| Norcal_Z4_Solano | Storage | 299 |  | Mountain_Pass_El_Dorado_Solar | 248 | 248 | SCADSNV_Z1_EldoradoAndMtnPass | Photovoltaic | 300 | -52 | 82.67% | 0 | 1 | -52 | 82.67% | 0 | 1
| Norcal_Z4_Solano | Wind Turbine | 433.704 |  | North_Victor_Solar | 300 | 300 | GK_Z3_NorthOfVictor | Photovoltaic | 210.88 | 89.12 | 142.3% | 0 | 1 | 89.12 | 142.3% | 0 | 1
| Norcal_Z4_Solano_subzone | Norcal_Z4_Solano_subzone | 120.4 |  | Northern_California_Ex_Solar | 0 | 0 | NorCalOutsideTxConstraintZones | Photovoltaic | 20.6 | -20.6 | 0% | 0 | 1 | -20.6 | 0% | 0 | 1
| Norcal_Z4_Solano_subzone | Storage | 120.4 |  | Northern_California_Ex_Wind | 865.9 | 865.9 | NorCalOutsideTxConstraintZones | Wind Turbine | 1774 | -908.1 | 48.81% | 0 | 1 | -908.1 | 48.81% | 0 | 1
| NorCalOutsideTxConstraintZones | NorCalOutsideTxConstraintZones | 1996.155 |  | NW_Ext_Tx_Wind | 1500 | 1500 | Norcal_Z3_SacramentoRiver |  | 0 | 1500 | No commercial interest; 1500 MW selected | 1 | 3 | 1500 | No commercial interest; 1500 MW selected | 1 | 3
| NorCalOutsideTxConstraintZones | Hydro | 5 |  | Riverside_Palm_Springs_Solar | 0 | 29 | SCADSNV_Z4_RiversideAndPalmSprings | Photovoltaic | 2182 | -2182 | 0% | 0 | 2 | -2153 | 1.329% | 0 | 2
| NorCalOutsideTxConstraintZones | Photovoltaic | 20.6 |  | Riverside_Palm_Springs_Wind | 0 | 0 | SCADSNV_Z4_RiversideAndPalmSprings | Wind Turbine | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1
| NorCalOutsideTxConstraintZones | Steam Turbine | 5.5 |  | Sacramento_River_Solar | 0 | 0 | Norcal_Z3_SacramentoRiver | Photovoltaic | 12 | -12 | 0% | 0 | 1 | -12 | 0% | 0 | 1
| NorCalOutsideTxConstraintZones | Storage | 191.055 |  | Sacramento_River_Wind | 0 | 0 | Norcal_Z3_SacramentoRiver | Wind Turbine | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1
| NorCalOutsideTxConstraintZones | Wind Turbine | 1774 |  | SCADSNV_Solar | 1970 | 4303 | SCADSNV_Z5_SCADSNV | Photovoltaic | 2000.104 | -30.104 | 98.49% | 0 | 1 | 2302.896 | 215.1% | 0 | 2
| SCADSNV_Z3_GreaterImperial | SCADSNV_Z3_GreaterImperial | 7194.91 |  | SCADSNV_Wind | 0 | 0 | SCADSNV_Z5_SCADSNV | Wind Turbine | 310 | -310 | 0% | 0 | 1 | -310 | 0% | 0 | 1
| SCADSNV_Z3_GreaterImperial | Photovoltaic | 3050.58 |  | Solano_Solar | 0 | 0 | Norcal_Z4_Solano | Photovoltaic | 431.4 | -431.4 | 0% | 0 | 1 | -431.4 | 0% | 0 | 1
| SCADSNV_Z3_GreaterImperial | Storage | 2429.03 |  | Solano_subzone_Solar | 0 | 0 | Norcal_Z4_Solano_subzone | Photovoltaic | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1
| SCADSNV_Z3_GreaterImperial | Wind Turbine | 1715.3 |  | Solano_subzone_Wind | 0 | 0 | Norcal_Z4_Solano_subzone | Wind Turbine | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1
| SCADSNV_Z4_RiversideAndPalmSprings | SCADSNV_Z4_RiversideAndPalmSprings | 8249.732 |  | Solano_Wind | 542 | 542 | Norcal_Z4_Solano | Wind Turbine | 433.704 | 108.296 | 125% | 0 | 1 | 108.296 | 125% | 0 | 1
| SCADSNV_Z4_RiversideAndPalmSprings | Photovoltaic | 4777.38 |  | Southern_California_Desert_Ex_Solar | 862 | 0 | SCADOutsideTxConstraintZones | Photovoltaic | 0 | 862 | No commercial interest; 862 MW selected | 1 | 3 | 0 | No commercial interest; 862 MW selected | 0 | 1
| SCADSNV_Z4_RiversideAndPalmSprings | Steam Turbine | 49.5 |  | Southern_California_Desert_Ex_Wind | 0 | 0 | SCADOutsideTxConstraintZones | Wind Turbine | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1
| SCADSNV_Z4_RiversideAndPalmSprings | Storage | 3422.852 |  | Southern_Nevada_Solar | 1470 | 1727 | SCADSNV_Z2_GLW_VEA | Photovoltaic | 0 | 1470 | No commercial interest; 1470 MW selected | 1 | 3 | 1727 | No commercial interest; 1470 MW selected | 1 | 3
| SCADSNV_Z5_SCADSNV | SCADSNV_Z5_SCADSNV | 3992.664 |  | Southern_Nevada_Wind | 442.03 | 442.03 | SCADSNV_Z2_GLW_VEA |  | 0 | 442.03 | No commercial interest; 442.03 MW selected | 1 | 3 | 442.03 | No commercial interest; 442.03 MW selected | 1 | 3
| SCADSNV_Z5_SCADSNV | Photovoltaic | 2000.104 |  | SW_Ext_Tx_Wind | 500 | 500 | SCADSNV_Z4_RiversideAndPalmSprings |  | 0 | 500 | No commercial interest; 500 MW selected | 1 | 3 | 500 | No commercial interest; 500 MW selected | 1 | 3
| SCADSNV_Z5_SCADSNV | Storage | 1682.56 |  | Tehachapi_Solar | 4801 | 4801 | Tehachapi | Photovoltaic | 4697.9116 | 103.0884 | 102.2% | 0 | 1 | 103.0884 | 102.2% | 0 | 1
| SCADSNV_Z5_SCADSNV | Wind Turbine | 310 |  | Tehachapi_Ex_Solar | 0 | 0 | TehachapiOutsideTxConstraintZones | Photovoltaic | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 | 0 | No commercial interest; 0 MW selected | 0 | 1
| SPGE_Z1_Westlands | SPGE_Z1_Westlands | 7402.177 |  | Tehachapi_Wind | 275 | 275 | Tehachapi | Wind Turbine | 728.66 | -453.66 | 37.74% | 0 | 1 | -453.66 | 37.74% | 0 | 1
| SPGE_Z1_Westlands | Combined Cycle | 60 |  | Westlands_Ex_Solar | 1778.57 | -0.43 | WestlandsOutsideTxConstraintZones | Photovoltaic | 604.239 | 1174.331 | 294.3% | 0 | 1 | -604.669 | -0.07116% | 0 | 1
| SPGE_Z1_Westlands | Gas Turbine | 63 |  | Westlands_Ex_Wind | 0 | 0 | WestlandsOutsideTxConstraintZones | Wind Turbine | 1568 | -1568 | 0% | 0 | 1 | -1568 | 0% | 0 | 1
| SPGE_Z1_Westlands | Photovoltaic | 5245.997 |  | Westlands_Solar | 633.68 | 1957.68 | SPGE_Z4_CentralValleyAndLosBanos | Photovoltaic | 298.35 | 335.33 | 212.4% | 0 | 1 | 1659.33 | 656.2% | 0 | 1
| SPGE_Z1_Westlands | Storage | 1953.18 |  | Cape_Mendocino_Offshore_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0
| SPGE_Z1_Westlands | Wind Turbine | 80 |  | Del_Norte_Offshore_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0
| SPGE_Z2_KernAndGreaterCarrizo | SPGE_Z2_KernAndGreaterCarrizo | 4025.666 |  | Diablo_Canyon_Offshore_Wind_Ext_Tx | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0
| SPGE_Z2_KernAndGreaterCarrizo | Photovoltaic | 1898.196 |  | Diablo_Canyon_Offshore_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0
| SPGE_Z2_KernAndGreaterCarrizo | Storage | 1097.27 |  | Humboldt_Bay_Offshore_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0
| SPGE_Z2_KernAndGreaterCarrizo | Wind Turbine | 1030.2 |  | Morro_Bay_Offshore_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0
| SPGE_Z4_CentralValleyAndLosBanos | SPGE_Z4_CentralValleyAndLosBanos | 1114.986 |  | Utah_Solar | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0
| SPGE_Z4_CentralValleyAndLosBanos | Photovoltaic | 298.35 |  | Arizona_Solar | 2140.97 | 1349.97 | SCADSNV_Z4_RiversideAndPalmSprings | Photovoltaic | 2595 | -454.03 | 82.5% | 0 | 1 | -1245.03 | 52.02% | 0 | 1
| SPGE_Z4_CentralValleyAndLosBanos | Storage | 816.636 |  | New_Mexico_Solar | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0
| Tehachapi | Tehachapi | 8631.4016 |  | Baja_California_Solar | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0
| Tehachapi | Photovoltaic | 4697.9116 |  | Baja_California_Wind | 600 | 600 | SCADSNV_Z3_GreaterImperial | Wind Turbine | 556 | 44 | 107.9% | 0 | 1 | 44 | 107.9% | 0 | 1
| Tehachapi | Storage | 3204.83 |  | Pacific_Northwest_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0
| Tehachapi | Wind Turbine | 728.66 |  | Idaho_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0
| TehachapiOutsideTxConstraintZones | TehachapiOutsideTxConstraintZones | 2528.65 |  | Utah_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0
| TehachapiOutsideTxConstraintZones | Storage | 2528.65 |  | Wyoming_Wind | 1500 | 1500 | SCADSNV_Z1_EldoradoAndMtnPass |  | 0 | 1500 | No commercial interest; 1500 MW selected | 1 | 3 | 1500 | No commercial interest; 1500 MW selected | 1 | 3
| WestlandsOutsideTxConstraintZones | WestlandsOutsideTxConstraintZones | 3424.35 |  | Arizona_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  | No commercial interest; MW selected | 0
| WestlandsOutsideTxConstraintZones | Storage | 1856.35 |  | New_Mexico_Wind | 1500 | 1500 | SCADSNV_Z4_RiversideAndPalmSprings | Wind Turbine | 0 | 1500 | No commercial interest; 1500 MW selected | 1 | 3 | 1500 | No commercial interest; 1500 MW selected | 1 | 3
| WestlandsOutsideTxConstraintZones | Wind Turbine | 1568 |  | Pumped Storage Hydro | 0 | 1216 | GreaterImpOutsideTxConstraintZones | Storage | 1319.1 | -1319.1 | 0% | 0 | 1 | -103.1 | 92.18% | 0 | 1
| WestlandsOutsideTxConstraintZones | #N/A | 1379.889 |  | Pumped Storage Hydro | 0 | 1582 | SCADSNV_Z4_RiversideAndPalmSprings | Storage | 3422.852 | -3422.852 | 0% | 0 | 3 | -1840.852 | 46.22% | 0 | 1
| WestlandsOutsideTxConstraintZones | Combined Cycle | 35 |  |  | 27899.86 | 27899.86
| WestlandsOutsideTxConstraintZones | Photovoltaic | 604.239
| WestlandsOutsideTxConstraintZones | Storage | 740.65
| SPGE_Z3_Carrizo | SPGE_Z3_Carrizo | 606.2
| SPGE_Z3_Carrizo | Storage | 606.2
| None | None | 4336.85
| None | Storage | 4336.85
| Outside | Outside | 1512.6
| Outside | Storage | 1512.6
| GK_Z4_Pisgah | GK_Z4_Pisgah | 302.85
| GK_Z4_Pisgah | Photovoltaic | 302.85
| GK_Z1_GreaterKramer | GK_Z1_GreaterKramer | 156
| GK_Z1_GreaterKramer | Photovoltaic | 156
| SCADSNV_Z1_EldoradoAndMtnPass | SCADSNV_Z1_EldoradoAndMtnPass | 900
| SCADSNV_Z1_EldoradoAndMtnPass | Photovoltaic | 300
| SCADSNV_Z1_EldoradoAndMtnPass | Storage | 600
|  | Grand Total | 66566.1176
Note on I33: Emily Leslie: departed from RESOLVE tx zone assignments, portfolio analytics tab, for better spatial match to queue substations
Note on L35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Note this is manually disentangled from resources physically located in AZ, with queue POI specified in Riverside Palm Springs zone
Note on R35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Note this is manually disentangled from resources physically located in AZ, with queue POI specified in Riverside Palm Springs zone
Note on L47: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Note: not found in queue, but this may be due to data structure, not lack of interest.
Note on L48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Note: not found in queue, but this may be due to data structure, not lack of interest.
Note on L63: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sumarized manually by state in queue spreadsheet, to distentangle overlap with other zones (RiversidePalm Springs and Greater Imperial)
Note on R63: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sumarized manually by state in queue spreadsheet, to distentangle overlap with other zones (RiversidePalm Springs and Greater Imperial)
Note on L66: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Summarized manually by county in queue spreadsheet, to distentangle overlap with other zones (Greater Imperial)
Note on R66: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Summarized manually by county in queue spreadsheet, to distentangle overlap with other zones (Greater Imperial)

## 4b_QueuePivotTable
Source: PublicQueueReport_2019-12-04_matchedToZones_iso.xlsx
Row Labels | Sum of MW-1
0 | 3204.733
Photovoltaic | 1102.265
Storage | 1571.848
Wind Turbine | 530.62
GK_Z2_InyokernAndNorthOfKramer | 1300.5
Photovoltaic | 824.26
Storage | 476.24
GK_Z3_NorthOfVictor | 320.92
Photovoltaic | 210.88
Storage | 110.04
GreaterImpOutsideTxConstraintZones | 1319.1
Storage | 1319.1
KramerInyoOutsideTxConstraintZones | 511.18
Storage | 511.18
Norcal_Z2_Humboldt | 348.1
Storage | 50.875
Wind Turbine | 297.225
Norcal_Z3_SacramentoRiver | 522
Photovoltaic | 12
Storage | 510
Norcal_Z4_Solano | 1164.104
Photovoltaic | 431.4
Storage | 299
Wind Turbine | 433.704
Norcal_Z4_Solano_subzone | 120.4
Storage | 120.4
NorCalOutsideTxConstraintZones | 1996.155
Hydro | 5
Photovoltaic | 20.6
Steam Turbine | 5.5
Storage | 191.055
Wind Turbine | 1774
SCADSNV_Z3_GreaterImperial | 7194.91
Photovoltaic | 3050.58
Storage | 2429.03
Wind Turbine | 1715.3
SCADSNV_Z4_RiversideAndPalmSprings | 8249.732
Photovoltaic | 4777.38
Steam Turbine | 49.5
Storage | 3422.852
SCADSNV_Z5_SCADSNV | 3992.664
Photovoltaic | 2000.104
Storage | 1682.56
Wind Turbine | 310
SPGE_Z1_Westlands | 7402.177
Combined Cycle | 60
Gas Turbine | 63
Photovoltaic | 5245.997
Storage | 1953.18
Wind Turbine | 80
SPGE_Z2_KernAndGreaterCarrizo | 4025.666
Photovoltaic | 1898.196
Storage | 1097.27
Wind Turbine | 1030.2
SPGE_Z4_CentralValleyAndLosBanos | 1114.986
Photovoltaic | 298.35
Storage | 816.636
Tehachapi | 8631.4016
Photovoltaic | 4697.9116
Storage | 3204.83
Wind Turbine | 728.66
TehachapiOutsideTxConstraintZones | 2528.65
Storage | 2528.65
WestlandsOutsideTxConstraintZones | 3424.35
Storage | 1856.35
Wind Turbine | 1568
#N/A | 1379.889
Combined Cycle | 35
Photovoltaic | 604.239
Storage | 740.65
SPGE_Z3_Carrizo | 606.2
Storage | 606.2
None | 4336.85
Storage | 4336.85
Outside | 1512.6
Storage | 1512.6
GK_Z4_Pisgah | 302.85
Photovoltaic | 302.85
GK_Z1_GreaterKramer | 156
Photovoltaic | 156
SCADSNV_Z1_EldoradoAndMtnPass | 900
Photovoltaic | 300
Storage | 600
Grand Total | 66566.1176

## BUSBAR ALLOC_Adj_TPPFeb2020
Source: CEC BUSBAR ALLOCATION_IRP 2020_PSP_02212020.xlsx
2018 PSP with Baseline Reconciliation and Norcal Geo Adjustments
Selected Renewables by Location
|  | Renewable Resource Summary by Location (MW) |  |  |  |  | Revised Busbar Allocation
|  | RESOLVE Resource | Tx Zone | 2030 FD | 2030 EO | TOTAL | SUBSTATION | MW ASSIGNED
|  | InState_Biomass | None
Greater_Imperial_Geothermal |  | Greater_Imperial_Geothermal | Greater_Imperial | 604 | 652 | 1256
Greater_Imperial_Geothermal | [6 empty] | Bannister 230kV (IID) | 628 | IID
Greater_Imperial_Geothermal | [6 empty] | Hudson Ranch 230kV (IID) | 628 | Connecting to IID Midway 230kV
Greater_Imperial_Geothermal
Greater_Imperial_Geothermal
|  | Inyokern_North_Kramer_Geothermal | Inyokern_North_Kramer
Northern_California_Ex_Geothermal |  | Northern_California_Ex_Geothermal | Northern_California_Ex
Northern_California_Ex_Geothermal | [6 empty] | Round Mountain
Pacific_Northwest_Geothermal
|  | Riverside_Palm_Springs_Geothermal | Riverside_Palm_Springs
|  | Solano_Geothermal | Solano
|  | Southern_Nevada_Geothermal | Mountain_Pass_El_Dorado
Carrizo_Wind |  | Carrizo_Wind | Carrizo |  | 160 | 160
Carrizo_Wind | [6 empty] | Templeton | 160
|  | Central_Valley_North_Los_Banos_Solar | Central_Valley_North_Los_Banos |  |  | 0
Central_Valley_North_Los_Banos_Wind |  | Central_Valley_North_Los_Banos_Wind | Central_Valley_North_Los_Banos | 146 |  | 146
Central_Valley_North_Los_Banos_Wind | [6 empty] | Los Banos | 146
|  | Distributed_Solar | None
|  | Distributed_Wind | None
|  | Greater_Imperial_Solar | Greater_Imperial |  |  | 0
|  | Greater_Imperial_Wind | Greater_Imperial
|  | Greater_Kramer_Wind | Greater_Kramer
|  | Humboldt_Wind | Humboldt
Inyokern_North_Kramer_Solar |  | Inyokern_North_Kramer_Solar | Inyokern_North_Kramer | 554 |  | 554
Inyokern_North_Kramer_Solar | [6 empty] | Caldwell | 263 | Victor Substation alloction removed due to significant land overlap with Caldwell Substation 81 MW reassigned form Victor to Caldwell | 63 | Pisgah 230kV | Connect Cool Water MWs at Pisgah, due to Tx constraints.
Inyokern_North_Kramer_Solar | [6 empty] | Calcite (Proposed) | 191 |  | 142 | Caldwell
Inyokern_North_Kramer_Solar | [6 empty] | Kramer 230kV | 100 |  | 191 | Calcite (Proposed)
Inyokern_North_Kramer_Solar | [9 empty] | 100 | Kramer 230kV
|  | Kern_Greater_Carrizo_Solar | Kern_Greater_Carrizo |  |  | 0
|  | Kern_Greater_Carrizo_Wind | Kern_Greater_Carrizo
|  | Kramer_Inyokern_Ex_Solar | Kramer_Inyokern_Ex
|  | Kramer_Inyokern_Ex_Wind | Kramer_Inyokern_Ex
|  | North_Victor_Solar | North_Victor_Solar |  |  | 0
|  | Northern_California_Ex_Solar | Northern_California_Ex
|  | Northern_California_Ex_Wind | Northern_California_Ex
|  | NW_Ext_Tx_Wind | Sacramento_River
Riverside_Palm_Springs_Solar |  | Riverside_Palm_Springs_Solar | Riverside_Palm_Springs | 192 | 1430 | 1622
Riverside_Palm_Springs_Solar | [6 empty] | Red Bluff | 1074
Riverside_Palm_Springs_Solar | [6 empty] | Colorado River | 548
Riverside_Palm_Springs_Wind |  | Riverside_Palm_Springs_Wind | Riverside_Palm_Springs | 42 |  | 42
Riverside_Palm_Springs_Wind | [6 empty] | Devers | 42
|  | Sacramento_River_Solar | Sacramento_River
Sacramento_River_Wind
|  | SCADSNV_Solar | SCADSNV
|  | SCADSNV_Wind | SCADSNV
|  | Solano_Solar | Solano
|  | Solano_subzone_Solar | Solano_subzone
|  | Solano_subzone_Wind | Solano_subzone
Solano_Wind |  | Solano_Wind | Solano |  | 643 | 643
Solano_Wind | [6 empty] | Lakeville | 270
Solano_Wind | [6 empty] | Tulucay | 27
Solano_Wind | [6 empty] | Vaca-Dixon & GC Yard | 203
Solano_Wind | [6 empty] | Shilo II | 100
Solano_Wind | [6 empty] | Lone Tree | 44
|  | Southern_California_Desert_Ex_Solar | Southern_California_Desert_Ex
|  | Southern_California_Desert_Ex_Wind | Southern_California_Desert_Ex
Southern_Nevada_Solar |  | Southern_Nevada_Solar | Mountain_Pass_El_Dorado | 802 | 2204 | 3006
Southern_Nevada_Solar | [6 empty] | Innovation | 152 | VA 700 MW FCDS Tx Constraint Limit
Southern_Nevada_Solar | [6 empty] | Desert View | 118
Southern_Nevada_Solar | [6 empty] | Crazy Eyes | 430
Southern_Nevada_Solar | [6 empty] | El Dorado 500 kV | 645 | EO
Southern_Nevada_Solar | [6 empty] | El Dorado 230 kV | 102 | FD
Southern_Nevada_Solar | [6 empty] | El Dorado 230 kV | 323 | EO
Southern_Nevada_Solar | [6 empty] | Mohave 500 kV | 1236 | EO Only
|  | Southern_Nevada_Wind | Mountain_Pass_El_Dorado
|  | SW_Ext_Tx_Wind | Riverside_Palm_Springs
Tehachapi_Solar |  | Tehachapi_Solar |  | 725 | 428 | 1153
Tehachapi_Solar | [6 empty] | WindHub | 277
Tehachapi_Solar | [6 empty] | Whirlwind | 307
Tehachapi_Solar | [6 empty] | Antelope | 300
Tehachapi_Solar | [6 empty] | Pearblossom | 269
|  | Tehachapi_Ex_Solar | Tehachapi_Ex
Tehachapi_Wind |  | Tehachapi_Wind | Tehachapi |  |  | 0
Tehachapi_Wind | [6 empty] | WindHub
|  | Westlands_Ex_Solar | Westlands_Ex
|  | Westlands_Ex_Wind | Westlands_Ex
|  | Westlands_Solar | Westlands |  |  | 0
|  | Utah_Solar | #N/A
Arizona_Solar |  | Arizona_Solar | #N/A |  | 428 | 428
Arizona_Solar | [6 empty] | Hassayampa | 47.08
Arizona_Solar | [6 empty] | Hoodoo Wash Switchyard | 222.56
Arizona_Solar | [6 empty] | Delaney-Colorado 500kV | 158.36
|  | New_Mexico_Solar | #N/A
|  | Baja_California_Wind | SCADSNV-Greater_Imperial
|  | Pacific_Northwest_Wind | #N/A
|  | Idaho_Wind | #N/A
|  | Utah_Wind | #N/A
|  | Wyoming_Wind | #N/A
|  | Arizona_Wind | #N/A
|  | New_Mexico_Wind | #N/A
|  | In-State |  | 3065 | 5945 | 9010 |  | 9011
|  | Out-Of-State |  | 0 | 0 | 0

## BUSBAR_ALLOC_SENS_2(1)
Source: CEC BUSBAR ALLOCATION_IRP 2020_SENSITIVITY2_v2.xlsx received from CEC 3/20/2020
30MMT_20200207_2045_2GWPRM_NOOTCEXT_ExpandedEO 03-11-2020
(Sensitivity 2 with Adjustments)
|  | Renewable Resource Summary by Location (MW) |  |  |  |  | Busbar Allocation
|  | RESOLVE Resource | Tx Zone | 2030 FD | 2030 EO | TOTAL | SUBSTATION | MW ASSIGNED | CEC NOTES
|  | InState_Biomass | None
Greater_Imperial_Geothermal |  | Greater_Imperial_Geothermal | SCADSNV-Greater_Imperial | 716 |  | 716
Greater_Imperial_Geothermal | [6 empty] | Bannister 230kV (IID) | 716
Greater_Imperial_Geothermal | [6 empty] | Hudson Ranch 230kV (IID)
|  | Inyokern_North_Kramer_Geothermal | Inyokern_North_Kramer-Greater_Kramer
|  | Northern_California_Ex_Geothermal | Northern_California_Ex
Pacific_Northwest_Geothermal
|  | Riverside_Palm_Springs_Geothermal | SCADSNV-Riverside_Palm_Springs
Solano_Geothermal |  | Solano_Geothermal | Sacramento_River-Solano | 135 |  | 135
Solano_Geothermal | [6 empty] | Sonoma 3 | 135 | PG&E 230kV
|  | Southern_Nevada_Geothermal | Mountain_Pass_El_Dorado-SCADSNV | [6 empty] | Carrizo-Kern_Greater_Carrizo-SPGE
Carrizo_Solar |  | Carrizo_Solar | Carrizo-Kern_Greater_Carrizo-SPGE |  | 600 | 600 | Caliente | 199 | Carrizo Tx - Templeton 224 MW solar + 287 MW Wind = 511 MW total |  |  |  | Carrizo_Solar | Carrizo_Wind
Carrizo_Solar | [6 empty] | Mesa | 177
Carrizo_Solar | [6 empty] | Templeton | 224 |  | Templeton |  |  | 224 | 287 | 511
Carrizo_Wind |  | Carrizo_Wind | Carrizo-Kern_Greater_Carrizo-SPGE | 187 | 100 | 287
Carrizo_Wind | [6 empty] | Templeton | 287
Central_Valley_North_Los_Banos_Solar |  | Central_Valley_North_Los_Banos_Solar | Central_Valley_North_Los_Banos-SPGE
Central_Valley_North_Los_Banos_Wind |  | Central_Valley_North_Los_Banos_Wind | Central_Valley_North_Los_Banos-SPGE | 173 |  | 173
Central_Valley_North_Los_Banos_Wind | [6 empty] | Los Banos 230kV | 173 | Assign this Wind Resource and MW to Westlands Tx Zone
|  | Distributed_Solar | None
|  | Distributed_Wind | None
Greater_Imperial_Solar |  | Greater_Imperial_Solar | SCADSNV-Greater_Imperial | 280 | 867 | 1147
Greater_Imperial_Solar | [6 empty] | East County | 250
Greater_Imperial_Solar | [6 empty] | Imperial Valley | 545
Greater_Imperial_Solar | [6 empty] | Ocotillo Express | 352
|  | Greater_Imperial_Wind | SCADSNV-Greater_Imperial
|  | Greater_Kramer_Wind | Greater_Kramer
Humboldt_Wind |  | Humboldt_Wind | Humboldt-Sacramento_River |  | 34 | 34
Humboldt_Wind | [6 empty] | Bridgeville 115kv | 34
Inyokern_North_Kramer_Solar |  | Inyokern_North_Kramer_Solar | Inyokern_North_Kramer-Greater_Kramer | 97 |  | 97
Inyokern_North_Kramer_Solar | [6 empty] | Kramer | 43
Inyokern_North_Kramer_Solar | [6 empty] | Randsburg | 54
Kern_Greater_Carrizo_Solar |  | Kern_Greater_Carrizo_Solar | Kern_Greater_Carrizo-SPGE | 752 | 2880 | 3632
Kern_Greater_Carrizo_Solar | [6 empty] | Arco | 749
Kern_Greater_Carrizo_Solar | [6 empty] | Midway | 724
Kern_Greater_Carrizo_Solar | [6 empty] | Renfro | 744
Kern_Greater_Carrizo_Solar | [6 empty] | Stockdale | 747
Kern_Greater_Carrizo_Solar | [6 empty] | Wheeler Ridge | 668
Kern_Greater_Carrizo_Wind |  | Kern_Greater_Carrizo_Wind | Kern_Greater_Carrizo-SPGE | 60 |  | 60
Kern_Greater_Carrizo_Wind | [6 empty] | Cholame 70 kV | 60 | Assign to Cholame Sub to reduce gentie distance. May require local upgrade to connect project(s)
|  | Kramer_Inyokern_Ex_Solar | Kramer_Inyokern_Ex
|  | Kramer_Inyokern_Ex_Wind | Kramer_Inyokern_Ex
Mountain_Pass_El_Dorado_Solar |  | Mountain_Pass_El_Dorado_Solar |  |  | 248 | 248
Mountain_Pass_El_Dorado_Solar | [6 empty] | El Dorado 230kV | 83
Mountain_Pass_El_Dorado_Solar | [6 empty] | EL Dorado 500kV | 165
North_Victor_Solar |  | North_Victor_Solar | North_Victor-Greater_Kramer | 300 |  | 300
North_Victor_Solar | [6 empty] | Victor | 215
North_Victor_Solar | [6 empty] | Coolwater | 85
|  | Northern_California_Ex_Solar | Northern_California_Ex
Northern_California_Ex_Wind |  | Northern_California_Ex_Wind | Sacramento_River | 866 |  | 866
Northern_California_Ex_Wind | [6 empty] | Glenn | 400
Northern_California_Ex_Wind | [6 empty] | Delevan | 94
Northern_California_Ex_Wind | [6 empty] | Thermalito | 201
Northern_California_Ex_Wind | [6 empty] | Rio Oso | 171
NW_Ext_Tx_Wind |  | NW_Ext_Tx_Wind | Sacramento_River | 530 | 970 | 1500
NW_Ext_Tx_Wind | [6 empty] | Round Mountain | 1500
Riverside_Palm_Springs_Solar |  | Riverside_Palm_Springs_Solar | SCADSNV-Riverside_Palm_Springs | 1780 |  | 1780
Riverside_Palm_Springs_Solar | [6 empty] | Red Bluff | 601
Riverside_Palm_Springs_Solar | [6 empty] | Colorado River | 1179
|  | Riverside_Palm_Springs_Wind | SCADSNV-Riverside_Palm_Springs
|  | Sacramento_River_Solar | Sacramento_River
|  | Sacramento_River_Wind | Sacramento_River
SCADSNV_Solar |  | SCADSNV_Solar | SCADSNV |  | 1970 | 1970
SCADSNV_Solar | [6 empty] | Innovation | 64
SCADSNV_Solar | [6 empty] | Desert View | 49
SCADSNV_Solar | [6 empty] | Crazy Eyes | 177
SCADSNV_Solar | [6 empty] | El Dorado 230kV | 246
SCADSNV_Solar | [6 empty] | El Dorado 500kV | 492
SCADSNV_Solar | [6 empty] | Mohave 500kV | 942
|  | SCADSNV_Wind | SCADSNV
|  | Solano_Solar | Sacramento_River-Solano
|  | Solano_subzone_Solar | Sacramento_River-Solano-Solano_subzone
|  | Solano_subzone_Wind | Sacramento_River-Solano-Solano_subzone
Solano_Wind |  | Solano_Wind | Sacramento_River-Solano | 464 | 78 | 542
Solano_Wind | [6 empty] | Lakeville | 227
Solano_Wind | [6 empty] | Tulucay | 23
Solano_Wind | [6 empty] | Vaca-Dixon & GC Yard | 171
Solano_Wind | [6 empty] | Shilo II | 84
Solano_Wind | [6 empty] | Lone Tree | 37
|  | Southern_California_Desert_Ex_Solar | Southern_California_Desert_Ex
|  | Southern_California_Desert_Ex_Wind | Southern_California_Desert_Ex
Southern_Nevada_Solar |  | Southern_Nevada_Solar | SCADSNV-GLW_VEA | 257 | 1470 | 1727 |  |  |  | SCADSNV | SCADSNV_Solar EO | Mountain_Pass_El_Dorado_Solar EO | Southern_Nevada_Solar FD | Southern_Nevada_Solar EO | Southern_Nevada_Wind FD | Wyoming_Wind | Substation Totals | FDCS | EO
Southern_Nevada_Solar | [6 empty] | Innovation | 380 | 57 FDCS + 323 EO | Innovation | 64 |  | 57 | 323 | 98 |  | 542
Southern_Nevada_Solar | [6 empty] | Desert View | 294 | 44 FDCS + 250 EO | Desert View | 49 |  | 44 | 250 | 76 |  | 419
Southern_Nevada_Solar | [6 empty] | Crazy Eyes | 1054 | 157 FDCS + 897 EO | Crazy Eyes | 177 |  | 157 | 897 | 268 |  | 1499
[9 empty] | EO | El Dorado 230kV | 246 | 83 |  |  |  |  | 329
[9 empty] | EO | El Dorado 500kV | 492 | 165 |  |  |  | 1500 | 2157
[9 empty] | EO | Mohave 500kV | 942 | [5 empty] | 942
Southern_Nevada_Wind |  | Southern_Nevada_Wind | SCADSNV-GLW_VEA | 442 |  | 442
Southern_Nevada_Wind | [6 empty] | Innovation | 98 | FDCS | Totals | 1970 | 248 | 258 | 1470 | 442 | 1500 | 5888 | 700 | 4940
Southern_Nevada_Wind | [6 empty] | Desert View | 76 | FDCS
Southern_Nevada_Wind | [6 empty] | Crazy Eyes | 268 | FDCS
SW_Ext_Tx_Wind |  | SW_Ext_Tx_Wind | SCADSNV-Riverside_Palm_Springs | 500 |  | 500
SW_Ext_Tx_Wind | [6 empty] | Palo Verde | 500 | SunZia/Devers-Palo Verde 500kV
Tehachapi_Solar |  | Tehachapi_Solar | Tehachapi | 2402 | 1399 | 3801
Tehachapi_Solar | [6 empty] | WindHub | 914
Tehachapi_Solar | [6 empty] | Whirlwind | 1012
Tehachapi_Solar | [6 empty] | Antelope | 988
Tehachapi_Solar | [6 empty] | Pearblossom | 888
|  | Tehachapi_Ex_Solar | Tehachapi_Ex
Tehachapi_Wind |  | Tehachapi_Wind | Tehachapi | 275 |  | 275
Tehachapi_Wind | [6 empty] | WindHub | 275
|  | Westlands_Ex_Solar | Westlands_Ex
|  | Westlands_Ex_Wind | Westlands_Ex
Westlands_Solar |  | Westlands_Solar | SPGE_Z1_Westlands | 827 | 500 | 1327 |  |  |  | SPGE_Z1_Westlands |  |  |  | Central_Valley_North_Los_Banos-SPGE
Westlands_Solar | [6 empty] | Gates | 191 |  | Gates | 213.5299 |  |  | Weber | 323
Westlands_Solar | [6 empty] | Helm | 224 |  | Helm | 311.7274 |  |  | Cottle | 348
Westlands_Solar | [6 empty] | Henrietta | 207 |  | Henrietta | 197.7846 |  |  | Wilson | 297
Westlands_Solar | [6 empty] | Mc Call | 259 |  | Mc Call | 110.1192 |  |  | Storey | 359
Westlands_Solar | [6 empty] | Mc Mullin | 242 |  | Mc Mullin | 130.4613
Westlands_Solar | [6 empty] | Panoche | 204 |  | Panoche | 135.3776
|  | Utah_Solar | #N/A
Arizona_Solar |  | Arizona_Solar | SCADSNV-Riverside_Palm_Springs | 573 | 1568 | 2141
Arizona_Solar | [6 empty] | Hassayampa | 236
Arizona_Solar | [6 empty] | Hoodoo Wash Switchyard | 1113
Arizona_Solar | [6 empty] | Delaney-Colorado 500kV | 792
|  | New_Mexico_Solar | #N/A
Baja_California_Wind |  | Baja_California_Wind | SCADSNV-Greater_Imperial | 203 | 397 | 600
Baja_California_Wind | [6 empty] | East County | 600
|  | Pacific_Northwest_Wind | #N/A
|  | Idaho_Wind | #N/A
|  | Utah_Wind | #N/A
Wyoming_Wind |  | Wyoming_Wind | Mountain_Pass_El_Dorado-SCADSNV |  | 1500 | 1500
Wyoming_Wind | [6 empty] | El Dorado 500kV | 1500
|  | Arizona_Wind | #N/A
New_Mexico_Wind |  | New_Mexico_Wind | SCADSNV-Riverside_Palm_Springs |  | 1500 | 1500
New_Mexico_Wind | [6 empty] | Palo Verde | 1500 | SunZia/Devers-Palo Verde 500kV
|  | In-State |  | 11819 | 16081 | 27900 |  | 27902
Out-Of-State

## BUSBAR ALLOCATION_SENS_2(2)
Source: received CEC BUSBAR ALLOCATION_IRP 2020_SENSITIVITY2_v3.xlsx received 3/26
30MMT_20200207_2045_2GWPRM_NOOTCEXT_ExpandedEO 03-25-2020
(Sensitivity 2 with Adjustments)
|  | Renewable Resource Summary by Location (MW) |  |  |  |  | Busbar Allocation
|  | RESOLVE Resource | Tx Zone | 2030 FD | 2030 EO | TOTAL | SUBSTATION | MW ASSIGNED | CEC NOTES
|  | InState_Biomass | None
|  | Greater_Imperial_Geothermal | SCADSNV-Greater_Imperial | 716 |  | 716
[7 empty] | Bannister 230kV (IID) | 716
Hudson Ranch 230kV (IID)
|  | Inyokern_North_Kramer_Geothermal | Inyokern_North_Kramer-Greater_Kramer
|  | Northern_California_Ex_Geothermal | Northern_California_Ex
Pacific_Northwest_Geothermal
|  | Riverside_Palm_Springs_Geothermal | SCADSNV-Riverside_Palm_Springs
|  | Solano_Geothermal | Sacramento_River-Solano | 135 |  | 135
[7 empty] | Sonoma 3 | 135 | PG&E 230kV
|  | Southern_Nevada_Geothermal | Mountain_Pass_El_Dorado-SCADSNV
|  | Carrizo_Solar | Carrizo-Kern_Greater_Carrizo-SPGE |  | 600 | 600 | Caliente | 199 | Carrizo Tx - Templeton 224 MW solar + 287 MW Wind = 511 MW total
[7 empty] | Mesa | 177
[7 empty] | Templeton | 224 |  |  |  |  | 0
|  | Carrizo_Wind | Carrizo-Kern_Greater_Carrizo-SPGE | 187 | 100 | 287
[7 empty] | Templeton | 287
|  | Central_Valley_North_Los_Banos_Solar | Central_Valley_North_Los_Banos-SPGE
|  | Central_Valley_North_Los_Banos_Wind | Central_Valley_North_Los_Banos-SPGE/SPGE_Z1_Westlands | 173 |  | 173 |  |  | Assign this Wind Resource and MW to Westlands Tx Zone
[7 empty] | Los Banos 230kV | 173
|  | Distributed_Solar | None
|  | Distributed_Wind | None
|  | Greater_Imperial_Solar | SCADSNV-Greater_Imperial |  | 356 | 356 |  |  | Adjustment Made
[7 empty] | Imperial Valley | 216
[7 empty] | Ocotillo Express | 140
|  | Greater_Imperial_Wind | SCADSNV-Greater_Imperial
|  | Greater_Kramer_Wind | Greater_Kramer
|  | Humboldt_Wind | Humboldt-Sacramento_River |  | 34 | 34
[7 empty] | Bridgeville 115kv | 34
|  | Inyokern_North_Kramer_Solar | Inyokern_North_Kramer-Greater_Kramer | 97 |  | 97
[7 empty] | Kramer | 43
[7 empty] | Randsburg | 54
|  | Kern_Greater_Carrizo_Solar | Kern_Greater_Carrizo-SPGE | 121 | 2880 | 3001 |  |  | Adjustment Made
[7 empty] | Arco | 619
[7 empty] | Midway | 599
[7 empty] | Renfro | 615
[7 empty] | Stockdale | 617
[7 empty] | Wheeler Ridge | 552
|  | Kern_Greater_Carrizo_Wind | Kern_Greater_Carrizo-SPGE | 60 |  | 60
[7 empty] | Cholame 70 kV | 60 | Assign to Cholame Sub to reduce gentie distance. May require local upgrade to connect project(s)
|  | Kramer_Inyokern_Ex_Solar | Kramer_Inyokern_Ex
|  | Kramer_Inyokern_Ex_Wind | Kramer_Inyokern_Ex
|  | Mountain_Pass_El_Dorado_Solar | Mountain_Pass_El_Dorado | 248 |  | 248 |  |  | Adjustment Made
[7 empty] | El Dorado 230kV | 83 | FD
[7 empty] | EL Dorado 500kV | 165 | FD
|  | North_Victor_Solar | North_Victor-Greater_Kramer | 300 |  | 300
[7 empty] | Victor | 215
[7 empty] | Coolwater | 85
|  | Northern_California_Ex_Solar | Northern_California_Ex
|  | Northern_California_Ex_Wind | Northern_California_Ex/Sacramento_River | 866 |  | 866 |  |  | Assign this Wind Resource and MW to Sacramento_River Tx Zone
[7 empty] | Glenn | 400
[7 empty] | Delevan | 94
[7 empty] | Thermalito | 201
[7 empty] | Rio Oso | 171
|  | NW_Ext_Tx_Wind | Sacramento_River | 530 | 970 | 1500
[7 empty] | Round Mountain | 1500
|  | Riverside_Palm_Springs_Solar | SCADSNV-Riverside_Palm_Springs |  |  | 0 |  |  | Adjustment Made
Red Bluff
Colorado River
|  | Riverside_Palm_Springs_Wind | SCADSNV-Riverside_Palm_Springs
|  | Sacramento_River_Solar | Sacramento_River
|  | Sacramento_River_Wind | Sacramento_River
|  | SCADSNV_Solar | SCADSNV | 2333 | 1970 | 4303 |  |  | Adjustment Made
[7 empty] | Innovation | 64 | EO
[7 empty] | Desert View | 49 | EO
[7 empty] | Crazy Eyes | 177 | EO
[7 empty] | El Dorado 230kV | 246 | EO
[7 empty] | El Dorado 500kV | 1292 | 800 FD + 492 EO
[7 empty] | Mohave 500kV | 2475 | 1533 FD + 942 EO
|  | SCADSNV_Wind | SCADSNV
|  | Solano_Solar | Sacramento_River-Solano
|  | Solano_subzone_Solar | Sacramento_River-Solano-Solano_subzone
|  | Solano_subzone_Wind | Sacramento_River-Solano-Solano_subzone
|  | Solano_Wind | Sacramento_River-Solano | 464 | 78 | 542
[7 empty] | Lakeville | 227
[7 empty] | Tulucay | 23
[7 empty] | Vaca-Dixon & GC Yard | 171
[7 empty] | Shilo II | 84
[7 empty] | Lone Tree | 37
|  | Southern_California_Desert_Ex_Solar | Southern_California_Desert_Ex
|  | Southern_California_Desert_Ex_Wind | Southern_California_Desert_Ex | [10 empty] | OLD
|  | Southern_Nevada_Solar | SCADSNV-GLW_VEA | 257 | 1470 | 1727 | [7 empty] | SCADSNV | SCADSNV_Solar EO | Mountain_Pass_El_Dorado_Solar EO | Southern_Nevada_Solar FD | Southern_Nevada_Solar EO | Southern_Nevada_Wind FD | Wyoming_Wind | Substation Totals | FDCS | EO
[7 empty] | Innovation | 380 | 57 FDCS + 323 EO |  |  |  |  | Innovation | 64 |  | 57 | 323 | 98 |  | 542
[7 empty] | Desert View | 294 | 44 FDCS + 250 EO |  |  |  |  | Desert View | 49 |  | 44 | 250 | 76 |  | 419
[7 empty] | Crazy Eyes | 1054 | 157 FDCS + 897 EO |  |  |  |  | Crazy Eyes | 177 |  | 157 | 897 | 268 |  | 1499
[14 empty] | El Dorado 230kV | 246 | 83 |  |  |  |  | 329
[14 empty] | El Dorado 500kV | 492 | 165 |  |  |  | 1500 | 2157
[14 empty] | Mohave 500kV | 942 | [5 empty] | 942
|  | Southern_Nevada_Wind | SCADSNV-GLW_VEA | 442 |  | 442
[7 empty] | Innovation | 98 | FDCS
[7 empty] | Desert View | 76 | FDCS |  |  |  |  | Totals | 1970 | 248 | 258 | 1470 | 442 | 1500 | 5888 | 700 | 4940
[7 empty] | Crazy Eyes | 268 | FDCS
|  | SW_Ext_Tx_Wind | SCADSNV-Riverside_Palm_Springs | 500 |  | 500
[7 empty] | Palo Verde | 500 | SunZia/Devers-Palo Verde 500kV
|  | Tehachapi_Solar | Tehachapi | 3402 | 1399 | 4801 |  |  | Adjustment Made
[7 empty] | WindHub | 1154
[7 empty] | Whirlwind | 1278
[7 empty] | Antelope | 1248
[7 empty] | Pearblossom | 1121
|  | Tehachapi_Ex_Solar | Tehachapi_Ex
|  | Tehachapi_Wind | Tehachapi | 275 |  | 275
[7 empty] | WindHub | 275
|  | Westlands_Ex_Solar | Westlands_Ex
|  | Westlands_Ex_Wind | Westlands_Ex
|  | Westlands_Solar | SPGE_Z1_Westlands | 1458 | 500 | 1958 |  |  | Adjustment Made
[7 empty] | Gates | 70 |  | 1475
[7 empty] | Helm | 82
[7 empty] | Henrietta | 75
[7 empty] | Mc Call | 94
[7 empty] | Mc Mullin | 88
[7 empty] | Panoche | 74 |  | Alternate Allocation
[7 empty] | Gates 500kV | 1475 | New Gates to Diablo 500kV Tx Line
[10 empty] | Gates 500kV | 1958 | New Gates to Diablo 500kV Tx Line
|  | Pumped Storage Project | GreaterImpOutsideTxConstraintZones |  |  | 608
[7 empty] | Lee Lake 500kV (Proposed) | 608 | Pumped Storage Project
|  | Pumped Storage Project | GreaterImpOutsideTxConstraintZones |  |  | 608
[7 empty] | Sycamore Canyon 230kV | 608 | Pumped Storage Project
|  | Pumped Storage Project | SCADSNV-Riverside_Palm_Springs |  |  | 1582
[7 empty] | Red Bluff | 1582 | Pumped Storage Project Palo Verde to Devers 500kV Line
|  | Utah_Solar | #N/A
|  | Arizona_Solar | SCADSNV-Riverside_Palm_Springs | 573 | 1568 | 2141 |  |  | Adjustment Made
[7 empty] | Hassayampa | 149
[7 empty] | Hoodoo Wash Switchyard | 702
[7 empty] | Delaney-Colorado 500kV | 500
|  | New_Mexico_Solar | #N/A
|  | Baja_California_Wind | SCADSNV-Greater_Imperial | 203 | 397 | 600
[7 empty] | East County | 600 | Adjustment Made
|  | Pacific_Northwest_Wind | #N/A
|  | Idaho_Wind | #N/A
|  | Utah_Wind | #N/A
|  | Wyoming_Wind | Mountain_Pass_El_Dorado-SCADSNV |  | 1500 | 1500
[7 empty] | El Dorado 500kV | 1500
|  | Arizona_Wind | #N/A
|  | New_Mexico_Wind | SCADSNV-Riverside_Palm_Springs |  | 1500 | 1500
[7 empty] | Palo Verde | 1500 | SunZia/Devers-Palo Verde 500kV
|  | In-State |  | 13340 | 15322 | 31460 |  | 30672
Out-Of-State
|  |  |  | 13340 | 15322 | 31460 |  | 31462

## SNV_Detail
SCADSNV | SCADSNV_Solar FD | SCADSNV_Solar EO | Mountain_Pass_El_Dorado_Solar FD | Southern_Nevada_Solar FD | Southern_Nevada_Solar EO | Southern_Nevada_Wind FD | Wyoming_Wind EO | Substation Totals | FDCS | EO
RESOLVE MW (adjusted) | 2333 | 1970 | 248 | 257 | 1470 | 442 | 1500 | 8220 | 3280 | 4940
Innovation |  | 64 |  | 57 | 323 | 98 |  | 542 | 155 | 387
Desert View |  | 49 |  | 44 | 250 | 76 |  | 419 | 120 | 299
Crazy Eyes |  | 177 |  | 157 | 897 | 268 |  | 1499 | 425 | 1074
El Dorado 230kV |  | 246 | 83 |  |  |  |  | 329 | 83 | 246
El Dorado 500kV | 800 | 492 | 165 |  |  |  | 1500 | 2957 | 965 | 1992
Mohave 500kV | 1533 | 942 | [5 empty] | 2475 | 1533 | 942
[9 empty] | 0 | 0
Allocation Sum | 2333 | 1970 | 248 | 258 | 1470 | 442 | 1500 | 8221 | 3281 | 4940

## 5b_ComparToPrevYr
What constitutes level 3 criteria flag? | 1000 | or greater | Difference from prior year
What constitutes level 2 criteria flag? | 0.6 | or greater | Difference from prior year
What constitutes level 1 criteria flag?
032019 FD + EO
RESOLVE Resource | 2018 PSP | 30MMT EO2 | Delta | Difference > 1000 MW? | Dashboard value |  | 30MMT EO2 adj | Delta | Difference > 1000 MW? | Dashboard value
InState_Biomass | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Greater_Imperial_Geothermal | 1256 | 716.46 | -42.96% | 0 | 1 |  | 716.46 | -42.96% | 0 | 1
Inyokern_North_Kramer_Geothermal | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Northern_California_Ex_Geothermal | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Pacific_Northwest_Geothermal | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Riverside_Palm_Springs_Geothermal | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Solano_Geothermal | 0 | 135 | 13500% | 0 | 2 | >60% difference from prior year | 135 | 13500% | 0 | 2
Southern_Nevada_Geothermal | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Carrizo_Solar | 0 | 600 | 60000% | 0 | 2 | >60% difference from prior year | 600 | 60000% | 0 | 2
Carrizo_Wind | 160 | 287 | 79.38% | 0 | 2 | >60% difference from prior year | 287 | 79.38% | 0 | 2
Central_Valley_North_Los_Banos_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Central_Valley_North_Los_Banos_Wind | 146 | 173 | 18.49% | 0 | 1 |  | 173 | 18.49% | 0 | 1
Distributed_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Distributed_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Greater_Imperial_Solar | 0 | 866.98 | 86698% | 0 | 2 | >60% difference from prior year | 355.98 | 35598% | 0 | 2
Greater_Imperial_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Greater_Kramer_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Humboldt_Wind | 0 | 34 | 3400% | 0 | 2 | >60% difference from prior year | 34 | 3400% | 0 | 2
Inyokern_North_Kramer_Solar | 554 | 97 | -82.49% | 0 | 2 | >60% difference from prior year | 97 | -82.49% | 0 | 2
Kern_Greater_Carrizo_Solar | 0 | 3001.27 | 300127% | 1 | 3 | >1000 MW difference from prior year | 3001.27 | 300127% | 1 | 3
Kern_Greater_Carrizo_Wind | 0 | 60 | 6000% | 0 | 2 | >60% difference from prior year | 60 | 6000% | 0 | 2
Kramer_Inyokern_Ex_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Kramer_Inyokern_Ex_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Mountain_Pass_El_Dorado_Solar | 0 | 248 | 24800% | 0 | 2 | >60% difference from prior year | 248 | 24800% | 0 | 2
North_Victor_Solar | 0 | 300 | 30000% | 0 | 2 | >60% difference from prior year | 300 | 30000% | 0 | 2
Northern_California_Ex_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Northern_California_Ex_Wind | 0 | 865.9 | 86590% | 0 | 2 | >60% difference from prior year | 865.9 | 86590% | 0 | 2
NW_Ext_Tx_Wind | 0 | 1500 | 150000% | 1 | 3 | >1000 MW difference from prior year | 1500 | 150000% | 1 | 3
Riverside_Palm_Springs_Solar | 1622 | 0 | -100% | 1 | 3 | >1000 MW difference from prior year | 29 | -98.21% | 1 | 3
Sacramento_River_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Sacramento_River_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
SCADSNV_Solar | 0 | 1970 | 197000% | 1 | 3 | >1000 MW difference from prior year | 4303 | 430300% | 1 | 3
SCADSNV_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Solano_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Solano_subzone_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Solano_subzone_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Solano_Wind | 644 | 542 | -15.84% | 0 | 1 |  | 542 | -15.84% | 0 | 1
Southern_California_Desert_Ex_Solar | 0 | 862 | 86200% | 0 | 2 | >60% difference from prior year | 0 | 0% | 0 | 1
Southern_California_Desert_Ex_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Southern_Nevada_Solar | 3006 | 1470 | -51.1% | 1 | 3 | >1000 MW difference from prior year | 1727 | -42.55% | 1 | 3
Southern_Nevada_Wind | 0 | 442.03 | 44203% | 0 | 2 | >60% difference from prior year | 442.03 | 44203% | 0 | 2
SW_Ext_Tx_Wind | 0 | 500 | 50000% | 0 | 2 | >60% difference from prior year | 500 | 50000% | 0 | 2
Tehachapi_Solar | 1153 | 4801 | 316.4% | 1 | 3 | >1000 MW difference from prior year | 4801 | 316.4% | 1 | 3
Tehachapi_Ex_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Tehachapi_Wind | 0 | 275 | 27500% | 0 | 2 | >60% difference from prior year | 275 | 27500% | 0 | 2
Westlands_Ex_Solar | 0 | 1778.57 | 177857% | 1 | 3 | >1000 MW difference from prior year | -0.43 | -43% | 0 | 1
Westlands_Ex_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Westlands_Solar | 0 | 633.68 | 63368% | 0 | 2 | >60% difference from prior year | 1957.68 | 195768% | 1 | 3
Cape_Mendocino_Offshore_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Del_Norte_Offshore_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Diablo_Canyon_Offshore_Wind_Ext_Tx | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Diablo_Canyon_Offshore_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Humboldt_Bay_Offshore_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Morro_Bay_Offshore_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Utah_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Arizona_Solar | 428 | 2140.97 | 400.2% | 1 | 3 | >1000 MW difference from prior year | 1349.97 | 215.4% | 0 | 2
New_Mexico_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Baja_California_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Baja_California_Wind | 0 | 600 | 60000% | 0 | 2 | >60% difference from prior year | 600 | 60000% | 0 | 2
Pacific_Northwest_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Idaho_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Utah_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Wyoming_Wind | 0 | 1500 | 150000% | 1 | 3 | >1000 MW difference from prior year | 1500 | 150000% | 1 | 3
Arizona_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
New_Mexico_Wind | 0 | 1500 | 150000% | 1 | 3 | >1000 MW difference from prior year | 1500 | 150000% | 1 | 3
Pumped Storage Hydro | 0 | 0 | 0% | 0 | 1 |  | 2798 | 279800% | 1 | 3
| 8969 | 27899.86 |  |  |  |  | 27899.86
Note on B4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Source: Mar 2019 Busbar Allocation Filename: TN227311_20190311T143938_UPDATED 2019 IRP Portfolio Allocations to Substations.xlsx Downloaded from CEC Docket 17-Misc-03