## READ ME
This dashboard provides an overview of busbar mapping results for the CPUC IRP Proceeding
Resource-to-busbar mapping (“busbar mapping”) is the process of refining the geographically coarse portfolios produced in the California Public Utilities Commission’s (CPUC) Integrated Resource Plan (IRP) proceeding, into plausible network modeling locations for electrical analysis in the California Independent System Operator’s (CAISO) annual Transmission Planning Process (TPP).
The purpose of this workbook is to communicate the results of the 2019 busbar mapping process performed by the CPUC, CAISO and California Energy Commission (CEC).
Tabs shaded blue are authored by CEC: busbar allocation results
Tabs shaded purple are authored by CPUC: these tabs show busbar mapping criteria and results
Tabs shaded green are authored by CPUC: these tabs show the underlying calculations used to review busbar mapping results against mapping criteria
See Methodology for more detail, available at:
https://www.cpuc.ca.gov/General.aspx?id=6442464144

## VERSIONS
Version # | Mapping Rounds Performed | Description | Changes to Prior Version
0.1 | 0 | RESOLVE portfolio: 46MMT_20200207_2045_2GWPRM_NOOTCEXT_RSP_PD | Not applicable
0.2 | 0 | Sending to CEC for mapping 3/10/20 | Updating commentary with latest status. Formatting.
1 | 1 & 2 |  | Includes feedback from ISO and PUC staff on 3/20 check-in call
2 | 2 |  | Imported round 2 mapping results, created round 2 dashboard, updated all criteria.
Revised rounds 0 and 1 dashboards to retain criteria values prior to round 2 (hard coded from prior version)
2.1 | 2 |  | Cleaned up for public posting

## Dashboard 2019RSP (Round 0)
IRP Busbar Mapping Dashboard
Purpose: Quickly communicate compliance of portfolio mapping with the criteria per the Methodology. Highlight MW amounts by zone that breach criteria, if any, and identify next steps as part of the iterative process.
2019 RSP
Pre Round 1 - RESOLVE selections |  |  | Selected | Selected |  |  | Compliance with Criteria
| Resource Selection |  | Resources | Resources | [1=Yes, 2=Possible/Moderate, 3=Materially in Breach] | [9 empty] | Actions
Resource | 2030 FCDS MW | 2030 EO MW | Total MW (2018 PSP) | Total MW (2019 RSP) | 1. Distance to Trans. |  | 2. Trans. Capability | 3a. Available Land Area | 3b. High Env. Impl. | [lookup formula] | 4. Comm. Interest | 5. Consistency with Prior Year's Mapping | Sum of criteria | Low-Effort Adjustment Available? | Further Round of Mapping Needed? | Comment; Potential Solutions for Consideration | Include in display?
InState_Biomass |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Greater_Imperial_Geothermal |  |  | 1256 | 0 |  | ok | 1 |  |  | 1 | 1 | 3 | 5 |  | No | [Prior yr]: >1000 MW difference from prior year | 1
Inyokern_North_Kramer_Geothermal |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Northern_California_Geothermal |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 |  | 2 |  |  |  | 0
Pacific_Northwest_Geothermal |  |  | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
Riverside_Palm_Springs_Geothermal |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Solano_Geothermal |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Southern_Nevada_Geothermal |  |  | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
Carrizo_Solar |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Carrizo_Wind |  |  | 160 | 287 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  | No | [Prior yr]: >60% difference from prior portfolio | 1
Central_Valley_North_Los_Banos_Solar |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Central_Valley_North_Los_Banos_Wind |  |  | 146 | 173 |  | ok | 1 |  |  | 1 | 1 | 1 | 3 | Yes | No |  | 1
Distributed_Solar |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Distributed_Wind |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Greater_Imperial_Solar |  |  | 0 | 547.9 |  | ok | 1 |  |  | 2 | 2 | 2 | 5 |  | Maybe? | [Commercial interest]: model selecting less than queue (model = 548 MW, queue = 3051 MW) | 1
Greater_Imperial_Wind |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Greater_Kramer_Wind |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  | Maybe? |  | 0
Humboldt_Wind |  |  | 0 | 34 |  | ok | 1 |  |  |  |  | 2 | 3 |  | No | [Prior yr]: >60% difference from prior portfolio | 1
Inyokern_North_Kramer_Solar |  |  | 554 | 97 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  | Maybe? | [Commercial interest]: Model selecting less than queue (model = 97; queue = 824 MW) | 1
Kern_Greater_Carrizo_Solar |  |  | 0 | 241.66 |  | ok | 1 |  |  | 1 | 1 | 2 |  |  | No | [Prior yr]: >60% difference from prior portfolio | 1
Kern_Greater_Carrizo_Wind |  |  | 0 | 60 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  | No | [Prior yr]: >60% difference from prior portfolio | 1
Kramer_Inyokern_Ex_Solar |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 | 3 | Yes |  |  | 0
Kramer_Inyokern_Ex_Wind |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Mountain_Pass_El_Dorado_Solar |  |  | 0 | 248 |  | ok | 2 |  |  | 1 | 1 | 2 |  |  |  | [Tx capability]: bug in model means this resource should be converted from FD to EO. See tab "proposedAdjustments", adjustment 4. [Prior yr]: >60% difference from prior portfolio | 1
North_Victor_Solar |  |  | 0 | 300 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  | No | [Prior yr]: >60% difference from prior portfolio | 1
Northern_California_Ex_Solar |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Northern_California_Ex_Wind |  |  | 0 | 865.9 |  | ok | 2 |  |  | 1 | 1 | 2 | 5 | Yes | After Rnd 1 | [Tx capability]: Note overlap in the tx capability estimates between “Ex” zone and core tx constraint zones – the estimates for the core zones have greater confidence and should probably supersede | 1
NW_Ext_Tx_Wind |  |  | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
Riverside_Palm_Springs_Solar |  |  | 1622 | 0 |  | ok | 1 |  |  | 2 | 2 | 3 | 6 |  | Yes | [Commercial interest]: Model selecting less than queue (model = 0; queue = 2182 MW in zone, plus 2595 MW delivering to zone from AZ) [Prior yr]: Changed from 1622 MW to 0 MW | 1
Riverside_Palm_Springs_Wind |  |  | 42 | NA |  | ok | 1 |  |  | 1 | 1 |  | 2 |  |  | Resource not included in latest version of RESOLVE | 1
Sacramento_River_Solar |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Sacramento_River_Wind |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
SCADSNV_Solar |  |  | 0 | 330 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  | Maybe? | [Prior yr]: >60% difference from prior portfolio | 1
SCADSNV_Wind |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Solano_Solar |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Solano_subzone_Solar |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Solano_subzone_Wind |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Solano_Wind |  |  | 644 | 542 |  | ok | 1 |  |  | 1 | 1 | 1 | 3 |  | No |  | 1
Southern_California_Desert_Ex_Solar |  |  | 0 | 862 |  | ok | 2 |  |  | 3 | 3 | 2 |  |  | Yes | [Tx capability]: Note overlap in the tx capability estimates between “Ex” zone and core tx constraint zones – the estimates for the core zones have greater confidence and should probably supersede. [Commercial interest]: model selecting less than queue (model = 862 MW, queue = 2000 MW). [Prior yr]: >60% difference from prior portfolio. | 1
Southern_California_Desert_Ex_Wind |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Southern_Nevada_Solar |  |  | 3006 | 0 |  | ok | 1 |  |  | 2 | 2 | 3 | 6 |  | Yes | [Commercial interest]: Model selecting less than queue (model = 0; queue = 2000 MW.) [Prior yr]: Changed from 3006 MW to 0 MW | 1
Southern_Nevada_Wind |  |  | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
SW_Ext_Tx_Wind |  |  | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
Tehachapi_Solar |  |  | 1153 | 4202 |  | ok | 1 |  |  | 1 | 1 | 3 | 5 |  | Yes | >1000 MW increase from prior year. Note Riverside Palm Springs went down to zero. Cosider balancing these two out. | 1
Tehachapi_Ex_Solar |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 | 3 | Yes |  |  | 0
Tehachapi_Wind |  |  | 0 | 275 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  | No | >60% difference from prior portfolio | 1
Westlands_Ex_Solar |  |  | 0 | 1778.57 |  | ok | 2 |  |  | 1 | 1 | 3 |  |  | Yes | [Tx capability]: Note overlap in the tx capability estimates between “Ex” zone and core tx constraint zones – the estimates for the core zones have greater confidence and should probably supersede. [Prior yr]: Changed from 0 to 1779 MW | 1
Westlands_Ex_Wind |  |  | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Westlands_Solar |  |  | 0 | 58.21 |  | ok | 1 |  |  | 3 | 3 | 2 |  |  | Yes | [Commercial interest]: Model selecting less than queue (model = 58; queue = 5246 MW.) [Prior yr]: Changed from 0 to 58 MW. | 1
Cape_Mendocino_Offshore_Wind |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Del_Norte_Offshore_Wind |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Diablo_Canyon_Offshore_Wind_Ext_Tx |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Diablo_Canyon_Offshore_Wind |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Humboldt_Bay_Offshore_Wind |  |  | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
Morro_Bay_Offshore_Wind |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Utah_Solar |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Arizona_Solar |  |  | 428 | 2352.08 |  | ok | 1 |  |  | 1 | 1 | 3 | 5 |  | No | [Commercial interest]: model selecting less than queue (model = 2352, queue = 2595 MW) [Prior yr]:Changed from 428 to 2352 MW. | 1
New_Mexico_Solar |  |  | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
Baja_California_Solar |  |  | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
Baja_California_Wind |  |  | 0 | 600 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  | No | [Consistency w prior year]: Baja wind does not appear in 2018 PSP busbar mapping results. Model selection is consistent with queue. | 1
Pacific_Northwest_Wind |  |  | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
Idaho_Wind |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Utah_Wind |  |  | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Wyoming_Wind |  |  | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
Arizona_Wind |  |  | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
New_Mexico_Wind |  |  | 0 | 606.17 |  | ok | 1 |  |  | 3 | 3 | 2 |  |  | No | [Commercial interest]: Stakeholder comments indicate commercial interest, but New Mexico wind is not found by state in the queue. [Prior yr]: Changed from 0 to 606 MW. | 1
Sub Total - Renewables |  |  | 9011 | 14460.49 | [12 empty] | 1
Pumped Storage Hydro |  |  | 0 | 973
Total |  |  | 9011 | 15433.49 | [12 empty] | 1

## Dashboard 2019RSP (Round 0 adj)
IRP Busbar Mapping Dashboard
Purpose: Quickly communicate compliance of portfolio mapping with the criteria per the Methodology. Highlight MW amounts by zone that breach criteria, if any, and identify next steps as part of the iterative process.
2019 RSP
Pre Round 1 - Adjusted with inter-resource Reallocations |  |  | Selected | Selected | Adjusted | Compliance with Criteria
| Resource Selection |  | Resources | Resources | Resources | [1=Yes, 2=Possible/Moderate, 3=Materially in Breach] | [9 empty] | Actions
Resource | 2030 FCDS MW | 2030 EO MW | Total MW (2018 PSP) | Total MW (2019 RSP) | Total MW (2019 RSP adj) | 1. Distance to Trans. |  | 2. Trans. Capability | 3a. Available Land Area | 3b. High Env. Impl. | [lookup formula] | 4. Comm. Interest | 5. Consistency with Prior Year's Mapping | Sum of criteria | Low-Effort Adjustment Available? | Further Round of Mapping Needed? | Comment; Potential Solutions for Consideration | Include in display?
InState_Biomass |  |  | 0 | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Greater_Imperial_Geothermal |  |  | 1256 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 3 | 5 |  |  |  | 1
Inyokern_North_Kramer_Geothermal |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Northern_California_Geothermal |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 |  | 2 |  |  |  | 0
Pacific_Northwest_Geothermal |  |  | 0 | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
Riverside_Palm_Springs_Geothermal |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Solano_Geothermal |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Southern_Nevada_Geothermal |  |  | 0 | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
Carrizo_Solar |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Carrizo_Wind |  |  | 160 | 287 | 287 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  |  |  | 1
Central_Valley_North_Los_Banos_Solar |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Central_Valley_North_Los_Banos_Wind |  |  | 146 | 173 | 173 |  | ok | 1 |  |  | 1 | 1 | 1 | 3 | Yes |  |  | 1
Distributed_Solar |  |  | 0 | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Distributed_Wind |  |  | 0 | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Greater_Imperial_Solar |  |  | 0 | 547.9 | 547.9 |  | ok | 1 |  |  | 2 | 2 | 2 | 5 |  |  |  | 1
Greater_Imperial_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Greater_Kramer_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Humboldt_Wind |  |  | 0 | 34 | 34 |  | ok | 1 |  |  |  |  | 2 | 3 |  |  |  | 1
Inyokern_North_Kramer_Solar |  |  | 554 | 97 | 97 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  |  |  | 1
Kern_Greater_Carrizo_Solar |  |  | 0 | 241.66 | 978.66 |  | ok | 3 |  |  | 1 | 1 | 2 |  |  | Yes after Round 1 | Moved 737 MW from Westlands_Ex solar to Kern Greater Carrizo, FCDS. See "porposedAdjustments" tab, adjustment 3. | 1
Kern_Greater_Carrizo_Wind |  |  | 0 | 60 | 60 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  |  |  | 1
Kramer_Inyokern_Ex_Solar |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 | 3 | Yes |  |  | 0
Kramer_Inyokern_Ex_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Mountain_Pass_El_Dorado_Solar |  |  | 0 | 248 | 248 |  | ok | 3 |  |  | 1 | 1 | 2 |  |  | Yes after Round 1 | Converted from FD to EO | 1
North_Victor_Solar |  |  | 0 | 300 | 300 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  |  |  | 1
Northern_California_Ex_Solar |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Northern_California_Ex_Wind |  |  | 0 | 865.9 | 865.9 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 | Yes | After Rnd 1 |  | 1
NW_Ext_Tx_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
Riverside_Palm_Springs_Solar |  |  | 1622 | 0 | 1000 |  | ok | 3 |  |  | 1 | 1 | 1 | 5 |  | Yes after Round 1 | Moved 1000 MW from Tehachapi solar to Riverside Palm Springs Solar. This improved criteria 4 (commercial interest) and 5 (delta from prior yr). See tab "proposedAdjustments", adjustment 1. However, after adjustment 1, the sum of the subzones exceeded the SCADSNV outermost zone limit. | 1
Riverside_Palm_Springs_Wind |  |  | 42 | NA | NA |  | ok | 1 |  |  | 1 | 1 |  | 2 |  |  | Resource not included in latest version of RESOLVE | 1
Sacramento_River_Solar |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Sacramento_River_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
SCADSNV_Solar |  |  | 0 | 330 | 330 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  |  |  | 1
SCADSNV_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Solano_Solar |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Solano_subzone_Solar |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Solano_subzone_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Solano_Wind |  |  | 644 | 542 | 542 |  | ok | 1 |  |  | 1 | 1 | 1 | 3 |  |  |  | 1
Southern_California_Desert_Ex_Solar |  |  | 0 | 862 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  | Moved 862 MW from Southern California Desert Ex Solar to SNV solar. This improved criteria 2 (tx capability), 4 (comm int) and 5 (delta from prior yr). See tab "proposedAdjustments", adjustment 2 | 1
Southern_California_Desert_Ex_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Southern_Nevada_Solar |  |  | 3006 | 0 | 862 |  | ok | 3 |  |  | 1 | 1 | 3 | 7 |  | Yes after Round 1 | Moved 862 MW from Southern California Desert Ex Solar to SNV solar. This improved criteria 4 (comm int). See tab "proposedAdjustments", adjustment 2 | 1
Southern_Nevada_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
SW_Ext_Tx_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
Tehachapi_Solar |  |  | 1153 | 4202 | 3202 |  | ok | 1 |  |  | 1 | 1 | 3 | 5 |  |  | Moved 1000 MW from Tehachapi solar to Riverside Palm Springs Solar. This did not change any criteria. See tab "proposedAdjustments", adjustment 1 | 1
Tehachapi_Ex_Solar |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 | 3 | Yes |  |  | 0
Tehachapi_Wind |  |  | 0 | 275 | 275 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  |  |  | 1
Westlands_Ex_Solar |  |  | 0 | 1778.57 | -0.43 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  | Moved 1779 from Westlands_Ex solar to Westlands solar (same rationale as above). [Update]: only 1041 MW can be added to Westlands before breaching FCDS tx limit. Move the remaining amount (737 MW) to Kern Greater Carrizo, FCDS. This improvied criteria 2 (tx capability) and 5 (delta from prior yr). See tab "proposedAdjustments", adjustment 3. | 1
Westlands_Ex_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  | 1 | 1 | 1 |  |  |  |  | 0
Westlands_Solar |  |  | 0 | 58.21 | 1099.21 |  | ok | 3 |  |  | 3 | 3 | 3 |  |  | Yes after Round 1 | Moved 1779 from Westlands_Ex solar to core zones. [Update]: only 1041 MW can be added to Westlands before breaching FCDS tx limit. Move the remaining amount (737 MW) to Kern Greater Carrizo, FCDS. This slightly improved criteria 4 (commercial interest), bringing Westlands solar up from 58 MW to 1099 MW, the max amount it can accept on the existing tx system without upgrades. It still falls short of commercial interest, which is ~5000 MW in this zone. This worsened the delta from prior yr (changed it from 2 to 3), since the delta increased. However, prior year departed from commercial interest even further, since prior year amount was zero. See tab "proposedAdjustments", adjustment 3. | 1
Cape_Mendocino_Offshore_Wind |  |  | 0 | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Del_Norte_Offshore_Wind |  |  | 0 | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Diablo_Canyon_Offshore_Wind_Ext_Tx |  |  | 0 | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Diablo_Canyon_Offshore_Wind |  |  | 0 | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Humboldt_Bay_Offshore_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
Morro_Bay_Offshore_Wind |  |  | 0 | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Utah_Solar |  |  | 0 | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Arizona_Solar |  |  | 428 | 2352.08 | 2352.08 |  | ok | 1 |  |  | 1 | 1 | 3 | 5 |  |  |  | 1
New_Mexico_Solar |  |  | 0 | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
Baja_California_Solar |  |  | 0 | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
Baja_California_Wind |  |  | 0 | 600 | 600 |  | ok | 1 |  |  | 1 | 1 | 2 | 4 |  |  |  | 1
Pacific_Northwest_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
Idaho_Wind |  |  | 0 | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Utah_Wind |  |  | 0 | 0 | 0 |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 0
Wyoming_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
Arizona_Wind |  |  | 0 | 0 | 0 |  | ok | 1 |  |  |  |  | 1 |  |  |  |  | 0
New_Mexico_Wind |  |  | 0 | 606.17 | 606.17 |  | ok | 1 |  |  | 1 | 1 | 2 |  |  |  | [Commercial interest]: Stakeholder comments indicate commercial interest, but New Mexico wind is not found by state in the queue. [Prior yr]: Changed from 0 to 606 MW. | 1
Sub Total - Renewables |  |  | 9011 | 14460.49 | 14459.49 | [12 empty] | 1
Total |  |  | 9011 | 14460.49 | 14459.49 | [12 empty] | 1

## Dashboard 2019RSP (Round 1)
IRP Busbar Mapping Dashboard
Purpose: Quickly communicate compliance of portfolio mapping with the criteria per the Methodology. Highlight MW amounts by zone that breach criteria, if any, and identify next steps as part of the iterative process.
2019 RSP
Post Round 1 | Selected | Selected | Adjusted | Compliance with Criteria
| Resources | Resources | Resources | [1=Yes, 2=Possible/Moderate, 3=Materially in Breach] | [6 empty] | Actions
Resource | Total MW (2018 PSP) | Total MW (2019 RSP) | Total MW (2019 RSP adj) | 1. Distance to Trans. |  | 2. Trans. Capability | 3a. Available Land Area | 3b. High Env. Impl. | 4. Comm. Interest | 5. Consistency with Prior Year's Mapping | Further Round of Mapping Needed? | Comment; Potential Solutions for Consideration | Include in display?
Greater_Imperial_Geothermal | 1256 | 0 | 0 | 1 | ok | 1 | 1 | 1 | 1 | 3 | No |  | 1
Carrizo_Wind | 160 | 287 | 287 | 1 | ok | 1 | 2 | 2 | 1 | 2 | No | [Available land area]: some sites exceed available land | 1
Central_Valley_North_Los_Banos_Wind | 146 | 173 | 173 | 2 | ok | 1 | 2 | 2 | 1 | 1 | Yes after Round 1 | [Distance to transmission]: Move to Westlands zone, because Westlands has closer substation. [Available land area]: some sites exceed available land. | 1
Greater_Imperial_Solar | 0 | 547.9 | 547.9 | 1 | ok | 1 | 1 | 1 | 2 | 2 | No |  | 1
Humboldt_Wind | 0 | 34 | 34 | 1 | ok | 1 | 2 | 2 |  | 2 | No | [Available land area]: some sites exceed available land | 1
Inyokern_North_Kramer_Solar | 554 | 97 | 97 | 1 | ok | 1 | 1 | 1 | 1 | 2 | No |  | 1
Kern_Greater_Carrizo_Solar | 0 | 241.66 | 978.66 | 1 | ok | 3 | 1 | 1 | 1 | 2 | Yes after Round 1 | [Tx capability]: After adjustment 3, the sum of the subzones exceeded the Southern PG&E outermost zone capability. Move the excess to Gates-Diablo 500 kV system, per ISO guidance. See tab "proposed adjustments", adjustment 5. | 1
Kern_Greater_Carrizo_Wind | 0 | 60 | 60 | 2 | ok | 1 | 1 | 1 | 1 | 2 | Yes after Round 1 | [Distance to transmission]: Assign to Cholame Sub to reduce gentie distance. May require local upgrade to connect project(s) See "proposedAdjustments" tab, adjustment 8. | 1
Mountain_Pass_El_Dorado_Solar | 0 | 248 | 248 | 1 | ok | 3 | 1 | 1 | 1 | 2 | Yes after Round 1 | [Tx capability]: Reverse FD to EO conversion. See tab "proposedAdjustments", adjustment 10. | 1
North_Victor_Solar | 0 | 300 | 300 | 1 | ok | 1 | 1 | 1 | 1 | 2 | No |  | 1
Northern_California_Ex_Wind | 0 | 865.9 | 865.9 | 1 | ok | 1 | 2 | 1 | 1 | 2 | No |  | 1
Riverside_Palm_Springs_Solar | 1622 | 0 | 1000 | 1 | ok | 3 | 1 | 1 | 1 | 1 | Yes after Round 1 | [Tx capability]: After adjustment 1, the sum of the subzones exceeded the SCADSNV outermost zone limit. Reverse adjustment. Move 1000 MW back from Riverside to Techachapi. See tab proposed adjustments, adjustment 6. | 1
Riverside_Palm_Springs_Wind | 42 | #N/A | #N/A | [7 empty] | No | Resource not included in latest version of RESOLVE
SCADSNV_Solar | 0 | 330 | 330 | 1 | ok | 1 | 1 | 1 | 1 | 2 | No |  | 1
Solano_Wind | 644 | 542 | 542 | 1 | ok | 1 | 2 | 2 | 1 | 1 | No | [Available land area]: some sites exceed available land. | 1
Southern_California_Desert_Ex_Solar | 0 | 862 | 0 | 1 | ok | 1 | 1 | 1 | 1 | 1 | No |  | 1
Southern_Nevada_Solar | 3006 | 0 | 862 | 1 | ok | 3 | 1 | 1 | 1 | 3 | Yes after Round 1 | [Tx capability]: Adjustment 2 resulted in the sum of subzones exceeding outermost zone tx capability. Move the excess (264 MW) to Mohave/Eldorado 500 kV substations. These are electrically outside the SCADSNV outermost zone transmission constraint. See tab "proposedAdjustments" adjustment 7. | 1
Tehachapi_Solar | 1153 | 4202 | 3202 | 1 | ok | 1 | 1 | 1 | 1 | 3 | Yes after Round 1 | [Tx capability]: After adjustment 1, the sum of the subzones exceeded the SCADSNV outermost zone limit. Reverse adjustment. Move 1000 MW back from Riverside to Techachapi. See tab proposed adjustments, adjustment 6. | 1
Tehachapi_Wind | 0 | 275 | 275 | 1 | ok | 1 | 2 | 1 | 1 | 2 | No | [Available land area]: some sites exceed available land. | 1
Westlands_Ex_Solar | 0 | 1778.57 | -0.43 | 1 | ok | 1 | 1 | 1 | 1 | 1 | No |  | 1
Westlands_Solar | 0 | 58.21 | 1099.21 | 1 | ok | 3 | 1 | 1 | 3 | 3 | Yes after Round 1 | [Tx capability]: Adjustment 3 caused the sum of the subzones to exceed the Southern PG&E outermost zone capability. Move the excess to Gates-Diablo 500 kV system, per ISO guidance. Gates-Diablo 500 kV system appears geographically in the Southern PG&E zone, but electrically it is outside the transmission constraint. See tab "proposedAdjustments" adjustment 5. | 1
Arizona_Solar | 428 | 2352.08 | 2352.08 |  | ok | 1 |  |  | 1 | 3 | No |  | 1
Baja_California_Wind | 0 | 600 | 600 |  | ok | 1 |  |  | 1 | 2 | No |  | 1
New_Mexico_Wind | 0 | 606.17 | 606.17 |  | ok | 1 |  |  |  | 2 | No |  | 1
Sub Total - Renewables | 9011 | 14460.49 | 14459.49 | [9 empty] | 1
Total | 9011 | 14460.49 | 14459.49 | [9 empty] | 1

## Dashboard 2019RSP (Round 2)
IRP Busbar Mapping Dashboard
Purpose: Quickly communicate compliance of portfolio mapping with the criteria per the Methodology. Highlight MW amounts by zone that breach criteria, if any, and identify next steps as part of the iterative process.
2019 RSP
Post Round 2 |  | Selected | Selected | Adjusted | Compliance with Criteria
|  | Resources | Resources | Resources | [1=Yes, 2=Possible/Moderate, 3=Materially in Breach] | [6 empty] | Actions
Resource | Tx Zone | Total MW (2018 PSP) | Total MW (2019 RSP) | Total MW (2019 RSP adj) | 1. Distance to Trans. |  | 2. Trans. Capability | 3a. Available Land Area | 3b. High Env. Impl. | 4. Comm. Interest | 5. Consistency with Prior Year's Mapping | Further Round of Mapping Needed? | Comment; Potential Solutions for Consideration
Greater_Imperial_Geothermal | SCADSNV-Greater_Imperial | 1256 | 0 | 0 | 1 | ok | 1 | 1 | 1 | 1 | 3 | No | [Prior yr]: delta from prior yr is ok, per tri-agency working group discussion.
Carrizo_Wind | Carrizo-Kern_Greater_Carrizo-SPGE | 160 | 287 | 287 | 1 | ok | 1 | 2 | 2 | 1 | 2 | No
Central_Valley_North_Los_Banos_Wind | Central_Valley_North_Los_Banos-SPGE | 146 | 173 | 173 | 1 | ok | 1 | 2 | 2 | 1 | 1 | No | [Distance to tx]: improved with adjustment: assigned to closer substation
Greater_Imperial_Solar | SCADSNV-Greater_Imperial | 0 | 547.9 | 547.9 | 1 | ok | 1 | 1 | 1 | 2 | 2 | No
Humboldt_Wind | Humboldt-Sacramento_River | 0 | 34 | 34 | 1 | ok | 1 | 2 | 2 |  | 2 | No | [Comm int]: not found in queue
Inyokern_North_Kramer_Solar | Inyokern_North_Kramer-Greater_Kramer | 554 | 97 | 97 | 1 | ok | 1 | 1 | 1 | 1 | 2 | No
Kern_Greater_Carrizo_Solar | Kern_Greater_Carrizo-SPGE | 0 | 241.66 | 241.66 | 1 | ok | 1 | 1 | 1 | 1 | 2 | No | Criteria 2 improved
Kern_Greater_Carrizo_Wind | Kern_Greater_Carrizo-SPGE | 0 | 60 | 60 | 1 | ok | 1 | 1 | 1 | 1 | 2 | No | [Distance to tx]: improved with adjustment: assigned to closer substation
Mountain_Pass_El_Dorado_Solar | N/A | 0 | 248 | 248 | 1 | ok | 1 | 1 | 1 | 1 | 2 | No
North_Victor_Solar | North_Victor-Greater_Kramer | 0 | 300 | 300 | 1 | ok | 1 | 1 | 1 | 1 | 2 | No
Northern_California_Ex_Wind | Sacramento_River | 0 | 865.9 | 865.9 | 1 | ok | 1 | 2 | 1 | 1 | 2 | No
Riverside_Palm_Springs_Solar | SCADSNV-Riverside_Palm_Springs | 1622 | 0 | 0 | 1 | ok | 1 | 1 | 1 | 2 | 3 | No | [Prior yr]: Adding MW to bring up closer to prior year created SCADSNV outermost zone tx limit exceedance
Riverside_Palm_Springs_Wind |  | 42 | #N/A | #N/A | [8 empty] | [Prior yr]: Resource not considered in RESOLVE in 2019 model version
SCADSNV_Solar | SCADSNV | 0 | 330 | 330 | 1 | ok | 1 | 1 | 1 | 1 | 2 | No
Solano_Wind | Sacramento_River-Solano | 644 | 542 | 542 | 1 | ok | 1 | 2 | 2 | 1 | 1 | No
Southern_California_Desert_Ex_Solar | Southern_California_Desert_Ex | 0 | 862 | 0 | 1 | ok | 1 | 1 | 1 | 1 | 1 | No
Southern_Nevada_Solar | SCADSNV-GLW_VEA | 3006 | 0 | 862 | 1 | ok | 1 | 1 | 1 | 1 | 3 | No | [Prior yr]: Delta from prior year is ok. See tab "SNV_Detail". The amount at the individual substations is consistent with prior yr. For example the sum of the allocation to three substations (Innovation, Desert View, Crazy Eyes) was 700 MW last year, and is 700 MW this year. Two substations receive allocations from three RESOLVE resources: SCADSNV_Solar, Mountain_Pass_El_Dorado_Solar, Southern_Nevada_Solar.
Tehachapi_Solar | Tehachapi | 1153 | 4202 | 4202 | 1 | ok | 1 | 1 | 1 | 1 | 3 | No | [Prior yr]: Delta from prior year is ok. Reducing MW to bring down closer to prior yr not possible: tried to move MW to SCADSNV but this exceeded tx capability in SCADSNV.
Tehachapi_Wind | Tehachapi | 0 | 275 | 275 | 1 | ok | 1 | 2 | 1 | 1 | 2 | No
Westlands_Ex_Solar | Westlands_Ex | 0 | 1778.57 | -0.43 | 1 | ok | 1 | 1 | 1 | 1 | 1 | No
Westlands_Solar | Central_Valley_North_Los_Banos-SPGE | 0 | 58.21 | 1836.21 | 1 | breach | 3 | 1 | 1 | 3 | 3 | No | [Tx limits]: What looks like an exceedance of transmission capability is in fact alleviated by adjustments to Westlands solar at the substation level. Excess is allocated to Gates-Diablo 500 kV system. Gates-Diablo 500 kV system appears geographically in the Southern PG&E zone, but electrically it is outside the transmission constraint. [Comm int]: Not possible to increasing MW to bring amount up closer to commercial interest, because tx capability is binding. Commercial interest = 5000 MW. Tx capability on existing system is 1100 MW. Criteria 2, 4 and 5 work against each other in this zone. Zero MW prior yr. 5000 MW commercial interest. 1000 MW tx capability.
Arizona_Solar | SCADSNV-Riverside_Palm_Springs | 428 | 2352.08 | 2352.08 |  | ok | 1 |  |  | 1 | 3 | No | [Prior yr]: Delta from prior year is ok. Increased more than 1000 MW from prior yr, but this brings the total up closer to commercial interest (queue = 2595 MW)
Baja_California_Wind | SCADSNV-Greater_Imperial | 0 | 600 | 600 |  | ok | 1 |  |  | 1 | 2 | No
New_Mexico_Wind | SCADSNV-Riverside_Palm_Springs | 0 | 606.17 | 606.17 |  | ok | 1 |  |  |  | 2 | No | [Distance to tx]: confirmed delivery point to California with commercial interest. [Comm int]: not found in queue
Sub Total - Renewables |  | 9011 | 14460.49 | 14459.49
Pumped Storage Hydro |  | 0 | 973 | 974 | 1 | breach | 1 |  |  | 1 | 2 | No | [Tx limits]: Located in GreaterImpOutsideTxConstraintZones. Confirmed ok with ISO.
Total |  | 9011 | 15433.49 | 15433.49

## SelectedPortfolio_2019RSP
Extract from: | RESOLVE_Results_Viewer_2020-02-07 | 46MMT_20200207_2045_2GWPRM_NOOTCEXT_RSP_PD
Portfolio Analytics
| FCDS Renewable Resource Summary by Location (MW) |  |  |  |  | EO Renewable Resource Summary by Location (MW)
| RESOLVE Resource | Tx Zone | 2030 FD | Proposed Adjustment | Adjusted Value (FD) | RESOLVE Resource | Tx Zone | 2030 EO | Proposed Adjustment | Adjusted Value (EO) | FD + EO | Adjusted (FD + EO)
| InState_Biomass | None | 0 | 0 | 0 | InState_Biomass | None | 0 | 0 | 0 | 0 | 0
| Greater_Imperial_Geothermal | SCADSNV-Greater_Imperial | 0 | 0 | 0 | Greater_Imperial_Geothermal | SCADSNV-Greater_Imperial | 0 | 0 | 0 | 0 | 0
| Inyokern_North_Kramer_Geothermal | Inyokern_North_Kramer-Greater_Kramer | 0 | 0 | 0 | Inyokern_North_Kramer_Geothermal | Inyokern_North_Kramer-Greater_Kramer | 0 | 0 | 0 | 0 | 0
| Northern_California_Ex_Geothermal | Northern_California_Ex | 0 | 0 | 0 | Northern_California_Ex_Geothermal | Northern_California_Ex | 0 | 0 | 0 | 0 | 0
| Pacific_Northwest_Geothermal | N/A | 0 | 0 | 0 | Pacific_Northwest_Geothermal | N/A | 0 | 0 | 0 | 0 | 0
| Riverside_Palm_Springs_Geothermal | SCADSNV-Riverside_Palm_Springs | 0 | 0 | 0 | Riverside_Palm_Springs_Geothermal | SCADSNV-Riverside_Palm_Springs | 0 | 0 | 0 | 0 | 0
| Solano_Geothermal | Sacramento_River-Solano | 0 | 0 | 0 | Solano_Geothermal | Sacramento_River-Solano | 0 | 0 | 0 | 0 | 0
| Southern_Nevada_Geothermal | Mountain_Pass_El_Dorado-SCADSNV | 0 | 0 | 0 | Southern_Nevada_Geothermal | Mountain_Pass_El_Dorado-SCADSNV | 0 | 0 | 0 | 0 | 0
| Carrizo_Solar | Carrizo-Kern_Greater_Carrizo-SPGE | 0 | 0 | 0 | Carrizo_Solar | Carrizo-Kern_Greater_Carrizo-SPGE | 0 | 0 | 0 | 0 | 0
| Carrizo_Wind | Carrizo-Kern_Greater_Carrizo-SPGE | 287 | 0 | 287 | Carrizo_Wind | Carrizo-Kern_Greater_Carrizo-SPGE | 0 | 0 | 0 | 287 | 287
| Central_Valley_North_Los_Banos_Solar | Central_Valley_North_Los_Banos-SPGE | 0 | 0 | 0 | Central_Valley_North_Los_Banos_Solar | Central_Valley_North_Los_Banos-SPGE | 0 | 0 | 0 | 0 | 0
| Central_Valley_North_Los_Banos_Wind | Central_Valley_North_Los_Banos-SPGE | 173 | 0 | 173 | Central_Valley_North_Los_Banos_Wind | Central_Valley_North_Los_Banos-SPGE | 0 | 0 | 0 | 173 | 173
| Distributed_Solar | None | 0 | 0 | 0 | Distributed_Solar | None | 0 | 0 | 0 | 0 | 0
| Distributed_Wind | #N/A | 0 | 0 | 0 | Distributed_Wind | #N/A | 0 | 0 | 0 | 0 | 0
| Greater_Imperial_Solar | SCADSNV-Greater_Imperial | 0 | 0 | 0 | Greater_Imperial_Solar | SCADSNV-Greater_Imperial | 547.9 | 0 | 547.9 | 547.9 | 547.9
| Greater_Imperial_Wind | SCADSNV-Greater_Imperial | 0 | 0 | 0 | Greater_Imperial_Wind | SCADSNV-Greater_Imperial | 0 | 0 | 0 | 0 | 0
| Greater_Kramer_Wind | Greater_Kramer | 0 | 0 | 0 | Greater_Kramer_Wind | Greater_Kramer | 0 | 0 | 0 | 0 | 0
| Humboldt_Wind | Humboldt-Sacramento_River | 0 | 0 | 0 | Humboldt_Wind | Humboldt-Sacramento_River | 34 | 0 | 34 | 34 | 34
| Inyokern_North_Kramer_Solar | Inyokern_North_Kramer-Greater_Kramer | 97 | 0 | 97 | Inyokern_North_Kramer_Solar | Inyokern_North_Kramer-Greater_Kramer | 0 | 0 | 0 | 97 | 97
| Kern_Greater_Carrizo_Solar | Kern_Greater_Carrizo-SPGE | 96.73 | 0 | 96.73 | Kern_Greater_Carrizo_Solar | Kern_Greater_Carrizo-SPGE | 144.93 | 0 | 144.93 | 241.66 | 241.66
| Kern_Greater_Carrizo_Wind | Kern_Greater_Carrizo-SPGE | 60 | 0 | 60 | Kern_Greater_Carrizo_Wind | Kern_Greater_Carrizo-SPGE | 0 | 0 | 0 | 60 | 60
| Kramer_Inyokern_Ex_Solar | Kramer_Inyokern_Ex | 0 | 0 | 0 | Kramer_Inyokern_Ex_Solar | Kramer_Inyokern_Ex | 0 | 0 | 0 | 0 | 0
| Kramer_Inyokern_Ex_Wind | Kramer_Inyokern_Ex | 0 | 0 | 0 | Kramer_Inyokern_Ex_Wind | Kramer_Inyokern_Ex | 0 | 0 | 0 | 0 | 0
| Mountain_Pass_El_Dorado_Solar | N/A | 248 | 0 | 248 | Mountain_Pass_El_Dorado_Solar | N/A | 0 | 0 | 0 | 248 | 248
| North_Victor_Solar | North_Victor-Greater_Kramer | 300 | 0 | 300 | North_Victor_Solar | North_Victor-Greater_Kramer | 0 | 0 | 0 | 300 | 300
| Northern_California_Ex_Solar | Northern_California_Ex | 0 | 0 | 0 | Northern_California_Ex_Solar | Northern_California_Ex | 0 | 0 | 0 | 0 | 0
| Northern_California_Ex_Wind | Sacramento_River | 865.9 | 0 | 865.9 | Northern_California_Ex_Wind | Sacramento_River | 0 | 0 | 0 | 865.9 | 865.9
| NW_Ext_Tx_Wind | Sacramento_River | 0 | 0 | 0 | NW_Ext_Tx_Wind | Sacramento_River | 0 | 0 | 0 | 0 | 0
| Riverside_Palm_Springs_Solar | SCADSNV-Riverside_Palm_Springs | 0 | 0 | 0 | Riverside_Palm_Springs_Solar | SCADSNV-Riverside_Palm_Springs | 0 | 0 | 0 | 0 | 0
| Sacramento_River_Solar | Sacramento_River | 0 | 0 | 0 | Sacramento_River_Solar | Sacramento_River | 0 | 0 | 0 | 0 | 0
| Sacramento_River_Wind | N/A | 0 | 0 | 0 | Sacramento_River_Wind | N/A | 0 | 0 | 0 | 0 | 0
| SCADSNV_Solar | SCADSNV | 0 | 0 | 0 | SCADSNV_Solar | SCADSNV | 330 | 0 | 330 | 330 | 330
| SCADSNV_Wind | SCADSNV | 0 | 0 | 0 | SCADSNV_Wind | SCADSNV | 0 | 0 | 0 | 0 | 0
| Solano_Solar | Sacramento_River-Solano | 0 | 0 | 0 | Solano_Solar | Sacramento_River-Solano | 0 | 0 | 0 | 0 | 0
| Solano_subzone_Solar | Sacramento_River-Solano-Solano_subzone | 0 | 0 | 0 | Solano_subzone_Solar | Sacramento_River-Solano-Solano_subzone | 0 | 0 | 0 | 0 | 0
| Solano_subzone_Wind | Sacramento_River-Solano-Solano_subzone | 0 | 0 | 0 | Solano_subzone_Wind | Sacramento_River-Solano-Solano_subzone | 0 | 0 | 0 | 0 | 0
| Solano_Wind | Sacramento_River-Solano | 542 | 0 | 542 | Solano_Wind | Sacramento_River-Solano | 0 | 0 | 0 | 542 | 542
| Southern_California_Desert_Ex_Solar | Southern_California_Desert_Ex | 862 | -862 | 0 | Southern_California_Desert_Ex_Solar | Southern_California_Desert_Ex | 0 | 0 | 0 | 862 | 0
| Southern_California_Desert_Ex_Wind | Southern_California_Desert_Ex | 0 | 0 | 0 | Southern_California_Desert_Ex_Wind | Southern_California_Desert_Ex | 0 | 0 | 0 | 0 | 0
| Southern_Nevada_Solar | SCADSNV-GLW_VEA | 0 | 862 | 862 | Southern_Nevada_Solar | SCADSNV-GLW_VEA | 0 | 0 | 0 | 0 | 862
| Southern_Nevada_Wind | SCADSNV-GLW_VEA | 0 | 0 | 0 | Southern_Nevada_Wind | SCADSNV-GLW_VEA | 0 | 0 | 0 | 0 | 0
| SW_Ext_Tx_Wind | SCADSNV-Riverside_Palm_Springs | 0 | 0 | 0 | SW_Ext_Tx_Wind | SCADSNV-Riverside_Palm_Springs | 0 | 0 | 0 | 0 | 0
| Tehachapi_Solar | Tehachapi | 3402 | 0 | 3402 | Tehachapi_Solar | Tehachapi | 800 | 0 | 800 | 4202 | 4202
| Tehachapi_Ex_Solar | Tehachapi_Ex | 0 | 0 | 0 | Tehachapi_Ex_Solar | Tehachapi_Ex | 0 | 0 | 0 | 0 | 0
| Tehachapi_Wind | Tehachapi | 275 | 0 | 275 | Tehachapi_Wind | Tehachapi | 0 | 0 | 0 | 275 | 275
| Westlands_Ex_Solar | Westlands_Ex | 1778.57 | -1779 | -0.43 | Westlands_Ex_Solar | Westlands_Ex | 0 | 0 | 0 | 1778.57 | -0.43
| Westlands_Ex_Wind | N/A | 0 | 0 | 0 | Westlands_Ex_Wind | N/A | 0 | 0 | 0 | 0 | 0
| Westlands_Solar | Central_Valley_North_Los_Banos-SPGE | 58.21 | 1778 | 1836.21 | Westlands_Solar | Central_Valley_North_Los_Banos-SPGE | 0 | 0 | 0 | 58.21 | 1836.21
| Cape_Mendocino_Offshore_Wind | N/A | 0 | 0 | 0 | Cape_Mendocino_Offshore_Wind | N/A | 0 | 0 | 0 | 0 | 0
| Del_Norte_Offshore_Wind | N/A | 0 | 0 | 0 | Del_Norte_Offshore_Wind | N/A | 0 | 0 | 0 | 0 | 0
| Diablo_Canyon_Offshore_Wind_Ext_Tx | N/A | 0 | 0 | 0 | Diablo_Canyon_Offshore_Wind_Ext_Tx | N/A | 0 | 0 | 0 | 0 | 0
| Diablo_Canyon_Offshore_Wind | N/A | 0 | 0 | 0 | Diablo_Canyon_Offshore_Wind | N/A | 0 | 0 | 0 | 0 | 0
| Humboldt_Bay_Offshore_Wind | N/A | 0 | 0 | 0 | Humboldt_Bay_Offshore_Wind | N/A | 0 | 0 | 0 | 0 | 0
| Morro_Bay_Offshore_Wind | N/A | 0 | 0 | 0 | Morro_Bay_Offshore_Wind | N/A | 0 | 0 | 0 | 0 | 0
| Utah_Solar | N/A | 0 | 0 | 0 | Utah_Solar | N/A | 0 | 0 | 0 | 0 | 0
| Arizona_Solar | SCADSNV-Riverside_Palm_Springs | 1195.91 | 0 | 1195.91 | Arizona_Solar | SCADSNV-Riverside_Palm_Springs | 1156.17 | 0 | 1156.17 | 2352.08 | 2352.08
| New_Mexico_Solar | N/A | 0 | 0 | 0 | New_Mexico_Solar | N/A | 0 | 0 | 0 | 0 | 0
| Baja_California_Solar | N/A | 0 | 0 | 0 | Baja_California_Solar | N/A | 0 | 0 | 0 | 0 | 0
| Baja_California_Wind | SCADSNV-Greater_Imperial | 600 | 0 | 600 | Baja_California_Wind | SCADSNV-Greater_Imperial | 0 | 0 | 0 | 600 | 600
| Pacific_Northwest_Wind | N/A | 0 | 0 | 0 | Pacific_Northwest_Wind | N/A | 0 | 0 | 0 | 0 | 0
| Idaho_Wind | N/A | 0 | 0 | 0 | Idaho_Wind | N/A | 0 | 0 | 0 | 0 | 0
| Utah_Wind | N/A | 0 | 0 | 0 | Utah_Wind | N/A | 0 | 0 | 0 | 0 | 0
| Wyoming_Wind | Mountain_Pass_El_Dorado-SCADSNV | 0 | 0 | 0 | Wyoming_Wind | Mountain_Pass_El_Dorado-SCADSNV | 0 | 0 | 0 | 0 | 0
| Arizona_Wind | N/A | 0 | 0 | 0 | Arizona_Wind | N/A | 0 | 0 | 0 | 0 | 0
| New_Mexico_Wind | SCADSNV-Riverside_Palm_Springs | 606.17 | 0 | 606.17 | New_Mexico_Wind | SCADSNV-Riverside_Palm_Springs | 0 | 0 | 0 | 606.17 | 606.17
| In-State |  | 10841.32 |  | 10840.32 | In-State |  | 3013 |  | 3013 | 13854.32 | 13853.32
| Out-Of-State |  | 606.17 |  | 606.17 | Out-Of-State |  | 0 |  | 0 | 606.17 | 606.17
| Grand Total |  | 11447.49 |  |  | Note: Resources with #N/A as transmission zone were not made available to the model for this scenario |  | 3013 |  |  | 14460.49
| Pumped Storage Hydro | GreaterImpOutsideTxConstraintZones | 0 | 974 | 974 | Pumped Storage Hydro | GreaterImpOutsideTxConstraintZones | 0 | 0 | 0 | 0 | 974

## proposedAdjustments
| Proposed Adjustments | FD | EO
1 | Tehachapi_Solar | -1000 |  | Move 1000 MW from Tehachapi solar to Riverside Palm Springs Solar (Tehachapi model selection increased a lot, and Riverside Palm Springs model selection decreased a lot, for reasons which are not well understood)
| Riverside_Palm_Springs_Solar | 1000 |  | Reverse this adjustment. Doesn't meet SCADSNV outermost zone transmission limits.
2 | Southern_California_Desert_Ex_Solar | -862 |  | Move 862 MW from Southern California Desert Ex Solar to SNV solar (due to overlap in the tx capability estimates between “Ex” zone and core tx constraint zones – the estimates for the core zones have greater confidence and should probably supersede)
| Southern_Nevada_Solar | 862 |  | Amount that can fit without exceeding tx limits (note overflow to Greater_Imperial)
3 | Westlands_Ex_Solar | -1779 |  | Move 1779 from Westlands_Ex solar to Westlands solar (same rationale as above)
| Westlands_Solar | 1041 |  | [Note: the full amount could not fit within Westlands tx fcds limit, so the excess was allocated to Central Valley North Los Banos)
| Central_Valley_North_Los_Banos_Solar | 737
| Central_Valley_North_Los_Banos_Solar | -737 |  | Move the overflow solar (737 MW) from Westlands_Ex and Westlands to Kern and Greater Carrizo instead of Central Valley North Los Banos, to better reflect commercial interest
| Kern_Greater_Carrizo_Solar | 737
4 | Mountain_Pass_El_Dorado_Solar | -248 | 248 | Convert Mountain_Pass_El_Dorado_Solar from FD to EO per E3 guidance
5 | Kern_Greater_Carrizo_Solar | -737 |  | Adjustment 3 above caused the sum of the subzones to exceed the Southern PG&E outermost zone limit.
| Westlands_Solar | -616 |  | Move the excess to Gates-Diablo 500 kV system, per ISO guidance.
| Westlands_Solar | 1353 |  | Gates-Diablo 500 kV system appears geographically in the Southern PG&E zone, but electrically it is outside the transmission constraint.
6 | Tehachapi_Solar | 1000 |  | Although adjustment 1 above was ok with respect to the subzones, the sum of the subzones exceeded the SCADSNV outermost zone limit.
| Riverside_Palm_Springs_Solar | -1000 |  | Reverse adjustment 1
7 | Southern_Nevada_Solar | 0 |  | Adjustment 2 resulted in exceeding outermost zone limits. Move the excess to Mohave/Eldorado 500 kV substations. These are electrically outside the SCADSNV outermost zone transmission constraint.
8 | Kern_Greater_Carrizo_Wind | 0 |  | Assign to Cholame Sub to reduce gentie distance.
9 | Central_Valley_North_Los_Banos_Wind | 0 |  | Move this selection (173 MW) to Westlands tx zone because Westlands has closer substation. Note there is no "Westlands_Wind" RESOLVE resource, so this will appear as a tx-zone re-assignment in RESOLVE
10 | Mountain_Pass_El_Dorado_Solar | 248 | -248 | Remove the Mountain pass el dorado FD to EO conversion.
11 | Pumped Storage Hydro | 0 |  | Add pumped storage hydro to busbar mapping. No change to RESOLVE selection, simply new to busbar mapping.
Note on C18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changes occur at substation level within zone.
Note on C19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changes occur at substation level within zone.

## 2_TxCapability
What constitutes level 3 criteria flag? |  |  |  | Selected portfolio exceeds tx capability (FD or EO)
What constitutes level 2 criteria flag? |  |  |  | None
What constitutes level 1 criteria flag? |  |  |  | All other
| Transmission Capability Estimated for IRP (dated May 20, 2019) | [9 empty] | RESOLVE Selected Portfolio (2019 RSP) | [12 empty] | RESOLVE Selected Portfolio (2019RSP) Aggregated and Compared to Tx Constraint Zone Limits
| Transmission Zones | Estimated FCDS Capability (MW) |  |  |  | Incremental Upgrade Cost Estimate ($million) |  |  |  | Estimated EODS Capability (MW) | Resource | Zone | Selected by RESOLVE | Selected by RESOLVE (FD) | FD tx limit check | Selected by RESOLVE (EO) | EO tx limit check | FD + EO tx limit check | Adjusted Selected resources (FD) | FD tx limit check | Adjusted Selected resources (EO) | EO tx limit check | FD + EO tx limit check | Zone | 2019 RSP | [5 empty] | 2019 RSP (Adjusted)
|  | Existing System | Minor Upgrades | Major Upgrade #1 | Major Upgrade #2 | Existing System | Minor Upgrades | Major Upgrade #1 | Major Upgrade #2 | Existing System | InState_Biomass |  | 0 | 0 |  | 0 |  |  | 0 |  | 0 |  |  | Zone Name in RESOLVE | Selected Resource (FD MW) | Selected Resource (EO MW) | Remaining Tx Capability (FD) | Exceeds Tx Capability (FD)? | Remaining Tx Capability (EO) | Exceeds Tx Capability (EO)? | Selected Resource (FD MW) | Selected Resource (EO MW) | Remaining Tx Capability (FD) | Exceeds Tx Capability (FD)? | Remaining Tx Capability (EO) | Exceeds Tx Capability (EO)?
| Northern CA | 2000 |  | 2000 |  |  |  | 285 |  | 3900 | Greater_Imperial_Geothermal | SCADSNV_Z3_GreaterImperial | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
| Round Mountain | 500 | [7 empty] | 2100 | Inyokern_North_Kramer_Geothermal | GK_Z2_InyokernAndNorthOfKramer | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | Northern CA |  |  | 1458 |  | 1866 |  |  |  | 1458 |  | 1866
| Humboldt | 0 | [7 empty] | 100 | Northern_California_Geothermal | Norcal_Z3_SacramentoRiver | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | Norcal_Z2_Humboldt | 0 | 34 | 0 | 0 | 66 | 0 | 0 | 34 | 0 | 0 | 66 | 0
| Sacramento River | 2000 | [7 empty] | 4600 | Pacific_Northwest_Geothermal | Norcal_Z3_SacramentoRiver | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | Norcal_Z3_SacramentoRiver | 0 | 0 | 2000 | 0 | 2600 | 0 | 0 | 0 | 2000 | 0 | 2600 | 0
| Solano | 600 |  | 2000 |  |  |  | 322 |  | 1300 | Riverside_Palm_Springs_Geothermal | SCADSNV_Z4_RiversideAndPalmSprings | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | Norcal_Z4_Solano | 542 | 0 | 58 | 0 | 700 | 0 | 542 | 0 | 58 | 0 | 700 | 0
[11 empty] | Solano_Geothermal | Norcal_Z4_Solano | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | Norcal_Z4_Solano_subzone | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Southern PG&E | 1100 |  | 1000 |  |  |  | 55 |  | 4180 | Southern_Nevada_Geothermal | SCADSNV_Z5_SCADSNV | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | Southern PG&E |  |  | 425.06 |  | 2935.07 | 0 |  |  | -1352.94 |  | 2935.07
| Westlands | 1100 |  | 1000 |  |  |  | 55 |  | 2200 | Carrizo_Solar | SPGE_Z3_Carrizo | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | SPGE_Z1_Westlands | 58.21 | 0 | 1041.79 | 0 | 2200 | 0 | 1836.21 | 0 | -736.21 | 1 | 2200 | 0
| Kern and Greater Carrizo | 1000 |  | 1500 |  |  |  | 241 |  | 4180 | Carrizo_Wind | SPGE_Z3_Carrizo | 287 | 287 | ok | 0 | ok | ok | 287 | ok | 0 | ok | ok | SPGE_Z2_KernAndGreaterCarrizo | 156.73 | 144.93 | 843.27 | 0 | 4035.07 | 0 | 156.73 | 144.93 | 843.27 | 0 | 4035.07 | 0
| Carrizo | 400 |  | 700 |  |  |  | 53 |  | 400 | Central_Valley_North_Los_Banos_Solar | SPGE_Z4_CentralValleyAndLosBanos | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | SPGE_Z3_Carrizo | 287 | 0 | 113 | 0 | 0 | 0 | 287 | 0 | 113 | 0 | 0 | 0
| Central Valley North & Los Banos | 1000 |  | 1000 |  |  |  | 274 |  | 1000 | Central_Valley_North_Los_Banos_Wind | SPGE_Z4_CentralValleyAndLosBanos | 173 | 173 | ok | 0 | ok | ok | 173 | ok | 0 | ok | ok | SPGE_Z4_CentralValleyAndLosBanos | 173 | 0 | 827 | 0 | 1000 | 0 | 173 | 0 | 827 | 0 | 1000 | 0
[11 empty] | Distributed_Solar |  | 0 | 0 |  | 0 |  |  | 0 |  | 0
| Tehachapi | 4300 | 1000 |  |  |  | 100 |  |  | 5100 | Distributed_Wind |  | 0 | 0 |  | 0 |  |  | 0 |  | 0 |  |  | Tehachapi | 3677 | 800 | 623 | 0 | 0 | 0 | 3677 | 800 | 623 | 0 | 0 | 0
[11 empty] | Greater_Imperial_Solar | SCADSNV_Z3_GreaterImperial | 547.9 | 0 | ok | 547.9 | ok | ok | 0 | ok | 547.9 | ok | ok | Greater Kramer (North of Lugo) |  |  | 203 |  | 0 |  |  |  | 203 |  | 0
| Greater Kramer (North of Lugo) | 600 |  | 400 |  |  |  | 146 |  | 600 | Greater_Imperial_Wind | SCADSNV_Z3_GreaterImperial | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | GK_Z1_GreaterKramer | 0 | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 0 | 0
| North of Victor | 300 |  | 400 |  |  |  | 485 |  | 300 | Greater_Kramer_Wind | GK_Z1_GreaterKramer | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | GK_Z3_NorthOfVictor | 300 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0
| Inyokern and North of Kramer | 100 |  | 400 |  |  |  | 485 |  | 100 | Humboldt_Wind | Norcal_Z2_Humboldt | 34 | 0 | ok | 34 | ok | ok | 0 | ok | 34 | ok | ok | GK_Z2_InyokernAndNorthOfKramer | 97 | 0 | 3 | 0 | 0 | 0 | 97 | 0 | 3 | 0 | 0 | 0
| Pisgah | 400 |  | 400 |  |  |  | 261 |  | 400 | Inyokern_North_Kramer_Solar | GK_Z2_InyokernAndNorthOfKramer | 97 | 97 | ok | 0 | ok | ok | 97 | ok | 0 | ok | ok | GK_Z4_Pisgah | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0
[11 empty] | Kern_Greater_Carrizo_Solar | SPGE_Z2_KernAndGreaterCarrizo | 241.66 | 96.73 | ok | 144.93 | ok | ok | 96.73 | ok | 144.93 | ok | ok | Southern CA Desert and Southern NV |  |  | 349.92 |  | 4565.93 |  |  |  | -512.08 | 0 | 4895.93 | 0
| Southern CA Desert and Southern NV | 3000 |  | 2800 |  |  |  | 2156 |  | 9600 | Kern_Greater_Carrizo_Wind | SPGE_Z2_KernAndGreaterCarrizo | 60 | 60 | ok | 0 | ok | ok | 60 | ok | 0 | ok | ok | SCADSNV_Z5_SCADSNV | 0 | 330 | 3000 | 0 | 6270 | 0 | 862 | 330 | 2138 | 0 | 6270 | 0
| El Dorado and Mountain Pass 230 kV | 250 |  | 1400 |  |  |  | 76 |  | 2400 | Kramer_Inyokern_Ex_Solar | GK_Z2_InyokernAndNorthOfKramer | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | SCADSNV_Z1_EldoradoAndMtnPass | 248 | 0 | 2 | 0 | 2150 | 0 | 248 | 0 | 2 | 0 | 2150 | 0
| Southern NV (GLW-VEA) | 700 |  | 1400 |  |  |  | 150 |  | 700 | Kramer_Inyokern_Ex_Wind | GK_Z2_InyokernAndNorthOfKramer | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | SCADSNV_Z2_GLW_VEA | 0 | 0 | 700 | 0 | 0 | 0 | 0 | 0 | 700 | 0 | 0 | 0
| Greater Imperial* | 1200 |  | 1400 |  |  |  | 2334 |  | 3100 | Mountain_Pass_El_Dorado_Solar | SCADSNV_Z1_EldoradoAndMtnPass | 248 | 248 | ok | 0 | ok | ok | 248 | ok | 0 | ok | ok | SCADSNV_Z3_GreaterImperial | 600 | 547.9 | 600 | 0 | 1352.1 | 0 | 600 | 547.9 | 600 | 0 | 1352.1 | 0
| Riverside East & Palm Springs | 2950 |  | 1500 |  |  |  | 2156 |  | 5500 | North_Victor_Solar | GK_Z3_NorthOfVictor | 300 | 300 | ok | 0 | ok | ok | 300 | ok | 0 | ok | ok | SCADSNV_Z4_RiversideAndPalmSprings | 1802.08 | 1156.17 | 1147.92 | 0 | 1393.83 | 0 | 1802.08 | 1156.17 | 1147.92 | 0 | 1393.83 | 0
[11 empty] | Northern_California_Ex_Solar | NorCalOutsideTxConstraintZones | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | Ex Zones |  |  | 0.53
| GreaterImpOutsideTxConstraintZones | 0 | [8 empty] | Northern_California_Ex_Wind | NorCalOutsideTxConstraintZones | 865.9 | 865.9 | ok | 0 | ok | ok | 865.9 | ok | 0 | ok | ok | GreaterImpOutsideTxConstraintZones | 0 | 0 | 0 | 0 |  | 0 | 974 | 0 | -974 | 1 |  | 0
| KramerInyoOutsideTxConstraintZones | 0 | [8 empty] | NW_Ext_Tx_Wind | Norcal_Z3_SacramentoRiver | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | KramerInyoOutsideTxConstraintZones | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0
| NorCalOutsideTxConstraintZones | 866 | [8 empty] | Riverside_Palm_Springs_Solar | SCADSNV_Z4_RiversideAndPalmSprings | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | NorCalOutsideTxConstraintZones | 865.9 | 0 | 0.1 | 0 |  | 0 | 865.9 | 0 | 0.1 | 0 |  | 0
| TehachapiOutsideTxConstraintZones | 0 | [8 empty] | Riverside_Palm_Springs_Wind | SCADSNV_Z4_RiversideAndPalmSprings | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | TehachapiOutsideTxConstraintZones | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0
| WestlandsOutsideTxConstraintZones | 1779 | [8 empty] | Sacramento_River_Solar | Norcal_Z3_SacramentoRiver | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | WestlandsOutsideTxConstraintZones | 1778.57 | 0 | 0.43 | 0 |  | 0 | -0.43 | 0 | 1779.43 | 0 |  | 0
| SCADOutsideTxConstraintZones | 862 | [8 empty] | Sacramento_River_Wind | Norcal_Z3_SacramentoRiver | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok | SCADOutsideTxConstraintZones | 862 | 0 | 0 | 0 |  | 0 | 0 | 0 | 862 | 0 |  | 0
[11 empty] | SCADSNV_Solar | SCADSNV_Z5_SCADSNV | 330 | 0 | ok | 330 | ok | ok | 0 | ok | 330 | ok | ok | Total | 11447.49 | 3013 |  |  |  |  | 12420.49 | 3013
[11 empty] | SCADSNV_Wind | SCADSNV_Z5_SCADSNV | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[11 empty] | Solano_Solar | Norcal_Z4_Solano | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[11 empty] | Solano_subzone_Solar | Norcal_Z4_Solano_subzone | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[11 empty] | Solano_subzone_Wind | Norcal_Z4_Solano_subzone | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[11 empty] | Solano_Wind | Norcal_Z4_Solano | 542 | 542 | ok | 0 | ok | ok | 542 | ok | 0 | ok | ok
[11 empty] | Southern_California_Desert_Ex_Solar | SCADOutsideTxConstraintZones | 862 | 862 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[11 empty] | Southern_California_Desert_Ex_Wind | SCADOutsideTxConstraintZones | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[11 empty] | Southern_Nevada_Solar | SCADSNV_Z5_SCADSNV | 0 | 0 | ok | 0 | ok | ok | 862 | ok | 0 | ok | ok
[11 empty] | Southern_Nevada_Wind | SCADSNV_Z5_SCADSNV | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[11 empty] | SW_Ext_Tx_Wind | SCADSNV_Z4_RiversideAndPalmSprings | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[11 empty] | Tehachapi_Solar | Tehachapi | 4202 | 3402 | ok | 800 | ok | ok | 3402 | ok | 800 | ok | ok
[11 empty] | Tehachapi_Ex_Solar | TehachapiOutsideTxConstraintZones | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[11 empty] | Tehachapi_Wind | Tehachapi | 275 | 275 | ok | 0 | ok | ok | 275 | ok | 0 | ok | ok
[11 empty] | Westlands_Ex_Solar | WestlandsOutsideTxConstraintZones | 1778.57 | 1778.57 | ok | 0 | ok | ok | -0.43 | ok | 0 | ok | ok
[11 empty] | Westlands_Ex_Wind | WestlandsOutsideTxConstraintZones | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[11 empty] | Westlands_Solar | SPGE_Z1_Westlands | 58.21 | 58.21 | ok | 0 | ok | ok | 1836.21 | breach | 0 | ok | breach
[11 empty] | Cape_Mendocino_Offshore_Wind |  | 0 | 0 |  | 0 |  |  | 0 |  | 0
[11 empty] | Del_Norte_Offshore_Wind |  | 0 | 0 |  | 0 |  |  | 0 |  | 0
[11 empty] | Diablo_Canyon_Offshore_Wind_Ext_Tx |  | 0 | 0 |  | 0 |  |  | 0 |  | 0
[11 empty] | Diablo_Canyon_Offshore_Wind |  | 0 | 0 |  | 0 |  |  | 0 |  | 0
[11 empty] | Humboldt_Bay_Offshore_Wind | Norcal_Z2_Humboldt | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[11 empty] | Morro_Bay_Offshore_Wind |  | 0 | 0 |  | 0 |  |  | 0 |  | 0
[11 empty] | Utah_Solar |  | 0 | 0 |  | 0 |  |  | 0 |  | 0
[11 empty] | Arizona_Solar | SCADSNV_Z4_RiversideAndPalmSprings | 2352.08 | 1195.91 | ok | 1156.17 | ok | ok | 1195.91 | ok | 1156.17 | ok | ok
[11 empty] | New_Mexico_Solar | SCADSNV_Z4_RiversideAndPalmSprings | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[11 empty] | Baja_California_Solar | SCADSNV_Z3_GreaterImperial | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[11 empty] | Baja_California_Wind | SCADSNV_Z3_GreaterImperial | 600 | 600 | ok | 0 | ok | ok | 600 | ok | 0 | ok | ok
[11 empty] | Pacific_Northwest_Wind | Norcal_Z3_SacramentoRiver | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[11 empty] | Idaho_Wind |  | 0 | 0 |  | 0 |  |  | 0 |  | 0
[11 empty] | Utah_Wind |  | 0 | 0 |  | 0 |  |  | 0 |  | 0
[11 empty] | Wyoming_Wind | SCADSNV_Z5_SCADSNV | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[11 empty] | Arizona_Wind | SCADSNV_Z4_RiversideAndPalmSprings | 0 | 0 | ok | 0 | ok | ok | 0 | ok | 0 | ok | ok
[11 empty] | New_Mexico_Wind | SCADSNV_Z4_RiversideAndPalmSprings | 606.17 | 606.17 | ok | 0 | ok | ok | 606.17 | ok | 0 | ok | ok
[11 empty] | Pumped Storage Hydro | GreaterImpOutsideTxConstraintZones |  | 0 | ok | 0 | ok | ok | 974 | breach | 0 | ok | breach
[11 empty] | Total |  | 14460.49 | 11447.49 |  | 3013 |  |  | 12420.49 |  | 3013
Note on L7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Source: Feb2020_Resolve_tx_zones
Note on L15: Barave, Sushant: 1100 FC + 900 MW conventional gen + 10% increase
Note on AM15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This appears as an exceedance, but in post-processing, the excess is assigned to Gates-Diablo 500 kV system which is electrically outside the constraint.
Note on L16: Barave, Sushant: 1000 FC + 2800 MW conventional gen + 10% increase
Note on L18: Barave, Sushant: 1000 FC + 0 MW conventional gen
Note on AM33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This appears as an exceedance, but it ok because the resource is pumped hydro energy storage.

## CheckTab
Analysis of compliance of Round 1 mapping with criterion 2 (transmission limits), to inform changes needed in Round 2 of mapping
| Zone Name in RESOLVE | Selected Resource (FD MW) | Estimated FCDS Capacity (MW) Existing System | Remaining tx capacity (subzone) | Remaining tx capacity (outermost zone) | Selected Resource Adj (FD MW) | Remaining tx capability (FD MW) (subzone) | Remaining tx capability (FD MW) (outermost zone)
| Northern CA |  | 2000 |  | 1458 |  |  | 1458
| Norcal_Z2_Humboldt | 0 | 0 | 0 |  | 0 | 0
| Norcal_Z3_SacramentoRiver | 0 | 2000 | 2000 |  | 0 | 2000
| Norcal_Z4_Solano | 542 | 600 | 58 |  | 542 | 58
| Norcal_Z4_Solano_subzone | 0 | 0 | 0 |  | 0 | 0
| Southern PG&E |  | 1100 |  | 425.06 |  |  | -1352.94 | Moved 1779 from Westlands_Ex solar to Westlands solar, with overflow to Kern and Greater Carrizo
| SPGE_Z1_Westlands | 58.21 | 1100 | 1041.79 |  | 1836.21 | -736.21 |  | The above changes were ok with respect to subzone limits, but the sum of changes results in exceeding outermost zone limits.
| SPGE_Z2_KernAndGreaterCarrizo | 156.73 | 1000 | 843.27 |  | 156.73 | 843.27 |  | Mapped the excess to Gates-Diablo 500 kV line, per ISO guidance. Appears geographically in the Southern PG&E zone, but electrically outside the transmission constraint.
| SPGE_Z3_Carrizo | 287 | 400 | 113 |  | 287 | 113
| SPGE_Z4_CentralValleyAndLosBanos | 173 | 1000 | 827 |  | 173 | 827
| Tehachapi | 3677 | 4300 |  | 623 | 3677 |  | 623
| Greater Kramer (North of Lugo) |  | 600 |  | 203 |  |  | 203
| GK_Z1_GreaterKramer | 0 | 600 | 600 |  | 0 | 600
| GK_Z3_NorthOfVictor | 300 | 300 | 0 |  | 300 | 0
| GK_Z2_InyokernAndNorthOfKramer | 97 | 100 | 3 |  | 97 | 3
| GK_Z4_Pisgah | 0 | 400 | 400 |  | 0 | 400
| Southern CA Desert and Southern NV |  | 3000 |  | 349.92 |  |  | -512.08 | Moved 862 MW from Southern California Desert Ex Solar to SNV solar
| SCADSNV_Z5_SCADSNV | 0 | 3000 |  |  | 862 | 2138 |  | The above changes were ok with respect to subzone limits, but the sum of changes results in exceeding outermost zone limits.
| SCADSNV_Z1_EldoradoAndMtnPass | 248 | 250 | 2 |  | 248 | 2 |  | Movedthe excess to Mohave/Eldorado 500 kV substations. These are electrically outside the SCADSNV outermost zone transmission constraint.
| SCADSNV_Z2_GLW_VEA | 0 | 700 | 700 |  | 0 | 700
| SCADSNV_Z3_GreaterImperial | 600 | 1200 | 600 |  | 600 | 600
| SCADSNV_Z4_RiversideAndPalmSprings | 1802.08 | 2950 | 1147.92 |  | 1802.08 | 1147.92
| Ex Zones |  | 3507 |  | 0.53
| GreaterImpOutsideTxConstraintZones | 0 | 0 |  |  | 974 | -974
| KramerInyoOutsideTxConstraintZones | 0 | 0 |  |  | 0 | 0
| NorCalOutsideTxConstraintZones | 865.9 | 866 |  |  | 865.9 | 0.1
| TehachapiOutsideTxConstraintZones | 0 | 0 |  |  | 0 | 0
| WestlandsOutsideTxConstraintZones | 1778.57 | 1779 |  |  | -0.43 | 1779.43
| SCADOutsideTxConstraintZones | 862 | 862 |  |  | 0 | 862

## 3.1_SUM SOLAR RESOURCE ACRES
What constitutes level 3 criteria flag? |  | None
What constitutes level 2 criteria flag? |  | 20% | Exceeds this percentage utilization of available land in proximity to substation
What constitutes level 1 criteria flag? |  | All other
SELECTED
| Tx Zone/Substation | ACRES_15_LOW | ACRES_15_HIGH | TOTAL ACRES_15 | 1 | Tx Zone/Substation | ACRES_15_LOW | ACRES_15_HIGH | TOTAL ACRES_15 | Porportion of Total Acres | Potential MW | Potential MW Low | Potential MW High | MW Allocation | Percent Total ACRES | Percent ACRES Low | RESOLVE Resource | RESOLVE MW | Exceeds 0.2 Total? | Exceeds 0.2 Low? | Aggregated RESOLVE Resource | Criteria Threshold: Exceeds 0.2 (Total)? | Criteria Threshold: Exceeds 0.2 (Low)?
| GK_Z2_InyokernAndNorthOfKramer |  |  |  | 1 | GK_Z2_InyokernAndNorthOfKramer | [11 empty] | 97 | 0 | 0 | Inyokern_North_Kramer_Solar | 1 | 1
| Kramer | 22291.7169 | 108531.3471 | 130823.0641 | 1 | Kramer | 22291.7169 | 108531.3471 | 130823.0641 | 0.44248 | 18689.0092 | 3184.531 | 15504.4782 | 42.9208 | 0.1016% | 1.348% | Inyokern_North_Kramer_Solar |  | 0 | 0 | North_Victor_Solar | 1 | 1
| Randsburg | 32006.017 | 132827.725 | 164833.7421 | 1 | Randsburg | 32006.017 | 132827.725 | 164833.7421 | 0.55752 | 23547.6774 | 4572.2881 | 18975.3893 | 54.0792 | 0.128% | 1.183% | Inyokern_North_Kramer_Solar |  | 0 | 0 | Greater_Imperial_Solar | 1 | 1
[5 empty] | 1 | Total | 54297.734 | 241359.0722 | 295656.8061 |  | 42236.6866 | 7756.8191 | 34479.8675 | [5 empty] | 0 | 0 | Riverside_Palm_Springs_Solar | 1 | 1
| GK_Z3_NorthOfVictor |  |  |  | 1 | GK_Z3_NorthOfVictor | [12 empty] | 0 | 0 | Westlands_Solar | 1 | 1
| Caldwell | 202589.8284 | 157848.9787 | 360438.8071 | 1 | Caldwell | [11 empty] | 300 | 0 | 0 | Kern_Greater_Carrizo_Solar | 1 | 1
| Cool Water | 37473.5686 | 118138.4948 | 155612.0633 | 1 | Coolwater | 37473.5686 | 118138.4948 | 155612.0633 | 0.28306 | 22230.2948 | 5353.3669 | 16876.9278 | 84.918 | 0.1081% | 1.586% | North_Victor_Solar |  | 0 | 0 | Tehachapi_Solar | 1 | 1
| Victor | 226643.6098 | 167494.0413 | 394137.651 | 1 | Victor | 226643.6098 | 167494.0413 | 394137.651 | 0.71694 | 56305.3787 | 32377.6585 | 23927.7202 | 215.082 | 0.2739% | 0.6643% | North_Victor_Solar |  | 0 | 0 | Southern_Nevada_Solar | 1 | 1
| GK_Z4_Pisgah |  |  |  | 1 | Total | 264117.1784 | 285632.536 | 549749.7144 |  | 78535.6735 | 37731.0255 | 40804.648 | [5 empty] | 0 | 0 | Mountain_Pass_El_Dorado_Solar | 1 | 1
| Calcite | 263892.9909 | 637139.2422 | 901032.2331 | 0
| Lugo | 172373.9318 | 130196.009 | 302569.9407 | 0
| Pisgah | 33413.4063 | 60109.1333 | 93522.5395 | 0
0
| GreaterImpOutsideTxConstraintZones |  |  |  | 0
| Batiquitos | 157633.2279 | 47687.7448 | 205320.9727 | 0
| Calpeak Power Enterprise 7 | 202401.0742 | 121913.0151 | 324314.0893 | 0
| Doublett | 80436.4119 | 44591.8086 | 125028.2206 | 0
| Elliott | 45306.7779 | 46729.0408 | 92035.8187 | 0
| Encina | 126453.5357 | 24920.1506 | 151373.6864 | 0
| Escondido | 203431.2316 | 121928.098 | 325359.3296 | 0
| Fashion Valley | 28282.4774 | 16982.609 | 45265.0864 | 0 | [18 empty] | Summary of Solar Resource Acre Values within 15 miles of Selected Substations
| Friars | 30269.0864 | 20371.3117 | 50640.398 | 0 | [18 empty] | Substation | Acres_15_ LOW | Acres_15_HIGH | Total ACRES | Potential MW | Potential MW_LOW | Potential MW_HIGH | MW Allocation | Percent of Total _MW | Percent of ACRES_LOW
| Main St. | 8746.7355 | 7666.9279 | 16413.6634 | 0
| Mesa Rim | 74254.3006 | 55526.6452 | 129780.9458 | 0
| Mission | 32441.3434 | 23992.6928 | 56434.0363 | 0
| North City West | 96479.2733 | 49201.9852 | 145681.2584 | 0
| Old Town | 25582.5134 | 12290.2734 | 37872.7868 | 0
| Palomar Airport | 143556.2751 | 37740.1784 | 181296.4536 | 0
| Penasquitos | 81522.3916 | 44597.6923 | 126120.084 | 0
| San Luis Rey | 133892.5768 | 33713.6815 | 167606.2584 | 0
| San Onofre | 23572.9517 | 62717.5171 | 86290.4688 | 0
| Shadowridge | 174758.176 | 56678.4514 | 231436.6275 | 0
| Silvergate | 8282.4579 | 7914.0333 | 16196.4912 | 0
| Sycamore Canyon | 81712.499 | 110787.768 | 192500.267 | 0
0
| KramerInyoOutsideTxConstraintZones |  |  |  | 0
| Chino | 115236.3359 | 34277.8753 | 149514.2112 | 0
| Etiwanda | 119521.0822 | 34143.9662 | 153665.0484 | 0
| Mira Loma | 153868.1406 | 44776.7507 | 198644.8913 | 0
| Padua | 103281.4096 | 37943.9349 | 141225.3445 | 0
| Rancho Vista | 117868.9942 | 35516.3754 | 153385.3696 | 0
| San Bernardino | 109189.6264 | 93582.3238 | 202771.9502 | 0
| Soquel | 112556.4999 | 38097.3188 | 150653.8187 | 0
| Vista | 154339.3024 | 71821.2363 | 226160.5387 | 0
0
| Norcal_Z3_SacramentoRiver |  |  |  | 0
| Carberry | 63074.3128 | 243737.7267 | 306812.0395 | 0
| Delevan | 226931.429 | 151233.1065 | 378164.5356 | 0
| Glenn | 312380.3423 | 98004.73 | 410385.0723 | 0
| Hat Creek 2 | 136010.3823 | 217546.2146 | 353556.5969 | 0
| Palermo | 214738.2962 | 187411.8637 | 402150.1599 | 0
| Pit 1 | 141777.2142 | 214369.5514 | 356146.7657 | 0
| Pit 1 Ph | 141554.7552 | 215092.9619 | 356647.7171 | 0
| Rio Oso | 390290.7861 | 40333.9026 | 430624.6887 | 0
| Table Mt. | 240287.3948 | 158423.4159 | 398710.8107 | 0
| Thermalito | 249279.7572 | 157778.7081 | 407058.4653 | 0
0
| Norcal_Z4_Solano |  |  |  | 0
| Amerigas | 260413.6709 | 114394.6488 | 374808.3196 | 0
| Bear Canyon | 117353.1805 | 203393.727 | 320746.9075 | 0
| Big Geysers | 130672.7993 | 197241.7972 | 327914.5965 | 0
| Calistoga 19 | 139609.4804 | 188704.0246 | 328313.5051 | 0
| Calpeak Power Vaca Dixon 1 | 262551.2185 | 111982.5397 | 374533.7582 | 0
| Castro Valley | 46178.7025 | 79406.8554 | 125585.5579 | 0
| Cayetano | 116507.784 | 230435.0267 | 346942.8107 | 0
| Cobb Creek | 146233.0272 | 181413.1069 | 327646.1341 | 0
| Contra Costa | 200921.8609 | 142150.3168 | 343072.1777 | 0
| Contra Costa Power | 210000.4144 | 136982.7775 | 346983.1919 | 0
| Fulton | 167498.4994 | 182135.9074 | 349634.4069 | 0
| Fumarole | 143276.331 | 186186.9032 | 329463.2343 | 0
| Geysers Unit 3 | 143689.1321 | 184447.8953 | 328137.0274 | 0
| Grant 20 | 139258.9193 | 192918.5383 | 332177.4576 | 0
| Lake View | 156924.1896 | 171485.9075 | 328410.0971 | 0
| Lakeville | 154619.4171 | 185621.2358 | 340240.6529 | 0
| Lambie Energy | 239213.1528 | 117480.771 | 356693.9238 | 0
| Lone Tree | 189537.5436 | 155953.7273 | 345491.2709 | 0
| Mccabe | 143113.7335 | 185477.3419 | 328591.0754 | 0
| N.N. | 449206.5858 | 549784.8816 | 998991.4674 | 0
| Ncpa 1 & 2 | 123947.0021 | 205474.0457 | 329421.0479 | 0
| Ncpa 3 & 4 | 121199.8005 | 206076.1177 | 327275.9182 | 0
| Oakmont North | 172006.2238 | 168014.5395 | 340020.7633 | 0
| Oakmont South | 178163.2055 | 164286.0515 | 342449.2571 | 0
| Peabody | 208220.5506 | 151124.4904 | 359345.0409 | 0
| Quicksilver | 124619.0788 | 201651.3827 | 326270.4615 | 0
| San Ramon | 59665.4883 | 164536.9464 | 224202.4347 | 0
| San Ramon Research Cntr. | 58453.2899 | 139042.1832 | 197495.4731 | 0
| Shiloh II | 225035.404 | 123666.5318 | 348701.9359 | 0
| Shiloh III | 223955.7302 | 124121.0506 | 348076.7808 | 0
| Socrates 18 | 135799.7582 | 198058.0195 | 333857.7776 | 0
| Sonoma 3 | 141347.4875 | 188616.9857 | 329964.4732 | 0
| Sulphur Springs | 139885.3262 | 191618.038 | 331503.3642 | 0
| Tassajara | 84879.4268 | 164186.7603 | 249066.1871 | 0
| Technical Ecological Services | 58453.2899 | 138967.763 | 197421.0529 | 0
| Trans Bay Cable | 169698.3246 | 134040.0136 | 303738.3382 | 0
| Tulucay | 167010.6069 | 134029.5226 | 301040.1295 | 0
| Vaca-Dixon & Gc Yard | 259967.5594 | 113942.9106 | 373910.47 | 0
| West Ford Flat | 132006.477 | 192813.0644 | 324819.5414 | 0
0
| Norcal_Z4_Solano_subzone |  |  |  | 0
| Bahia | 89717.6016 | 122145.7596 | 211863.3612 | 0
| Embarcadero (Sf Z) | 11281.9223 | 9586.7575 | 20868.6798 | 0
| Ignacio | 97444.3114 | 129758.5219 | 227202.8334 | 0
| Moraga | 39756.753 | 50910.0988 | 90666.8518 | 0
| Parkway | 130355.1143 | 119287.6411 | 249642.7555 | 0
| Pittsburg | 142317.3105 | 145503.8206 | 287821.131 | 0
| Rossmoor | 57400.5593 | 90527.015 | 147927.5743 | 0
| Sobrante | 34876.0698 | 49388.9096 | 84264.9794 | 0
| Tidewater | 69222.6397 | 127137.4364 | 196360.0761 | 0
| Unocal | 88845.2603 | 87790.2136 | 176635.474 | 0
0
| NorCalOutsideTxConstraintZones |  |  |  | 0
| Brighton | 191632.1015 | 60091.9943 | 251724.0959 | 0
| Gold Hill | 129525.3865 | 192147.9308 | 321673.3173 | 0
| Jefferson | 7653.7133 | 89704.2996 | 97358.0129 | 0
| Logan Creek | 250598.194 | 139780.0319 | 390378.2259 | 0
| Martin | 5969.6971 | 14049.8915 | 20019.5886 | 0
| San Mateo | 9079.2625 | 37973.8466 | 47053.1091 | 0
0
| SCADOutsideTxConstraintZones |  |  |  | 0
| Cima | 0 | 8101.2618 | 8101.2618 | 0
0
| SCADSNV_Z1_EldoradoAndMtnPass |  |  |  | 0
| ElDorado | 0 | 0 | 0 | 0
0
| SCADSNV_Z3_GreaterImperial |  |  |  | 1 | SCADSNV_Z3_GreaterImperial | [11 empty] | 548 | 0 | 0 | SCADSNV_Solar | 1 | 1
| East County | 11024.5372 | 96155.6295 | 107180.1666 | 1 | East County | [12 empty] | 0 | 0
| Imperial Valley | 207772.1766 | 25482.8984 | 233255.075 | 1 | Imperial Valley | 207772.1766 | 25482.8984 | 233255.075 | 0.60793 | 33322.1536 | 29681.7395 | 3640.4141 | 333.1441 | 0.6078% | 1.122% | Greater_Imperial_Solar |  | 0 | 0
| Ocotillo Express | 38327.3915 | 112106.6951 | 150434.0866 | 1 | Ocotillo Express | 38327.3915 | 112106.6951 | 150434.0866 | 0.39207 | 21490.5838 | 5475.3416 | 16015.2422 | 214.8559 | 0.392% | 3.924% | Greater_Imperial_Solar |  | 0 | 0
| Suncrest | 14208.8214 | 224325.5091 | 238534.3305 | 1 | Suncrest | [12 empty] | 0 | 0
[5 empty] | 1 | Total |  |  | 383689.1616 |  | 54812.7374 | 35157.0812 | 19655.6562 | [5 empty] | 0 | 0
0
| SCADSNV_Z4_RiversideAndPalmSprings |  |  |  | 1 | SCADSNV_Z4_RiversideAndPalmSprings | [12 empty] | 0 | 0
| Colorado River | 121669.3342 | 200351.3694 | 322020.7036 | 1 | Colorado River | 121669.3342 | 200351.3694 | 322020.7036 | 0.66247 | 46002.9577 | 17381.3335 | 28621.6242 | 662.4742 | 0.954% | 3.811% | Riverside_Palm_Springs_Solar | 1000 | 0 | 0
| Red Bluff | 51719.5818 | 112347.5969 | 164067.1787 | 1 | Red Bluff | 51719.5818 | 112347.5969 | 164067.1787 | 0.33753 | 23438.1684 | 7388.5117 | 16049.6567 | 337.5258 | 0.4861% | 4.568% | Riverside_Palm_Springs_Solar |  | 0 | 0
[5 empty] | 1 | Total |  |  | 486087.8823 |  | 69441.126 | 24769.8451 | 44671.2809 | [5 empty] | 0 | 0
| SCADSNV_Z5_SCADSNV |  |  |  | 0
| Capacitor | 18967.9466 | 48994.843 | 67962.7896 | 0
| Eagle Mt. | 47355.3448 | 84478.5763 | 131833.9211 | 0
| Iron Mt. | 32233.3948 | 161416.1964 | 193649.5912 | 0
| Julian Hinds | 9794.171 | 39712.1997 | 49506.3708 | 0
| Los Coches | 45299.875 | 141878.3741 | 187178.2491 | 0
| Miguel | 11515.3357 | 58209.2263 | 69724.562 | 0
| Mohave | 252.3457 | 5822.8718 | 6075.2175 | 0
| Otay Mesa | 7815.131 | 59710.2948 | 67525.4258 | 0
| South Bay | 7191.9922 | 12576.9679 | 19768.9601 | 0
0
| SPGE_Z1_Westlands |  |  |  | 1 | SPGE_Z1_Westlands | [11 empty] | 1099 | 0 | 0
| Ashlan Ave. | 339741.7717 | 55625.8303 | 395367.602 | 0
| Fig Garden | 325839.8294 | 67855.9079 | 393695.7373 | 0
| Gates | 244790.1476 | 61943.4468 | 306733.5943 | 1 | Gates | 244790.1476 | 61943.4468 | 306733.5943 | 0.14423 | 43819.0849 | 34970.0211 | 8849.0638 | 158.5125 | 0.05218% | 0.4533% | Westlands_Solar |  | 0 | 0
| Gregg | 317053.4155 | 74590.2185 | 391643.6339 | 0
| Helm | 351333.2811 | 7886.9101 | 359220.1912 | 1 | Helm | 351333.2811 | 7886.9101 | 359220.1912 | 0.16891 | 51317.1702 | 50190.4687 | 1126.7014 | 185.6363 | 0.0611% | 0.3699% | Westlands_Solar |  | 0 | 0
| Henrietta | 332147.2882 | 0 | 332147.2882 | 1 | Henrietta | 332147.2882 | 0 | 332147.2882 | 0.15618 | 47449.6126 | 47449.6126 | 0 | 171.6456 | 0.0565% | 0.3617% | Westlands_Solar |  | 0 | 0
| Herndon | 323716.0747 | 66266.3941 | 389982.4687 | 0
| Kearney (New) | 371486.0414 | 60.7305 | 371546.7719 | 0
| Los Banos | 114225.5629 | 174190.3625 | 288415.9254 | 0
| Mc Call | 409347.0596 | 5918.4196 | 415265.4792 | 1 | Mc Call | 409347.0596 | 5918.4196 | 415265.4792 | 0.19527 | 59323.6399 | 58478.1514 | 845.4885 | 214.5991 | 0.07064% | 0.367% | Westlands_Solar |  | 0 | 0
| Mc Mullin | 386505.5976 | 648.197 | 387153.7946 | 1 | Mc Mullin | 386505.5976 | 648.197 | 387153.7946 | 0.18205 | 55307.6849 | 55215.0854 | 92.5996 | 200.0717 | 0.06585% | 0.3623% | Westlands_Solar |  | 0 | 0
| Oxford | 161974.2756 | 150132.069 | 312106.3446 | 0
| Panoche | 208836.716 | 117290.9153 | 326127.6313 | 1 | Panoche | 208836.716 | 117290.9153 | 326127.6313 | 0.15335 | 46589.6616 | 29833.8166 | 16755.845 | 168.5348 | 0.05547% | 0.5649% | Westlands_Solar |  | 0 | 0
| San Luis | 108748.8872 | 201483.0001 | 310231.8873 | 0
| San Luis 3 | 195956.321 | 128527.0548 | 324483.3759 | 1 | Total | 1932960.0901 | 193687.8887 | 2126647.9788 |  | 303806.8541 | 276137.1557 | 27669.6984 | 1099 |  |  |  |  | 0 | 0
| San Luis 5 | 173321.3842 | 138034.6142 | 311355.9984 | 0
| Wright | 138416.5448 | 143289.1497 | 281705.6945 | 0
0
| SPGE_Z2_KernAndGreaterCarrizo |  |  |  | 1 | SPGE_Z2_KernAndGreaterCarrizo | [11 empty] | 979 | 0 | 0
| Arco | 273894.9336 | 115184.61 | 389079.5436 | 1 | Arco | 273894.9336 | 115184.61 | 389079.5436 | 0.20625 | 55582.7919 | 39127.8477 | 16454.9443 | 201.9149 | 0.07492% | 0.516% | Kern_Greater_Carrizo_Solar |  | 0 | 0
| Buena Vista Pumps | 210937.6669 | 156404.3615 | 367342.0284 | 1 | Buena Vista Pumps | [12 empty] | 0 | 0
| Kern Power | 316543.5343 | 76163.7254 | 392707.2597 | 1 | Kern Power | [12 empty] | 0 | 0
| Midway | 275515.9004 | 100733.5 | 376249.4004 | 1 | Midway | 275515.9004 | 100733.5 | 376249.4004 | 0.19944 | 53749.9143 | 39359.4143 | 14390.5 | 195.2566 | 0.07245% | 0.4961% | Kern_Greater_Carrizo_Solar |  | 0 | 0
| Renfro | 318206.2071 | 68185.7886 | 386391.9958 | 1 | Renfro | 318206.2071 | 68185.7886 | 386391.9958 | 0.20482 | 55198.8565 | 45458.0296 | 9740.8269 | 200.5202 | 0.07441% | 0.4411% | Kern_Greater_Carrizo_Solar |  | 0 | 0
| Stockdale | 329570.6643 | 58200.378 | 387771.0423 | 1 | Stockdale | 329570.6643 | 58200.378 | 387771.0423 | 0.20555 | 55395.8632 | 47081.5235 | 8314.3397 | 201.2358 | 0.07467% | 0.4274% | Kern_Greater_Carrizo_Solar |  | 0 | 0
| Wheeler Ridge | 238849.923 | 108140.4149 | 346990.3379 | 1 | Wheeler Ridge | 238849.923 | 108140.4149 | 346990.3379 | 0.18394 | 49570.0483 | 34121.4176 | 15448.6307 | 180.0725 | 0.06682% | 0.5277% | Kern_Greater_Carrizo_Solar |  | 0 | 0
[5 empty] | 1 | Total | 1436037.6285 | 450444.6914 | 1886482.3199 |  |  |  |  | 979 |  |  |  |  | 0 | 0
| SPGE_Z3_Carrizo |  |  |  | 0
| Caliente | 153856.6636 | 222592.8349 | 376449.4985 | 0
| Mesa | 183463.2714 | 152282.0231 | 335745.2944 | 0
| Solar | 129612.6335 | 260323.1903 | 389935.8237 | 0
| Templeton | 246398.0105 | 178426.6302 | 424824.6408 | 0
0
| SPGE_Z4_CentralValleyAndLosBanos |  |  |  | 0
| Bellota | 255519.9564 | 190398.795 | 445918.7514 | 0
| Cottle | 244115.4368 | 184777.5408 | 428892.9777 | 0
| Eight Mile | 361384.9129 | 26159.0407 | 387543.9536 | 0
| Stagg | 361483.7987 | 19362.6578 | 380846.4565 | 0
| Storey | 293286.0857 | 148690.1618 | 441976.2475 | 0
| Weber | 390024.4437 | 7132.1547 | 397156.5984 | 0
| Wilson | 221460.6649 | 144010.4955 | 365471.1604 | 0
0
| Tehachapi |  |  |  | 1 | Tehachapi | [11 empty] | 3202 | 0 | 0
| Antelope | 283494.6086 | 91597.5112 | 375092.1198 | 1 | Antelope | 283494.6086 | 91597.5112 | 375092.1198 | 0.25986 | 53584.5885 | 40499.2298 | 13085.3587 | 832.0755 | 0.4035% | 2.055% | Tehachapi_Solar |  | 0 | 0
| Arbwind | 187469.0637 | 131236.3051 | 318705.3688 | 1 | Arbwind | [8 empty] | 0 |  |  |  | 0 | 0
| Bailey | 51084.6647 | 172593.7956 | 223678.4603 | 1 | Bailey | [8 empty] | 0 |  |  |  | 0 | 0
| Highwind | 177593.1111 | 122671.0948 | 300264.2058 | 1 | Highwind | [8 empty] | 0 |  |  |  | 0 | 0
| Mojave 17 | 219898.1683 | 123482.8752 | 343381.0436 | 1 | Mojave 17 | [8 empty] | 0 |  |  |  | 0 | 0
| N.N. | 449206.5858 | 549784.8816 | 998991.4674 | 1 | N.N. | [8 empty] | 0 |  |  |  | 0 | 0
| Pardee | 103540.6965 | 134265.1503 | 237805.8468 | 1 | Pardee | [8 empty] | 0 |  |  |  | 0 | 0
| Pearblossom | 161230.5478 | 175860.4673 | 337091.0151 | 1 | Pearblossom | 161230.5478 | 175860.4673 | 337091.0151 | 0.23353 | 48155.8593 | 23032.9354 | 25122.9239 | 747.7768 | 0.3626% | 3.247% | Tehachapi_Solar |  | 0 | 0
| Saugus | 104148.9977 | 130389.4178 | 234538.4155 | 1 | Saugus | [8 empty] | 0 |  |  |  | 0 | 0
| Sky River North | 42559.4625 | 138617.3388 | 181176.8013 | 1 | Sky River North | [8 empty] | 0 |  |  |  | 0 | 0
| Vincent | 184408.9052 | 117262.3318 | 301671.237 | 1 | Vincent | [8 empty] | 0 |  |  |  | 0 | 0
| Warne | 33576.2089 | 158595.9827 | 192172.1916 | 1 | Warne | [8 empty] | 0 |  |  |  | 0 | 0
| Westwind | 219616.5744 | 124770.4984 | 344387.0727 | 1 | Westwind | [8 empty] | 0 |  |  |  | 0 | 0
| Whirlwind | 242518.5078 | 141802.2074 | 384320.7152 | 1 | Whirlwind | 242518.5078 | 141802.2074 | 384320.7152 | 0.26625 | 54902.9593 | 34645.5011 | 20257.4582 | 852.5475 | 0.4134% | 2.461% | Tehachapi_Solar |  | 0 | 0
| Winderness | 224940.2791 | 119399.7675 | 344340.0466 | 1 | Winderness | [8 empty] | 0 |  |  |  | 0 | 0
| Windhub | 224363.6679 | 122565.196 | 346928.864 | 1 | Windhub | 224363.6679 | 122565.196 | 346928.864 | 0.24035 | 49561.2663 | 32051.9526 | 17509.3137 | 769.6003 | 0.3732% | 2.401% | Tehachapi_Solar |  | 0 | 0
[5 empty] | 1 | Total | 911607.3321 | 531825.382 | 1443432.7141 |  |  |  |  | 3202 |  |  |  | 7225 | 0 | 0
| TehachapiOutsideTxConstraintZones |  |  |  | 0
| Airchem | 0 | 0 | 0 | 1 | Southern_Nevada_Solar | [12 empty] | 0 | 0
| Arcogen | 0 | 0 | 0 | 1 | Crazy Eyes |  |  | 155787 | 0.61 | 22255.2857 |  |  | 427 | 1.919% |  | Southern_Nevada_Solar |  | 0 | 0
| Cameron | 0 | 0 | 0 | 1 | Desert View |  |  | 42719 | 0.17 | 6102.7143 |  |  | 119 | 1.95% |  | Southern_Nevada_Solar |  | 0 | 0
| Casitas | 105110.5747 | 55297.4168 | 160407.9915 | 1 | Innovation |  |  | 54904 | 0.22 | 7843.4286 |  |  | 154 | 1.963% |  | Southern_Nevada_Solar |  | 0 | 0
| Center | 834.8357 | 0 | 834.8357 | 1 | El Dorado 230kV |  |  | 42263 | 1 | 6037.5714 |  |  | 410 | 6.791% |  | Mountain_Pass_El_Dorado_Solar |  | 0 | 0
| Chevmain | 0 | 0 | 0 | 0
| Del Amo | 0 | 0 | 0 | 1 | SCADSNV_Solar | [12 empty] | 0 | 0
| Eagle Rock | 89.8475 | 20648.2167 | 20738.0643 | 1 | Mohave 500kV |  |  | 28764 | 1 | 4109.1429 |  |  | 330 | 8.031% |  | SCADSNV_Solar |  | 0 | 0
| El Nido | 0 | 0 | 0 | 0
| El Segundo | 0 | 3.37 | 3.37 | 0
| Federalgen | 0 | 0 | 0 | 0
| Goodrich | 90.2923 | 23212.4228 | 23302.7151 | 0
| Gould | 3646.5285 | 48488.1105 | 52134.639 | 0
| Harborgen | 0 | 0 | 0 | 0
| Hinson | 0 | 0 | 0 | 0
| Kinetic | 0 | 0 | 0 | 0
| La Cienega | 60.4448 | 3.37 | 63.8147 | 0
| La Fresa | 0 | 0 | 0 | 0
| Laguna Bell | 0 | 0 | 0 | 0
| Lawndale | 0 | 0 | 0 | 0
| Lighthipe | 0 | 0 | 0 | 0
| Mandalay | 121907.7341 | 24738.7736 | 146646.5076 | 0
| Mesa | 183463.2714 | 152282.0231 | 335745.2944 | 0
| Moorpark | 175849.823 | 76091.5603 | 251941.3833 | 0
| N.N. | 449206.5858 | 549784.8816 | 998991.4674 | 0
| Olinda | 28973.3032 | 12098.187 | 41071.4902 | 0
| Ormond Beach | 110407.0725 | 14884.7 | 125291.7726 | 0
| Redondo 1 | 0 | 0 | 0 | 0
| Repro | 0 | 0 | 0 | 0
| Rio Hondo | 18154.1772 | 19395.3754 | 37549.5526 | 0
| Rosecrans | 0 | 0 | 0 | 0
| Santa Clara | 176304.6776 | 44572.428 | 220877.1056 | 0
| Stadium | 0 | 0 | 0 | 0
| Stanhill | 0 | 0 | 0 | 0
| Tahiti | 60.4448 | 13.3854 | 73.8302 | 0
| Venice Hydro | 60.4448 | 8.0744 | 68.5191 | 0
| Walnut | 26759.3165 | 8355.5954 | 35114.9118 | 0
| Windsor Hills | 0 | 0 | 0 | 0
0
| WestlandsOutsideTxConstraintZones |  |  |  | 0
| Coburn | 162720.8122 | 218556.7929 | 381277.605 | 0
| Diablo Canyon | 52516.4306 | 78414.7828 | 130931.2133 | 0
| Goleta | 50794.101 | 53728.8796 | 104522.9806 | 0
| Grand Total | 28058029.0728 | 21760032.2769 | 49818061.3496

## 3.1_SUM WIND RESOURCE ACRES
What constitutes level 3 criteria flag? |  |  | None
What constitutes level 2 criteria flag? |  |  | 20% | Exceeds this percentage utilization of available land in proximity to substation
What constitutes level 1 criteria flag? |  |  | All other
|  |  | Wind Project | ACRES_LOW | ACRES_HIGH | TOTAL_ACRES | Potential MW | MW Allocation | Percent of Total _MW | PROJECT ACRES | Percent of Acres_LOW |  | Criteria Threshold: Exceeds 20% (Total)? | Criteria Threshold: Exceeds 20% (Low)? | RESOLVE Resource | Aggregated RESOLVE Resource | Criteria Threshold: Exceeds 20% (Total)? | Criteria Threshold: Exceeds 20% (Low)?
| Carrizo Wind | [6 empty] | 287 | [5 empty] | 0 | Carrizo_Wind | Carrizo_Wind | 2 | 2
|  | Templeton | Wind 124 | 6729.9534 | 24299.8298 | 31029.7832 | 288 |  | 99.65% | 11480 | 170.6% |  | 1 | 1 | Carrizo_Wind | Central_Valley_North_Los_Banos_Wind | 2 | 2
[13 empty] | 0 | 0 | 0 | Humboldt_Wind | 2 | 2 | No low value land
| Central Valley and North Los Banos Wind | [6 empty] | 173 |  |  |  |  | 0 | 0 | Central_Valley_North_Los_Banos_Wind | Kern_Greater_Carrizo_Wind | 1 | 1
|  | Los Banos | Wind 112 | 16166.129 | 23407.3429 | 39573.472 | 170 |  | 101.8% | 6920 | 42.81% |  | 1 | 1 | Central_Valley_North_Los_Banos_Wind | Northern_California_Ex_Wind | 2 | 1
[13 empty] | 0 | 0 | 0 | Solano_Wind | 2 | 2
| Humboldt Wind | [6 empty] | 34 |  |  |  |  | 0 | 0 | Humboldt_Wind | Tehachapi_Wind | 2 | 1
|  | Bridgeville | Wind 7 | 0 | 11414.6331 | 11414.6331 | 34 |  | 50.75% | 5022.2 |  |  | 1 | 0 | Humboldt_Wind
|  |  | Wind 8 | 0 | 11355.8557 | 11356.3005 | 33 |  | 49.25% | 4837.3 |  |  | 1 | 0 | Humboldt_Wind
|  |  |  | 0 | 22770.4889 | 22770.9337 | 67 |  |  | 1360 | #DIV/0! | No Low Value ACRES | 0 | #DIV/0! | Humboldt_Wind
[13 empty] | 0 | 0 | 0
| Kern Greater Carrizo Wind | [6 empty] | 60 |  |  |  |  | 0 | 0 | 0
|  | Cholame | Wind 207 | 11176.1755 | 9449.3403 | 20625.5157 | 69 |  | 86.96% | 2400 | 21.47% |  | 1 | 1 | 0
[13 empty] | 0 | 0 | 0
| Sacramento Valley Wind | [6 empty] | 866 |  |  |  |  | 0 | 0 | Northern_California_Ex_Wind
|  | Glenn | Wind 34 | 21839.4351 | 0 | 21839.4351 | 120 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 35 | 32087.1942 | 0 | 32087.1942 | 166 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 36 | 27505.3046 | 1796.0503 | 29301.3548 | 149 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 37 | 25021.9988 | 3740.2999 | 28762.2988 | 168 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 38 | 13114.3746 | 16735.7764 | 29850.1511 | 157 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 39 | 25914.2428 | 7966.2534 | 33880.4961 | 166 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 40 | 20908.7046 | 8987.8427 | 29896.5473 | 166 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 42 | 31674.5459 | 1332.0413 | 33006.5872 | 183 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 43 | 21329.2313 | 11015.7038 | 32344.9351 | 183 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 50 | 17028.3306 | 12467.3163 | 29495.647 | 166 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 51 | 33870.1339 | 247.1054 | 34117.2393 | 163 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 204 | 13663.4689 | 0 | 13663.4689 | 69 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  |  | 283956.9655 | 64288.3895 | 348245.355 | 1856 | 400 | 21.55% | 16000 | 5.635% |  | 1 | 0 | Northern_California_Ex_Wind
|  | Delevan | [10 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 31 | 6084.8094 | 1282.7612 | 7367.5707 | 38 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 32 | 31202.9317 | 2641.358 | 33844.2897 | 175 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 33 | 29015.8768 | 0 | 29015.8768 | 222 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  |  | 66303.6179 | 3924.1192 | 70227.7371 | 435 | 94 | 21.61% | 3760 | 5.671% |  | 1 | 0 | Northern_California_Ex_Wind
|  | Thermalito | [10 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 52 | 32608.7529 | 0 | 32608.7529 | 182 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 53 | 29609.2617 | 0 | 29609.2617 | 172 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 54 | 30953.4561 | 377.0251 | 31330.4812 | 174 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 55 | 23422.0305 | 0 | 23422.0305 | 138 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 56 | 31228.9783 | 633.892 | 31862.8703 | 172 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 202 | 16889.0583 | 0 | 16889.0583 | 96 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  |  | 164711.5378 | 1010.9171 | 165722.4549 | 934 | 201 | 21.52% | 8040 | 4.881% |  | 1 | 0 | Northern_California_Ex_Wind
|  | Rio Oso | [10 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 62 | 30714.3441 | 0 | 30714.3441 | 176 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 73 | 29002.0732 | 0 | 29002.0732 | 172 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 77 | 35294.3904 | 0 | 35294.3904 | 181 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 78 | 30267.3127 | 0 | 30267.3127 | 160 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  | Wind 79 | 20227.9346 | 0 | 20227.9346 | 107 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
|  |  |  | 145506.0551 | 0 | 145506.0551 | 796 | 171 | 21.48% | 6840 | 4.701% |  | 1 | 0 | Northern_California_Ex_Wind
[13 empty] | 0 | 0 | 0
| Solano Wind | [11 empty] | 0 | 0 | Solano_Wind
|  | Lakeville | Wind 198 | 2361.3656 | 15002.7991 | 17364.1647 | 71 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 101 | 2393.1548 | 29048.7635 | 31441.9184 | 166 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 102 | 7207.3104 | 8590.8881 | 15798.1985 | 70 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 196 | 2948.0119 | 31570.5233 | 34518.5353 | 146 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 197 | 4625.9771 | 26007.4994 | 30633.4765 | 117 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 199 | 4046.7783 | 26316.1556 | 30362.9339 | 136 | [5 empty] | 0 | 0 | Solano_Wind
|  |  |  | 23582.5981 | 136536.6291 | 160119.2272 | 706 | 227 | 32.15% | 9080 | 38.5% |  | 1 | 1 | Solano_Wind
|  | Tulucay | [10 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 103 | 3479.2106 | 13204.9372 | 16684.1477 | 22 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 106 | 5958.7606 | 19351.3274 | 25310.088 | 50 | [5 empty] | 0 | 0 | Solano_Wind
|  |  |  | 9437.9712 | 32556.2646 | 41994.2357 | 72 | 23 | 31.94% | 920 | 9.748% |  | 1 | 0 | Solano_Wind
|  | Vaca-Dixon & GC Yard | [10 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 80 | 11733.2651 | 20668.7168 | 32401.9819 | 86 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 81 | 23098.3902 | 11485.509 | 34583.8992 | 114 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 82 | 30872.3849 | 0 | 30872.3849 | 77 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 83 | 34973.0826 | 573.8062 | 35546.8888 | 80 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 84 | 32773.4554 | 3679.007 | 36452.4624 | 89 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 85 | 29812.5532 | 6243.4009 | 36055.9541 | 85 | [5 empty] | 0 | 0 | Solano_Wind
|  |  |  | 163263.1314 | 42650.4398 | 205913.5713 | 531 | 171 | 32.2% | 6840 | 4.19% |  | 1 | 0 | Solano_Wind
|  | Shilo III | [10 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 91 | 28653.8156 | 5619.5354 | 34273.3509 | 82 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 206 | 10020.747 | 4704.6326 | 14725.3796 | 34 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 88 | 38048.726 | 3368.0093 | 41416.7354 | 88 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 90 | 22115.5238 | 689.4769 | 22805.0007 | 57 | [5 empty] | 0 | 0 | Solano_Wind
|  |  |  | 98838.8124 | 14381.6542 | 113220.4666 | 261 | 84 | 32.18% | 3360 | 3.399% |  | 1 | 0 | Solano_Wind
|  | Lone Tree | [10 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 104 | 5792.3906 | 16974.6621 | 22767.0528 | 35 | [5 empty] | 0 | 0 | Solano_Wind
|  |  | Wind 107 | 15567.8983 | 23209.4731 | 38777.3714 | 79 | [5 empty] | 0 | 0 | Solano_Wind
|  |  |  | 21360.289 | 40184.1352 | 61544.4242 | 114 | 37 | 32.46% | 1480 | 6.929% |  | 1 | 0 | Solano_Wind
[13 empty] | 0 | 0 | 0
| Tehachapi Wind | [11 empty] | 0 | 0 | Tehachapi_Wind
|  | Windhub | Wind 129 | 13670.7998 | 16116.6015 | 29787.4013 | 128 | [5 empty] | 0 | 0 | Tehachapi_Wind
|  |  | Wind 156 | 12435.83 | 922.2979 | 13358.1279 | 86 | [5 empty] | 0 | 0 | Tehachapi_Wind
|  |  | Wind 157 | 30641.6782 | 1300.9199 | 31942.5981 | 138 | [5 empty] | 0 | 0 | Tehachapi_Wind
|  |  |  | 56748.308 | 18339.8193 | 75088.1273 | 352 | 275 | 78.12% | 11000 | 19.38% |  | 1 | 0 | Tehachapi_Wind

## 3.2_SUM SOLAR RESOURCE ACRES
What constitutes level 3 criteria flag? | None
What constitutes level 2 criteria flag? | 20% | Exceeds this percentage utilization of available land in proximity to substation
What constitutes level 1 criteria flag? | All other
SELECTED
| Tx Zone/Substation | ACRES_15_LOW | ACRES_15_HIGH | TOTAL ACRES_15 | 1 | Tx Zone/Substation | ACRES_15_LOW | ACRES_15_HIGH | TOTAL ACRES_15 | Porportion of Total Acres | Potential MW | Potential MW Low | Potential MW High | MW Allocation | Percent Total ACRES | Percent ACRES Low | RESOLVE Resource | RESOLVE MW | Exceeds 0.2 Total? | Exceeds 0.2 Low? | Aggregated RESOLVE Resource | Criteria Threshold: Exceeds 0.2 (Total)? | Criteria Threshold: Exceeds 0.2 (Low)?
| GK_Z2_InyokernAndNorthOfKramer | 1 | GK_Z2_InyokernAndNorthOfKramer | [8 empty] | 97 | - | - |  |  |  |  | 0 | 0 | Inyokern_North_Kramer_Solar | 1 | 1
| Kramer | 22292 | 108531 | 130823 | 1 | Kramer | 22292 | 108531 | 130823 | 0.44 | 18689 | 3185 | 15504 | 43 | 0.1% | 1.35% | Inyokern_North_Kramer_Solar | - | 0 | 0 | North_Victor_Solar | 1 | 1
| Randsburg | 32006 | 132828 | 164834 | 1 | Randsburg | 32006 | 132828 | 164834 | 0.56 | 23548 | 4572 | 18975 | 54 | 0.13% | 1.18% | Inyokern_North_Kramer_Solar | - | 0 | 0 | Greater_Imperial_Solar | 1 | 1
[5 empty] | 1 | Total | 54298 | 241359 | 295657 |  | 42237 | 7757 | 34480 | [5 empty] | 0 | 0 | Riverside_Palm_Springs_Solar | 1 | 1
| GK_Z3_NorthOfVictor |  | 1 | GK_Z3_NorthOfVictor | [14 empty] | 0 | 0 | Westlands_Solar | 1 | 1
| Caldwell | 202590 | 157849 | 360439 | 1 | Caldwell | [11 empty] | 300 | 0 | 0 | Kern_Greater_Carrizo_Solar | 1 | 1
| Cool Water | 37474 | 118138 | 155612 | 1 | Coolwater | 37474 | 118138 | 155612 | 0.28 | 22230 | 5353 | 16877 | 85 | 0.11% | 1.59% | North_Victor_Solar | - | 0 | 0 | Tehachapi_Solar | 1 | 1
| Victor | 226644 | 167494 | 394138 | 1 | Victor | 226644 | 167494 | 394138 | 0.72 | 56305 | 32378 | 23928 | 215 | 0.27% | 0.66% | North_Victor_Solar | - | 0 | 0 | Southern_Nevada_Solar | 1 | 1
| GK_Z4_Pisgah |  |  | 1 | Total | 264117 | 285633 | 549750 |  | 78536 | 37731 | 40805 | [5 empty] | - | 0 | 0 | Mountain_Pass_El_Dorado_Solar | 1 | 1
| Calcite | 263893 | 637139 | 901032 | 0 | [13 empty] | 0 | 0 | SCADSNV_Solar | 1 | 1
| Lugo | 172374 | 130196 | 302570 | 0 | [13 empty] | 0 | 0
| Pisgah | 33413 | 60109 | 93523 | 0 | [13 empty] | 0 | 0
[5 empty] | 0 | [13 empty] | 0 | 0
| GreaterImpOutsideTxConstraintZones | 0 | [14 empty] | - |  | 0 | 0
| Batiquitos | 157633 | 47688 | 205321 | 0 | [13 empty] | 0 | 0
| Calpeak Power Enterprise 7 | 202401 | 121913 | 324314 | 0 | [13 empty] | 0 | 0
| Doublett | 80436 | 44592 | 125028 | 0 | [13 empty] | 0 | 0
| Elliott | 45307 | 46729 | 92036 | 0 | [13 empty] | 0 | 0
| Encina | 126454 | 24920 | 151374 | 0 | [13 empty] | 0 | 0
| Escondido | 203431 | 121928 | 325359 | 0 | [13 empty] | 0 | 0
| Fashion Valley | 28282 | 16983 | 45265 | 0 | [13 empty] | 0 | 0
| Friars | 30269 | 20371 | 50640 | 0 | [13 empty] | 0 | 0
| Main St. | 8747 | 7667 | 16414 | 0 | [13 empty] | 0 | 0
| Mesa Rim | 74254 | 55527 | 129781 | 0 | [13 empty] | 0 | 0
| Mission | 32441 | 23993 | 56434 | 0 | [13 empty] | 0 | 0
| North City West | 96479 | 49202 | 145681 | 0 | [13 empty] | 0 | 0
| Old Town | 25583 | 12290 | 37873 | 0 | [13 empty] | 0 | 0
| Palomar Airport | 143556 | 37740 | 181296 | 0 | [13 empty] | 0 | 0
| Penasquitos | 81522 | 44598 | 126120 | 0 | [13 empty] | 0 | 0
| San Luis Rey | 133893 | 33714 | 167606 | 0 | [13 empty] | 0 | 0
| San Onofre | 23573 | 62718 | 86290 | 0 | [13 empty] | 0 | 0
| Shadowridge | 174758 | 56678 | 231437 | 0 | [13 empty] | 0 | 0
| Silvergate | 8282 | 7914 | 16196 | 0 | [13 empty] | 0 | 0
| Sycamore Canyon | 81712 | 110788 | 192500 | 0 | [13 empty] | 0 | 0
[5 empty] | 0 | [13 empty] | 0 | 0
| KramerInyoOutsideTxConstraintZones | 0 | [14 empty] | - |  | 0 | 0
| Chino | 115236 | 34278 | 149514 | 0 | [13 empty] | 0 | 0
| Etiwanda | 119521 | 34144 | 153665 | 0 | [13 empty] | 0 | 0
| Mira Loma | 153868 | 44777 | 198645 | 0 | [13 empty] | 0 | 0
| Padua | 103281 | 37944 | 141225 | 0 | [13 empty] | 0 | 0
| Rancho Vista | 117869 | 35516 | 153385 | 0 | [13 empty] | 0 | 0
| San Bernardino | 109190 | 93582 | 202772 | 0 | [13 empty] | 0 | 0
| Soquel | 112556 | 38097 | 150654 | 0 | [13 empty] | 0 | 0
| Vista | 154339 | 71821 | 226161 | 0 | [13 empty] | 0 | 0
[5 empty] | 0 | [13 empty] | 0 | 0
| Norcal_Z3_SacramentoRiver |  | 0 | [13 empty] | - | - | 0 | 0
| Carberry | 63074 | 243738 | 306812 | 0 | [13 empty] | 0 | 0
| Delevan | 226931 | 151233 | 378165 | 0 | [13 empty] | 0 | 0
| Glenn | 312380 | 98005 | 410385 | 0 | [13 empty] | 0 | 0
| Hat Creek 2 | 136010 | 217546 | 353557 | 0 | [13 empty] | 0 | 0
| Palermo | 214738 | 187412 | 402150 | 0 | [13 empty] | 0 | 0
| Pit 1 | 141777 | 214370 | 356147 | 0 | [13 empty] | 0 | 0
| Pit 1 Ph | 141555 | 215093 | 356648 | 0 | [13 empty] | 0 | 0
| Rio Oso | 390291 | 40334 | 430625 | 0 | [13 empty] | 0 | 0
| Table Mt. | 240287 | 158423 | 398711 | 0 | [13 empty] | 0 | 0
| Thermalito | 249280 | 157779 | 407058 | 0 | [13 empty] | 0 | 0
[5 empty] | 0 | [13 empty] | 0 | 0
| Norcal_Z4_Solano |  |  | 0 | [13 empty] | - | 0 | 0
| Amerigas | 260414 | 114395 | 374808 | 0 | [13 empty] | 0 | 0
| Bear Canyon | 117353 | 203394 | 320747 | 0 | [13 empty] | 0 | 0
| Big Geysers | 130673 | 197242 | 327915 | 0 | [13 empty] | 0 | 0
| Calistoga 19 | 139609 | 188704 | 328314 | 0 | [13 empty] | 0 | 0
| Calpeak Power Vaca Dixon 1 | 262551 | 111983 | 374534 | 0 | [13 empty] | 0 | 0
| Castro Valley | 46179 | 79407 | 125586 | 0 | [13 empty] | 0 | 0
| Cayetano | 116508 | 230435 | 346943 | 0 | [13 empty] | 0 | 0
| Cobb Creek | 146233 | 181413 | 327646 | 0 | [13 empty] | 0 | 0
| Contra Costa | 200922 | 142150 | 343072 | 0 | [13 empty] | 0 | 0
| Contra Costa Power | 210000 | 136983 | 346983 | 0 | [13 empty] | 0 | 0
| Fulton | 167498 | 182136 | 349634 | 0 | [13 empty] | 0 | 0
| Fumarole | 143276 | 186187 | 329463 | 0 | [13 empty] | 0 | 0
| Geysers Unit 3 | 143689 | 184448 | 328137 | 0 | [13 empty] | 0 | 0
| Grant 20 | 139259 | 192919 | 332177 | 0 | [13 empty] | 0 | 0
| Lake View | 156924 | 171486 | 328410 | 0 | [13 empty] | 0 | 0
| Lakeville | 154619 | 185621 | 340241 | 0 | [13 empty] | 0 | 0
| Lambie Energy | 239213 | 117481 | 356694 | 0 | [13 empty] | 0 | 0
| Lone Tree | 189538 | 155954 | 345491 | 0 | [13 empty] | 0 | 0
| Mccabe | 143114 | 185477 | 328591 | 0 | [13 empty] | 0 | 0
| N.N. | 449207 | 549785 | 998991 | 0 | [13 empty] | 0 | 0
| Ncpa 1 & 2 | 123947 | 205474 | 329421 | 0 | [13 empty] | 0 | 0
| Ncpa 3 & 4 | 121200 | 206076 | 327276 | 0 | [13 empty] | 0 | 0
| Oakmont North | 172006 | 168015 | 340021 | 0 | [13 empty] | 0 | 0
| Oakmont South | 178163 | 164286 | 342449 | 0 | [13 empty] | 0 | 0
| Peabody | 208221 | 151124 | 359345 | 0 | [13 empty] | 0 | 0
| Quicksilver | 124619 | 201651 | 326270 | 0 | [13 empty] | 0 | 0
| San Ramon | 59665 | 164537 | 224202 | 0 | [13 empty] | 0 | 0
| San Ramon Research Cntr. | 58453 | 139042 | 197495 | 0 | [13 empty] | 0 | 0
| Shiloh II | 225035 | 123667 | 348702 | 0 | [13 empty] | 0 | 0
| Shiloh III | 223956 | 124121 | 348077 | 0 | [13 empty] | 0 | 0
| Socrates 18 | 135800 | 198058 | 333858 | 0 | [13 empty] | 0 | 0
| Sonoma 3 | 141347 | 188617 | 329964 | 0 | [13 empty] | 0 | 0
| Sulphur Springs | 139885 | 191618 | 331503 | 0 | [13 empty] | 0 | 0
| Tassajara | 84879 | 164187 | 249066 | 0 | [13 empty] | 0 | 0
| Technical Ecological Services | 58453 | 138968 | 197421 | 0 | [13 empty] | 0 | 0
| Trans Bay Cable | 169698 | 134040 | 303738 | 0 | [13 empty] | 0 | 0
| Tulucay | 167011 | 134030 | 301040 | 0 | [13 empty] | 0 | 0
| Vaca-Dixon & Gc Yard | 259968 | 113943 | 373910 | 0 | [13 empty] | 0 | 0
| West Ford Flat | 132006 | 192813 | 324820 | 0 | [13 empty] | 0 | 0
[5 empty] | 0 | [13 empty] | 0 | 0
| Norcal_Z4_Solano_subzone |  | 0 | [15 empty] | 0 | 0
| Bahia | 89718 | 122146 | 211863 | 0 | [13 empty] | 0 | 0
| Embarcadero (Sf Z) | 11282 | 9587 | 20869 | 0 | [13 empty] | 0 | 0
| Ignacio | 97444 | 129759 | 227203 | 0 | [13 empty] | 0 | 0
| Moraga | 39757 | 50910 | 90667 | 0 | [13 empty] | 0 | 0
| Parkway | 130355 | 119288 | 249643 | 0 | [13 empty] | 0 | 0
| Pittsburg | 142317 | 145504 | 287821 | 0 | [13 empty] | 0 | 0
| Rossmoor | 57401 | 90527 | 147928 | 0 | [13 empty] | 0 | 0
| Sobrante | 34876 | 49389 | 84265 | 0 | [13 empty] | 0 | 0
| Tidewater | 69223 | 127137 | 196360 | 0 | [13 empty] | 0 | 0
| Unocal | 88845 | 87790 | 176635 | 0 | [13 empty] | 0 | 0
[5 empty] | 0 | [13 empty] | 0 | 0
| NorCalOutsideTxConstraintZones | 0 | [16 empty] | 0 | 0
| Brighton | 191632 | 60092 | 251724 | 0 | [13 empty] | 0 | 0
| Gold Hill | 129525 | 192148 | 321673 | 0 | [13 empty] | 0 | 0
| Jefferson | 7654 | 89704 | 97358 | 0 | [13 empty] | 0 | 0
| Logan Creek | 250598 | 139780 | 390378 | 0 | [13 empty] | 0 | 0
| Martin | 5970 | 14050 | 20020 | 0 | [13 empty] | 0 | 0
| San Mateo | 9079 | 37974 | 47053 | 0 | [13 empty] | 0 | 0
[5 empty] | 0 | [13 empty] | 0 | 0
| SCADOutsideTxConstraintZones | 0 | [16 empty] | 0 | 0
| Cima | - | 8101 | 8101 | 0 | [13 empty] | 0 | 0
[5 empty] | 0 | [13 empty] | 0 | 0
| SCADSNV_Z1_EldoradoAndMtnPass | 0 | [16 empty] | 0 | 0
| ElDorado | - | - | - | 0 | [13 empty] | 0 | 0
[5 empty] | 0 | [13 empty] | 0 | 0
| SCADSNV_Z3_GreaterImperial |  | 1 | SCADSNV_Z3_GreaterImperial | [9 empty] | 548 |  |  |  |  | 0 | 0
| East County | 11025 | 96156 | 107180 | 1 | East County | [11 empty] | - | 0 | 0
| Imperial Valley | 207772 | 25483 | 233255 | 1 | Imperial Valley | 207772 | 25483 | 233255 | 0.61 | 33322 | 29682 | 3640 | 333 | 0.61% | 1.12% | Greater_Imperial_Solar | - | 0 | 0
| Ocotillo Express | 38327 | 112107 | 150434 | 1 | Ocotillo Express | 38327 | 112107 | 150434 | 0.39 | 21491 | 5475 | 16015 | 215 | 0.39% | 3.92% | Greater_Imperial_Solar | - | 0 | 0
| Suncrest | 14209 | 224326 | 238534 | 1 | Suncrest | [12 empty] | 0 | 0
[5 empty] | 1 | Total |  |  | 383689 |  | 54813 | 35157 | 19656 | [5 empty] | 0 | 0
[5 empty] | 0 | [13 empty] | 0 | 0
| SCADSNV_Z4_RiversideAndPalmSprings | 1 | SCADSNV_Z4_RiversideAndPalmSprings | [9 empty] | - | - |  |  |  |  | 0 | 0
| Colorado River | 121669 | 200351 | 322021 | 1 | Colorado River | 121669 | 200351 | 322021 | 0.66 | 46003 | 17381 | 28622 | - | 0% | 0% | Riverside_Palm_Springs_Solar | - | 0 | 0
| Red Bluff | 51720 | 112348 | 164067 | 1 | Red Bluff | 51720 | 112348 | 164067 | 0.34 | 23438 | 7389 | 16050 | - | 0% | 0% | Riverside_Palm_Springs_Solar | - | 0 | 0
[5 empty] | 1 | Total |  |  | 486088 |  | 69441 | 24770 | 44671 | [5 empty] | 0 | 0
| SCADSNV_Z5_SCADSNV |  | 0 | [15 empty] | 0 | 0
| Capacitor | 18968 | 48995 | 67963 | 0 | [13 empty] | 0 | 0
| Eagle Mt. | 47355 | 84479 | 131834 | 0 | [13 empty] | 0 | 0
| Iron Mt. | 32233 | 161416 | 193650 | 0 | [13 empty] | 0 | 0
| Julian Hinds | 9794 | 39712 | 49506 | 0 | [13 empty] | 0 | 0
| Los Coches | 45300 | 141878 | 187178 | 0 | [13 empty] | 0 | 0
| Miguel | 11515 | 58209 | 69725 | 0 | [13 empty] | 0 | 0
| Mohave | 252 | 5823 | 6075 | 0 | [13 empty] | 0 | 0
| Otay Mesa | 7815 | 59710 | 67525 | 0 | [13 empty] | 0 | 0
| South Bay | 7192 | 12577 | 19769 | 0 | [13 empty] | 0 | 0
[5 empty] | 0 | [13 empty] | 0 | 0
| SPGE_Z1_Westlands |  |  | 1 | SPGE_Z1_Westlands | [13 empty] | 0 | 0
| Ashlan Ave. | 339742 | 55626 | 395368 | 0 | [13 empty] | 0 | 0
| Fig Garden | 325840 | 67856 | 393696 | 0 | [13 empty] | 0 | 0
| Gates | 244790 | 61943 | 306734 | 1 | Gates | 244790 | 61943 | 306734 | 0.14 | 43819 | 34970 | 8849 | 70 | 0.02% | 0.2% | Westlands_Solar | - | 0 | 0
| Gregg | 317053 | 74590 | 391644 | 0 | [13 empty] | 0 | 0
| Helm | 351333 | 7887 | 359220 | 1 | Helm | 351333 | 7887 | 359220 | 0.17 | 51317 | 50190 | 1127 | 82 | 0.03% | 0.16% | Westlands_Solar | - | 0 | 0
| Henrietta | 332147 | - | 332147 | 1 | Henrietta | 332147 | - | 332147 | 0.16 | 47450 | 47450 | - | 75 | 0.02% | 0.16% | Westlands_Solar | - | 0 | 0
| Herndon | 323716 | 66266 | 389982 | 0 | [13 empty] | 0 | 0
| Kearney (New) | 371486 | 61 | 371547 | 0 | [13 empty] | 0 | 0
| Los Banos | 114226 | 174190 | 288416 | 0 | [13 empty] | 0 | 0
| Mc Call | 409347 | 5918 | 415265 | 1 | Mc Call | 409347 | 5918 | 415265 | 0.2 | 59324 | 58478 | 845 | 94 | 0.03% | 0.16% | Westlands_Solar | - | 0 | 0
| Mc Mullin | 386506 | 648 | 387154 | 1 | Mc Mullin | 386506 | 648 | 387154 | 0.18 | 55308 | 55215 | 93 | 88 | 0.03% | 0.16% | Westlands_Solar | - | 0 | 0
| Oxford | 161974 | 150132 | 312106 | 0 | [13 empty] | 0 | 0
| Panoche | 208837 | 117291 | 326128 | 1 | Panoche | 208837 | 117291 | 326128 | 0.15 | 46590 | 29834 | 16756 | 74 | 0.02% | 0.25% | Westlands_Solar | - | 0 | 0
| San Luis | 108749 | 201483 | 310232 | 0 | [13 empty] | 0 | 0
| San Luis 3 | 195956 | 128527 | 324483 | 1 | Total | 1932960 | 193688 | 2126648 |  | 303807 | 276137 | 27670 | 483 |  |  |  |  | 0 | 0
| San Luis 5 | 173321 | 138035 | 311356 | 0 | [13 empty] | 0 | 0
| Wright | 138417 | 143289 | 281706 | 0 | [13 empty] | 0 | 0
[5 empty] | 0 | [13 empty] | 0 | 0
| SPGE_Z2_KernAndGreaterCarrizo | 1 | SPGE_Z2_KernAndGreaterCarrizo | [8 empty] | 242 | - | - |  |  |  |  | 0 | 0
| Arco | 273895 | 115185 | 389080 | 1 | Arco | 273895 | 115185 | 389080 | 0.21 | 55583 | 39128 | 16455 | 50 | 0.02% | 0.13% | Kern_Greater_Carrizo_Solar | - | 0 | 0
| Buena Vista Pumps | 210938 | 156404 | 367342 | 1 | Buena Vista Pumps | [11 empty] | - | 0 | 0
| Kern Power | 316544 | 76164 | 392707 | 1 | Kern Power | [11 empty] | - | 0 | 0
| Midway | 275516 | 100733 | 376249 | 1 | Midway | 275516 | 100733 | 376249 | 0.2 | 53750 | 39359 | 14390 | 48 | 0.02% | 0.12% | Kern_Greater_Carrizo_Solar | - | 0 | 0
| Renfro | 318206 | 68186 | 386392 | 1 | Renfro | 318206 | 68186 | 386392 | 0.2 | 55199 | 45458 | 9741 | 50 | 0.02% | 0.11% | Kern_Greater_Carrizo_Solar | - | 0 | 0
| Stockdale | 329571 | 58200 | 387771 | 1 | Stockdale | 329571 | 58200 | 387771 | 0.21 | 55396 | 47082 | 8314 | 50 | 0.02% | 0.11% | Kern_Greater_Carrizo_Solar | - | 0 | 0
| Wheeler Ridge | 238850 | 108140 | 346990 | 1 | Wheeler Ridge | 238850 | 108140 | 346990 | 0.18 | 49570 | 34121 | 15449 | 45 | 0.02% | 0.13% | Kern_Greater_Carrizo_Solar | - | 0 | 0
[5 empty] | 1 | Total | 1436038 | 450445 | 1886482 |  |  |  |  | 242 |  |  |  |  | 0 | 0
| SPGE_Z3_Carrizo |  |  | 0 | [13 empty] | - | 0 | 0
| Caliente | 153857 | 222593 | 376449 | 0 | [13 empty] | 0 | 0
| Mesa | 183463 | 152282 | 335745 | 0 | [13 empty] | 0 | 0
| Solar | 129613 | 260323 | 389936 | 0 | [13 empty] | 0 | 0
| Templeton | 246398 | 178427 | 424825 | 0 | [13 empty] | 0 | 0
[5 empty] | 0 | [13 empty] | 0 | 0
| SPGE_Z4_CentralValleyAndLosBanos | 0 | [16 empty] | 0 | 0
| Bellota | 255520 | 190399 | 445919 | 0 | [13 empty] | 0 | 0
| Cottle | 244115 | 184778 | 428893 | 0 | [13 empty] | 0 | 0
| Eight Mile | 361385 | 26159 | 387544 | 0 | [13 empty] | 0 | 0
| Stagg | 361484 | 19363 | 380846 | 0 | [13 empty] | 0 | 0
| Storey | 293286 | 148690 | 441976 | 0 | [13 empty] | 0 | 0
| Weber | 390024 | 7132 | 397157 | 0 | [13 empty] | 0 | 0
| Wilson | 221461 | 144010 | 365471 | 0 | [13 empty] | 0 | 0
[5 empty] | 0 | [13 empty] | 0 | 0
| Tehachapi |  |  | 1 | Tehachapi | [13 empty] | 0 | 0
| Antelope | 283495 | 91598 | 375092 | 1 | Antelope | 283495 | 91598 | 375092 | 0.26 | 53585 | 40499 | 13085 | 1092 | 0.53% | 2.7% | Tehachapi_Solar | - | 0 | 0
| Arbwind | 187469 | 131236 | 318705 | 1 | Arbwind | [12 empty] | 0 | 0
| Bailey | 51085 | 172594 | 223678 | 1 | Bailey | [12 empty] | 0 | 0
| Highwind | 177593 | 122671 | 300264 | 1 | Highwind | [12 empty] | 0 | 0
| Mojave 17 | 219898 | 123483 | 343381 | 1 | Mojave 17 | [7 empty] | - |  |  |  |  | 0 | 0
| N.N. | 449207 | 549785 | 998991 | 1 | N.N. | [12 empty] | 0 | 0
| Pardee | 103541 | 134265 | 237806 | 1 | Pardee | [12 empty] | 0 | 0
| Pearblossom | 161231 | 175860 | 337091 | 1 | Pearblossom | 161231 | 175860 | 337091 | 0.23 | 48156 | 23033 | 25123 | 981 | 0.48% | 4.26% | Tehachapi_Solar | - | 0 | 0
| Saugus | 104149 | 130389 | 234538 | 1 | Saugus | [12 empty] | 0 | 0
| Sky River North | 42559 | 138617 | 181177 | 1 | Sky River North | [7 empty] | - |  |  |  |  | 0 | 0
| Vincent | 184409 | 117262 | 301671 | 1 | Vincent | [12 empty] | 0 | 0
| Warne | 33576 | 158596 | 192172 | 1 | Warne | [12 empty] | 0 | 0
| Westwind | 219617 | 124770 | 344387 | 1 | Westwind | [7 empty] | - |  |  |  |  | 0 | 0
| Whirlwind | 242519 | 141802 | 384321 | 1 | Whirlwind | 242519 | 141802 | 384321 | 0.27 | 54903 | 34646 | 20257 | 1119 | 0.54% | 3.23% | Tehachapi_Solar | - | 0 | 0
| Winderness | 224940 | 119400 | 344340 | 1 | Winderness | [7 empty] | - |  |  |  | - | 0 | 0
| Windhub | 224364 | 122565 | 346929 | 1 | Windhub | 224364 | 122565 | 346929 | 0.24 | 49561 | 32052 | 17509 | 1010 | 0.49% | 3.15% | Tehachapi_Solar | - | 0 | 0
[5 empty] | 1 | Total | 911607 | 531825 | 1443433 |  |  |  |  | 4202 |  |  |  | 5872 | 0 | 0
| TehachapiOutsideTxConstraintZones | 0 | [16 empty] | 0 | 0
| Airchem | - | - | - | 1 | Southern_Nevada_Solar | [12 empty] | 0 | 0
| Arcogen | - | - | - | 1 | Crazy Eyes |  | 155787 | 0.61 | 22255 |  |  |  | 427 | 1.92% |  | Southern_Nevada_Solar |  | 0 | 0
| Cameron | - | - | - | 1 | Desert View |  | 42719 | 0.17 | 6103 |  |  |  | 119 | 1.95% |  | Southern_Nevada_Solar |  | 0 | 0
| Casitas | 105111 | 55297 | 160408 | 1 | Innovation |  | 54904 | 0.22 | 7843 |  |  |  | 154 | 1.96% |  | Southern_Nevada_Solar |  | 0 | 0
| Center | 835 | - | 835 | 1 | El Dorado 230kV |  | 42263 | 1 | 6038 |  |  |  | 410 | 6.79% |  | Mountain_Pass_El_Dorado_Solar |  | 0 | 0
| Chevmain | - | - | - | 0 | [13 empty] | 0 | 0
| Del Amo | - | - | - | 1 | SCADSNV_Solar | [11 empty] | - | 0 | 0
| Eagle Rock | 90 | 20648 | 20738 | 1 | Mohave 500kV |  | 28764 | 1 | 4109 |  |  |  | 330 | 8.03% |  | SCADSNV_Solar | - | 0 | 0
| El Nido | - | - | - | 0 | [13 empty] | 0 | 0
| El Segundo | - | 3 | 3 | 0 | [13 empty] | 0 | 0
| Federalgen | - | - | - | 0 | [13 empty] | 0 | 0
| Goodrich | 90 | 23212 | 23303 | 0 | [13 empty] | 0 | 0
| Gould | 3647 | 48488 | 52135 | 0 | [13 empty] | 0 | 0
| Harborgen | - | - | - | 0 | [13 empty] | 0 | 0
| Hinson | - | - | - | 0 | [13 empty] | 0 | 0
| Kinetic | - | - | - | 0 | [13 empty] | 0 | 0
| La Cienega | 60 | 3 | 64 | 0 | [13 empty] | 0 | 0
| La Fresa | - | - | - | 0 | [13 empty] | 0 | 0
| Laguna Bell | - | - | - | 0 | [13 empty] | 0 | 0
| Lawndale | - | - | - | 0 | [13 empty] | 0 | 0
| Lighthipe | - | - | - | 0 | [13 empty] | 0 | 0
| Mandalay | 121908 | 24739 | 146647 | 0 | [13 empty] | 0 | 0
| Mesa | 183463 | 152282 | 335745 | 0 | [13 empty] | 0 | 0
| Moorpark | 175850 | 76092 | 251941 | 0 | [13 empty] | 0 | 0
| N.N. | 449207 | 549785 | 998991 | 0 | [13 empty] | 0 | 0
| Olinda | 28973 | 12098 | 41071 | 0 | [13 empty] | 0 | 0
| Ormond Beach | 110407 | 14885 | 125292 | 0 | [13 empty] | 0 | 0
| Redondo 1 | - | - | - | 0 | [13 empty] | 0 | 0
| Repro | - | - | - | 0 | [13 empty] | 0 | 0
| Rio Hondo | 18154 | 19395 | 37550 | 0 | [13 empty] | 0 | 0
| Rosecrans | - | - | - | 0 | [13 empty] | 0 | 0
| Santa Clara | 176305 | 44572 | 220877 | 0 | [13 empty] | 0 | 0
| Stadium | - | - | - | 0 | [13 empty] | 0 | 0
| Stanhill | - | - | - | 0 | [13 empty] | 0 | 0
| Tahiti | 60 | 13 | 74 | 0 | [13 empty] | 0 | 0
| Venice Hydro | 60 | 8 | 69 | 0 | [13 empty] | 0 | 0
| Walnut | 26759 | 8356 | 35115 | 0 | [13 empty] | 0 | 0
| Windsor Hills | - | - | - | 0 | [13 empty] | 0 | 0
[5 empty] | 0 | [13 empty] | 0 | 0
| WestlandsOutsideTxConstraintZones | 0 | [16 empty] | 0 | 0
| Coburn | 162721 | 218557 | 381278 | 0 | [13 empty] | 0 | 0
| Diablo Canyon | 52516 | 78415 | 130931 | 0 | [13 empty] | 0 | 0
| Goleta | 50794 | 53729 | 104523 | 0 | [13 empty] | 0 | 0
[5 empty] | 0 | [13 empty] | 0 | 0
| Grand Total | ######## | ######## | ######## | 0 | [13 empty] | 0 | 0

## 3.2_SUM WIND RESOURCE ACRES
What constitutes level 3 criteria flag? |  |  | None
What constitutes level 2 criteria flag? |  |  | 20% | Exceeds this percentage utilization of available land in proximity to substation
What constitutes level 1 criteria flag? |  |  | All other
|  |  | Wind Project | ACRES_LOW | ACRES_HIGH | TOTAL_ACRES | Potential MW | MW Allocation | Percent of Total _MW | PROJECT ACRES | Percent of Acres_LOW |  | Criteria Threshold: Exceeds 20% (Total)? | Criteria Threshold: Exceeds 20% (Low)? | RESOLVE Resource | Aggregated RESOLVE Resource | Criteria Threshold: Exceeds 20% (Total)? | Criteria Threshold: Exceeds 20% (Low)?
Carrizo Wind | Carrizo Wind | [6 empty] | 287 | [5 empty] | 0 | Carrizo_Wind | Carrizo_Wind | 2 | 2
Carrizo Wind |  | Templeton | Wind 124 | 6729.9534 | 24299.8298 | 31029.7832 | 288 |  | 99.65% | 11480 | 170.6% |  | 1 | 1 | Carrizo_Wind | Central_Valley_North_Los_Banos_Wind | 2 | 2
[13 empty] | 0 | 0 | 0 | Humboldt_Wind | 2 | 2 | No low value land
Central Valley and North Los Banos Wind | Central Valley and North Los Banos Wind | [6 empty] | 173 |  |  |  |  | 0 | 0 | Central_Valley_North_Los_Banos_Wind | Kern_Greater_Carrizo_Wind | 1 | 1
Central Valley and North Los Banos Wind |  | Los Banos | Wind 112 | 16166.129 | 23407.3429 | 39573.472 | 170 |  | 101.8% | 6920 | 42.81% |  | 1 | 1 | Central_Valley_North_Los_Banos_Wind | Northern_California_Ex_Wind | 2 | 1
[13 empty] | 0 | 0 | 0 | Solano_Wind | 2 | 2
Humboldt Wind | Humboldt Wind | [6 empty] | 34 |  |  |  |  | 0 | 0 | Humboldt_Wind | Tehachapi_Wind | 2 | 1
Humboldt Wind |  | Bridgeville | Wind 7 | 0 | 11414.6331 | 11414.6331 | 34 |  | 50.75% | 5022.2 |  |  | 1 | 0 | Humboldt_Wind
Humboldt Wind |  |  | Wind 8 | 0 | 11355.8557 | 11356.3005 | 33 |  | 49.25% | 4837.3 |  |  | 1 | 0 | Humboldt_Wind
Humboldt Wind |  |  |  | 0 | 22770.4889 | 22770.9337 | 67 |  |  | 1360 | #DIV/0! | No Low Value ACRES | 0 | #DIV/0! | Humboldt_Wind
[13 empty] | 0 | 0 | 0
Kern Greater Carrizo Wind | Kern Greater Carrizo Wind | [6 empty] | 60 |  |  |  |  | 0 | 0 | Kern Greater Carrizo Wind
Kern Greater Carrizo Wind |  | Cholame | Wind 207 | 11176.1755 | 9449.3403 | 20625.5157 | 69 |  | 86.96% | 2400 | 21.47% |  | 1 | 1 | Kern Greater Carrizo Wind
[13 empty] | 0 | 0 | 0
Sacramento Valley Wind | Sacramento Valley Wind | [6 empty] | 866 |  |  |  |  | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  | Glenn | Wind 34 | 21839.4351 | 0 | 21839.4351 | 120 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 35 | 32087.1942 | 0 | 32087.1942 | 166 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 36 | 27505.3046 | 1796.0503 | 29301.3548 | 149 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 37 | 25021.9988 | 3740.2999 | 28762.2988 | 168 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 38 | 13114.3746 | 16735.7764 | 29850.1511 | 157 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 39 | 25914.2428 | 7966.2534 | 33880.4961 | 166 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 40 | 20908.7046 | 8987.8427 | 29896.5473 | 166 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 42 | 31674.5459 | 1332.0413 | 33006.5872 | 183 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 43 | 21329.2313 | 11015.7038 | 32344.9351 | 183 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 50 | 17028.3306 | 12467.3163 | 29495.647 | 166 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 51 | 33870.1339 | 247.1054 | 34117.2393 | 163 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 204 | 13663.4689 | 0 | 13663.4689 | 69 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  |  | 283956.9655 | 64288.3895 | 348245.355 | 1856 | 400 | 21.55% | 16000 | 5.635% |  | 1 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  | Delevan | [10 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 31 | 6084.8094 | 1282.7612 | 7367.5707 | 38 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 32 | 31202.9317 | 2641.358 | 33844.2897 | 175 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 33 | 29015.8768 | 0 | 29015.8768 | 222 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  |  | 66303.6179 | 3924.1192 | 70227.7371 | 435 | 94 | 21.61% | 3760 | 5.671% |  | 1 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  | Thermalito | [10 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 52 | 32608.7529 | 0 | 32608.7529 | 182 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 53 | 29609.2617 | 0 | 29609.2617 | 172 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 54 | 30953.4561 | 377.0251 | 31330.4812 | 174 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 55 | 23422.0305 | 0 | 23422.0305 | 138 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 56 | 31228.9783 | 633.892 | 31862.8703 | 172 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 202 | 16889.0583 | 0 | 16889.0583 | 96 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  |  | 164711.5378 | 1010.9171 | 165722.4549 | 934 | 201 | 21.52% | 8040 | 4.881% |  | 1 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  | Rio Oso | [10 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 62 | 30714.3441 | 0 | 30714.3441 | 176 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 73 | 29002.0732 | 0 | 29002.0732 | 172 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 77 | 35294.3904 | 0 | 35294.3904 | 181 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 78 | 30267.3127 | 0 | 30267.3127 | 160 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  | Wind 79 | 20227.9346 | 0 | 20227.9346 | 107 | [5 empty] | 0 | 0 | Northern_California_Ex_Wind
Sacramento Valley Wind |  |  |  | 145506.0551 | 0 | 145506.0551 | 796 | 171 | 21.48% | 6840 | 4.701% |  | 1 | 0 | Northern_California_Ex_Wind
[13 empty] | 0 | 0 | 0
Solano Wind | Solano Wind | [11 empty] | 0 | 0 | Solano_Wind
Solano Wind |  | Lakeville | Wind 198 | 2361.3656 | 15002.7991 | 17364.1647 | 71 | [5 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  | Wind 101 | 2393.1548 | 29048.7635 | 31441.9184 | 166 | [5 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  | Wind 102 | 7207.3104 | 8590.8881 | 15798.1985 | 70 | [5 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  | Wind 196 | 2948.0119 | 31570.5233 | 34518.5353 | 146 | [5 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  | Wind 197 | 4625.9771 | 26007.4994 | 30633.4765 | 117 | [5 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  | Wind 199 | 4046.7783 | 26316.1556 | 30362.9339 | 136 | [5 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  |  | 23582.5981 | 136536.6291 | 160119.2272 | 706 | 227 | 32.15% | 9080 | 38.5% |  | 1 | 1 | Solano_Wind
Solano Wind |  | Tulucay | [10 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  | Wind 103 | 3479.2106 | 13204.9372 | 16684.1477 | 22 | [5 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  | Wind 106 | 5958.7606 | 19351.3274 | 25310.088 | 50 | [5 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  |  | 9437.9712 | 32556.2646 | 41994.2357 | 72 | 23 | 31.94% | 920 | 9.748% |  | 1 | 0 | Solano_Wind
Solano Wind |  | Vaca-Dixon & GC Yard | [10 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  | Wind 80 | 11733.2651 | 20668.7168 | 32401.9819 | 86 | [5 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  | Wind 81 | 23098.3902 | 11485.509 | 34583.8992 | 114 | [5 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  | Wind 82 | 30872.3849 | 0 | 30872.3849 | 77 | [5 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  | Wind 83 | 34973.0826 | 573.8062 | 35546.8888 | 80 | [5 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  | Wind 84 | 32773.4554 | 3679.007 | 36452.4624 | 89 | [5 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  | Wind 85 | 29812.5532 | 6243.4009 | 36055.9541 | 85 | [5 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  |  | 163263.1314 | 42650.4398 | 205913.5713 | 531 | 171 | 32.2% | 6840 | 4.19% |  | 1 | 0 | Solano_Wind
Solano Wind |  | Shilo III | [10 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  | Wind 91 | 28653.8156 | 5619.5354 | 34273.3509 | 82 | [5 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  | Wind 206 | 10020.747 | 4704.6326 | 14725.3796 | 34 | [5 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  | Wind 88 | 38048.726 | 3368.0093 | 41416.7354 | 88 | [5 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  | Wind 90 | 22115.5238 | 689.4769 | 22805.0007 | 57 | [5 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  |  | 98838.8124 | 14381.6542 | 113220.4666 | 261 | 84 | 32.18% | 3360 | 3.399% |  | 1 | 0 | Solano_Wind
Solano Wind |  | Lone Tree | [10 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  | Wind 104 | 5792.3906 | 16974.6621 | 22767.0528 | 35 | [5 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  | Wind 107 | 15567.8983 | 23209.4731 | 38777.3714 | 79 | [5 empty] | 0 | 0 | Solano_Wind
Solano Wind |  |  |  | 21360.289 | 40184.1352 | 61544.4242 | 114 | 37 | 32.46% | 1480 | 6.929% |  | 1 | 0 | Solano_Wind
[13 empty] | 0 | 0 | 0
Tehachapi Wind | Tehachapi Wind | [11 empty] | 0 | 0 | Tehachapi_Wind
Tehachapi Wind |  | Windhub | Wind 129 | 13670.7998 | 16116.6015 | 29787.4013 | 128 | [5 empty] | 0 | 0 | Tehachapi_Wind
Tehachapi Wind |  |  | Wind 156 | 12435.83 | 922.2979 | 13358.1279 | 86 | [5 empty] | 0 | 0 | Tehachapi_Wind
Tehachapi Wind |  |  | Wind 157 | 30641.6782 | 1300.9199 | 31942.5981 | 138 | [5 empty] | 0 | 0 | Tehachapi_Wind
Tehachapi Wind |  |  |  | 56748.308 | 18339.8193 | 75088.1273 | 352 | 275 | 78.12% | 11000 | 19.38% |  | 1 | 0 | Tehachapi_Wind

## 4_CommercialInterest
What constitutes level 3 criteria flag? |  | 300 | MW | Model selection 300 MW or more, in absence of any commercial interest
|  | 3000 | MW | Difference from commercial interest
What constitutes level 2 criteria flag? |  | 2000 | MW or greater | Difference from commercial interest
What constitutes level 1 criteria flag? |  | All other
Adjusted Portfolio
| Summary of Commercial Interest (Interconnection Queue / Zones Intersection) |  |  |  | Summary of Selected Portfolio (new RSP) | Selected by RESOLVE (2019 RSP) | Selected by RESOLVE (2019 RSP adj) | Zone | Technology | Commercial Interest, Summarized by RESOLVE Resource | Difference (Selected Portfolio) - (Commercial Interest) | Selected Portfolio, as Percent of Queue | Boolean: significant model selection in absence of commercial interest | Mapping criteria compliance level |  | Commercial Interest, Summarized by RESOLVE Resource | Difference (Selected Portfolio) - (Commercial Interest) | Selected Portfolio, as Percent of Queue | Boolean: significant model selection in absence of commercial interest | Mapping criteria compliance level
|  | Row Labels | Sum of MW-1 |  | InState_Biomass | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| 0 | 0 | 3204.733 |  | Greater_Imperial_Geothermal | 0 | 0 | SCADSNV_Z3_GreaterImperial | Geothermal | 100 | -100 | 0% | 0 | 1 |  | 0 | 100 | No commercial interest; 0 MW selected | 0 | 1
| 0 | Photovoltaic | 1102.265 |  | Inyokern_North_Kramer_Geothermal | 0 | 0 | GK_Z2_InyokernAndNorthOfKramer |  | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 |  | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1
| 0 | Storage | 1571.848 |  | Northern_California_Ex_Geothermal | 0 | 0 | NorCalOutsideTxConstraintZones | Geothermal | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 |  | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1
| 0 | Wind Turbine | 530.62 |  | Pacific_Northwest_Geothermal | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| GK_Z2_InyokernAndNorthOfKramer | GK_Z2_InyokernAndNorthOfKramer | 1300.5 |  | Riverside_Palm_Springs_Geothermal | 0 | 0 | SCADSNV_Z4_RiversideAndPalmSprings | Geothermal | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 |  | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1
| GK_Z2_InyokernAndNorthOfKramer | Photovoltaic | 824.26 |  | Solano_Geothermal | 0 | 0 | Norcal_Z4_Solano | Geothermal | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 |  | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1
| GK_Z2_InyokernAndNorthOfKramer | Storage | 476.24 |  | Southern_Nevada_Geothermal | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| GK_Z3_NorthOfVictor | GK_Z3_NorthOfVictor | 320.92 |  | Carrizo_Solar | 0 | 0 | SPGE_Z3_Carrizo | Photovoltaic | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 |  | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1
| GK_Z3_NorthOfVictor | Photovoltaic | 210.88 |  | Carrizo_Wind | 287 | 287 | SPGE_Z3_Carrizo | Wind Turbine | 0 | 287 | No commercial interest; 287 MW selected | 0 | 1 |  | 0 | -287 | No commercial interest; 287 MW selected | 0 | 1
| GK_Z3_NorthOfVictor | Storage | 110.04 |  | Central_Valley_North_Los_Banos_Solar | 0 | 0 | SPGE_Z4_CentralValleyAndLosBanos | Photovoltaic | 298.35 | -298.35 | 0% | 0 | 1 |  | 298.35 | 298.35 | 0% | 0 | 1
| GreaterImpOutsideTxConstraintZones | GreaterImpOutsideTxConstraintZones | 1319.1 |  | Central_Valley_North_Los_Banos_Wind | 173 | 173 | SPGE_Z4_CentralValleyAndLosBanos | Wind Turbine | 0 | 173 | No commercial interest; 173 MW selected | 0 | 1 |  | 0 | -173 | No commercial interest; 173 MW selected | 0 | 1
| GreaterImpOutsideTxConstraintZones | Storage | 1319.1 |  | Distributed_Solar | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| KramerInyoOutsideTxConstraintZones | KramerInyoOutsideTxConstraintZones | 511.18 |  | Distributed_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| KramerInyoOutsideTxConstraintZones | Storage | 511.18 |  | Greater_Imperial_Solar | 547.9 | 547.9 | SCADSNV_Z3_GreaterImperial | Photovoltaic | 3050.58 | -2502.68 | 17.96% | 0 | 2 |  | 3050.58 | 2502.68 | 17.96% | 0 | 2
| Norcal_Z2_Humboldt | Norcal_Z2_Humboldt | 348.1 |  | Greater_Imperial_Wind | 0 | 0 | SCADSNV_Z3_GreaterImperial | Wind Turbine | 1715.3 | -1715.3 | 0% | 0 | 1 |  | 1715.3 | 1715.3 | 0% | 0 | 1
| Norcal_Z2_Humboldt | Storage | 50.875 |  | Greater_Kramer_Wind | 0 | 0 | GK_Z1_GreaterKramer | Wind Turbine | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 |  | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1
| Norcal_Z2_Humboldt | Wind Turbine | 297.225 |  | Humboldt_Wind | 34 | 34 |  |  |  |  | No commercial interest; 34 MW selected | 0 |  |  |  |  | No commercial interest; 34 MW selected | 0
| Norcal_Z3_SacramentoRiver | Norcal_Z3_SacramentoRiver | 522 |  | Inyokern_North_Kramer_Solar | 97 | 97 | GK_Z2_InyokernAndNorthOfKramer | Photovoltaic | 824.26 | -727.26 | 11.77% | 0 | 1 |  | 824.26 | 727.26 | 11.77% | 0 | 1
| Norcal_Z3_SacramentoRiver | Photovoltaic | 12 |  | Kern_Greater_Carrizo_Solar | 241.66 | 241.66 | SPGE_Z2_KernAndGreaterCarrizo | Photovoltaic | 1898.196 | -1656.536 | 12.73% | 0 | 1 |  | 1898.196 | 1656.536 | 12.73% | 0 | 1
| Norcal_Z3_SacramentoRiver | Storage | 510 |  | Kern_Greater_Carrizo_Wind | 60 | 60 | SPGE_Z2_KernAndGreaterCarrizo | Wind Turbine | 1030.2 | -970.2 | 5.824% | 0 | 1 |  | 1030.2 | 970.2 | 5.824% | 0 | 1
| Norcal_Z4_Solano | Norcal_Z4_Solano | 1164.104 |  | Kramer_Inyokern_Ex_Solar | 0 | 0 | KramerInyoOutsideTxConstraintZones | Photovoltaic | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 |  | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1
| Norcal_Z4_Solano | Photovoltaic | 431.4 |  | Kramer_Inyokern_Ex_Wind | 0 | 0 | KramerInyoOutsideTxConstraintZones | Wind Turbine | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 |  | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1
| Norcal_Z4_Solano | Storage | 299 |  | Mountain_Pass_El_Dorado_Solar | 248 | 248 | SCADSNV_Z1_EldoradoAndMtnPass | Photovoltaic | 300 | -52 | 82.67% | 0 | 1 |  | 300 | 52 | 82.67% | 0 | 1
| Norcal_Z4_Solano | Wind Turbine | 433.704 |  | North_Victor_Solar | 300 | 300 | GK_Z3_NorthOfVictor | Photovoltaic | 210.88 | 89.12 | 142.3% | 0 | 1 |  | 210.88 | -89.12 | 142.3% | 0 | 1
| Norcal_Z4_Solano_subzone | Norcal_Z4_Solano_subzone | 120.4 |  | Northern_California_Ex_Solar | 0 | 0 | NorCalOutsideTxConstraintZones | Photovoltaic | 20.6 | -20.6 | 0% | 0 | 1 |  | 20.6 | 20.6 | 0% | 0 | 1
| Norcal_Z4_Solano_subzone | Storage | 120.4 |  | Northern_California_Ex_Wind | 865.9 | 865.9 | NorCalOutsideTxConstraintZones | Wind Turbine | 1774 | -908.1 | 48.81% | 0 | 1 |  | 1774 | 908.1 | 48.81% | 0 | 1
| NorCalOutsideTxConstraintZones | NorCalOutsideTxConstraintZones | 1996.155 |  | NW_Ext_Tx_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| NorCalOutsideTxConstraintZones | Hydro | 5 |  | Riverside_Palm_Springs_Solar | 0 | 0 | SCADSNV_Z4_RiversideAndPalmSprings | Photovoltaic | 2182 | -2182 | 0% | 0 | 2 | Model selecting less than queue (model = 0; queue = 2182 MW.) Note queue summary for this zone includes significant AZ solar (2595 MW), with POI specified in Riverside. | 4777.38 | 2182 | 0% | 0 | 2
| NorCalOutsideTxConstraintZones | Photovoltaic | 20.6 |  | Riverside_Palm_Springs_Wind | 0 | 0 | SCADSNV_Z4_RiversideAndPalmSprings | Wind Turbine | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 |  | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1
| NorCalOutsideTxConstraintZones | Steam Turbine | 5.5 |  | Sacramento_River_Solar | 0 | 0 | Norcal_Z3_SacramentoRiver | Photovoltaic | 12 | -12 | 0% | 0 | 1 |  | 12 | 12 | 0% | 0 | 1
| NorCalOutsideTxConstraintZones | Storage | 191.055 |  | Sacramento_River_Wind | 0 | 0 | Norcal_Z3_SacramentoRiver | Wind Turbine | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 |  | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1
| NorCalOutsideTxConstraintZones | Wind Turbine | 1774 |  | SCADSNV_Solar | 330 | 330 | SCADSNV_Z5_SCADSNV | Photovoltaic | 2000.104 | -1670.104 | 16.5% | 0 | 1 |  | 2000.104 | 1670.104 | 16.5% | 0 | 1
| SCADSNV_Z3_GreaterImperial | SCADSNV_Z3_GreaterImperial | 7194.91 |  | SCADSNV_Wind | 0 | 0 | SCADSNV_Z5_SCADSNV | Wind Turbine | 310 | -310 | 0% | 0 | 1 |  | 310 | 310 | 0% | 0 | 1
| SCADSNV_Z3_GreaterImperial | Photovoltaic | 3050.58 |  | Solano_Solar | 0 | 0 | Norcal_Z4_Solano | Photovoltaic | 431.4 | -431.4 | 0% | 0 | 1 |  | 431.4 | 431.4 | 0% | 0 | 1
| SCADSNV_Z3_GreaterImperial | Storage | 2429.03 |  | Solano_subzone_Solar | 0 | 0 | Norcal_Z4_Solano_subzone | Photovoltaic | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 |  | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1
| SCADSNV_Z3_GreaterImperial | Wind Turbine | 1715.3 |  | Solano_subzone_Wind | 0 | 0 | Norcal_Z4_Solano_subzone | Wind Turbine | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 |  | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1
| SCADSNV_Z4_RiversideAndPalmSprings | SCADSNV_Z4_RiversideAndPalmSprings | 8249.732 |  | Solano_Wind | 542 | 542 | Norcal_Z4_Solano | Wind Turbine | 433.704 | 108.296 | 125% | 0 | 1 |  | 433.704 | -108.296 | 125% | 0 | 1
| SCADSNV_Z4_RiversideAndPalmSprings | Photovoltaic | 4777.38 |  | Southern_California_Desert_Ex_Solar | 862 | 0 | SCADOutsideTxConstraintZones | Photovoltaic | 0 | 862 | No commercial interest; 862 MW selected | 1 | 3 |  | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1
| SCADSNV_Z4_RiversideAndPalmSprings | Steam Turbine | 49.5 |  | Southern_California_Desert_Ex_Wind | 0 | 0 | SCADOutsideTxConstraintZones | Wind Turbine | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 |  | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1
| SCADSNV_Z4_RiversideAndPalmSprings | Storage | 3422.852 |  | Southern_Nevada_Solar | 0 | 862 | SCADSNV_Z5_SCADSNV | Photovoltaic | 2000.104 | -2000.104 | 0% | 0 | 2 | Model selecting less than queue (model = 0; queue = 2000 MW.) | 2000.104 | 1138.104 | 43.1% | 0 | 1
| SCADSNV_Z5_SCADSNV | SCADSNV_Z5_SCADSNV | 3992.664 |  | Southern_Nevada_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| SCADSNV_Z5_SCADSNV | Photovoltaic | 2000.104 |  | SW_Ext_Tx_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| SCADSNV_Z5_SCADSNV | Storage | 1682.56 |  | Tehachapi_Solar | 4202 | 4202 | Tehachapi | Photovoltaic | 4697.9116 | -495.9116 | 89.44% | 0 | 1 |  | 4697.9116 | 495.9116 | 89.44% | 0 | 1
| SCADSNV_Z5_SCADSNV | Wind Turbine | 310 |  | Tehachapi_Ex_Solar | 0 | 0 | TehachapiOutsideTxConstraintZones | Photovoltaic | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1 |  | 0 | 0 | No commercial interest; 0 MW selected | 0 | 1
| SPGE_Z1_Westlands | SPGE_Z1_Westlands | 7402.177 |  | Tehachapi_Wind | 275 | 275 | Tehachapi | Wind Turbine | 728.66 | -453.66 | 37.74% | 0 | 1 |  | 728.66 | 453.66 | 37.74% | 0 | 1
| SPGE_Z1_Westlands | Combined Cycle | 60 |  | Westlands_Ex_Solar | 1778.57 | -0.43 | WestlandsOutsideTxConstraintZones | Photovoltaic | 604.239 | 1174.331 | 294.3% | 0 | 1 |  | 604.239 | 604.669 | -0.07116% | 0 | 1
| SPGE_Z1_Westlands | Gas Turbine | 63 |  | Westlands_Ex_Wind | 0 | 0 | WestlandsOutsideTxConstraintZones | Wind Turbine | 1568 | -1568 | 0% | 0 | 1 |  | 1568 | 1568 | 0% | 0 | 1
| SPGE_Z1_Westlands | Photovoltaic | 5245.997 |  | Westlands_Solar | 58.21 | 1836.21 | SPGE_Z1_Westlands | Photovoltaic | 5245.997 | -5187.787 | 1.11% | 0 | 3 |  | 5245.997 | 3409.787 | 35% | 0 | 3
| SPGE_Z1_Westlands | Storage | 1953.18 |  | Cape_Mendocino_Offshore_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| SPGE_Z1_Westlands | Wind Turbine | 80 |  | Del_Norte_Offshore_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| SPGE_Z2_KernAndGreaterCarrizo | SPGE_Z2_KernAndGreaterCarrizo | 4025.666 |  | Diablo_Canyon_Offshore_Wind_Ext_Tx | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| SPGE_Z2_KernAndGreaterCarrizo | Photovoltaic | 1898.196 |  | Diablo_Canyon_Offshore_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| SPGE_Z2_KernAndGreaterCarrizo | Storage | 1097.27 |  | Humboldt_Bay_Offshore_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| SPGE_Z2_KernAndGreaterCarrizo | Wind Turbine | 1030.2 |  | Morro_Bay_Offshore_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| SPGE_Z4_CentralValleyAndLosBanos | SPGE_Z4_CentralValleyAndLosBanos | 1114.986 |  | Utah_Solar | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| SPGE_Z4_CentralValleyAndLosBanos | Photovoltaic | 298.35 |  | Arizona_Solar | 2352.08 | 2352.08 | SCADSNV_Z4_RiversideAndPalmSprings | Photovoltaic | 2595 | -242.92 | 90.64% | 0 | 1 | Model selecting less than queue (model = 0; queue = 2595 MW). Sumarized manually by state in queue spreadsheet, to distentangle AZ solar overlap with other zones (interconnecting to substations in RiversidePalm Springs and Greater Imperial) | 4777.38 | 242.92 | 49.23% | 0 | 1
| SPGE_Z4_CentralValleyAndLosBanos | Storage | 816.636 |  | New_Mexico_Solar | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| Tehachapi | Tehachapi | 8631.4016 |  | Baja_California_Solar | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| Tehachapi | Photovoltaic | 4697.9116 |  | Baja_California_Wind | 600 | 600 | SCADSNV_Z3_GreaterImperial | Wind Turbine | 556 | 44 | 107.9% | 0 | 1 |  | 1715.3 | -44 | 34.98% | 0 | 1
| Tehachapi | Storage | 3204.83 |  | Pacific_Northwest_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| Tehachapi | Wind Turbine | 728.66 |  | Idaho_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| TehachapiOutsideTxConstraintZones | TehachapiOutsideTxConstraintZones | 2528.65 |  | Utah_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| TehachapiOutsideTxConstraintZones | Storage | 2528.65 |  | Wyoming_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| WestlandsOutsideTxConstraintZones | WestlandsOutsideTxConstraintZones | 3424.35 |  | Arizona_Wind | 0 | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0 |  |  |  |  | No commercial interest; 0 MW selected | 0
| WestlandsOutsideTxConstraintZones | Storage | 1856.35 |  | New_Mexico_Wind | 606.17 | 606.17 | SCADSNV_Z4_RiversideAndPalmSprings | Wind Turbine | 0 | 606.17 | No commercial interest; 606.17 MW selected | 1 | 3 |  | 0 | -606.17 | No commercial interest; 606.17 MW selected | 0 | 1
| WestlandsOutsideTxConstraintZones | Wind Turbine | 1568 |  | Pumped Storage Hydro | 0 | 974 | GreaterImpOutsideTxConstraintZones | Storage | 1319.1 | -1319.1 | 0% | 0 | 1 |  | 1319.1 | 345.1 | 73.84% | 0 | 1
| WestlandsOutsideTxConstraintZones | #N/A | 1379.889 |  |  | 14460.49 | 14459.49
| WestlandsOutsideTxConstraintZones | Combined Cycle | 35
| WestlandsOutsideTxConstraintZones | Photovoltaic | 604.239
| WestlandsOutsideTxConstraintZones | Storage | 740.65
| SPGE_Z3_Carrizo | SPGE_Z3_Carrizo | 606.2
| SPGE_Z3_Carrizo | Storage | 606.2
| None | None | 4336.85
| None | Storage | 4336.85
| Outside | Outside | 1512.6
| Outside | Storage | 1512.6
| GK_Z4_Pisgah | GK_Z4_Pisgah | 302.85
| GK_Z4_Pisgah | Photovoltaic | 302.85
| GK_Z1_GreaterKramer | GK_Z1_GreaterKramer | 156
| GK_Z1_GreaterKramer | Photovoltaic | 156
| SCADSNV_Z1_EldoradoAndMtnPass | SCADSNV_Z1_EldoradoAndMtnPass | 900
| SCADSNV_Z1_EldoradoAndMtnPass | Photovoltaic | 300
| SCADSNV_Z1_EldoradoAndMtnPass | Storage | 600
|  | Grand Total | 66566.1176
Note on L35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Note this is manually disentangled from resources physically located in AZ, with queue POI specified in Riverside Palm Springs zone
Note on S35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Note this is manually disentangled from resources physically located in AZ, with queue POI specified in Riverside Palm Springs zone
Note on L63: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sumarized manually by state in queue spreadsheet, to distentangle overlap with other zones (RiversidePalm Springs and Greater Imperial)
Note on S63: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sumarized manually by state in queue spreadsheet, to distentangle overlap with other zones (RiversidePalm Springs and Greater Imperial)
Note on L66: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Summarized manually by county in queue spreadsheet, to distentangle overlap with other zones (Greater Imperial)
Note on S66: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Summarized manually by county in queue spreadsheet, to distentangle overlap with other zones (Greater Imperial)

## 4b_QueuePivotTable
Source: PublicQueueReport_2019-12-04_matchedToZones_iso.xlsx
Row Labels | Sum of MW-1
0 | 3204.733
Photovoltaic | 1102.265
Storage | 1571.848
Wind Turbine | 530.62
GK_Z2_InyokernAndNorthOfKramer | 1300.5
Photovoltaic | 824.26
Storage | 476.24
GK_Z3_NorthOfVictor | 320.92
Photovoltaic | 210.88
Storage | 110.04
GreaterImpOutsideTxConstraintZones | 1319.1
Storage | 1319.1
KramerInyoOutsideTxConstraintZones | 511.18
Storage | 511.18
Norcal_Z2_Humboldt | 348.1
Storage | 50.875
Wind Turbine | 297.225
Norcal_Z3_SacramentoRiver | 522
Photovoltaic | 12
Storage | 510
Norcal_Z4_Solano | 1164.104
Photovoltaic | 431.4
Storage | 299
Wind Turbine | 433.704
Norcal_Z4_Solano_subzone | 120.4
Storage | 120.4
NorCalOutsideTxConstraintZones | 1996.155
Hydro | 5
Photovoltaic | 20.6
Steam Turbine | 5.5
Storage | 191.055
Wind Turbine | 1774
SCADSNV_Z3_GreaterImperial | 7194.91
Photovoltaic | 3050.58
Storage | 2429.03
Wind Turbine | 1715.3
SCADSNV_Z4_RiversideAndPalmSprings | 8249.732
Photovoltaic | 4777.38
Steam Turbine | 49.5
Storage | 3422.852
SCADSNV_Z5_SCADSNV | 3992.664
Photovoltaic | 2000.104
Storage | 1682.56
Wind Turbine | 310
SPGE_Z1_Westlands | 7402.177
Combined Cycle | 60
Gas Turbine | 63
Photovoltaic | 5245.997
Storage | 1953.18
Wind Turbine | 80
SPGE_Z2_KernAndGreaterCarrizo | 4025.666
Photovoltaic | 1898.196
Storage | 1097.27
Wind Turbine | 1030.2
SPGE_Z4_CentralValleyAndLosBanos | 1114.986
Photovoltaic | 298.35
Storage | 816.636
Tehachapi | 8631.4016
Photovoltaic | 4697.9116
Storage | 3204.83
Wind Turbine | 728.66
TehachapiOutsideTxConstraintZones | 2528.65
Storage | 2528.65
WestlandsOutsideTxConstraintZones | 3424.35
Storage | 1856.35
Wind Turbine | 1568
#N/A | 1379.889
Combined Cycle | 35
Photovoltaic | 604.239
Storage | 740.65
SPGE_Z3_Carrizo | 606.2
Storage | 606.2
None | 4336.85
Storage | 4336.85
Outside | 1512.6
Storage | 1512.6
GK_Z4_Pisgah | 302.85
Photovoltaic | 302.85
GK_Z1_GreaterKramer | 156
Photovoltaic | 156
SCADSNV_Z1_EldoradoAndMtnPass | 900
Photovoltaic | 300
Storage | 600
Grand Total | 66566.1176

## 5_BUSBAR ALLOC_Adj_TPPFeb2020
Source: CEC BUSBAR ALLOCATION_IRP 2020_PSP_02212020.xlsx
2018 PSP with Baseline Reconciliation and Norcal Geo Adjustments
Selected Renewables by Location
|  | Renewable Resource Summary by Location (MW) |  |  |  |  | Revised Busbar Allocation
|  | RESOLVE Resource | Tx Zone | 2030 FD | 2030 EO | TOTAL | SUBSTATION | MW ASSIGNED
|  | InState_Biomass | None
Greater_Imperial_Geothermal |  | Greater_Imperial_Geothermal | Greater_Imperial | 604 | 652 | 1256
Greater_Imperial_Geothermal | [6 empty] | Bannister 230kV (IID) | 628 | IID
Greater_Imperial_Geothermal | [6 empty] | Hudson Ranch 230kV (IID) | 628 | Connecting to IID Midway 230kV
Greater_Imperial_Geothermal
Greater_Imperial_Geothermal
|  | Inyokern_North_Kramer_Geothermal | Inyokern_North_Kramer
Northern_California_Ex_Geothermal |  | Northern_California_Ex_Geothermal | Northern_California_Ex
Northern_California_Ex_Geothermal | [6 empty] | Round Mountain
Pacific_Northwest_Geothermal
|  | Riverside_Palm_Springs_Geothermal | Riverside_Palm_Springs
|  | Solano_Geothermal | Solano
|  | Southern_Nevada_Geothermal | Mountain_Pass_El_Dorado
Carrizo_Wind |  | Carrizo_Wind | Carrizo |  | 160 | 160
Carrizo_Wind | [6 empty] | Templeton | 160
|  | Central_Valley_North_Los_Banos_Solar | Central_Valley_North_Los_Banos |  |  | 0
Central_Valley_North_Los_Banos_Wind |  | Central_Valley_North_Los_Banos_Wind | Central_Valley_North_Los_Banos | 146 |  | 146
Central_Valley_North_Los_Banos_Wind | [6 empty] | Los Banos | 146
|  | Distributed_Solar | None
|  | Distributed_Wind | None
|  | Greater_Imperial_Solar | Greater_Imperial |  |  | 0
|  | Greater_Imperial_Wind | Greater_Imperial
|  | Greater_Kramer_Wind | Greater_Kramer
|  | Humboldt_Wind | Humboldt
Inyokern_North_Kramer_Solar |  | Inyokern_North_Kramer_Solar | Inyokern_North_Kramer | 554 |  | 554
Inyokern_North_Kramer_Solar | [6 empty] | Caldwell | 263 | Victor Substation alloction removed due to significant land overlap with Caldwell Substation 81 MW reassigned form Victor to Caldwell | 63 | Pisgah 230kV | Connect Cool Water MWs at Pisgah, due to Tx constraints.
Inyokern_North_Kramer_Solar | [6 empty] | Calcite (Proposed) | 191 |  | 142 | Caldwell
Inyokern_North_Kramer_Solar | [6 empty] | Kramer 230kV | 100 |  | 191 | Calcite (Proposed)
Inyokern_North_Kramer_Solar | [9 empty] | 100 | Kramer 230kV
|  | Kern_Greater_Carrizo_Solar | Kern_Greater_Carrizo |  |  | 0
|  | Kern_Greater_Carrizo_Wind | Kern_Greater_Carrizo
|  | Kramer_Inyokern_Ex_Solar | Kramer_Inyokern_Ex
|  | Kramer_Inyokern_Ex_Wind | Kramer_Inyokern_Ex
|  | North_Victor_Solar | North_Victor_Solar |  |  | 0
|  | Northern_California_Ex_Solar | Northern_California_Ex
|  | Northern_California_Ex_Wind | Northern_California_Ex
|  | NW_Ext_Tx_Wind | Sacramento_River
Riverside_Palm_Springs_Solar |  | Riverside_Palm_Springs_Solar | Riverside_Palm_Springs | 192 | 1430 | 1622
Riverside_Palm_Springs_Solar | [6 empty] | Red Bluff | 1074
Riverside_Palm_Springs_Solar | [6 empty] | Colorado River | 548
Riverside_Palm_Springs_Wind |  | Riverside_Palm_Springs_Wind | Riverside_Palm_Springs | 42 |  | 42
Riverside_Palm_Springs_Wind | [6 empty] | Devers | 42
|  | Sacramento_River_Solar | Sacramento_River
Sacramento_River_Wind
|  | SCADSNV_Solar | SCADSNV
|  | SCADSNV_Wind | SCADSNV
|  | Solano_Solar | Solano
|  | Solano_subzone_Solar | Solano_subzone
|  | Solano_subzone_Wind | Solano_subzone
Solano_Wind |  | Solano_Wind | Solano |  | 643 | 643
Solano_Wind | [6 empty] | Lakeville | 270
Solano_Wind | [6 empty] | Tulucay | 27
Solano_Wind | [6 empty] | Vaca-Dixon & GC Yard | 203
Solano_Wind | [6 empty] | Shilo II | 100
Solano_Wind | [6 empty] | Lone Tree | 44
|  | Southern_California_Desert_Ex_Solar | Southern_California_Desert_Ex
|  | Southern_California_Desert_Ex_Wind | Southern_California_Desert_Ex
Southern_Nevada_Solar |  | Southern_Nevada_Solar | Mountain_Pass_El_Dorado | 802 | 2204 | 3006
Southern_Nevada_Solar | [6 empty] | Innovation | 152 | VA 700 MW FCDS Tx Constraint Limit
Southern_Nevada_Solar | [6 empty] | Desert View | 118
Southern_Nevada_Solar | [6 empty] | Crazy Eyes | 430
Southern_Nevada_Solar | [6 empty] | El Dorado 500 kV | 645 | EO
Southern_Nevada_Solar | [6 empty] | El Dorado 230 kV | 102 | FD
Southern_Nevada_Solar | [6 empty] | El Dorado 230 kV | 323 | EO
Southern_Nevada_Solar | [6 empty] | Mohave 500 kV | 1236 | EO Only
|  | Southern_Nevada_Wind | Mountain_Pass_El_Dorado
|  | SW_Ext_Tx_Wind | Riverside_Palm_Springs
Tehachapi_Solar |  | Tehachapi_Solar |  | 725 | 428 | 1153
Tehachapi_Solar | [6 empty] | WindHub | 277
Tehachapi_Solar | [6 empty] | Whirlwind | 307
Tehachapi_Solar | [6 empty] | Antelope | 300
Tehachapi_Solar | [6 empty] | Pearblossom | 269
|  | Tehachapi_Ex_Solar | Tehachapi_Ex
Tehachapi_Wind |  | Tehachapi_Wind | Tehachapi |  |  | 0
Tehachapi_Wind | [6 empty] | WindHub
|  | Westlands_Ex_Solar | Westlands_Ex
|  | Westlands_Ex_Wind | Westlands_Ex
|  | Westlands_Solar | Westlands |  |  | 0
|  | Utah_Solar | #N/A
|  | Arizona_Solar | #N/A |  | 428 | 428
Arizona_Solar | [6 empty] | Hassayampa | 47.08
Arizona_Solar | [6 empty] | Hoodoo Wash Switchyard | 222.56
Arizona_Solar | [6 empty] | Delaney-Colorado 500kV | 158.36
|  | New_Mexico_Solar | #N/A
|  | Baja_California_Wind | SCADSNV-Greater_Imperial
|  | Pacific_Northwest_Wind | #N/A
|  | Idaho_Wind | #N/A
|  | Utah_Wind | #N/A
|  | Wyoming_Wind | #N/A
|  | Arizona_Wind | #N/A
|  | New_Mexico_Wind | #N/A
|  | In-State |  | 3065 | 5945 | 9010 |  | 9011
|  | Out-Of-State |  | 0 | 0 | 0

## BUSBAR_ALLOC_AdjMar2020
Source file: CEC BUSBAR ALLOCATION_IRP 2020_SENSITIVITY1_v5.xlsx received 3/20/20
46MMT_20200207_2045_2GWPRM_NOOTCEXT_RSP_PD 03-10-2020
(Sensitivity 1 with Adjustments)
|  | Renewable Resource Summary by Location (MW) |  |  |  |  | Busbar Allocation
|  | RESOLVE Resource | Tx Zone | 2030 FD | 2030 EO | TOTAL | SUBSTATION | MW ASSIGNED | CEC NOTES
|  | InState_Biomass | None
|  | Greater_Imperial_Geothermal | SCADSNV-Greater_Imperial
|  | Inyokern_North_Kramer_Geothermal | Inyokern_North_Kramer
|  | Northern_California_Ex_Geothermal | Northern_California_Ex
Pacific_Northwest_Geothermal
|  | Riverside_Palm_Springs_Geothermal | Riverside_Palm_Springs
|  | Solano_Geothermal | Solano
|  | Southern_Nevada_Geothermal | Mountain_Pass_El_Dorado
Carrizo_Wind |  | Carrizo_Wind | Carrizo-Kern_Greater_Carrizo-SPGE | 287 |  | 287
Carrizo_Wind | [6 empty] | Templeton | 287
Central_Valley_North_Los_Banos_Solar |  | Central_Valley_North_Los_Banos_Solar | Central_Valley_North_Los_Banos-SPGE
Central_Valley_North_Los_Banos_Wind |  | Central_Valley_North_Los_Banos_Wind | Central_Valley_North_Los_Banos-SPGE | 173 |  | 173
Central_Valley_North_Los_Banos_Wind | [6 empty] | Los Banos 230kV | 173 | Assign this Wind Resource and MW to Westlands Tx Zone
|  | Distributed_Solar | None
|  | Distributed_Wind | None
Greater_Imperial_Solar |  | Greater_Imperial_Solar | SCADSNV-Greater_Imperial |  | 548 | 548
Greater_Imperial_Solar | [6 empty] | Imperial Valley | 332
Greater_Imperial_Solar | [6 empty] | Ocotillo Express | 216
|  | Greater_Imperial_Wind | SCADSNV-Greater_Imperial
|  | Greater_Kramer_Wind | Greater_Kramer
Humboldt_Wind |  | Humboldt_Wind | Humboldt-Sacramento_River |  | 34 | 34
Humboldt_Wind | [6 empty] | Bridgeville 115kv | 34
Inyokern_North_Kramer_Solar |  | Inyokern_North_Kramer_Solar | Inyokern_North_Kramer-Greater_Kramer | 97 |  | 97
Inyokern_North_Kramer_Solar | [6 empty] | Kramer | 43
Inyokern_North_Kramer_Solar | [6 empty] | Randsburg | 54
Kern_Greater_Carrizo_Solar |  | Kern_Greater_Carrizo_Solar | Kern_Greater_Carrizo-SPGE | 834 | 145 | 979
Kern_Greater_Carrizo_Solar | [6 empty] | Arco | 202
Kern_Greater_Carrizo_Solar | [6 empty] | Midway | 195
Kern_Greater_Carrizo_Solar | [6 empty] | Renfro | 201
Kern_Greater_Carrizo_Solar | [6 empty] | Stockdale | 201
Kern_Greater_Carrizo_Solar | [6 empty] | Wheeler Ridge | 180
Kern_Greater_Carrizo_Wind |  | Kern_Greater_Carrizo_Wind | Kern_Greater_Carrizo-SPGE | 60 |  | 60
Kern_Greater_Carrizo_Wind | [6 empty] | Arco | 60 | Gen-tie 19-23 miles, add to Arco solar MW
|  | Kramer_Inyokern_Ex_Solar | Kramer_Inyokern_Ex
|  | Kramer_Inyokern_Ex_Wind | Kramer_Inyokern_Ex
Mountain_Pass_El_Dorado_Solar |  | Mountain_Pass_El_Dorado_Solar |  |  | 248 | 248
Mountain_Pass_El_Dorado_Solar | [6 empty] | El Dorado 230kV | 83
Mountain_Pass_El_Dorado_Solar | [6 empty] | EL Dorado 500kV | 165
North_Victor_Solar |  | North_Victor_Solar | North_Victor-Greater_Kramer | 300 |  | 300
North_Victor_Solar | [6 empty] | Victor | 215
North_Victor_Solar | [6 empty] | Coolwater | 85
|  | Northern_California_Ex_Solar | Northern_California_Ex
Northern_California_Ex_Wind |  | Northern_California_Ex_Wind | Sacramento_River | 866 |  | 866
Northern_California_Ex_Wind | [6 empty] | Glenn | 400
Northern_California_Ex_Wind | [6 empty] | Delevan | 94
Northern_California_Ex_Wind | [6 empty] | Thermalito | 201
Northern_California_Ex_Wind | [6 empty] | Rio Oso | 171
|  | NW_Ext_Tx_Wind | Sacramento_River
Riverside_Palm_Springs_Solar |  | Riverside_Palm_Springs_Solar | SCADSNV-Riverside_Palm_Springs | 1000 |  | 1000
Riverside_Palm_Springs_Solar | [6 empty] | Red Bluff | 662
Riverside_Palm_Springs_Solar | [6 empty] | Colorado River | 338
|  | Riverside_Palm_Springs_Wind | SCADSNV-Riverside_Palm_Springs
|  | Sacramento_River_Solar | Sacramento_River
|  | Sacramento_River_Wind | Sacramento_River
SCADSNV_Solar |  | SCADSNV_Solar | SCADSNV |  | 330 | 330
SCADSNV_Solar | [6 empty] | Mohave 500kV | 330
|  | SCADSNV_Wind | SCADSNV
|  | Solano_Solar | Sacramento_River-Solano
|  | Solano_subzone_Solar | Sacramento_River-Solano-Solano_subzone
|  | Solano_subzone_Wind | Sacramento_River-Solano-Solano_subzone
Solano_Wind |  | Solano_Wind | Sacramento_River-Solano | 542 |  | 542
Solano_Wind | [6 empty] | Lakeville | 227
Solano_Wind | [6 empty] | Tulucay | 23
Solano_Wind | [6 empty] | Vaca-Dixon & GC Yard | 171
Solano_Wind | [6 empty] | Shilo III | 84
Solano_Wind | [6 empty] | Lone Tree | 37
|  | Southern_California_Desert_Ex_Solar | Southern_California_Desert_Ex |  |  | 0
|  | Southern_California_Desert_Ex_Wind | Southern_California_Desert_Ex
Southern_Nevada_Solar |  | Southern_Nevada_Solar | SCADSNV-GLW_VEA | 862 |  | 862
Southern_Nevada_Solar | [6 empty] | Innovation | 154 | FD 700 MW
Southern_Nevada_Solar | [6 empty] | Desert View | 119
Southern_Nevada_Solar | [6 empty] | Crazy Eyes | 427
Southern_Nevada_Solar | [6 empty] | El Dorado 230kV | 54 | FD
Southern_Nevada_Solar | [6 empty] | El Dorado 500kV | 108 | FD
Southern_Nevada_Solar | [6 empty] | Mohave 500kV
|  | Southern_Nevada_Wind | SCADSNV-GLW_VEA
|  | SW_Ext_Tx_Wind | SCADSNV-Riverside_Palm_Springs
Tehachapi_Solar |  | Tehachapi_Solar | Tehachapi | 2402 | 800 | 3202
Tehachapi_Solar | [6 empty] | WindHub | 770
Tehachapi_Solar | [6 empty] | Whirlwind | 852
Tehachapi_Solar | [6 empty] | Antelope | 832
Tehachapi_Solar | [6 empty] | Pearblossom | 748
|  | Tehachapi_Ex_Solar | Tehachapi_Ex
Tehachapi_Wind |  | Tehachapi_Wind | Tehachapi | 275 |  | 275
Tehachapi_Wind | [6 empty] | WindHub | 275
|  | Westlands_Ex_Solar | Westlands_Ex
|  | Westlands_Ex_Wind | Westlands_Ex
Westlands_Solar |  | Westlands_Solar | SPGE_Z1_Westlands | 1041 | 58 | 1099
Westlands_Solar | [6 empty] | Gates | 158.5125
Westlands_Solar | [6 empty] | Helm | 185.6363
Westlands_Solar | [6 empty] | Henrietta | 171.6456
Westlands_Solar | [6 empty] | Mc Call | 214.5991
Westlands_Solar | [6 empty] | Mc Mullin | 200.0717
Westlands_Solar | [6 empty] | Panoche | 168.5348
|  | Utah_Solar | #N/A
Arizona_Solar |  | Arizona_Solar | SCADSNV-Riverside_Palm_Springs | 1196 | 1156 | 2352
Arizona_Solar | [6 empty] | Hassayampa | 258.72
Arizona_Solar | [6 empty] | Hoodoo Wash Switchyard | 1223.04
Arizona_Solar | [6 empty] | Delaney-Colorado 500kV | 870.24
|  | New_Mexico_Solar | #N/A
Baja_California_Wind |  | Baja_California_Wind | SCADSNV-Greater_Imperial | 600 |  | 600
Baja_California_Wind | [6 empty] | East County | 600
|  | Pacific_Northwest_Wind | #N/A
|  | Idaho_Wind | #N/A
|  | Utah_Wind | #N/A
|  | Wyoming_Wind | Mountain_Pass_El_Dorado-SCADSNV
|  | Arizona_Wind | #N/A
New_Mexico_Wind |  | New_Mexico_Wind | SCADSNV-Riverside_Palm_Springs |  |  | 606
New_Mexico_Wind | [6 empty] | Palo Verde | 606 | SunZia/Devers-Palo Verde 500kV
|  | In-State |  | 10535 | 3319 | 14460 |  | 14460
Out-Of-State

## BUSBAR ALLOCATION_Adj (2)
Source: CEC BUSBAR ALLOCATION_IRP 2020_SENSITIVITY1_v6.xlsx received 3/25/20
46MMT_20200207_2045_2GWPRM_NOOTCEXT_RSP_PD 03-25-2020
(Sensitivity 1 with Adjustments)
|  | Renewable Resource Summary by Location (MW) |  |  |  |  | Busbar Allocation
|  | RESOLVE Resource | Tx Zone | 2030 FD | 2030 EO | TOTAL | SUBSTATION | MW ASSIGNED | CEC NOTES
|  | InState_Biomass | None
|  | Greater_Imperial_Geothermal | SCADSNV-Greater_Imperial
|  | Inyokern_North_Kramer_Geothermal | Inyokern_North_Kramer
|  | Northern_California_Ex_Geothermal | Northern_California_Ex
Pacific_Northwest_Geothermal
|  | Riverside_Palm_Springs_Geothermal | Riverside_Palm_Springs
|  | Solano_Geothermal | Solano
|  | Southern_Nevada_Geothermal | Mountain_Pass_El_Dorado
Carrizo_Wind |  | Carrizo_Wind | Carrizo-Kern_Greater_Carrizo-SPGE | 287 |  | 287
Carrizo_Wind | [6 empty] | Templeton | 287
Central_Valley_North_Los_Banos_Solar |  | Central_Valley_North_Los_Banos_Solar | Central_Valley_North_Los_Banos-SPGE
Central_Valley_North_Los_Banos_Wind |  | Central_Valley_North_Los_Banos_Wind | Central_Valley_North_Los_Banos-SPGE/SPGE_Z1_Westlands | 173 |  | 173 |  |  | Assign this Wind Resource and MW to Westlands Tx Zone
Central_Valley_North_Los_Banos_Wind | [6 empty] | Los Banos 230kV | 173
|  | Distributed_Wind | None
Greater_Imperial_Solar |  | Greater_Imperial_Solar | SCADSNV-Greater_Imperial |  | 548 | 548
Greater_Imperial_Solar | [6 empty] | Imperial Valley | 332
Greater_Imperial_Solar | [6 empty] | Ocotillo Express | 216
|  | Greater_Imperial_Wind | SCADSNV-Greater_Imperial
|  | Greater_Kramer_Wind | Greater_Kramer
Humboldt_Wind |  | Humboldt_Wind | Humboldt-Sacramento_River |  | 34 | 34
Humboldt_Wind | [6 empty] | Bridgeville 115kv | 34
Inyokern_North_Kramer_Solar |  | Inyokern_North_Kramer_Solar | Inyokern_North_Kramer-Greater_Kramer | 97 |  | 97
Inyokern_North_Kramer_Solar | [6 empty] | Kramer | 43
Inyokern_North_Kramer_Solar | [6 empty] | Randsburg | 54
Kern_Greater_Carrizo_Solar |  | Kern_Greater_Carrizo_Solar | Kern_Greater_Carrizo-SPGE | 97 | 145 | 242 |  |  | Adjustment Made
Kern_Greater_Carrizo_Solar | [6 empty] | Arco | 50
Kern_Greater_Carrizo_Solar | [6 empty] | Midway | 48
Kern_Greater_Carrizo_Solar | [6 empty] | Renfro | 50
Kern_Greater_Carrizo_Solar | [6 empty] | Stockdale | 50
Kern_Greater_Carrizo_Solar | [6 empty] | Wheeler Ridge | 45
Kern_Greater_Carrizo_Wind |  | Kern_Greater_Carrizo_Wind | Kern_Greater_Carrizo-SPGE | 60 |  | 60
Kern_Greater_Carrizo_Wind | [6 empty] | Cholame 70 kV | 60 | Assign to Cholame Sub to reduce gentie distance. May require local upgrade to connect project(s)
|  | Kramer_Inyokern_Ex_Solar | Kramer_Inyokern_Ex
|  | Kramer_Inyokern_Ex_Wind | Kramer_Inyokern_Ex
Mountain_Pass_El_Dorado_Solar |  | Mountain_Pass_El_Dorado_Solar |  | 248 |  | 248
Mountain_Pass_El_Dorado_Solar | [6 empty] | El Dorado 230kV | 83
Mountain_Pass_El_Dorado_Solar | [6 empty] | EL Dorado 500kV | 165
North_Victor_Solar |  | North_Victor_Solar | North_Victor-Greater_Kramer | 300 |  | 300
North_Victor_Solar | [6 empty] | Victor | 215
North_Victor_Solar | [6 empty] | Coolwater | 85
|  | Northern_California_Ex_Solar | Northern_California_Ex
Northern_California_Ex_Wind |  | Northern_California_Ex_Wind | Northern_California_Ex/Sacramento_River | 866 |  | 866 |  |  | Assign this Wind Resource and MW to Sacramento_River Tx Zone
Northern_California_Ex_Wind | [6 empty] | Glenn | 400
Northern_California_Ex_Wind | [6 empty] | Delevan | 94
Northern_California_Ex_Wind | [6 empty] | Thermalito | 201
Northern_California_Ex_Wind | [6 empty] | Rio Oso | 171
|  | NW_Ext_Tx_Wind | Sacramento_River
Riverside_Palm_Springs_Solar |  | Riverside_Palm_Springs_Solar | SCADSNV-Riverside_Palm_Springs |  |  | 0 |  |  | Adjustment Made
Riverside_Palm_Springs_Solar | [6 empty] | Red Bluff
Riverside_Palm_Springs_Solar | [6 empty] | Colorado River
|  | Riverside_Palm_Springs_Wind | SCADSNV-Riverside_Palm_Springs
|  | Sacramento_River_Solar | Sacramento_River
|  | Sacramento_River_Wind | Sacramento_River
SCADSNV_Solar |  | SCADSNV_Solar | SCADSNV |  | 330 | 330
SCADSNV_Solar | [6 empty] | Mohave 500kV | 330
|  | SCADSNV_Wind | SCADSNV
|  | Solano_Solar | Sacramento_River-Solano
|  | Solano_subzone_Solar | Sacramento_River-Solano-Solano_subzone
|  | Solano_subzone_Wind | Sacramento_River-Solano-Solano_subzone
Solano_Wind |  | Solano_Wind | Sacramento_River-Solano | 542 |  | 542
Solano_Wind | [6 empty] | Lakeville | 227
Solano_Wind | [6 empty] | Tulucay | 23
Solano_Wind | [6 empty] | Vaca-Dixon & GC Yard | 171
Solano_Wind | [6 empty] | Shilo III | 84
Solano_Wind | [6 empty] | Lone Tree | 37
|  | Southern_California_Desert_Ex_Solar | Southern_California_Desert_Ex |  |  | 0
|  | Southern_California_Desert_Ex_Wind | Southern_California_Desert_Ex
Southern_Nevada_Solar |  | Southern_Nevada_Solar | SCADSNV-GLW_VEA | 862 |  | 862
Southern_Nevada_Solar | [6 empty] | Innovation | 154 | FD 700 MW
Southern_Nevada_Solar | [6 empty] | Desert View | 119
Southern_Nevada_Solar | [6 empty] | Crazy Eyes | 427
Southern_Nevada_Solar | [6 empty] | El Dorado 230kV | 54 | FD
Southern_Nevada_Solar | [6 empty] | El Dorado 500kV | 108 | FD
Southern_Nevada_Solar | [6 empty] | Mohave 500kV
|  | Southern_Nevada_Wind | SCADSNV-GLW_VEA
|  | SW_Ext_Tx_Wind | SCADSNV-Riverside_Palm_Springs
Tehachapi_Solar |  | Tehachapi_Solar | Tehachapi | 3402 | 800 | 4202 |  |  | Adjustment Made
Tehachapi_Solar | [6 empty] | WindHub | 1010
Tehachapi_Solar | [6 empty] | Whirlwind | 1119
Tehachapi_Solar | [6 empty] | Antelope | 1092
Tehachapi_Solar | [6 empty] | Pearblossom | 981
|  | Tehachapi_Ex_Solar | Tehachapi_Ex
Tehachapi_Wind |  | Tehachapi_Wind | Tehachapi | 275 |  | 275
Tehachapi_Wind | [6 empty] | WindHub | 275
|  | Westlands_Ex_Solar | Westlands_Ex
|  | Westlands_Ex_Wind | Westlands_Ex
Westlands_Solar |  | Westlands_Solar | SPGE_Z1_Westlands | 1778 | 58 | 1836 |  |  | Adjustment Made | 1353
Westlands_Solar | [6 empty] | Gates | 70
Westlands_Solar | [6 empty] | Helm | 82
Westlands_Solar | [6 empty] | Henrietta | 75
Westlands_Solar | [6 empty] | Mc Call | 94
Westlands_Solar | [6 empty] | Mc Mullin | 88 |  | Alternate Allocation
Westlands_Solar | [6 empty] | Panoche | 74
Westlands_Solar | [6 empty] | Gates 500kV | 1353 | New Gates to Diablo 500kV Tx Line | Gates 500kV | 1836 | New Gates to Diablo 500kV Tx Line
|  | Pumped Storage Project | GreaterImpOutsideTxConstraintZones |  |  | 487
[7 empty] | Lee Lake 500kV (Proposed) | 487 | Pumped Storage Project
|  | Pumped Storage Project | GreaterImpOutsideTxConstraintZones |  |  | 487
[7 empty] | Sycamore Canyon 230kV | 487 | Pumped Storage Project
|  | Utah_Solar | #N/A
Arizona_Solar |  | Arizona_Solar | SCADSNV-Riverside_Palm_Springs | 1196 | 1156 | 2352
Arizona_Solar | [6 empty] | Hassayampa | 258.72
Arizona_Solar | [6 empty] | Hoodoo Wash Switchyard | 1223.04
Arizona_Solar | [6 empty] | Delaney-Colorado 500kV | 870.24
|  | New_Mexico_Solar | #N/A
Baja_California_Wind |  | Baja_California_Wind | SCADSNV-Greater_Imperial | 600 |  | 600
Baja_California_Wind | [6 empty] | East County | 600
|  | Pacific_Northwest_Wind | #N/A
|  | Idaho_Wind | #N/A
|  | Utah_Wind | #N/A
|  | Wyoming_Wind | Mountain_Pass_El_Dorado-SCADSNV
|  | Arizona_Wind | #N/A
|  | New_Mexico_Wind | SCADSNV-Riverside_Palm_Springs |  |  | 606
[7 empty] | Palo Verde | 606 | SunZia/Devers-Palo Verde 500kV
|  | In-State |  | 10783 | 3071 | 15434 |  | 15435
Out-Of-State

## SNV_Detail
Analysis of Round 2 mapping with focus on Southern Nevada
| SCADSNV | SCADSNV_Solar EO | Mountain_Pass_El_Dorado_Solar | Southern_Nevada_Solar FD | Southern_Nevada_Solar EO | Southern_Nevada_Wind FD | Wyoming_Wind | Substation Totals | FDCS | EO
| Innovation |  |  | 154 |  |  |  | 154
| Desert View |  |  | 119 |  |  |  | 119
| Crazy Eyes |  |  | 427 |  |  |  | 427
| El Dorado 230kV |  | 83 | 54 |  |  |  | 137
| El Dorado 500kV |  | 165 | 108 |  |  |  | 273
| Mohave 500kV | 330 | [5 empty] | 330
| Totals | 330 | 248 | 862 |  | 0 | 0 | 1440 | 862 | 578

## 5b_ComparToPrevYr
What constitutes level 3 criteria flag? | 1000 | or greater | Difference from prior year
What constitutes level 2 criteria flag? | 0.6 | or greater | Difference from prior year
What constitutes level 1 criteria flag?
032019 FD + EO
RESOLVE Resource | 2018 PSP | 2019 RSP | Delta | Difference > 1000 MW? | Dashboard value |  | 2019 RSP adj | Delta | Difference > 1000 MW? | Dashboard value
InState_Biomass | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Greater_Imperial_Geothermal | 1256 | 0 | -100% | 1 | 3 | >1000 MW difference from prior year | 0 | -100% | 1 | 3 | >1000 MW difference from prior year
Inyokern_North_Kramer_Geothermal | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Northern_California_Ex_Geothermal | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Pacific_Northwest_Geothermal | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Riverside_Palm_Springs_Geothermal | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Solano_Geothermal | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Southern_Nevada_Geothermal | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Carrizo_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Carrizo_Wind | 160 | 287 | 79.38% | 0 | 2 | >60% difference from prior portfolio | 287 | 79.38% | 0 | 2 | >60% difference from prior portfolio
Central_Valley_North_Los_Banos_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1 | >60% difference from prior portfolio
Central_Valley_North_Los_Banos_Wind | 146 | 173 | 18.49% | 0 | 1 |  | 173 | 18.49% | 0 | 1
Distributed_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Distributed_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Greater_Imperial_Solar | 0 | 547.9 | 54790% | 0 | 2 | >60% difference from prior portfolio | 547.9 | 54790% | 0 | 2 | >60% difference from prior portfolio
Greater_Imperial_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Greater_Kramer_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Humboldt_Wind | 0 | 34 | 3400% | 0 | 2 | >60% difference from prior portfolio | 34 | 3400% | 0 | 2 | >60% difference from prior portfolio
Inyokern_North_Kramer_Solar | 554 | 97 | -82.49% | 0 | 2 | >60% difference from prior portfolio | 97 | -82.49% | 0 | 2 | >60% difference from prior portfolio
Kern_Greater_Carrizo_Solar | 0 | 241.66 | 24166% | 0 | 2 | >60% difference from prior portfolio | 241.66 | 24166% | 0 | 2 | >60% difference from prior portfolio
Kern_Greater_Carrizo_Wind | 0 | 60 | 6000% | 0 | 2 | >60% difference from prior portfolio | 60 | 6000% | 0 | 2 | >60% difference from prior portfolio
Kramer_Inyokern_Ex_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Kramer_Inyokern_Ex_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Mountain_Pass_El_Dorado_Solar | 0 | 248 | 24800% | 0 | 2 | >60% difference from prior portfolio | 248 | 24800% | 0 | 2 | >60% difference from prior portfolio
North_Victor_Solar | 0 | 300 | 30000% | 0 | 2 | >60% difference from prior portfolio | 300 | 30000% | 0 | 2 | >60% difference from prior portfolio
Northern_California_Ex_Solar | 0 | 0 | 0% | 0 | 1 | >60% difference from prior portfolio | 0 | 0% | 0 | 1 | >60% difference from prior portfolio
Northern_California_Ex_Wind | 0 | 865.9 | 86590% | 0 | 2 | >60% difference from prior portfolio | 865.9 | 86590% | 0 | 2 | >60% difference from prior portfolio
NW_Ext_Tx_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Riverside_Palm_Springs_Solar | 1622 | 0 | -100% | 1 | 3 | >1000 MW difference from prior year | 0 | -100% | 1 | 3
Sacramento_River_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Sacramento_River_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
SCADSNV_Solar | 0 | 330 | 33000% | 0 | 2 | >60% difference from prior portfolio | 330 | 33000% | 0 | 2 | >60% difference from prior portfolio
SCADSNV_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Solano_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Solano_subzone_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Solano_subzone_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Solano_Wind | 644 | 542 | -15.84% | 0 | 1 |  | 542 | -15.84% | 0 | 1
Southern_California_Desert_Ex_Solar | 0 | 862 | 86200% | 0 | 2 | >60% difference from prior portfolio | 0 | 0% | 0 | 1
Southern_California_Desert_Ex_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Southern_Nevada_Solar | 3006 | 0 | -100% | 1 | 3 | >1000 MW difference from prior year | 862 | -71.32% | 1 | 3 | >1000 MW difference from prior year
Southern_Nevada_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
SW_Ext_Tx_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Tehachapi_Solar | 1153 | 4202 | 264.4% | 1 | 3 | >1000 MW difference from prior year | 4202 | 264.4% | 1 | 3 | >1000 MW difference from prior year
Tehachapi_Ex_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Tehachapi_Wind | 0 | 275 | 27500% | 0 | 2 | >60% difference from prior portfolio | 275 | 27500% | 0 | 2 | >60% difference from prior portfolio
Westlands_Ex_Solar | 0 | 1778.57 | 177857% | 1 | 3 | >1000 MW difference from prior year | -0.43 | -43% | 0 | 1 | >1000 MW difference from prior year
Westlands_Ex_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Westlands_Solar | 0 | 58.21 | 5821% | 0 | 2 | >60% difference from prior portfolio | 1836.21 | 183621% | 1 | 3 | >60% difference from prior portfolio
Cape_Mendocino_Offshore_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Del_Norte_Offshore_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Diablo_Canyon_Offshore_Wind_Ext_Tx | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Diablo_Canyon_Offshore_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Humboldt_Bay_Offshore_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Morro_Bay_Offshore_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Utah_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Arizona_Solar | 428 | 2352.08 | 449.6% | 1 | 3 | >1000 MW difference from prior year | 2352.08 | 449.6% | 1 | 3 | >1000 MW difference from prior year
New_Mexico_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Baja_California_Solar | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Baja_California_Wind | 0 | 600 | 60000% | 0 | 2 | >60% difference from prior portfolio | 600 | 60000% | 0 | 2 | >60% difference from prior portfolio
Pacific_Northwest_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Idaho_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Utah_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Wyoming_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
Arizona_Wind | 0 | 0 | 0% | 0 | 1 |  | 0 | 0% | 0 | 1
New_Mexico_Wind | 0 | 606.17 | 60617% | 0 | 2 | >60% difference from prior portfolio | 606.17 | 60617% | 0 | 2 | >60% difference from prior portfolio
Pumped Storage Hydro | 0 | 0 | 0% | 0 | 1 |  | 974 | 97400% | 0 | 2 | >60% difference from prior portfolio
| 8969 | 14460.49 |  |  |  |  | 14459.49
Note on B4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Source: Feb 2020 Busbar Allocation