## Cover
2020-05-11
This workbook creates wind, solar, and battery ELCC assumptions to be used exclusively for estimating capacity contribution from resources included in an LSE's portfolio in the 2020 IRP filings due to the CPUC on September 1, 2020.
The Resource Data Template directly uses these ELCC assumptions to create the "System Reliability Progress Tracking Table" for each LSE within the Data Template.
The ELCCs are based on current Resource Adequacy values through 2023 and based on RESOLVE-derived ELCCs afterwards.
The tab "ELCC Timeseries_46MMT" shows the assumptions to be used for 46 MMT Conforming Portfolios.
The tab "ELCC Timeseries_38MMT" shows the assumptions to be used for 38 MMT Conforming Portfolios.
These ELCC assumptions are solely for the purpose of estimating capacity contribution in 2020 IRP filings and no other purpose.

## Methodology
Step | Description
1 | SERVM-based September monthly ELCC values from the RA proceeding are used for wind and utility-scale solar resources from 2020-2023.
2 | Wind and utility-scale solar values for 2026 and 2030 are developed using the RESOLVE model's solar and wind ELCC surface. 2027, 2028, and 2029 are based on interpolation between 2026 and 2030.
2a | The peak reduction of Customer PV is calculated from IEPR data and is removed from the RESOLVE total wind + solar ELCC.
2b | In-state wind ELCC is derived from the RESOLVE ELCC surface.
2c | Out-of-state wind is given a higher ELCC value than in-state wind based on its higher capacity factor.
2d | After removing the customer PV peak reduction and the wind ELCC MW from the RESOLVE total wind + solar portfolio ELCC, the remaining ELCC MW are assigned to utility-scale solar. The utility-scale solar ELCC % is then derived by dividing the remaining ELCC MW by utility-scale solar installed capacity.
3 | For the years 2024 and 2025, an interpolation is done between the RA proceeding 2023 and RESOLVE 2026 values.
4 | Energy storage ELCC values are derived from the SERVM-informed battery ELCC curve used as an input into RESOLVE, combined with the storage penetrations in each year of the RESOLVE model outputs.

## ELCC Timeseries_46MMT
Annual ELCC Summary (46MMT / RSP) | [12 empty] | Notes
| Year | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
| Data Source | Resource Data Template (CPUC SERVM for RA) |  |  |  | Blend |  | RESOLVE
ELCC % (Average) | Solar (utility-scale) | 14% | 14% | 14% | 14% | 12.27% | 10.54% | 8.811% | 8.837% | 8.863% | 8.889% | 8.915%
ELCC % (Average) | Wind (in-state) | 15% | 15% | 15% | 15% | 17.33% | 19.67% | 22% | 22% | 22% | 22% | 22%
ELCC % (Average) | Wind (OOS, new Tx) | 18.88% | 18.88% | 18.88% | 18.88% | 21.82% | 24.75% | 27.69% | 27.69% | 27.69% | 27.69% | 27.69%
ELCC % (Average) | 4-hour battery | 100% | 100% | 100% | 100% | 100% | 98.3% | 96.6% | 96.6% | 96.6% | 96.6% | 96.6% | Declining marginal ELCC causes 4-hour battery capacity value to be <100% in the late 2020s.
ELCC % (Average) | 2-hour battery | 50% | 50% | 50% | 50% | 50% | 49.15% | 48.3% | 48.3% | 48.3% | 48.3% | 48.3% | Consistent with current RA accounting rules, the ELCC % of a 2 hour battery is half that of a 4-hour battery
Wind and Solar ELCCs
Month for SERVM ELCC | 9
Variable Renewable ELCC (Incl. BTM) | Wind + Solar | 8514 | 8675 | 9330 | 9414 | 9690 |  | 10094 |  |  |  | 10383 | Wind+solar (inc. BTM) variable renewable portfolio ELCC MW from RESOLVE outputs
Customer PV
Installed MW | Customer_PV | 9827 | 11137 | 12284 | 13303 | 14288 |  | 16156 |  |  |  | 20066
Customer PV Implied ELCC (%) | Customer_PV | 44.86% | 47.09% | 45.62% | 43.03% | 40.86% |  | 36.12% |  |  |  | 28.11% | Because customer PV is on the demand-side, peak reductions from customer PV count "before" utility-scale PV because the load profile on which the utility-scale ELCC is calculated has already been reduced by customer PV production
Assumed Peak Contribution MW | Customer_PV | 4408.1621 | 5244.5288 | 5604.0355 | 5724.86 | 5837.6946 |  | 5834.9161 |  |  |  | 5641.323
Wind, in-state
Installed MW, in-state Wind | Wind | 7357 | 7490 | 9406 | 9406 | 10193 |  | 10193 |  |  |  | 10293
ELCC % (Average), from RA | Wind | 15% | 15% | 15% | 15% | [7 empty] | Per existing ELCC in RA proceeding
ELCC % (Marginal @ 35% CF), from RESOLVE | Wind | [6 empty] | 22% |  |  |  | 22%
ELCC %, combined | Wind | 15% | 15% | 15% | 15% | 17.33% | 19.67% | 22% | 22% | 22% | 22% | 22% | Use RA through 2023, then switch to RESOLVE marginal by 2026. For wind, marginal is assumed to be reasonably close to average, especially in the mid-2020s and beyond when the net peak has shifted into the early evening.
ELCC MW | Wind | 1103.55 | 1123.5 | 1410.9 | 1410.9 | 1766.7867 |  | 2242.46 |  |  |  | 2264.46
Capacity factor used to calculate RESOLVE marginal ELCC | Wind | 35% | 35% | 35% | 35% | 35% |  | 35% |  |  |  | 35% | Not used directly in the in-state wind calculation, but used to scale OOS wind ELCC below
Wind, OOS
New Mexico Wind CF % | 44.05% | [11 empty] | Representative of a NM wind resource (note: WY wind has a very similar CF)
Installed MW, OOS Wind | Wind OOS New Tx | [6 empty] | - |  |  |  | 606
ELCC % (Average), from RA | Wind OOS New Tx | 18.88% | 18.88% | 18.88% | 18.88% | [7 empty] | Scaled up RA values by higher CF
ELCC % (Marginal @ 44% CF), from RESOLVE | Wind OOS New Tx | [6 empty] | 27.69% |  |  |  | 27.69% | NOTE: OOS wind not available before 2026 in RESOLVE
ELCC %, combined | Wind OOS New Tx | 18.88% | 18.88% | 18.88% | 18.88% | 21.82% | 24.75% | 27.69% | 27.69% | 27.69% | 27.69% | 27.69% | For wind, marginal is assumed to be reasonably close to average, especially in the mid-2020s and beyond when the net peak has shifted into the early evening.
ELCC MW | Wind OOS New Tx | [6 empty] | 0 |  |  |  | 167.7927
Solar, Utility-Scale
Remaining ELCC | Solar | 3002.2879 | 2306.9712 | 2315.0645 | 2278.24 | 2085.5187 |  | 2016.6239 |  |  |  | 2309.4243 | Utility-scale solar is assigned remaining variable renewable portfolio ELCC that is not attributed to either customer PV or wind
Installed MW | Solar | 16310 | 18766 | 20887 | 22887 | 22887 |  | 22887 |  |  |  | 25905
ELCC %, from SERVM runs | Solar | 14% | 14% | 14% | 14% | [7 empty] | Per existing ELCC in RA proceeding
ELCC %, Implied average from RESOLVE | Solar | [6 empty] | 8.811% |  |  |  | 8.915% | Remaining portfolio ELCC divided by installed utility-scale solar capacity
ELCC %, combined | Solar | 14% | 14% | 14% | 14% | 12.27% | 10.54% | 8.811% | 8.837% | 8.863% | 8.889% | 8.915%
ELCC MW | Solar | 2283.4 | 2627.24 | 2924.18 | 3204.18 | 2808.328 |  | 2016.6239 |  |  |  | 2309.4243
Battery Storage ELCCs
Battery, 4 hour
Installed MW |  | 1123.8 | 3774.94 | 3774.94 | 3832.51 | 4916.32 |  | 7744.63 |  |  |  | 10490.7 | Raw power capacity - includes all durations.
Installed MWh |  | 4495.19 | 15099.77 | 15394.77 | 15764.77 | 19665.28 |  | 30978.54 |  |  |  | 30978.54 | Information only - duration de-rate performed on Raw_Resource_Build_LiBattery tab
Duration (hours) |  | 4 | 4 | 4 | 4 | 4 |  | 4 |  |  |  | 2.953 | Information only - duration de-rate performed on Raw_Resource_Build_LiBattery tab
4-hour equivalent capacity, pre-ELCC curve, MW |  | 1123.7975 | 3774.94 | 3774.94 | 3832.51 | 4916.32 |  | 7744.63 |  |  |  | 7744.63 | Any battery that has less than four hours of duration is converted into a 4-hr equivalent based on ratio of MWh to MW
PRM Contribution, MW |  | 1123.8 | 3774.94 | 3774.94 | 3832.51 | 4916.32 | 0 | 7481.58 | 0 | 0 | 0 | 7481.58 | ELCC curve de-rate applied to 4-hr equivalent capacity
ELCC %, 4 hour duration |  | 100% | 100% | 100% | 100% | 100% | 98.3% | 96.6% | 96.6% | 96.6% | 96.6% | 96.6% | Declining marginal ELCC causes 4-hour battery capacity value to be <100% in the late 2020s.
Battery, 2 hour
ELCC %, 2 hour duration |  | 50% | 50% | 50% | 50% | 50% | 49.15% | 48.3% | 48.3% | 48.3% | 48.3% | 48.3% | Consistent with current RA accounting rules, the ELCC % of a 2 hour battery is half that of a 4-hour battery

## ELCC Timeseries_38MMT
Annual ELCC Summary (38 MMT) | [12 empty] | Notes
| Year | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
| Data Source | Resource Data Template (CPUC SERVM for RA) |  |  |  | Blend |  | RESOLVE
ELCC % (Average) | Solar (utility-scale) | 14% | 14% | 14% | 14% | 12.16% | 10.32% | 8.485% | 7.524% | 6.564% | 5.603% | 4.642%
ELCC % (Average) | Wind (in-state) | 15% | 15% | 15% | 15% | 17.27% | 19.53% | 21.8% | 21.77% | 21.75% | 21.72% | 21.69%
ELCC % (Average) | Wind (OOS, new Tx) | 18.88% | 18.88% | 18.88% | 18.88% | 21.73% | 24.59% | 27.44% | 27.4% | 27.37% | 27.34% | 27.3%
ELCC % (Average) | 4-hour battery | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 98.3% | 96.6% | 94.9% | 93.21% | Declining marginal ELCC causes 4-hour battery capacity value to be <100% in the late 2020s.
ELCC % (Average) | 2-hour battery | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 49.15% | 48.3% | 47.45% | 46.6% | Consistent with current RA accounting rules, the ELCC % of a 2 hour battery is half that of a 4-hour battery
Wind and Solar ELCCs
Month for SERVM ELCC | 9
Variable Renewable ELCC (Incl. BTM) | Wind + Solar | 8513.72 | 8675.27 | 9552.02 | 9652.11 | 9881.72 |  | 10291.36 |  |  |  | 10470.85 | Wind+solar (inc. BTM) variable renewable portfolio ELCC MW from RESOLVE outputs
Customer PV
Installed MW | Customer_PV | 9827.31 | 11136.82 | 12284.27 | 13303.04 | 14288.23 |  | 16155.51 |  |  |  | 20066.03
Customer PV Implied ELCC (%) | Customer_PV | 44.86% | 47.09% | 45.62% | 43.03% | 40.86% |  | 36.12% |  |  |  | 28.11% | Because customer PV is on the demand-side, peak reductions from customer PV count "before" utility-scale PV because the load profile on which the utility-scale ELCC is calculated has already been reduced by customer PV production
Assumed Peak Contribution MW | Customer_PV | 4408.1621 | 5244.5288 | 5604.0355 | 5724.86 | 5837.6946 |  | 5834.9161 |  |  |  | 5641.323
Wind, in-state
Installed MW, in-state Wind | Wind | 7356.56 | 7490.31 | 10380.08 | 10380.08 | 11267.08 |  | 11267.08 |  |  |  | 12735.24
ELCC % (Average), from RA | Wind | 15% | 15% | 15% | 15% | [7 empty] | Per existing ELCC in RA proceeding
ELCC % (Marginal @ 35% CF), from RESOLVE | Wind | [6 empty] | 21.8% |  |  |  | 21.69%
ELCC %, combined | Wind | 15% | 15% | 15% | 15% | 17.27% | 19.53% | 21.8% | 21.77% | 21.75% | 21.72% | 21.69% | Use RA through 2023, then switch to RESOLVE marginal by 2026. For wind, marginal is assumed to be reasonably close to average, especially in the mid-2020s and beyond when the net peak has shifted into the early evening.
ELCC MW | Wind | 1103.484 | 1123.5465 | 1557.012 | 1557.012 | 1945.5179 |  | 2456.4296 |  |  |  | 2762.5618
Capacity factor used to calculate RESOLVE marginal ELCC | Wind | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 |  | 35% |  |  |  | 35% | Not used directly in the in-state wind calculation, but used to scale OOS wind ELCC below
Wind, OOS
New Mexico Wind CF % | 44.05% | [11 empty] | Representative of a NM wind resource (note: WY wind has a very similar CF)
Installed MW, OOS Wind | Wind OOS New Tx | [6 empty] | 0 |  |  |  | 3000
ELCC % (Average), from RA | Wind OOS New Tx | 18.88% | 18.88% | 18.88% | 18.88% | [7 empty] | Scaled up RA values by higher CF
ELCC % (Marginal @ 44% CF), from RESOLVE | Wind OOS New Tx | [6 empty] | 27.44% |  |  |  | 27.3% | NOTE: OOS wind not available before 2026 in RESOLVE
ELCC %, combined | Wind OOS New Tx | 18.88% | 18.88% | 18.88% | 18.88% | 21.73% | 24.59% | 27.44% | 27.4% | 27.37% | 27.34% | 27.3% | For wind, marginal is assumed to be reasonably close to average, especially in the mid-2020s and beyond when the net peak has shifted into the early evening.
ELCC MW | Wind OOS New Tx | [6 empty] | 0 |  |  |  | 819.0379
Solar, Utility-Scale
Remaining ELCC | Solar | 3002.0739 | 2307.1947 | 2390.9725 | 2370.238 | 2098.5075 |  | 2000.0143 |  |  |  | 1247.9273 | Utility-scale solar is assigned remaining variable renewable portfolio ELCC that is not attributed to either customer PV or wind
Installed MW | Solar | 16310.33 | 18765.85 | 20887.45 | 22887.45 | 22887.45 |  | 23571.29 |  |  |  | 26882.73
ELCC %, from SERVM runs | Solar | 14% | 14% | 14% | 14% | [7 empty] | Per existing ELCC in RA proceeding
ELCC %, Implied average from RESOLVE | Solar | [6 empty] | 8.485% |  |  |  | 4.642% | Remaining portfolio ELCC divided by installed utility-scale solar capacity
ELCC %, combined | Solar | 14% | 14% | 14% | 14% | 12.16% | 10.32% | 8.485% | 7.524% | 6.564% | 5.603% | 4.642%
ELCC MW | Solar | 2283.4462 | 2627.219 | 2924.243 | 3204.243 | 2783.4923 |  | 2000.0143 |  |  |  | 1247.9273
Battery Storage ELCCs
Battery, 4 hour
Installed MW |  | 1123.82 | 3774.96 | 3774.96 | 3774.96 | 4724.81 |  | 6653.14 |  |  |  | 11331.24 | Raw power capacity - includes all durations.
Installed MWh |  | 4495.28 | 15099.85 | 15394.85 | 15764.85 | 18899.23 |  | 26612.58 |  |  |  | 37062.01 | Information only - duration de-rate performed on Raw_Resource_Build_LiBattery tab
Duration (hours) |  | 4 | 4 | 4 | 4 | 4 |  | 4 |  |  |  | 3.271 | Information only - duration de-rate performed on Raw_Resource_Build_LiBattery tab
4-hour equivalent capacity, pre-ELCC curve, MW |  | 1123.82 | 3774.96 | 3774.96 | 3774.96 | 4724.8075 |  | 6653.14 |  |  |  | 9265.4975 | Any battery that has less than four hours of duration is converted into a 4-hr equivalent based on ratio of MWh to MW
PRM Contribution, MW |  | 1123.82 | 3774.96 | 3774.96 | 3774.96 | 4724.81 | 0 | 6653.14 | 0 | 0 | 0 | 8635.92 | ELCC curve de-rate applied to 4-hr equivalent capacity
ELCC %, 4 hour duration |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 98.3% | 96.6% | 94.9% | 93.21% | Declining marginal ELCC causes 4-hour battery capacity value to be <100% in the late 2020s.
Battery, 2 hour
ELCC %, 2 hour duration |  | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 49.15% | 48.3% | 47.45% | 46.6% | Consistent with current RA accounting rules, the ELCC % of a 2 hour battery is half that of a 4-hour battery

## elcc (RDT)
type | month | elcc_percent | From technology factor tab of
wind | 1 | 0.14 | https://www.cpuc.ca.gov/WorkArea/DownloadAsset.aspx?id=6442463337
wind | 2 | 0.12
wind | 3 | 0.28
wind | 4 | 0.25
wind | 5 | 0.25
wind | 6 | 0.33
wind | 7 | 0.23
wind | 8 | 0.21
wind | 9 | 0.15
wind | 10 | 0.08
wind | 11 | 0.12
wind | 12 | 0.13
solar | 1 | 0.04
solar | 2 | 0.03
solar | 3 | 0.18
solar | 4 | 0.15
solar | 5 | 0.16
solar | 6 | 0.31
solar | 7 | 0.39
solar | 8 | 0.27
solar | 9 | 0.14
solar | 10 | 0.02
solar | 11 | 0.02
solar | 12 | 0
biomass | 1 | 0.82
biomass | 2 | 0.86
biomass | 3 | 0.84
biomass | 4 | 0.76
biomass | 5 | 0.83
biomass | 6 | 0.89
biomass | 7 | 0.87
biomass | 8 | 0.9
biomass | 9 | 0.9
biomass | 10 | 0.81
biomass | 11 | 0.85
biomass | 12 | 0.86
cogen | 1 | 0.81
cogen | 2 | 0.79
cogen | 3 | 0.73
cogen | 4 | 0.66
cogen | 5 | 0.79
cogen | 6 | 0.85
cogen | 7 | 0.83
cogen | 8 | 0.83
cogen | 9 | 0.8
cogen | 10 | 0.72
cogen | 11 | 0.78
cogen | 12 | 0.82
geothermal | 1 | 0.95
geothermal | 2 | 0.92
geothermal | 3 | 0.88
geothermal | 4 | 0.76
geothermal | 5 | 0.74
geothermal | 6 | 0.7
geothermal | 7 | 0.84
geothermal | 8 | 0.82
geothermal | 9 | 0.83
geothermal | 10 | 0.86
geothermal | 11 | 0.93
geothermal | 12 | 0.95
hydro | 1 | 0.6
hydro | 2 | 0.7
hydro | 3 | 0.73
hydro | 4 | 0.72
hydro | 5 | 0.69
hydro | 6 | 0.74
hydro | 7 | 0.73
hydro | 8 | 0.72
hydro | 9 | 0.71
hydro | 10 | 0.64
hydro | 11 | 0.56
hydro | 12 | 0.64
thermal | 1 | 1
thermal | 2 | 1
thermal | 3 | 1
thermal | 4 | 1
thermal | 5 | 1
thermal | 6 | 1
thermal | 7 | 1
thermal | 8 | 1
thermal | 9 | 1
thermal | 10 | 1
thermal | 11 | 1
thermal | 12 | 1
battery | 1 | 1
battery | 2 | 1
battery | 3 | 1
battery | 4 | 1
battery | 5 | 1
battery | 6 | 1
battery | 7 | 1
battery | 8 | 1
battery | 9 | 1
battery | 10 | 1
battery | 11 | 1
battery | 12 | 1
nuclear | 1 | 1
nuclear | 2 | 1
nuclear | 3 | 1
nuclear | 4 | 1
nuclear | 5 | 1
nuclear | 6 | 1
nuclear | 7 | 1
nuclear | 8 | 1
nuclear | 9 | 1
nuclear | 10 | 1
nuclear | 11 | 1
nuclear | 12 | 1

## elcc_type_map (RDT)
elcc_type | resolve_final_group | lower
battery | IID_Li_Battery | iid_li_battery
battery | CAISO_Li_Battery | caiso_li_battery
battery | CAISO_Battery | caiso_battery
biomass | CAISO_Biogas | caiso_biogas
biomass | CAISO_Biomass | caiso_biomass
biomass | Excluded_Biomass | excluded_biomass
biomass | NW_Biomass | nw_biomass
biomass | SW_Biomass | sw_biomass
biomass | IID_Biomass | iid_biomass
biomass | BANC_Biomass | banc_biomass
cogen | Excluded_CHP | excluded_chp
cogen | CAISO_CHP | caiso_chp
geothermal | SW_Geothermal | sw_geothermal
geothermal | NW_Geothermal | nw_geothermal
geothermal | CAISO_Geothermal | caiso_geothermal
geothermal | Excluded_Geothermal | excluded_geothermal
geothermal | IID_Geothermal | iid_geothermal
hydro | CAISO_Small_Hydro | caiso_small_hydro
hydro | Excluded_Hydro | excluded_hydro
hydro | SW_Hydro | sw_hydro
hydro | NW_Hydro | nw_hydro
hydro | CAISO_Hydro | caiso_hydro
hydro | LDWP_Hydro | ldwp_hydro
hydro | Excluded_Pumped_Hydro | excluded_pumped_hydro
hydro | BANC_Hydro | banc_hydro
hydro | LDWP_Pumped_Hydro | ldwp_pumped_hydro
hydro | IID_Hydro | iid_hydro
hydro | NW_Pumped_Hydro | nw_pumped_hydro
hydro | SW_Pumped_Hydro | sw_pumped_hydro
hydro | CAISO_Pumped_Hydro | caiso_pumped_hydro
nuclear | NW_Nuclear | nw_nuclear
nuclear | SW_Nuclear | sw_nuclear
nuclear | CAISO_Nuclear | caiso_nuclear
nuclear | LDWP_Nuclear | ldwp_nuclear
solar | CAISO_Solar | caiso_solar
solar | SW_Solar | sw_solar
solar | LDWP_Solar | ldwp_solar
solar | NW_Solar | nw_solar
solar | Excluded_Solar | excluded_solar
solar | BANC_Solar | banc_solar
solar | IID_Solar | iid_solar
thermal | Excluded_ST | excluded_st
thermal | Excluded_Reciprocating_Engine | excluded_reciprocating_engine
thermal | SW_CCGT | sw_ccgt
thermal | SW_ST | sw_st
thermal | SW_Peaker | sw_peaker
thermal | Excluded_Peaker | excluded_peaker
thermal | BANC_Peaker | banc_peaker
thermal | SW_Coal | sw_coal
thermal | LDWP_CCGT | ldwp_ccgt
thermal | Excluded_CCGT | excluded_ccgt
thermal | NW_Peaker | nw_peaker
thermal | Excluded_Coal | excluded_coal
thermal | NW_CCGT | nw_ccgt
thermal | NW_Coal | nw_coal
thermal | BANC_CCGT | banc_ccgt
thermal | IID_Peaker | iid_peaker
thermal | IID_CCGT | iid_ccgt
thermal | LDWP_ST | ldwp_st
thermal | LDWP_Peaker | ldwp_peaker
thermal | CAISO_Peaker2 | caiso_peaker2
thermal | CAISO_CCGT2 | caiso_ccgt2
thermal | CAISO_ST | caiso_st
thermal | CAISO_Peaker1 | caiso_peaker1
thermal | CAISO_CCGT1 | caiso_ccgt1
thermal | CAISO_Reciprocating_Engine | caiso_reciprocating_engine
thermal | CAISO_Coal | caiso_coal
thermal | LDWP_Coal | ldwp_coal
thermal | CAISO_Steam | caiso_steam
unknown | LDWP_Var-DEVICE | ldwp_var-device
unknown | SW_Imports | sw_imports
unknown | NW_Var-DEVICE | nw_var-device
unknown | CAISO_Imports | caiso_imports
unknown | Excluded_Imports | excluded_imports
unknown | LDWP_Unknown | ldwp_unknown
unknown | IID_Load | iid_load
unknown | NW_Unknown | nw_unknown
unknown | Excluded_Load | excluded_load
unknown | Excluded_Var-DEVICE | excluded_var-device
unknown | CAISO_Unknown | caiso_unknown
unknown | CAISO_Hybrid | caiso_hybrid
unknown | unspecified_import | unspecified_import
unknown | transfer_purchase | transfer_purchase
unknown | transfer_sale | transfer_sale
unknown | blended | blended
unknown | unbundled_rec | unbundled_rec
unknown | unspecified_non_import | unspecified_non_import
unknown | CAISO_DR | caiso_dr
unknown | CAISO_Specified_Imports | caiso_specified_imports
unknown | CAISO_Loadmod | caiso_loadmod
wind | CAISO_Wind | caiso_wind
wind | SW_Wind | sw_wind
wind | Excluded_Wind | excluded_wind
wind | NW_Wind | nw_wind
wind | LDWP_Wind | ldwp_wind

## Loads - Forecast
Load Assumptions
|  | T&D losses | 7.24%
|  | CAISO share of statewide load | 82%
| CAISO Sales Forecast Buildup |  | Values represent demand at customer meter
|  | Baseline Consumption (GWh) |  |  | Method | Last Year | Period | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | CEC 2018 IEPR - Mid Demand | CAISO |  |  |  |  | 235681.2673 | 237318.7247 | 239965.896 | 243136.2001 | 246638.1404 | 249764.4813 | 252520.0054 | 255257.1474 | 257559.1998 | 259843.9046 | 261895.0979 | 263830.4482 | 265707.3431 | 267069.3213 | 268431.2995 | 269793.2776 | 271155.2558 | 272517.2339 | 273879.2121 | 275241.1902 | 276603.1684 | 277965.1466 | 279327.1247 | 280689.1029 | 282051.081 | 283413.0592 | 284775.0374 | 286137.0155 | 287678.5662 | 289239.0004 | 290816.5779 | 292407.5008 | 294004.1891
|  | CEC 2018 IEPR - High Demand | CAISO |  | CAGR | 2030 | 5 | 236552.1242 | 240210.5928 | 244103.2463 | 248230.4887 | 252470.636 | 256499.7486 | 260076.3525 | 263674.9322 | 266752.913 | 269729.6247 | 272608.4527 | 275198.3327 | 277856.5157 | 280783.0801 | 283740.469 | 286729.0071 | 289749.0223 | 292800.8463 | 295884.8141 | 299001.2643 | 302150.5389 | 305332.9837 | 308548.948 | 311798.785 | 315082.8514 | 318401.5076 | 321755.1181 | 325144.051 | 328568.6784 | 332029.3761 | 335526.5241 | 339060.5064 | 342631.7108
|  | CEC Pathways Baseload | CAISO |  |  |  |  | 235681.2673 | 237318.7247 | 239965.896 | 243136.2001 | 246638.1404 | 249764.4813 | 252520.0054 | 255257.1474 | 257559.1998 | 259843.9046 | 261895.0979 | 263830.4482 | 265707.3431 | 266240.8855 | 267068.4824 | 268138.1631 | 269372.4707 | 270759.6149 | 272190.5907 | 273733.8155 | 275374.0763 | 277085.3078 | 278852.7046 | 280234.9099 | 281660.2964 | 283122.6372 | 284616.7131 | 286137.0155 | 287678.5662 | 289239.0004 | 290816.5779 | 292407.5008 | 294004.1891
|  | Active: CEC 2018 IEPR - Mid Demand | CAISO |  |  |  |  | 235681.2673 | 237318.7247 | 239965.896 | 243136.2001 | 246638.1404 | 249764.4813 | 252520.0054 | 255257.1474 | 257559.1998 | 259843.9046 | 261895.0979 | 263830.4482 | 265707.3431 | 267069.3213 | 268431.2995 | 269793.2776 | 271155.2558 | 272517.2339 | 273879.2121 | 275241.1902 | 276603.1684 | 277965.1466 | 279327.1247 | 280689.1029 | 282051.081 | 283413.0592 | 284775.0374 | 286137.0155 | 287678.5662 | 289239.0004 | 290816.5779 | 292407.5008 | 294004.1891
|  | Electric Vehicles (GWh) |  |  | Method | Last Year | Period | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | CEC 2018 IEPR - Mid Demand | CAISO |  |  |  |  | 2741.1311 | 3659.4928 | 4577.9906 | 5641.2911 | 6817.2503 | 8044.5787 | 9078.5063 | 10016.361 | 10726.5989 | 11356.6772 | 12068.3541 | 12796.7098 | 13566.6575 | 14694.5253 | 15822.3932 | 16950.2611 | 18078.129 | 19205.9969 | 20333.8648 | 21461.7327 | 22589.6006 | 23717.4685 | 24845.3364 | 25973.2042 | 27101.0721 | 28228.94 | 29356.8079 | 30484.6758 | 25562.4074 | 26055.8842 | 26483.8328 | 26849.5295 | 27152.5871
|  | CEC 2018 IEPR - High Demand | CAISO |  |  |  |  | 2741.1311 | 3738.5672 | 4764.6237 | 5930.4497 | 7205.0541 | 8549.2053 | 9887.3912 | 11188.8239 | 12039.5982 | 12715.358 | 13515.8606 | 14308.918 | 15159.6856 | 16181.3516 | 17203.0176 | 18224.6836 | 19246.3496 | 20268.0157 | 21289.6817 | 22311.3477 | 23333.0137 | 24354.6797 | 25376.3457 | 26398.0117 | 27419.6778 | 28441.3438 | 29463.0098 | 30484.6758 | 25562.4074 | 26055.8842 | 26483.8328 | 26849.5295 | 27152.5871
|  | CEC Pathways High Biofuels | CAISO |  |  |  |  | 577.9967 | 883.5174 | 1109.6841 | 1461.3063 | 1946.3607 | 2601.8949 | 3502.6177 | 4527.0432 | 5861.8796 | 7103.5046 | 8304.1635 | 9600.924 | 11098.5158 | 12673.0181 | 14368.7848 | 16099.0238 | 17758.6115 | 19324.7948 | 20769.4939 | 22124.9586 | 23388.4343 | 24552.2059 | 25624.8651 | 26796.8552 | 27865.3434 | 28834.346 | 29707.0644 | 30484.6758 | 31173.6675 | 31775.4685 | 32297.357 | 32743.3286 | 33112.9111
|  | CEC Pathways High Electrification | CAISO |  |  |  |  | 578.0944 | 883.7998 | 1110.141 | 1461.8451 | 1946.5034 | 2600.6429 | 3496.6817 | 4514.3486 | 5838.3783 | 7078.897 | 8303.887 | 9694.5937 | 11442.3815 | 13514.5031 | 15916.3255 | 18436.8747 | 20879.4478 | 23166.5554 | 25275.8482 | 27246.6972 | 29074.195 | 30745.5394 | 32267.9463 | 33850.344 | 35259.9181 | 36494.1091 | 37550.7019 | 38427.4671 | 39128.5715 | 39655.7501 | 40021.3145 | 40234.7749 | 40305.9284
|  | CEC Pathways High Hydrogen | CAISO |  |  |  |  | 578.0944 | 883.7998 | 1110.141 | 1461.8451 | 1946.5034 | 2600.6429 | 3496.6817 | 4514.3486 | 5838.3783 | 7078.897 | 8303.887 | 9694.5937 | 11442.3815 | 13514.5031 | 15916.3255 | 18436.8747 | 20879.4478 | 23166.5554 | 25275.8482 | 27246.6972 | 29074.195 | 30745.5394 | 32267.9463 | 33850.344 | 35259.9181 | 36494.1091 | 37550.7019 | 38427.4671 | 39128.5715 | 39655.7501 | 40021.3145 | 40234.7749 | 40305.9284
|  | Active: CEC 2018 IEPR - Mid Demand | CAISO |  |  |  |  | 2741.1311 | 3659.4928 | 4577.9906 | 5641.2911 | 6817.2503 | 8044.5787 | 9078.5063 | 10016.361 | 10726.5989 | 11356.6772 | 12068.3541 | 12796.7098 | 13566.6575 | 14694.5253 | 15822.3932 | 16950.2611 | 18078.129 | 19205.9969 | 20333.8648 | 21461.7327 | 22589.6006 | 23717.4685 | 24845.3364 | 25973.2042 | 27101.0721 | 28228.94 | 29356.8079 | 30484.6758 | 25562.4074 | 26055.8842 | 26483.8328 | 26849.5295 | 27152.5871
|  | Other Transport Electrification (GWh) |  |  | Method | Last Year | Period | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | CEC 2018 IEPR - Mid Demand | CAISO |  |  |  |  | 114.6355 | 167.4178 | 222.3265 | 261.6296 | 306.145 | 356.3201 | 408.3882 | 464.4035 | 520.4005 | 543.7903 | 571.5257 | 640.6938 | 682.9825 | 2427.5517 | 4172.1209 | 5916.6902 | 7661.2594 | 9405.8287 | 11150.3979 | 12894.9671 | 14639.5364 | 16384.1056 | 18128.6748 | 19873.2441 | 21617.8133 | 23362.3825 | 25106.9518 | 26851.521 | 23051.2872 | 24077.9698 | 25098.0163 | 26108.7262 | 27110.9033
|  | None | CAISO |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CEC Pathways High Biofuels | CAISO |  |  |  |  | 732.9311 | 894.3532 | 1198.1575 | 1445.945 | 1734.2731 | 2045.6837 | 2478.0695 | 2987.602 | 3596.208 | 4268.6565 | 4995.5304 | 5785.1814 | 6615.1322 | 7772.0924 | 8974.747 | 10204.8601 | 11491.3766 | 12867.2229 | 14292.6529 | 15789.614 | 17304.2461 | 18826.4226 | 20332.6862 | 21669.8979 | 22990.8497 | 24295.7423 | 25579.7474 | 26851.521 | 28111.3258 | 29363.3778 | 30607.3369 | 31839.91 | 33062.0772
|  | CEC Pathways High Electrification | CAISO |  |  |  |  | 732.9311 | 894.3533 | 1198.1576 | 1445.9452 | 1734.2738 | 2045.6854 | 2478.0748 | 2987.6179 | 3596.2553 | 4268.7914 | 4995.8915 | 5786.1062 | 6617.4115 | 7777.5675 | 8987.9186 | 10235.7548 | 11561.8496 | 13017.6942 | 14572.5312 | 16235.1925 | 17911.8229 | 19584.7261 | 21210.5801 | 22664.4602 | 24091.5994 | 25492.9345 | 26862.3216 | 28208.5087 | 29529.9629 | 30828.8096 | 32101.8094 | 33343.6229 | 34554.116
|  | CEC Pathways High Hydrogen | CAISO |  |  |  |  | 700.9658 | 845.6552 | 1126.7149 | 1343.3859 | 1589.8406 | 1861.8789 | 2200.3738 | 2593.3659 | 3053.659 | 3549.2743 | 4060.3912 | 4582.6603 | 5107.2749 | 5905.9936 | 6718.4061 | 7527.7679 | 8342.0651 | 9164.1464 | 9990.7341 | 10808.0126 | 11611.2763 | 12410.8248 | 13209.4576 | 13956.3548 | 14707.3707 | 15465.8783 | 16233.8601 | 17013.4856 | 17803.4526 | 18605.4153 | 19419.4518 | 20240.8144 | 21067.2254
|  | Active: CEC 2018 IEPR - Mid Demand | CAISO |  |  |  |  | 114.6355 | 167.4178 | 222.3265 | 261.6296 | 306.145 | 356.3201 | 408.3882 | 464.4035 | 520.4005 | 543.7903 | 571.5257 | 640.6938 | 682.9825 | 2427.5517 | 4172.1209 | 5916.6902 | 7661.2594 | 9405.8287 | 11150.3979 | 12894.9671 | 14639.5364 | 16384.1056 | 18128.6748 | 19873.2441 | 21617.8133 | 23362.3825 | 25106.9518 | 26851.521 | 23051.2872 | 24077.9698 | 25098.0163 | 26108.7262 | 27110.9033
|  | Building Electrification (GWh) |  |  | Method | Last Year | Period | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | None | CAISO |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | None Through 2030 | CAISO |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2340.2557 | 4680.5113 | 7020.767 | 9361.0226 | 11701.2783 | 14041.5339 | 16381.7896 | 18722.0452 | 21062.3009 | 23402.5565 | 25742.8122 | 28083.0678 | 30423.3235 | 32763.5791 | 35103.8348 | 30356.1119 | 31807.9285 | 33131.3389 | 34321.3648 | 35377.1688
|  | CEC Pathways High Biofuels | CAISO |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.3265 | 255.0961 | 593.9817 | 1144.0362 | 1944.292 | 3022.7311 | 4371.5745 | 5977.9128 | 7800.2631 | 9786.4328 | 11931.4458 | 14211.8027 | 16600.9552 | 19049.7373 | 21506.6681 | 23937.8961 | 26326.3701 | 28652.9734 | 30902.3133 | 33058.4839 | 35103.8348 | 37019.6487 | 38790.1567 | 40404.0718 | 41855.3229 | 43142.8887
|  | CEC Pathways High Electrification | CAISO |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.3265 | 255.0961 | 593.9817 | 1144.0362 | 1944.292 | 3022.7311 | 4371.5745 | 5977.9128 | 7800.2631 | 9786.4328 | 11931.4458 | 14211.8027 | 16600.9552 | 19049.7373 | 21506.6681 | 23937.8961 | 26326.3701 | 28652.9734 | 30902.3133 | 33058.4839 | 35103.8348 | 37019.6487 | 38790.1567 | 40404.0718 | 41855.3229 | 43142.8887
|  | CEC Pathways High Hydrogen | CAISO |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.3265 | 255.0961 | 593.9817 | 1144.0362 | 1944.292 | 3022.7311 | 4371.5745 | 5977.9128 | 7800.2631 | 9786.4328 | 11931.4458 | 14211.8027 | 16600.9552 | 19049.7373 | 21506.6681 | 23937.8961 | 26326.3701 | 28652.9734 | 30902.3133 | 33058.4839 | 35103.8348 | 37019.6487 | 38790.1567 | 40404.0718 | 41855.3229 | 43142.8887
|  | Active: None Through 2030 | CAISO |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2340.2557 | 4680.5113 | 7020.767 | 9361.0226 | 11701.2783 | 14041.5339 | 16381.7896 | 18722.0452 | 21062.3009 | 23402.5565 | 25742.8122 | 28083.0678 | 30423.3235 | 32763.5791 | 35103.8348 | 30356.1119 | 31807.9285 | 33131.3389 | 34321.3648 | 35377.1688
|  | Hydrogen Production (GWh) | [5 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | No Hydrogen | CAISO |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | None Through 2030 | CAISO |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.7603 | 131.5205 | 197.2808 | 263.0411 | 328.8013 | 394.5616 | 460.3219 | 526.0821 | 591.8424 | 657.6027 | 723.3629 | 789.1232 | 854.8835 | 920.6437 | 986.404 | 824.8469 | 839.0777 | 851.4065 | 862.351 | 872.2621
|  | CEC Pathways High Biofuels | CAISO |  |  |  |  | 144.4729 | 168.4808 | 202.8477 | 257.9069 | 331.1521 | 417.7761 | 520.6881 | 636.1022 | 611.1319 | 596.2432 | 585.8425 | 580.6014 | 578.6906 | 588.4656 | 603.7173 | 622.3809 | 645.2951 | 672.8818 | 702.2583 | 735.1257 | 770.7983 | 809.1733 | 849.1123 | 880.6399 | 911.0017 | 939.1098 | 964.2083 | 986.404 | 1005.9108 | 1023.2655 | 1038.3007 | 1051.6475 | 1063.7343
|  | CEC Pathways High Electrification | CAISO |  |  |  |  | 173.0538 | 224.6467 | 275.6752 | 357.9104 | 499.4965 | 694.5083 | 967.1823 | 1285.7432 | 1562.6218 | 1843.8045 | 2159.1517 | 3052.0364 | 4476.0925 | 6237.0579 | 7827.9465 | 9366.6868 | 10977.3628 | 12839.2957 | 14951.5309 | 17283.5439 | 19672.1278 | 21992.4054 | 24143.26 | 26065.0591 | 27808.9728 | 29367.8454 | 30730.6853 | 31912.9214 | 32933.0643 | 33802.9055 | 34542.459 | 35148.8071 | 35635.8037
|  | CEC Pathways High Hydrogen | CAISO |  |  |  |  | 173.8501 | 226.4946 | 278.8401 | 362.587 | 505.8109 | 702.0906 | 977.0069 | 1297.8942 | 1577.5741 | 1862.6404 | 2185.0226 | 3094.0371 | 4558.5352 | 6420.9324 | 8274.5487 | 10471.0552 | 13667.4311 | 18913.0358 | 26211.401 | 34908.0642 | 43825.0456 | 52448.1412 | 60591.5369 | 67494.0625 | 73815.2943 | 79550.7184 | 84660.6157 | 89226.1164 | 93309.1863 | 96955.4093 | 100207.0813 | 103033.9165 | 105457.9756
|  | Active: None Through 2030 | CAISO |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.7603 | 131.5205 | 197.2808 | 263.0411 | 328.8013 | 394.5616 | 460.3219 | 526.0821 | 591.8424 | 657.6027 | 723.3629 | 789.1232 | 854.8835 | 920.6437 | 986.404 | 824.8469 | 839.0777 | 851.4065 | 862.351 | 872.2621
|  | Energy Efficiency (GWh) |  |  | Method | Last Year | Period | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | CEC 2018 IEPR - High Low AAEE | CAISO |  |  |  |  | 1650.6257 | 3314.2717 | 4882.3321 | 6415.2143 | 7948.0383 | 9787.8296 | 11464.7337 | 13137.9634 | 14780.5769 | 16433.5733 | 18038.2592 | 19569.4828 | 21112.5588 | 22797.7253 | 24482.8917 | 26168.0582 | 27853.2247 | 29538.3912 | 31223.5577 | 32908.7241 | 34593.8906 | 36279.0571 | 37964.2236 | 39649.3901 | 41334.5565 | 43019.723 | 44704.8895 | 46390.056 | 47620.056 | 48850.056 | 50080.056 | 51310.056 | 52540.056
|  | CEC 2018 IEPR - Mid Mid AAEE | CAISO |  |  |  |  | 1906.1723 | 3889.8408 | 5929.7095 | 8069.3043 | 10186.1455 | 12701.0478 | 15028.882 | 17321.7309 | 19549.9879 | 21765.5676 | 23895.8853 | 25925.4699 | 27940.056 | 29170.056 | 30400.056 | 31630.056 | 32860.056 | 34090.056 | 35320.056 | 36550.056 | 37780.056 | 39010.056 | 40240.056 | 41470.056 | 42700.056 | 43930.056 | 45160.056 | 46390.056 | 47620.056 | 48850.056 | 50080.056 | 51310.056 | 52540.056
|  | CEC 2018 IEPR - Low High AAEE | CAISO |  |  |  |  | 2092.7084 | 4220.2165 | 6431.7549 | 8827.517 | 11196.8675 | 13957.7912 | 16728.1212 | 19509.0835 | 22277.1081 | 25053.0806 | 27704.265 | 30237.6207 | 32723.511 | 33634.614 | 34545.717 | 35456.82 | 36367.923 | 37279.026 | 38190.129 | 39101.232 | 40012.335 | 40923.438 | 41834.541 | 42745.644 | 43656.747 | 44567.85 | 45478.953 | 46390.056 | 47620.056 | 48850.056 | 50080.056 | 51310.056 | 52540.056
|  | NoNewDER | CAISO |  |  |  |  | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723 | 1906.1723
|  | CEC Pathways Baseload | CAISO |  | Linear interpolation 2030-2050 |  |  | 1906.1723 | 3889.8408 | 5929.7095 | 8069.3043 | 10186.1455 | 12701.0478 | 15028.882 | 17321.7309 | 19549.9879 | 21765.5676 | 23895.8853 | 25925.4699 | 27940.056 | 29170.056 | 30400.056 | 31630.056 | 32860.056 | 34090.056 | 35320.056 | 36550.056 | 37780.056 | 39010.056 | 40240.056 | 41470.056 | 42700.056 | 43930.056 | 45160.056 | 46390.056 | 47620.056 | 48850.056 | 50080.056 | 51310.056 | 52540.056
|  | Active: CEC 2018 IEPR - Mid Mid AAEE | CAISO |  |  |  |  | 1906.1723 | 3889.8408 | 5929.7095 | 8069.3043 | 10186.1455 | 12701.0478 | 15028.882 | 17321.7309 | 19549.9879 | 21765.5676 | 23895.8853 | 25925.4699 | 27940.056 | 29170.056 | 30400.056 | 31630.056 | 32860.056 | 34090.056 | 35320.056 | 36550.056 | 37780.056 | 39010.056 | 40240.056 | 41470.056 | 42700.056 | 43930.056 | 45160.056 | 46390.056 | 47620.056 | 48850.056 | 50080.056 | 51310.056 | 52540.056
|  | Baseline Load Net of EE (GWh) | [5 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | CEC Pathways Baseload | CAISO |  |  |  |  | 235855.6909 | 236606.6 | 236331.4076 | 234893.4612 | 233117.3775 | 231005.6474 | 228575.6679 | 226421.3582 | 224117.5891 | 221905.5681 | 219896.8737 | 218140.9376 | 216672.3455 | 215975.8879 | 215573.4848 | 215413.1655 | 215417.4732 | 215574.6173 | 215775.5931 | 216088.818 | 216499.0787 | 216980.3102 | 217517.707 | 217669.9123 | 217865.2988 | 218097.6396 | 218361.7156 | 218652.0179 | 218963.5686 | 219294.0028 | 219641.5803 | 220002.5032 | 220369.1915
|  | Active | CAISO |  |  |  |  | 233775.0951 | 233428.8839 | 234036.1865 | 235066.8958 | 236451.9948 | 237063.4335 | 237491.1233 | 237935.4165 | 238009.2119 | 238078.337 | 237999.2127 | 237904.9783 | 237767.2871 | 237899.2653 | 238031.2435 | 238163.2216 | 238295.1998 | 238427.1779 | 238559.1561 | 238691.1343 | 238823.1124 | 238955.0906 | 239087.0687 | 239219.0469 | 239351.0251 | 239483.0032 | 239614.9814 | 239746.9595 | 240058.5102 | 240388.9444 | 240736.5219 | 241097.4448 | 241464.1331
|  | Behind-the-Meter PV (GWh) |  |  | Method | Last Year | Period | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Commited BTM PV
|  | CEC 2018 IEPR - Low PV + High-Low AAPV | CAISO |  | Linear | 2030 | 5 | 12365.7606 | 14029.4601 | 15305.8911 | 16442.8332 | 17429.0108 | 18296.5161 | 19058.6231 | 19763.8046 | 20493.2026 | 21254.2706 | 22059.393 | 22925.3279 | 23873.0359 | 24694.8822 | 25516.7284 | 26338.5747 | 27160.421 | 27982.2672 | 28804.1135 | 29625.9598 | 30447.806 | 31269.6523 | 32091.4986 | 32913.3448 | 33735.1911 | 34557.0374 | 35378.8836 | 36200.7299 | 37022.5762 | 37844.4224 | 38666.2687 | 39488.1149 | 40309.9612
|  | CEC 2018 IEPR - Mid PV + Mid-Mid AAPV | CAISO |  | Linear | 2030 | 5 | 12439.0189 | 14597.1512 | 16796.7096 | 18962.3301 | 20896.9391 | 22540.3594 | 24032.335 | 25446.0933 | 26806.2669 | 28159.8436 | 29536.7013 | 30958.1587 | 32466.0117 | 33869.9954 | 35273.979 | 36677.9627 | 38081.9464 | 39485.9301 | 40889.9137 | 42293.8974 | 43697.8811 | 45101.8648 | 46505.8484 | 47909.8321 | 49313.8158 | 50717.7995 | 52121.7831 | 53525.7668 | 54929.7505 | 56333.7341 | 57737.7178 | 59141.7015 | 60545.6852
|  | CEC 2018 IEPR - High PV + Low-High AAPV | CAISO |  | Linear | 2030 | 5 | 12512.2771 | 15174.1316 | 18314.209 | 21525.9989 | 24423.6134 | 26855.343 | 29091.6485 | 31231.9227 | 33244.8608 | 35217.2822 | 37196.7943 | 39209.4615 | 41318.2404 | 43335.5039 | 45352.7675 | 47370.031 | 49387.2945 | 51404.5581 | 53421.8216 | 55439.0851 | 57456.3487 | 59473.6122 | 61490.8757 | 63508.1393 | 65525.4028 | 67542.6663 | 69559.9299 | 71577.1934 | 73594.4569 | 75611.7205 | 77628.984 | 79646.2475 | 81663.5111
|  | NoNewDER | CAISO |  |  |  |  | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189 | 12439.0189
AAPV
|  | CEC 2018 IEPR - Low PV + High-Low AAPV | CAISO |  | Linear | 2030 | 5 | 0 | 0 | 148.1108 | 438.1232 | 768.2761 | 1114.8391 | 1457.6432 | 1799.1204 | 2127.4583 | 2440.6444 | 2745.3825 | 3047.0484 | 3345.1955 | 4487.4584 | 4874.1346 | 5260.8108 | 5647.487 | 6034.1632 | 6420.8394 | 6807.5156 | 7194.1918 | 7580.868 | 7967.5442 | 8354.2204 | 8740.8966 | 9127.5729 | 9514.2491 | 9900.9253 | 10287.6015 | 10674.2777 | 11060.9539 | 11447.6301 | 11834.3063
|  | CEC 2018 IEPR - Mid PV + Mid-Mid AAPV | CAISO |  | Linear | 2030 | 5 | 0 | 0 | 133.8518 | 380.1112 | 639.7103 | 910.1587 | 1177.0328 | 1440.916 | 1697.1133 | 1944.0738 | 2184.967 | 2422.6919 | 2656.7584 | 3420.2562 | 3711.8261 | 4003.396 | 4294.9658 | 4586.5357 | 4878.1056 | 5169.6755 | 5461.2453 | 5752.8152 | 6044.3851 | 6335.955 | 6627.5248 | 6919.0947 | 7210.6646 | 7502.2345 | 7793.8043 | 8085.3742 | 8376.9441 | 8668.514 | 8960.0838
|  | CEC 2018 IEPR - High PV + Low-High AAPV | CAISO |  | Linear | 2030 | 5 | 0 | 0 | 119.9287 | 322.957 | 512.6069 | 707.7896 | 899.7378 | 1087.143 | 1272.3575 | 1454.3373 | 1632.7433 | 1807.9962 | 1979.6149 | 2370.3631 | 2568.528 | 2766.6928 | 2964.8576 | 3163.0225 | 3361.1873 | 3559.3521 | 3757.517 | 3955.6818 | 4153.8466 | 4352.0115 | 4550.1763 | 4748.3411 | 4946.506 | 5144.6708 | 5342.8356 | 5541.0005 | 5739.1653 | 5937.3301 | 6135.495
|  | NoNewDER | CAISO |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Active: CEC 2018 IEPR - Mid PV + Mid-Mid AAPV | [5 empty] | 12439.0189 | 14597.1512 | 16930.5613 | 19342.4413 | 21536.6494 | 23450.5181 | 25209.3678 | 26887.0093 | 28503.3802 | 30103.9174 | 31721.6683 | 33380.8506 | 35122.7701 | 37290.2516 | 38985.8051 | 40681.3587 | 42376.9122 | 44072.4658 | 45768.0193 | 47463.5729 | 49159.1264 | 50854.68 | 52550.2335 | 54245.7871 | 55941.3406 | 57636.8942 | 59332.4477 | 61028.0013 | 62723.5548 | 64419.1084 | 66114.6619 | 67810.2155 | 69505.769
|  | Behind-the-Meter CHP (GWh) | [5 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | CEC 2018 IEPR - Mid Demand | CAISO |  |  |  |  | 13594.4223 | 13621.7175 | 13637.1519 | 13647.5713 | 13655.2122 | 13657.0378 | 13654.9139 | 13648.3766 | 13637.8523 | 13627.2586 | 13616.5964 | 13605.8667 | 13595.0705 | 12235.5635 | 10876.0564 | 9516.5494 | 8157.0423 | 6797.5353 | 5438.0282 | 4078.5212 | 2719.0141 | 1359.5071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | NoNewDER | CAISO |  |  |  |  | 13594.4223 | 13594.4223 | 13594.4223 | 13594.4223 | 13594.4223 | 13594.4223 | 13594.4223 | 13594.4223 | 13594.4223 | 13594.4223 | 13594.4223 | 13594.4223 | 13594.4223 | 12235.5635 | 10876.0564 | 9516.5494 | 8157.0423 | 6797.5353 | 5438.0282 | 4078.5212 | 2719.0141 | 1359.5071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Active: CEC 2018 IEPR - Mid Demand | [5 empty] | 13594.4223 | 13621.7175 | 13637.1519 | 13647.5713 | 13655.2122 | 13657.0378 | 13654.9139 | 13648.3766 | 13637.8523 | 13627.2586 | 13616.5964 | 13605.8667 | 13595.0705 | 12235.5635 | 10876.0564 | 9516.5494 | 8157.0423 | 6797.5353 | 5438.0282 | 4078.5212 | 2719.0141 | 1359.5071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Non-PV Non-CHP Self Generation (includes storage losses) (GWh) | [5 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | CEC 2018 IEPR - Mid Demand | CAISO |  | Linear | 2030 | 5 | 764.0216 | 759.3948 | 750.9625 | 744.8846 | 737.4564 | 730.0481 | 722.7263 | 715.5174 | 708.4327 | 701.4812 | 694.4932 | 687.5804 | 680.7513 | 673.7981 | 666.8448 | 659.8916 | 652.9384 | 645.9852 | 639.0319 | 632.0787 | 625.1255 | 618.1723 | 611.219 | 604.2658 | 597.3126 | 590.3594 | 583.4062 | 576.4529 | 569.4997 | 562.5465 | 555.5933 | 548.64 | 541.6868
|  | NoNewDER | CAISO |  |  |  |  | 764.0216 | 759.3948 | 750.9625 | 744.8846 | 737.4564 | 730.0481 | 722.7263 | 715.5174 | 708.4327 | 701.4812 | 694.4932 | 687.5804 | 680.7513 | 673.7981 | 666.8448 | 659.8916 | 652.9384 | 645.9852 | 639.0319 | 632.0787 | 625.1255 | 618.1723 | 611.219 | 604.2658 | 597.3126 | 590.3594 | 583.4062 | 576.4529 | 569.4997 | 562.5465 | 555.5933 | 548.64 | 541.6868
|  | None | CAISO |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Active: CEC 2018 IEPR - Mid Demand | [5 empty] | 764.0216 | 759.3948 | 750.9625 | 744.8846 | 737.4564 | 730.0481 | 722.7263 | 715.5174 | 708.4327 | 701.4812 | 694.4932 | 687.5804 | 680.7513 | 673.7981 | 666.8448 | 659.8916 | 652.9384 | 645.9852 | 639.0319 | 632.0787 | 625.1255 | 618.1723 | 611.219 | 604.2658 | 597.3126 | 590.3594 | 583.4062 | 576.4529 | 569.4997 | 562.5465 | 555.5933 | 548.64 | 541.6868
|  | TOU Effects (GWh) | [5 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | None | CAISO |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CEC 2018 IEPR | CAISO |  | Flat | 2030 | 5 | 0 | -0.01645 | 0.027968 | 20.5996 | 26.7567 | 27.8888 | 29.1022 | 29.9971 | 31.0518 | 32.1028 | 33.2905 | 34.0821 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186
|  | Active: CEC 2018 IEPR | [5 empty] | 0 | -0.01645 | 0.027968 | 20.5996 | 26.7567 | 27.8888 | 29.1022 | 29.9971 | 31.0518 | 32.1028 | 33.2905 | 34.0821 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186
|  | CA Retail Sales (GWh) | [5 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | Baseline Consumption | CAISO |  |  |  |  | 235681.2673 | 237318.7247 | 239965.896 | 243136.2001 | 246638.1404 | 249764.4813 | 252520.0054 | 255257.1474 | 257559.1998 | 259843.9046 | 261895.0979 | 263830.4482 | 265707.3431 | 267069.3213 | 268431.2995 | 269793.2776 | 271155.2558 | 272517.2339 | 273879.2121 | 275241.1902 | 276603.1684 | 277965.1466 | 279327.1247 | 280689.1029 | 282051.081 | 283413.0592 | 284775.0374 | 286137.0155 | 287678.5662 | 289239.0004 | 290816.5779 | 292407.5008 | 294004.1891
|  | + Electric Vehicles | CAISO |  |  |  |  | 2741.1311 | 3659.4928 | 4577.9906 | 5641.2911 | 6817.2503 | 8044.5787 | 9078.5063 | 10016.361 | 10726.5989 | 11356.6772 | 12068.3541 | 12796.7098 | 13566.6575 | 14694.5253 | 15822.3932 | 16950.2611 | 18078.129 | 19205.9969 | 20333.8648 | 21461.7327 | 22589.6006 | 23717.4685 | 24845.3364 | 25973.2042 | 27101.0721 | 28228.94 | 29356.8079 | 30484.6758 | 25562.4074 | 26055.8842 | 26483.8328 | 26849.5295 | 27152.5871
|  | + Other Transport Electrification | CAISO |  |  |  |  | 114.6355 | 167.4178 | 222.3265 | 261.6296 | 306.145 | 356.3201 | 408.3882 | 464.4035 | 520.4005 | 543.7903 | 571.5257 | 640.6938 | 682.9825 | 2427.5517 | 4172.1209 | 5916.6902 | 7661.2594 | 9405.8287 | 11150.3979 | 12894.9671 | 14639.5364 | 16384.1056 | 18128.6748 | 19873.2441 | 21617.8133 | 23362.3825 | 25106.9518 | 26851.521 | 23051.2872 | 24077.9698 | 25098.0163 | 26108.7262 | 27110.9033
|  | + Building Electrification | CAISO |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2340.2557 | 4680.5113 | 7020.767 | 9361.0226 | 11701.2783 | 14041.5339 | 16381.7896 | 18722.0452 | 21062.3009 | 23402.5565 | 25742.8122 | 28083.0678 | 30423.3235 | 32763.5791 | 35103.8348 | 30356.1119 | 31807.9285 | 33131.3389 | 34321.3648 | 35377.1688
|  | + Hydrogen Production | CAISO |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.7603 | 131.5205 | 197.2808 | 263.0411 | 328.8013 | 394.5616 | 460.3219 | 526.0821 | 591.8424 | 657.6027 | 723.3629 | 789.1232 | 854.8835 | 920.6437 | 986.404 | 824.8469 | 839.0777 | 851.4065 | 862.351 | 872.2621
|  | - Energy Efficiency | CAISO |  |  |  |  | -1906.1723 | -3889.8408 | -5929.7095 | -8069.3043 | -10186.1455 | -12701.0478 | -15028.882 | -17321.7309 | -19549.9879 | -21765.5676 | -23895.8853 | -25925.4699 | -27940.056 | -29170.056 | -30400.056 | -31630.056 | -32860.056 | -34090.056 | -35320.056 | -36550.056 | -37780.056 | -39010.056 | -40240.056 | -41470.056 | -42700.056 | -43930.056 | -45160.056 | -46390.056 | -47620.056 | -48850.056 | -50080.056 | -51310.056 | -52540.056
|  | - Behind-the-Meter PV | CAISO |  |  |  |  | -12439.0189 | -14597.1512 | -16930.5613 | -19342.4413 | -21536.6494 | -23450.5181 | -25209.3678 | -26887.0093 | -28503.3802 | -30103.9174 | -31721.6683 | -33380.8506 | -35122.7701 | -37290.2516 | -38985.8051 | -40681.3587 | -42376.9122 | -44072.4658 | -45768.0193 | -47463.5729 | -49159.1264 | -50854.68 | -52550.2335 | -54245.7871 | -55941.3406 | -57636.8942 | -59332.4477 | -61028.0013 | -62723.5548 | -64419.1084 | -66114.6619 | -67810.2155 | -69505.769
|  | - Behind-the-Meter CHP | CAISO |  |  |  |  | -13594.4223 | -13621.7175 | -13637.1519 | -13647.5713 | -13655.2122 | -13657.0378 | -13654.9139 | -13648.3766 | -13637.8523 | -13627.2586 | -13616.5964 | -13605.8667 | -13595.0705 | -12235.5635 | -10876.0564 | -9516.5494 | -8157.0423 | -6797.5353 | -5438.0282 | -4078.5212 | -2719.0141 | -1359.5071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | - Non-PV Non-CHP Self Generation (includes storage losses) | CAISO |  |  |  |  | -764.0216 | -759.3948 | -750.9625 | -744.8846 | -737.4564 | -730.0481 | -722.7263 | -715.5174 | -708.4327 | -701.4812 | -694.4932 | -687.5804 | -680.7513 | -673.7981 | -666.8448 | -659.8916 | -652.9384 | -645.9852 | -639.0319 | -632.0787 | -625.1255 | -618.1723 | -611.219 | -604.2658 | -597.3126 | -590.3594 | -583.4062 | -576.4529 | -569.4997 | -562.5465 | -555.5933 | -548.64 | -541.6868
|  | + TOU Effects | CAISO |  |  |  |  | 0 | -0.01645 | 0.027968 | 20.5996 | 26.7567 | 27.8888 | 29.1022 | 29.9971 | 31.0518 | 32.1028 | 33.2905 | 34.0821 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186 | 35.1186
|  | = Total Managed Retail Sales | CAISO |  |  |  |  | 209833.3989 | 208277.5146 | 207517.8558 | 207255.5188 | 207672.8288 | 207654.6171 | 207420.112 | 207195.2748 | 206437.5979 | 205578.2501 | 204639.625 | 203702.1663 | 202653.4538 | 207262.8638 | 212344.2018 | 217425.5397 | 222506.8776 | 227588.2155 | 232669.5535 | 237750.8914 | 242832.2293 | 247913.5673 | 252994.9052 | 256716.7361 | 260438.567 | 264160.3978 | 267882.2287 | 271604.0596 | 256595.2277 | 258223.2683 | 259665.9799 | 260915.6794 | 261964.7172
|  | Pumping Loads (included in retail sales; GWh) |  |  | Method | Last Year | Period | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | CEC 2018 IEPR | CAISO |  | Flat | 2030 |  | 7902 | 7908 | 7918 | 7933 | 7950 | 7970 | 7985 | 7998 | 8008 | 8018 | 8028 | 8037 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047
|  | Active | [5 empty] | 7902 | 7908 | 7918 | 7933 | 7950 | 7970 | 7985 | 7998 | 8008 | 8018 | 8028 | 8037 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047 | 8047
| CA Net Energy for Load (grossed up for T&D Losses) |  | Values represent demand at the utility-scale generator busbar
|  | Loads by contributors with known shape - grossed up for T&D losses (GWh) | [5 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | Load without BTM PV, EV, other TE, Hydrogen, EE, BE and TOU | CAISO |  |  |  |  | 238597.2655 | 240518.575 | 243424.0061 | 246879.4455 | 250702.476 | 254132.9404 | 257169.8505 | 260195.8353 | 262756.9159 | 265264.0741 | 267524.2928 | 269704.2851 | 271792.2637 | 276614.3936 | 281436.5234 | 286258.6533 | 291080.7832 | 295902.9131 | 300725.0429 | 305547.1728 | 310369.3027 | 315191.4326 | 320013.5624 | 323370.0745 | 326726.5866 | 330083.0987 | 333439.6108 | 336796.1229 | 334368.6434 | 337165.1829 | 339973.0497 | 342785.2383 | 345594.4433
|  | + Electric Vehicles | CAISO |  |  |  |  | 2955.0788 | 3945.1195 | 4935.3068 | 6081.5988 | 7349.3427 | 8672.4652 | 9787.0918 | 10798.1468 | 11563.8195 | 12243.0759 | 13010.2998 | 13795.5043 | 14625.5471 | 15841.446 | 17057.345 | 18273.244 | 19489.143 | 20705.0419 | 21920.9409 | 23136.8399 | 24352.7389 | 25568.6378 | 26784.5368 | 28000.4358 | 29216.3348 | 30432.2338 | 31648.1327 | 32864.0317 | 27557.5759 | 28089.569 | 28550.9193 | 28945.159 | 29271.8706
|  | + Other Transport Electrification | CAISO |  |  |  |  | 123.5829 | 180.4849 | 239.6793 | 282.05 | 330.0399 | 384.1312 | 440.2632 | 500.6506 | 561.0182 | 586.2336 | 616.1338 | 690.7005 | 736.2899 | 2617.0243 | 4497.7587 | 6378.4931 | 8259.2275 | 10139.9619 | 12020.6963 | 13901.4307 | 15782.1651 | 17662.8995 | 19543.6339 | 21424.3683 | 23305.1027 | 25185.8372 | 27066.5716 | 28947.306 | 24850.4605 | 25957.2766 | 27056.9386 | 28146.5354 | 29226.9333
|  | + Building Electrification | CAISO |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2522.9147 | 5045.8294 | 7568.744 | 10091.6587 | 12614.5734 | 15137.4881 | 17660.4027 | 20183.3174 | 22706.2321 | 25229.1468 | 27752.0614 | 30274.9761 | 32797.8908 | 35320.8055 | 37843.7201 | 32725.4333 | 34290.5655 | 35717.2692 | 37000.1776 | 38138.388
|  | + Hydrogen Production | CAISO |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8929 | 141.7858 | 212.6787 | 283.5717 | 354.4646 | 425.3575 | 496.2504 | 567.1433 | 638.0362 | 708.9291 | 779.8221 | 850.715 | 921.6079 | 992.5008 | 1063.3937 | 889.2269 | 904.5684 | 917.8596 | 929.6582 | 940.3429
|  | - Energy Efficiency | CAISO |  |  |  |  | -2054.9507 | -4193.4463 | -6392.5286 | -8699.1206 | -10981.1832 | -13692.3758 | -16201.8996 | -18673.7073 | -21075.8817 | -23464.3894 | -25760.9802 | -27948.9758 | -30120.8021 | -31446.8046 | -32772.8072 | -34098.8098 | -35424.8124 | -36750.815 | -38076.8176 | -39402.8202 | -40728.8228 | -42054.8253 | -43380.8279 | -44706.8305 | -46032.8331 | -47358.8357 | -48684.8383 | -50010.8409 | -51336.8435 | -52662.846 | -53988.8486 | -55314.8512 | -56640.8538
|  | - Behind-the-Meter PV | CAISO |  |  |  |  | -13409.8953 | -15736.4717 | -18252.0066 | -20852.136 | -23217.6039 | -25280.8518 | -27176.9813 | -28985.5642 | -30728.0943 | -32453.5547 | -34197.5726 | -35986.2554 | -37864.1333 | -40200.7887 | -42028.6817 | -43856.5747 | -45684.4677 | -47512.3607 | -49340.2537 | -51168.1467 | -52996.0397 | -54823.9327 | -56651.8257 | -58479.7187 | -60307.6117 | -62135.5047 | -63963.3977 | -65791.2907 | -67619.1837 | -69447.0767 | -71274.9697 | -73102.8627 | -74930.7557
|  | - TOU Effects | CAISO |  |  |  |  | 0 | -0.017734 | 0.030151 | 22.2075 | 28.8451 | 30.0656 | 31.3736 | 32.3384 | 33.4755 | 34.6084 | 35.8888 | 36.7422 | 37.8597 | 37.8597 | 37.8597 | 37.8597 | 37.8597 | 37.8597 | 37.8597 | 37.8597 | 37.8597 | 37.8597 | 37.8597 | 37.8597 | 37.8597 | 37.8597 | 37.8597 | 37.8597 | 37.8597 | 37.8597 | 37.8597 | 37.8597 | 37.8597
|  | = Total Managed Net Energy for Load (GWh) | [5 empty] | 226211.0812 | 224714.2437 | 223954.4871 | 223714.0452 | 224211.9166 | 224246.3748 | 224049.6983 | 223867.6997 | 223111.2531 | 222210.0479 | 221228.0624 | 220292.0009 | 219207.0249 | 226056.9378 | 233415.6131 | 240774.2883 | 248132.9636 | 255491.6389 | 262850.3141 | 270208.9894 | 277567.6646 | 284926.3399 | 292285.0151 | 298178.0726 | 304071.1301 | 309964.1876 | 315857.2451 | 321750.3025 | 301473.1725 | 304335.0993 | 306990.0778 | 309426.9143 | 311638.2283
BTM PV and BTM Storage Capacity from CEC 2018 IEPR
|  | BTM PV Capacity (MW) | [5 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | Commited BTM PV |  | Resolve Resource Name
|  | CEC 2018 IEPR - Low PV + High-Low AAPV | CAISO | Customer_PV |  |  |  | 7196.2183 | 7964.1479 | 8639.1935 | 9260.8394 | 9783.0236 | 10278.6328 | 10697.572 | 11129.6991 | 11577.7558 | 12046.8832 | 12545.073 | 13082.2103 | 13670.7706 | 14141.3966 | 14612.0226 | 15082.6487 | 15553.2747 | 16023.9007 | 16494.5267 | 16965.1527 | 17435.7787 | 17906.4048 | 18377.0308 | 18847.6568 | 19318.2828 | 19788.9088 | 20259.5349 | 20730.1609 | 21200.7869 | 21671.4129 | 22142.0389 | 22612.6649 | 23083.291
|  | CEC 2018 IEPR - Mid PV + Mid-Mid AAPV | CAISO |  |  |  |  | 7269.2906 | 8467.6969 | 9693.7723 | 10873.4047 | 11873.2545 | 12747.8146 | 13588.0641 | 14386.8028 | 15174.3424 | 15971.1763 | 16789.4547 | 17640.1013 | 18555.27 | 19357.6875 | 20160.105 | 20962.5225 | 21764.94 | 22567.3575 | 23369.775 | 24172.1925 | 24974.61 | 25777.0275 | 26579.445 | 27381.8625 | 28184.28 | 28986.6975 | 29789.1151 | 30591.5326 | 31393.9501 | 32196.3676 | 32998.7851 | 33801.2026 | 34603.6201
|  | CEC 2018 IEPR - High PV + Low-High AAPV | CAISO |  |  |  |  | 7342.3629 | 8980.5099 | 10766.9355 | 12514.0219 | 13998.1012 | 15258.6718 | 16528.97 | 17705.1026 | 18845.2047 | 19985.1991 | 21141.5729 | 22326.3385 | 23591.6368 | 24743.4416 | 25895.2464 | 27047.0512 | 28198.8561 | 29350.6609 | 30502.4657 | 31654.2705 | 32806.0754 | 33957.8802 | 35109.685 | 36261.4898 | 37413.2946 | 38565.0995 | 39716.9043 | 40868.7091 | 42020.5139 | 43172.3188 | 44324.1236 | 45475.9284 | 46627.7332
|  | NoNewDER | CAISO |  |  |  |  | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906 | 7269.2906
AAPV (Additional Achievable BTM PV)
|  | CEC 2018 IEPR - Low PV + High-Low AAPV | CAISO |  |  |  |  | 0 | 0 | 147.5191 | 308.4084 | 499.0984 | 681.8071 | 869.3814 | 1053.1291 | 1228.7847 | 1397.9684 | 1565.8773 | 1733.2685 | 1899.0156 | 2547.4605 | 2766.9706 | 2986.4807 | 3205.9908 | 3425.5009 | 3645.011 | 3864.521 | 4084.0311 | 4303.5412 | 4523.0513 | 4742.5614 | 4962.0714 | 5181.5815 | 5401.0916 | 5620.6017 | 5840.1118 | 6059.6218 | 6279.1319 | 6498.642 | 6718.1521
|  | CEC 2018 IEPR - Mid PV + Mid-Mid AAPV | CAISO |  |  |  |  | 0 | 0 | 133.5408 | 263.4159 | 411.0118 | 555.2264 | 700.1668 | 842.8689 | 981.171 | 1115.3684 | 1248.3279 | 1380.3864 | 1510.7623 | 1944.9243 | 2110.7252 | 2276.526 | 2442.3268 | 2608.1277 | 2773.9285 | 2939.7294 | 3105.5302 | 3271.331 | 3437.1319 | 3602.9327 | 3768.7335 | 3934.5344 | 4100.3352 | 4266.1361 | 4431.9369 | 4597.7377 | 4763.5386 | 4929.3394 | 5095.1402
|  | CEC 2018 IEPR - High PV + Low-High AAPV | CAISO |  |  |  |  | 0 | 0 | 119.5624 | 218.4233 | 322.9252 | 428.6456 | 530.9521 | 632.6086 | 733.5573 | 832.7684 | 930.7785 | 1027.5043 | 1122.5089 | 1344.0764 | 1456.4426 | 1568.8088 | 1681.175 | 1793.5412 | 1905.9074 | 2018.2736 | 2130.6398 | 2243.006 | 2355.3722 | 2467.7384 | 2580.1046 | 2692.4708 | 2804.837 | 2917.2032 | 3029.5694 | 3141.9356 | 3254.3018 | 3366.668 | 3479.0341
|  | NoNewDER | CAISO |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Active: CEC 2018 IEPR - Mid PV + Mid-Mid AAPV | [5 empty] | 7269.2906 | 8467.6969 | 9827.3131 | 11136.8205 | 12284.2663 | 13303.041 | 14288.2308 | 15229.6717 | 16155.5134 | 17086.5447 | 18037.7827 | 19020.4877 | 20066.0322 | 21302.6118 | 22270.8302 | 23239.0485 | 24207.2668 | 25175.4852 | 26143.7035 | 27111.9219 | 28080.1402 | 29048.3586 | 30016.5769 | 30984.7952 | 31953.0136 | 32921.2319 | 33889.4503 | 34857.6686 | 35825.887 | 36794.1053 | 37762.3236 | 38730.542 | 39698.7603
|  | BTM Storage (MW) |  |  | Method | Last Year | Period | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  |  |  | Resolve Resource Name |  |  |  | -0.88346 | -0.88527 | -0.88814 | -0.88339 | -0.87878 | -0.87426 | -0.86982 | -0.86543 | -0.86109 | -0.85679 | -0.85253 | -0.8483 | -0.84411 | -0.84155 | -0.83931 | -0.83733 | -0.83557 | -0.834 | -0.83258 | -0.8313 | -0.83013 | -0.82907 | -0.82809 | -0.82719 | -0.82637 | -0.8256 | -0.82489 | -0.82422 | -0.8236 | -0.82302 | -0.82248 | -0.82197 | -0.82149
|  | CEC 2018 IEPR - BTM Storage installed capacity |  | CAISO_BTM_Li_Battery | Flat | 2030 | 5 | 92.14 | 525.9142 | 721.9885 | 839.4472 | 942.3579 | 1054.1886 | 1157.0992 | 1238.7599 | 1320.4206 | 1402.0813 | 1483.742 | 1565.4027 | 1647.0634 | 1647.0634 | 1647.0634 | 1647.0634 | 1647.0634 | 1647.0634 | 1647.0634 | 1647.0634 | 1647.0634 | 1647.0634 | 1647.0634 | 1647.0634 | 1647.0634 | 1647.0634 | 1647.0634 | 1647.0634 | 1647.0634 | 1647.0634 | 1647.0634 | 1647.0634 | 1647.0634
|  | CEC 2018 IEPR - BTM Storage peak impact |  |  | Flat | 2030 | 5 | -81.4023 | -465.5747 | -641.2288 | -741.5587 | -828.1247 | -921.6391 | -1006.4662 | -1072.0585 | -1136.9968 | -1201.285 | -1264.9281 | -1327.9313 | -1390.3004 | -1386.0821 | -1382.3902 | -1379.1321 | -1376.2355 | -1373.6435 | -1371.3103 | -1369.1991 | -1367.2796 | -1365.5269 | -1363.9201 | -1362.4417 | -1361.0769 | -1359.8131 | -1358.6395 | -1357.5468 | -1356.5269 | -1355.5727 | -1354.6781 | -1353.8377 | -1353.0467
|  | Active: CEC 2018 IEPR - BTM Storage peak impact | [5 empty] | -81.4023 | -465.5747 | -641.2288 | -741.5587 | -828.1247 | -921.6391 | -1006.4662 | -1072.0585 | -1136.9968 | -1201.285 | -1264.9281 | -1327.9313 | -1390.3004 | -1386.0821 | -1382.3902 | -1379.1321 | -1376.2355 | -1373.6435 | -1371.3103 | -1369.1991 | -1367.2796 | -1365.5269 | -1363.9201 | -1362.4417 | -1361.0769 | -1359.8131 | -1358.6395 | -1357.5468 | -1356.5269 | -1355.5727 | -1354.6781 | -1353.8377 | -1353.0467
| CAISO Peak Load Buildup |  | Values represent demand at the utility-scale generator busbar
|  | Mid Peak Load Values Calculated Using CEC 2018 IEPR Hourly Load Shapes (MW) | [5 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | CAISO Consumption Peak: Mid Load Baseline - For information only | [5 empty] | 2018: 49256.7365; 2019: 49577.8112; 2020: 50105.6167; 2021: 50762.861; 2022: 51470.3217; 2023: 52144.4888; 2024: 52730.9075; 2025: 53310.6231; 2026: 53814.3223; 2027: 54336.1546; 2028: 54736.321; 2029: 55142.2521; 2030: 55563.3022
|  | + Other Electrification: Mid (included in hourly consumption load) | [5 empty] | 2018: Peak load impacts of Other Electrification and non-PV Self Generation are embedded in the CEC IEPR's hourly consumption load shapes and are thereby included in the CAISO consumption peak values above.
- Non-PV Self Generation (BTM CHP, BTM Storage, etc.; included in hourly consumption load) | bar: 2018 to 2030
|  | + Load from SVP Data Centers and Vernon | [5 empty] | 2018: Peak load impacts for individual load modifiers are not calculated because interactive effects between hourly shapes and the timing of peak demand result in load modifier peak impacts that are interdependent and non-linear. The peak load impacts of load modifiers on these rows are included by adding or subtracting an hourly shape for each component to the CAISO consumption hourly shape. The result is shown in the CAISO Managed Net Peak row below.
+ Time-Of-Use: Mid (can increase or decrease hourly demand) | bar: 2018 to 2030
+ Climate Change Impacts: Mid (can increase or decrease hourly demand) | bar: 2018 to 2030
+ Light Duty Electric Vehicles: Mid | bar: 2018 to 2030
- Additional Acheivable Energy Efficiency: Mid-Mid | bar: 2018 to 2030
- Committed BTM PV: Mid | bar: 2018 to 2030
- Additional Achievable BTM PV: Mid-Mid | bar: 2018 to 2030
|  | CAISO Managed Net Mid Peak through 2030, excluding LMDR | [5 empty] | 2018: 45724.947; 2019: 45406.1627; 2020: 45277.0588; 2021: 44984.0724; 2022: 45103.1971; 2023: 45245.4365; 2024: 45331.3207; 2025: 45506.8166; 2026: 45610.3333; 2027: 45774.2833; 2028: 45819.4069; 2029: 45882.6334; 2030: 45970.186
|  | Load-Modifying Demand Response: Mid Mid AAEE | [5 empty] | 2018: -136.7928; 2019: -161.2174; 2020: -162.3817; 2021: -158.4089; 2022: -165.5454; 2023: -172.3429; 2024: -180.5019; 2025: -185.9058; 2026: -192.4544; 2027: -199.6817; 2028: -199.449; 2029: -199.8552; 2030: -199.7733
|  | CAISO Managed Net Mid Peak through 2030 | [5 empty] | 2018: 45588.1542; 2019: 45244.9453; 2020: 45114.6771; 2021: 44825.6635; 2022: 44937.6517; 2023: 45073.0937; 2024: 45150.8188; 2025: 45320.9108; 2026: 45417.8789; 2027: 45574.6015; 2028: 45619.958; 2029: 45682.7782; 2030: 45770.4127
|  | Mid Peak Load Extrapolation (MW, incremental to 2030) | [5 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | Baseline Consumption | [18 empty] | 318.7143 | 637.4286 | 956.1429 | 1274.8571 | 1593.5714 | 1912.2857 | 2231 | 2549.7143 | 2868.4286 | 3187.1429 | 3505.8571 | 3824.5714 | 4143.2857 | 4462 | 4780.7143 | 5141.45 | 5506.6047 | 5875.771 | 6248.0603 | 6621.6987
|  | Electric Vehicles (Light Duty) | [18 empty] | 284.3354 | 568.6707 | 853.0061 | 1137.3414 | 1421.6768 | 1706.0121 | 1990.3475 | 2274.6828 | 2559.0182 | 2843.3535 | 3127.6889 | 3412.0242 | 3696.3596 | 3980.6949 | 4265.0303 | 3024.127 | 3148.5325 | 3256.4183 | 3348.6104 | 3425.0112
|  | Energy Efficiency | [18 empty] | -252.9794 | -505.9587 | -758.9381 | -1011.9174 | -1264.8968 | -1517.8761 | -1770.8555 | -2023.8348 | -2276.8142 | -2529.7935 | -2782.7729 | -3035.7522 | -3288.7316 | -3541.7109 | -3794.6903 | -4047.6696 | -4300.649 | -4553.6283 | -4806.6077 | -5059.587
|  | BTM PV | [18 empty] | -1.233 | -2.1975 | -3.162 | -4.1265 | -5.091 | -6.0555 | -7.02 | -7.9845 | -8.949 | -9.9135 | -10.878 | -11.8425 | -12.807 | -13.7715 | -14.736 | -15.7005 | -16.665 | -17.6295 | -18.594 | -19.5585
|  | Load-Modifying Demand Response (Flat post 2030) | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Post-2030 Net Mid Peak, incremental to 2030 Net Mid Peak | [18 empty] | 348.8373 | 697.9431 | 1047.0489 | 1396.1547 | 1745.2605 | 2094.3663 | 2443.4721 | 2792.5778 | 3141.6836 | 3490.7894 | 3839.8952 | 4189.001 | 4538.1068 | 4887.2126 | 5236.3184 | 4102.207 | 4337.8232 | 4560.9315 | 4771.469 | 4967.5644
|  | CAISO Managed Net Mid Peak, all years (MW) | [5 empty] | 45588.1542 | 45244.9453 | 45114.6771 | 44825.6635 | 44937.6517 | 45073.0937 | 45150.8188 | 45320.9108 | 45417.8789 | 45574.6015 | 45619.958 | 45682.7782 | 45770.4127 | 46119.25 | 46468.3558 | 46817.4616 | 47166.5674 | 47515.6731 | 47864.7789 | 48213.8847 | 48562.9905 | 48912.0963 | 49261.2021 | 49610.3079 | 49959.4137 | 50308.5194 | 50657.6252 | 51006.731 | 49872.6197 | 50108.2359 | 50331.3442 | 50541.8817 | 50737.9771
|  | Peak Load Difference From Mid (MW) | [5 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Baseline Consumption
|  | CEC 2018 IEPR - Mid Demand | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CEC 2018 IEPR - High Demand | [5 empty] | 0 | 668.2345 | 976.6246 | 1224.096 | 1345.5734 | 1570.8062 | 1784.43 | 1916.4589 | 2113.6447 | 2283.5948 | 2507.3941 | 2652.6812 | 2843.008 | 3209.1343 | 3582.4738 | 3963.1024 | 4351.097 | 4746.535 | 5149.495 | 5560.0561 | 5978.2985 | 6404.3029 | 6838.1512 | 7279.9259 | 7729.7107 | 8187.5897 | 8653.6483 | 9127.9727 | 9568.6284 | 10013.306 | 10462.5015 | 10917.1937 | 11379.247
|  | CEC Pathways Baseload | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -193.8609 | -318.9106 | -387.3106 | -417.1866 | -411.2976 | -395.1515 | -352.7383 | -287.6178 | -205.8896 | -111.0183 | -106.285 | -91.4469 | -67.9612 | -37.0492 | 0 | 0 | 0 | 0 | 0 | 0
|  | Active: CEC 2018 IEPR - Mid Demand | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electric Vehicles (Light Duty)
|  | CEC 2018 IEPR - Mid Demand | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CEC 2018 IEPR - High Demand | [5 empty] | 0 | 24.9406 | 48.7056 | 75.7332 | 113.9003 | 148.3623 | 183.9172 | 248.5334 | 298.4487 | 313.0075 | 353.3418 | 376.3175 | 401.6022 | 374.8287 | 348.0552 | 321.2818 | 294.5083 | 267.7348 | 240.9613 | 214.1878 | 187.4144 | 160.6409 | 133.8674 | 107.0939 | 80.3204 | 53.547 | 26.7735 | 0 | 0 | 0 | 0 | 0 | 0
|  | CEC Pathways High Biofuels | [5 empty] | -545.3259 | -699.823 | -874.3596 | -1053.7736 | -1227.9506 | -1372.0999 | -1405.6808 | -1383.8563 | -1226.3951 | -1072.2243 | -948.952 | -805.6572 | -622.2182 | -509.6217 | -366.4545 | -214.5968 | -80.5503 | 29.9489 | 109.822 | 167.1992 | 201.3859 | 210.4372 | 196.5191 | 207.6423 | 192.6727 | 152.6228 | 88.2996 | 0 | 1414.598 | 1441.9065 | 1465.5887 | 1485.826 | 1502.5969
|  | CEC Pathways High Electrification | [5 empty] | -545.3013 | -699.7519 | -874.2444 | -1053.6378 | -1227.9147 | -1372.4155 | -1407.1773 | -1387.0566 | -1232.3198 | -1078.4278 | -949.0217 | -782.0431 | -535.5297 | -297.4835 | 23.6803 | 374.7751 | 706.2121 | 998.4563 | 1245.8734 | 1458.3888 | 1634.7654 | 1771.7758 | 1871.239 | 1985.8259 | 2056.844 | 2083.6481 | 2065.6796 | 2002.3767 | 3420.0283 | 3428.5245 | 3412.7974 | 3374.4187 | 3315.9557
|  | CEC Pathways High Hydrogen | [5 empty] | -545.3013 | -699.7519 | -874.2444 | -1053.6378 | -1227.9147 | -1372.4155 | -1407.1773 | -1387.0566 | -1232.3198 | -1078.4278 | -949.0217 | -782.0431 | -535.5297 | -297.4835 | 23.6803 | 374.7751 | 706.2121 | 998.4563 | 1245.8734 | 1458.3888 | 1634.7654 | 1771.7758 | 1871.239 | 1985.8259 | 2056.844 | 2083.6481 | 2065.6796 | 2002.3767 | 3420.0283 | 3428.5245 | 3412.7974 | 3374.4187 | 3315.9557
|  | Active: CEC 2018 IEPR - Mid Demand | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy Efficiency
|  | CEC 2018 IEPR - High Low AAEE | [5 empty] | 0 | 60.4191 | 164.0835 | 283.8822 | 382.2677 | 533.1669 | 677.5716 | 720.4875 | 830.947 | 939.256 | 1043.2988 | 1141.307 | 1235.9639 | 1310.6245 | 1217.0084 | 1123.3924 | 1029.7764 | 936.1603 | 842.5443 | 748.9283 | 655.3122 | 561.6962 | 468.0802 | 374.4641 | 280.8481 | 187.2321 | 93.616 | 0 | 0 | 0 | 0 | 0 | 0
|  | CEC 2018 IEPR - Mid Mid AAEE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CEC 2018 IEPR - Low High AAEE | [5 empty] | 0 | -34.0786 | -73.4127 | -126.1784 | -170.5324 | -227.7975 | -310.9329 | -409.2624 | -526.4737 | -650.3914 | -765.965 | -877.472 | -983.8336 | -918.2447 | -852.6558 | -787.0669 | -721.478 | -655.8891 | -590.3002 | -524.7113 | -459.1224 | -393.5334 | -327.9445 | -262.3556 | -196.7667 | -131.1778 | -65.5889 | 0 | 0 | 0 | 0 | 0 | 0
|  | NoNewDER | [5 empty] | 0 | 407.9896 | 827.5381 | 1267.5977 | 1702.9774 | 2220.2281 | 2699.0037 | 3170.5837 | 3628.8789 | 4084.5666 | 4522.7181 | 4940.1515 | 5354.5 | 5607.4794 | 5860.4587 | 6113.4381 | 6366.4174 | 6619.3968 | 6872.3761 | 7125.3555 | 7378.3348 | 7631.3142 | 7884.2935 | 8137.2729 | 8390.2522 | 8643.2316 | 8896.2109 | 9149.1903 | 9402.1696 | 9655.149 | 9908.1283 | 10161.1077 | 10414.087
|  | CEC Pathways Baseload | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Active: CEC 2018 IEPR - Mid Mid AAEE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BTM PV
|  | CEC 2018 IEPR - Low PV + High-Low AAPV | [5 empty] | 0 | 85.4957 | 224.6024 | 379.062 | 382.1402 | 239.4259 | 170.8132 | 96.2867 | 3.4335 | 3.7326 | 4.0195 | 4.2956 | 4.5599 | 4.6121 | 4.8892 | 5.1662 | 5.4432 | 5.7203 | 5.9973 | 6.2744 | 6.5514 | 6.8285 | 7.1055 | 7.3825 | 7.6596 | 7.9366 | 8.2137 | 8.4907 | 8.7678 | 9.0448 | 9.3219 | 9.5989 | 9.8759
|  | CEC 2018 IEPR - Mid PV + Mid-Mid AAPV | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CEC 2018 IEPR - High PV + Low-High AAPV | [5 empty] | 0 | -86.8644 | -228.5383 | -210.2255 | -123.3203 | -132.7546 | -13.6702 | -3.1586 | -3.4885 | -3.7962 | -4.0919 | -4.377 | -4.6503 | -4.7871 | -5.0829 | -5.3786 | -5.6743 | -5.9701 | -6.2658 | -6.5615 | -6.8572 | -7.153 | -7.4487 | -7.7444 | -8.0401 | -8.3359 | -8.6316 | -8.9273 | -9.223 | -9.5188 | -9.8145 | -10.1102 | -10.4059
|  | NoNewDER | [5 empty] | 0 | 1.2276 | 2.555 | 3.927 | 5.1751 | 6.2638 | 7.2643 | 8.2186 | 9.1381 | 10.0485 | 10.9688 | 11.9126 | 12.9035 | 14.1364 | 15.1009 | 16.0654 | 17.0299 | 17.9944 | 18.9589 | 19.9234 | 20.8879 | 21.8524 | 22.8169 | 23.7814 | 24.7459 | 25.7104 | 26.6749 | 27.6394 | 28.6039 | 29.5684 | 30.5329 | 31.4974 | 32.4619
|  | Active: CEC 2018 IEPR - Mid PV + Mid-Mid AAPV | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Building Electrification (MW)
|  | None | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | None Through 2030 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182.5399 | 365.0799 | 547.6198 | 730.1598 | 912.6997 | 1095.2396 | 1277.7796 | 1460.3195 | 1642.8595 | 1825.3994 | 2007.9394 | 2190.4793 | 2373.0192 | 2555.5592 | 2738.0991 | 2367.7767 | 2481.0184 | 2584.2444 | 2677.0665 | 2759.4192
|  | CEC Pathways High Biofuels | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8755 | 19.8975 | 46.3306 | 89.2348 | 151.6548 | 235.773 | 340.9828 | 466.2772 | 608.4205 | 763.3418 | 930.6528 | 1108.5206 | 1294.8745 | 1485.8795 | 1677.5201 | 1867.1559 | 2053.4569 | 2234.9319 | 2410.3804 | 2578.5617 | 2738.0991 | 2887.5326 | 3025.6322 | 3151.5176 | 3264.7152 | 3365.1453
|  | CEC Pathways High Electrification | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8755 | 19.8975 | 46.3306 | 89.2348 | 151.6548 | 235.773 | 340.9828 | 466.2772 | 608.4205 | 763.3418 | 930.6528 | 1108.5206 | 1294.8745 | 1485.8795 | 1677.5201 | 1867.1559 | 2053.4569 | 2234.9319 | 2410.3804 | 2578.5617 | 2738.0991 | 2887.5326 | 3025.6322 | 3151.5176 | 3264.7152 | 3365.1453
|  | CEC Pathways High Hydrogen | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8755 | 19.8975 | 46.3306 | 89.2348 | 151.6548 | 235.773 | 340.9828 | 466.2772 | 608.4205 | 763.3418 | 930.6528 | 1108.5206 | 1294.8745 | 1485.8795 | 1677.5201 | 1867.1559 | 2053.4569 | 2234.9319 | 2410.3804 | 2578.5617 | 2738.0991 | 2887.5326 | 3025.6322 | 3151.5176 | 3264.7152 | 3365.1453
|  | Active: None Through 2030 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182.5399 | 365.0799 | 547.6198 | 730.1598 | 912.6997 | 1095.2396 | 1277.7796 | 1460.3195 | 1642.8595 | 1825.3994 | 2007.9394 | 2190.4793 | 2373.0192 | 2555.5592 | 2738.0991 | 2367.7767 | 2481.0184 | 2584.2444 | 2677.0665 | 2759.4192
Other Transport Electrification, Difference from Mid (MW)
|  | CEC 2018 IEPR - Mid Demand | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | None | [5 empty] | -18.2271 | -26.6194 | -35.3499 | -41.5991 | -48.6771 | -56.6549 | -64.9337 | -73.8402 | -82.7437 | -86.4627 | -90.8726 | -101.8703 | -108.5942 | -385.9807 | -663.3672 | -940.7537 | -1218.1402 | -1495.5268 | -1772.9133 | -2050.2998 | -2327.6863 | -2605.0728 | -2882.4593 | -3159.8458 | -3437.2323 | -3714.6188 | -3992.0053 | -4269.3918 | -3665.1547 | -3828.3972 | -3990.5846 | -4151.2875 | -4310.6336
|  | CEC Pathways High Biofuels | [5 empty] | 98.309 | 115.5827 | 155.1571 | 188.3061 | 227.0724 | 268.6088 | 329.0793 | 401.1886 | 489.0534 | 592.2537 | 703.4167 | 817.9735 | 943.2118 | 849.782 | 763.6175 | 681.819 | 608.9886 | 550.3617 | 499.6185 | 460.2488 | 423.6888 | 388.3284 | 350.4378 | 285.668 | 218.3128 | 148.4042 | 75.1745 | 0 | 804.5461 | 840.3799 | 875.982 | 911.2582 | 946.2367
|  | CEC Pathways High Electrification | [5 empty] | 98.309 | 115.5827 | 155.1572 | 188.3062 | 227.0725 | 268.6091 | 329.0802 | 401.1911 | 489.0609 | 592.2752 | 703.4742 | 818.1206 | 943.5742 | 850.6525 | 765.7118 | 686.7313 | 620.1938 | 574.2866 | 544.1192 | 531.0958 | 520.2936 | 508.8987 | 490.0229 | 443.8034 | 393.332 | 338.7578 | 279.1038 | 215.761 | 1030.1094 | 1073.3835 | 1113.6031 | 1150.3486 | 1183.4708
|  | CEC Pathways High Hydrogen | [5 empty] | 93.2265 | 107.8397 | 143.7978 | 171.9993 | 204.1076 | 239.3838 | 284.9257 | 338.505 | 402.7881 | 477.872 | 554.7296 | 626.7727 | 703.4625 | 553.0723 | 404.8593 | 256.1614 | 108.2481 | -38.4275 | -184.3865 | -331.8258 | -481.4933 | -631.7516 | -782.1555 | -940.7854 | -1098.7604 | -1255.5442 | -1410.8216 | -1564.2476 | -834.4057 | -870.1362 | -902.8918 | -932.998 | -960.9448
|  | Active: CEC 2018 IEPR - Mid Demand | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Peak load increase per unit of demand (MW / GWh) | [5 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | Baseline Consumption | [5 empty] | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401 | 0.23401
|  | Electric Vehicles (Light Duty) | [5 empty] | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521 | 0.2521
|  | Energy Efficiency | [5 empty] | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567 | -0.20567
|  | BTM PV | [5 empty] | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884 | -0.00056884
|  | Building Electrification | [5 empty] | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078
|  | Other Transport Electrification | [5 empty] | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159
|  | Hydrogen Production (MW) | [5 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | No Hydrogen | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | None Through 2030 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CEC Pathways High Biofuels | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CEC Pathways High Electrification | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CEC Pathways High Hydrogen | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Active: None Through 2030 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Scenario-Specific Managed Net Peak (MW) | [5 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | CAISO Managed Net Mid Peak, all years (MW) | [5 empty] | 45588.1542 | 45244.9453 | 45114.6771 | 44825.6635 | 44937.6517 | 45073.0937 | 45150.8188 | 45320.9108 | 45417.8789 | 45574.6015 | 45619.958 | 45682.7782 | 45770.4127 | 46119.25 | 46468.3558 | 46817.4616 | 47166.5674 | 47515.6731 | 47864.7789 | 48213.8847 | 48562.9905 | 48912.0963 | 49261.2021 | 49610.3079 | 49959.4137 | 50308.5194 | 50657.6252 | 51006.731 | 49872.6197 | 50108.2359 | 50331.3442 | 50541.8817 | 50737.9771
|  | Baseline Consumption: Difference from Mid | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Electric Vehicles (Light Duty): Difference from Mid | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Energy Efficiency: Difference from Mid | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | BTM PV: Difference from Mid | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Building Electrification: Difference from Mid | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182.5399 | 365.0799 | 547.6198 | 730.1598 | 912.6997 | 1095.2396 | 1277.7796 | 1460.3195 | 1642.8595 | 1825.3994 | 2007.9394 | 2190.4793 | 2373.0192 | 2555.5592 | 2738.0991 | 2367.7767 | 2481.0184 | 2584.2444 | 2677.0665 | 2759.4192
|  | Hydrogen Production | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Other Transport Electrification: Difference from Mid | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CAISO Managed Net Peak, Scenario Specific | [5 empty] | 45588.1542 | 45244.9453 | 45114.6771 | 44825.6635 | 44937.6517 | 45073.0937 | 45150.8188 | 45320.9108 | 45417.8789 | 45574.6015 | 45619.958 | 45682.7782 | 45770.4127 | 46301.7899 | 46833.4357 | 47365.0814 | 47896.7271 | 48428.3729 | 48960.0186 | 49491.6643 | 50023.31 | 50554.9558 | 51086.6015 | 51618.2472 | 52149.8929 | 52681.5387 | 53213.1844 | 53744.8301 | 52240.3964 | 52589.2543 | 52915.5886 | 53218.9482 | 53497.3962
|  | Capacity Contribution of Behind The Meter Resources Modeled as Supply-Side in RESOLVE |  |  | Method | Last Year | Period | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
BTM PV (MW peak reduction)
|  | CEC 2018 IEPR - Low PV + High-Low AAPV |  |  | Flat | 2030 |  | 3531.7895 | 3912.0091 | 4183.5598 | 4865.4668 | 5221.8953 | 5485.4341 | 5666.8814 | 5762.6956 | 5831.4826 | 5778.6954 | 5715.3853 | 5679.4377 | 5636.7631 | 5636.7631 | 5636.7631 | 5636.7631 | 5636.7631 | 5636.7631 | 5636.7631 | 5636.7631 | 5636.7631 | 5636.7631 | 5636.7631 | 5636.7631 | 5636.7631 | 5636.7631 | 5636.7631 | 5636.7631 | 5636.7631 | 5636.7631 | 5636.7631 | 5636.7631 | 5636.7631
|  | CEC 2018 IEPR - Mid PV + Mid-Mid AAPV |  |  | Flat | 2030 |  | 3531.7895 | 3997.5048 | 4408.1621 | 5244.5288 | 5604.0355 | 5724.86 | 5837.6946 | 5858.9822 | 5834.9161 | 5782.428 | 5719.4048 | 5683.7333 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323
|  | CEC 2018 IEPR - High PV + Low-High AAPV |  |  | Flat | 2030 |  | 3531.7895 | 4084.3692 | 4636.7005 | 5454.7543 | 5727.3559 | 5857.6146 | 5851.3648 | 5862.1409 | 5838.4046 | 5786.2242 | 5723.4967 | 5688.1103 | 5645.9733 | 5645.9733 | 5645.9733 | 5645.9733 | 5645.9733 | 5645.9733 | 5645.9733 | 5645.9733 | 5645.9733 | 5645.9733 | 5645.9733 | 5645.9733 | 5645.9733 | 5645.9733 | 5645.9733 | 5645.9733 | 5645.9733 | 5645.9733 | 5645.9733 | 5645.9733 | 5645.9733
|  | NoNewDER | [5 empty] | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895 | 3531.7895
|  | Active: CEC 2018 IEPR - Mid PV + Mid-Mid AAPV | [5 empty] | 3531.7895 | 3997.5048 | 4408.1621 | 5244.5288 | 5604.0355 | 5724.86 | 5837.6946 | 5858.9822 | 5834.9161 | 5782.428 | 5719.4048 | 5683.7333 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323 | 5641.323
|  | Active: CEC 2018 IEPR - BTM Storage peak impact | [5 empty] | 81.4023 | 465.5747 | 641.2288 | 741.5587 | 828.1247 | 921.6391 | 1006.4662 | 1072.0585 | 1136.9968 | 1201.285 | 1264.9281 | 1327.9313 | 1390.3004 | 1386.0821 | 1382.3902 | 1379.1321 | 1376.2355 | 1373.6435 | 1371.3103 | 1369.1991 | 1367.2796 | 1365.5269 | 1363.9201 | 1362.4417 | 1361.0769 | 1359.8131 | 1358.6395 | 1357.5468 | 1356.5269 | 1355.5727 | 1354.6781 | 1353.8377 | 1353.0467
|  | Total BTM capacity contribution modeled as supply-side in RESOLVE (MW peak reduction) | [5 empty] | 3613.1918 | 4463.0795 | 5049.391 | 5986.0875 | 6432.1603 | 6646.4992 | 6844.1608 | 6931.0408 | 6971.9128 | 6983.713 | 6984.3328 | 7011.6646 | 7031.6234 | 7027.405 | 7023.7132 | 7020.4551 | 7017.5585 | 7014.9664 | 7012.6333 | 7010.5221 | 7008.6026 | 7006.8499 | 7005.243 | 7003.7646 | 7002.3998 | 7001.1361 | 6999.9625 | 6998.8698 | 6997.8498 | 6996.8957 | 6996.0011 | 6995.1607 | 6994.3697
|  | Planning Reserve Margin (%) | [5 empty] | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
|  | Reduction in Planning Reserve from demand-side capacity contribution (MW) | [5 empty] | 541.9788 | 669.4619 | 757.4086 | 897.9131 | 964.824 | 996.9749 | 1026.6241 | 1039.6561 | 1045.7869 | 1047.5569 | 1047.6499 | 1051.7497 | 1054.7435 | 1054.1108 | 1053.557 | 1053.0683 | 1052.6338 | 1052.245 | 1051.895 | 1051.5783 | 1051.2904 | 1051.0275 | 1050.7865 | 1050.5647 | 1050.36 | 1050.1704 | 1049.9944 | 1049.8305 | 1049.6775 | 1049.5344 | 1049.4002 | 1049.2741 | 1049.1555
|  | Peak Demand RESOLVE Input - Moves peak contribtuion of BTM PV and Storage to the supply side | [5 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | Scenario-Specific Managed Net Peak (MW) | [5 empty] | 45588.1542 | 45244.9453 | 45114.6771 | 44825.6635 | 44937.6517 | 45073.0937 | 45150.8188 | 45320.9108 | 45417.8789 | 45574.6015 | 45619.958 | 45682.7782 | 45770.4127 | 46301.7899 | 46833.4357 | 47365.0814 | 47896.7271 | 48428.3729 | 48960.0186 | 49491.6643 | 50023.31 | 50554.9558 | 51086.6015 | 51618.2472 | 52149.8929 | 52681.5387 | 53213.1844 | 53744.8301 | 52240.3964 | 52589.2543 | 52915.5886 | 53218.9482 | 53497.3962
|  | + Total BTM capacity contribution modeled as supply-side in RESOLVE (MW peak reduction) | [5 empty] | 3613.1918 | 4463.0795 | 5049.391 | 5986.0875 | 6432.1603 | 6646.4992 | 6844.1608 | 6931.0408 | 6971.9128 | 6983.713 | 6984.3328 | 7011.6646 | 7031.6234 | 7027.405 | 7023.7132 | 7020.4551 | 7017.5585 | 7014.9664 | 7012.6333 | 7010.5221 | 7008.6026 | 7006.8499 | 7005.243 | 7003.7646 | 7002.3998 | 7001.1361 | 6999.9625 | 6998.8698 | 6997.8498 | 6996.8957 | 6996.0011 | 6995.1607 | 6994.3697
|  | - Reduction in Planning Reserve from demand-side capacity contribution (MW) | [5 empty] | -541.9788 | -669.4619 | -757.4086 | -897.9131 | -964.824 | -996.9749 | -1026.6241 | -1039.6561 | -1045.7869 | -1047.5569 | -1047.6499 | -1051.7497 | -1054.7435 | -1054.1108 | -1053.557 | -1053.0683 | -1052.6338 | -1052.245 | -1051.895 | -1051.5783 | -1051.2904 | -1051.0275 | -1050.7865 | -1050.5647 | -1050.36 | -1050.1704 | -1049.9944 | -1049.8305 | -1049.6775 | -1049.5344 | -1049.4002 | -1049.2741 | -1049.1555
|  | = RESOLVE Pre-adjustment peak demand for battery ELCC tranches calculation (MW) | [5 empty] | 48659.3673 | 49038.5628 | 49406.6594 | 49913.8379 | 50404.9879 | 50722.618 | 50968.3555 | 51212.2955 | 51344.0048 | 51510.7576 | 51556.6409 | 51642.6932 | 51747.2925 | 52275.0842 | 52803.5919 | 53332.4682 | 53861.6518 | 54391.0943 | 54920.7569 | 55450.6081 | 55980.6223 | 56510.7781 | 57041.0581 | 57571.4472 | 58101.9328 | 58632.5043 | 59163.1525 | 59693.8694 | 58188.5688 | 58536.6157 | 58862.1896 | 59164.8347 | 59442.6105
|  | + Additional increase in PRM constraint for reliability calibration (MW) | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304 | 1739.1304
|  | = RESOLVE Peak Demand for PRM (BTM PV and BTM Storage are modeled on supply side) | [5 empty] | 48659.3673 | 49038.5628 | 49406.6594 | 49913.8379 | 50404.9879 | 50722.618 | 50968.3555 | 51212.2955 | 53083.1352 | 53249.888 | 53295.7713 | 53381.8236 | 53486.4229 | 54014.2146 | 54542.7223 | 55071.5986 | 55600.7823 | 56130.2248 | 56659.8873 | 57189.7385 | 57719.7527 | 58249.9086 | 58780.1885 | 59310.5776 | 59841.0633 | 60371.6348 | 60902.283 | 61432.9999 | 59927.6992 | 60275.7461 | 60601.32 | 60903.9652 | 61181.7409
| Total Net Energy for Load by Resolve Zone |  | Values represent demand at the utility-scale generator busbar
|  | Net Energy for Load - grossed up for T&D losses (GWh) |  |  | Method | Last Year | Period | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
|  | NW | NW |  |  |  |  | 238199.104 | 239513.5897 | 240828.0754 | 241700 | 243368 | 245069 | 246927 | 247725 | 248416 | 249729 | 251304 | 252366.5357 | 253972.9325 | 255287.4183 | 256601.904 | 257916.3897 | 259230.8754 | 260545.3611 | 261859.8468 | 263174.3325 | 264488.8183 | 265803.304 | 267117.7897 | 268432.2754 | 269746.7611 | 271061.2468 | 272375.7325 | 273690.2183 | 275004.704 | 276319.1897 | 277633.6754 | 278948.1611 | 280262.6468
|  | SW | SW |  |  |  |  | 139174.2635 | 140815.8183 | 142457.373 | 143635 | 146338 | 147490 | 148960 | 150580 | 152407 | 153761 | 155531 | 157284.3214 | 158872.9206 | 160514.4754 | 162156.0302 | 163797.5849 | 165439.1397 | 167080.6944 | 168722.2492 | 170363.804 | 172005.3587 | 173646.9135 | 175288.4683 | 176930.023 | 178571.5778 | 180213.1325 | 181854.6873 | 183496.2421 | 185137.7968 | 186779.3516 | 188420.9063 | 190062.4611 | 191704.0159
|  | LDWP | LDWP |  | CAGR | 2030 | 5 | 27774.3287 | 27575.1112 | 27416.649 | 27376.1214 | 27401.3123 | 27101.2132 | 26970.9969 | 26701.5883 | 26595.2837 | 26357.1733 | 26146.8869 | 25910.8108 | 25622.0454 | 25411.4318 | 25202.5495 | 24995.3842 | 24789.9218 | 24586.1483 | 24384.0498 | 24183.6126 | 23984.823 | 23787.6674 | 23592.1324 | 23398.2048 | 23205.8712 | 23015.1186 | 22825.934 | 22638.3045 | 22452.2174 | 22267.6598 | 22084.6194 | 21903.0835 | 21723.0398
|  | IID | IID |  | CAGR | 2030 | 5 | 3891.4673 | 3873.0917 | 3883.0449 | 3882.6812 | 3894.9838 | 3889.0621 | 3887.8538 | 3892.4906 | 3887.8456 | 3883.6783 | 3882.4001 | 3874.2311 | 3860.8118 | 3854.5071 | 3848.2126 | 3841.9284 | 3835.6545 | 3829.3909 | 3823.1374 | 3816.8942 | 3810.6612 | 3804.4383 | 3798.2256 | 3792.0231 | 3785.8307 | 3779.6484 | 3773.4762 | 3767.314 | 3761.162 | 3755.0199 | 3748.8879 | 3742.766 | 3736.654
|  | BANC | BANC |  | CAGR | 2030 | 5 | 19166.4025 | 19114.9175 | 19031.8768 | 18995.4317 | 18978.5889 | 18871.1995 | 18809.6878 | 18751.7781 | 18690.2673 | 18647.5313 | 18646.7342 | 18658.8209 | 18651.2071 | 18631.1577 | 18611.1299 | 18591.1236 | 18571.1388 | 18551.1755 | 18531.2337 | 18511.3133 | 18491.4143 | 18471.5367 | 18451.6805 | 18431.8456 | 18412.032 | 18392.2398 | 18372.4688 | 18352.719 | 18332.9905 | 18313.2832 | 18293.5971 | 18273.9322 | 18254.2883

## RSP_ResultsViewer_TotRsrc_PA
Total Resources by Technology
| Technology | Unit | 2020 | 2021 | 2022 | 2023 | 2024 | 2026 | 2030 | 2045
| CAISO_ST | MW | 3733 | - | - | - | - | - | - | -
| CAISO_CCGT1 | MW | 12049 | 13333 | 13333 | 13333 | 13333 | 13333 | 13333 | 13333
| CAISO_CCGT2 | MW | 2928 | 2928 | 2928 | 2928 | 2928 | 2928 | 2928 | 1885
| CAISO_Peaker1 | MW | 4914 | 4914 | 4914 | 4914 | 4914 | 4914 | 4884 | 3163
| CAISO_Peaker2 | MW | 3683 | 3683 | 3683 | 3683 | 3683 | 3683 | 3683 | 1309
| CAISO_Advanced_CCGT | MW | - | - | - | - | - | - | - | -
| CAISO_Aero_CT | MW | - | - | - | - | - | - | - | -
| CAISO_Reciprocating_Engine | MW | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255
| CAISO_CHP | MW | 2296 | 2296 | 2296 | 2296 | 2296 | 2296 | 2296 | -
| CAISO_Coal | MW | 480 | 480 | 480 | 480 | 480 | - | - | -
| CAISO_Nuclear | MW | 2935 | 2935 | 2935 | 2935 | 1785 | 635 | 635 | 635
| Hydro | MW | 7070 | 7070 | 7070 | 7070 | 7070 | 7070 | 7070 | 7070
| Hydro_NW_CAISO | MW | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852 | 2852
| CAISO_Conventional_DR | MW | 2195 | 2418 | 2418 | 2418 | 2418 | 2418 | 2418 | 2418
| Customer_PV | MW | 9827 | 11137 | 12284 | 13303 | 14288 | 16156 | 20066 | 34858
| Solar | MW | 16310 | 18766 | 20887 | 22887 | 22887 | 22887 | 25905 | 91999
| Geothermal | MW | 1851 | 1851 | 1851 | 1851 | 1851 | 1851 | 1851 | 4159
| Biomass | MW | 903 | 903 | 903 | 903 | 903 | 903 | 901 | 2048
| Small_Hydro | MW | 974 | 974 | 974 | 974 | 974 | 974 | 974 | 974
| Wind | MW | 7357 | 7490 | 9406 | 9406 | 10193 | 10193 | 10293 | 12293
| Wind OOS New Tx | MW | - | - | - | - | - | - | 606 | 3000
| Offshore_Wind | MW | - | - | - | - | - | - | - | -
| Pumped_Hydro | MW | 1599 | 1599 | 1599 | 1599 | 1599 | 2573 | 2573 | 2573
| Li_Battery | MW | 1124 | 3775 | 3775 | 3833 | 4916 | 7745 | 10491 | 55887
| BTM_Li_Battery | MW | 722 | 839 | 942 | 1054 | 1157 | 1320 | 1647 | 1647
| Flow_Battery | MW | - | - | - | - | - | - | - | -
| Hydrogen_Electrolysis | MW | - | - | - | - | - | - | - | 450
| Flexible_Load | MW | - | - | - | - | - | - | - | -

## RSP_ResultsViewer_PRM_Summary
Planning Reserve Margin Summary
| Metric | Unit | 2020 | 2021 | 2022 | 2023 | 2024 | 2026 | 2030 | 2045
| Peak Load | MW | 49407 | 49914 | 50405 | 50723 | 50968 | 53083 | 53486 | 61433
| Reserve Margin Requirement | % | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Total Reserve Margin Requirement | MW | 56818 | 57401 | 57966 | 58331 | 58614 | 61046 | 61509 | 70648
| Firm Capacity | MW | 40130 | 37827 | 37827 | 37827 | 36685 | 35072 | 35043 | 30104
| CCGT | MW | 14248 | 15454 | 15454 | 15454 | 15454 | 15454 | 15454 | 14411
| Peaker | MW | 8334 | 8334 | 8334 | 8334 | 8334 | 8334 | 8307 | 4435
| Steam Turbine | MW | 3731 | - | - | - | - | - | - | -
| CHP | MW | 1456 | 1456 | 1456 | 1456 | 1456 | 1456 | 1456 | -
| Hydro (small + large) | MW | 5645 | 5645 | 5645 | 5645 | 5645 | 5645 | 5644 | 5644
| Nuclear | MW | 2280 | 2280 | 2280 | 2280 | 1138 | - | - | -
| Coal | MW | 470 | 470 | 470 | 470 | 470 | - | - | -
| Geothermal | MW | 1140 | 1140 | 1140 | 1140 | 1140 | 1140 | 1140 | 1597
| Biomass | MW | 630 | 630 | 630 | 630 | 630 | 630 | 629 | 1604
| Shed DR | MW | 2195 | 2418 | 2418 | 2418 | 2418 | 2418 | 2418 | 2418
| Import Capacity | MW | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
| Hoover and Palo Verde | MW | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457
| Other Firm Imports | MW | 3543 | 3543 | 3543 | 3543 | 3543 | 3543 | 3543 | 3543
| Storage | MW | 3174 | 5899 | 5963 | 6091 | 7239 | 10880 | 11084 | 23689
| Battery (incl. BTM) | MW | 1575 | 4300 | 4364 | 4491 | 5640 | 8307 | 8511 | 21116
| Pumped Storage | MW | 1599 | 1599 | 1599 | 1599 | 1599 | 2573 | 2573 | 2573
| Variable Renewable ELCC (Incl. BTM) | MW | 8514 | 8675 | 9330 | 9414 | 9690 | 10094 | 10383 | 11855
| Total Available Capacity | MW | 56818 | 57401 | 58120 | 58331 | 58614 | 61046 | 61509 | 70648
| Actual Reserve Margin | % | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Marginal PRM Cost | $/kW-yr. | 531 | 1223 | $ - | 5 | 272 | 259 | 15 | 7
| Solar Capacity Factor for Marginal ELCC (input assumption) | % | 32% | 32% | 32% | 32% | 32% | 32% | 32% | 32%
| Wind Capacity Factor for Marginal ELCC (input assumption) | % | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35%
| Marginal Solar ELCC | % | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2%
| Marginal Wind ELCC | % | 32% | 33% | 32% | 32% | 21% | 22% | 22% | 26%

## RSP_Raw_Resource_Build_LiBatt
period | resource | zone | contract | technology | planned_capacity_mw | new_build_mw | cumulative_new_build_mw | operational_capacity_mw | transmission_zone | fully_deliverable_capacity_mw | energy_only_capacity_mw | new_build_flexible_load_capacity_mwh_per_day | total_flexible_load_capacity_mwh_per_day | hydrogen_electrolysis_capacity_mw | capacity_limit_dual_$ | unit_size_mw | operational_units | capital_cost_$ | fixed_o_and_m_cost_$ | period_discount_factor | operational_planned_capacity_mw | retired_planned_capacity_mw | operational_new_capacity_mw | retired_new_capacity_mw | min_cumulative_new_build_mw | prm_mw | total_energy_capacity_mwh | 4-hour equivalent capacity, pre-ELCC curve, MW
2020 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 0 | 1123.8 | 1123.8 | 1123.8 | [6 empty] | 0 |  |  | 92237815.6 | 7153254.76 | 1 | 0 |  | 1123.8 |  | 971.35 | 1123.8 | 4495.19 | 1123.7975
2020 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 1 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2020 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 1 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2020 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 1 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2020 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 1 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2020 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 1 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2021 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 0 | 2651.15 | 3774.94 | 3774.94 | [6 empty] | 0 |  |  | 506019184.27 | 43994076.39 | 0.95238 | 0 |  | 3774.94 |  | 1321.85 | 3774.94 | 15099.77 | 3774.94
2021 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 0.95238 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2021 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 0.95238 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2021 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 0.95238 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2021 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0.95238 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2021 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0.95238 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2022 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 0 | 0 | 3774.94 | 3774.94 | [6 empty] | 0 |  |  | 506019184.27 | 43994076.39 | 0.90703 | 0 |  | 3774.94 |  | 1420.18 | 3774.94 | 15394.77 | 3774.94
2022 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 0.90703 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2022 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 0.90703 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2022 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 0.90703 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2022 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0.90703 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2022 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0.90703 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2023 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 0 | 57.57 | 3832.51 | 3832.51 | [6 empty] | 0 |  |  | 506914518.71 | 44028921.2 | 0.86384 | 0 |  | 3832.51 |  | 1543.52 | 3832.51 | 15764.77 | 3832.51
2023 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 0.86384 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2023 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 0.86384 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2023 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 0.86384 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2023 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0.86384 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2023 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0.86384 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2024 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 0 | 1083.81 | 4916.32 | 4916.32 | [6 empty] | 0 |  |  | 621533793.68 | 55198311.49 | 1.2145 | 0 |  | 4916.32 |  | 1617.45 | 4916.32 | 19665.28 | 4916.32
2024 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 1.2145 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2024 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 1.2145 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2024 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 1.2145 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2024 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 1.2145 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2024 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 1.2145 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2026 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 0 | 1736.82 | 6653.14 | 6653.14 | [6 empty] | 0 |  |  | 807424141.24 | 73630178.93 | 2.1706 | 0 |  | 6653.14 |  | 1617.45 | 6653.14 | 26612.58 | 6653.14
2026 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 1091.49 | 1091.49 | 1091.49 | [6 empty] | 0 |  |  | 116820867.97 | 11583316.62 | 2.1706 | 0 |  | 1091.49 |  | 0 | 828.44 | 4365.96 | 1091.49
2026 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 2.1706 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2026 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 2.1706 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2026 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 2.1706 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2026 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 2.1706 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2030 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 0 | 0 | 6653.14 | 6653.14 | [6 empty] | -22580.64 |  |  | 807424141.24 | 73630178.93 | 4.9706 | 0 |  | 6653.14 |  | 1617.45 | 6653.14 | 26612.58 | 6653.14
2030 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 2746.07 | 3837.56 | 3837.56 | [6 empty] | 0 |  |  | 145216095.35 | 12738281.22 | 4.9706 | 0 |  | 3837.56 |  | 0 | 828.44 | 4365.96 | 1091.49
2030 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 4.9706 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2030 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 4.9706 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2030 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 4.9706 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2030 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 4.9706 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2045 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 0 | 1148.16 | 7801.3 | 7801.3 | [6 empty] | -6789.02 |  |  | 1128857001.61 | 107782568.22 | 6.6952 | 0 |  | 7801.3 |  | 1617.45 | 7801.3 | 44752.45 | 7801.3
2045 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 2186.56 | 6024.12 | 6024.12 | [6 empty] | -5109.32 |  |  | 685115131.76 | 69948121.6 | 6.6952 | 0 |  | 6024.12 |  | 0 | 4572.31 | 34701.86 | 6024.12
2045 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 9020.45 | 9020.45 | 9020.45 | [6 empty] | -3297.2 |  |  | 896355035.07 | 91750268.6 | 6.6952 | 0 |  | 9020.45 |  | 0 | 4501.2 | 47586.87 | 9020.45
2045 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 5917.35 | 5917.35 | 5917.35 | [6 empty] | -1331.21 |  |  | 789558649.79 | 82034515.15 | 6.6952 | 0 |  | 5917.35 |  | 0 | 1503.01 | 42962.34 | 5917.35
2045 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 27123.87 | 27123.87 | 27123.87 | [9 empty] | 3503674969.29 | 363510196.72 | 6.6952 | 0 |  | 27123.87 |  | 0 | 1708.8 | 190199.82 | 27123.87
2045 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 6.6952 | 0 |  | 0 |  | 0 | 0 | 0 | 0

## RSP_Raw_Storage_Build_LiBatt
period | resource | zone | contract | technology | planned_energy_capacity_mwh | new_build_mwh | cumulative_new_build_mwh | total_energy_capacity_mwh
2020 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 2914.05 | 1581.14 | 1581.14 | 4495.19
2020 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2020 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2020 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2020 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2020 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2021 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 3965.55 | 9553.08 | 11134.22 | 15099.77
2021 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2021 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2021 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2021 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2021 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2022 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 4260.55 | 0 | 11134.22 | 15394.77
2022 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2022 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2022 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2022 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2022 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2023 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 4630.55 | 0 | 11134.22 | 15764.77
2023 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2023 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2023 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2023 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2023 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2024 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 4852.35 | 3678.71 | 14812.93 | 19665.28
2024 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2024 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2024 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2024 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2024 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2026 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 4852.35 | 6947.3 | 21760.23 | 26612.58
2026 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 4365.96 | 4365.96 | 4365.96
2026 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2026 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2026 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2026 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2030 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 4852.35 | 0 | 21760.23 | 26612.58
2030 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 4365.96 | 4365.96
2030 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2030 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2030 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2030 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2045 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 4852.35 | 18139.87 | 39900.1 | 44752.45
2045 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 30335.9 | 34701.86 | 34701.86
2045 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 47586.87 | 47586.87 | 47586.87
2045 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 42962.34 | 42962.34 | 42962.34
2045 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 190199.82 | 190199.82 | 190199.82
2045 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0

## 38mmt_ResultsViewer_TotRsrc_PA
Total Resources by Technology
| Technology | Unit | 2020 | 2021 | 2022 | 2023 | 2024 | 2026 | 2030 | 2045
| CAISO_ST | MW | 3733 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CAISO_CCGT1 | MW | 12049.47 | 13333.47 | 13333.47 | 13333.47 | 13333.47 | 13333.47 | 13333.47 | 13333.47
| CAISO_CCGT2 | MW | 2927.93 | 2927.93 | 2927.93 | 2927.93 | 2927.93 | 2927.93 | 2927.93 | 1885
| CAISO_Peaker1 | MW | 4913.93 | 4913.93 | 4913.93 | 4913.93 | 4913.93 | 4913.93 | 3163 | 3163
| CAISO_Peaker2 | MW | 3682.71 | 3682.71 | 3682.71 | 3682.71 | 3682.71 | 3682.71 | 3387.88 | 1309
| CAISO_Advanced_CCGT | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CAISO_Aero_CT | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CAISO_Reciprocating_Engine | MW | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 184
| CAISO_CHP | MW | 2296.02 | 2296.02 | 2296.02 | 2296.02 | 2296.02 | 2296.02 | 2296.02 | 0
| CAISO_Coal | MW | 480 | 480 | 480 | 480 | 480 | 0 | 0 | 0
| CAISO_Nuclear | MW | 2935 | 2935 | 2935 | 2935 | 1785 | 635 | 635 | 635
| Hydro | MW | 7070.1 | 7070.1 | 7070.1 | 7070.1 | 7070.1 | 7070.1 | 7069.51 | 7069.51
| Hydro_NW_CAISO | MW | 2851.77 | 2851.77 | 2851.77 | 2851.77 | 2851.77 | 2851.77 | 2851.77 | 2851.77
| CAISO_Conventional_DR | MW | 2195.45 | 2417.69 | 2417.69 | 2417.69 | 2417.69 | 2417.69 | 2417.69 | 2417.69
| Customer_PV | MW | 9827.31 | 11136.82 | 12284.27 | 13303.04 | 14288.23 | 16155.51 | 20066.03 | 34857.67
| Solar | MW | 16310.33 | 18765.85 | 20887.45 | 22887.45 | 22887.45 | 23571.29 | 26882.73 | 91623.25
| Geothermal | MW | 1851.31 | 1851.31 | 1851.31 | 1851.31 | 1851.31 | 1851.31 | 1851.31 | 4159.41
| Biomass | MW | 902.65 | 902.65 | 902.65 | 902.65 | 902.65 | 902.65 | 900.75 | 2047.6
| Small_Hydro | MW | 974.03 | 974.03 | 974.03 | 974.03 | 974.03 | 974.03 | 974.03 | 974.03
| Wind | MW | 7356.56 | 7490.31 | 10380.08 | 10380.08 | 11267.08 | 11267.08 | 12735.24 | 12735.24
| Wind OOS New Tx | MW | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 3000
| Offshore_Wind | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumped_Hydro | MW | 1599.2 | 1599.2 | 1599.2 | 1599.2 | 1599.2 | 3203.7 | 3203.7 | 3203.7
| Li_Battery | MW | 1123.82 | 3774.96 | 3774.96 | 3774.96 | 4724.81 | 6653.14 | 11331.24 | 54961.59
| BTM_Li_Battery | MW | 721.99 | 839.45 | 942.36 | 1054.19 | 1157.1 | 1320.42 | 1647.06 | 1647.06
| Flow_Battery | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hydrogen_Electrolysis | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450.41
| Flexible_Load | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 38mmt_ResultsViewer_PRM_Summary
Planning Reserve Margin Summary
| Metric | Unit | 2020 | 2021 | 2022 | 2023 | 2024 | 2026 | 2030 | 2045
| Peak Load | MW | 49406.66 | 49913.84 | 50404.99 | 50722.62 | 50968.36 | 53083.14 | 53486.42 | 61433
| Reserve Margin Requirement | % | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Total Reserve Margin Requirement | MW | 56817.659 | 57400.916 | 57965.7385 | 58331.013 | 58613.614 | 61045.611 | 61509.383 | 70647.95
| Firm Capacity | MW | 40129.67 | 37826.82 | 37826.82 | 37826.82 | 36684.7 | 35072.14 | 33169.5 | 30007.48
| CCGT | MW | 14247.68 | 15453.96 | 15453.96 | 15453.96 | 15453.96 | 15453.96 | 15453.96 | 14411.15
| Peaker | MW | 8334.04 | 8334.04 | 8334.04 | 8334.04 | 8334.04 | 8334.04 | 6433.23 | 4363.69
| Steam Turbine | MW | 3731.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHP | MW | 1455.68 | 1455.68 | 1455.68 | 1455.68 | 1455.68 | 1455.68 | 1455.68 | 0
| Hydro (small + large) | MW | 5644.65 | 5644.65 | 5644.65 | 5644.65 | 5644.65 | 5644.65 | 5644.15 | 5644.15
| Nuclear | MW | 2279.91 | 2279.91 | 2279.91 | 2279.91 | 1137.78 | 0 | 0 | 0
| Coal | MW | 470.43 | 470.43 | 470.43 | 470.43 | 470.43 | 0 | 0 | 0
| Geothermal | MW | 1140.41 | 1140.41 | 1140.41 | 1140.41 | 1140.41 | 1140.41 | 1140.41 | 1571.6
| Biomass | MW | 630.05 | 630.05 | 630.05 | 630.05 | 630.05 | 630.05 | 628.73 | 1603.56
| Shed DR | MW | 2195.45 | 2417.69 | 2417.69 | 2417.69 | 2417.69 | 2417.69 | 2417.69 | 2417.69
| Import Capacity | MW | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
| Hoover and Palo Verde | MW | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457 | 1457
| Other Firm Imports | MW | 3543 | 3543 | 3543 | 3543 | 3543 | 3543 | 3543 | 3543
| Storage | MW | 3174.26 | 5898.82 | 5963.14 | 6033.03 | 7047.19 | 10682.11 | 12869.04 | 23878.35
| Battery (incl. BTM) | MW | 1575.06 | 4299.61 | 4363.93 | 4433.83 | 5448 | 7478.4 | 9665.33 | 20674.64
| Pumped Storage | MW | 1599.2 | 1599.2 | 1599.2 | 1599.2 | 1599.2 | 3203.7 | 3203.7 | 3203.7
| Variable Renewable ELCC (Incl. BTM) | MW | 8513.72 | 8675.27 | 9552.02 | 9652.11 | 9881.72 | 10291.36 | 10470.85 | 11773.89
| Total Available Capacity | MW | 56817.65 | 57400.91 | 58341.98 | 58511.96 | 58613.61 | 61045.61 | 61509.39 | 70659.72
| Actual Reserve Margin | % | 15% | 15% | 15.75% | 15.36% | 15% | 15% | 15% | 15.02%
| Marginal PRM Cost | $/kW-yr. | 531.3924 | 1226.6573 | 0 | 0 | 270.5558 | 204.3306 | 14.246 | 0
| Solar Capacity Factor for Marginal ELCC (input assumption) | % | 32% | 32% | 32% | 32% | 32% | 32% | 32% | 32%
| Wind Capacity Factor for Marginal ELCC (input assumption) | % | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35%
| Marginal Solar ELCC | % | 2.374% | 1.989% | 2.371% | 2.365% | 2.361% | 2.434% | 2.421% | 1.565%
| Marginal Wind ELCC | % | 32.31% | 32.52% | 21.24% | 21.19% | 21.15% | 21.8% | 21.69% | 25.58%

## 38mmt_Raw_Resource_Build_LiBatt
period | resource | zone | contract | technology | planned_capacity_mw | new_build_mw | cumulative_new_build_mw | operational_capacity_mw | transmission_zone | fully_deliverable_capacity_mw | energy_only_capacity_mw | new_build_flexible_load_capacity_mwh_per_day | total_flexible_load_capacity_mwh_per_day | hydrogen_electrolysis_capacity_mw | capacity_limit_dual_$ | unit_size_mw | operational_units | capital_cost_$ | fixed_o_and_m_cost_$ | period_discount_factor | operational_planned_capacity_mw | retired_planned_capacity_mw | operational_new_capacity_mw | retired_new_capacity_mw | min_cumulative_new_build_mw | prm_mw | total_energy_capacity_mwh | 4-hour equivalent capacity, pre-ELCC curve, MW
2020 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 0 | 1123.82 | 1123.82 | 1123.82 | [6 empty] | 0 |  |  | 92242195.57 | 7153636.47 | 1 | 0 |  | 1123.82 |  | 971.35 | 1123.82 | 4495.28 | 1123.82
2020 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 1 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2020 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 1 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2020 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 1 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2020 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 1 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2020 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 1 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2021 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 0 | 2651.14 | 3774.96 | 3774.96 | [6 empty] | 0 |  |  | 506022957.64 | 43994403.66 | 0.95238 | 0 |  | 3774.96 |  | 1321.85 | 3774.96 | 15099.85 | 3774.96
2021 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 0.95238 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2021 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 0.95238 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2021 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 0.95238 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2021 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0.95238 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2021 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0.95238 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2022 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 0 | 0 | 3774.96 | 3774.96 | [6 empty] | 0 |  |  | 506022957.64 | 43994403.66 | 0.90703 | 0 |  | 3774.96 |  | 1420.18 | 3774.96 | 15394.85 | 3774.96
2022 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 0.90703 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2022 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 0.90703 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2022 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 0.90703 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2022 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0.90703 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2022 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0.90703 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2023 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 0 | 0 | 3774.96 | 3774.96 | [6 empty] | 0 |  |  | 506022957.64 | 43994403.66 | 0.86384 | 0 |  | 3774.96 |  | 1543.52 | 3774.96 | 15764.85 | 3774.96
2023 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 0.86384 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2023 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 0.86384 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2023 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 0.86384 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2023 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0.86384 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2023 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0.86384 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2024 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 0 | 949.85 | 4724.81 | 4724.81 | [6 empty] | 0 |  |  | 598060109.27 | 52889418.74 | 1.2145 | 0 |  | 4724.81 |  | 1617.45 | 4724.81 | 18899.23 | 4724.8075
2024 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 1.2145 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2024 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 1.2145 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2024 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 1.2145 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2024 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 1.2145 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2024 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 1.2145 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2026 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 0 | 1928.34 | 6653.14 | 6653.14 | [6 empty] | 0 |  |  | 804447902.36 | 73353700.46 | 2.1706 | 0 |  | 6653.14 |  | 1617.45 | 6653.14 | 26612.58 | 6653.14
2026 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 2.1706 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2026 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 2.1706 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2026 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 2.1706 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2026 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 2.1706 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2026 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 2.1706 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2030 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 0 | 0 | 6653.14 | 6653.14 | [6 empty] | -21143.79 |  |  | 804447902.36 | 73353700.46 | 4.9706 | 0 |  | 6653.14 |  | 1617.45 | 6653.14 | 26612.58 | 6653.14
2030 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 4678.1 | 4678.1 | 4678.1 | [6 empty] | 0 |  |  | 257988555.31 | 24747304.55 | 4.9706 | 0 |  | 4678.1 |  | 0 | 1982.78 | 10449.43 | 2612.3575
2030 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 4.9706 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2030 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  | 0 | 0 | 4.9706 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2030 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 4.9706 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2030 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 4.9706 | 0 |  | 0 |  | 0 | 0 | 0 | 0
2045 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 0 | 1148.16 | 7801.3 | 7801.3 | [6 empty] | -272.49 |  |  | 1120834973.31 | 106959168.53 | 6.6952 | 0 |  | 7801.3 |  | 1617.45 | 7801.3 | 44458.4 | 7801.3
2045 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 1346.02 | 6024.12 | 6024.12 | [6 empty] | -272.49 |  |  | 713214104.7 | 73283093.15 | 6.6952 | 0 |  | 6024.12 |  | 0 | 4572.31 | 36284.11 | 6024.12
2045 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 9020.45 | 9020.45 | 9020.45 | [6 empty] | -272.49 |  |  | 866893356.28 | 88556869.85 | 6.6952 | 0 |  | 9020.45 |  | 0 | 4501.2 | 45869.99 | 9020.45
2045 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 5917.35 | 5917.35 | 5917.35 | [6 empty] | 0 |  |  | 792136253.82 | 82313905.8 | 6.6952 | 0 |  | 5917.35 |  | 0 | 1503.01 | 43112.55 | 5917.35
2045 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 20117.62 | 20117.62 | 20117.62 | [9 empty] | 2565335672.67 | 266001824.98 | 6.6952 | 0 |  | 20117.62 |  | 0 | 1267.41 | 139128.4 | 20117.62
2045 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 6080.75 | 6080.75 | 6080.75 | [9 empty] | 793303649.62 | 82342497.13 | 6.6952 | 0 |  | 6080.75 |  | 0 | 0 | 43096.38 | 6080.75

## 38mmt_Raw_Storage_Build_LiBatt
period | resource | zone | contract | technology | planned_energy_capacity_mwh | new_build_mwh | cumulative_new_build_mwh | total_energy_capacity_mwh
2020 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 2914.05 | 1581.23 | 1581.23 | 4495.28
2020 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2020 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2020 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2020 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2020 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2021 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 3965.55 | 9553.07 | 11134.3 | 15099.85
2021 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2021 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2021 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2021 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2021 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2022 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 4260.55 | 0 | 11134.3 | 15394.85
2022 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2022 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2022 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2022 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2022 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2023 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 4630.55 | 0 | 11134.3 | 15764.85
2023 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2023 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2023 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2023 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2023 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2024 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 4852.35 | 2912.58 | 14046.88 | 18899.23
2024 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2024 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2024 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2024 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2024 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2026 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 4852.35 | 7713.35 | 21760.23 | 26612.58
2026 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2026 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2026 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2026 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2026 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2030 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 4852.35 | 0 | 21760.23 | 26612.58
2030 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 10449.43 | 10449.43 | 10449.43
2030 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2030 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2030 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2030 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 0 | 0 | 0
2045 | CAISO_New_Li_Battery | CAISO | CAISO | Li_Battery | 4852.35 | 17845.83 | 39606.05 | 44458.4
2045 | CAISO_New_Li_Battery_2 | CAISO | CAISO | Li_Battery | 0 | 25834.69 | 36284.11 | 36284.11
2045 | CAISO_New_Li_Battery_3 | CAISO | CAISO | Li_Battery | 0 | 45869.99 | 45869.99 | 45869.99
2045 | CAISO_New_Li_Battery_4 | CAISO | CAISO | Li_Battery | 0 | 43112.55 | 43112.55 | 43112.55
2045 | CAISO_New_Li_Battery_5 | CAISO | CAISO | Li_Battery | 0 | 139128.4 | 139128.4 | 139128.4
2045 | CAISO_New_Li_Battery_6 | CAISO | CAISO | Li_Battery | 0 | 43096.38 | 43096.38 | 43096.38