## Slide 1: SERVM analysis of IRP 46 MMT Portfolio for use in 2021-22 TPP
January 14, 2021

## Slide 2: Purpose of this Presentation
Present SERVM reliability and operational modeling results of the CPUC Integrated Resource Plan (IRP) 46 MMT portfolio proposed for use in the CAISO’s 2021-22 Transmission Planning Process (TPP)
  Proposed Decision Transferring Electric Resource Portfolios to CAISO for 2021-2022 TPP
  Portfolios & Modeling Assumptions for the 2021-2022 Transmission Planning Process
Serve as supplemental documentation of the IRP 46 MMT portfolio, demonstrating sufficient system reliability and emissions reduction for use in the CAISO TPP

## Slide 3: Background
In the CPUC’s IRP process:
  Staff used the RESOLVE capacity expansion model to design portfolios of new resources expected to meet electric system planning goals at least cost
  Staff used the SERVM probabilistic reliability and production cost model to validate the reliability, operability, and emissions of resource portfolios generated by RESOLVE
IRP Decision (D.)20-03-028 adopted a Reference System Portfolio (RSP) to serve as a guide for long-term electric resource procurement that achieves state policy goals
  Staff designed the RSP to achieve statewide electric sector GHG emissions of 46 MMT using the CEC’s 2018 IEPR demand forecast for projected electric demand
For the CAISO’s 2021-22 TPP, the CPUC is providing as a base case portfolio a revised version of the 46 MMT portfolio that was adopted as the RSP
  Staff reoptimized the 46 MMT portfolio using the CEC’s 2019 IEPR demand forecast for projected electric demand and with other small updates in place

## Slide 4: SERVM Updates Since RSP Adoption (Group 1)
These updates were completed first and tested:
Wind shapes rebuilt using MERRA dataset from NASA
  https://gmao.gsfc.nasa.gov/reanalysis/MERRA/FAQ/
  Original wind shapes were developed from National Climate Data Center wind speed data which had bad or incomplete data in Alberta, East Riverside, and New Mexico
  MERRA dataset is based on satellite data and more complete
  Capacity factor increased in rebuilt wind shapes
Updated SERVM software
  Unit commitment logic improved, generally making CCGTs more flexible
  Storage dispatch logic improved, linking current state of charge to ability to provide ancillary services
    Total storage split into categories of utility-scale or BTM
    Utility-scale modeled as providing up and down reserves up to 2x current state of charge
    BTM modeled as not providing ancillary services
  Various enhancements to input tables and output reports

## Slide 5: SERVM Updates Since RSP Adoption (Group 2)
These updates were completed after the first group of updates:
Incorporated CEC’s 2019 IEPR demand forecast to model future electric demand
  2019 IEPR Workshops, Notices and Documents (ca.gov)
  Developed 2031 demand-side projections by linearly extrapolating electric demand, AAEE, BTM PV, Light and Medium Duty Electric Vehicles components using IEPR forecast growth rate for 2026-2030. TOU rate impacts assumed same in 2031 as in 2030.
Updated burner-tip fuel price forecast (to CEC’s June 2020 vintage)
  Natural Gas Burner Tip Prices for California and the Western United States
Reran RESOLVE 46 MMT portfolio optimization with 2019 IEPR demand forecast, including 2031 as a simulation year, and input the revised electric resource buildout into SERVM
  RESOLVE inputs and results with the 2019 IEPR will be posted here: Portfolios & Modeling Assumptions for the 2021-2022 Transmission Planning Process
All other inputs and SERVM configuration are identical to that described as final in D.20-03-028, the Reference System Plan decision

## Slide 6: 2019 IEPR-updated 46 MMT Portfolio in RESOLVE and SERVM
Staff studied years 2026 and 2031 of the 46 MMT portfolio designed by RESOLVE. This table summarizes the fleet installed capacity modeled in RESOLVE and SERVM.
    BTMPV installed capacity is at customer side
    RESOLVE counts pumping load units as DR, hence the higher capacities than SERVM
    SERVM models hydro as hourly profiles and counts installed capacity differently than RESOLVE
    Battery Storage is total of utility-scale and BTM
Comparison of installed capacity in MW |  |  |  | 
 | 2026 | 2026 | 2031 | 2031
Unit Category | RESOLVE | SERVM | RESOLVE | SERVM
Battery Storage | 10,279 | 9,149 | 14,071 | 13,969
Biomass | 903 | 856 | 901 | 854
BTMPV | 17,409 | 17,409 | 21,303 | 22,087
CC | 16,261 | 16,081 | 16,261 | 16,081
Coal | - | - | - | -
Cogen | 2,296 | 2,320 | 2,066 | 2,320
CT | 8,597 | 8,029 | 8,597 | 8,029
DR | 2,803 | 1,776 | 2,803 | 1,750
Geothermal | 1,851 | 1,881 | 1,851 | 1,881
Hydro | 8,044 | 6,353 | 8,044 | 6,353
ICE | 255 | 255 | 255 | 255
Nuclear | 635 | 635 | 635 | 635
PSH | 2,227 | 2,346 | 2,227 | 2,346
Solar | 21,398 | 20,940 | 27,282 | 27,009
Steam | - | - | - | -
Wind | 10,125 | 10,076 | 11,808 | 11,867

## Slide 7: Review of SERVM Metrics
Reliability Metrics
  Loss-of-Load Expectation (LOLE): expected frequency of events
  Loss-of-Load Hours (LOLH): expected duration of unserved energy
  Expected Unserved Energy (EUE): expected volume of unserved energy
  Loss-of-load events modeled to occur when operating reserves of 4.5% of hourly demand cannot be maintained (based on 3% spinning reserve and 1.5% regulation requirements)
  Electric system considered sufficiently reliable if probability-weighted LOLE <= 0.1, which corresponds to about 1 day in 10 years where firm load must be shed to balance the grid
Operational Metrics
  Annual energy by resource type, imports and exports, curtailment, storage dispatch, and emissions

## Slide 8: Overview of Modeling Cases Presented
The tables on the following slides compare reliability and operational results for the following cases:
  RESOLVE 2030 simulation of the 46 MMT RSP (i.e. 2018 IEPR input into RESOLVE)
  SERVM 2030 simulation of A. and with SERVM wind shape and software updates
  SERVM 2030 simulation of B. and with 2019 IEPR input into SERVM
  RESOLVE 2026 and 2031 simulation of the 46 MMT RSP but with 2019 IEPR input into RESOLVE
  SERVM 2026 and 2031 simulation using the RESOLVE candidate resources produced in D. and with SERVM wind shape and software updates, and with 2019 IEPR input into SERVM

## Slide 9: SERVM Reliability Results
When SERVM was updated to the 2019 IEPR but the candidate resources from RESOLVE were not updated (i.e. still based on the 2018 IEPR), LOLE increased since the 2019 IEPR projected higher demand in 2030 than the 2018 IEPR (2nd column of results in table)
When SERVM was also updated to include candidates from RESOLVE rerun with the 2019 IEPR, LOLE decreased back down (4th column of results in table)
2026 and 2031 LOLE results of the 46 MMT portfolio recommended for study in the 2021-22 TPP are acceptably close to the 0.1 LOLE standard
* Normalized EUE = EUE/annual load expressed as a percent
 | 46 MMT RSP w/ SERVM wind shape & software updates | 46 MMT RSP w/ SERVM wind shape & software updates, & 2019 IEPR | 46 MMT RSP w/ SERVM wind shape & software updates, & 2019 IEPR, & RESOLVE rerun | 
Study Year | 2030 |  | 2026 | 2031
LOLE (expected events/year) | 0.0935 | 0.1901 | 0.1081 | 0.0643
LOLH (expected hours of events/year) | 0.1262 | 0.3095 | 0.2442 | 0.0976
EUE (MWh) | 122.8 | 400.3 | 205.2 | 122.41
annual load (GWh) | 255,778 | 263,837 | 255,118 | 267,969
normalized EUE (%) | 0.0000480% | 0.0001517% | 0.0000805% | 0.0000457%

## Slide 10: Months and Hours When EUE Occurred
Case: 46 MMT RSP w/ SERVM wind shape & software updates, & 2019 IEPR, & RESOLVE rerun
Bulk of EUE occurs in August and September evening hours
In 2031, the EUE hours shift later, likely due to further peak shift from solar penetration
2026 Expected Unserved Energy GWh - hours and months not shown have no EUE |  |  |  |  |  | 
Hour Ending | May | June | July | August | September | October
17 | - | - | - | - | - | -
18 | - | - | 0.021 | 4.241 | 34.860 | -
19 | - | - | 3.202 | 14.542 | 51.302 | -
20 | - | - | 2.587 | 8.519 | 27.086 | -
21 | - | - | 5.060 | 12.586 | 34.696 | -
22 | - | 0.059 | 0.549 | 4.718 | 1.212 | -
23 | - | - | - | - | - | -
24 | - | - | - | - | - | -
2031 Expected Unserved Energy GWh - hours and months not shown have no EUE |  |  |  |  |  | 
Hour Ending | May | June | July | August | September | October
17 | - | - | - | - | - | -
18 | - | - | - | - | 0.088 | -
19 | - | - | 0.047 | - | 0.743 | -
20 | - | - | 0.215 | 0.035 | 1.197 | -
21 | - | - | 3.596 | 1.429 | 37.075 | -
22 | - | - | 17.019 | 7.177 | 53.788 | -
23 | - | - | - | - | - | -
24 | - | - | - | - | - | -

## Slide 11: SERVM Annual Energy Balance Results
Case | 46 MMT RSP | 46 MMT RSP w/ SERVM wind shape & software updates | 46 MMT RSP w/ SERVM wind shape & software updates, & 2019 IEPR | 46 MMT RSP RESOLVE rerun w/ 2019 IEPR | 46 MMT RSP w/ SERVM wind shape & software updates, & 2019 IEPR, & RESOLVE rerun | 46 MMT RSP RESOLVE rerun w/ 2019 IEPR | 46 MMT RSP w/ SERVM wind shape & software updates, & 2019 IEPR, & RESOLVE rerun
Study Year | 2030 |  |  | 2026 |  | 2031 | 
Model | RESOLVE | SERVM | SERVM | RESOLVE | SERVM | RESOLVE | SERVM
Category | CAISO Energy Balance (GWh) |  |  |  |  |  | 
CHP | 10,881 | 9,950 | 10,015 | 10,881 | 9,494 | 9,793 | 9,786
Nuclear | 5,108 | 5,136 | 5,136 | 5,108 | 5,563 | 5,108 | 5,136
Hydro In-state | 22,995 | 25,393 | 25,393 | 22,996 | 25,393 | 22,995 | 25,392
Hydro From NW | 11,311 | 11,000 | 11,000 | 11,447 | 11,000 | 11,404 | 11,000
CCGT | 38,564 | 44,556 | 45,966 | 56,451 | 45,249 | 47,896 | 51,087
Peaker | 69 | 3,283 | 3,166 | 372 | 2,223 | 19 | 4,234
Reciprocating Engine | 19 | 78 | 82 | 42 | 64 | 32 | 84
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0
Steam | 0 | 0 | 0 | 0 | 0 | 0 | 0
BTM PV | 38,046 | 37,949 | 39,177 | 33,007 | 32,256 | 40,390 | 40,917
Solar | 68,249 | 65,177 | 65,177 | 54,911 | 52,076 | 71,850 | 68,420
Wind | 29,215 | 27,700 | 27,700 | 26,253 | 25,570 | 32,567 | 30,536
Geothermal | 13,042 | 13,906 | 14,179 | 13,042 | 14,849 | 13,042 | 14,488
Biomass | 6,764 | 5,484 | 5,738 | 6,778 | 5,894 | 6,764 | 5,332
Pumped Storage Roundtrip Losses | -1,478 | -1,237 | -1,292 | -793 | -1,194 | -1,310 | -1,164
Battery Storage Roundtrip Losses | -2,705 | -2,299 | -2,314 | -2,211 | -2,323 | -3,190 | -2,831
Curtailment | -5,541 | -1,944 | -1,363 | -1,362 | -343 | -4,792 | -2,308
Imports (unspecified) | 30,527 | 21,004 | 23,517 | 22,166 | 28,296 | 21,559 | 15,720
Exports | -6,316 | -9,212 | -7,298 | -3,026 | -2,217 | -5,071 | -7,404
Load | 257,010 | 255,778 | 263,837 | 254,963 | 255,118 | 267,350 | 267,969

## Slide 12: SERVM Annual GHG Emissions Results
Case | 46 MMT RSP | 46 MMT RSP w/ SERVM wind shape & software updates | 46 MMT RSP w/ SERVM wind shape & software updates, & 2019 IEPR | 46 MMT RSP RESOLVE rerun w/ 2019 IEPR | 46 MMT RSP w/ SERVM wind shape & software updates, & 2019 IEPR, & RESOLVE rerun | 46 MMT RSP RESOLVE rerun w/ 2019 IEPR | 46 MMT RSP w/ SERVM wind shape & software updates, & 2019 IEPR, & RESOLVE rerun
Study Year | 2030 |  |  | 2026 |  | 2031 | 
Model | RESOLVE | SERVM | SERVM | RESOLVE | SERVM | RESOLVE | SERVM
Category | CAISO GHG Emissions (MMtCO2/Yr) |  |  |  |  |  | 
CAISO Generator Emissions | 19.4 | 23.7 | 24.2 | 26.2 | 23.1 | 22.5 | 27.0
Unspecified Import Emissions | 13.1 | 9.0 | 10.1 | 9.5 | 12.1 | 9.2 | 6.7
CAISO Emissions w/o BTM CHP | 32.4 | 32.7 | 34.3 | 35.7 | 35.2 | 31.7 | 33.7
CAISO BTM CHP Emissions | 5.5 | 5.5 | 5.5 | 5.0 | 5.0 | 4.5 | 4.5
CAISO Emissions w/ BTM CHP | 37.9 | 38.2 | 39.8 | 40.6 | 40.2 | 36.2 | 38.2
Emissions delta relative to RESOLVE |  | 0.31 | 1.91 |  | -0.4 |  | 2.0
 | CAISO Generation and Imports (GWh) |  |  |  |  |  | 
Zero-GHG | 178,689 | 177,053 | 181,235 | 166,152 | 166,524 | 189,757 | 184,374
GHG-emitting | 80,061 | 78,870 | 82,748 | 89,912 | 85,325 | 79,300 | 80,912

## Slide 13: Conclusion
For the CAISO’s 2021-22 TPP, the CPUC is providing as a base case portfolio a revised version of the 46 MMT portfolio that was adopted as the RSP
  Staff reoptimized the 46 MMT portfolio using the CEC’s 2019 IEPR demand forecast for projected electric demand and with other small updates in place
CPUC staff conducted SERVM studies of years 2026 and 2031 using the IRP RSP Decision’s 46 MMT portfolio reoptimized with the 2019 IEPR demand forecast
Results show that the portfolio is expected to be reliable in both 2026 and 2031, with a LOLE of 0.108 in 2026 and a LOLE of 0.064 in 2031; these LOLE values meet or go below the 0.1 LOLE industry reliability standard
Emissions modeled in SERVM are very similar to RESOLVE in both 2026 and 2031 study years
CPUC recommends that this portfolio can be used by the CAISO for 2021-22 TPP studies