## Attachment A
ATTACHMENT A

## Summary System
|  |  | 2000 INSPECTION CYCLES | [6 empty] | 2000 INSPECTIONS | [5 empty] | YEAR END 2000 CONDITION RATING | [6 empty] | 2000 CORRECTIVE ACTIONS | [11 empty] | YEAR 2001 PLAN
(Maximum Intervals in Years)
|  |  | Patrol |  | Detailed |  | Intrusive |  | Yr End 2000 | Patrols |  |  | Detail or Intrusive |  |  | Level 1, 2, 3 |  | Level 4 |  | Level 5 |  |  | Level 4 |  |  |  | Level 5 |  |  |  | Level 4 + Level 5 |  |  |  |  | Detail or Intrusive Inspections |  |  | Corrective Actions
|  |  | Urban | Rural | Urban | Rural | Urban | Rural | Total Inventory | Planned (1) | Complete (2) | Balance | Planned | Complete | Balance (3) | Total | % (1) | Total | % (1) | Total | % (1) | Total | Scheduled | Completed | Balance | % (1) | Scheduled | Completed | Balance | % (1) | Scheduled | Completed | Balance | % (1) | Yr 2001 Patrols (1) | 2000 Remaining | 2001 Planned | 2001 Total | 2000 Remaining | 2001 Planned (2) | Total 2001 Planned
Distribution Equipment
Transformers
|  | Overhead | 1 | 2 | 5 | 5 | -- | -- | 456337 | 418018.9605 | 448701.0343 | 0 | 63520.8281 | 134552.9563 | 0 | 456013 | 99.93% | 277 | 0.0607% | 47 | 0.0103% | 456337 | 218 | 192 | 122 | 55.96% | 66 | 711 | 2 | 3.03% | 284 | 903 | 124 | 43.66% | 409729.1327 | 0 | 54219.4703 | 54219.4703 | 124 | 324 | 448
|  | Underground | 1 | 2 | 3 | 3 | -- | -- | 100798 | 94695.1237 | 98833.2069 | 0 | 26580 | 37002 | 0 | 100727 | 99.93% | 71 | 0.07044% | 0 | 0% | 100798 | 47 | 87 | 0 | 0% | 0 | 45 | 0 | 0% | 47 | 132 | 0 | 0% | 95793.2406 | 0 | 25990 | 25990 | 0 | 71 | 71
|  | Pad Mounted | 1 | 2 | 5 | 5 | -- | -- | 107001 | 98156.6071 | 104715.8487 | 0 | 9251 | 16321 | 0 | 106836 | 99.85% | 164 | 0.1533% | 1 | 0.0009346% | 107001 | 122 | 200 | 0 | 0% | 0 | 88 | 0 | 0% | 122 | 288 | 0 | 0% | 98753.8647 | 0 | 21133 | 21133 | 0 | 165 | 165
|  | Sub-Total | [6 empty] | 664136 | 610870.6913 | 652250.0899 | 0 | 99351.8281 | 187875.9563 | 0 | 663576 | 99.92% | 512 | 0.07709% | 48 | 0.007227% | 664136 | 387 | 479 | 122 | 31.52% | 66 | 844 | 2 | 3.03% | 453 | 1323 | 124 | 27.37% | 604276.2381 | 0 | 101342.4703 | 101342.4703 | 124 | 560 | 684
Switching/Protective Devices
|  | Overhead | 1 | 2 | 5 | 5 | -- | -- | 7597 | 6744.8501 | 7430.2706 | 0 | 936.3053 | 2252.0357 | 0 | 7557 | 99.47% | 29 | 0.3817% | 11 | 0.1448% | 7597 | 49 | 60 | 21 | 42.86% | 11 | 74 | 4 | 36.36% | 60 | 134 | 25 | 41.67% | 6559.5166 | 0 | 833.7189 | 833.7189 | 25 | 40 | 65
|  | Underground | 1 | 2 | 3 | 3 | -- | -- | 29796 | 28029.2435 | 29280.424 | 0 | 6115 | 10036 | 0 | 29699 | 99.67% | 92 | 0.3088% | 5 | 0.01678% | 29796 | 93 | 139 | 0 | 0% | 7 | 63 | 0 | 0% | 100 | 202 | 0 | 0% | 28274.3589 | 0 | 9116 | 9116 | 0 | 97 | 97
|  | Pad Mounted | 1 | 2 | 5 | 5 | -- | -- | 6780 | 6092.3983 | 6602.2133 | 0 | 606 | 1645 | 0 | 6757 | 99.66% | 22 | 0.3245% | 1 | 0.01475% | 6780 | 28 | 39 | 0 | 0% | 1 | 6 | 0 | 0% | 29 | 45 | 0 | 0% | 6134.7967 | 0 | 0 | 0 | 0 | 23 | 23
|  | Sub-Total | [6 empty] | 44173 | 40866.4919 | 43312.9079 | 0 | 7657.3053 | 13933.0357 | 0 | 44013 | 99.64% | 143 | 0.3237% | 17 | 0.03849% | 44173 | 170 | 238 | 21 | 12.35% | 19 | 143 | 4 | 21.05% | 189 | 381 | 25 | 13.23% | 40968.6722 | 0 | 9949.7189 | 9949.7189 | 25 | 160 | 185
Regulators
|  | Overhead | 1 | 2 | 5 | 5 | -- | -- | 99 | 71.0095 | 95.6892 | 0 | 17 | 37 | 0 | 99 | 100% | 0 | 0% | 0 | 0% | 99 | 0 | 6 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 6 | 0 | 0% | 61.2169 | 0 | 24 | 24 | 0 | 0 | 0
|  | Underground | 1 | 2 | 3 | 3 | -- | -- | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 100% | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Pad Mounted | 1 | 2 | 5 | 5 | -- | -- | 8 | 6.7937 | 7.8678 | 0 | 0 | 0 | 0 | 8 | 100% | 0 | 0% | 0 | 0% | 8 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | 6.8762 | 0 | 1 | 1 | 0 | 0 | 0
|  | Sub-Total | [6 empty] | 107 | 77.8032 | 103.5569 | 0 | 18 | 37 | 0 | 107 | 100% | 0 | 0% | 0 | 0% | 107 | 0 | 6 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 6 | 0 | 0% | 68.0931 | 0 | 25 | 25 | 0 | 0 | 0
Capacitors
|  | Overhead | 1 | 2 | 5 | 5 | -- | -- | 10744 | 10040.0032 | 10563.0138 | 0 | 165 | 2966 | 0 | 10314 | 96% | 430 | 4.002% | 0 | 0% | 10744 | 251 | 1251 | 0 | 0% | 7 | 210 | 0 | 0% | 258 | 1461 | 0 | 0% | 10007.0397 | 0 | 2151 | 2151 | 0 | 430 | 430
|  | Underground | 1 | 2 | 3 | 3 | -- | -- | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 100% | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Pad Mounted | 1 | 2 | 5 | 5 | -- | -- | 1001 | 946.6836 | 979.1923 | 0 | 73 | 600 | 0 | 950 | 94.91% | 51 | 5.095% | 0 | 0% | 1001 | 5 | 5 | 0 | 0% | 0 | 0 | 0 | 0% | 5 | 5 | 0 | 0% | 964.5287 | 0 | 199 | 199 | 0 | 51 | 51
|  | Sub-Total | [6 empty] | 11745 | 10986.6868 | 11542.2061 | 0 | 246 | 3566 | 0 | 11264 | 95.9% | 481 | 4.095% | 0 | 0% | 11745 | 256 | 1256 | 0 | 0% | 7 | 210 | 0 | 0% | 263 | 1466 | 0 | 0% | 10971.5684 | 0 | 2350 | 2350 | 0 | 481 | 481
| Conductors, Cables | [21 empty] | # of problems |  |  |  | # of problems |  |  |  | # of problems | [7 empty] | # of problems
|  | Overhead (Conductor Miles) | 1 | 2 | 5 | 5 | -- | -- | 167540.5 | 150980.6468 | 164350.371 | 0 | 22258.1012 | 47397.9408 | 0 |  | # of problems | 2206 | N/A | 364 | N/A | 2570 | 700 | 565 | 393 | 56.14% | 211 | 1122 | 8 | 3.791% | 911 | 1687 | 401 | 44.02% | 145920.1718 | 0 | 20383.5268 | 20383.5268 | 401 | 833 | 1234
Circuits |  |  | 1 | 2 | 5 | 5 | -- | -- | 4028 | 3741 | 3964 | 0 | 500 | 1057 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 3687 | 0 | 450 | 450 | N/A | N/A | N/A
Street Lights |  |  | 1 | 2 | -- | -- | -- | -- | 566264 | 566264 | 566264 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 558541 | N/A | N/A | N/A | N/A | N/A | N/A
Wood Poles |  |  | 1 | 2 | -- | -- | 20 | 20 | 1448794 | 1305588.376 | 1421163.3962 | 0 | 60000 | 102991 | 25196 | 1434934 | 99.04% | 11631 | 0.8028% | 2229 | 0.1539% | 1448794 | 383 | 7908 | 0 | 0% | 2208 | 2491 | 97 | 4.393% | 2591 | 10399 | 97 | 3.744% | 1271734.232 | 0 | 50000 | 50000 | 97 | 2939 | 3036
TOTAL | [8 empty] | 2906787.5 | 2689375.696 | 2862950.528 | 0 | 190031.2346 | 356857.9328 | 25196 | 2153894 |  | 14973 |  | 2658 |  | 2171525 | 1896 | 10452 | 536 | 28.27% | 2511 | 4810 | 111 | 4.421% | 4407 | 15262 | 647 | 14.68% | 2636166.9756 | 0 | 184050.7161 | 184051 | 647 | 4973 | 5620
|  |  |  | (1) Planned Inspection quantities are different from 1999 GO 165 Report due to changes in the inventory and the | [11 empty] | (1) Percentage of Total Year End 2000 Inventory. | [6 empty] | (1) Remaining as % of Scheduled | [11 empty] | (1) SCE is required to patrol 93% (100% of urbans & 18% of rurals) of its circuits in 2001 (excluding street lights).
|  |  |  | resultant quantity of required circuit patrols. | [30 empty] | SCE is required to patrol 99% (100% of urbans & no rurals) of its street lights in 2001.
|  |  |  | (2) Completed Patrol Inspections are based on the percentage of total patrolled circuits (excluding street lights). | [30 empty] | (2) Corrective actions planned to be completed in 2001 based on items found through previous inspections.
(3) Remaining underground regulators and capacitors were removed from service, therefore no inventory exists.