STATE OF CALIFORNIA	GRAY DAVIS, Governor

PUBLIC UTILITIES COMMISSION

505 VAN NESS AVENUE

SAN FRANCISCO, CA 94102-3298

August 17, 2001

TO: PARTIES OF RECORD IN RULEMAKING 00-10-002

The following documents are transmitted with this letter:

- A draft decision of Commissioner Wood;

- Attachment A to the draft decision (the report of Exponent titled “Recommendations Regarding Exemptions from Rotating Power Outages”);

- Instructions on how to file and serve comments on the draft decision;

- Reminder on mailing Statement of Authenticity;

- An Assigned Commissioner’s Ruling (ACR) regarding applications by agencies which provide police, fire and prison services; and

- An ACR regarding creation of a special service list.

The draft decision will be on the Commission's September 6, 2001 meeting agenda.  The Commission may act then, or it may postpone action until later.  When the Commission acts on a draft decision, it may adopt all or part of it as written, amend or modify it, or set it aside and prepare its own decision.  Only when the Commission acts does the decision become binding on the parties.

A shortened comment period for the draft decision is adopted.  (Rule 77.7 of the Commission’s Rules of Practice and Procedure.)  As a result, comments on the draft decision must be filed and served by 5:00 p.m. Monday, August 27, 2001.  Only limited service of comments is required, as explained in the instructions on how to file and serve comments.  Reply comments may not be filed and served.

Finally, comments may be filed on the ACR regarding creation of a special service list.  These comments must be in a separate document from comments on the draft decision.  Instructions for service of these comments are stated in the Ruling.

/s/ LYNN T. CAREW

Lynn T. Carew, Chief

Administrative Law Judge

LTC:eap

Attachments

COM/CXW/eap	DRAFT	Item 3

9/6/2001

Decision DRAFT DECISION OF COMMISSIONER WOOD
	      (Mailed August 17, 2001)

BEFORE THE PUBLIC UTILITIES COMMISSION OF THE STATE OF CALIFORNIA

| Order Instituting Rulemaking into the operation of interruptible load programs offered by Pacific Gas & Electric Company, San Diego Gas & Electric Company, and Southern California Edison Company and the effect of these programs on energy prices, other demand responsiveness programs, and the reliability of the electric system. | Rulemaking 00-10-002 (Filed October 5, 2000) |
| --- | --- |

INTERIM OPINION
ON CATEGORY M EXEMPTIONS FROM ROTATING OUTAGES

TABLE OF CONTENTS

Title	Page

INTERIM OPINION ON CATEGORY M EXEMPTIONS FROM ROTATING OUTAGES	1

1.	Summary	2

2.	Background	3

3.	Exponent Report and Results	5

3.1	Methodology and Analysis	5

3.2	Exponent’s Recommendations	8

4.	Discussion	9

4.1	Exponent’s Methodology	9

4.2	Electric Generators	12

4.3	Police, Fire, Prisons	14

4.4	Exponent List Ranked by Public Health and Safety Risk	15

4.5	Skilled Nursing Facilities and Dialysis Treatment Centers	17

4.6	Statement of Authenticity	19

4.7	Incomplete or Late Applications	20

5.	Implementation	21

6.	Expiration in 24 months	22

7.	Notice Before Rotating Outages	24

8.	Limited Service of Attachment A	25

9.	Limited Service of Applications for Rehearing	25

10.	Need for Expedited Consideration	26

11.	Comments on Draft Decision	27

Findings of Fact	27

Conclusions of Law	32

ORDER	34

(Attachment A is on a separate document)	39

Attachment A – “Recommendations Regarding Exemptions from Rotating
Power Outages” prepared by Exponent, August 2001

Attachment B –  Electric Generator Applicants

Attachment C –  Presiding Officer and Assigned Commissioner’s Ruling
dated August 17, 2001 Regarding Treatment of Category M
Applications by Police, Fire and prisons as Applications
for Category A

Attachment D –  Applicants Granted Category M Status

# Summary

Nearly 10,000 customers applied by the June 4, 2001 deadline to be essential customers normally exempt from rotating outages based on public health and safety (Category M).  Those applications are considered in this decision.  Late or incomplete applications are not considered.

We find many of 41 electric generator applicants to be essential customers under essential customer Categories F and K.  (See Attachment B.)  The remaining electric generator applications need further analysis to determine whether or not they are net contributors to their circuit.  Utilities must submit a report regarding circuit net generation for these customers within 30 days.

We treat 51 applications from customers who provide police, fire and prison services as applications for Category A.  We refer these applications to respondent utilities.  (See Attachment C.)

We find 405 customers eligible for Category M.  (See Attachment D.)  Respondent utilities must exempt involved circuits from rotating outages within 10 days of the date of this order, or within 10 days of being notified by the Energy Division Director as additional customers become exempt.  The Category M status granted by this order expires in 24 months.

Customers who have not yet submitted the required Statement of Authenticity are not exempt until they submit this Statement.  They must do so within 60 days of the effective date of the decision, or their eligibility expires.

Respondent utilities must notify Category M customers as circuits are exempted, and 30 days before the Category M status expires.  Utilities must submit certain reports to ensure actions are undertaken promptly, and to permit further Commission action, if necessary.  Finally, we adopt limited procedural modifications to limit otherwise burdensome service of comments, and applications for rehearing.

# Background

By Decision (D.) 01-05-089 adopted on May 24, 2001, the Commission added Category M to the list of essential customers normally exempt from rotating outages.  Category M is: “limited other customers as necessary to protect public health and safety, to the extent exempted by the Commission.”

To facilitate implementation of Category M for Summer 2001, the Commission determined that it was necessary to contract for outside assistance on an expedited basis.  This determination was based on the extraordinary circumstance of alleviating unacceptable jeopardy or imminent danger to the general public health and safety from rotating outages during Summer 2001.  (D.01-05-089, Finding of Fact 2, Conclusion of Law 5.)  The Commission invited competitive bids, and hired Exponent as the consultant and advisor for this project.

To further expedite Category M procedures, the Commission also approved and confirmed a May 21, 2001 Assigned Commissioner’s Ruling (ACR).  (D.01-05-089, Ordering Paragraph 1, mimeo. p 12.)  The ACR established a process to consider non-residential customer requests to be included in Category M.  Further, it directed that Pacific Gas and Electric Company (PG&E), Southern California Edison Company (SCE), and San Diego Gas & Electric Company (SDG&E) each provide direct mail notice of the process to each non-residential customer within four business days of the date of the ruling.

In brief, the adopted process permitted each non-residential customer of PG&E, SCE or SDG&E to file an application seeking Category M essential customer status.  Each applicant was strongly encouraged to submit its application electronically using the form on a Commission web page dedicated to this project.  Applicants without internet access were directed to a toll-free number for further assistance.

Each applicant was required to demonstrate that its inclusion in a rotating outage would present imminent jeopardy or danger to public health and safety.  Applicants were specifically advised that claims of economic harm or inconvenience would not be considered.  Applicants were also advised that each applicant would be required to state under penalty of perjury that the application was true and correct by submission of a Statement of Authenticity.

Further, applicants were informed that the number of customers who may eventually be exempted is severely limited.  As a result, the process included both the review of each application to determine the risks posed to public health and safety, and the prioritization of all applications based on those risks.  Moreover, the adopted process required utilities to analyze the effects on electric system load and reliability if exemptions are granted, and measurement of those results against the Commission’s standard of maintaining at least 40% of all customers eligible for rotating outage.  The process provided for the filing and service of a draft decision upon which applicants and parties could comment.  Finally, the ACR provided that the Commission decision would be based on each petition, the consultant’s report and recommendations, the load/system analysis, any other data or analysis submitted at the Commission’s or consultant’s request, the customer’s verification of the truth of the application, and comments on the draft decision.

Applications were due no later than June 4, 2001.  A total of 9,522 complete applications were filed by that deadline.

Applicants were advised that pleadings filed after June 4, 2001 would be considered only if conditions permit additional exemptions.  A final deadline for late applications was set, with applications permitted only through June 15, 2001.

Exponent’s analysis and report, and this decision, address applications received through June 4, 2001.  Late applications will be considered in a subsequent decision, to the extent system conditions and Commission resources permit.

# Exponent Report and Results

Exponent submitted its report to the Commission on August 9, 2001.  (See Attachment A.)  The report explains in detail the application process, Exponent’s analysis, and Exponent’s recommendations.

## Methodology and Analysis

Exponent applied several tools to rank applicants in order of risk to public health and safety, and identify customers which it recommends be considered for Category M.  First, Exponent developed a numeric risk index score based on self-reported information by each applicant.  The risk index score is based on three health outcome factors: (a) severity, (b) likelihood, and (c) affected population.  These factors are assessed for two outage durations:  (a) less than 2 hours, and (b) 2 to 4 hours.  The values for each health outcome factor are multiplied by the outage duration probability to yield a quantitative risk index score.

Applicants were sorted into 42 business groups.  Applicants already classified by their utility company as essential customers were identified and removed, since these applicants need not be considered further for Category M.  Similarly, applications from electricity generators were identified and removed from further ranking, since these applications are primarily based on contribution to the electricity grid and only indirectly on potential health and safety impacts.

Initial results showed a large degree of variability.  Outlier applicants (i.e., applicants with a risk index score greater than four standard deviations from the mean of their business group) were given follow-up interviews to assess whether or not their facilities faced risks substantially different from those of other applicants in their peer group.  Absent individual justification for a high risk index score, each outlier applicant’s score was adjusted to reflect the upper end of peer group results.

Second, a panel group study and an expert panel review were used to assess risk results.  The panel group and expert review were used because of inherent limitations in relying solely on risk index scores.  Individual applicants, for example, may have overestimated or underestimated adverse health and safety effects, resulting in risk index scores that are relatively too high or too low.  Further, risk index scores rely on a somewhat narrow interpretation of risk.  That is, applicants might make systematic judgments about the level of risk not strictly tied to objective measures.  Instead, perceived (and self-reported) risk might differ from actual risk.

The panel group and expert panel review were used to correct for these limitations.  The panel group was used to make broad judgments about a number of potentially risky situations, in contrast to each applicant judging only their own facility.  Representatives of the various business groups that requested exemption from outages were invited to participate.  Applicants for exemption were not invited.  Thus, participants had knowledge of their industries, but no particular vested interest in the outcome.

An Exponent expert panel also reviewed a subset of application responses regarding reported hazards, and prepared a list summarizing hazards for each business group.  This information was presented and reviewed during the panel group study.  The panel group results were used to assess applicant bias, and tap a range of concerns that influence public attitudes about potential risks.

Third, Exponent identified 51 applicants from the list of 9,522 that are police departments, fire departments or high-security prisons but who are not currently exempt within existing essential customer categories.  Exponent recommends that these applicants be treated independently of their risk index score.

Finally, Exponent individually reviewed the top 2,000 applicants based on calculated risk index scores, and applied 17 screening criteria to further narrow the list.  (See Attachment A, pages 6-1 to 6-5 for the 17 screening factors.)  From this review, 1,595 of the top 2,000 applicants were found to present relatively less risk to public health and safety.  This leaves a list of 405 customers, ranked in order of relative risk to public health and safety.

## Exponent’s Recommendations

Based on its analysis, Exponent recommends that the 51 police, fire and prison applicants not already in an essential customer category be given the highest priority for exemption.  Exponent makes this recommendation since, according to Exponent, the Commission currently grants exemptions to many similar facilities.  Exponent points out, however, that many of these applicants have backup generation and may not need exemption, thereby preserving the number of potentially available exemptions for others.

Further, of the list of 405 customers, Exponent recommends that the Commission grant as many exemptions as possible.  Exponent suggests the Commission base that determination on other influencing factors, such as circuit load analysis and compatibility with earlier Commission decisions.  For example, exemptions should be compatible with prior decisions requiring the maintenance of at least 40% of load available for rotating outage to avoid involuntary load shedding and general system collapse.

Exponent points out that six customers are included in the list of 405 despite being in business groups considered low risk by the focus group (i.e., medical buildings, security, retail).  Exponent includes these customers, however, because upon further analysis Exponent determined that they actually provide services such as outpatient surgery, or communication services to support vital law enforcement activities.  Further, at least one presents a somewhat unique fire/explosion hazard because of a heat treatment manufacturing process.  Exponent concludes that these risks are not easily mitigated by other means.

Finally, Exponent addresses skilled nursing facilities (SNFs) and dialysis treatment centers.  Exponent points out that these two business types were ranked the highest by the panel study group based on their perception of a high likelihood of severe health effect or death in the event of a rotating outage.  Only a few SNFs and dialysis treatment centers are within the list of 405 customers, however, because of low risk index scores based on self-reported information provided by each applicant.  Exponent highlights these two business groups because of the high risk ranking given by the panel group, and the probable underreporting of potential risks.  Exponent recommends that the Commission further investigate the feasibility of exempting these two business groups, despite their apparent low self-reported risk.

# Discussion

## Exponent’s Methodology

Exponent applied a rational and objective methodology to determine relative risk between applicants.  First, Exponent developed a risk index formula based on Exponent’s experience with risk assessment.  Weighting factors were compared to published factors used in other studies to assess reasonableness.  The algorithm was tested before Category M applications were received.  Second, the limitation of relying solely on the calculated risk index score was addressed by follow-up interviews with outlier applicants, along with use of a panel group and an expert panel review.  Third, applicants who could reasonably qualify for essential customer status in a category other than Category M were removed from consideration to focus the limited available exemptions here on those without another course of relief.  Finally, the top 2,000 applications ranked by adjusted calculated risk index score were individually reviewed, and 17 screening criteria were applied to further narrow the list.

The approach was thorough and complete.  It applied the consultant’s expertise, tested against published information.  It utilized verification of data from outliers, assessment based on panel groups, elimination of customers otherwise eligible under other criteria, and screening based on 17 factors.

The 17 factors reasonably apply the results of the panel group, and criteria we endorse.  For example, applicants (other than verified outliers) were found relatively less risky if they are in a business group ranked low in priority by the panel group (e.g., automobile repair shops, financial institutions, convenience stores, grocery stores, manufacturing plants, office complexes, churches).  We agree with the perception of the panel group that these applicants present relatively less risk to public health and safety than do other applicants.

Applicants were found relatively less risky if they have an alternative source of electrical supply (i.e., backup generation) that would cover 100% of an applicant’s critical health and safety needs for more than 2 hours.  We agree with this criterion.  There is little or no need for all ratepayers collectively to protect these customers from rotating outage when these customers can reasonably protect themselves.  As such, these applicants present relatively less risk to public health and safety than do other applicants.

Applicants were ranked lower if they are restaurants or food processing plants whose concerns pertain to food contamination.  We agree, since applicable health codes prohibit the marketing of spoiled or contaminated foods, and methods exist to reasonably assess the risk of foods being spoiled or contaminated (e.g., monitoring of refrigeration temperatures).

Applicants were ranked lower if they are either a water district or water company.  We agree.  Absent a particular entity being a justified outlier, these entities have backup generators or storage facilities, and backflow protection systems, to reasonably mitigate danger to public health and safety from rotating outages of moderate duration.

Applicants were found relatively less risky if they do not provide a time-critical or unique service.  We agree.  For example, customers may be reasonably expected to wait a few hours to have a prescription filled at a pharmacy if the pharmacy is experiencing a rotating outage of up to two hours, or, if urgent, have the prescription filled at another pharmacy or a hospital.  As such, these applicants present relatively less risk to public health and safety than do other applicants.

Applicants were ranked lower if the request is based on traffic control that can be mitigated by following standard traffic safety rules.  We agree.  Not only must citizens be expected to reasonably obey the law in such circumstances, but utilities are under both Commissioner Ruling and Governor Executive Order to provide data to public safety agencies as necessary for the agency to plan its response to rotating outages.  As such, cities can get reasonable information regarding forthcoming outages to dispatch police and other traffic safety personnel to control traffic.

Applicants were found relatively less risky if the danger to public health and safety as represented in the application could be reasonably mitigated by applicant following health codes and Occupational Safety and Health Administration regulations.  We agree.  We expect each business to honor all applicable laws, codes and regulations.  We decline to exempt a customer from rotating outage if that customer is operating outside the law, or could on its own mitigate danger to public health and safety by reasonable application of existing public health and safety provisions in the law.  As such, these applicants present relatively less risk to public health and safety than do other applicants.

The methodology employed by Exponent is reasonable in achieving the desired result.  That result is a list of applicants ranked in order of presenting relative danger or jeopardy to public health and safety if the customer is not classified as an essential customer normally exempt from rotating outage.

## Electric Generators

Early in its analysis, Exponent removed 41 electric generator applicants from further consideration for Category M.  We agree.  These applicants do not present the danger to public health and safety contemplated for successful Category M customers.  Rather, their applications are better analyzed in the context of whether or not they make a positive (or at least neutral) contribution to the system if they are not subject to rotating outages.  Each application must be viewed individually to make that assessment.

For example, a 1 MW generator may be on a circuit that can serve 5 MW.  In this case, all other customers are better off if the entire circuit is subject to rotating outage, with 5 MW available for the rotating outage pool, rather than exclude the 5 MW from rotating outages in order to secure generation of 1 MW.  That is, an exemption from rotating outage for an electric generator is reasonable for all other customers only if the generator can at least meet the needs of the circuit.

Similarly, there are cases where multiple circuits are involved.  Small electric generator applicants may make a neutral or net positive contribution to their individual circuit, but ancillary services may be on another circuit (e.g., control room facilities).  When viewed as a whole on the involved circuits, the generator may or may not make a neutral or positive contribution to the combined circuits, and therefore the grid.

Further, whether these 41 generators are at transmission or distribution level voltage, the load analysis must be consistent with existing treatment of transmission level customers.  That is, we already permit essential customer status for customers served at transmission level voltage when they supply power to the grid in excess of their load at the time of the rotating outage, or their inclusion in rotating outages would jeopardize system integrity.  (Category K of the essential customer list; see D.01-04-006, Attachment C.)

All 41 applications were examined on this basis, and many are found to make reasonable contributions to their circuit, or local combination of circuits, and merit exemption.  On this basis, we grant these applicants essential customer status normally exempt from rotating outage.  These customers are included as essential customers in Category F when at distribution level (i.e., “electric utility facilities…critical to continuity of electric power system operation”), and in Category K when at transmission level.  These customers are listed in Attachment B.

Load and resource analysis continues on a few applicants, as noted in Attachment B.  Each utility shall submit a report within 30 days stating the final load and resource assessment of these remaining few customers.  The report shall be filed, served on the remaining few electric generator customers at issue, and served on a limited list at the Commission composed of Commissioner Wood, Administrative Law Judge (ALJ) Mattson, ALJ Galvin, Jonathan Lakritz, and Laura Martin.  Parties may file and serve comments on the report within 10 days, with service on the respondent utility, plus the same service list as used for the report.

## Police, Fire, Prisons

Exponent recommends that 51 Category M applicants who are police, fire and high security prison customers not already in Category A be given the highest priority for exemption, since, according to Exponent, the Commission currently grants exemptions to many similar facilities.  We generally agree, but believe these applicants, if essential customers, should be included in Category A.

Respondent utilities must already classify qualified police, fire and prison customers as essential customers in Category A, unless a particular customer has adequate backup or standby generation.  (D.82-06-021 (June 2,1982), D.01-04-006, mimeo. page 65.)  We have insufficient information to determine whether or not these Category M applicants previously requested Category A status, but are not included in Category A based on an evaluation by the utility regarding the adequacy of backup or standby generation.  Nonetheless, results reported by Exponent show that several of these customers have backup generation capable of meeting 100% of the customer’s critical health and safety needs for more than 4 hours.  This is adequate backup generation to eliminate each such customer from Category A, absent a particularly compelling reason to the contrary in any specific case.

If these customers are qualified police, fire and high security prisons without adequate standby or backup generation, they should be included in Category A.  If they do not qualify for Category A, however, we are not persuaded that they present sufficient imminent jeopardy or danger to public health and safety if exposed to rotating outages to qualify for Category M.

By ACR dated August 17, 2001, respondent utilities were directed to treat these 51 Category M applications as applications for Category A.  (See Attachment C.)  We approve and confirm that ACR.  (Pub. Util. Code Section 310.)  Respondent utilities should include these 51 customers in Category A to the extent they are police, fire or prison customers without adequate backup or standby generation.  (See Table 7-1 of Attachment A for a list of the 51 police, fire and high security prison applicants.)

## Exponent List Ranked by Public Health and Safety Risk

Exponent recommends that the Commission exempt as many of the 405 customers as possible of those ranked by Exponent in order of relative risk to public health and safety.  We agree.  Exponent’s list represents a reasonable relative ranking of customers presenting imminent danger or jeopardy to public health and safety if exposed to rotating outages.  We are persuaded that these customers present sufficient relative risk to merit inclusion in Category M to the fullest extent possible.

We have previously determined that each utility must maintain at least 40% of its load available for rotating outages to avoid involuntary load shedding and general system collapse.  (D.82-06-021, D.01-04-006, D.01-06-085.)  We continue to apply this criterion here.

Respondent utilities and Commission staff analyzed the effect on load and resources of exempting up to the full list of 405 customers.  The analysis shows that all 405 customers are able to be included in Category M without jeopardizing the 40% limit for each utility.  Customers whose applications for Category M status are granted are listed in Attachment D.  As discussed more below, applicants who have not yet submitted a Statement of Authenticity are granted Category M status conditioned upon their submitting a Statement within 60 days.

A few applications remain for further consideration based on processing difficulties.  For example, some applicants appear to have transposed utility account numbers, or used a gas account number rather than an electricity account number.  Staff is working with each respondent utility to determine whether each such applicant is a valid customer, or that the correct account number or other information is available to ensure an applicant granted Category M status can be properly included by the utility.  Those applicants are identified within Attachment D, and are included in Category M conditioned upon successful resolution of these processing difficulties.  Staff and utilities should complete that effort within 30 days.

If the status of any applicant is unresolved at the end of 30 days, the respondent utility should file and serve a report.  The report should state the customer name, unresolved issue, estimated time to resolve the issue, and the utility’s recommendation.  The report should be served on the involved customer, and the following persons at the Commission: Commissioner Wood, ALJ Mattson, ALJ Galvin, Jonathan Lakritz, and Laura Martin.  Comments on the report may be filed and served within 10 days of the date of the report.  Service should be on the respondent utility, and the same persons identified above at the Commission.

## Skilled Nursing Facilities and Dialysis Treatment Centers

Exponent recommends that the Commission further investigate the feasibility of exempting all SNFs and dialysis treatment centers.  We adopt this recommendation.

California has more than 1,200 SNFs.  (Reporter’s Transcript, March 22, 2001, Volume 3, page 399.)  These facilities are located throughout the state.  Each SNF is located on a circuit different from the circuit serving another SNF, with few, if any, exceptions.  Exempting more than 1,200 SNFs would exempt nearly, if not exactly, that same number of circuits, along with the load of other customers on the same circuit as the SNF.  Retaining at least 40% of load for rotating outages does not allow including all SNFs in Category M at this time.

From the total candidate population of these two customer types, we received Category M applications from 568 SNFs and 220 dialysis treatment centers.  Exponent’s list of 405 customers recommended for Category M includes 88 SNFs and 29 dialysis treatment centers.  Granting Category M to the 405 (including 88 SNFs and 29 dialysis treatment centers) leaves 671 applicants from these two customer types.  We are unable to grant Category M status for these 671 applicants, since there is insufficient margin left to exempt another 671 customers in addition to the 405 (i.e., expanding the number of exempt customers by 166%, from 405 to 1076).

Nonetheless, 88 SNFs and 29 dialysis treatment center are given Category M status as part of the 405.  Even with some self-reporting bias, we think SNF and dialysis treatment center applicants generally reported risk relative to other SNFs and dialysis treatment centers that allowed Exponent to reasonably rank these applicants relative to each other, and relative to the other applicants within the group of 405.

We are concerned, however, that the population within SNFs and dialysis treatment centers is among the most vulnerable in our society.  Some of these patients would have been in acute care hospitals a few years ago, but are now discharged to SNFs and outpatient treatment centers.

We must for now maintain the pool of at least 40% of load from which to draw for rotating outage to prevent widespread and generalized system collapse.  We do this for the good of all electricity customers, including SNFs and dialysis treatment centers, and for the overall public health and safety.

We may, however, have the opportunity to later explore other options to address risks from rotating outages.  This may include application of a rotating outage pool percentage lower than 40%, given changes in technology and risk assessment.  Further, utilities are rewiring some circuits to make more circuits available for rotating outage.  This may in the future allow exemption of additional customers not now exempt.  Also, we may subsequently take the initiative to re-examine customers now identified as essential in Categories A-L, and N.  For example, we may re-examine application of the backup and standby generation criterion, resulting in removal of some customers now classified as essential.  We may also evaluate the ability of some customers now classified as essential to withstand outages caused by accidents, earthquakes and other natural disasters.  If certain customers are able to reasonably withstand such events, we may conclude that they can withstand temporary electricity outages from rotating outages.  This may allow exemption of additional customers not now exempt.

## Statement of Authenticity

We have received a Statement of Authenticity, where necessary, from most, but not all, applicants.  We consider denying the applications of those who have failed to provide this Statement by the date due, but decline to do so.  Rather, we think it reasonable to grant applicants a limited amount of additional time to comply with this administrative detail.

Attachments B and D show whether Statements of Authenticity have or have not been received from those applicants to whom we grant essential customer status.  Where a Statement has not yet been received, we grant that applicant essential customer status conditioned upon that applicant submitting a Statement within 60 days.

A period of 60 days is a reasonable amount of time for this administrative—but important—detail to be resolved, while providing some finality to the process.  We authorize the Assigned Commissioner or the ALJ to permit deviations from the 60-day time limit for good cause in an individual case, but the threshold to justify a deviation must be very high.  That is, we expect any deviations to be limited to truly exceptional situations, and that this portion of the process will be concluded without unreasonable delay.

## Incomplete or Late Applications

Only complete applications submitted by June 4, 2001 are considered for Category M in this decision.  Incomplete applications, or applications submitted after the June 4, 2001 deadline, are not considered at this time.  We are unable to consider incomplete or late applications due to the large number of applications; limited resources available to process applications; limited resources to do follow-up interviews on applications generally; inability to do follow-up interviews on incomplete applications due to limited resources, with very few exceptions (e.g., transposed account number on the final list of 405 customers); and the limited time for reaching a decision for Summer 2001.

We further clarify that we will not devote resources to consideration of any incomplete applications.  The burden reasonably rested with applicants to submit a complete application by June 4, or late by June 15. A toll-free telephone number was available for applicants to call with questions.  The application could be completed in parts, with answers updated or modified, until the application was complete.  In fact, electronic submission was permitted only when the form was complete.  Applicants submitting their form by fax or mail could review their form to ensure that was complete, accurate and fully representative of their situation before its submission.  On balance, the best use of resources while meeting the goal of promoting public health and safety does not justify consideration of any incomplete applications.

While we will not consider incomplete applications, we may later consider complete applications received after June 4, 2001, but before June 15, 2001.  Subsequent consideration of late applications, if any, however, will depend upon the availability of Commission resources to process and consider late applications, and whether or not the electric system permits additional exemptions (e.g., at least 40% of system load remains available for rotating outage).  Further, it will depend upon whether or not the electricity crisis continues, with a reasonably high probability of rotating outages, thereby necessitating continuation of the Category M process.

# Implementation

This order is effective immediately.  We understand, however, that it may take a reasonable amount of time for utilities to identify circuits, and make changes necessary to ensure that rotating outages do not occur on the circuits of customers added to the essential customer group herein.  Nonetheless, we expect utilities to make these changes effective no later than 10 days of the date of this order.  Further, as customers are added upon submission of their Statements of Authenticity, respondent utilities shall exempt the circuits of those added customers within 10 days of the date notified by the Energy Division Director that the Statement has been received.

A period of 10 days for respondent utilities to accomplish these changes is reasonable.  This decision was issued as a draft for comment in mid-August 2001.  Utilities at that time may have begun to make implementation plans based on knowing the customers proposed to be found essential.  Further, the urgent need to provide reasonable protection to public health and safety based on the final list of those awarded Category M status requires that each utility apply all necessary and reasonable efforts to make the required changes without delay.

Each respondent utility unable to implement all required circuit modifications within 10 days must file and serve a report.  The report must state the name of the customer granted essential customer status herein whose circuit has not yet been exempted from rotating outages, the reason, an estimate of when the change will become effective, the utility’s recommendation, and anything else reasonably needed for the Commission to assess the matter.  The report must be filed, served on 5 individuals at the Commission (i.e., Commissioner Wood, ALJ Mattson, ALJ Galvin, Jonathan Lakritz, Laura Martin), and served on each Category M customer affected by the delay.  Comments on the report may be filed and served within 10 days of the date of the report.  Service of comments should be on the respondent utility, and the same persons identified above at the Commission.

# Expiration in 24 months

The Category M status granted today will expire in 24 months.  We do this for several reasons.

First, Category M was established due to circumstances in the electricity market requiring extraordinary steps to protect public health and safety.  As Governor Gray Davis stated in his January 17, 2001 Proclamation of a State of Emergency, electricity shortages had resulted in blackouts affecting millions of Californians.  Further, the Governor stated that the imminent threat of widespread and prolonged disruption of electricity constituted a condition of extreme peril to the safety of persons and property within California.

This condition, however, is not expected to be indefinite.  Rather, due to actions by the Governor, this Commission, and others, we expect within 2 years to return to an electricity market that can operate reasonably well without the need for extraordinary measures.

Second, each customer awarded Category M status today should take steps to reduce or eliminate any significant risk to public health and safety which occurs if that customer is exposed to an outage from any cause, including weather, accidents, or supply shortages.  That is, despite the cause, frequency, or duration, customers should take reasonable steps in the next 24 months to reduce any risk they present to public health and safety if they experience an outage.

Third, notification procedures for rotating outages (as discussed more below) are improving, and will continue to improve with experience and need.  Better and more timely notification before rotating outages provides the opportunity for businesses to take necessary steps to mitigate or eliminate any jeopardy to public health and safety.  This should reduce, if not eliminate, the need for the total exemption granted Category M customers.

Fourth, we do not want Category M status to forever remove incentives for Category M customers to make health and safety modifications to their operations.  It is reasonable in these particularly difficult and troubled times to protect public health and safety by excusing some customers from rotating outages.  This sensibly transfers the relative risk presented by some businesses to all customers.  In the long run, however, we want each business itself to be exposed to the risk it places on the community in which it operates, and have the incentive to take whatever steps are reasonable to mitigate or eliminate that risk.

Finally, customers change as economic conditions evolve and time passes.  New businesses enter the market, other businesses depart; some businesses grow, others contract; some businesses merge, others divest parts into new companies; and existing businesses may change the amount or type of activity that jeopardizes public health and safety.  The award of Category M status should not be a government benefit that accrues indefinitely to only a select group of individually named customers.  It should not become part of the economic worth of some businesses, and not others.  Rather, the status awarded today is intended to address relative risk for some customers during a temporary State of Emergency.

Therefore, we limit Category M status awarded today to a period of no more than 24 months.  We will not at that time eliminate Category M itself, since use of the category may continue to be necessary at intermittent times.  Absent a specific Commission order to the contrary, however, Category M status granted today will expire in 24 months.

We direct each respondent utility to individually notify each customer granted Category M essential customer status in today’s order that the customer’s circuit is, or will become, exempt from rotating outages.  In that same notice, the utility must inform the customer that such status will expire in 24 months.  Further, 30 days before the expiration of Category M status, each respondent utility shall notify each customer granted this status that such status will expire 30 days after the date of that notice, absent a specific Commission order to the contrary.

# Notice Before Rotating Outages

Several approaches are available to assist business customers reduce or eliminate danger or jeopardy to public health and safety when exposed to a rotating outage.  Category M is one method.  Another is advance notification.

The California Independent System Operator (ISO) now provides forecasts both 48 hours, and 24 hours, in advance of expected rotating outages.  The ISO provides frequent updates to the public during periods of forecast electricity emergencies.  The ISO also notifies utilities and public agencies one hour in advance of any firm load curtailment.  Each utility is in turn required to notify the public and the media no less than one hour in advance of any reduction in electricity output, including the time and location where the anticipated blackout will occur.  (Executive Order D-38-01.)

Individual customers may also receive energy alerts regarding Stage 1, 2 and 3 emergencies.  Customers may register on the State of California home page (http://my.ca.gov/wireless) to receive wireless notifications of energy alerts via pager, cell phone, or hand-held personal digital assistant.  (Governor’s Press Release, PRO1:323, dated July 10, 2001.)  As experience is gained with this system, and improvements are made, if necessary, this advance notification is, and will become, a powerful tool to reduce and manage risk to public health and safety from outages.

Because we are unable to provide Category M status to all applicants, we are pleased that other tools are available to mitigate or eliminate danger to public health and safety.  We encourage all applicants denied Category M status to take advantage of the new real-time electronic system for advance notification.

# Limited Service of Attachment A

The draft decision of Commissioner Wood was served on all of the approximately 10,000 Category M applicants, as well as about 200 on the Phase 1 service list.  The draft decision included a complete copy of the Exponent Report (Attachment A).  Attachment A is in excess of 200 pages.

We do not include a copy of Attachment A with service of paper copies of the final decision because each Category M and Phase 1 party has already received a copy of the Exponent Report.  Not serving paper copies of exactly the same document a second time will save substantial cost and administrative burden.

# Limited Service of Applications for Rehearing

By D.01-08-018, we limited service of comments on the Category M draft decision.  We did this because requiring a party filing a comment to serve that comment on nearly 10,000 other parties would be unreasonably burdensome, and provide little benefit.  We do the same for applications for rehearing of this order.

That is, a party seeking rehearing of this order must apply for rehearing within 30 days.  (Public Utilities Code Section 1731(b).)  The application for rehearing must be filed and served.  (Rule 85 of the Commission’s Rules of Practice and Procedure.)  Service must be on all parties to the proceeding.  (Rule 85.)   We may, however, liberally construe our rules to secure just, speedy and inexpensive determination of the issues presented.  (Rule 87.)

Service of an application for rehearing in this proceeding would require service of a copy on nearly 10,000 parties.  That is unreasonable.  Therefore, we limit service of applications for rehearing to only the applicant’s serving utility (e.g., PG&E, SCE or SDG&E) and the following persons at the Commission:  Commissioner Wood, General Counsel Cohen, ALJ Mattson, ALJ Galvin, Jonathan Lakritz, and Laura Martin.

# Need for Expedited Consideration

Rule 77.7(f)(9) of the Commission’s Rules of Practice and Procedure provides in relevant part that:

“…the Commission may reduce or waive the period for public review and comment under this rule…for a decision where the Commission determines, on the motion of a party or on its own motion, that public necessity requires reduction or waiver of the 30-day period for public review and comment.  For purposes of this subsection, "public necessity" refers to circumstances in which the public interest in the Commission adopting a decision before expiration of the 30-day review and comment period clearly outweighs the public interest in having the full 30-day period for review and comment.  "Public necessity" includes, without limitation, circumstances where failure to adopt a decision before expiration of the 30-day review and comment period…would cause significant harm to public health or welfare.  When acting pursuant to this subsection, the Commission will provide such reduced period for public review and comment as is consistent with the public necessity requiring reduction or waiver.“

We balance the public interest in quickly finding limited customers eligible for Category M against the public interest in having a full 30-day comment cycle on the proposed modification.  We conclude that the former outweighs the latter. Category M serves to protect public health, safety and welfare.  Any delay in placing customers in Category M jeopardizes public health, safety and welfare by increasing the risk of those customers experiencing rotating outages.  We seek valuable public review of, and comment on, our proposed change, and find that a reduced period balances the need for that input with the need for timely action.

# Comments on Draft Decision

On August 17, 2001, the draft decision of Presiding Officer and Assigned Commissioner Wood on this matter was filed and served on parties in accordance with Section 311(g) of the Public Utilities Code and Rule 77.7 of the Rules of Practice and Procedure.  Comments were filed and served on August 27, 2001.

Findings of Fact

- Exponent applied a rational and objective methodology to determine relative risk between applicants using a risk index formula based on Exponent’s experience with risk assessment, weighting factors which were compared to published factors used in other studies, and an algorithm that was tested before any Category M applications were received.

- The limitation of relying solely on the calculated risk index score was addressed by follow-up interviews with outlier applicants, and use of a panel group, and an Exponent expert panel.

- Applicants who could reasonably qualify for essential customer status in a category other than Category M were removed from consideration to focus the limited available Category M exemptions on those without another course of relief.

- The top 2,000 applications ranked by adjusted calculated risk index score were individually reviewed, and 17 screening criteria were applied to further narrow the list.

- The 17 screening factors apply the results of the panel group.

- Applicants (other than verified outliers) are relatively less risky if they are in a business group ranked low in priority by the focus group (e.g., automobile repair shops, financial institutions, convenience stores, grocery stores, manufacturing plants, office complexes, churches).

- Applicants are relatively less risky if they have an alternative source of electrical supply (i.e., backup generation) that covers 100% of an applicant’s critical health and safety needs for more than 2 hours.

- Applicants are relatively less risky if they are restaurants or food processing plants whose concerns pertain to food contamination since health codes prohibit the sale of spoiled or contaminated foods, and means exist to assess such food risks.

- Applicants are relatively less risky if they are either a water district or water company since backup generation, storage facilities and backflow protection systems mitigate risk to the public.

- Applicants are relatively less risky if they do not provide a time-critical or unique service.

- Applicants are relatively less risky if the request is based on traffic control that can be mitigated by following standard traffic safety rules.

- Applicants are relatively less risky if the potential danger to public health and safety can be reasonably mitigated by applicant following health codes, and Occupational Safety and Health Administration regulations.

- Exponent’s methodology achieves the desired result of a list of applicants ranked in order of presenting relative danger or risk to public health and safety if the customer is not classified as an essential customer normally exempt from rotating outage.

- Electric generator applicants do not present the same danger to public health and safety as other applicants for Category M.

- An exemption from rotating outage for an electric generator is reasonable for all other customers only if the generator can at least meet the needs of the circuit, or limited circuits where more than one electric generator applicant provides electricity.

- Respondent utilities must already classify qualified customers providing police, fire and prison services as essential customers in Category A, unless a particular customer has adequate backup or standby generation.

- Several police, fire and prison applicants have backup generation capable of meeting 100% of the customer’s critical health and safety needs for more than 4 hours.

- Exponent lists 405 customers by relative ranking of those presenting imminent danger or jeopardy to public health and safety if exposed to rotating outages.

- Each utility must maintain at least 40% of its load available for rotating outages to avoid involuntary load shedding and general system collapse.

- Exempting all 405 customers recommended for Category M by Exponent will not jeopardize the minimum 40% load available for rotating outage criterion.

- California has more than 1,200 SNFs located throughout the state, with each SNF located on a circuit different from the circuit serving another SNF, with few, if any, exceptions.

- Exempting more than 1,200 SNFs would exempt nearly, if not exactly, that same number of circuits, along with the load of other customers on the same circuit as the SNF.

- Retaining at least 40% of load for rotating outage does not allow including all SNFs in Category M at this time.

- Exponent’s list of 405 customers recommended for Category M includes 88 SNFs and 29 dialysis treatment centers.

- Category M status cannot be given to 671 SNF and dialysis treatment center applicants beyond those included in the 405, since there is insufficient margin left to exempt another 671 customers in addition to the 405.

- A toll-free telephone number was available for applicants to call with questions.

- Electronic submission of the application was permitted only when the form was complete.

- Applicants submitting their form by fax or mail could review their form to ensure that was complete, accurate and fully representative of their situation before its submission.

- The burden rested with applicants to submit a complete application by June 4, or late by June 15.

- Category M was established due to circumstances in the electricity market requiring extraordinary steps to protect public health and safety, but these circumstances are expected to be temporary.

- Actions taken by the Governor, this Commission, and others, will likely return the electricity market within 2 years to one that can operate reasonably well without the extraordinary steps taken by this Commission and others.

- Electrical outages have many causes, including weather, accidents, or supply shortages.

- Customers change as economic conditions evolve and time passes.

- The ISO provides forecasts both 48 hours, and 24 hours, in advance of expected rotating outages, with frequent updates to the public during periods of forecast electricity emergencies, and notifies utilities and public agencies one hour in advance of any firm load curtailment.

- Each utility is in turn required to notify the public and the media no less than one hour in advance of any reduction in electricity output, including the time and location where the anticipated blackout will occur.

- Individual customers may also receive energy alerts regarding Stage 1, 2 and 3 emergencies by registering on the State of California home page to receive wireless notifications of energy alerts via pager, cell phone, or hand-held personal digital assistant.

- Notification procedures for rotating outages are improving, and will continue to improve with experience and need.

- Better and more timely notification before rotating outages provides the opportunity for businesses to take necessary steps to mitigate or eliminate any jeopardy to public health and safety.

- As notification improves, the need for the total exemption granted Category M customers will lessen, if not end.

- The draft decision of Commissioner Wood was served on all of the approximately 10,000 Category M applicants, as well as approximately 200 parties and persons on the Phase 1 service list, and included a complete copy of the Exponent Report (Attachment A), which is in excess of 200 pages.

- Not serving paper copies of exactly the same document a second time will save substantial cost and administrative burden.

- Service of an application for rehearing in this proceeding would require service of a copy on nearly 10,000 parties.

- The public interest in quickly finding limited customers eligible for Category M outweighs the public interest in a full 30-day period for public review and comment.

Conclusions of Law

- Electric generator applicants should normally be exempt from rotating outage only if the exemption results in their making a positive (or at least neutral) contribution to the system absent being subject to rotating outages.

- Electric generators listed in Attachment B, upon completion of load/resource analysis showing they are net contributors, should be treated as essential customers normally exempt from rotating outage in Category F or K, with utilities filing a report on final load analysis in 30 days on those applicants where the analysis is continuing.

- The 51 Category M applicants listed in Exponent’s Table 7-1 who are police, fire and high security prison customers not already in Category A should be included in Category A if they are otherwise essential police, fire or prison customers without adequate standby or backup generation.

- Absent a particularly compelling reason to the contrary, an applicant able to meet 100% of its critical health and safety needs for more than 4 hours by using standby or backup generation should not be included in Category A.

- The ACR dated August 17, 2001, should be approved and confirmed.

- All of the 405 customers recommended by Exponent for Category M should be included in Category M.

- Customers listed in Attachment D who have unresolved processing difficulties should be granted Category M status conditioned upon their successful resolution of the processing difficulty.

- Customers listed in Attachments B and D who have not yet submitted a Statement of Authenticity should be granted essential customer status conditioned upon their submitting a Statement of Authenticity within 60 days.

- The Assigned Commissioner or the ALJ should be delegated authority to permit deviations from the 60-day time limit for submission of a Statement of Authenticity, but deviations should be only for good cause in an individual case with the threshold to justify a deviation very high.

- Respondent utilities should exempt the circuits of those customers added to Category M no later than 10 days of the date of this order.

- As customers are added upon submission of their Statements of Authenticity, respondent utilities should exempt the circuits of those added customers within 10 days of the date notified by the Energy Division Director that the Statement has been received.

- Each respondent utility unable to effectuate today’s order within 10 days, as required, should file and serve a report, stating the name of each customer granted essential customer status herein whose circuit has not yet been exempted from rotating outages, the reason it has not yet been exempted, and an estimate of when the change will become effective.

- The Category M status awarded today should be intended to address relative risk for some customers during a temporary State of Emergency that should expire within 24 months.

- Each respondent utility should individually notify each customer granted Category M essential customer status in today’s order that the customer’s circuit is, or will become, exempt from rotating outages, and state in the same notice that such status will expire in 24 months.

- Thirty days before the expiration of Category M status, each respondent utility should notify each customer granted Category M essential customer status that the Category M status will expire 30 days after the date of that notice, absent a specific Commission order to the contrary.

- A copy of the Exponent Report (Attachment A) should not be included with service of paper copies of the final decision because each Category M and Phase 1 party received a copy of the Exponent Report with the draft decision.

- Service of copies of applications for rehearing should be limited to the applicant’s serving utility (e.g., PG&E, SCE or SDG&E) and the following persons at the Commission:  Commissioner Wood, General Counsel Cohen, ALJ Mattson, ALJ Galvin, Jonathan Lakritz, and Laura Martin.

- The period for public review and comment on the draft decision should be reduced, pursuant to Rule 77.7(f)(9).

- This order should be effective today so that customers may be included in Category M without delay.

ORDER

IT IS ORDERED that:

- Electric generator customers identified in Attachment B, other than those for whom load and resource analysis continues (as shown in Attachment B), are granted essential customer status in Category F (for distribution level customers) or K (for transmission level customers).  Respondent utilities Pacific Gas and Electric Company (PG&E) and Southern California Edison Company (SCE) shall submit a report within 30 days stating the final load and resource assessment for customers shown in Attachment B where this analysis is not yet complete.  The report shall be filed, served on the electric generator customers at issue, and served on a limited list at the Commission composed of Commissioner Wood, Administrative Law Judge (ALJ) Mattson, ALJ Galvin, Jonathan Lakritz, and Laura Martin.  Parties may file and serve comments on the report within 10 days, with service on the respondent utility, and service on the same service list as used for the report.

- The August 17, 2001 Assigned Commissioner’s Ruling (Attachment C) is approved and confirmed.  Respondent utilities PG&E, SCE, and San Diego Gas and Electric Company (SDG&E) shall treat Category M applications by 51 customers who provide police, fire, and prison services (Table 7-1 in Exponent Report, Attachment A) as applications for Category A, and consider these applications without unreasonable delay.  Respondent utilities shall evaluate the adequacy of standby or backup generation of each of the 51 applicants, and not include any applicant for Category A who has adequate backup or standby generation.

- Respondent utilities shall include all customers listed in Attachment D as essential customers in Category M.  Where Attachment D shows a processing difficulty remains, the customer is granted Category M status conditioned upon satisfactory resolution of the processing difficulty.  If the status of an applicant is unresolved at the end of 30 days, the respondent utility whose customer is at issue shall file and serve a report.  The report shall state the customer’s name, unresolved issue, estimated time to resolve the issue, the utility’s recommendation, and anything else reasonably needed for the Commission to assess the matter.  The report shall be served on the involved customer, and the following persons at the Commission: Commissioner Wood, ALJ Mattson, ALJ Galvin, Jonathan Lakritz, and Laura Martin.  Comments on the report may be filed and served within 10 days of the date of the report.  Service of comments shall be on the respondent utility, and the same persons identified above at the Commission.

- Where Attachments B and D show a Statement of Authenticity has not been filed, the essential customer status is granted upon the condition that applicant submits a Statement of Authenticity within 60 days.  The Assigned Commissioner or Administrative Law Judge may grant a motion for limited extension of the 60-day time limit to submit a Statement of Authenticity for good cause in individual cases.  The essential customer status conditionally granted herein shall expire at the end of 60 days if a Statement of Authenticity has not been received, unless a motion for extension has been granted.

- Respondent utilities shall, within 10 days of today, effectuate the Category M status granted herein by removing from rotating outage the circuit upon which each such customer granted such status is served.  Respondent utilities shall effectuate the Category M status conditionally granted herein upon resolution of a processing difficulty within 10 days of the date the processing difficulty is resolved.  Respondent utilities shall effectuate the Category M status conditionally granted herein within 10 days of the date of a letter from the Energy Division Director reporting receipt of a Statement of Authenticity.  Each respondent utility unable to effectuate circuit exemption shall file a report within 15 days of today, or 15 days of the date circuit exemption is required upon resolution of processing difficulties or late Statements of Authenticity.  The report shall state the name of each customer granted essential customer status herein whose circuit has not yet been exempted from rotating outages, the reason, an estimate of when the change will become effective, the utility’s recommendation and anything else reasonably needed for the Commission to assess the matter.  The report must be filed, served on 5 individuals at the Commission (i.e., Commissioner Wood, ALJ Mattson, ALJ Galvin, Jonathan Lakritz, Laura Martin), and served on each Category M customer affected by the delay.  Comments on the report may be filed and served within 10 days of the date of the report.  Service of comments shall be on the respondent utility, and the same persons identified above at the Commission.

- Category M status granted herein shall expire 24 months from today, unless by specific order the Commission directs otherwise.

- Respondent utilities shall notify each customer granted Category M essential customer status in this order that the customer’s circuit is, or will become, exempt from rotating outages.  In that same notice, the utility must inform the customer that such status will expire in 24 months.  Further, 30 days before the expiration of Category M status, each respondent utility shall notify each customer granted Category M essential customer status that Category M status will expire 30 days after the date of that notice.

- Attachment A shall not be included with paper copies of this decision served on the service list.

- Applications for rehearing must be filed (original plus four copies) and served within 30 days of the date this order is mailed, but service shall be limited to applicant’s serving utility and the following persons at the Commission: Commissioner Wood, General Counsel Cohen, ALJ Mattson, ALJ Galvin, Jonathan Lakritz, and Laura Martin.

- This proceeding remains open.

This order is effective today.

Dated 				, at San Francisco, California.

ATTACHMENT A

“Recommendations Regarding Exemptions from
Rotating Power Outages” prepared by Exponent
August 2001

(Attachment A is a separate document.  
Please see separately enclosed document)

ATTACHMENT B

Electric Generator Applicants

| Line No. | FW | Application No. | Company Name | Utility | Net Generator Yes/No | Statement of Authenticity Yes/No |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | * | 280169 | Enron Wind | SCE | 1 Yes; 1 No | No |
| 2 |  | 402392 | Enron Wind | SCE | No | No |
| 3 |  | 1193408 | Enron Wind | SCE | Yes | No |
| 4 |  | 1273059 | Enron Wind | SCE | No | No |
| 5 | * | 1419390 | Enron Wind | SCE | No | No |
| 6 | * | 1499150 | Enron Wind | SCE | No | No |
| 7 |  | 1820849 | Enron Wind | SCE | Yes | No |
| 8 | * | 2067736 | Enron Wind | SCE | No | No |
| 9 |  | 2157763 | Enron Wind | SCE | Yes | No |
| 10 |  | 2179692 | Enron Wind | SCE | Yes | No |
| 11 | * | 2749957 | Enron Wind | SCE | No | No |
| 12 |  | 3029193 | Enron Wind | SCE | No | No |
| 13 |  | 3669146 | Enron Wind | SCE | Yes | No |
| 14 |  | 3816503 | Enron Wind | SCE | Yes | No |
| 15 | * | 3917101 | Enron Wind | SCE | No | No |
| 16 | * | 4050921 | Enron Wind | SCE | 1 Yes; 1 No | No |
| 17 |  | 5445879 | Enron Wind | SCE | No | No |
| 18 |  | 5529040 | Enron Wind | SCE | No | No |
| 19 |  | 6097386 | Enron Wind | SCE | Yes | No |
| 20 | * | 6741503 | Enron Wind | SCE | No | No |
| 21 |  | 6781023 | Enron Wind | SCE | Yes | No |
| 22 |  | 6964543 | Enron Wind | SCE | No | No |
| 23 | * | 7004717 | Enron Wind | SCE | No | No |
| 24 |  | 7024248 | Enron Wind | SCE | Yes | No |
| 25 | * | 7769335 | Enron Wind | SCE | No | No |
| 26 | * | 7813128 | Enron Wind | SCE | No | No |
| 27 |  | 7977923 | Enron Wind | SCE | Yes | No |
| 28 | * | 8188799 | Enron Wind | SCE | No | No |
| 29 | * | 9602678 | Enron Wind | SCE | 1 Yes; 1 No | No |
| 30 | * | 9702580 | Enron Wind | SCE | No | No |
| 31 |  | 9860857 | Enron Wind | SCE | Yes | No |
| 32 | * | 6344622 | Enron Wind | SCE | No | No |
| 33 | * | 4838841 | Enron Wind | SCE | 1 Yes; 1 No | No |
| 34 |  | 8136461 | Zond System – Monolith XII | SCE | Yes | No |
| 35 |  | 4125689 | Luz Solar Partners VIII & IX | SCE | No | No |
| 36 | * | 4287846 | CTV Management Group | SCE | 1 Yes; 1 No | No |
| 37 |  | 5254076 | Daniel M. Bates (Deer Creek Hydro) | SCE | No | No |
| 38 | * | 5772417 | CTV Management Group | SCE | 1 Yes; 1 No | No |
| 39 |  | 7511461 | Zond Systems Inc. | PG&E | No | No |
| 40 | * | 7560747 | CTV Management Group | SCE | 1 Yes; 1 No | No |
| 41 |  | 9074877 | Zond Systems Inc. | PG&E | Yes | No |

FW:  Further Work.  An asterisk denotes unknown circuit and/or invalid account number, and where the load and resources analysis is not yet complete.  Essential customer status is not granted to these customers.

Net generator:  Some applications included two accounts, with one account a net generator, and the other not a net generator.

(END OF ATTACHMENT B)

ATTACHMENT C

See separately enclose document titled: “Presiding Officer and Assigned Commissioner’s Ruling Directing Respondent Utilities to Treat Category M Applications by Police, Fire and Prisons as Applications for Category A.”

ATTACHMENT D

Applicants Granted Category M Status

| Line No. | FW | Application No. | Company Name | Utility | Business | Statement of Authenticity Yes/No |
| --- | --- | --- | --- | --- | --- | --- |
| 1 |  | 7726153 | First Responder EMS, Inc. | PG&E | Emergency Services | No |
| 2 |  | 2945880 | Sequoia Safety Council, Inc. | PG&E | Emergency Services | No |
| 3 |  | 4946764 | Port of Oakland | PG&E | Transportation | No |
| 4 |  | 1826037 | State of California - CALTRANS | SCE | Transportation | No |
| 5 |  | 7161730 | City of Victorville | SCE | Government | No |
| 6 |  | 177173 | REIT Management & Research, Inc. | SDG&E | Security | No |
| 7 |  | 2617816 | Casa Pacifica Youth Connection | SCE | Emergency Services | Yes |
| 8 |  | 331744 | Quest Diagnostics | PG&E | Labs/Blood | No |
| 9 |  | 3714770 | Westcliff Medical Laboratories, Inc. | SCE | Labs/Blood | No |
| 10 |  | 685138 | Central California Blood Center | PG&E | Labs/Blood | No |
| 11 |  | 4862994 | Central California Blood Center | SCE | Labs/Blood | No |
| 12 |  | 1696490 | Central California Blood Center | PG&E | Labs/Blood | No |
| 13 |  | 7305315 | Central California Blood Center | SCE | Labs/Blood | No |
| 14 |  | 589312 | American Red Cross Blood Services | SDG&E | Labs/Blood | No |
| 15 |  | 1454638 | Jacobsen Pilot Service, Inc. | SCE | Transportation | No |
| 16 |  | 4983996 | Tri - Counties Blood Bank | PG&E | Labs/Blood | No |
| 17 |  | 7800463 | Tri - Counties Blood Bank | PG&E | Labs/Blood | No |
| 18 |  | 8035906 | Tri - Counties Blood Bank | PG&E | Labs/Blood | No |
| 19 | * | 209979 | American Red Cross Blood Services | SCE | Labs/Blood | No |
| 20 |  | 9494951 | American Red Cross Blood Services | SCE | Labs/Blood | No |
| 21 |  | 8259600 | California Transplant Services, Inc. | SDG&E | Medical Supplies/Records | No |
| 22 |  | 3133563 | FFF Enterprises Inc. | SCE | Medical Supplies/Records | No |
| 23 |  | 8555162 | Mil Spec Heat Treating, Inc. | SCE | Retail | No |
| 24 |  | 6113146 | Satchmed | SCE | Medical Building | No |
| 25 |  | 5600756 | Walaka Development | SCE | Medical Building | No |
| 26 |  | 2423876 | APT Ambulance Company | SCE | Emergency Services | No |
| 27 |  | 9359301 | ViroLogic, Inc. | PG&E | Labs/Blood | No |
| 28 | * | 2260760 | Elm Long Beach, ltd | SCE | Medical Building | No |
| 29 |  | 277881 | Sun Care Health Care | SCE | Nursing Home | No |
| 30 |  | 9530199 | Sunmar Healthcare | SCE | Nursing Home | No |
| 31 |  | 6728075 | Butte Home Health Inc. | PG&E | Nursing Home | No |
| 32 |  | 1200579 | Mariner Post Acute Network | PG&E | Nursing Home | No |
| 33 |  | 8863085 | Cal Nev Methodist Home dba Pacific Grove Conv. Hosp. | PG&E | Nursing Home | No |
| 34 |  | 7609881 | Marriott MapleRidge of Palm Springs | SCE | Nursing Home | No |
| 35 |  | 7054570 | Upland Convalescent Operations, Inc. | SCE | Nursing Home | No |
| 36 |  | 1712512 | American Red Cross Blood Services | SDG&E | Labs/Blood | No |
| 37 |  | 2460607 | American Red Cross Blood Services | SDG&E | Labs/Blood | No |
| 38 |  | 7711504 | American Red Cross Blood Services | SCE | Labs/Blood | No |
| 39 |  | 8466051 | American Red Cross Blood Services | SCE | Labs/Blood | No |
| 40 |  | 8868687 | American Red Cross Blood Services | SCE | Labs/Blood | No |
| 41 |  | 5348071 | American Red Cross Blood Services | SCE | Labs/Blood | No |
| 42 |  | 9994677 | Royal Gardens of Ojai | SCE | Nursing Home | No |
| 43 |  | 4322985 | Torrance Medical Associates, LLC | SCE | Medical Building | No |
| 44 |  | 3654193 | Waterman Industries Inc. (Foundry Division) | SCE | Production | Yes |
| 45 |  | 5087298 | PPG Industries, Inc. | PG&E | Production | Yes |
| 46 |  | 1520556 | Dental Alloy Products, Inc./Shogun Precision Castings, Inc. | SCE | Production | No |
| 47 |  | 3033618 | Commercial Enameling | SCE | Production | No |
| 48 |  | 5223864 | Techi-Cast Corp. | SCE | Production | No |
| 49 |  | 6583117 | Johannessen Trading Co. | SCE | Production | No |
| 50 |  | 7051823 | REIT Management & Research, Inc. | SDG&E | Security | No |
| 51 |  | 5118578 | UCLA Immunogenetics Center | SCE | Health Service | No |
| 52 |  | 8135241 | General Grinding, Inc | PG&E | Production | No |
| 53 |  | 1687596 | Beverly Enterprises Inc | PG&E | Skilled Nursing | No |
| 54 |  | 1695117 | Sun Health Group/Sunbridge Care Center Fullerton | SCE | Skilled Nursing | No |
| 55 |  | 4243334 | B.P. Care, Inc. Palm Vista Care | SCE | Skilled Nursing | Yes |
| 56 |  | 6441210 | Woodside Nursing Center | PG&E | Skilled Nursing | No |
| 57 |  | 3385943 | Edgewater Convalescent Hospital | SCE | Skilled Nursing | No |
| 58 |  | 3759631 | Central Convalescent Homes Inc. | PG&E | Skilled Nursing | No |
| 59 |  | 374621 | SunBridge Care Center for Temple City | SCE | Skilled Nursing | No |
| 60 |  | 9683397 | Bartlett Care Center | SCE | Skilled Nursing | Yes |
| 61 |  | 905475 | Monclair Manor Comvalescent Hospital | SCE | Skilled Nursing | No |
| 62 |  | 896319 | Mission Medical Enterprises, Inc. dba Delta Nursing and Rehabilitation Hospital | SCE | Skilled Nursing | No |
| 63 |  | 1004381 | Mission Medical Enterprises, Inc. dba Kings Nursing and Rehabilitation Hospital | SCE | Skilled Nursing | No |
| 64 |  | 7982958 | Mission Medical Enterprises, Inc. dba Hanford Nursing and Rehabilitation Hospital | SCE | Skilled Nursing | No |
| 65 |  | 9272020 | Mission Medical Enterprises, Inc. dba Tulare Nursing and Rehabilitation Hospital | SCE | Skilled Nursing | No |
| 66 |  | 600451 | Chapman Harbor Skilled Nursing | SCE | Skilled Nursing | No |
| 67 |  | 8527544 | SunBridge Health Care Corp | SDG&E | Skilled Nursing | No |
| 68 |  | 2751940 | Quality Nursing Home dba Majestic Pines Care Center | PG&E | Skilled Nursing | Yes |
| 69 |  | 7262285 | Sunbridge Care Center for Willows | PG&E | Skilled Nursing | No |
| 70 |  | 2011889 | Lakeshore Convalescent Hospital | PG&E | Skilled Nursing | No |
| 71 |  | 5010241 | David Kleis III, LLC | SCE | Skilled Nursing | No |
| 72 |  | 6677111 | Southern California Edison | SCE | Skilled Nursing | No |
| 73 |  | 9389012 | Beaumont Convalescent Hospital | SCE | Skilled Nursing | No |
| 74 |  | 4299334 | Beverly Enterprises Inc. Conv. Hospital #570 | PG&E | Skilled Nursing | No |
| 75 |  | 3895587 | Casa Palmera Care Center | SDG&E | Skilled Nursing | Yes |
| 76 |  | 4537676 | Californian Care Center | PG&E | Skilled Nursing | No |
| 77 |  | 6452807 | Regenerative Health Systems, Inc. dba Live Oak Living Center | PG&E | Skilled Nursing | No |
| 78 |  | 7331560 | Santa Ynez Valley Airport Authority | PG&E | Transportation | No |
| 79 |  | 4406603 | Renaissance at Ocean House | SCE | Nursing Home | No |
| 80 |  | 9414995 | Planned Parenthood Mar Monte | PG&E | Doctor | No |
| 81 |  | 7478350 | Planned Parenthood | PG&E | Doctor | No |
| 82 |  | 2907580 | Planned Parenthood Mar Monte | PG&E | Doctor | No |
| 83 |  | 3093432 | Planned Parenthood | PG&E | Doctor | No |
| 84 |  | 3645037 | Planned Parenthood Mar Monte | PG&E | Doctor | No |
| 85 |  | 7544420 | Planned Parenthood | PG&E | Doctor | No |
| 86 |  | 8348253 | Planned Parenthood | PG&E | Doctor | No |
| 87 |  | 5050219 | Pleasant Hill Manor | PG&E | Nursing Home | No |
| 88 |  | 6194170 | Melencon Corp. | SDG&E | Nursing Home | Yes |
| 89 |  | 3992327 | Fireside Convalescent Hospital-North American Healthcare | SCE | Nursing Home | No |
| 90 |  | 9201525 | Arcadia Convalescent Hospital | SCE | Skilled Nursing | No |
| 91 |  | 6311053 | D&U, LLC dba Mission Lodge | SCE | Skilled Nursing | No |
| 92 |  | 1363238 | Lakewood Park Manor | SCE | Nursing Home | Yes |
| 93 |  | 1883410 | Port City Steel | PG&E | Production | No |
| 94 |  | 1571782 | American Red Cross Blood Services | SCE | Labs/Blood | No |
| 95 |  | 2407855 | Quest Diagnostics | SDG&E | Labs/Blood | No |
| 96 |  | 4344805 | Lomita Care Center | SCE | Skilled Nursing | No |
| 97 |  | 1875628 | Planned Parenthood | PG&E | Doctor | No |
| 98 |  | 2384770 | Planned Parenthood | PG&E | Doctor | No |
| 99 |  | 9691484 | Lamplighter Senior Citizens Inn Ltd. | PG&E | Nursing Home | No |
| 100 |  | 4928912 | BG Nursing Home & Convalescent Hospital, INC | PG&E | Skilled Nursing | No |
| 101 | * | 3515643 | ARV Assisted Living, Inc. | SCE | Nursing Home | No |
| 102 |  | 3643315 | ARV Assisted Living, Inc. | SDG&E | Nursing Home | No |
| 103 |  | 4684771 | ARV Assisted Living, Inc. | SCE | Nursing Home | No |
| 104 |  | 5031298 | ARV Assisted Living, Inc. | SCE | Nursing Home | No |
| 105 |  | 8450487 | ARV Assisted Living, Inc. | PG&E | Nursing Home | No |
| 106 |  | 8599566 | ARV Assisted Living, Inc. | PG&E | Nursing Home | No |
| 107 |  | 9663103 | ARV Assisted Living, Inc. | SCE | Nursing Home | No |
| 108 |  | 9747898 | ARV Assisted Living, Inc. | SCE | Nursing Home | No |
| 109 |  | 3091448 | Independant Qual Care/Valley Pointe | PG&E | Nursing Home | No |
| 110 |  | 1223925 | Lonza Inc. | SCE | Production | No |
| 111 |  | 7226275 | Cottonwood Healthcare Center | PG&E | Skilled Nursing | No |
| 112 |  | 7460039 | Walnut Professional LLC | SDG&E | Medical Building | No |
| 113 |  | 3694323 | SunBridge Care and Rehabilitation for Tustin | SCE | Skilled Nursing | No |
| 114 |  | 2788562 | St. Michaels Convalescent Hospital | PG&E | Skilled Nursing | No |
| 115 |  | 4361590 | Vintage Estates of Kentfield | PG&E | Skilled Nursing | No |
| 116 |  | 5412157 | St. Francis Extended Care INC | PG&E | Skilled Nursing | No |
| 117 |  | 4001134 | Spring Hill Manor Convalescent Hospital | PG&E | Skilled Nursing | No |
| 118 |  | 2439746 | Homewood Care Center | PG&E | Skilled Nursing | No |
| 119 |  | 4730809 | Redding Area Bus Authority | PG&E | Transportation | No |
| 120 |  | 3627642 | City & Country San Francisco | PG&E | Emergency Services | No |
| 121 |  | 2129840 | Harsch Investment Properties, LLC, Series A, dba 450 Sutter Building | PG&E | Medical Building | No |
| 122 |  | 6194628 | Norlyn Builders dba Newport Beach Plaza | SCE | Nursing Home | No |
| 123 |  | 1037005 | Country Place | PG&E | Nursing Home | No |
| 124 |  | 2834948 | Beverly Enterprises Inc | PG&E | Skilled Nursing | No |
| 125 |  | 2763842 | El Paso de Robles Youth Corr. Facility | PG&E | Jail | No |
| 126 |  | 291003 | Merritt Manor Convalescent | SCE | Skilled Nursing | No |
| 127 |  | 1059741 | Kaweah Manor Convalescent | SCE | Skilled Nursing | No |
| 128 |  | 3025836 | Moyles Central Valley Health Care | SCE | Nursing Home | No |
| 129 |  | 4063738 | Browning Manor Convalescent | SCE | Skilled Nursing | No |
| 130 |  | 6100176 | Porterville Convalescent Hospital | SCE | Skilled Nursing | No |
| 131 | * | 1365680 | Bancap Investment Group | SCE | Medical Building | Yes |
| 132 |  | 5623339 | Bancap Investment Group | SCE | Medical Building | Yes |
| 133 |  | 6952837 | Bancap Investment Group | SCE | Medical Building | Yes |
| 134 |  | 9257067 | Bancap Investment Group | SCE | Medical Building | Yes |
| 135 |  | 4114245 | Evas Guest Home | SCE | Nursing Home | No |
| 136 | * | 5783861 | The Breakers of Long Beach | SCE | Nursing Home | Yes |
| 137 |  | 531024 | Westside Sober Living Centers, Inc dba Promises Residential Treatment Centers | SCE | Nursing Home | No |
| 138 |  | 7981432 | Westside Sober Living Centers, Inc dba Promises Residential Treatment Centers | SCE | Nursing Home | No |
| 139 |  | 7632921 | Davita, Union City | PG&E | Dialysis | No |
| 140 |  | 8768023 | DaVita | SCE | Dialysis | No |
| 141 |  | 5359209 | Davita Dialysis -Napa | PG&E | Dialysis | No |
| 142 |  | 8424852 | Imperial Care, Inc. | SCE | Dialysis | Yes |
| 143 |  | 2090930 | Davita, Antioch | PG&E | Dialysis | No |
| 144 |  | 9071215 | DaVita, Pleasanton | PG&E | Dialysis | No |
| 145 |  | 953387 | Davita Inc. San Leandro Dialysis Center | PG&E | Dialysis | Yes |
| 146 |  | 8256701 | South Hayward Dialysis Center | PG&E | Dialysis | Yes |
| 147 |  | 610980 | Santa Barbara Artificial Kidney Center, LLC | SCE | Dialysis | No |
| 148 |  | 1135272 | DaVita (formerly Total Renal Care) Hayward Dialysis | PG&E | Dialysis | Yes |
| 149 |  | 1501788 | DaVita - Ocean Garden Dialysis Center | PG&E | Dialysis | Yes |
| 150 |  | 3939532 | DaVita - Community Hemodialysis of San Francisco | PG&E | Dialysis | Yes |
| 151 |  | 5286992 | DaVita - Potrero Hill Dialysis Center | PG&E | Dialysis | Yes |
| 152 |  | 6438921 | SR Management | PG&E | Skilled Nursing | No |
| 153 |  | 8689898 | Lav Care Corporation dba Castle Hill Retirement Village | SCE | Nursing Home | No |
| 154 |  | 3438738 | Williams Medical Company | SCE | Labs/Blood | No |
| 155 |  | 230426 | Charles Dunn Real Estate Services, Inc. | SCE | Medical Building | No |
| 156 |  | 6189702 | DaVita, Inc. | PG&E | Dialysis | No |
| 157 |  | 330218 | Fowler Convalescent Hospital | PG&E | Skilled Nursing | Yes |
| 158 |  | 5156878 | Villa Elena Convalescent | SCE | Skilled Nursing | No |
| 159 |  | 9256762 | Valley Healthcare Center | SCE | Skilled Nursing | No |
| 160 |  | 9831407 | Stanley Healthcare Center | SCE | Skilled Nursing | No |
| 161 |  | 8023546 | ViroLogic, Inc. | PG&E | Labs/Blood | No |
| 162 |  | 6442583 | Crestwood Behavioral Health, Inc. | PG&E | Skilled Nursing | No |
| 163 |  | 1375140 | Master Cutting & Engineering, Inc. | SCE | Production | No |
| 164 |  | 9133623 | Acme Castings, Inc | SCE | Production | Yes |
| 165 |  | 9432957 | Crest Steel Corporation | SCE | Production | No |
|  |  |  |  |  |  | No |
| 166 |  | 4053515 | FLM Ent. dba Lakewood Gardens | SCE | Nursing Home | Yes |
| 167 |  | 7600878 | Beverly Enterprises dba Reedley Convalescent Hospital | PG&E | Skilled Nursing | Yes |
| 168 | * | 2299517 | Knott Avenue Care Center, Inc. | SCE | Skilled Nursing | No |
| 169 |  | 2347277 | Camarillo Healthcare, Inc. | SCE | Skilled Nursing | No |
| 170 |  | 7173937 | Premier Care Simi, LLC dba Simi Valley Care Center | SCE | Skilled Nursing | No |
| 171 |  | 6314104 | Eastwood Care Center | SCE | Skilled Nursing | No |
| 172 |  | 4138659 | Summit Professional Medical Center | PG&E | Medical Building | No |
| 173 |  | 919207 | Hope Manor | PG&E | Skilled Nursing | No |
| 174 |  | 6684435 | Guardian Industries Corp. | PG&E | Production | Yes |
| 175 |  | 2975634 | Imperial Convalescent Hospital | SCE | Skilled Nursing | No |
| 176 |  | 1050280 | La Palma Hospital-Medical Office Building/La Palma Dialysis Center | SCE | Dialysis | No |
| 177 | * | 7947252 | Dr. Robert E. Cole | SCE | Outpatient Care/Surgery | No |
| 178 |  | 8411425 | Dr. Craig Creasman | PG&E | Outpatient Care/Surgery | No |
| 179 | * | 1142444 | Plastic and Reconstructive Surgery Center | PG&E | Outpatient Care/Surgery | No |
| 180 |  | 3164385 | Ali Heidari, DO | SCE | Outpatient Care/Surgery | Yes |
| 181 |  | 7303789 | Dr. Stephen Krant | SDG&E | Outpatient Care/Surgery | Yes |
| 182 |  | 1196917 | Gary J. Alter, M.D. | SCE | Outpatient Care/Surgery | No |
| 183 |  | 9848759 | Kaiser Permanente | SCE | Outpatient Care/Surgery | No |
| 184 |  | 4496935 | Held Properties | SCE | Outpatient Care/Surgery | No |
| 185 |  | 7190722 | Jane Norton, M.D. | SCE | Outpatient Care/Surgery | No |
| 186 |  | 264758 | Ventura Outpatient Surgery, Inc. | SCE | Outpatient Care/Surgery | No |
| 187 |  | 3692645 | Parkside Surgery Institute | SCE | Outpatient Care/Surgery | Yes |
| 188 |  | 7346972 | Plastic Surgery Assoc | PG&E | Outpatient Care/Surgery | No |
| 189 |  | 2020739 | Doctor Office | PG&E | Outpatient Care/Surgery | No |
| 190 |  | 9161808 | Doctor Office | PG&E | Outpatient Care/Surgery | No |
| 191 |  | 4992388 | Healthsouth Surgery Center of Huntington Beach | SCE | Outpatient Care/Surgery | No |
| 192 |  | 2104663 | 1750 El Camino Medical Building | PG&E | Outpatient Care/Surgery | No |
| 193 |  | 5083178 | University Cernter Medical Partners | SDG&E | Outpatient Care/Surgery | Yes |
| 194 |  | 7636583 | Mohammed Golshani, MD, Inc. | SCE | Outpatient Care/Surgery | No |
| 195 |  | 6612871 | DaVita-Fairfield Dialysis Center | PG&E | Dialysis | No |
| 196 |  | 9153154 | Sun Healthcare Corp. | PG&E | Skilled Nursing | No |
| 197 |  | 8846409 | Jimmy C Wu DDS | SDG&E | Dentist | No |
| 198 |  | 7242296 | Morris A. Budak, DDS | PG&E | Dentist | No |
| 199 |  | 6875780 | Paradise Health Care | PG&E | Skilled Nursing | Yes |
| 200 |  | 4165209 | Healthsouth SurgiCenter at Woodward Park | PG&E | Outpatient Care/Surgery | No |
| 201 |  | 4076861 | Rapid Recovery Hyperbarics | SCE | Doctor | No |
| 202 |  | 4461230 | The Hacienda Retirement Community | PG&E | Nursing Home | No |
| 203 |  | 831164 | First Imperial Properties, LLC | SCE | Medical Building | No |
| 204 |  | 4418963 | Driftwood Health Care Center | PG&E | Skilled Nursing | No |
| 205 |  | 5002154 | Beverly Enterprises Inc | PG&E | Skilled Nursing | No |
| 206 |  | 1230029 | Sun Healthcare Group | PG&E | Skilled Nursing | No |
| 207 |  | 6250780 | Frederick S. Wright MD, / General Surgeon | PG&E | Outpatient Care/Surgery | No |
| 208 |  | 9827244 | Valley Medical Group of Santa Maria | PG&E | Medical Building | No |
| 209 |  | 7121447 | RES-CARE dba RCCA Services | PG&E | Nursing Home | No |
| 210 |  | 8339512 | Kearny Mesa Convalescent Hospital | SDG&E | Skilled Nursing | No |
| 211 |  | 7948124 | Horizon Health and Subacute Center | PG&E | Skilled Nursing | No |
| 212 |  | 4424151 | Bowers Companies | SCE | Emergency Services | No |
| 213 |  | 928058 | Heritage Gardens Health Care Center | SCE | Skilled Nursing | No |
| 214 |  | 654620 | Gerald E. Peters M.D. Inc | PG&E | Outpatient Care/Surgery | No |
| 215 |  | 6834276 | TAMCO | SCE | Production | No |
| 216 |  | 6728533 | County of Santa Cruz | PG&E | Jail | No |
| 217 |  | 9255083 | La Veta Surgical Center, an affiliate of Healthsouth | SCE | Outpatient Care/Surgery | No |
| 218 |  | 3086260 | DaVita-Vacaville | PG&E | Dialysis | No |
| 219 |  | 8680895 | Manor Care of Palm Desert | SCE | Skilled Nursing | No |
| 220 | * | 5263689 | Beverly Enterprises Inc., Dept #0559 | PG&E | Skilled Nursing | No |
| 221 |  | 6597613 | Sneath Lane Investment Group | PG&E | Medical Building | No |
| 222 |  | 3239154 | Sun Health Group | PG&E | Nursing Home | No |
| 223 |  | 1313342 | Beverly Enterprises | PG&E | Skilled Nursing | No |
| 224 |  | 1635913 | Manor Healthcare Corporation | SDG&E | Skilled Nursing | No |
| 225 |  | 1060962 | Dr. Michael Digiacomo | PG&E | Outpatient Care/Surgery | No |
| 226 |  | 3631457 | Pacific Care Center | PG&E | Skilled Nursing | No |
| 227 |  | 2132434 | Beverly Enterprises Beverly Manor Petaluma | PG&E | Skilled Nursing | No |
| 228 |  | 3364428 | Woodbrook Professional Group Drs. Fred, Scott Hanosh; Thomas A. Stewart; Seldin Greer | PG&E | Doctor | No |
| 229 |  | 3653430 | Vencor Inc #926 dba 19th Ave Healthcare | PG&E | Skilled Nursing | No |
| 230 |  | 578784 | California Convalescent Hospital | PG&E | Skilled Nursing | No |
| 231 |  | 6518420 | Timberlake-Forrest, Inc. | PG&E | Skilled Nursing | No |
| 232 |  | 6985491 | Fifth Avenue Healthcare Center | PG&E | Skilled Nursing | No |
| 233 |  | 4185961 | San Antonia Urology Medical Group | SCE | Outpatient Care/Surgery | No |
| 234 |  | 2682666 | Washington Outpatient Surgery Center | PG&E | Outpatient Care/Surgery | No |
| 235 |  | 572375 | New West Dialysis - New Name - DaVita, Inc. | PG&E | Dialysis | No |
| 236 |  | 1822375 | DaVita Dialysis | PG&E | Dialysis | Yes |
| 237 |  | 6683214 | Third Avenue Medical Building Associates | SDG&E | Medical Building | No |
| 238 |  | 3980883 | SunBridge Healthcare Group, Inc. | SDG&E | Skilled Nursing | No |
| 239 |  | 386981 | Los Gatos Professional Building Associates, LLC | PG&E | Outpatient Care/Surgery | No |
| 240 |  | 7243975 | South Bascom Medical Professional Center | PG&E | Dialysis | No |
| 241 |  | 3198413 | Ygnacio Adobe Building | PG&E | Medical Building | No |
| 242 |  | 9215868 | Shadowbrook Health Care | PG&E | Skilled Nursing | Yes |
| 243 |  | 842761 | DaVita, Inc. - Walnut Creek | PG&E | Dialysis | No |
| 244 |  | 1260089 | American Red Cross Blood Services | SCE | Labs/Blood | No |
| 245 |  | 6707018 | American Red Cross Blood Services | SCE | Labs/Blood | No |
| 246 |  | 6771214 | Delano District Skilled Nursing Facility | SCE | Skilled Nursing | No |
| 247 |  | 8778246 | Guardian Post Acute | PG&E | Nursing | No |
| 248 |  | 3738726 | Sun Bridge-Park Central | PG&E | Skilled Nursing | No |
| 249 |  | 9496325 | Sunford Investment Co. dba De Anza View Medical Center | SDG&E | Medical Building | No |
| 250 |  | 960254 | Orange Show Dental | SCE | Dentist | No |
| 251 |  | 379657 | Bel Vista Convalescent Hospital | SCE | Skilled Nursing | No |
| 252 |  | 5482958 | Life Care Center of Corona | SCE | Skilled Nursing | No |
| 253 |  | 1521777 | Rimrock Villa Convalescent Hospital | SCE | Skilled Nursing | No |
| 254 |  | 5851611 | San Tomas Convalescent Hospital | PG&E | Skilled Nursing | No |
| 255 |  | 9398668 | Beauty & Health Medical Center of California | PG&E | Outpatient Care/Surgery | No |
| 256 |  | 3325976 | Central Coast Institute for Plastic Surgery Gary R. Donath, M.D. | PG&E | Outpatient Care/Surgery | Yes |
| 257 |  | 5116137 | Oak Park Convalescent Hospital | PG&E | Skilled Nursing | No |
| 258 |  | 7908800 | Bethany Home Society of San Joaquin County, Inc. | PG&E | Skilled Nursing | No |
| 259 |  | 2019061 | Richard A Gangnes, M.D., Inc. | SDG&E | Outpatient Care/Surgery | No |
| 260 |  | 7234209 | Guardian Post Acute | PG&E | Nursing | No |
| 261 |  | 3510716 | Palmdale Regional Dialysis Center | SCE | Dialysis | No |
| 262 |  | 3459033 | Victor Szanto | PG&E | Outpatient Care/Surgery | No |
| 263 |  | 7258471 | The 5th & Palm Corp | SDG&E | Office/Property | No |
| 264 |  | 4415606 | Robert Mraule, MD, Inc/Monterey Bay Medical Surgery Center | PG&E | Outpatient Care/Surgery | Yes |
| 265 | * | 6323717 | WHC-Six Real Estate L.P. | SCE | Office/Property | No |
| 266 |  | 9493229 | WHC-Six REal Estate | SCE | Medical Building | No |
| 267 |  | 2856158 | Robert A. Shuken, D.D.S, Jeffrey L. Foltz, DDS, Inc. | SCE | Outpatient Surgery/Dentist | No |
| 268 |  | 8858355 | DBa Taradent | PG&E | Outpatient Surgery/Dentist | No |
| 269 |  | 1091327 | Anthony D. Beech, DDS | PG&E | Outpatient Surgery/Dentist | No |
| 270 |  | 8698595 | Dr. Robert E. Jarvis II | PG&E | Outpatient Surgery/Dentist | No |
| 271 |  | 1415728 | Dr Clifford Fowler | PG&E | Outpatient Surgery/Dentist | No |
| 272 |  | 9367693 | Dr. Clifford Fowler | PG&E | Outpatient Surgery/Dentist | No |
| 273 |  | 877551 | Nicholas N. Gadler DDS | SDG&E | Outpatient Surgery/Dentist | No |
| 274 |  | 4710406 | Paul Riley | SCE | Outpatient Surgery/Dentist | No |
| 275 |  | 586871 | Brian K. Higgins, DDS | PG&E | Outpatient Surgery/Dentist | Yes |
| 276 |  | 8285997 | G. Robert Osborn, DDS, Inc. | PG&E | Outpatient Surgery/Dentist | No |
| 277 |  | 4267291 | Ronald Gardner, DDS, Inc. | SCE | Outpatient Surgery/Dentist | No |
| 278 |  | 3491948 | Young Lee, DDS | SCE | Outpatient Surgery/Dentist | No |
| 279 |  | 9132555 | Ralph Roberts, DDS | PG&E | Outpatient Surgery/Dentist | No |
| 280 |  | 4015215 | Oral and Maxillofacial Surgery | PG&E | Outpatient Surgery/Dentist | No |
| 281 |  | 6363695 | Casey K. Shimane DDS Oral and Maxillofacial Surgery | PG&E | Outpatient Surgery/Dentist | No |
| 282 |  | 8447283 | NC Oral & Facial Center | SDG&E | Outpatient Surgery/Dentist | No |
| 283 |  | 6914690 | Robert V. Fontanesi, DDS, Inc. | SCE | Outpatient Surgery/Dentist | Yes |
| 284 |  | 5642413 | Sunhill Corporation-Owner, Richard Robert Tenant | PG&E | Outpatient Surgery/Dentist | No |
| 285 |  | 2220019 | Brian C. Blalock DDS, MD | SDG&E | Outpatient Surgery/Dentist | No |
| 286 | * | 5709093 | Brian C. Chung, DDS, M.D. | SCE | Outpatient Surgery/Dentist | No |
| 287 |  | 9940050 | Robert G. Allen DDS | PG&E | Outpatient Surgery/Dentist | No |
| 288 |  | 1950854 | Richard Torchia DDS PC | SDG&E | Outpatient Surgery/Dentist | No |
| 289 |  | 1627978 | Howard J. Winer, DDS, Inc. | SCE | Outpatient Surgery/Dentist | No |
| 290 |  | 2310199 | Anthony Torres DDS and Kevin Dorsey DDS | SCE | Outpatient Surgery/Dentist | No |
| 291 |  | 262774 | Harrison D. Fortney DDS | SDG&E | Outpatient Surgery/Dentist | No |
| 292 |  | 3192462 | Mark Nocera, DDS, Avia Dental Care | SDG&E | Outpatient Surgery/Dentist | No |
| 293 |  | 2503222 | Gentle Dental Service Corporation | SDG&E | Outpatient Surgery/Dentist | No |
| 294 |  | 5665301 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 295 |  | 1019153 | Ezaki Dental Practice | SCE | Outpatient Surgery/Dentist | No |
| 296 |  | 8717669 | David R. Crouch, DDS & Associates | SCE | Outpatient Surgery/Dentist | No |
| 297 |  | 224017 | Gentle Dental Service Corporation | SDG&E | Outpatient Surgery/Dentist | No |
| 298 |  | 289935 | Gentle Dental Service Corporation | SCE | Outpatient Surgery/Dentist | No |
| 299 |  | 673388 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 300 |  | 707568 | Pacific Dental Services, Inc. | SDG&E | Outpatient Surgery/Dentist | No |
| 301 |  | 713214 | Gentle Dental Service Corporation | SDG&E | Outpatient Surgery/Dentist | No |
| 302 |  | 856145 | Gentle Dental Service Corporaton | SCE | Outpatient Surgery/Dentist | No |
| 303 |  | 1130084 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 304 |  | 1137103 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 305 |  | 1159076 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 306 |  | 1435107 | Gentle Dental Service Corporation | SCE | Outpatient Surgery/Dentist | No |
| 307 |  | 1765307 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 308 |  | 1975421 | Gentle Dental Service Corporation | SDG&E | Outpatient Surgery/Dentist | No |
| 309 |  | 2106189 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 310 |  | 2455157 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 311 |  | 2501086 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 312 |  | 2605151 | Camarillo Dental Group | SCE | Outpatient Surgery/Dentist | No |
| 313 |  | 3018054 | Pacific Dental Services | SCE | Outpatient Surgery/Dentist | No |
| 314 |  | 3046130 | Gentle Dental Service Corporation | SDG&E | Outpatient Surgery/Dentist | No |
| 315 |  | 3646105 | Pacific Dental Services | SCE | Outpatient Surgery/Dentist | No |
| 316 |  | 3889788 | Pacific Dental Services | SCE | Outpatient Surgery/Dentist | No |
| 317 |  | 4548357 | Pacific Dental Services | SCE | Outpatient Surgery/Dentist | No |
| 318 |  | 4709490 | Inland Empire Dental Group | SCE | Outpatient Surgery/Dentist | No |
| 319 |  | 4848803 | Stromberg, Louis, Desert Valley Dental | SCE | Outpatient Surgery/Dentist | No |
| 320 |  | 5215014 | Gentle Dental Service Corporation | SDG&E | Outpatient Surgery/Dentist | No |
| 321 |  | 5584124 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 322 |  | 5922259 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 323 |  | 6190508 | Pacific Dental Services | SDG&E | Outpatient Surgery/Dentist | No |
| 324 |  | 6326617 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 325 |  | 6413897 | Gentle Dental Service Corporation | SCE | Outpatient Surgery/Dentist | No |
| 326 |  | 6581743 | Mission Dental Group | SCE | Outpatient Surgery/Dentist | No |
| 327 |  | 6680577 | Pacific Dental Services, Inc. | SDG&E | Outpatient Surgery/Dentist | No |
| 328 |  | 7282732 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 329 |  | 7444475 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 330 |  | 7464312 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 331 |  | 7860692 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 332 |  | 8136309 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 333 |  | 8843248 | Desert Dental Services | SCE | Outpatient Surgery/Dentist | No |
| 334 |  | 9197710 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 335 |  | 9449785 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 336 |  | 9452074 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 337 |  | 9525927 | Pacific Dental Services | SCE | Outpatient Surgery/Dentist | No |
| 338 |  | 9583910 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 339 |  | 9726732 | Pacific Dental Services | SCE | Outpatient Surgery/Dentist | No |
| 340 |  | 2917956 | Guardian Post Acute | PG&E | Nursing | No |
| 341 |  | 1793994 | Slutsky Dental Corporation | SCE | Outpatient Surgery/Dentist | No |
| 342 |  | 2260913 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 343 |  | 2466601 | GDSC | SCE | Outpatient Surgery/Dentist | No |
| 344 |  | 4355792 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 345 |  | 5997136 | GDSC | SCE | Outpatient Surgery/Dentist | No |
| 346 |  | 7937945 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 347 |  | 8726213 | De La Vina Surgicenter | SCE | Outpatient Care/Surgery | No |
| 348 |  | 9556902 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 349 |  | 9626024 | GDSC | SCE | Outpatient Surgery/Dentist | No |
| 350 |  | 9944279 | Gentle Dental Service Corporation | PG&E | Outpatient Surgery/Dentist | No |
| 351 |  | 8074053 | Graybill Medical Group | SDG&E | Outpatient Care/Surgery | No |
| 352 |  | 6430485 | SunBridge Granada Care and Rehabilition | PG&E | Skilled Nursing | Yes |
| 353 |  | 4140643 | Bevery Entriprises, Inc. Convalescent Hospital | PG&E | Nursing Home | No |
| 354 |  | 7448900 | South Bascom Medical Professional Center | PG&E | Outpatient Care/Surgery | No |
| 355 |  | 9289721 | Thomas Lile Sycamore Medical | PG&E | Office/Property | No |
| 356 |  | 1496905 | Temecula Valley Facial and Oral Surgery Center | SCE | Outpatient Surgery/Dentist | No |
| 357 |  | 6978167 | Bernard I. Raskin, M.D., Inc. | SCE | Outpatient Care/Surgery | No |
| 358 |  | 9399736 | Bakersfield Dialysis Center Inc | PG&E | Dialysis | No |
| 359 |  | 7157305 | Palmdale Urology / Valencia Urology | SCE | Outpatient Care/Surgery | No |
| 360 |  | 9561022 | Franklin Croft Management, Inc. | SDG&E | Medical Building | No |
| 361 |  | 7651690 | Victor Ho D.M.D. | SCE | Outpatient Surgery/Dentist | No |
| 362 |  | 4260729 | Sign of The Dove | SCE | Nursing Home | No |
| 363 |  | 6437090 | Regency Park La Mesa | SDG&E | Nursing Home | No |
| 364 |  | 8395250 | Amparo Ragudo dba Camden Convalescent Hospital | PG&E | Skilled Nursing | No |
| 365 |  | 1878833 | HealthSouth San Francisco Surgery Center | PG&E | Outpatient Care/Surgery | No |
| 366 |  | 8551348 | Bryan Jennings dba Valley View Conv Hosp | PG&E | Skilled Nursing | No |
| 367 |  | 413684 | Health Care Property Investors, Inc. c/o Prentiss | SDG&E | Medical Building | No |
| 368 |  | 723590 | Endre Selmeczy D.M.D. | PG&E | Outpatient Surgery/Dentist | No |
| 369 |  | 2119006 | David J. Tracy, DDS | SDG&E | Outpatient Surgery/Dentist | No |
| 370 |  | 6228808 | E M Matsuishi DDS Inc. | PG&E | Dentist | No |
| 371 |  | 6640642 | Robert A. Rees DDS, APC | SDG&E | Outpatient Surgery/Dentist | No |
| 372 |  | 9607408 | Robert L. Fisher, DDS Inc., Dentistry for Children | PG&E | Dentist | Yes |
| 373 |  | 2209491 | Ric S. Garrison, M.D. | SCE | Outpatient Care/Surgery | No |
| 374 |  | 5626849 | HCP Medical Buildings II, LLC c/o Prentiss Properties, Ltd. | SDG&E | Medical Building | No |
| 375 |  | 9266069 | Dr. Sloan Mc Donald, DDS | PG&E | Outpatient Surgery/Dentist | No |
| 376 |  | 679644 | St. John Kronstadt Care Center | PG&E | Skilled Nursing | No |
| 377 | * | 7795537 | BV Conv Hosp | SCE | Skilled Nursing | No |
| 378 | * | 2344989 | Newport Medical Arts Building,LLC | SCE | Medical Building | No |
| 379 |  | 2997454 | Philip C. Roberts, DDS | SDG&E | Outpatient Surgery/Dentist | No |
| 380 |  | 4048632 | Douglas, Emmett & Company | SCE | Medical Building | No |
| 381 |  | 480060 | Simmons Dental Care | SCE | Outpatient Surgery/Dentist | Yes |
| 382 |  | 229815 | Dr. Raymond T.Matsunaga Hillside Professional Cen | PG&E | Dentist | No |
| 383 |  | 317706 | Mary A. Delsol, DDS - Oral and Maxillofacial Surgery | SDG&E | Outpatient Surgery/Dentist | No |
| 384 |  | 2723406 | Hillside Professional Center | PG&E | Dentist | No |
| 385 |  | 4313220 | Barry Johnsin, DDS, Inc. | SCE | Outpatient Surgery/Dentist | No |
| 386 |  | 6275805 | Westlake Eye Surgery Center | SCE | Outpatient Care/Surgery | No |
| 387 |  | 5176257 | Alamar Dental Center | SCE | Outpatient Surgery/Dentist | No |
| 388 |  | 3240832 | Heda Koh DDS | PG&E | Dentist | No |
| 389 |  | 4574297 | Northern California Facial & Oral Surgery | PG&E | Outpatient Surgery/Dentist | No |
| 390 |  | 7393664 | Northern California Facial & Oral Surgery | PG&E | Outpatient Surgery/Dentist | No |
| 391 |  | 7436846 | Paul J. Carroll, DDS, Oral and Maxillofacial Surgery | PG&E | Outpatient Surgery/Dentist | No |
| 392 |  | 8285235 | Northern California Facial & Oral Surgery | PG&E | Outpatient Surgery/Dentist | No |
| 393 |  | 8532732 | Northern California Facial & Oral Surgery | PG&E | Outpatient Surgery/Dentist | No |
| 394 |  | 8817308 | Sid Mirrafati, MD (Mira Aesthetic Medical Center | SCE | Outpatient Care/Surgery | Yes |
| 395 |  | 6285723 | Los Angeles Pump & Valve Products | SCE | Production | No |
| 396 |  | 719317 | Thomas S. Adamich, DDS (CDF II) | SCE | Outpatient Surgery/Dentist | No |
| 397 |  | 603351 | Alpha Therapeutic Corporation | SCE | Dialysis | No |
| 398 |  | 1949939 | Alpha Therapeutic Corporation | PG&E | Dialysis | No |
| 399 |  | 3904131 | Alpha Therapeutic Corporation | PG&E | Dialysis | No |
| 400 |  | 5582903 | Alpha Therapeutic Corporation | SDG&E | Dialysis | No |
| 401 |  | 8521898 | Alpha Therapeutic Corporation | SDG&E | Dialysis | No |
| 402 |  | 8875444 | Alpha Therapeutic Corporation | SCE | Dialysis | No |
| 403 |  | 7928789 | Lane J. Lopez, DDS, Inc. | SCE | Outpatient Surgery/Dentist | No |
| 404 | * | 8463871 | Independent Quality Care | PG&E | Skilled Nursing | No |
| 405 |  | 364551 | Dr. Fred Bunch | PG&E | Outpatient Surgery/Dentist | No |

FW:  Further Work.  An asterisk denotes unknown circuit and/or invalid account number, or other processing difficulty.  Category M status is granted upon the condition that the difficulty is resolved satisfactorily.

Statement of Authenticity:  If a Statement of Authenticity has not been submitted, the Category M status is granted on the condition that the Statement is submitted within 60 days.

(End of Attachment D)

# Footnotes

The ACR established a process for each customer to file a ‘petition’ for Category M status.  Over the course of the project, the term ‘application’ became commonly used.  As a result, we use the term application in this decision with the same meaning as petition.  Using the term application will minimize reader confusion for those who applied using the Commission’s web page, or are otherwise not familiar with use of the term petition.

The original deadline of June 1, 2001 was extended to June 4, 2001, due to the large number of applications.  (June 1, 2001 ACR.)

The Commission identifies 14 groups as essential customers, classified into Categories A through N.  (See D.01-06-085, Appendix A.)  Applicants not given further consideration for Category M here are already in Categories A through L or N.

Exponent says that this discrepancy (i.e., high risk assessment by the panel group but low calculated risk index scores based on each application) can be explained in several ways.  For example, according to Exponent, panel group study participants may not have understood procedures at SNFs and dialysis treatment centers well enough to properly judge risk.  Also, applicants might have been reluctant to admit high levels of risk due to concerns over liability.  Further, these facilities have smaller populations at risk than some emergency services and communications facilities.  Finally, nursing home and dialysis treatment clinics may have appropriately estimated public health risks while other facilities may have overestimated risk.

See, for example, ACR dated March 28, 2001, directing PG&E to provide data which was in turn given to the City and County of San Francisco.  The same ACR directed SCE to provide reasonable data to the City of Huntington Beach, or one or both parties to file a motion for release of certain information.  Also see Governor’s Executive Order D-38-01, dated June 1, 2001.

Category A is: “Government and other agencies providing essential fire, police, and prison services.”  (D.01-04-006, Attachment C.)

If each circuit carries 5 MW of load, exempting 1,200 circuits would exempt 6,000 MW of load.

Assuming the state’s summertime peak demand is 50,000 MW (D.01-04-006, mimeo. page 35), 6,000 MW of load on circuits including a SNF represents 12% of peak demand.  If about 50% of summer peak load is now available for rotating outage, that means about 25,000 MW is now available for rotating outage.  Removing 6,000 MW would reduce the available load from 25,000 MW to 19,000, or from 50% of total load to 38% of total load for rotating outage.

Not all applicants were required to submit a Statement of Authenticity.  Rather, only those granted essential customer status in the August 17, 2001 Draft Decision of Commissioner Wood were required to submit the Statement, with the Statement due no later than August 27, 2001 (i.e., the date comments were due on the Draft Decision).

For example, a business that is granted an exemption herein because it performs some outpatient surgery, or other activity that results in it being ranked high in relative risk to public health and safety, might reduce the amount of outpatient surgery, or reduce other relatively risky activity, over time.  This may reduce its relative risk ranking compared to other businesses.

“The application for a rehearing shall set forth specifically the ground or grounds on which the applicant considers the decision or order to be unlawful.”  (Pub. Util. Code § 1732.)

Pursuant to D.01-08-018, adopted on August 2, 2001, the burden of serving comments on nearly 10,000 parties was moderated by limiting service to only 5 persons at the Commission.