OPERATION STANDARDS

For Generating Asset Owners

Proposal for Committee Adoption on October 27

Issued: October 26, 2004

Version 2

California Electric Generation Facilities Standards Committee

Chairman:

Carl Wood, California Public Utilities Commission

Members:

Michael Kahn, Chair, Board of Governors, California Independent System Operator

Glenn Bjorklund, Southern California Edison Company (Retired)

[This page left blank intentionally.]

Table of Contents

INTRODUCTION	6

The Relationship of the Operation Standards to Maintenance Standards Previously Adopted by the Committee	6

Use of Terms Related to GAO Personnel	6

Guidelines	7

Implementation	7

OPERATION STANDARDS COMMON WITH MAINTENANCE STANDARDS	9

Standard 1: Safety	9

Standard 2: Organizational Structure and Responsibilities	9

Standard 3: Operations  Management and Leadership	9

Standard 4:  Problem Resolution and Continuing Improvement	9

Standard 5: Operations Personnel Knowledge and Skills	9

Standard 6:  Training Support	10

Standard 7: Operation Procedures and Documentation	10

Standard 8:  Plant Status and Configuration	10

Standard 9:  Engineering and Technical Support	10

Standard 10:  Environmental Regulatory Requirements	10

Standard 11:  Operations Facilities, Tools and Equipment	10

GENERAL OPERATION STANDARDS	11

Standard 12:  Operations Conduct	11

Standard 13: Routine Inspections	11

Standard 14: Clearances	12

Standard 15: Communications and Work Order Meetings	12

Standard 16: Participation by Operations Personnel in Work Orders	12

Standard 17:  Records of Operation	13

Standard 18:  Unit Performance Testing	13

Standard 19: Emergency Grid Operations	13

Standard 20:  Preparedness for On-Site and Off-Site Emergencies	14

Standard 21: Plant Security	14

Standard 22: Readiness	15

Standard 23: Notification of Changes in Long-Term Status of a Unit	15

Standard 23:  Approval of Changes in Long-Term Status of a Unit	15

Standard 25: Transfer of Ownership	15

Standard 26: Planning for Long-Term Unit Storage	15

Standard 27: Flow Assisted Corrosion	16

Standard 28:  Equipment and Systems	16

Appendix	16

A.	Definitions	16

# INTRODUCTION

On October 27, 2004, the California Electric Generation Facilities Standards Committee (“the Committee”) adopted these Operation Standards in compliance with the requirements of Section 761.3 of the California Public Utilities Code, established by Senate Bill 39xx (Burton, Speier).  The California Public Utilities Commission (“the Commission”) is responsible for implementation and enforcement of these standards.  By law, the Committee is composed of one member of the Commission, one board member of the California Independent System Operator (“the CAISO”), and a third member chosen by the first two.

## The Relationship of the Operation Standards to Maintenance Standards Previously Adopted by the Committee

The first eleven standards (and associated guidelines) are similar to several of the Maintenance Standards adopted by the Committee in May 2003.   These standards address areas that are common to both operation and maintenance, such as training, management, and problem resolution.  Standards 12 through 28 are new standards specifically tailored to the operation of power plants.

## Use of Terms Related to GAO Personnel

The Operation Standards and associated Guidelines benefited from the participation of many authors.  One artifcact of the collaborative writing process is a variety of terms used to refer to GAO personel.  References within the Standards and Guidelines to “individuals,” “employees,”  “operations personnel”, “personnel,”  “management,” or other staffing descriptions are not intended to require a GAO to follow any particular organizational structure, or to dictate whether work should be performed by the GAO’s own employees or contractors.  Rather, a GAO is free to organize its work force in the manner it deems most appropriate.

Whether or not it employs contractors, the GAO is solely responsible for complying with these Operation Standards.  The GAO is required to take reasonable and prudent steps to assure that contract employees are held to equally stringent performance standards as GAO employees, and that contract employees receive comparable training and safety protections related to their duties.  Some standards and guidelines specifically mention contractors or temporary workers and some do not.  The GAO’s duties regarding contractors and temporary workers, as discussed above, apply to all standards and guidelines when contractors or temporary workers are involved in compliance-related activities, whether or not such workers are specifically mentioned in relevant standards and guidelines.

## Guidelines

In addition to the Operation Standards, the Committee adopts a set of recommended Guidelines for all but one standard.   We intend these guidelines to assist GAOs in developing plans, procedures and training programs that comply with the Operation Standards, as well as to assist Commission staff in implementing the standards through audits or other implementation activities.

The Committee does not intend  these guidelines to be enforceable.   There may be reasonable ways of meeting a particular standard that do not follow every provision of the associated guidelines.   On the other hand, the guidelines may not be an exhaustive list of the actions required by a standard, because at particular plants there may be special conditions not contemplated here.

GAOs should consider the guidelines in reviewing or reformulating their own policies, operating procedures, and implementation schedules, to ensure that the concerns raised by the guidelines are addressed, where relevant, at each power generation unit.  We anticipate that that Commission staff will use the guidelines as indicators of the kinds of GAO activities that are sufficient to meet standards.  Failure to meet guidelines under a particular standard may of course raise questions about the completeness of a GAO’s program.  However, failure to meet a guideline should not be taken, per se, as a failure to meet the associated standard.

Finally, the Equipment and System Operating Standard (Number 28) has particularly extensive guidelines addressing 28 separate critical systems in operation at various power plants around the state. We recognize that not all of the systems are in operation at each generation unit (hydroelectric units will contain only a few of these systems).  However, where the systems are in operation, they are critical to plant reliability and safety.

## Implementation

The Commission has indicated that it will incorporate the Operation Standards into General Order (GO) 167, along with the Maintenance and Logbook Standards previously adopted by this Committee.  Therefore, we assume and intend that the general implementation provisions of the GO will also apply to these Operation Standards.  We are not adopting an implementation plan for the Operation Standards, because that is the Commission’s role, not the Committee’s.  Comments have suggested that we address such topics as confidentiality and penalties, yet those are implementation issues that are already addressed in GO 167.

GO 167 states that these standards will not modify, delay or abrogate any deadline standard, rule or regulation imposed by other agencies.  While we have not tried to identify or reference every applicable requirement, we do note that failure to follow certain requirements imposed by other agencies may threaten the safety and reliability of a power unit.  Therefore, behavior that constitutes a violation of another agency’s requirements may also constitute a violation of these operation standards.

Although the Committee’s task is to adopt standards, not to implement them, we offer the following implementation recommendations to the Commission for consideration in its implementation proceeding.  The Committee recommends that the Commission implement the standards in a way that provides GAOs considerable flexibility in meeting the standards while retaining accountability.   Accordingly, the Committee recommends that the Commission require GAOs to file for each power generation unit an Operation Plan detailing how the generation owner meets (or plans to meet) the Operation Standards.  The Committee recommends that this Operation Plan should include, at a minimum:

- A brief Unit Plan including the expected years the plant will remain in operation, whether the plant is regarded as a baseload plant or peaking plant (or some intermediate designation), what level of availability the GAO intends for the plant, whether the plant will operate year-round or only seasonally, and whether the GAO views the plant as a long-term resource that requires continued maintenance and investment.

- A general description and timetable of how the GAO meets or plans to meet the provisions of each Operation Standard at each unit (or identical groups of units), identifying by title (and location) and summarizing the various operating policies, procedures, training programs and routines the GAO has in place (or will put in place) to demonstrate compliance with the Operation Standards.

The Committee recommends that the Commission 1) require the Operation Plans to be updated appropriately, and 2) use the Operation Plans during audits of power generation units.

We request that the Commission insert appropriate implementation language into its general order to effectuate the recommendations in this section.

# OPERATION STANDARDS COMMON WITH MAINTENANCE STANDARDS

## Standard 1: Safety

(Similar to Maintenance Standard I A)

The protection of life and limb for the work force is paramount.  GAOs have a comprehensive safety program in place at each site.  The company behavior ensures that personnel at all levels of the organization consider safety as the overriding priority.  This is manifested in decisions and actions based on this priority. The work environment and the policies and procedures foster such a safety culture, and the attitudes and behaviors of personnel are consistent with the policies and procedures.

## Standard 2: Organizational Structure and Responsibilities

(Similar to Maintenance Standard 1B)

The organization with responsibility and accountability for establishing and implementing an operation strategy to support company objectives for reliable plant operation is clearly defined, communicated, understood and is effectively implemented.  Reporting relationships, control of resources, and individual authorities support and are clearly defined and commensurate with responsibilities.

## Standard 3: Operations  Management and Leadership

(Similar to Maintenance Standard 1C)

Operations management establishes high standards of performance and aligns the operations organization to effectively implement and control operations activities.

## Standard 4:  Problem Resolution and Continuing Improvement

(Similar to Maintenance Standard I D)

The GAO values and fosters an environment of continuous improvement and timely and effective problem resolution.

## Standard 5: Operations Personnel Knowledge and Skills

(Similar to Maintenance Standard II A)

Operations personnel are trained and qualified to possess and apply the knowledge and skills needed to perform operations activities that support safe and reliable plant operation.

## Standard 6:  Training Support

(Similar to Maintenance Standard II B)

A systematic approach to training is used to achieve, improve, and maintain a high level of personnel knowledge, skill, and performance.  Each GAO provides a site-specific training program including on-the-job training, covering operations, including reasonably anticipated abnormal and emergency operations.  Personnel are trained commensurate with their duties.

## Standard 7: Operation Procedures and Documentation

(Similar to Maintenance Standard IV A)

Operation procedures exist for critical systems and states of those systems necessary for the operation of the unit including startup, shutdown, normal operation, and reasonably anticipated abnormal and emergency conditions.  Operation procedures and documents are clear and technically accurate, provide appropriate direction, and are used to support safe and reliable plant operation.  Procedures are current to the actual methods being employed to accomplish the task and are comprehensive to ensure reliable energy delivery to the transmission grid.

## Standard 8:  Plant Status and Configuration

(Similar to Maintenance Standard V B)

Station activities are effectively managed so plant status and configuration are maintained to support safe, reliable and efficient operation.

## Standard 9:  Engineering and Technical Support

(Similar to Maintenance Standard VIIB)

Engineering activities are conducted such that equipment performance supports reliable plant operation.  Engineering provides the technical information necessary for the plant to be operated and maintained within the operating parameters defined by plant design.  Engineering provides support, when needed, to operations and maintenance groups to resolve operations and maintenance problems.

## Standard 10:  Environmental Regulatory Requirements

(Similar to Maintenance Standard VII D)

Environmental regulatory compliance is paramount in the operation of the generating asset.  Each regulatory event is identified, reported and appropriate action taken to prevent recurrence.

## Standard 11:  Operations Facilities, Tools and Equipment

(Similar to Maintenance Standard IX A)

Facilities and equipment are adequate to effectively support operations activities.

# GENERAL OPERATION STANDARDS

## Standard 12:  Operations Conduct

To ensure safety, and optimize plant availability, the GAO conducts operations systematically, professionally, and in accordance with approved policies and procedures.  The GAO takes responsibility for personnel actions, assigns personnel to tasks for which they are trained, and requires personnel to follow plant and operation procedures and instructions while taking responsibility for safety.

Among other things:

- All personnel follow approved policies and procedures.  Procedures are current, and include a course of action to be employed when an adopted procedure is found to be deficient.

- All operations are performed in a professional manner.  Basic rules of conduct apply throughout the plant at all times.

- All personnel on-duty are trained, qualified, and capable of performing their job functions.  Personnel are assigned only to duties for which they are properly trained and qualified.

- Personnel take immediate actions to prevent or correct unsafe situations.

## Standard 13: Routine Inspections

Routine inspections by plant personnel ensure that all areas and critical parameters of plant operations are continually monitored, equipment is operating normally, and that routine maintenance is being performed.  Results of data collection and monitoring of parameters during routine inspections are utilized to identify and resolve problems, to improve plant operations, and to identify the need for maintenance.  All personnel are trained in the routine inspections procedures relevant to their responsibilities.

Among other things, the GAO creates, maintains, and implements routine inspections by:

- Identifying systems and components critical to system operation (such as those identified in the guidelines to Standard 28).

- Establishing procedures for routine inspections that define critical parameters of these systems, describe how those parameters are monitored, and delineate what action is taken when parameters meet alert or action levels.

- Training personnel to conduct routine inspections.

- Monitoring routine inspections.

## Standard 14: Clearances

Work is performed on equipment only when safe.  When necessary, equipment is taken out of service, de-energized, controlled, and tagged in accordance with a clearance procedure.    Personnel are trained in the clearance procedure and its use, and always verify that equipment is safe before any work proceeds.

Among other things:

- The GAO prepares and maintains a clearance procedure.  The clearance procedure contains requirements for removing a component from service and/or placing a component back into service.

- The GAO ensures that personnel are trained in and follow the clearance procedure.

## Standard 15: Communications and Work Order Meetings

The availability of the generating asset and safety of employees is ensured during the execution of work orders by adequate communications and meetings, which may be scheduled or as needed, to review work plans with all affected personnel before work begins.  Clear lines of communication exist between personnel responsible for operations, maintenance and engineering groups.

Among other things:

- The GAO prepares and maintains a procedure for review of work plans through communications and work order meetings at the facility.

- Work is analyzed to determine what personnel, components, and systems are affected.

- Affected personnel meet before work begins to define the work, identify safety issues, to minimize the impact on plant operation, and to determine the need for further meetings.

- Personnel are trained in and follow the procedure.

## Standard 16: Participation by Operations Personnel in Work Orders

Operations personnel identify potential system and equipment problems and initiate work orders necessary to correct system or equipment problems that may inhibit or prevent plant operations.  Operations personnel monitor the progress of work orders affecting operations to ensure timely completion and closeout of the work orders, so that the components and systems are returned to service.

Among other things:

- Operations personnel identify problems requiring work orders, and initiate work orders to correct those problems

- The operations manager or other appropriate operating personnel periodically review work orders that affect operations to ensure timely completion and closeout of the work orders, so that components and systems are returned to service.

- Personnel responsible for prioritizing work orders consult operations personnel to assure that work orders affecting the operations of the plant are properly prioritized.  .

### Appropriate personnel are trained in and follow procedures applicable to work orders.

## Standard 17:  Records of Operation

The GAO assures that data, reports and other records reasonably necessary for ensuring proper operation and monitoring of the generating asset are collected by trained personnel and retained for at least five years, and longer if appropriate .

## Standard 18:  Unit Performance Testing

The GAO conducts periodic performance tests as appropriate to identify trends and possible improvements in unit operation.  The GAO responds to test results with changes to equipment, policies, routines, or procedures necessary to maintaining unit availability and the unit’s ability to support grid operations consistent with the Unit Plan.

## Standard 19: Emergency Grid Operations

The GAO prepares for conditions that may be reasonably anticipated to occur during periods of stress or shortage on the state’s electric grid.  During such periods of stress or shortage, the GAO makes operational decisions to maximize each unit’s availability and ability to support grid operations.

Among other things the GAO:

### Takes reasonable steps to maintain the ability to communicate with the Control Area Operator all times.

### In preparing for periods of stress or shortage, takes steps to clarify the regulatory requirements, such as emissions, water discharge temperature, etc., which will apply during emergencies,

### When emergencies appear imminent, seeks regulatory relief from those regulatory requirements that reduce output,

### Assists the Control Area Operator in responding to the various kinds of possible problems on the electrical grid, including restoration of service after a disturbance.

### When practical, during periods of stress or shortage, consults with the Control Area Operator before derating a unit or taking a unit off line and defers outages and derates at the Control Area Operator’s request when continued operation is

### Possible and practical,

### Safe to plant personnel and to the public,

### In accordance with applicable law and regulations, and

### Will not cause major damage to the plant.

## Standard 20:  Preparedness for On-Site and Off-Site Emergencies

The GAO plans for, prepares for, and responds to reasonably anticipated emergencies on and off the plant site, primarily to protect plant personnel and the public, and secondarily to minimize damage to maintain the reliability and availability of the plant.

Among other things, the GAO:

### Plans for the continuity of management and communications during emergencies, both within and outside the plant,

### Trains personnel in the emergency plan periodically, and

### Ensures provision of emergency information and materials to personnel.

## Standard 21: Plant Security

To ensure safe and continued operations, each GAO provides a prudent level of security for the plant, its personnel, operating information and communications, stepping up security measures when necessary.

## Standard 22: Readiness

### Until a change in a unit’s long-term status, except during necessary maintenance or forced outages, the GAO is prepared to operate the unit at full available power if the Control Area Operator so requests, after reasonable notice, when such operation is permitted by law and regulation.

### Among other things, the GAO:

### A.  Maintains contingency plans to secure necessary personnel, fuel, and supplies, and

### B.  Prepares facilities for reasonably anticipated severe weather conditions.

## Standard 23: Notification of Changes in Long-Term Status of a Unit

### The GAO notifies the Commission and the Control Area Operator in writing at least 90 days prior to a change in the long-term status of a unit.  The notification includes a description of the planned change.

## Standard 23:  Approval of Changes in Long-Term Status of a Unit

### The GAO maintains a unit in readiness for service in conformance with Standard 22 unless the Commission, after consultation with the Control Area Operator, affirmatively declares that a generation facility is unneeded during a specified period of time.  This standard is applicable only to the extent that the regulatory body with relevant ratemaking authority has instituted a mechanism to compensate the GAO for readiness services provided.

## Standard 25: Transfer of Ownership

The GAO notifies the Commission and the Control Area Operator in writing at least 90 days prior to any change in ownership.

## Standard 26: Planning for Long-Term Unit Storage

### At least 90 days before a change in the long-term status of an electric generation unit, other than permanent shutdown and/or decommissioning, the GAO shall submit to the Commission plans and procedures for storage, reliable restart, and operation of the unit.

## Standard 27: Flow Assisted Corrosion

Where circumstances require it, the GAO has a flow-assisted corrosion program, which identifies vulnerable equipment, provides for regular testing of that equipment, and responds appropriately to prevent high energy pipe failures.

## Standard 28:  Equipment and Systems

GAO complies with these Operation Standards (1-27) considering the design bases (as defined in the Appendix) of plant equipment and critical systems.  The GAO considers the design basis of power plant equipment when as required by other standards it, among other things:

### Establishes procedures for the operation of critical systems at each unit (Ref. Standard No. 7).

### For each system, identifies critical parameters that require monitoring (Ref. Standard No. 8 and 13).

### For each critical parameter, establishes values at which to increase observation of the system or take actions to protect it (Ref. Standard No. 8 and 13).

### Assures that systems are monitored and actions are taken. (Ref. Standard 8 and 13)

### Establishes parameters for operation during periods of stress or shortage on the state’s electric grid (Ref. Standard No. 9 and 19).

### Assures that personnel operating critical systems are trained and qualified (Ref. Standard No. 6).

# Appendix

## A.	Definitions

Design Basis Documents – Vendor and engineering documents used in the design, or used to instruct in the correct operation and maintenance, of the systems and equipment used in the power plant.  Design basis documents consist of OEM Manuals, vendor documents, industry standards, codes and documented engineering assessments.

Documented deviations from the above documents are also considered part of the design basis documents provided there is documented reasoning for those deviations.  Documented reasoning includes the benefit of the deviation and why the deviation is consistent with the Unit Plan.