| 10-21683-1 |  |  | 1 | Gathering |  | Mechanical Joint |  |  | Incorrect Operation |  | 2010-09-03 | 2010-09-03 | Replace Partial Service |  | PE2406 (Yellow or Orange) |  | SAN JOSE | REPLACE RISER; SOAP TEST RISER
| 10-21711-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2010-09-10 | 2010-12-06 | Soap and/or Tape - Other |  | Steel/Wrought Iron |  | SANTA CLARA | SOAP TAPE 3" L.P. MAIN HOLE. A NEW JOB WILL BE DRAWN UP TO REPLACE OR ABANDON 3".
| 10-21718-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2010-09-14 | 2010-12-13 | Replace Dist Main >= 100 ft |  | Steel/Wrought Iron |  | SAN JOSE | INSERTED MAIN DUE TO LEAKS & PIPE CONDITION; INSERTED 2" PL INSIDE 4" STL FROM 1908 DIE TO MULTIPLE LEAKS & POOR PIPE CONDITION
| 10-21745-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-16 | 2011-01-11 | Soap and/or Tape - Other |  | Steel/Wrought Iron |  | SAN JOSE | SOAP & TAPED OVER PITTED SECTION OF 3" MAIN; INSTALLED SOAP & TAPE OVER PITTED SECTION OF 3" L.P. MAIN. SOAP TESTED OK .
| 10-21763-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-14 | 2011-01-10 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | SANTA CLARA | INSTALLED 2 -2" FULL CIRCLE CLAMPS OVER PITTED MAIN; CASED SHORING FOR HOLE. INSTALLED 2 -2" FULL CIRCLE CLAMPS W/ANODES OVER PITTED SECTION OF 2" MAIN. SOAP TESTED OK
| 10-10574-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Plastic Crack Failure |  | 2010-09-08 | 2010-11-29 | Replace Dist Main < 100 ft |  | Aldyl A (Tan or Gray) |  | S.J. | REPLACED 2' OF 2" PIPE.; INSTALLED 24" OF 2" PIPE USED MET FIT COUPLINGS ALSO INSTALLED NEW ELECTROFUSION SERVICE TEE 2" X 1"
| 10-10726-1 |  |  | 1.25 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2010-03-17 | 2011-01-13 | Tighten Cap or Bolt |  | Aldyl A (Tan or Gray) |  | SAN JOSE | TIGHTENED LOOSE ALDYL "A" REPAIR CAP; SOAP TEST "OK" TIGHTENED LEAKING ALDYL "A" REPAIR CAP
| 10-10846-1 |  |  | 1.25 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2010-09-20 | 2010-12-08 | Replace Dist Main < 100 ft |  | PE2406/2708 (Yellow) |  | SAN JOSE | REPLACED 2' OF 1 1/4" MAIN & LEAKING TEE; REPLACED 2' OF 1 1/4" MAIN, & 1 1/4" X 1" ELECTROFUSION TEE TO ADDRESS 5550 HEYLLYER AVE
| 10-11073-1 |  |  | 4 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2010-10-05 | 2010-12-27 | Other | REPLACE PLUG ON 4" M-2 | Steel/Wrought Iron |  | SAN JOSE | REPLACE PLUG IN 4" M-2; REPLACED PLUG ON 4" M-2
| 10-11131-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-07 | 2010-12-23 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | SAN JOSE | PUT FULL CIRCLE CLAMP ON SOAP TESTED
| 10-11277-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Unknown |  | 2010-10-19 | 2011-01-12 | Soap and/or Tape - Other |  | Steel/Wrought Iron |  | GILROY | SOAP & TAPE; "SOAP TEST OK", SOAP & TAPE OVER PITS NEXT TO DRESSER COUPLING
| 10-11278-1 |  |  | 3 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2010-10-18 | 2011-01-11 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | GILROY | TIGHTENED PLUG & CAP OF 3" M-2; TIGHTENED 3" CAP ON M-2, LEFT LOCATION BAN ON M-2 LOCATION
| 10-11320-1 |  |  | 3 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2010-10-26 | 2011-01-20 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | GILROY | INSTALLED LEAK REPAIR CAN 6"; INSTALLED WELDED (ARC) 6" LEAK REPAIR CAN AT 141' N/O FIFTH OVER LEAKING THREADED COUPLING ON MAIN
| 09-10916-1 |  |  | 4 | Distribution Main |  | Other Welds |  |  | Construction Defect |  | 2009-11-17 | 2011-01-21 | Fill Weld - Weld |  | Steel/Wrought Iron |  | MORGAN HILL | ARC WELDED OVER LEAKS; ARC WELD OVER (4) LEAKS ON 6" CAN OVER 4" MAIN
78 | 09-10740-1 |  |  | 2 | Distribution Main >60 PSIG and <20% SYMS |  | Fitting |  |  | Construction Defect |  | 2009-11-02 | 2011-04-29 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | MORGAN HILL | REMOVED, REDOPED & REPLACED PLUG ON GAUGE TAP FITTING; REMOVED, REDOPED & REPLACED PLUG ON GAUGE TAP
| 09-10740-1 | [10 empty] | 2009-11-02 | [5 empty] | MORGAN HILL | INFO ONLY
| 09-20111 |  |  | 1 | Gathering |  | Fitting |  |  |  |  | 2009-03-31 | 2009-03-31 | Replace Partial Service |  | PE2406 (Yellow or Orange) |  | SAN JOSE | STRUCK 1" PLASTIC, DAMAGED PLASTIC NEXT TO 3 WAY TEE; INSTALLED NEW 3 WAY TEE
| 09-20111 |  |  | 1 | Gathering |  | Fitting |  |  |  |  | 2009-03-31 | 2009-03-31 | Replace Partial Service |  | PE2406 (Yellow or Orange) |  | SAN JOSE | STRUCK 1" PLASTIC, DAMAGED PLASTIC NEXT TO 3 WAY TEE; INSTALLED NEW 3WAY TEE; DRAIN WORKS PLUMMING WAS REPAIRING BROKEN WATER LINE IN THE SIDEWALK DURING REPAIR BROKE A 1" PLASTIC SERVICE TO BUILDING #4; COULD NOT WAIT 48HRS FOR USA TO SHOW UP TO FIX WATER PROBLEM
| 09-20216-1 |  |  | 1.25 | Gathering |  | Fitting |  |  | Equipment Malfunction |  | 2009-06-08 | 2010-04-07 | Other | REPLACE RISER | Steel/Wrought Iron |  | SAN JOSE | REPLACE RISER; REPLACE RISER
| 09-20217-1 |  |  | 1.25 | Gathering |  | Fitting |  |  | Equipment Malfunction |  | 2009-06-08 | 2010-04-07 | Other | REPLACE RISER | Steel/Wrought Iron |  | SAN JOSE | REPLACE RISER; REPLACE 1 1/4" RISER
| 09-20319-1 |  |  | 2 | Distribution Main |  | Valves |  |  | Other | NEEDED GREASE | 2009-06-25 | 2010-12-21 | Other | GREASED VALVE (M & C) | Steel/Wrought Iron |  | SAN JSOE | FOUND BURRIED LEAKING VALVE & HAD M& C GREASE IT; FOUND BURRIED, LEAKING 2" MAIN VALVE & HAD T&R GREASE IT. SOAP TESTED O.K.; TIGHTEN M2 CAP SOAP TEST OK
| 09-20415-1 |  |  | 2 | Distribution Main |  | Other |  | M-2 CAP | Unknown |  | 2009-07-18 | 2011-01-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SANTA CLARA | TIGHTEN M2 CAP
| 08-10146-1 |  |  | 6 | Transmission |  | Fitting |  |  | Other | CRACKED CAP | 2008-07-29 | 2009-03-17 | Other | REPLACED CRACKED CAP | Steel/Wrought Iron |  | GILROY | REPLACED CRACKED CAP; REPLACED DAMAGED SAVE-A-VALVE CAP
| 07-10165-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2010-02-24 | 2010-11-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN JOSE | RE-DOPED & TIGHTENED 2" CONTROL CAP; TIGHTENED CAP ON 2" M2 ON 2" MAIN
| 07-10165-1 |  |  |  | Service | [6 empty] | 2007-10-06 | [5 empty] | SAN JOSE
80 | 10-30750-A | 109 |  | 0.5 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-12-02 | 2010-12-20 | Replace Main Valve < 2-inch |  | Steel-Other |  | MOUNTAIN VIEW | EXPOSED & SHUT OF PIN OFF TEE. I REPLACED 1/2" GAUGE TAP VALVE
80 | 11-30558-B |  |  | 16 | Distribution Main > 60 PSIG |  | Line Valve |  |  | Other | NEEDED GREASE | 2011-03-12 | 2011-03-12 | Greased - Other |  | Steel-Other |  | MOUNTAIN VIEW | REQUIRED GREASE TO STOP LEAK.; GREASED VALVE TO STOP LEAK, & SOAP TESTED
80 | 11-30559-B |  |  | 4 | Distribution Main > 60 PSIG |  | Line Valve |  |  | Other | NEEDED GREASE | 2011-03-12 | 2011-03-12 | Greased - Other |  | Steel-Other |  | MOUNTAIN VIEW | REQUIRED GREASE TO STOP LEAK; GREASED VALVE TO STOP LEAK & SOAP TESTED
80 | 11-30563-B |  |  | 1.25 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | Digin/Excavation |  | 2011-03-29 | 2011-03-29 | Mechanical Repair Fitting - Fitting |  | PE2406/2708 (Yellow) |  | MT. VIEW | USED 1 1/4" MET FIT COUPLING; SOAP TEST 1 1/4" MET FIT COUPLING
MCH ELECTRIC, THEY WERE DIGGING BELL HOLE FOR GAS MAIN TEE IN USING BACK HOE THEY DUE INTO 1 1/4" PL GAS MAIN
60 | 11-20309-B | 132 |  | 6 | Transmission >= 20% SMYS |  | Line Valve |  |  | Construction Defect |  | 2011-04-17 | 2011-04-20 | Greased - Other |  | Steel-Other |  | SAN FRANCISCO | GREASED VALVE; GREASE VALVE
60 | 84-27683 |  |  | 20 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1984-10-10 | 1984-10-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | MADE PERM REPAIR ON 20" TRANS MAIN 10-20-84 WELDED 3 PATCHES ON MAIN
60 | 82-40512-1 |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1982-05-10 | 1982-05-12 | Patch Welded |  | Steel/Wrought Iron |  |  | WELDED 6" X 6: PATCH ON BOTTOM OF 17' E/W/L HARVARD 24' S/N/L FELTON
| 82-40512-1 | [10 empty] | 1982-05-10 | [6 empty] | DRILLED VENTED WILL, MUST RETURN IN AM TO COMPLETE JOB
| 91-20829-1 |  |  | 3 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1991-02-06 | 1991-02-09 | Clamp |  | Steel/Wrought Iron |  | S.F. | TEMP REPAIR CLAMP PITT ON 3" STL. T.P. MAIN
| 88-273-1 |  |  | 2 | Transmission |  | Body of Pipe |  |  | Digin |  | 1988-06-21 |  | Replace Pipe |  | Steel/Wrought Iron |  |  | REPAIR 2" TRANSMISSION BY PASS
40 | 93-00211-1 |  |  | 16 | Transmission |  | Valves |  |  | Other |  | 1993-06-21 | 1993-07-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | NO | REPAIR LEAKING VALVE FLANGE
| 99-03204-1 | [10 empty] | 1999-06-30 | [5 empty] | KENTFIELD
| 99-05005-1 | DFM |  | 6 | Transmission |  | Other |  | REINFORCING PAD | Construction Defect |  | 1999-06-22 | 2002-10-22 | Tee Fused Over Defect - Plastic | WELD | Steel/Wrought Iron |  | LARKSPUR | WELDED SAV-A-VALVE OVER VENT HOLE ON REINFORCING PAD; NO CHANGE TO S/O
| 00-00279-1 | [10 empty] | 2000-05-16 | [5 empty] | MILL VALLEY
| 03-00250-1 | [10 empty] | 2003-06-09 | [5 empty] | CORTE MADER
| 10-30128-1 | [10 empty] | 2010-09-10 | [5 empty] | MILL VALLEY
| 10-00119-1 |  |  | 6 | Distribution Main |  | Valves |  |  | External Corrosion |  | 2010-03-03 |  |  |  | Steel/Wrought Iron |  | GREENBRAE
| 07-00127-1 |  |  | 0.75 | Service |  | Riser |  |  | Atmospheric Corrosion |  | 2007-07-10 | 2007-07-10 | Other | SHORTENED RISER VERTICAL. | Steel/Wrought Iron |  | SAN RAFAEL | CUT DOWN RISER & RETHREADED. INST'D. NEW VALVE & BY PASS VALVE; ATMOS. CORR. WAS LOCALIZED TO TOP 3" (+/-) OF RISER
| 03-00062-1 | 21S | 2.2 | 6 | Transmission |  | Physical/Mechanical Joint | Other | FLANGE | Other | LOOSE BOLTS | 2003-07-14 | 2003-08-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | NAPA | REPLACED BOLTS ON 6" FLANGED VALVE
| 03-00047-1 |  |  | 4 | Transmission |  | Other Welds |  |  | Other | BAD WELD | 2003-05-15 | 2003-05-19 | Patch Weld - Weld |  | Steel/Wrought Iron |  | ST. HELENA | STEEL PIT SVC TEE FRIND OUT BAD WELD RE-WELD
| 00-40035-1 |  |  | 0.01 | Service |  | Body of Pipe |  |  | Digin |  | 2000-04-18 | 2000-04-18 | Mechanical Repair Fitting - Fitting |  | TR 418 |  | VALLEJO | INST. 2 PERMA SERTS COUPLINGS & 5' 1" PLAS.
| 02-00008-1 |  |  | 0.25 | Transmission |  | Tap Connection |  |  | Vehicle |  | 2002-02-28 | 2002-02-28 | Other | REPLACED VENT STACK & RECORDER | Other | S.S. | NAPA | SHUT OFF VALVE & REPLACE
| 10-30128 |  |  | 2 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2010-04-01 | 2010-12-06 | Skinner Clamp - Clamp |  | Steel-Other |  | MILL VALLEY | PUT SKINNER CLAMP ON MAIN
40 | 10-31059-1 |  |  | 2 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-04 | 2010-12-21 | Skinner Clamp - Clamp |  | Steel-Other |  | TIBURON | PLACED A SKINNER CLAMP OVER CORROSION PIT; PLACED A SKINNER CLAMP OVER CORROSION PIT ON ZINCH MAIN. SOAP GOOD WRAPPED PIPE AND BACK FILLED
40 | 10-31081-1 |  |  | 2 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-04 | 2010-12-21 | Skinner Clamp - Clamp |  | Steel-Other |  | TIBURON | PUT 2" SKINNER CLAMP ON MAIN
40 | 11-20100-B |  |  | 16 | Transmission >= 20% SMYS |  | Other |  |  | No/Deteriorated Pipe Dope |  | 2011-04-28 | 2011-04-28 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SAN RAFAEL | PUT NEW DOPE ON PLUG AND CAP OF PIN OFF TEE
40 | 11-20044-A |  |  | 0.75 | Distribution Main > 60 PSIG |  | Regulator/Pilot | Threads |  | Construction Defect |  | 2011-02-12 | 2011-02-12 | Replace Partial Service |  | Steel-Other |  | MILL VALLEY | REMOVED & REPLACED CORRODED & LEAKING PIPING, FITTINGS & REG.; REPAIRED LEAKING H.P.R MULTIPLE LEAKS WITH ATMOSPHERIC CORROSION. REPLACED WITH NEW PIPE & EQUIMENT
40 | 11-20039-B |  |  | 4 | Distribution Main > 60 PSIG |  | Line Valve |  |  | Construction Defect |  | 2011-02-07 | 2011-02-07 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SAN RAFAEL | TIGHTENED BOLTS ON FLANGE VALVE
| 09-00812-1 |  |  |  | Single Service |  | Other |  | STOP COCK | Unknown |  | 2009-08-05 | 2009-09-08 | Other | STOP COCK | Steel/Wrought Iron |  | KENTFIELD | REPLACED SERVICE VALVE & FITTED METER SET INSIDE CABINET
| 09-01002-1 |  |  | 0.75 | Single Service |  | Fitting |  |  | Unknown |  | 2009-08-18 | 2009-09-05 | Other | REPLACED SERV VALVE & REG | Steel/Wrought Iron |  | CORTE MADERA | REPLACED SERV. VALVE & REG; REPLACED SERV. VALVE & REG
| 00-00279-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2000-05-16 | 2010-11-15 | Other | REDOPED PLUG & CAP | Steel/Wrought Iron |  | MILL VALLEY | REDOPED PLUG & CAP; REDOPED PLUG & CAP TO SPLIT MUELLER FITTING 1' N/W OF SVC TEE #30
| 03-00103-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2003-03-18 | 2010-12-11 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | KENTFIELD | PUT 6" FULL CIRCLE CLAMP W/ ANODE
| 03-00250-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2003-06-09 | 2000-11-15 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | CORTE MADERA | INSTALLED 3 BOLT 6" SKINNER; MAIN IS 2' INSIDE CURB - IN GRASS AREA.; INSTALLED: (1) 3 BOLT 6" SKINNER CLAMP
| 04-00215 |  |  | 2 | Distribution Main <= 60 PSIG |  | Other |  | SCREWED SADDLE | Other | SCREWED FITTING | 2004-06-04 | 2010-12-07 | Deactivate Dist Main =>1 foot |  | Wrought Iron |  | KENTFIELD | C/O 12' OF 2" SCREWED STL MAIN; INSTALLED: 2" M2, SAVE A VALVE, 11' OF 2" STL MAIN 3/4" STL TEE, 3' OF 3/4" STL
| 05-00144-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2005-05-06 | 2010-11-12 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | MILL VALLEY | INSTALLED: (1) 2 BOLT SS CLAMP (ANODES); MAIN IN BAD SHAPE
| 09-00440-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2009-05-13 | 2010-11-10 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | SAN ANSEIMO | INSTALLED: (1) 1 BOLT PARTIAL 2" SS CLAMP
| 09-00571-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2009-05-13 | 2010-11-10 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | ROSS | CLAMPED TWO LEAKS; ISNTALED ONE FULL CIRCLE CLAMP OVER TWO LEAKS
| 09-00590 |  |  | 1.25 | Distribution Main <= 60 PSIG |  | Plastic Tee Cap |  |  | Construction Defect |  | 2009-06-08 | 2010-12-06 | Tighten Cap/Bolt - Fitting |  | PE2406 (Yellow or Orange) |  | NOVATO | GREASED AND TIGHTEN 1 1/4" TEE CAP; GREASED AND TIGHTEN 1 1/4" TEE CAP
| 10-00346 |  |  | 2 | Distribution Main <= 60 PSIG |  | Body of Pipe | Other |  | Damage by 3rd Party |  | 2010-09-22 | 2010-12-20 | Replace Dist Main < 100 ft |  | Steel-Other |  | MILL VALLEY | WELDED TWO 2" TOP TAPS AND REPLACED 5' OF 2" STEEL MAIN
40 | 10-00215-B |  |  | 4 | Distribution Main > 60 PSIG |  | Other Mechanical Joint |  |  | Other | LOOSE BOLTS | 2010-12-01 | 2010-12-01 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SAN RAFAEL | BLOW OFF FLANGE
| 09-91993-1 |  |  | 0.5 | Single Service |  | Body of Pipe |  |  | Stress Corrosion Cracking |  | 2009-08-26 | 2009-12-04 | Replace Partial Service |  | Copper |  | SAN RAFAEL | C/O 2' OF CU 1/2" & INST. 2' OF 1/2" PL; LEAK ON 1/2" CU 1' OUT FROM SVC TEE, INST BUZZ NUT ON 3/4" STL & INST 2' OF 1/2" PL & CUT TO PL COMP FITTING
| 09-40477 |  |  | 6 | Transmission |  | Valves |  |  | Other | GREASED | 2009-09-24 | 2009-09-24 | Other | REGREASED IN LINE VALVE | Steel/Wrought Iron |  | YOURTVILLE | REGREASED VALVE
| 10-81181-1 | 1 | [9 empty] | 2010-10-05 |  |  |  | Steel/Wrought Iron |  | VALLEJO
|  | 09-00266-1 |  | 10.75 | Distribution Main |  | Other |  | STOP COCK | Construction Defect |  | 2009-04-15 | 2009-05-02 | Other | CHANGED CODE | Steel/Wrought Iron |  | FAIRFAX | CHANGED CODE
| 98-40124-1 |  |  | 2 | Distribution Main |  | Other Welds |  |  | Weld Failure |  | 1998-12-09 | 2010-11-22 | Fill Weld - Weld |  | Steel/Wrought Iron |  | VALLEJO | ARC WELDED OVER BUTT O.A. WELD TO P.C.F.; BUTT WELD INTO P.C.F. LEAKING
44 | 87-39001-1 |  |  | 16 | Transmission |  |  | Valves |  | Other |  | 1987-02-17 | 1987-04-02 | Other |  | Steel/Wrought Iron |  | SONOMA | GREASED OPEN AND CLOSED, OPERATED
44 | 86-40059-1 | 21 |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1986-04-17 | 1986-04-24 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | GRYSERVILLE
44 | 85-40093-1 |  |  | 3 | Transmission |  | Valves |  |  | Other |  | 1985-07-05 | 1985-07-08 | Other |  | Steel/Wrought Iron |  | SANTA ROSA | REPAIRED LEAKING VALVE. REPAIRED GREASE FITTING AND GREASED VALVE
44 | 80-40232-1 |  |  | 12 | Transmission |  | Valves |  |  | Other |  | 1980-11-05 | 1980-11-05 | Other |  | Steel/Wrought Iron |  | SANTA ROSA | V-11 STEM PACKING LEAKING REPACKED VALVE; MAIN NOT EXPOSED
44 | 79-58005 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-03-05 | 1979-03-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PETALLUMA | 12" TRANS MAIN LEAKING DUE TO CORROSION. REPLACED 15' SECTION- TESTED OK. 3-7-79
44 | 77-58017-1 |  |  | 12 | Transmission |  | Fitting |  | SAV-A-VALVE | Corrosion |  | 1977-04-29 | 1977-05-18 | Other | REPLACE CAP | Steel/Wrought Iron |  | PETALUMA | REPLACE CAP SOAP TEST OK
| 77-58012-1 |  |  | 8 | Transmission |  | Fitting |  |  | Material Failure |  | 1977-04-12 | 1977-04-12 | Other |  | Steel/Wrought Iron |  | PETALUMA | 8" VALVE LEAKING. TIGHTEN FLANGE BOLTS SOAP TESTED OK
44 | 77-38023-1 |  |  | 8 | Transmission |  | Valves |  |  | Material Failure |  | 1977-02-22 | 1977-06-13 | Other |  | Steel/Wrought Iron |  | PET. | FOUND 2" VALVE LEAKING ON 8" DRIP. GREASED. SOAP TEST OK; ON VALVE FOR
44 | 75-20011-1 |  |  | 2 | Transmission |  | Fitting | Valves |  | Construction Defect |  | 1975-09-25 | 1976-08-03 | Other |  | Steel/Wrought Iron |  | WINDSOR | 10% IN REG. PIT. 3% IN GROUND 10' N/W OF BOX; REPAIRED LEAKING FITTING IN HPR BOX; GREASED VALVE AND REDOPED 2" PLUG; *SEE ABOVE
44 | 75-18005-1 |  |  | 0.34 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-03-17 | 1976-06-11 | Other |  | Steel/Wrought Iron |  | PETALUMA
44 | 74-40168-1 |  |  | 6 | Transmission |  | Fitting |  |  | Material Failure |  | 1974-03-21 | 1974-05-16 | Other |  | Steel/Wrought Iron |  | FULTE | LEAKING CAP WAS REDOPED AND TIGHTENED
44 | 72-38036-1 |  |  | 12 | Transmission |  | Fitting |  |  | Damage by outside Forces |  | 1972-12-28 | 1973-05-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | INSTALLED COMPRESSION FITTING ON RISER
| 00-40241-1 |  |  | 6 | Transmission |  | Valves |  |  | Other | LACK OF GREASE | 2000-10-11 | 2000-10-11 | Other | GREASE | Steel/Wrought Iron |  | LARKFIELD | VALVE #1 DISTRICT REG 12-121
| 07-02072-1 | 1305-01 |  | 4 | Transmission | 1305-01 | Valves |  |  | Other | NEEDS GREASE | 2007-07-29 | 2007-08-01 | Other | GREASED VALVE | Steel/Wrought Iron |  | SANTA ROSA | GREASED VALVE; GREASED VALVE, SOAP TESTED
| 08-02019-1 | DFM 1307-01 |  | 8 | Transmission |  | Valves |  |  | Other | GREASE | 2008-03-17 | 2008-12-01 | Other | GREASED VALVE | Steel/Wrought Iron |  | WINDSOR | GREASED
| 08-02642-1 | 21C |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2008-09-25 | 2009-04-20 | Tighten Cap or Bolt | OTHER - NEW O-RING | Steel/Wrought Iron |  | COTATI | NEW O RING IN VALVE TEE; NO TEST
44 | 08-12238-1 |  |  | 3 | Distribution Main <= 60 PSIG |  | Line Valve |  |  | Construction Defect |  | 2008-03-03 | 2011-01-12 | Greased - Other |  | Steel-Other |  | ROHNERT PARK | GREASED VALVE; EXCAVATED 3" VALVE CALLED T&R TO COME OUT AND GREASE VALVE TO STOP LEAK. VALVE WAS UNDER ASPHALT
| 08-12276-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Unknown |  | 2008-03-05 | 2008-04-30 | Other | TIGHTEN | Steel/Wrought Iron |  | SEBASTOPOL | TIGHTEN GAUGE RISER VALVES SOAP TEST OK. SMALL LEAK ON SIDE OF REG (T&R). COULD NOT FIND LEAK ON VALVE ABOVE REG 462.; ALAN -WAYNG. 1) LEAKING RELEF ON REG #462 (JOHNSON & PETERS) 2) LEAKS ON GAUGE RISER ON 8" 450*, WILL NEED TO DIG UP FOR M&C 3) LEAK ON VALVE ABOVE REG #462- NEED TO GREASE DOWN GRADE TO #2+
| 08-12761-1 | 1305-01 |  | 2 | Transmission |  | Other |  | CAP | Unknown |  | 2008-03-17 | 2008-05-16 | Other | TIGHTEN | Steel/Wrought Iron |  | SONOMA
44 | 08-13009-1 |  |  | 2 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2008-02-28 | 2011-01-27 | Patch Weld - Weld |  | Steel-Other |  | SANTA ROSA | WELDED 2C59 PATCHES ON 2" STL.
| 09-00308-1 | 21D | 36.91 | 12 | Transmission |  | Fitting |  |  | Other |  | 2009-03-13 | 2009-04-15 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | PETALUMA | FOUND LEAK AT PCF FIXED LEAK; TORQUE AND TACK WELD BOLTS ON P.C.F. TO FIX LEAK
44 | 09-00470-1 |  |  | 3 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2009-07-13 | 2011-01-11 | Skinner Clamp - Clamp |  | Steel-Other |  | SANTA ROSA | INSTALLED SKINNER CLAMP; INSTALLED SKINNER CLAMP ON 3" STEEL GAS MAIN 1062 CLARK ST. SANTA ROSA
| 10-00002-1 |  | 21E | 0.75 | Transmission |  | Valves |  |  | Other | GREASED | 2010-01-05 | 2010-01-06 | Other | GREASED | Steel/Wrought Iron |  | CLOVERDALE
| 10-00054-1 | 21 |  | 12.75 | Transmission |  | Other |  | 3/4" PLUG IN TOP OF TDW P.C.F. | Incorrect Operation |  | 2010-02-11 | 2010-02-11 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SANTA ROSA | REMOVED, CLEANED, REINSTALLED 3/4" PLUG; REMOVED, CLEANED, REINSTALLED THREAD SEALECT AND REINSTALLED PLUG IN TOP OF 12" TOW FITTING
| 10-00063-1 | 21D |  | 16 | Transmission |  | Fitting |  |  | Other | COMP. PLUG | 2010-02-18 | 2010-02-18 | Other | 2" COMP. PLUG | Steel/Wrought Iron |  | PETALUMA | EXTRACT, RE-DOPE, RE-INSERTED COMP. PLUG SAV-A-VALVE; FOUND 2" SAV-A-VALVE ON 16" LINE 21 LEAKING. GL EXTRACTED COMPLETION PLUG, RE-DOPED, AND RE-INSERTED. INSTALL E.T.S. AT THIS LOCATION
| 10-00084-1 | 1305-01 |  | 0.25 | Transmission |  | Other |  | ELECTRONIC RECORDER | Other |  | 2010-03-10 | 2010-03-30 | Other |  | Other | STAINLESS STEEL TUBING | SONOMA | INSIDE RECORDER BOX, REPLACED FITTINGS; SOAPED FITTINGS
44 | 10-00319-1 | 1301-01 | 0.35 | 0.75 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-09 | [5 empty] | PETALUMA
44 | 10-02790-1 |  |  | 4 | Distribution Main <= 60 PSIG |  | Girth Weld |  |  | Weld Failure |  | 2010-10-13 | 2011-01-06 | Welded Sleeve/Can - Weld |  | Steel-Other |  | FORESTVILLE | WELDED CAN OVER GIRTH WELD; 4" STEEL DISTRIBUTION MAIN UNDER FENCE WELDED CAN OVER GIRTH WELD
44 | 10-02884-1 |  |  | 2 | Distribution Main <= 60 PSIG |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-13 | 2011-01-10 | Tighten Cap or Bolt |  | Steel-Other |  | SANTA ROSA; | REMOVED INTERNAL PLUG APPLIED PIPE DOPE INSTALLED INTERNAL PLUG; REMOVED CAP & REMOVED INTERNAL PLUG REDOPED AND INSTALLED PLUG AND CAP SOAP TESTED OK
| 10-02884-1 | [10 empty] | 2010-10-13 | [5 empty] | SANTA ROSA
44 | 10-03156-1 |  |  | 2 | Distribution Main <= 60 PSIG |  | Pressure Control Fittings |  |  | No/Deteriorated Pipe Dope |  | 2010-10-21 | 2011-01-07 | Remove/Replace Completion Plug Fitting |  | Steel-Other |  | SEBASTOPOL | EXTRACT, REPLACE TEFLON TAPE, DOPE NEW 2" COMPLETION PLUG; EXTRACT, REPLACE, TEFLON TAPE AND DOPE NEW COMPLETION PLUG ON 2" PCF-SIDE TAP
44 | 10-03177-1 |  |  | 1.5 | Distribution Main <= 60 PSIG |  | Line Valve |  |  | Other |  | 2010-10-28 | 2011-01-18 | Greased - Other |  | Wrought Iron |  | GRATON | GREASED VALVE IN HPR BOX/AT R-390; GREASED 1 1/2" VALVE TO STOP LEAK
44 | 10-03296-1 |  |  | 2 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2010-11-01 | 2011-01-10 | Skinner Clamp - Clamp |  | Steel-Other |  | SEBASTOPOL | INSTALLED 2" SKINNER CLAMP; SOAP TEST ONLY
44 | 11-00041-1 | 1305-01 |  | 0.75 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other |  | 2011-02-03 | 2011-02-08 | Greased - Other |  | Steel-Other |  | SONOMA | COULD NOT SAVE LEAK WITHOUT INPUTTING DEPTH OF DENTS; GREASED V-1; GREASED V-1 AT R-548
44 | 11-00062-1 |  |  | 8 | Distribution Main >60 PSIG and <20% SYMS |  | Body of Pipe |  |  | External Corrosion |  | 2011-03-25 | 2011-04-22 | Type B Sleeve - Weld |  | Steel-Other |  | PENNGROVE | INSTALLED TYPE B SLEEVE; INSTALLED TYPE B SLEEVE FOUGE COVERED UNDER SLEEVE SLEEVE THICKNESS IS 0.375 MATERIAL CONE #02.-1077 SLEEVE INFOR P.O. 3500-838928 RYCO STEEL INC. A572 GR50 50K E8E 306 8625 "I.D. X 24.00"
44 | 11-00134-B |  |  | 0.5 | Branch Service |  | Plastic Tee Cap |  |  | Unknown |  | 2011-06-29 | 2011-06-29 | Replace Plastic Tee Cap - Plastic |  | PE2406 (Yellow or Orange) |  | SANTA ROSA | REPLACE SERVICE TEE CAP; SOAP TESTED
98 | 11-51002-B | 300A | 242.48A | 2 | Transmission |  | Line Valve |  |  |  |  | 2011-04-21 | 2011-05-06 | Tighten Cap/Bolt - Fitting | GREASED - OTHER | Steel-Other |  | TEHACHAPI | GREASED, TIGHTENED BUTTON HEAD
98 | 11-51002-B | 300A | 242.48A | 2 | Transmission >= 20% SMYS |  | Line Valve |  |  |  |  | 2011-04-21 |  |  |  | Steel-Other |  | TEHACHAPI
98 | 11-55002-A | 300A | 10.85A | 0.5 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2011-04-18 |  |  |  | Steel-Other |  | NEEDLES DISTRICT
37 | 96-10018-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1996-09-12 | 1996-09-27 | Other |  | Steel/Wrought Iron |  | EUREKA | VALVE HIGH TO HIGH SET, GREASED VALVE
36 | 94-30085-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1994-03-21 | 1995-12-08 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EUREKA | TIGHTEN NUT ON VALVE STEM
37 | 94-30458-1 |  |  | 2 | Distribution Main <= 60 PSIG |  | Fitting |  |  | Construction Defect |  | 1994-07-05 | 2011-01-02 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | ARCATA | TIGHTEN CAP
37 | 94-30459-1 |  |  | 2 | Distribution Main <= 60 PSIG |  | Threads |  |  | Construction Defect |  | 1994-07-07 | 2011-01-03 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | ARCATA | TIGHTEN CAP
19 | 95-30106-1 |  |  | 10 | Other | I | Body of Pipe |  |  | Corrosion |  | 1995-10-03 | 1995-10-03 | Patch Welded |  | Steel/Wrought Iron |  | ARCATA | AND SAVE-A-VALVE NIPPLE 1"
36 | 73-10158-1 |  |  | 0.75 | Service | TRANS | Body of Pipe |  | H.P.R. | Damage by outside Forces |  | 1973-11-30 | 1973-11-30 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | WEINHOLDT OLD SERVICE & H.P.R. CUT OFF NEW SERVICE RUN TO DISTR. MAIN 12-6-73
36 | 79-30163-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1979-12-07 | 1980-01-11 | Other | INST. GREASE FITTING | Steel/Wrought Iron |  | EUREKA | INST. GREASE FITTING STEM & GREASE VALVE
36 | 80-30178-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1980-11-26 | 1981-04-30 | Other |  | Steel/Wrought Iron |  | HUMBOLDT HILL | DOWN GRADE TO 3 & RECHECK IN 6 MOS
36 | 80-30179-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1980-11-26 | 1980-12-23 | Other |  | Steel/Wrought Iron |  | HUMBOLDT HILL
37 | 81-30084-1 |  |  | 4 | Transmission |  | Valves |  | 4" | Other | NO GREASE | 1981-09-21 | 1982-01-05 | Other |  | Steel/Wrought Iron |  | ARC
36 | 81-30112-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1981-10-20 | 1981-10-26 | Other |  | Steel/Wrought Iron |  | EUR | FOUND FLANGE ON 6" VALVE LEAKING TIGHTENED BOLTS GREASED VALVE
36 | 82-10091-1 |  |  | 4 | Transmission |  | Longitudinal Weld |  |  | Construction Defect |  | 1982-08-03 | 1982-08-03 | Other | 6" CAN/WELD | Steel/Wrought Iron
36 | 82-10091-1 |  |  | 4 | Transmission |  | Longitudinal Weld |  |  | Construction Defect |  | 1982-08-03 | 1982-08-03 | Patch Welded |  | Steel/Wrought Iron |  | EUREKA
36 | 84-30007-1 |  |  | 4 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 1984-01-19 | 1984-05-04 | Other |  | Steel/Wrought Iron |  | EUR | BAD WELD ON MAIN INSTALLED CAN
37 | 86-10011-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1986-02-18 | 1986-03-04 | Replace Pipe and/or Service |  | Plastic |  | BLUE LAKE | 1/2" PL. SER WAS WASHED OUT BY ROCKS CREEK. TIED TERM. AIR TO -NEED ENG TO NEW PLAN
36 | 86-30009-1 |  |  | 4 | Transmission |  | Other |  |  | Other |  | 1986-01-27 | 1986-11-05 | Other |  | Other |  | EUR | BAD GASKET/ REPLACED
| 86-30281-1 | [10 empty] | 1986-10-13 | [5 empty] | EUREKA | HOUSELINE LEAK REPORTED TO MAN @ SCHOOL
| 09-50167 |  |  | 4 | Distribution Main <= 60 PSIG |  | Other Mechanical Joint |  |  | Other |  | 2009-06-29 | 2010-12-07 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | ARCATA | VALVE BURRIED LEAKING @ FLANGE; DUG UP & EXPOSED VALVE WITH LEAK ON FLANGE. TIGHTENED FLANGE TO STOP LEAK. INSTALLED 3M MARKER BALL & RECOMMEND THAT VALVE BE REMOVED FROM SERVICE. VALVE WAS BURRIED & NOW FUNCTIONING 6' NORTH OF SERCICE @ 1361 Q ST.
35 | 09-95096-1 |  |  | 2 |  |  | Body of Pipe |  |  | External Corrosion |  | 2009-08-28 | 2011-02-20 | Skinner Clamp - Clamp |  | Steel-Other |  | RIO DELL | INSTALLED 2" SKINNER CLAMP; INSTALLED SKINNER CLAMP 14" EAST OF SERVICE MAIN 40" DEEP. SHITTY HAND DIG. MUDDY FILLED WITH WATTER LOTS OF RIVER ROCK (BIG SUCKERS)!
| 10-10025 |  |  | 2 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | Construction Defect |  | 2010-10-20 | 2011-01-06 | Fill Weld - Weld |  | Steel-Other |  | FORTUNA | REPAIRED LEAK ON WELD; LEAK ON WELD REPAIRED WELD
87 | 11-80003-B | 402/DFM | 16.09 | 6 | Transmission >= 20% SMYS |  | Other |  |  | Other | FAILED THREMAL CHECK VALVE | 2011-01-20 | 2011-02-08 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | ANDERSON | INSTALLED & BLEW DOWN VALVE. PLUG WAS ON BODY OF VALVE
87 | 74-00026-1 |  |  | 6 | Transmission |  | Fitting |  |  | Damage by outside Forces |  | 1974-05-29 | 1974-08-14 | Other |  | Steel/Wrought Iron
| 10-05020-1 |  |  | 1.25 | Distribution Main |  | Fitting |  |  | Other | DRIED OUT PIPE DOPE | 2010-10-13 | 2010-11-16 | Other | REMOVE, DOPE, REINSTALL 1 1/4" MUELLER TEE CAP | Steel/Wrought Iron |  | AUBURN | TIGHTEN 1 1/4 TEE CAP + DOPE; SOAP TEST TEE CAP. REMOVE, DOPE TIGHTEN TEE CAP.
| 10-03112-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Other | M2 CAP | 2010-08-24 | 2010-11-12 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | SHERIDAN | LEAK ON MAIN BETWEEN 5631 & 5641; TRENCHED OUT 2' TEES FOUND LOOSE LINESTOPPER CAP.
| 09-01551-1 |  |  | 2 | Distribution Main |  | Plastic Tee Cap |  |  | Other | CRACKED CAP | 2000-06-13 | 2010-11-09 | Aldyl A Overcap - Plastic |  | Aldyl A (Tan or Gray) |  | ROSEVILLE | CRACK ON ALDYL CAP. ALDYL ELECTROFUSION OVERCAP; TEES ON ALDYL CAP CRACKED SERVICE 1005-1007 AZURE CT. REPLACED WITH OVERCAP.
| 09-00562-1 |  |  | 0.75 | Single Service |  | Valves |  |  | Equipment Malfunction |  | 2009-04-13 | 2009-10-07 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | ROSEVILLE | RAISED RISER + INSTALLED NEW SERVICE VALVE. SOAPED ... LEAKS; SOAP TEST. THIS SERVICE IS TOTALLY UNDER PAVEMENT FROM MAIN TO RISER. SERVICE VALVE WAS IN CONTACT WITH GROUND AT TOP OF RISER.
| 09-00474-1 | 4518 |  | 0.25 | Transmission |  | Regulator |  |  | Other | LOOSE NIPPLE | 2009-03-24 | 2010-07-30 | Other | TIGHTEN NIPPLE | Steel/Wrought Iron |  | ROSEVILLE | 1/4" NIPPLE ON R-SIDE MONITOR IN REG. STATION R-385. REMOVED 1/4" NIPPLE - REDOPED + TIGHTENED; MONITOR REGULATOR ON R-SIDE RUN.
11 | 11-20031-A |  |  | 0.25 | Distribution Main |  | Body of Pipe |  |  | Damage by 3rd Party |  | 03/06/1201 | 2011-03-06 | Other | SHUT + CAPED VALVES | Steel-Other |  | YUBA CITY | SHUT AND CAPED VALVES; CUT AND CAPED VALVES. SOAP TEST. CUT + CAPED LINES IN REG PIT.
| 09-00600-1 |  |  |  | Transmission |  | Fitting |  |  | Other | GREASE | 2009-03-25 | 2009-04-15 | Other | GREASED VALVE | Steel/Wrought Iron |  | OLIVEHURST | GREASE VALVE
| 09-00061-1 |  |  | 0.75 | Transmission |  | Other |  | 3/4" SERVICE TEE REINFORCING PIECE OF WELD | Weld Failure |  | 2009-03-26 | 2009-03-26 | Other |  | Steel/Wrought Iron |  | SHERIDAN | SOAP TEST WELD ON EXISTING SERVICE TEE; 457' N/O ELEC TAP LINE EASEMENT / SERVICE TEE. WASHED OVER LEAK WITH ARC WELD; EXISTING WELD ON REINFORCING PIECE ON SERVICE TEE WAS LEAKING - ARC WELDER WASHED OVER LEAK TO REPAIR. SERVICE TO 4710 N. DOWD WAS BEING ABANDONED. 3/4" LEAK AND REPAIR SERVICE TEE.
11 | 71-00040-0 |  |  | 6 | Transmission |  | Regulator |  |  | Other |  | 1971-08-23 | 1971-10-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | MAIN & SER. REPLACED ON GM...
11 | 71-00040-1 | [10 empty] | 1971-08-23
11 | 71-00040-1 |  |  | 6 | Transmission |  | Regulator |  |  | Other |  |  | 1972-10-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron
11 | 71-00041-1 |  |  | 6 | Transmission |  | Regulator |  |  | Other |  | 1971-08-23 | 1971-10-15 | Replace Pipe and/or Service |  |  |  |  | MAIN & SER. REPAIRED ON GM 4660 05.
11 | 71-00041-1 | [10 empty] | 1971-08-23 | [6 empty] | ERROR ON ORIGINAL COL 1B.
11 | 71-00041-1 | [10 empty] | 1971-08-23
11 | 72-40018-1 |  |  | 8.62 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 1972-08-30 | 1972-09-06 | Other |  | Steel/Wrought Iron |  |  | OTHER = SOAP TESTED WELD FOUND LEAKING; LEAK INSIDE 16" VALVE. LEAK IN WELD ON BOTTOM OF 8" CROSSOVER. REWELDED. TRANSMISSION VALVE...
11 | 73-00091-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-12-05 | 1979-04-19 | Patch Welded |  | Steel/Wrought Iron |  | LIVE OAK | LEAK ST. = LINE 50; LEAK IN MAIN ON HIGHWAY 99 30' N/O MAILBOX 11400 EASTSIDE OF ROAD MARKED YELLOW X. FOUND LEAK ON 8" LINE 50. NO RECHECK REQUIRED 4/27/79.
11 | 73-00091-1 | [10 empty] | 1973-12-05 | [5 empty] | LIVE OAK | LEAK IN MAIN ON HWY-99 0FT. NORTH OF MAILBOX 11400 E-SIDE OF RD. MARKED YELLOW X.
11 | 73-40057-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-05-16 | 1973-05-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | INSTALLED 2' NEW PIPE.
11 | 73-40057-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-05-16 | 1973-05-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | CALL IN. 8" - 124. 2MI. S/O BEALE TAP.
11 | 73-40081-1 |  |  | 8 | Transmission |  | Valves |  |  | Material Failure |  | 1973-12-26 | 1974-08-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | MARYSVILLE | REPLACED 8" CHECK VALVE.
11 | 75-60004-1 |  |  | 3 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-01-20 | 1975-01-21 | Other |  | Steel/Wrought Iron |  | LIVE OAK | WELD ON DEAD END LEAKING. INSTALLED NEW 3" FLANGE W/ DEAD-END
11 | 76-00005-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-05-24 | 1979-04-25 | Patch Welded |  | Steel/Wrought Iron |  | MARYSVILLE | DOWNGRADE TO #3.
11 | 77-40003-1 |  |  | 8 | Transmission |  | Other |  |  | Corrosion |  | 1977-01-11 | 1977-01-12 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | LEAK ST. = LINE 302.
11 | 77-40015-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1977-06-22 | 1977-06-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SUTTER BUTTES WEST GAS FIELD | INTERNAL CORROSION; LEAK 840' E/O DIP TUBE AT FENCE LINE WHERE LINE CROSSES WEST BUTTE ROAD.
11 | 77-60037-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1977-07-28 | 1977-07-28 | Clamp |  | Steel/Wrought Iron |  |  | LEAK ST = LINE 121.
11 | 78-60071-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-09-06 | 1978-09-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OLIVEHURST | E-SIDE 2820' N/ VIRGINIA RD. STRUCK BY ... EQUIPMENT.
11 | 79-30159-1 |  |  | 8 | Transmission |  | Fitting |  |  | Construction Defect |  | 1979-07-27 | 1980-01-14 | Other |  | Steel/Wrought Iron |  | MARYSVILLE | FOREMAN SAYS PLUG LEAKING - UNABLE TO FIX UNTIL HIGH PRESSURE PLUGING UNIT IS ... 1-21-80.
11 | 79-20159-1 |  |  |  | Transmission | [6 empty] | 1979-07-27 | [5 empty] | MARYSVILLE | 100' SOUTH OF 8TH ON WALNUT ST.
9 | 79-40014-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1979-04-02 | 1979-04-02 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | LEAK ST = LINE 302
11 | 80-40039-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1980-07-15 | 1980-11-17 | Patch Welded |  | Steel/Wrought Iron |  | WHEATLAND | LEAK ST = LINE 124.
9 | 80-40038-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-12-21 | 1980-12-22 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SUTTER CO. | LEAK ST. = LINE 302; INTERNAL CORROSION LEAK ON BOTTOM 8" LINE. WELDED FULL ENCIRCLEMENT BAND TO REPAIR W/ DODGE PATCH. PITTING + RUST LOCALIZED IN AREA OF REPAIR.
11 | 81-00154-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1981-04-08 | 1981-04-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SUTTER | LEAK ST = LINE 302. INTERNAL CORROSION; NEW 6" GR X-42 D.156" W.J.
11 | 81-00166-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1981-10-22 | 1981-10-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SUTTER COUNTY | LEAK ST = LINE 302. INTERNAL CORROSION; REPLACED 7'-3" PIPE. SOTUH OF SOUTH BUTE RD + EAST OF WEST BUTE RD.
9 | 81-00203-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1981-10-12 | 1981-10-13 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SUTTER CO. | LEAK ST. = LINE 302. INTERNAL CORROSION; REPLACED 32" PIPE 6 5/8" ODX.156N
11 | 82-00128-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1982-11-28 | 1982-11-29 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | LEAK ST = LINE 302. INTERNAL CORROSION; INSTALLED 10" SLEEVE.
9 | 83-00007-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1983-01-06 | 1983-01-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | LEAK ST. = LINE 302. INTERNAL CORROSION; 6" LEAK. C.C. REPLACE 21" OF LINE.
11 | 83-00166-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1983-11-21 | 1984-01-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | MARYSVILLE | S.W. CORNER/ RAMIREZ ST. AND 24TH ST.
9 | 85-00001-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1985-01-09 | 1985-11-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SUTTER CO. | LEAK ST = LINE 302. INTERNAL CORROSION. GM4467247; 8" 302 S/ ...
9 | 85-00001-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1985-01-09 | 1985-11-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SUTTER CO. | GM 4467242; SEE J. LE GATE. G.C. GAS IN GOING TO REPLACE THIS SECTION OF MAIN. SEE ATTACHED. 8" 302 S/ BUTTES... SPECIAL LEAK SURVEY.
11 | 85-00046-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1985-03-28 | 1985-03-28 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | MARYSVILLE | LEAK ST = LINE 50; 14TH ST + E ST.
11 | 85-00049-1 |  |  | 8 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 1985-04-12 | 1985-08-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | LINDA-OLIVEHURST | ...RESTAURANT. LEAK IS NEXT TO PIPE.
11 | 85-00135-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1985-09-24 | 1985-10-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | YUBA CITY | LEAK ST = LIVE OAK BLVD. REPAIRED 10-18-85 BLEVINS; HPR BOX @ CURBSIDE E-SIDE 10' S/NR NORTHGATE DR.
11 | 85-00134-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1985-09-24 | 1985-10-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | YUBA CITY | LEAK ST. = LIVE OAK BLVD. REPAIRED 10-18-85 BLEVINS; HPR BOX AT CURB SIDE TIWN PALMS MOTEL E-SIDE 250' +- S/ NORTH-GATE.
11 | 86-00075-1 |  |  | 8 | Transmission |  | Fitting |  |  | Other |  | 1986-06-18 | 1986-06-25 | Other |  | Steel/Wrought Iron |  | LINDA (MARYSVILLE) | VALVE PIT (V-22.02) E-SIDE 8"-124.
11 | 86-00280-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1986-10-14 | 1986-11-12 | Other |  | Steel/Wrought Iron |  | TIERRA BUENA | N/W CORNER ELMER & BUTTE HSE. RD., GAS VALVE IN ST. LUBED VALVE, STOPPED LEAK.
11 | 86-00291-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1986-10-16 | 1986-11-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | YUBA CITY | LEAK ST = LINE 55. AT PLUG ON BACK SIDE OF V-34. TAPED PLUG 11-21-86.
11 | 86-00290-1 |  |  | 12 | Transmission |  | Valves |  |  | Other |  | 1986-10-16 | 1986-11-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | YUBA CITY | LEAK ST. = LINE 55; AT PLUG ON BACK SIDE OF V-33. TAPED PLUG 11-21-86.
11 | 86-00289-1 |  |  | 12 | Transmission |  | Valves |  |  | Other |  | 1986-10-16 | 1986-11-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | YUBA CITY | LEAK ST = LINE 55; AT PLUG ON BACK SIDE OF V-31. TAPED PLUG 11-21-86.
11 | 86-00288-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1986-10-16 | 1986-11-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | YUBA CITY | LEAK ST = LINE 55; AT PLUG IN FRONT OF NUMBER PLATE, V-38. TAPED PLUG 11-21-86.
11 | 86-00287-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1984-10-16 | 1986-11-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | YUBA CITY | LEAK ST = LINE 55; AT PLUG IN FRON OF NUMBER PLATE, V-30. TAPED PLUG 11-21-86.
11 | 86-00286-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1986-10-16 | 1986-11-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | YUBA CITY | LEAK ST = LINE 55; AT PLUG IN FRONT OF NUMBER PLATE, V-7. TAPED PLUG 11-01-86.
11 | 86-00296-1 |  |  | 2 | Transmission |  | Fitting |  |  | Other |  | 1986-10-16 | 1986-11-25 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | YUBA CITY | LEAK ST = LINE 55; AT REG. R-2.
11 | 86-00294-1 |  |  | 2 | Transmission |  | Fitting |  |  | Other |  | 1986-10-16 | 1986-11-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | YUBA CITY | LEAK ST = LINE 55; AT REG R-4.
11 | 86-00297-1 |  |  | 2 | Transmission |  | Fitting |  |  | Other |  | 1986-10-16 | 1986-11-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | YUBA CITY | LEAK ST = LINE 55; AT REG R-7.
11 | 86-00299-1 |  |  | 8 | Transmission |  | Valves |  |  | Other |  | 1986-10-16 | 1986-11-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | YUBA CITY | LEAK ST. = LINE 55; FROM BEHIND VALVES 41 & 42.
11 | 86-00418-1 |  |  | 3 | Transmission |  | Valves |  |  | Other |  | 1986-11-11 | 1986-11-19 | Other |  | Steel/Wrought Iron |  | OLIVEHURST | LEAK ST. = LINE 124; OLIVEHURST REG STA. MRC10. VALVE LEAK-BLOWOFF VALVE "B".
11 | 87-00260-1 |  |  | 8 | Transmission |  | Fitting |  |  | Other |  | 1987-10-21 | 1987-11-05 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MARYSVILLE | LEAK ST. = LINE 50; TIGHTENED PACKING NUT METRIC VLV. STOPPED LEAK.
11 | 87-00283-1 |  |  | 2 | Transmission |  | Tap Connection |  |  | Other |  | 1987-10-23 | 1990-01-23 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MARYSVILLE | INSTERSECTION OF 9TH/ST. + WALNUT WHERE MAIN BRANCHES. REPLACED 2" MULLER TEE CAP FEEDING REG. STATION 9TH + YUBA ST. (SEE PLAT SHEET)
11 | 86-00298-1 |  |  | 2 | Transmission |  | Fitting |  |  | Other |  | 1986-10-16 | 1986-11-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | YUBA CITY | LEAK ST = LINE 55; AT REG R-3. TIGHTENED TUBE FITTINGS 11-21-86.
11 | 87-00347-1 |  |  | 3 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1987-12-07 | 1987-12-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SUTTER CO | LEAK ST = LINE 302. INTERNAL CORROSION; PIT HOLE EXTERNAL LOOKED LIKE... 1/16" +- DEEP INTERNAL COULD NOT SEE ANY PIT. PER CHARLIE CURTIS LEAK WAS INTERNAL...
9 | 87-00348-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1987-12-02 | 1988-03-30 | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER | LEAK ST. = LINE 302. REPLACED 15' OF 4". INTERNAL CORROSION.
9 | 87-00343-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1987-12-21 | 1987-12-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SUTTER CO. | LEAK ST = LINE 302; CLAMP IS 24 FEET EAST FROM EXPOSED SECTION OF 4" PIPE. REPLACED 15' OF 4" PIPE 7 1/2' BOTH SIDE OF LEAK. FIELD WRAP & PTW. 3-30-88.
9 | 88-90020-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1988-06-17 | 1988-06-17 | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER CO. | REPLACED 8 FT OF 6" L-302.
11 | 88-90095-1 |  |  | 8 | Transmission |  | Valves |  |  | Other |  | 1988-10-28 | 1988-11-09 | Other |  | Steel/Wrought Iron |  | LINDA | LUBED VALVE.
11 | 91-00083-1 | 50 |  | 8 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 1991-09-05 | 1992-01-16 | Other |  | Steel/Wrought Iron |  | LIVE OAK | 36' S/O MELTON CIR ON LINE 50. FOUND ABANDONNED T ON LINE 50 - CAP LOOSE INST. HIGH DOME CAP + REDOPE. PERM REP... TO FOLLOW.
11 | 91-00095-1 |  |  | 8 | Transmission |  | Valves |  |  | Damage by outside Forces |  | 1991-10-02 | 1991-11-05 | Replace Pipe |  | Steel/Wrought Iron |  | MARYSVILLE | SECTION OF MAIN REPLACED. GM 4808192THIS SECTION OF GAS MAIN WAS REPLCED BY G.C. GAS 12/91.
| 92-00007-1 | 121 | 1.4 | 6 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1992-02-27 | 1992-02-27 | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER | REPLACED 26" SECTION...
11 | 92-00058-1 |  |  | 4 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 1992-08-04 | 1992-08-04 | Other |  | Steel/Wrought Iron |  | DIST. 10 - MARYSVILLE | W-SIDE 1015' N/MAGNOLIA RD AT SERVICE TEE. REPAIRED LEAK ON TEE - WELDED OVER.
11 | 93-00009-1 |  |  | 4 | Transmission |  | Girth Weld |  |  | Material Failure |  | 1994-05-18 | 1994-05-18 | Other |  | Steel/Wrought Iron |  | DIST. 10 | E/S HWY 70 104' S/O ... FOUND WELD LEAKING - HAD GC REPAIR...
11 | 93-00009-1 | [10 empty] | 1993-01-19 | [5 empty] | MARYSVILLE
| 93-00073-1 |  |  | 8 | Transmission |  | Valves |  |  | Other |  | 1993-09-29 | 1994-10-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | YUBA CITY | VAULT R-8, R-9. TIGHTENED PACKING GLAND ON VALVE STEMS.
| 93-00073-1 | [10 empty] | 1993-09-29 | [5 empty] | YUBA CITY
11 | 93-00073-1 | [10 empty] | 1993-09-29 | [5 empty] | YUBA CITY
| 93-00073-1 | [10 empty] | 1993-09-29 | [5 empty] | YUBA CITY | NOT A SAFETY HAZARD. R-8 IN VAULT - REGULATOR PARTS ON ORDER.
11 | 93-00072-1 |  |  | 4 |  |  | Valves |  |  | Other |  | 1993-09-29 | 1994-01-18 | Other |  | Steel/Wrought Iron |  | YUBA CITY | VALVE BOX 17. WORKED VALVE NO LEAK.
11 | 93-0122-1 |  |  |  | Transmission |  | Fitting |  |  | Other |  | 1993-11-24 | 1993-12-10 | Other |  | Steel/Wrought Iron |  | WHEATLAND | REPLACED LEAKING FITTING ON TUBING.
11 | 93--1 |  |  | 6 | Transmission |  | Fitting |  |  | Other |  | 1993-11-24 | 1993-12-08 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | LINCOLN | REG/ MONITOR CRACKED/ PINHLE LEAK @ METRIC. TIGHTENED FITTINGS AROUND TUBING.
11 | 94-00009-1 |  |  | 4 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 1994-02-15 |  | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MARYSVILLE | IN FRONT OF HOUSE ON WELD. INST TEMP CLAMP. INSTALLED SLEEVE OVER WELD.
11 | 94-00027-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1994-03-24 | 1994-04-05 | Other |  | Steel/Wrought Iron |  | OLIVEHURST | FITTING OF VALVE #2- MARKED/YELLOW PAINT. REMOVED R.V. ON 6" BALL VALVE & INSTALLED PLUG.
11 | 94-00086-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Material Failure |  | 1994-05-24 | 1994-05-24 | Other |  | Steel/Wrought Iron |  | LIVE OAK | S/S EAGER 98' W/O L.O. BLVD. VAL. LEAKS ON HPR SET. REPLACED BOTH 3/4" S.O. VALVES.
11 | 94-00216-1 |  |  | 3 | Transmission |  | Fitting |  |  | Other |  | 1994-11-02 | 1995-10-24 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | YUBA CITY | GIVEN TO T&R 9-26-95. REG. AND MONITOR VAULT.
11 | 94-00216-1 | [10 empty] | 1994-11-02 | [5 empty] | YUBA CITY
11 | 95-00048-1 |  |  | 8 | Transmission |  | Valves |  |  | Other |  | 1995-05-22 | 1995-06-05 | Other |  | Steel/Wrought Iron |  | LINDA | AT VALVE #2. GREASE VALVE 20.64.
11 | 95-00049-1 |  |  | 12 | Transmission |  | Valves |  |  | Other |  | 1995-05-22 | 1995-06-05 | Other |  | Steel/Wrought Iron |  | LINDA | AT VALVE #1. GREASE VALVE 20.64.
11 | 95-00094-1 | 124 |  | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1995-10-25 | 1995-10-27 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | WHEATLAND | DIRT AREA ABOVE PIPE. E/S HWY 65 6/10 MILE N/O REG STATION 46. EXTERNAL CORROSION CAUSED LEAK. REPAIRED WITH AN EIGHT INCH SLEEVE (0.375" INT); FOOT PATROL 200 YARDS IN BOTH DIRECTIONS FROM HIGHEST READING --> 0% GAS. LOCATION IS IN COW PASTURE; NO BUILDINGS WITHIN 1/2 MILE RADIUS. APPROXIMATE M.P. 12.41 @ 8" L-124. NOTE: PMR MOULDER IDENTIFIED A "GAS LEAK" DURING MARK-AND-LOCATE WORK ON 10/25/95. G.C. INVESTIGATED AND DUG-UP LEAK ON FRIDAY 10/27. INSTALLED AN 8" REPAIR SLEEVE. X-RA O.K. SAV-A-VALVE CAPPED. LOWERED LINE PRESSURE TP 175 PSIG FOR PRECAUTIONS.
11 | 96-00052-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other |  | 1996-07-24 | 1996-10-10 | Other |  | Steel/Wrought Iron |  | YUBA CITY | 2ND ST. SO./ DOG POUND. REMOVED 2 STAGE REGS & BOXES. INSTALLED NEW ABOVE GROUND 2 STAGE REGS. NS.
11 | 96-00079-1 |  |  | 8 | Transmission |  | Fitting |  |  | Other |  | 1996-09-27 | 1997-11-07 | Other |  | Steel/Wrought Iron |  | YUBA CITY | REG. PIT MARKED "M". INSTALLED NEW GASKET ON PLATE HOLDER.
11 | 96-00079-1 |  |  | 8 | Transmission |  | Fitting |  |  | Other |  | 1997-11-07 | 1997-11-07 | Other |  | Steel/Wrought Iron |  | YUBA CITY | 8" METER TUBE. INSTALLED NEW GASKET ON PLATE HOLDER.
11 | 96-00080-1 |  |  | 1 | Transmission |  | Valves |  |  | Other |  | 1996-09-27 | 1997-06-27 | Other |  | Steel/Wrought Iron |  | YUBA CITY | GREASED VALVE
| 00-00043-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Digin |  | 2000-06-12 | 2000-06-13 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | YUBA CITY | 5398 HWY 99 SUTTER COUNTY YUBA CITY. GC GAS MADE REPAIRS; ALL SOAP TESTED, BY CREW. SEE ATTACHED SKETCH.
| 00-00043-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Digin |  | 06/12/0000 | 2000-06-13 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | YUBA CITY | 5398 HWY 99 SUTTER COUNTY YUBA CITY. GC GAS MADE REPAIRS; ALL SOAP TESTED, BY CREW. SEE ATTACHED SKETCH.
20 | 93-00030-1 |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1993-02-09 | 1993-07-07 | Other |  | Steel/Wrought Iron |  | LOOMIS | GREASE VALVE.
| 93-00269-1 |  |  | 6 | Transmission |  | Tap Connection |  |  | Material Failure |  | 1993-10-20 | 1993-10-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | AUBURN | LEAK AT CAP FOR TEE TO HI TO HI #176. REMOVED CAP. REPLACED "O" RING. REDOPED CAP. STOPPED LEAK.
20 | 84-243-1 |  |  | 4 | Transmission |  | Valves |  |  | Material Failure |  | 1984-12-07 | 1984-12-07 | Other |  | Steel/Wrought Iron |  | ROCKRIDGE | ... GREASE STEM BROKE, CHECK CALL IN STEM FAILED TO OPERATE ALLOWING GAS TO ... REPLACE THREADS ... AND GREASED VALVE ...
20 | 96-00099-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1996-05-28 | 1997-06-26 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | PENRYN | GREASED VALVE.
20 | 96-00109-1 |  |  | 2 | Transmission |  | Valves |  |  | Other |  | 1996-06-04 | 1997-07-12 | Other |  | Steel/Wrought Iron |  | NEWCASTLE | GREASED VALVE.
20 | 96-00121-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1996-06-19 | 1997-06-26 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | OPHIR | TIGHTENED PLUG.
20 | 92-00047-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1992-10-02 | 1992-11-30 | Other |  | Steel/Wrought Iron |  | ELDOR HILLS | GREASED VALVE (ABOVE GROUND).
15 | 90-00451-1 |  |  | 6 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1990-10-23 | 1990-10-24 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | GRASS VALLEY | ON BOLTED FLANGE 6' W/O V-23.72. TIGHTENED BOLTS ON FLANGE TO STOP LEAK.
| 07-40043-1 |  |  | 0.5 | Service |  | Riser |  |  | Damage by outside Forces | VEHICLE | 2007-03-31 | 2007-03-31 | Replace Partial Service |  | Steel/Wrought Iron |  | RIDGECREST | AT METER NEXT TO HOUSE. AT HOUSE ON W/S OF GARAGE. RISER VALVE SNAPPED AT THREADS. REPLACED RISER ONLY.
| 08-20521-1 | DFM OFF OF 372 |  | 2 | Transmission |  | Valves |  |  | Construction Defect |  | 2008-07-31 | 2009-09-23 | Other | BOILDER PLANT #2 REG. #1 PRI. VALVE IN CASING. GREASED VALVES; SOAP TESTED ALL OK. | Steel/Wrought Iron |  | RIDGECREST
| 08-20525-1 |  |  |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2008-07-31 | 2009-07-16 | Other | OPENED VALVE AGAINST SEAT | Steel/Wrought Iron |  | RIDGECREST | VALVE #1 N/OF TOWN STA. R-522. OPENED VALVE COMPLETELY, RESEATED SEAL; SOAP TESTED.
| 08-20517-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | VALVE | 2008-07-30 | 2008-07-30 | Other | GREASED VALVE | Steel/Wrought Iron |  | RIDGECREST | SALT WELLS ACCESS RE. CHINA LAKE CALIFORNIA.
| 07-40037-1 |  |  | 1 | Service | DISTRIBUTION MAIN | Plastic Tee Cap |  |  | Material Failure |  | 2007-03-20 | 2007-03-20 | Other | REPLACED BROKEN CAP ON SERV. TEE; REPLACED BROKEN CAP ON SERVICE TEE TO 603 WOODROW OILDALE. SOAP TESTED CAP WITH GAS. | TR 418 |  | OILDALE | IN ALLEY BEHIND 603 WOODROW OILDALE (SERVICE TEE). REPLACED BROKEN CAP ON SERVICE TEE TO 603 WOODROW OILDALE.
| 08-20161-1 |  |  | 8 | Transmission |  | Valves |  |  | Construction Defect |  | 2008-07-25 | 2009-03-27 | Other | GREASE | Steel/Wrought Iron |  | BAKERSFIELD | GOSFORD RO.C V-D401
| 09-20193-1 |  |  | 0.75 | Gathering |  | Other |  | 3/4" NIPPLE BELOW STOPCOCK | Construction Defect |  | 2009-08-11 | 2009-09-21 | Other | DOPED + RETIGHTEN NIPPLE | PE2406/2708 (Yellow) |  | BAKERSFIELD | ON RISER AT 4838 BURR ST. A,B,C,+D. DOPED AND RETIGHTENED NIPPLE; SOAP TEST.
| 09-20123-1 |  |  |  | Transmission |  | Valves |  |  | Construction Defect |  | 2009-07-09 | 2009-07-17 | Other | GREASE VALVE | Steel/Wrought Iron |  | BAKERSFIELD | BY-PASS VALVE @ BRANDAGE + "V" STREETS ON L-1425. GREASED VALVE RECHECKED; CHECK WITH ORION.
| 09-20124-1 | 142 |  | 8 | Transmission |  | Fitting |  |  | Construction Defect |  | 2009-07-09 | 2009-09-27 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | BAKERSFIELD | BRUNDAGE & "V" STREET NORTH PIT. TIGHTENED FITTINGS.
| 09-20125-1 | 142 |  | 8 | Transmission |  | Other |  | TREADS ON PIPE. | Construction Defect |  | 2009-07-09 | 2009-10-05 | Deactivated Entire Service |  | Steel/Wrought Iron |  | BAKERSFIELD | MIDDLE REG PIT. 130' N/O BRUNDAGE. CUT SERVICE OFF AT MAIN; SOAP TEST GOOD. 3/4 LINE WAS GAGE TAP NOT BEING USED. C/O AT MAIN. LOCATION OF C/O TO REPAIR LEAK IN VALT.
| 09-40165-1 |  |  | 0.5 | Gathering |  | Plastic Tee Cap |  |  | Material Failure |  | 2009-10-08 | 2009-10-08 | Replace Plastic Tee Cap - Plastic |  | PE2406 (Yellow or Orange) |  | BAKERSFIELD | IN G-5 BOX OVER 1/2" SERVICE; ON SERVICE TEE CAP @ MAIN. REPLACED BROKEN PLASTIC CAP. W/2" SERVICE IS INSERTED UNDER BACK HOUSE HAS G-5 WITH VENT IN ALLEY. 4" PLASTIC IS 7' OFF NORTH FENCE. REPLACED SPLIT CAP.
| 09-81430-1 |  |  | 0.5 | Gathering |  | Other |  | THREADS ON RISE | Construction Defect |  | 2009-12-20 | 2009-12-28 | Replace Partial Service |  | PE2406 (Yellow or Orange) |  | BAKERSFIELD | ON RISER AT APT. BUILDING IN ALLEY. REPLACED RISER WITH NEW; REPLACED RISER WITH NEW LONG RISER.
| 10-20323-1 |  |  | 1.25 | Distribution Main |  | Plastic Tee Cap |  |  | Plastic Crack Failure |  | 2010-09-15 | 2010-12-07 | Replace Plastic Tee Cap - Plastic |  | PE2406 (Yellow or Orange) |  | BAKERSFIELD | MAIN CAP LEAKING; 1409 RALSTON ST. REPLACED CRACKED SERVICE TEE CAP. LINE SIZE 21.00; SOAP TESTED SERVICE TEE CAP. REPLACED CRACKED SERVICE TEE CAP.
| 10-20566-1 |  |  | 10 | Transmission |  | Valves |  |  | Construction Defect |  | 2010-05-14 | 2010-07-27 | Other | GREASE VALVE | Steel/Wrought Iron |  | DESERT LAKE | BORAX DFM 20 MULE TEAM RD DESERT LAKES. GREASED VALVE; SOAP TESTED.
| 10-20500-1 |  |  | 6 | Transmission |  | Fitting |  |  | Construction Defect |  | 2010-01-06 | 2010-01-15 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | RIDGECREST | RIDGECREST PRIMARY STATION. REMOVED, REDOPED FITTINGS, AND TIGHTENED FITTINGS; SOAP TESTED.
| 10-20629-1 |  |  | 4 | Transmission |  | Fitting |  |  | Construction Defect |  | 2010-06-23 | 2010-07-20 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | KRAMER | 41100 HWY 395 BORON SEGS III @ MTR. SET. REMOVED, REDOPED, REPLACED VARIOUS FITTINGS, REMOVE TURBINE CART. GREASED "O" RING.
13 | 11-60008-B | 151 | 10.43 | 6 | Transmission >= 20% SMYS |  | Line Valve |  |  | Construction Defect |  | 2011-02-10 | 2011-02-10 | Greased - Other |  | Steel-Other |  | RICHVALE | AT VALVE #24. GREASED VALVE. GREASED TRANS VALVE.
13 | 11-60009-B | 151 | 10.43 | 6 | Transmission >= 20% SMYS |  | Line Valve |  |  | Construction Defect |  | 2011-02-10 | 2011-02-10 | Greased - Other |  | Steel-Other |  | RICHVALE | AT VALVE #31. GREASED VALVE. GREASED TRANS VALVE.
| 09-20226-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2009-06-02 | 2009-07-07 | Other | TIGHTEN PIN OFF CAPS | Steel/Wrought Iron |  | CHICO | REMOVED INSLET & OUTLET PIN OFF TEE CAPS - TAPED & REPAIRED LEAK.
| 09-90031-1 |  |  | 3 | Transmission |  | Fitting |  |  | Construction Defect |  | 2009-02-03 | 2009-12-05 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | GRIDLEY | PLUG; SOAP TEST GOOD. TIGHTENED PLUG ON 1/4" METRIC.
10 | 95-50971-1 |  |  | 8 | Transmission |  | Fitting |  |  | Other |  | 1995-10-14 | 1996-04-10 | Other |  | Steel/Wrought Iron |  | OROVILLE | ENTERED NEW LEAK & COMPLETED. AT VALVE # (034) AT N/E CORNER IN STREET. GREASED VALVE.
19 | 90-10004-1 |  |  | 2 | Transmission |  | Other |  |  | Other |  | 1990-01-19 | 1990-02-08 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MILLS ORCHARD
14 | 81-00003-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other |  | 1981-05-04 | 1982-04-26 | Other | TIGHTENED 2 VALVE TEE CAPS | Steel/Wrought Iron |  | WILLOWS
14 | 80-00006-1 |  |  | 0.25 | Transmission |  | Valves |  |  | Other |  | 1980-07-25 | 1981-02-24 | Other |  | Steel/Wrought Iron
14 | 80-00005-1 |  |  | 1.25 | Transmission |  | Valves |  |  | Other |  | 1980-07-24 | 1980-07-30 | Other |  | Steel/Wrought Iron |  | WILLOWS | E/S RD. KK 21' S/O RD. 48 2' NORTH EAST OF VALVE 12.52. TERMINATED LINE AT VALVE NO. W01 WITH A SOLID STEEL PLUG. WRAPPED VALVE AND ABANDONED IN PLACE AND REMOVED VALVE FRAME AND COVER.
19 | 87-10005-1 |  |  | 2 | Transmission |  | Regulator |  |  | Other |  | 1987-01-29 | 1988-01-28 | Other |  | Steel/Wrought Iron |  |  | REAPIRED FUZZ LEAK AT CONNECTION ON REGULATOR.
19 | 95-10002-1 |  |  | 10 | Transmission |  | Valves |  |  | Other |  | 1995-01-18 | 1995-02-10 | Other |  | Steel/Wrought Iron |  | CHICO | NO GAS LEAKAGE AFTER LUBING VALVE. DELETE -LEAK. VALVE AT MCFADEN. LUBED VALVE.
17 | 95-30010-1 |  |  | 8 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 1995-05-08 | 1995-11-29 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | PARADISE | E/S NEAL RD. 59' S/O VALVE #304. FOUND LEAK ON 8" WELD. GAVE TO G.C.; GIRTH WELD LEAKING AT 6:00 O'CLOCK. CAUTION ABANDONED SERVICE TEE (H.P.) 57' S/O VALVE #304.
19 | 95-10005-1 |  |  | 8 | Transmission |  | Fitting |  |  | Construction Defect |  | 1995-07-11 | 1995-11-27 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | PARADISE | SAVE-A-VALVE & 112' E/O NEAL RD. REDOPED & TIGHTENED PLUG AND CAP. (3/4" FITTING) FOUND SAVE-A-VALVE LEAKING 6" N/O 8" P.C.F. & 112' E/O NEAL ROAD. REDOPED & TIGHTENED PLUG AND CAP. 11-27-95.
19 | 90-10003-1 |  |  | 2 | Transmission |  | Other |  |  | Other |  | 1990-01-15 | 1990-02-02 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | CHICO
16 | 95-20013-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1995-02-28 | 1995-07-27 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | CHICO | GIANELLA RD. REPAIRED LEAKS ON HIGH TO HIGH SET NO LEAKAGE FOUND IN GROUND.
43 | 95-40031-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1995-08-07 | 1995-09-17 | Other |  | Steel/Wrought Iron |  | NAPA | GREASED 3/4" VALVE. FOUND ABANDONED VALVE TO OLD H.P.R VALVE IS LEAKING.
42 | 95-20062-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1995-05-20 | 1996-11-01 | Other |  | Steel/Wrought Iron |  | BENICIA | SOAP AND GREASED VALVE.
42 | 95-20062-1 |  |  | 0.34 | Transmission |  | Valves |  |  | Other |  | 1995-05-20 | 1996-06-15 | Other |  | Steel/Wrought Iron |  | BENICIA | GREASED & OPERATED VALVE. ELECTRIC U.G.
42 | 75-20014-1 |  |  | 24 | Transmission |  | Fitting |  |  | Other |  | 1975-01-07 | 1975-01-29 | Other |  | Steel/Wrought Iron |  | VALLEJO | HERMANN STA. 10%. SMALL LEAKS ON FITTINGS; SHUT OFF VALVE #4 FROM TOP & GROUND FILTERS IN CAGE. TIGHTENED SEVERAL FITTINGS IN STATION...
42 | 73-40026-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-02-26 | 1973-02-28 | Patch Welded |  | Steel/Wrought Iron |  | VALLEJO | 856 ANNETTE; LEAK REPAIRED ON TRANS. MAIN PERMANENT REPAIR 2/28/73. THE ABOVE LEAK WAS P. REPAIRED BY WELDING PATCHES 5X4" ON 12" TRANSMISSION MAIN.
42 | 74-20077-1 |  |  | 12 | Transmission |  | Valves |  |  | Other |  | 1974-01-11 | 1974-01-15 | Other |  | Steel/Wrought Iron |  | VALLEJO | KENTUCKY & TUOLUMNE 10%+. NO U.G. ELECT. 1% READING FROM SAND PIPE AT S/E CORNER .03 READING AT PIT; MANHOLE COVER.
42 | 82-20559-1 |  |  | 8 | Transmission |  | Other Welds |  |  | Construction Defect |  | 1982-02-24 | 1982-08-12 | Other |  | Steel/Wrought Iron |  | NAPA | H.P. MAIN LEAKING. OVER MAIN IN PARKING STRIP APPROX. 25 E OF HICKORY.
52 | 71-00157 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1971-10-19 | 1971-10-20 | Other |  | Steel/Wrought Iron |  | SACRAMENTO | STOPPED LEAK AT MAIN VALVE BY REGREASING.
52 | 83-58000-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-10-28 | 1983-11-10 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SACRAMENTO | 12/2/83 POSTED FORM 'C' ... DENSITY 12/5/83 ... CHG REC'D 12/5/83 ...; 2-HOLES 1/16'' DIA (APPROX.)
52 | 76-91000-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-12-06 | 1976-12-09 | Patch Welded |  | Steel-Other |  | SACRAMENTO
52 | 81-58004-1 | 108 |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1981-06-29 | 1981-06-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SACRAMENTO | BAND COVER (1) HOLE 3/4'' DIA. AND FIVE HVY PITS RANGE, .200, .160, .166, .190, .100.
52 | 81-58002-1 | 108 |  | 16 | Transmission |  | Body of Pipe |  |  | Compression Coupling |  | 1981-06-22 | 1981-06-23 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SACRAMENTO | FORM 'C' 8/12/81; POSTED DENSITY; POSTED CHG. REC'D.; SEE ATTACHED DWG.; INST'D FULL ENCIRCLEMENT SLEEVE.
52 | 81-58001-1 | 108 |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1981-06-16 | 1981-06-17 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SACRAMENTO | FORM 'C' 8/12/81; POSTED DENSITY; POSTED CHG REC'D.; .2 HOLES 1/4'' DIA. & 2 HOLES - 3/4'' DIA.; 28 PIT RANGE .08 .160 .180 .180 .190 .156 .200 .190 .166 .140 .160 .186 ... .220 .210 .170 .164 .100 .150 .090 .21 .220 .200 .190 .186 .190 .200 ... FULL CIRCLEMENT SLEEVE, ASTM-A .375'' WT.
52 | 81-58003-1 | 108 |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1981-06-29 | 1981-06-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SACRAMENTO | FORM 'C' 8/12/81; POSTED DENSITY; POSTED CHG. REC'D.; #1 BAND COVER 1 HOLE 3/4'' DIA X 4'' LONG & 11 PITS RANGE .055, .050, .180, .100, .055, .180, .150, .100, .160, .170
52 | 79-58001-1 | 108 |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-11-07 | 1979-11-08 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SACRAMENTO | SSN ... FORM C 11/30/79; DENSITY AMT CHG. REC'D. ; LEAK REPAIRED BY GENERAL CONSTRUCTION - GAS; WELDED A 16'' SLEEVE.;
52 | 79-38001-1 | 108 |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-06-22 | 1979-06-22 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SACRAMENTO | FORM C 11/30/74; DENSITY AMT CHG REC'D 12/5/79.; FOUND ELECTROLYSIS LEAK ON A 16' TRANSMISSION 108 MAIN, MADE PERMANENT REPAIR, WELDED A ... 12'' WIDE AROUND GAS MAIN, BY ...
52 | 74-91002-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1974-04-12 | 1974-04-12 | Other | WELDED A 2'' ALL STEEL SAV-A-VALVE OVER LEAK | Steel/Wrought Iron |  | SACRAMENTO | POSTED DENSITY ... PLOT 108-39 4/15/74.; REPAIRED A SMALL 1 1/2'' X 1 1/2 ELECTOLYSIS LEAK ON A 16'' TRANSMISSION MAIN. WELDED A 2'' ALL STEEL SAV-A-VALVE OVER LEAK. INSTALLED A 32LB. MAGNESIUM LEAK. PITT 1 1/2'' X 1 1/2''.; WELDED A 2'' ALL STEEL SAV-A-VALVE OVER LEAK.
52 | 75-18000-1 | 116 |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-07-14 | 1975-11-04 | Patch Welded |  | Steel/Wrought Iron |  | DAVIS | LEAK SHT - 11-11-75; DENSITY - 11/11/75; CHG. REC'D - 11-11-75.; FILE.; LINE 116. ; FOUND CORROSION HOLE, ON 8'' MAIN, THE SIZE OF A DIME, WITH A PINHOLE LEAKING. G.C. ARC WELDER, DAVE COOPER, WELDED A 6 1/2'' X 7'' PATEN OVER HOLE.
|  |  |  | 16 | Transmission | [6 empty] | 1977-02-15 | [5 empty] | DAVIS | RUST ON MAIN WAS CONDITION GOOD.
|  |  |  | 12.75 | Transmission | [6 empty] | 1977-02-15 | [5 empty] | DAVIS | W.O. 4249-C - 1124- ...
|  |  |  | 75 | Transmission | [12 empty] | DAVIS
52 | 74-91001-1 | 116 |  | 8 | Transmission |  | Tap Connection |  |  | Corrosion |  | 1974-01-02 | 1974-01-04 | Other |  | Steel/Wrought Iron |  | SACRAMENTO | POSTED 1-7-75.; EXTERNAL CORROSION. THREADS ON 3/4 NIPPLE AT BASE OF 2224 VALOC WERE P... AWAY CAUSING LEAK. NIPPLE WAS CUT OFF. FLASH ... LINE... WELDING ...; SERVICE # 116-19-(40-127) F.S. 525+17
52 | 73-91000-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-04-10 | 1973-04-10 | Patch Welded |  | Steel/Wrought Iron |  | SACRAMENTO | PLAT 5-10-75; WALL MAP SENT ...; DENSITY 5-10-73.
50 | 73-18004-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-07-02 | 1973-07-11 | Patch Welded |  | Steel/Wrought Iron |  | DAVIS | ...
52 | 80-58001-1 |  |  | 6 | Transmission |  | Girth Weld |  |  | Damage by outside Forces |  | 1980-06-23 | 1980-06-25 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | NORTH SACRAMENTO | (1) POSTED FORM 'C'. (2) POSTED DENSITY. (3) POSTED CHG. REC'D.;
52 | 74-58000-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-03-01 | 1974-03-04 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | 12'' LINE 11 ... EAST OF V9.68. LEAK 4'' LONG ... ; LEAK AREA, IS A 4'' GOUGE DONE BY EQUIPMENT-PIPE IS NOT CRACKED PER BILL ... 3-8-74.
52 | 77-38001-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1977-03-23 | 1977-03-24 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | DAVIS | POSTED LEAK REPORT 3/29/77. DENSITY 3/30/77. CHG REC'D 3/30/77.; REPAIR LEAK LINE # 150-6''. BETWEEN VALVE #15.18 AND 17.75 ... TAP .9 OF MILE... WEST OF ... 17.75 DITCH CROSSING. INSTALLED (1) 6'' SLEEVE, 12'' LONG, ..375'' WT TO STOP LEAK. EXTENSIVE CORROSION ON BOTH SIDES AT LEAK. SECTION SHOULD BE LOWERED BY REPLACEMENT.
48 | 77-38001-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1977-03-23 | 1977-03-24 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | CONTACTED M.R. O.E. LONG - 3-... REGARDING CONDITION AND DEPTH OF LINE AND ... MADE UP TO LOWER LINE AT A LATER DATE. ; LEAK ON BOTTOM OF PIPE. INSTALLED FULL ENCIRCLEMENT SLEEVE ... TO REPAIR LEAK.
| 77-38001-1 |  |  | 6 | [13 empty] | DAVIS | REPAIR LEAK LINE #150-6'' BETWEEN VALVE #15.18 AND 17.75 TAP OF MILE WEST OF VALVE 17.75. INSTALLED (1) 6'' SLEEVE, 12'' LONG, .375'' WT TO STOP LEAK. EXTENSIVE CORROSION ON BOTH SIDES OF LEAK. SECTION SHOULD BE LOWERED BY REPLACEMENT.; MAIN WAS 8'' DEEP AND WAS PIITTED BAD.
52 | 76-90001-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-12-08 | 1976-12-09 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | NOTED 1-5-70. LEAK FORM 1/7 CF. DENSITY 1/7CF. CHANGE REC 1/7 CF. ; EXTERNAL CORROSION - 7 O'CLOCK; HOLE SIZE 1/16'' X 3/8'' - CORRODED AREA ... PERMANENT REPAIRS - WELD SPLIT SLEEVE .188 WALL.
48 | 72-90001-1 |  |  | 10 | Transmission |  | Drip |  |  | Corrosion |  | 1972-02-18 | 1972-02-24 | Patch Welded |  | Steel/Wrought Iron |  | DAVIS
48 | 72-90000-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-09-26 | 1972-09-27 | Patch Welded |  | Steel/Wrought Iron
48 | 73-57000-1 |  |  | 0.75 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-03-02 | 1973-03-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron
48 | 72-90001-1 |  |  | 10 | Transmission |  | Drip |  |  | Corrosion |  | 1972-02-18 | 1972-02-24 | Patch Welded |  | Steel/Wrought Iron |  | DAVIS | 150.; POSTSED ... 11/ ...;
48 | 72-90000-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-09-26 | 1972-09-27 | Patch Welded |  | Steel/Wrought Iron |  |  | HERE SIZE 1/32" X 1/32" - CORROSION AREA 1"X1" WELD PATCH. 3"X3" - .250 WALL ROUND CORNERS.
52 | 78-58002-1 |  |  | 18 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-08-09 | 1978-08-10 | Patch Welded |  | Steel/Wrought Iron |  | DAVIS, UNINC. | INST'D 4" X 6" PATCH .250" WT 1" SAVE-A-VALVE NIPPLE. EXTERNAL RUST HEAVY ONLY IN THE SMALL AREA OF THE LEAK LOCATION/ OTHERWISE NO RUST.
52 | 78-90003-1 |  |  | 8 | Transmission |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1978-01-10 | 1978-01-11 | Other |  | Steel/Wrought Iron |  |  | LEAK IN FLANGES IF VALVE "S" TOWARDS 16"- LINE 210 - RIO VISTA "Y" MIXER STATION. REMOVED OLD GASKET AND REPLACED WITH A NEW GASKET - VALVE "J" ROCKWELL FIG 4749.
52 | 78-91000-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-01-06 | 1978-01-07 | Other |  | Steel/Wrought Iron |  | DAVIS | INST'D 2" SAV-A-VALVE NIPPLE. ELECTROLYSIS LEAK 1/8" HOLE. ELECTROLYSIS HOLE .125 DEEP. WRAP IS DOUBLE WRAP AND LOOKS GOOD BUT BRITTLE AND BREAKS AWAY EASY.
52 | 78-25000-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-07-07 | 1978-07-08 |  |  | Steel/Wrought Iron |  | DAVIS | INST'D 2 1/2" X 2 1/2" PATCH W/ 1" SAV-A-VALVE NIPPLE. ELECTROLYSIS LEAK. WHEN WRAP IS KNOCKED OF, SOME RUST SPOTS ARE VISIBLE - NON VISIBLE CORROSION BUT SURFACE RUST.
| 78-58001-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-08-01 | 1978-08-02 | Other |  | Steel/Wrought Iron |  |  | ELECTROLYSIS HOLE INST'D SAV-A-VALVE NIPPLE. WRAP IS DOUBLE WRAP IN VERY POOR CONDITION.
52 | 77-58000-3 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1977-07-05 | 1977-07-15 | Patch Welded |  | Steel/Wrought Iron |  | SACRAMENTO | INSTALLED REPAIR LEAK. INSTALLED PATCHES TO REPAIR PITTING OF PIPE.
52 | 75-91000-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1975-07-16 | 1975-07-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | DAVIS | REPAIRS BY GCGAS 7-16 &7-17 1995. WO 4196 1502-2-220.
48 | 74-58002-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1974-05-31 | 1974-08-07 | Patch Welded |  | Steel/Wrought Iron |  | SACRAMENTO
50 | 73-18005-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-07-02 | 1973-07-13 | Patch Welded |  | Steel/Wrought Iron |  | SACRAMENTO
50 | 71-58001-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1971-12-13 | 1971-12-13 | Replace Pipe and/or Service |  | Steel/Wrought Iron
50 |  |  |  | 8 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1971-12-13 | 1971-12-13 | Replace Pipe and/or Service |  | Steel-Other |  | WOODLAND
52 | 74-91000-1 |  |  | 16 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 1974-02-15 | 1974-02-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | F.S. 3935+95. POINT OF RUPTURE. LINE 172 LINE BREAK MILE POINT 74.57 ... FLOOD CONTROL FILL ADOBE, SAND, ROCK... PLAT 176-43. W.O. 4149-B74. CONCRETE CUT OFF WALL.
46 | 74-40004-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Other |  | 1974-01-17 | 1974-01-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron
19 | 75-00003-1 |  |  | 8 | Transmission |  | Valves |  |  | Other |  | 1975-12-04 | 1976-04-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | LEAK SURVEYED VALVE 7.80 NEAL RD. WITH FLAME PACK. NO LEAKS FOUND. 4-14-77. VAKVE 7.80 NEAL RD, N/SUTTER (VALVE UPSTREAM OF PRIMARY REG SET)
19 | 92-10001-1 | 42.97 |  | 10 | Transmission |  | Fitting |  |  | Other |  | 1992-01-18 | 1992-02-03 | Other |  | Steel/Wrought Iron |  | CHICO | LINE VALVE # @ MIDWAY AND ORO-CHICO HWAY. REPAIRED FITTING ON 10" BALL VAVE.
19 | 90-10013-1 | 50 | 41.2 | 6 | Transmission |  |  |  |  | Digin |  | 00/22/1990 |  | Other |  | Steel/Wrought Iron |  |  | 6" LINE 50 M.P. 41.20. REPLACED 4' OF 6" MAIN. MAIN REPLACEMENT IN PROGRESS. EXISTING MAIN IS BEING REPLACED WITH 10" ON GM4W1294. MAIN REPLACED GM4 ...
19 | 90-10002-1 | 50 | 33.41 | 6 | Transmission |  | Other |  |  | Other |  | 1990-01-11 | 1990-02-05 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | CHICO
19 | 86-10001-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1986-01-21 | 1988-03-09 | Other |  | Steel/Wrought Iron |  |  | LINE 50 SHT. 23
19 | 78-00001-1 |  |  | 6 | Transmission |  | Longitudinal Weld |  |  | Material Failure |  | 1978-04-25 | 1978-05-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CHICO | SEE WO. 4104 E-78. F.S. 1889420 & FS 1886490 MAIN 50.
19 | 75-00004-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1975-10-22 | 1975-10-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | LEAK REPAIRED + MAIN REPAIRED ON G.G. 485178 (COMP. 12-1-75)
19 | 72-00001-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-01-20 | 1972-07-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | LINE 50; AT APPROX 11AM 1-20-72 CREW ... CALLED TO ... GAS LEAK ... IN ... TRANSMISSION 50 ST CHICO OROVILLE ... SQUAW CREEK. GAS USE BLOWING THROUGH A 1/4" PUNCTURE ... 6" ... BY TOOTH OF BUTTE CO ... EXCAVATING TO REMOVE LARGE ... TEMP. REPAIRS WERE MADE BY INSTALLING A TWO U BOLT SERVICE SADDLE OVER RUPTURED MAIN WITH 24" EH 1 1/4" ... + VALVE ... INSTALLED AROUND STAND PIPE TO ... TRANS. MAIN #50 HAD APPROX. 19" ... BED. 2-4 BOLT SERVICE SADDLE INSTALLED OVER RUPTURE. PERMANENT REPLACEMENT DONE ON H.O. 4007-D.
19 | 93-10001-1 | 128 | 4.46 | 4 | Transmission |  | Valves |  |  | Other |  | 1993-01-15 | 1996-11-26 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | GLENN CO. | TIGHTENED PLUGS ON TWO VALVES LOCATED IN VALVE BOX - NO LEAKS PRESENT NOW.
19 | 91-10004-1 | 128 | 4.46 | 3 | Transmission |  | Valves |  |  | Other |  | 1991-01-30 | 1991-08-29 | Other |  | Steel/Wrought Iron |  | GLENN CO. | FOUND FUZZ LEAK ON METRIC, TIGHTENED PACKING.
19 | 90-10006-1 | 128 | 4.46 |  | Transmission |  | Other |  |  | Other |  | 1990-01-30 | 1990-02-07 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | GLENN CO.
19 | 73-00001-1 |  |  | 3.5 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-04-06 | 1973-04-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | L-128. REPLACED 30" SECTION OF 3" PIPE.
19 | 73-00002-1 |  |  | 3 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1973-08-30 | 1973-08-31 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | LINE 128; RIPPER TOOTH STUCK HOLE IN PIPE. REPLACED 3' SECTION OF PIPE WITH .216 WALL SMLS PIPE. SEE W.D. 4299-D.
19 | 85-00003-1 |  |  | 3 | Transmission |  | Body of Pipe |  |  | Digin |  | 1985-06-25 | 1985-06-25 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ORO BEND | LINE 128 SHT. 4. REPLACED 4' OF 3" PIPE.
19 | 81-00004-1 |  |  | 3 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1981-09-26 | 1981-09-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | W/S RD "S" W/O RD. "33"
19 | 71-00001-1 |  |  | 6 | Transmission |  | Girth Weld |  |  | Other |  | 1971-06-17 | 1971-06-17 | Other |  | Steel/Wrought Iron |  |  | PIPE ABANDONED ON 4054-D 4-10-73.
19 | 76-00001-1 |  |  | 6 | Transmission |  | Tap Connection |  |  | Other |  | 1976-06-10 | 1976-06-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron
19 | 90-10010-1 |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1990-07-09 | 1991-04-30 | Other |  | Steel/Wrought Iron |  | CHICO | GRAPE WAY REG STATION. GREASED STEM SEAL ON 8" OUTLET VALVE.
19 | 87-10008-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1987-06-22 | 1987-07-02 | Other |  | Steel/Wrought Iron |  |  | GREASED VALVE V0.03.
19 | 90-10011-1 |  |  | 3 | Transmission |  | Regulator |  |  | Other |  | 1990-07-03 | 1990-08-06 | Other |  | Steel/Wrought Iron |  | WILLOWS | WILLOWS 209 TAP REGS. REPLACED DIAPHRAMS IN PILOT REGS REGULATOR #6 + #3. GREASED VALVE #16.
| 99-70006- |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1999-06-01 |  | Other | GREASED | Steel/Wrought Iron |  | ESCALON | VALVE 4.86 H.
| 90-30436-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1990-07-03 | 1990-07-20 | Other |  | Steel/Wrought Iron |  | RIVERBANK | MADE REPAIRS TO VALVE.
| 99-30268- |  |  | 6 | Transmission |  | Valves |  |  | Other | GREASE VALVE | 1999-11-29 | 2002-04-08 | Other | GREASE VALVE | Steel/Wrought Iron |  | RIVERBANK | GREASE VALVE (DONE BY WORLEY).
| 99-70053- |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1999-08-05 | 1999-09-27 | Other |  | Steel/Wrought Iron |  | RIVERBANK | VALVE 5.35E. GREASED; SEE ATTACHED PLAT SHEET.
91 | 73-30185-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-02-21 | 1974-03-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | ON LINE 148. THIS LEAK IS BLOWING. ASSIGNED FOR REPAIR PER SMR.
91 | 95-30071-1 | 148 |  | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1995-08-02 | 1997-07-19 | Patch Welded |  | Steel/Wrought Iron |  | MODESTO | CORROSION LEAK ON BOTTOM OF MAIN. REPAIRED WITH WELD OVER PATCH; WAS ORIGINALY A GRADE 2 (BY LEAK SURVEYOR) AND WAS CHANGED TO A 3 ON APPROX 8/13 WHEN DANG S. WAS COMPLETING THE A-FORM FOR R. BAKER. SEE ATTACHED SHEET.
91 | 93-70001-1 | 148 |  | 8 | Transmission | [6 empty] | 1993-03-30 |  |  |  | Steel/Wrought Iron |  | MODESTO
91 | 97-30075-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1997-07-01 | 1997-07-19 | Patch Welded |  | Steel/Wrought Iron |  | MODESTO | CORROSION LEAK ON GIRTH WELD. REPAIRED WITH WELD OVER PATCH.
91 | 98-30115-1 | 148 |  | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1998-06-19 | 2001-05-29 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | MODESTO | 2' N OF LINE MARKER SEE MAP. WELD 8" HALF SOLE OVER LEAKS (12" PATCH). PIPE TO SO L-985.
91 | 78-10029-1 |  |  | 2 | Transmission |  | Fitting |  |  | Other |  | 1978-03-30 | 1978-03-30 | Other |  | Steel/Wrought Iron |  | SALIDA | IN PG&E DIST. REG PIT RISER STACK.
91 | 79-50140-1 |  |  | 6 | Transmission |  | Valves |  |  | Material Failure |  | 1979-04-23 | 1979-04-23 | Other |  | Steel/Wrought Iron |  | MODESTO | FOUND GREASE PLUG + PACKING GLAND LEAK ON 3/4" MOLD VALVE. I GREASED + TIGHTENED GLAND. VALVE WAS OLD SERVICE TAP. NEW TAP 2' SOUTH.
91 | 78-30188-1 |  |  | 4 | Transmission |  | Other |  |  | Other |  | 1978-10-04 | 1978-10-24 | Other |  | Steel/Wrought Iron |  | MODESTO | REPAIRED LEAKING FILTER. @ DIST. REG PIT S/E CORNER OF INTERSECTION
91 | 79-50330-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-08-14 | 1979-08-14 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | MODESTO | 3177-J8. CAN WELDED ON MAIN - POOR FIELD WRAP CAUSE CORROSION.
91 | 74-30128-1 |  |  | 6 | Transmission |  | Fitting |  |  | Other |  | 1974-04-29 | 1974-05-02 | Other |  | Steel/Wrought Iron |  | MODESTO
91 | 74-30129-1 |  |  | 6 | Transmission |  | Fitting |  |  | Other |  | 1974-04-29 | 1974-05-02 | Other |  | Steel/Wrought Iron |  | MODESTO
91 | 74-30126-1 |  |  | 6 | Transmission |  | Fitting |  |  | Other |  | 1974-04-29 | 1974-05-02 | Other |  | Steel/Wrought Iron |  | MODESTO | 5% H.P.R. BOX
91 | 74-30125-1 |  |  | 6 | Transmission |  | Fitting |  |  | Other |  | 1974-04-29 | 1974-05-02 | Other |  | Steel/Wrought Iron |  | MODESTO | REPAIRED LEAK ON INLET UNION.
91 | 72-30104-1 | 148 |  | 2 | Transmission |  | Valves |  |  | Other |  | 1972-11-02 | 1973-09-20 | Other |  | Steel/Wrought Iron |  | MODESTO | LINE 148; LEAK IN VALVE BOX. GREASE LEAKING 2" B/O VALVE.
91 | 78-30044-1 |  |  | 0.75 | Transmission |  | Drip |  |  | Other |  | 1978-04-14 | 1979-01-02 | Other |  | Steel/Wrought Iron |  | MODESTO | ON CANAL BANK & 1000 PPM AT 6" PIPE ON N/S OF CANAL.
91 | 76-100- |  |  | 8 | Transmission |  | Fitting |  |  | Other |  | 1976-11-16 | 1978-05-30 | Other |  | Steel/Wrought Iron |  | MODESTO | DOPED THREADS ON 1/4" METRIC VALVE.
91 | 88-30025-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1988-05-10 | 1989-09-27 | Replace Pipe |  | Steel/Wrought Iron |  | TURLOCK | W.O. 41001-C REPLACED LEAKING VALVE; SEE W.O. 41001 C.
91 | 83-10017- | [10 empty] | 1983-08-25 | [5 empty] | TURLOCK | DOWNGRADED 6-19-84.
91 | 90-30150-1 |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1990-01-26 | 1990-02-06 | Other |  | Steel/Wrought Iron |  | TURLOCK | MADE REPAIRS.
91 | 90-30151-1 |  |  | 6 | Transmission |  | Fitting |  |  | Other |  | 1990-01-26 | 1990-02-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | TURLOCK | MADE REPAIRS TO REG SET.
91 | 90-70159-1 |  |  | 6 | Transmission |  | Fitting |  |  | Other |  | 1990-08-20 | 1992-10-31 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | TURLOCK | REAPIRS MADE DURING L-215 UPRATE. GM 4073045; REG PIT GAS VENTING. TAG TO GAS MECHANIC.
91 | 90-70160-1 |  |  | 6 | Transmission |  | Fitting |  |  | Other |  | 1990-08-20 | 1992-10-31 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | TURLOCK | REPAIRS MADE DURING L-21 UPRATE. GM 4073045.
91 | 97-70120-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other |  | 1997-09-26 | 1999-02-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | TURLOCK | FOUND PLUG LEAKING ON GUAUGE TAP.
91 | 97-70122-1 |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1997-09-26 | 2001-08-21 | Other |  | Steel/Wrought Iron |  | TURLOCK | REPLACED 6" VALVE; PER DISCUSSION WITH GUS QUIROZ, DOWNGRADE TO GRADE 3 AND MONITOR/RECHECK WITH NEXT SCHEDULED SURVEY. VALVE IS NOT REPAIRABLE OR GREASABLE PER HAMILTON AND WILL BE REFERRED TO CGT BY GUS QUIROZ. 10% IN VALVE ... GC WORKING IN ... WHEN COMPLETE LEAK WILL BE ELIMINATED 8-1-1.
| 99-70069- |  |  | 6 | Transmission |  | Fitting | Regulator | VALVES | Other |  |  | 2001-08-21 | Other |  | Steel/Wrought Iron |  | TURLOCK | GAS ODOR. ON REG SET. REBUILT REG STATION.
| 99-70070- |  |  | 6 | Transmission |  | Fitting | Regulator | VALVES | Other |  |  | 2001-08-21 | Other |  | Steel/Wrought Iron |  | TURLOCK | GAS ODOR. ON REG SET. REBUILT REG STATION.
91 | 97-50029-1 |  |  | 2 | Transmission |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1997-03-06 | 1997-03-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | HILMAR | AT VALVE TEE ON 2" SERVICE TO HILMAR CAP LEAKING. REMOVED, REDOPED AND TIGHTEN CAP; LEAK ON CAP.
91 | 82-30249-1 |  |  | 8 | Transmission | [6 empty] | 1982-05-07 |  |  |  | Steel/Wrought Iron |  |  | DOWNGRADE PER EMI KROUPA ON 5-13-82. ACTUAL LOCATION ON MAP 317A-65.
91 | 97-70086-1 |  |  | 2 | Transmission |  | Valves |  |  | Other |  | 1992-09-23 | 1997-09-29 | Other |  | Steel/Wrought Iron |  | TURLOCK | GREASED 2" VALVE.
91 | 97-70038-1 |  |  | 2 | Transmission |  | Valves |  |  | Other |  | 1997-08-08 | 1997-09-29 | Other |  | Steel/Wrought Iron |  | TURLOCK | GREASED VALVE.
91 | 78-10001-1 |  |  | 6 | Transmission |  | Fitting |  |  | Other |  | 1978-02-10 | 1978-10-20 | Other |  | Steel/Wrought Iron |  | TULOCK | REPAIRED VARIOUS TUBE FITTING LEAKS. AT VALVE ON N/W CORNER.
91 | 79-50083-1 |  |  | 2 | Transmission |  | Valves |  |  | Material Failure |  | 1979-03-15 | 1979-03-16 | Other |  | Steel/Wrought Iron |  | TURLOCK | 12" LINE 215; VALVE WAS LEAKING AT THE BONNET - M.C. MECHANIC GREASED THE VALVE FIXING SAME. @ VALVE ON TRANSMISSION 2" MAIN.
91 | 72-10203-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1972-12-05 | 1973-10-26 | Other |  | Steel/Wrought Iron |  | HILMAR | LEAK IN H.P.R. BOX ON LANDER EAST SIDE OF STREET. FIRST H.P.R. SOUTH OF FOWLER. 60 LEL - MSA. LEAK ON DIAPHRAM OF HPR REPAIRED SAME.
91 | 73-50341-1 |  |  | 0.75 | Service |  | Other Welds | Valves |  | Other |  | 1973-10-31 | 1974-10-03 | Other |  | Steel/Wrought Iron |  | TURLOCK | 6" LINE 118.
20% J.W. IN H.P.R BOX 6-17-74. REPAIRED LEAK ON WELD ON 3/4" ELBOW.
91 | 74-30243- |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1974-12-10 | 1975-01-16 | Other |  | Steel/Wrought Iron |  | TURLOCK
| 74-30243-1 | [17 empty] | REPAIR LEAK ON HPR SET.
91 | 72-10201-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1972-12-05 | 1973-09-14 | Other |  | Steel/Wrought Iron |  | HILMAR | 6" LINE 118. REPORTED UNDER 260. DELETED UNDER 320.
| 72-10201-1 | [16 empty] | HILMAR | LEAK OVER MAIN ON AUGUST RD 75 FT EAST OF 17491 AUGUST. YELLOW MARK. READING 50% MSA AT H.P.R. BOX SOUTH SIDE RD - 4% LEL OVER SERVICE TEE.
91 | 72-10202-1 |  |  | 4 | Transmission |  | Fitting |  |  | Other |  | 1972-12-05 | 1973-09-14 | Other |  | Steel/Wrought Iron |  | HILMAR | LEAK OVER MAIN ACROSS ST. FROM DRIVEWAY TO 19224 AUGUST RD. NO READING OVER MAIN ACROSS FROM DRIVEWAY. 4% MSA IN H.P.R. BOX ON SOUTH SIDE ST ACROSS FROM THE O'SHANAS'...
91 | 84-30160- |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-07-31 | 1985-01-17 | Patch Welded |  | Steel/Wrought Iron |  | WESTLY
| 84-30160- |  |  | 4 | [8 empty] | 1985-01-17 |  |  |  |  | WESTLEY | @ V-3.48. VALVE LEAKING IN SIDEWALK. ABANDONED LEAKING TEE AND PUT IN VALVE TEE.
91 | 80-30189-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1980-04-24 | 1984-02-03 | Other |  | Steel/Wrought Iron |  | WESTLEY
| 80-30189-1 | [16 empty] | WESTLEY | ALSO @ VENT PIPE TO REG BOXES. PG+E VALVE IN SIDEWALK. ZERO READING WITH J.W. TESTER PER RON HAMILTON 8-24-82.
91 | 77-30191-1 |  |  | 2 | Distribution Main |  | Valves |  |  | Other |  | 1977-06-16 | 1978-06-16 |  |  | Steel/Wrought Iron |  | WESTLEY | PG&E R. VALVE
| 77-30191-1 | [11 empty] | 1978-06-16 |  |  |  |  | WESTLEY
| 01-30073-1 |  |  | 6 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 2001-10-30 |  | Other |  | Steel/Wrought Iron |  | PATTERSON | 50' W/O DEL PUERTO CAMINO CANYON RD ON W/S OF CALIF. AQUADUCT ON ENTRANCE RD. REPLACED GASKET ON 6" PCF.
| 00-30077- |  |  | 3 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 2000-08-15 | 2000-03-16 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | PATTERSON | CAP ON ABANDONED SERV TEE NOT TIGHTENED VERY LOOSE T.P. MAIN; TIGHTENED CAP.
91 | 10-30584-1 |  |  | 3 | Transmission >= 20% SMYS |  | Fitting |  |  | Other | LOOSE | 2010-10-26 | 2010-12-31 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | PATTERSON | REBUILT 3" MOONEY; REBUILT MOONE IN REG STATION & SOAP TESTED.
| 00-30077- |  |  | 3 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 2000-08-15 | 2000-03-16 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | PATTERSON | CAP ON ABANDONED SERV. TEE NOT TIGHTENED VERY LOOSE. T.P. MAIN.
| 01-10020- |  |  | 3 | Transmission |  | Fitting | Valves |  | Other |  | 2001-10-09 | 2002-09-12 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | PATTERSON | TIGHTENED CAP ON 1 1/4" SAV @ VALVE.
| 01-10020- | [10 empty] | 2001-10-30 | [5 empty] | PATTERSON | VALVE IN INTERSECTION. N/W INTERSETION SPERRY RIO DEL PUERTO AVE.
| 01-10020- | [10 empty] | 2001-10-09 | [5 empty] | PATERSON | VALVE IN INERSECTION.
| 01-30076- |  |  | 6 | Transmission |  | Valves |  |  | Unknown |  | 2001-11-07 | 2002-08-14 | Other | SERVICE VALVE | Steel/Wrought Iron |  | PATTERSON | AREA VERY WET. RE-CHECK 90 DRIP. AT V-2.79. SERVICED VALVE.
91 | 90-30242-1 |  |  | 2 | Transmission |  | Valves |  |  | Other |  | 1990-08-08 | 1991-02-15 | Other |  | Steel/Wrought Iron |  | CERES | PIT ... VALVE. GREASED VALVE.
91 | 90-30239-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1990-08-07 | 1990-08-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MODESTO | FOUND COLLAR ON 1/4" VALVE MADE REPAIRS.
| 99-30060- |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1999-03-09 | 1999-03-09 | Other |  | Steel/Wrought Iron |  | CERES | @ VALVE STATION ON WHITMORE 144' W/O AT VALVE. GREASED + OPERATED.
91 | 85-30114- |  |  | 2 | Transmission |  | Valves |  |  | Other |  | 1985-08-22 | 1985-08-23 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MODESTO | GREASED 2" VALVE.
| 00-30074- |  |  | 0.25 | Transmission |  | Other |  | TUBING | Other |  | 2000-08-10 | 2001-12-27 | Other | REPLACE TUBING | Steel/Wrought Iron |  | CERES | @ VENT STACK W/ CHART MO HP 83. IN VAULT ON PILOT LOOP TUBING. REPLACED TUBING + FITTINGS.
| 00-30074- | [10 empty] | 2000-08-10 | [5 empty] | CERES | @ VENT STACL W/ CHART MO HP 83.
91 | 90-70013-1 |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1990-07-27 | 1990-08-17 | Other |  | Steel/Wrought Iron |  | MODESTO | REPAIRED VARIOUS 301 ON RED SET.
| 01-30052- |  |  | 2 | Transmission |  | Valves |  |  | Other |  | 2001-08-03 | 2002-11-14 | Other |  | Steel/Wrought Iron |  | MODESTO | GREASED VALVE. GREASED 2" VALVE.
| 10-50195-1 |  |  | 0.5 | Distribution Main |  | Other |  | THREADS ON GAUGE TAP | Other | DRY DOPE | 2010-10-16 | 2010-12-02 | Other | REDOPE VALVE | Steel/Wrought Iron |  | RIVERBANK | THREADS ON GAUGE TAP. REMOVED AND REDOPED METRIC VALVE.
91 | 97-70006-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1997-02-10 | 1997-08-04 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MODESTO | LOSE PACKING ON SMALL VALVE. TIGHTEN PACKING ON VALVE.
| 08-30147-1 |  |  | 0.5 | Branch Service |  | Plastic Tee Cap |  |  | Construction Defect |  | 2006-05-14 | 2008-05-14 | Other | RAN CUTTER DOWN A LITTLE REGREASED O RING TIGHTENED CAP | PE2406 (Yellow or Orange) |  | MODESTO | TIGHTENED CAP; SOAP TESTED. RAN CUTTER DOWN A LITTLE GREASD GASKET TIGHTENED CAP.
| 08-20078-1 | [10 empty] | 2008-03-26 | [5 empty] | MODESTO | HAS FIZZER LEAK ON THREADS UNDER REG. ABOVE VALVE. REBUILD MERREET. DELETE THIS LEAK. TRANSFER TO PURPOSE
LEAK REPORTED REPAIRED ON 5/1/08 @17:45 HOURS.
| 08-20078-1 |  |  | 0.75 | Gathering |  | Riser |  |  | Other | DRIED PIPE DOPE | 2008-03-26 |  |  |  | Steel/Wrought Iron |  | MODESTO | 3016 VALDEZ DR. RE DOPED RISER THREADS.
[13 empty] | 2008-05-01 | Other | RE DOPED VALVE |  |  |  | AT RISER THREADS. RE DOPED RISER THREADS.
|  |  |  | 0.75 | Gathering | [10 empty] | Steel/Wrought Iron
| 08-20078-1 |  |  | 0.75 | Gathering |  | Riser |  |  | Other |  | 2008-03-26 |  |  |  | Steel/Wrought Iron |  | MODESTO
[13 empty] | 2008-05-01 | Other |  |  |  |  | @ RISER THREADS. REDOPED RISER THREADS.
|  |  |  | 0.75 | Gathering | [10 empty] | Steel/Wrought Iron
91 | 90-70007-1 |  |  | 0.25 | Transmission |  | Fitting |  |  | Other |  | 1990-07-06 | 1990-08-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MODESTO | MADE REPAIRS T 1/4" UNION OF STATIC LINE.
72 | 10-35230-B | 7206-01 | 0.87 | [14 empty] | MERCED | REG STN IFO ADD W/O DRIVE.
|  |  |  | 0.375 | Transmission >= 20% SMYS |  | Fitting |  |  | Construction Defect |  |  | 2010-10-14 | Tighten Cap/Bolt - Fitting |  | Other | S.S. |  | MONITOR REG STN LINE RA38. TIGHTEN FITTING.
|  |  |  | 0.375 | [11 empty] | Steel-Other
SEE ATTACHED.
| 10-31422-1 | 7206-01 | 0 87 | 0.375 | Transmission |  | Fitting |  |  | Construction Defect |  | 2010-10-07 |  |  |  | Other | S.S. | MERCED
|  |  |  | 0.375 | [8 empty] | 2010-10-14 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron
72 | 95-75030-1 | 118 |  | 8 | Transmission |  | Body of Pipe |  |  | Damage by Electrical Facility |  | 1995-12-11 | 1995-12-11 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | ATWATER | LINE 118 625' S/O BUTTACK TAP 6-200 12. 12 AV CONTACT DAMAGED 8" TP LINE 118. INSTALLED 8 5/8" 10 X12" L X .375" SLEEVE. SPLIT , 42,000 SMYS.
| 09-35195-1 |  |  | 0.75 | Transmission |  | Regulator |  |  | Construction Defect |  | 2009-10-07 | 06/22/1010 | Other | REG | Steel/Wrought Iron |  | LIVINGSTON | HPR REG AND RELIEF HAS BEEN REPLACED. REPLACED REG + RELIEF.
| 08-10207-1 |  |  | 0.75 | Single Service |  | Other |  | RISER THREADS | Other | PIPE DOPE | 2008-04-22 | 2008-02-29 | Other | REDOPE + TIGHTEN | Steel/Wrought Iron |  | WINTON | ROAMER LEAK @ RISER THREADS; REDOPE + TIGHTEN VALVE.
72 | 11-75030-B |  |  | 2 | Distribution Main <= 60 PSIG |  | Unknown |  |  | Unknown |  | 2011-03-27 | 2011-03-27 | Deactivate Dist Main =>1 foot |  | Aldyl A (Tan or Gray) |  | PLENADA | C/0 250' OF 2" PL. DEAD END; EM MARKER INSTALLED. SOAP TESTED OK. NO SIGNS OF SAND ON MAIN. LARGE COBBLE IN TRENCH OVER MAIN. SUSPECTED LEAK COULD HEAR BLOWING.
72 | 11-75026-1 | 118B | 10 30 | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-17 | 2011-04-18 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | MADERA | ON SAVER VALVE ON MAIN. REDOPED AND TIGHTENED CAP; LEAK ON SAVER VALVE DRIED PIPE DOPE, REMOVED CAP, REDOPED AND TIGHTENED CAP. SOAP TEST NO LEAK.
72 | 10-81705-1 | 118B | 10 30 | [8 empty] | 2010-10-14 | [5 empty] | MADERA
|  |  |  | 0.75 | Transmission >= 20% SMYS |  | Other |  |  | Other |  |  | 2010-11-08 | Tighten Cap/Bolt - Fitting |  |  |  |  | 3/4" CAP FOR SAV-A-VLV. RMVD CAP RDOPED TIGHTEN.
0.75
72 | 09-35126-B |  |  | 2 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2009-07-31 | 2011-03-04 | SS Clamp w/Anode - Clamp |  | Steel-Other |  | MERCED | OVER MAIN AT SERVICE TEE; ON 2" STEEL MAIN. PUT ON FULL CIRCLE CLAMP WITH ANODE (SS CLAMP); PUT ON SS CLAMP WITH ANODE THEN SOAP TESTED THE CLAMP.
| 09-35126-1 | [10 empty] | 2009-07-31 | [5 empty] | MERCED | OVER MAIN AT SERVICE TEE IN STREET. UPGRADE TO 2 SEND THIS LEAK TO THE ORIGINAL REPAIR MUST REPAIR IN FEB. 1346 DUG UP SERVICE TEE. NO LEAK POSSIBLY ON M/2.
| 09-35126-1 | [10 empty] | 2009-07-31 | [5 empty] | MERCED | OVER MAIN AT SERVICE TEE IN STREET.
| 09-35126-1 | [10 empty] | 2009-07-31 | [5 empty] | MERCED | UPGRADE SEND THIS TO ORIGINAL REPAIR FEB.
| 99-35011 |  |  | 2 | Distribution Main <= 60 PSIG |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 1999-05-11 | 2011-01-06 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | MERCED | OVER 2" MUELLER TEE. RE-DOPED & TIGHTENED 2" MUELLER TEE CAP; RE-DOPED & TIGHTENED 2" MUELLER TEE CAP. SOAP TESTED OK.
| 99-35011-1 | [10 empty] | 1999-05-11 | [5 empty] | MERCED | NEW FROM NOV 2010.
| 99-35011-1 | [10 empty] | 2008-04-18 | [5 empty] | MERCED | MAIN IN INTERSECTN TH & K ST.
| 99-35011-1 | [10 empty] | 1999-05-11 | [5 empty] | MERCED | PCF AT 5TH & K STS
| 99-35011-1 | [10 empty] | 1999-05-11 | [5 empty] | MERCED | SEE #89-35057. LEAK AT PCF.
72 | 09-35203-1 | 261 |  |  |  |  | Body of Pipe |  |  | Previously Damaged |  | 2009-10-09 | 2011-03-31 | SS Clamp w/Anode - Clamp |  | Steel-Other |  | WINTON | OVER MAIN 261 INTO PROPERTY. INSTALLED 2" S/STL FULL CIRCLE CLAMP W/ ANODE ON UNDERSIDE OF 2" STL MAIN 261 FROM PL. SOAP TESTED.
| 09-35203-1 | [10 empty] | 2009-10-09 | [5 empty] | WINTON | OVER MAIN BETWEEN 6612 & 6616.
| 09-35512-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2009-07-18 | 2010-11-16 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | LOS BANOS | 133' M/OF JEFFERSON ON 4" STL MAIN. INSTALLED 4" FULL CIRCLE CLAMP W/ ANODE; SOAP TETED OK.
| 91-35050-1 | [10 empty] | 1991-05-20 | [5 empty] | LOS BANOS | SVC-OLD BELLHLE PATCH IN ST OVER MAIN. NO LEAK BEHIND CURB.
| 10-35188-B |  |  | 3 | Distribution Main <= 60 PSIG |  | Line Valve |  |  | Other | NON-GREASABLE 3" VALVE | 2010-09-23 | 2010-12-14 | Replace Main Valve >= 2-inch |  | Steel-Other |  | MADERA | CORNER OF "E" ST AND 9TH ST-200' EAST; WELDED ONE 4" LINE STOPER. WELDED ONE 3" LINE STOPER CUT OUT 3" IN LINE VALVE & 4" X 3" MITER WELD. WELDED IN 32" OF 3" STL & ONE 4" X 3" WELD BY WELD REDUCER.
| 10-35188-1 | [10 empty] | 2010-09-23 | [5 empty] | MADERA
VALVE SCHEDULED TO BE REPLACED.
72-55042-1 |  |  |  | 800 | Transmission |  | Body of Pipe |  |  | Digin |  | 1987-07-31 | 1987-07-31 | Replace Pipe and/or Service |  | Steel/Wrought Iron
| 95-35039-1 |  |  | 2 | Transmission |  | Regulator |  |  | Material Failure |  | 1995-10-19 | 2000-10-25 | Other |  | Steel/Wrought Iron |  | MADERA | LEAK AT BASE OF RISER. REPLACED VARIABLE ORIFICE "O" RINGS ON GROVE REG @ PRIMARY REG SET; LEAK WAS H.P.R CALLED IN FOR REPAIR. MEC ON WAY.
| 01-55081-1 | 186 | 5.1 | 4 | Transmission |  | Body of Pipe |  |  | Digin |  | 2001-12-20 | 2001-12-21 | Replace TP Main |  | Steel/Wrought Iron |  | OROLONIA AREA | CLEANING DRAINAGE DAMAGED 4" TP L 186 OF 4" STL.
72 | 75-55022-1 |  |  | 3 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1975-10-01 | 1975-10-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | DIG-IN BY HAMBURG RANCH WITH SUB SOILER.
| 93-75000-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Other |  | 1993-02-11 | 1993-02-11 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | MADERA CO | WELDED ON 12" FULL CAN TO MAKE PERMANENT REPAIR.
| 76-55007-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-03-18 | 1976-03-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | 6" T.P. MAIN.
72 | 82-35106-1 | 104 |  | 0.75 | Transmission |  | Other |  |  | Other |  | 1982-10-04 | 1982-11-05 | Other |  | Steel/Wrought Iron |  |  | LINE 104. FIRE VALVE TO PIECE OF DBN MAIN. H.D.R. BOX 11/4/82. METRIC LEAK REPAIRED
72 | 88-55054-2 |  |  | 12.75 | Transmission |  | Body of Pipe |  |  | Digin |  | 1988-12-10 | 1988-12-10 | Replace Pipe |  |  |  | ILLIGOSA | REPLACED GET SECTION 12" T.P. MAIN 118.
| 09-35093-1 |  |  | 0.75 | Gathering |  | Fitting | Valves |  | Equipment Malfunction |  | 2009-06-26 | 2009-09-02 | Other | REPLACED HPR REGULATOR | Steel/Wrought Iron |  | MADERA | REPLACED REGULATOR W/ NEWER MODEL.
| 86-55020-1 | 183 | 6.19 | 3 | Transmission |  | Body of Pipe |  |  | Digin |  | 1986-12-01 | 1986-12-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | FIREBAUGH | LEAK BY DIG-IN ON LINE. REPLACED 9' OF 3" TP LINE.
| 99-55027-1 |  |  | 3 | Transmission | DFM | Body of Pipe |  |  | Damage by 3rd Party |  | 1999-06-22 | 1999-06-23 |  |  | Steel/Wrought Iron |  | FIREBAUGH | 3" MAIN DAMAGE ABOVE GROUND, SMALL LEAK. INSTALLED TWO 3" NTL REPLACED 3' OF3".
72 | 75-55002-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Construction Defect |  | 1975-01-13 | [6 empty] | WELDED SLEEVE OVER DENTS WELDER SAVE-A-VALVE. PIT STANDUP TEST FOR 3 MIN AT 100 PSI.
|  |  |  | 4 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  |  | 1975-02-05 | Patch Welded |  | Steel/Wrought Iron
INST. 12" SLEEVE + TESTED FOR 7 MIN AT 97 LBS AND WRAPPED AN BACKFILLED.
72 | 72-60005-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-04-11 | 1972-04-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | TWO 90 DEGREE ANGLES BACK TO BACK. CORROSION LEAK. ORIGINAL INSTALLATION. REPLACED 18' AT MAIN WITH NEW .188 WALL PIPE. 6" T.P. ,AIN #134.
72 | 88-55046-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Digin |  | 1988-11-14 | 1988-11-14 | Replace Pipe |  | Steel/Wrought Iron |  | MADERA | APPROX 2.6 MI E/O RD 16 - 1/2 MI S/O AVE 5. REPLACED 5 FT. SECTION. 8" T.D. MAIN.
72 | 10-81175-1
72 | 82-55005-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1982-07-02 | 1982-07-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | M.P. 999
72 | 82-35102-1 | 134 |  | 0.75 | Transmission |  | Regulator |  |  | Material Failure |  | 1982-10-04 | 1982-11-05 | Other |  | Steel/Wrought Iron |  | MADERA COUNTY | IN REG BOX NEXT TO LINE #134 APPROX 1/4 EAST OF RD. 25. ALSO IDLE RISER NEXT REG BOX "OUT OF SVC" LEAK.
72 | 92-55024-1 | 134.05 | 9.52 | 8 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1992-11-18 | 1992-11-18 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | MADERA | INSTALLED 8" WELD SLEEVE OVER GAUGE ON T.P. LINE 134.
72 | 82-75041-1 | 134 | 12.25 | 8 | Transmission |  | Other Welds |  |  | Damage by outside Forces |  | 1982-12-20 | 1982-12-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | BROKEN 8" T.P. LINE REPAIRS WERE MADE BY INSTALLING A 36' PCIK OF 8" STL. PIPE WRAPING AND BACKFILLING.
25 | 83-75004-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1983-03-17 | 1983-03-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | MADERA | M.P. 12.13. REPAIRS.
| 09-35060-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | NEEDED TO BE GREASED | 2009-05-08 | 2010-09-01 | Other | GREASE VALVE | Steel/Wrought Iron |  | MADERA | GREASED VALVE NORD VALVE SOAP TEST; GREASED 3/4 NORD VALVE ON H.P.R SET. SOAP TESTED OK.
| 10-35024-1 | 134 | 8 18 | [8 empty] | 2010-04-02 | [5 empty] | MADERA | SAME AS 09-35060
72 | 82-35108-1 |  |  | 8 | Transmission |  | Valves |  |  | Other |  | 1982-10-04 | 1982-10-06 | Other |  | Steel/Wrought Iron |  |  | ROAD 27 & AVE 5.5 VALVE CASING 69' W/WPL OF NEW ROAD 27 10'. S/NPL TO ISOLATE LOCATION DOWNGRADED TO HOT H2. CALLED JACOBS TO REPAIR.
25 | 82-35107-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Construction Defect |  | 1982-10-04 | 1982-11-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | MADERA | NEED WELDER TRANS LINE 3/4. 3835 A5. REPAIRS WERE MADE BY TURNING LINE OFF AND CUTTING NEW NIPPLE IN LINE REWRAPPING AND BACKFILLING. TP REG PIT THREADS LEAKING ON DOWNSTREAM SIDE OF VALVE.
25 | 83-75018-1 |  |  | 3 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1985-05-19 | 1983-06-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | REPAIRS WERE MADE BY REPLACING 2' OF 3" PIPE.
72 | 84-55009-1 |  |  | 3 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1984-05-14 | 1984-05-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CHANEY RANCH | REPAIRED 3" TP
72 | 72-40008-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-08-22 | 1972-08-29 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | FIREBAUGH | WELDED FULL ENCIRCLEMENT SLEEVE OVER LEAK ON 6" TP MAIN 134 AT M.P. 26.00.
72 | 87-55033-1 | 134 |  | 6 | Transmission |  | Body of Pipe |  |  | Digin |  | 1987-05-07 | 1987-05-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | N/E OF MENDOTA | T.P. MAIN 134. REPLACED SET SECTION OF 6" MAIN.
72 | 81-33142-1 |  | 27 | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1981-07-10 | 1985-05-13 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | MENDOTA | M.P. MARKER 27.0 E/O STA. BASE OF MARKER.
72 | 78-75000 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion | ; | 1978-05-25 | 1978-05-25 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | MENDOTA | MENDOTA - LINE 134 E/O ARBIOS STA.
72 | 82-35097-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1982-10-04 | 1985-05-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | MENDOTA | CORNER FENCE LINE E/O ARBIOS. AREA OF APR TAP.
72 | 11-75006-1 | 307 | 15 | 2 | Distribution Main |  | Regulator/Pilot |  |  | Other | LUBRICATION | 2077-01-19 | 2011-01-20 | Remove/Replace Completion Plug Fitting |  | Steel-Other |  | MENDOTA | LEAK IN STATION. FIX LEAK ON RESTRICKER VALVE. SOAP TESTED - GOOD.
72 | 73-55013-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  |  | 1973-08-24 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | LEAK REPAIRED WITH FULL SLEEVE; PROPSED WORK INSTALL WELDING SLEEVE ON 8" TP TO REPAIR LEAKAGE. THROTTLE V-8.63 TP 307 TO LOWER PRES. BELOW 366 PSI DOWNSTREAM DURING WELDING OPERATIONS. NOTE 1. MAIN IS UNDER CATHODIC PROTECTION. 2. PIPE IS E.R.W., .188 WALL, 42POOPSI S.M.V.S.
72 | 75-22031-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-12-18 | 1976-07-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | MENDOTA | HAD A HARD TIME LOCATING GOOD PIPE TO WELD ON.
72 | 72-60006-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-04-20 | 1972-04-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | WELDED .375 WALL FULL ENCIRCLEMENT SLEEVE OVER CORROSION LEAK.
| 88-35065-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 1988-06-21 |  |  |  | Steel/Wrought Iron |  | MERCED
| 88-35065 | [10 empty] | 1988-06-21 | 2010-12-17 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | MERCED | OVER MAIN. MAIN TO BE DEACTIVATED, INSTALLED SS CLAMP DID NOT INSTALL ANODE.
| 88-30065-1 | [10 empty] | 1988-06-21 | [5 empty] | MERCED
93 | 74-204011 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1974-06-26 | 1974-07-16 | Patch Welded |  | Steel/Wrought Iron
LEAK ON P/L. 4"X6" ... PATCH.
| 02-01085- |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 2002-08-14 | 2002-08-14 | Mechanical Repair Fitting - Fitting | SERVICE PARTIALLY REPLACED | Aldyl A (Tan or Gray) |  | STOCKTON | 60' N/O SIDEWALK AT P.L. OF 2535 + 2543. REPLACED PIPE.
| 03-01009-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 2003-01-30 | 2003-01-30 | Service Partially Replaced |  | TR 418 |  | STOCKTON | OVER SERV. 5' BACK FROM GAS RISER. INST. 1' PF 1/2" PL. PIPE + 2 - 1/2" PERF. COUPLINGS; POINT OF IMPACT 5' BACK FROM GAS RISER.
| 03-01051-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 2003-07-03 | 2003-07-03 | Service Partially Replaced |  | TR 418 |  | STOCKTON | CENTER OF NIGHTINGALE 100' S/O JORDAN CT. INSTALLED 1/2" DEAD END; NEW SEWER. ALL UTILITIES DAMAGED.
93 | 95-00699-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other |  | 1993-08-05 | 1995-11-03 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | TRACY | IN H.P.R BOX ON W/S MACARTHUR DR. 150' N/O MAILBOX TO 29900 MACARTHUR DR. REDOPED AND TIGHTENED UNION FITTING IN H.P.R BOX.
| 04-01002-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Digin |  | 2004-01-10 |  | Other | C/O SERVICE | Steel/Wrought Iron |  | MANTECA | 100% AT RISER. C/O SERVICE.
| 01-05009- |  |  | 0.5 | Service |  | Plastic Tee Cap |  |  |  |  | 2001-03-08 | 2001-03-08 | Other | INSTALL ALDYL A CAP REPAIR KIT. | Aldyl A (Tan or Gray) |  | MANTECA | OVER SUC T @ MAIN. REPAIR LEAKING CAP @ SUC T ON 2" ALDYL A CAP REPAIR KIT; LINE SIZE 02.00. SOAP TESTED OK.
| 02-01044-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Other | MOVE GROUND RISER LEAK | 2002-05-23 | 2002-05-23 | Service Partially Replaced | OTHER - REPLACED 3" OF PIPE BELOW VALVE | Steel/Wrought Iron |  | STOCKTON | 100% AT RISER. LEAK ON RISER BELOW VALVE. REPLACED PIPE; CUT AND THREADED STEEL RISER.
16 | 92-00006-1 |  |  | 8 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1992-01-06 | 1992-01-07 | Patch Welded |  | Steel/Wrought Iron |  |  | LEAK M.P. 4.0. L-176. HEAVY EXTERNAL CORROSION.
| 06-01117- |  |  | 0.5 | Gathering |  | Body of Pipe |  |  | Unknown |  | 2006-09-15 | 2006-09-15 | Service Partially Replaced |  | TR 418 |  | LODI | 1835 W. LOCKFORD ST. AT CURB + GUTTER AT ABOVE ADDRESS. REPLACED 3' OF TR 418 GAS SERVICE.
93 | 73-20008-1 |  |  | 8 | Distribution Main |  | Girth Weld |  |  | Construction Defect |  | 1973-04-10 | 1973-04-13 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | SOAP TEST CLEAR 5-17-73; LEAK AT WELD. TOP OF 8" PIPE AT WELD.
93 | 74-60006-1 |  |  | 8 | Transmission |  | Fitting |  |  | Construction Defect |  | 1974-03-22 | 1975-05-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | FOUND LEAKS ON FITTINGS IN VALVE PIT VALVE # V-7.23. REPAIRED 9 MINOR GAS LEAKS IN VALVE AT V. 7.23. PAINTED PIPING. VALVE 7.23 SHOULD BE CHAINED & LOCKED. PLEASE REPAIR MINOR LEAKS @ VALVE STATION. SEE ATTACHED SKETCH. ABOVE GAS LEAKS WERE REPAIRED AND PIT PAINTED. VALVE 7.23 SHOULD BE CHAIN + LOCK.
| 04-01016-1 |  |  | 0.5 | Service |  | Riser |  |  | Atmospheric Corrosion |  | 2004-02-10 | 2004-02-10 | Service Partially Replaced |  | Aldyl A (Tan or Gray) |  | STOCKTON | 307 JANIE CRT. ON RISER. REPLACED GAS RISER WITH 3/4 PREFABUL RISER.
93 | 73-00335-1 | 162 |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-01-29 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | TRACY | GM 181317 REPAIRED.
| 02-01056-1 |  |  | 0.5 | Service |  | Riser |  |  | Digin |  | 2002-06-17 | 2002-06-17 | Service Partially Replaced |  | TR 418 |  | STOCKTON | 4253 TSUSHING CT @ RISER. INSTALLED NEW RISER.
| 04-01045-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Other | GOFERS | 2004-04-06 | 2004-04-07 | Service Partially Replaced |  | TR 418 |  | STOCKTON | INSERTED 34' OF 1/4" PRISCOPIRO PIPE INTO ... 1/2" SERV.
| 02-01068- |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 2002-07-09 | 2002-07-09 | Service Partially Replaced |  | TR 418 |  | STOCKTON | 2429 DELAWARE. N/E CORNER OF PROPERTY @ EDGE OF SIDEWALK. INSTALLED 2-COUPLING + 1' OF PIPE.
93 | 11-06072-B |  |  | 2 | Distribution Main <= 60 PSIG |  | Plastic Tee Cap |  |  | Material Failure |  | 2011-04-21 | 2011-04-21 | Replace Plastic Tee Cap - Plastic |  | PE2406 (Yellow or Orange) |  | STOCKTON | 1442 W. HARDING WAY. REPLACED LEAKING CAP; INSTALL EFV 1/2" 400 - CUT & TEST 1/2" P/S SERVICE AT 100# - 5 MIN O.K. SOAP TEST. NEW EFV & 1-COUPING
93 | 10-88241-1 | 108 |  | 0.75 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Other |  | 2010-10-15 | 2010-11-24 | Other |  | Steel-Other |  | LODI | REPL HPR REG & RELIEF VLV.
| 10-02411 |  |  | 2 | Distribution Main >60 PSIG and <20% SYMS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-09-02 | 1974-02-16 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | STOCKTON | ON MAIN AT ISO E MENDOCINO. REDOPE RETIGHTEN CAP; LEAK ON CAP OF SAVER VALVE REDOPE & SOAP TESTED. SAVE VALVE CAP LEAKING.
93 | 10-81502-1 | GCUS5969 |  | 0.75 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Other |  | 2010-09-29 | 2010-10-12 | Other |  |  |  | LATHROP | REPLACE REG. RPLC REG RELIEF VALV&1/4" METRIC; SOAP.
| 09-81924-1 |  |  | 0.75 | Single Service |  | Other |  | VALVE THREAD | Other | THREADS | 2009-03-12 | 2009-03-25 | Other | TIGHTENED VALVE | Steel/Wrought Iron |  | FRESNO | AT RISER. TIGHTENED VALVE; TIGHTENED VALVE TO STOP LEAK.
| 09-83603-1 |  |  | 1 | Gathering |  | Riser | Valves | OTHER - THREADS ON VALVE | Other | THREADS | 2009-05-20 | 2009-07-22 | Other | TIGHTEN VALVE & FITTINGS | Steel/Wrought Iron |  | FRESNO | TIGHTEN VALVE & FITTINGS
| 09-83608-1 |  |  | 0.75 | Gathering |  | Valves |  |  | Unknown |  | 2009-05-21 | 2009-07-22 | Other | TIGHTEN VALVE | Steel/Wrought Iron |  | FRESNO | SERVICE VALVE; TIGHTEN VALVE. CASA BLANCAS APPARTMENTS. #248.
| 09-83609-1 |  |  | 0.75 | Gathering |  | Valves |  |  | Other | LOOSE FITTING | 2009-05-21 | 2009-07-23 | Other | TIGHTEN VALVE | Steel/Wrought Iron |  | FRESNO | RISER; TIGHTEN VALVE. APPARTMENT #139 CASA BLANCAS.
| 09-83642-1 |  |  | 0.75 | Single Service |  | Other |  | RISER THREADS | Construction Defect |  | 2009-05-21 | 2009-08-04 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | FRESNO | SOAP TEST OK. REPAIRED LEAK AT THREADS UNDER STOP COCK.
| 09-83687-1 |  |  | 0.75 | Single Service |  | Other |  | RISER THREADS | Construction Defect |  | 2009-05-27 | 2009-08-04 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | FRESNO | SOAP TEST OK. REPAIRED LEAK AT THREADS UNDER STOP-COCK.
| 09-83701-1 |  |  | 1.25 | Single Service |  | Plastic Tee Cap |  |  | Material Failure |  | 2009-05-28 | 2009-11-12 | Replace Plastic Tee Cap - Plastic |  | PE2406 (Yellow or Orange) |  | FRESNO | EXCAVATED BELLHOLE EXPOSED SERVICE TEE, REPLACED CAP BACKFILLED WITH NEW MATERIAL.
| 09-81498-1 |  |  | 0.75 | Single Service |  | Other |  | VALVE THREADS | Other | LOOSE VALVE | 2009-01-30 | 2009-03-23 | Other | TIGHTENED VALVE | Other | RISER | FRESNO | THREADS BELOW VALVE; CREW TIGHTENED VALVE ON RISER.
| 09-81570-1 |  |  | 8 | Transmission |  | Fitting |  |  | Weld Failure |  | 2009-02-03 | 2009-11-04 | Fill Weld - Weld |  | Steel/Wrought Iron |  | FRESNO | PIN-OFF TEE CAP LEAKING; SOAP TEST PIN-OFF TEE. WELD CAP ON ABANDON PIN-OFF TEE LEAKING.
| 09-82051-1 |  |  | 0.5 | Single Service |  | Other |  | VALVE THREADS | Other | LOOSE VALVE | 2009-03-17 | 2009-03-23 | Other | TIGHTENED VALVE | Other | RISER | FRESNO | THREADS BELOW VALVE; TIGHTENED VALVE ON RISER.
| 09-86119-1 |  |  | 0.75 | Single Service |  | Other |  | RISER THREADS | Construction Defect |  | 2009-07-25 | 2009-09-08 | Other | SKINNER PIPE JOINT CLAMP | Steel/Wrought Iron |  | FRESNO | SOAP TEST OK. REPAIRED LEAK AT THREADS UNDER STOP COCK.
| 09-86125-1 |  |  | 0.75 | Single Service |  | Other |  | RISER THREADS | Construction Defect |  | 2009-07-15 | 2009-09-20 | Other | TIGHTEN VALVE | Steel/Wrought Iron |  | FRESNO | TIGHTENED VALVE ON RISER, TIGHTENED FITTING ABOVE VALVE. SOAP TEST - OK.
| 09-86175-1 |  |  | 0.75 | Single Service |  | Other |  | RISER THREADS | Construction Defect |  | 2009-07-21 | 2009-09-10 | Other | SKINNER PIPE JOINT CLAMP | Steel/Wrought Iron |  | FRESNO | SOAP TEST OK. REPAIR LEAK AT THREADS UNDER STOPCOCK.
| 09-86296-1 |  |  | 0.75 | Service |  | Valves |  |  | Unknown |  | 2009-07-27 | 2009-12-14 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | FRESNO | CURB VALVE. GREASED & TIGHTEN VALVE; SOAP TSTED CURB VALVE.
| 09-86396-1 |  |  | 0.75 | Branch Service |  | Other |  | RISER THREADS | Construction Defect |  | 2009-08-03 | 2009-09-21 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | FRESNO
| 09-86379-1 |  |  | 0.75 | Gathering |  | Valves |  |  | Other | LOOSE | 2009-07-31 | 2009-11-12 | Other | TIGHTEN VALVE | Steel/Wrought Iron |  | FRESNO | VALVE ON RISER WAS LOOSE. TIGHTEN VALVE STOP LEAK
| 09-86543-1 |  |  | 0.75 | Single Service |  | Other |  | RISER THREADS | Construction Defect |  | 2009-08-11 | 2009-09-22 | Other | TIGHTENED VALVE | Steel/Wrought Iron |  | FRESNO
| 09-86690-1 |  |  |  | Single Service |  | Other |  | RISER THREADS | Construction Defect |  | 2009-08-19 | 2009-09-16 | Other | SKINNER PIPE JOINT CLAMP | Steel/Wrought Iron |  | FRESNO | SOAP TESTED OK.
| 09-86823-1 |  |  | 0.75 | Single Service |  | Other |  | RISER THREADS | Construction Defect |  | 2009-08-28 | 2009-09-18 | Other | TIGHTEN VALVE | Steel/Wrought Iron |  | FRESNO | SOAP TEST OK. REPAIR LEAK AT THREADS UNDER STOPCOCK. USED STOPCOCK CHANGER.
| 09-86868-1 |  |  | 0.75 | Single Service |  | Other |  | RISER THREADS | Construction Defect |  | 2009-08-31 | 2009-09-18 | Other | TIGHTEN VALVE | Steel/Wrought Iron |  | FRESNO | SOAP TEST OK. REPAIRED LEAK AT THREADS ON BYPASS STOPCOCK.
| 09-87340-1 |  |  | 0.75 | Single Service |  | Other |  | RISER THREADS | Construction Defect |  | 2009-10-06 | 2009-10-21 | Other | TIGHTENED VALVE | Steel/Wrought Iron |  | FRESNO | SOAP TEST OK. TIGHTENED VALVE ON RISER TO REPAIR LEAKS.
| 09-87521-1 |  |  | 1.25 | Single Service |  | Other |  | RISER THREADS | Construction Defect |  | 2009-10-21 | 2009-10-28 | Other | TIGHTENED VALVE | Steel/Wrought Iron |  | FRESNO | SOAP TESTED OK.
| 09-87588-1 |  |  | 0.75 | Single Service |  | Other |  | RISER THREADS |  |  |  | 2009-10-28 | Skinner Clamp - Clamp |  |  |  |  | SOAP TESTED OK.
| 09-87654-1 |  |  | 0.75 | Single Service |  | Other |  | RISER THREADS | Construction Defect |  | 2009-10-28 | 2009-12-03 | Other | TIGHTEN VALVE | Steel/Wrought Iron |  | FRESNO | SOAP TEST OK. TIGHTEN VALVE ON RISER TO CORRECT LEAK.
| 09-87725-1 |  |  | 0.75 | Branch Service |  | Other |  |  | Construction Defect |  | 2009-11-06 | 2009-11-17 | Other | SKINNER PIPE JOINT CLAMP | Steel/Wrought Iron |  | FRESNO | SOAP TEST OK. INSTALLED SKINNER PIPE JOINT CLAMP.
| 09-87784-1 |  |  | 1.25 | Single Service |  | Other |  | RISER THREADS | Construction Defect |  | 2009-11-05 | 2009-11-17 | Other | TIGHTENED BY-PASS VALVE | Steel/Wrought Iron |  | FRESNO | SOAP TESTED OK.
| 09-87808-1 |  |  | 0.75 | Single Service |  | Other |  | RISER THREADS | Construction Defect |  | 2009-11-06 | 2009-12-07 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | HELM | SOAP TESTED OK.
70 | 81-70054-1 |  |  | 16 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1981-10-09 | 1981-10-09 | Other |  | Steel/Wrought Iron |  | FRESNO | TIGHTENED FITTINGS ON MON. CONTROL VALVE.
70 | 90-30122-1 |  |  |  | Transmission |  | Valves |  |  | Other |  | 1990-05-09 | 1990-06-05 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | FRESNO | CLAY & CHESTNUT. TIGHTEN PLUG ON VALVE. LEAK STOPPED.
70 | 83-30182-1 |  |  | 10 | Distribution Main |  | Physical/Mechanical Joint |  |  | Other |  | 1983-10-18 | 1984-01-03 | Replace Pipe and/or Service |  | Cast/Ductile Iron |  | FRESNO | VENTED LEAKAGE BY DRILLING OVER MAIN.
| 84-91286 |  |  | 10 | [14 empty] | TIED 10" STL TO 10" C.I. WITH (2) 10" STL TO C.I. INSULATD COUPLINGS.
70 | 81-30045-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1981-02-10 | 1981-03-02 | Other |  | Steel/Wrought Iron |  | FRESNO | TIGHTENED BONNETT ON METER FTG FOUND VALVES #4&5 LEAKING LEAKING AT DOWN STREAM FLANGES. REPLACED GASKETS + INSULATION KITS IN BOTH VALVES. 3-10-81. 1/4" METRIC LEAKING FROM BONNET PROPOSED HOLES 12" DEEP D.S. OF VALVES #3, 4, & 5, #3 CLEAR , #4 & 5 30% READINGS ON J.W.
70 | 81-30367-1 |  |  | 12 | Transmission |  | Valves |  |  | Other |  | 1981-10-09 | 1981-10-09 | Other |  | Steel/Wrought Iron |  | FRESNO | METRIC VALVE LEAKING. TIGHTENED PLUG STAFFORD. 10-5-81.
70 | 81-30507-1 |  |  | 12 | Transmission |  | Other |  |  | Other |  | 1981-12-02 | 1982-11-02 | Other |  | Steel/Wrought Iron |  |  | MADE PERM B LINE ON TP MAIN # 138 RETHREADING 1/4" NIPPLE ON BODY AND REPLACING 1/4" METER VALVE. DOWNGRADE TO #2 5-3-82 FOUND #3 READING IN VALVE CASING ISSUED NEW #3 LEAK REPORT LG 12-1-83.
70 | 81-30380-1 |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1980-10-27 | 1981-12-03 | Other |  | Steel/Wrought Iron |  | FRESNO | REPAIR LEAK IN 25C PILOT REG. FOUND READINGS IN REG VAULTS ISSUED NEW LEAK REPORT 2-2-72.
| -0040- |  |  | 12 | Transmission |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1985-03-12 | 1985-04-17 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | FRESNO | REDOPE + TOGHTEN 1" PLUG ON BLOW OFF VALVE A. VAKVE A-24 6' E/E PL OF CHERRY + 37' S/N PL OF JENSEN.
70 | 84-30242-1 | [10 empty] | 1982-12-01 | 1984-12-19 |  |  |  |  | FRESNO | IN VALVE CASING 37' S/N PL JENSEN. 6' E/E PL CHERRY 12-1-82. UPGRADE #2 1% GREASED VALVES. STOPPED LEAK.
| 10-30192-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other | LOOSE PLUG | 2010-09-21 | 2010-10-10 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | FRESNO | REDOPED PLUG ON DRIP SOAP TEST; TIGHTEN & REDOPED 3/4" PLUG ON DRIP VALVE.
| 10-30197-1 | 138 |  | 3 | Transmission |  | Valves |  |  | Other | NEEDED GREASE | 2010-09-30 | 2010-10-09 | Other | GREASED |  |  | HELM | GREASED VALVE SOAP TEST.
70 | 90-30533-1 |  |  | 5 | Transmission |  | Valves |  |  | Other |  | 1980-02-25 | 1981-01-07 | Other |  | Steel/Wrought Iron |  | COALINGA | REPAIRED BY REMOVING METRIC VALVE AND WELDING 2" SAVER VALVE OVER NIPPLE 1-7-81. OVER FEEDER BOTTOM OF HILL BETWEEN 1ST AND 2ND MARKER. READING AT BOTTOM OF HILL WILL BE CHECKED ON ANNUAL IN MAY.
| 91-0-1 |  |  |  | Transmission
68 | 98-70112-1 | 164 |  | 8.625 | Transmission |  | Body of Pipe |  |  | Digin |  | 1998-08-17 | 1998-08-17 | Replace Pipe |  | Steel/Wrought Iron |  | COALINGA | ISOLATED 3 MILES OF TRANSMISSION MAIN TO THE END OF LINE #164, USING VALVE AT AMADOR STA. CUT OUT 6' SECTION OF DAMAGED 8" PIPE, WELDED IN PRE-TESTED 6' SECTION OF 8" PIPE, WLDED IN PRE-TESTED 6' SECTION OF 8" PIPE.
70 | 90-30125-1 |  |  | 4 | Transmission |  | Valves |  |  | Material Failure |  | 1990-05-21 | 1990-05-23 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  |  | ES 514 + 52 LINE MARKER COALINGA; FOUD BOLTS UNDER LEAKING REMOVED BOLTS UNDER VALVE LEAKING. REMOVED BOLTS AND INSTALLED LOCK WASHERS. SIX BOLTS UNDER VALVE COULD NOT BE TIGHTENED.
70 | 80-30530-1 |  |  | 5 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1980-02-14 | 1981-01-07 | Other |  | Steel/Wrought Iron |  | COALINGA | REPAIRED LOOSENING CAP, DOPING AND PUTTING CAP BACK ON 1-7-81. CAP ON NIPPLE UNDER FEEDER LINE ABOVE GROUND.
70 | 90-30127-1 |  |  | 8 | Transmission |  | Fitting |  |  | Corrosion |  | 1990-05-24 | 1990-05-24 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | COALINGA | TIGHTENED CAP & PLUG ON BLOW OFF SAV-A-VALVE; FOUND CAO & PLUG. LEAKING ON 8" TP MAIN TIGHTENED TO STOP LEAK.
68 | 94-70090-1 |  |  | 2 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1994-06-27 | 1994-06-28 | Replace Pipe |  | Steel/Wrought Iron |  | HURON | REPAIR CORRSION LEAK BY REPLACING PIPE 1' SECTION; WELDED 1' SECTION OF 2" .154 ADSI SL GB SMLS. TESTED 12-2-81.
98 | 10-58220-1 | DCUS2451 |  | 2 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-22 | 2011-02-18 | Other | TURNED INLET VALVE OFF | Steel-Other |  | KETTLEMAN CITY | TO BE REPAIRED WHEN IDLE SERVICE IS REQUESTED TO BE TURNED BACK ON; ABOVE GROUND INLET/ OUTLET VALVE AT REG STATION SHUT OFF SERVICE TO METER SET IS NOT USE AT THIS TIME. LEAKS WUKK BE REPAIRED WHEN REQUEST FOR GAS TO BE TURNED BACK ON.
| 09-31021-1 |  |  |  | Service |  | Valves |  |  | Atmospheric Corrosion |  | 2009-08-11 | 2009-09-17 | Other | TIGHTEN VALVE | Steel/Wrought Iron | STEEL | FRESNO | AT BYPASS VALVE - NO ROOM FOR SKINNER CLAMP; TIGHTEN VALVE; SOAP TESTED BY PASS.
| 09-30549-1 |  |  | 0.75 | Single Service |  | Other |  | RISER THREADS | Construction Defect |  | 2009-05-27 | 2009-08-04 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | FRESNO | SOAP TEST OK - REPAIRED BY INSTALLING CLAMP.
| 86-30398-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1986-10-07 | 1986-10-08 | Other | REPLACED CURB VALVE | Copper |  | FRESNO | FOUND CRACKED CURB VALVE. GREASED & WRAPPED VALVE. SOAP TESTED FOR LEAK. NOT LEAK. GREASE VALVE. CALLED FOR CREW AT 2750 S. EAST 3710 CREW RESPONDED.
70 | 86-30416-1 |  |  | 12 | Transmission |  | Other |  |  | Other |  |  | 1986-10-08 | Other |  | Steel/Wrought Iron |  |  | GREASED VALVE.
70 | 90-70017-1 |  |  | 6 | Transmission |  | Valves |  |  | Material Failure |  | 1990-05-07 | 1990-05-07 | Other |  | Steel/Wrought Iron |  | FRESNO | LEAK FOUND ON 3/4" TP VALVE #2024 ON THE THREADS. REPLACED 3/4" TP VALVE # 2024 WITH NEW ONE AND WELDED ON NEW 3/4" TP THREADED NIPPLE FOR PERMANENT REPAIRS; THE SERVICE WAS PLUGGED DOWN AT MAIN. SO 3/4 VALVE COULD BE REPLACED AND 3/4" STL TP NIPPLES AT EACH END OF VALVE WERE REPLACED FOR PERMANENT REPAIRS. J.W. ARE AND SOAP TEST ALL FITTINGS. (NO LEAKS).
70 | 91-30092-1 | 138 |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1991-04-02 | 1991-04-04 | Other |  | Steel/Wrought Iron |  | FRESNO | POSSIBLE LEAK ON T.P. VALVE LINE #138. DRILLED HOLES AND BAR TESTED AREA FOR TEMPORARY REPAIRS; LEAK ON TP VALVE, GREASE VALVE TO STOP LEAK BUT STILL GETTING READINGS ON THE E/O SIDE OF TP VALVE. BAR TESTED AND JW AREA AGAIN. SOAP TESTED GREASE STEM AND STOPPED FOAMER BUT LEAK NEEDS TO BE FURTHER INVESTIGATED. BAR HOLED OVER MAIN AND VALVE 0% READINGS ON LEL.
70 | 87-30164-1 |  |  | 6 | Transmission |  | Regulator |  |  | Other |  | 1987-09-10 | 1987-09-11 | Other |  | Steel/Wrought Iron |  |  | BY PASS VALVE - LEAKING BY, SEAT CUT OUT AN DIPH BLOWING REPAIR AS NEEDED + GREASE VALVE.
70 | 90-30028-1 |  |  | 4 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1990-01-12 | 1990-01-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SANGER | TIGHTEN BOLTS, STOPPED LEAKS.
| 87-30136-1 |  |  |  | Transmission |  | Regulator |  |  | Digin |  | 1987-09-10 | 1987-09-18 | Other |  |  |  |  | TURN OFF H.P.R SET - TRACTOR DROVE OVER WITH DICE - BOX BROCKEN ON EXETC. - HAS 5 METER MANIFOLD 4 METERS ALL OFF - SEND CREW. INST NEW 24X17 BOX W/ EXTENSION. REPLACE HPR WITH REBUILD SET. SOUTH SIDE OF NORTH SET.
70 | 79-30309-1 |  |  | 3 | Transmission |  | Valves |  |  | Other |  | 1979-09-12 | 1980-02-05 | Other |  | Steel/Wrought Iron |  | FRESNO COUNTY | VALVE WAS GREASED AND LEAK STOPPED 2-5-80. B.O. BOX FOR DRIP.
70 | 83-50112-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion | INTERNAL | 1983-09-26 | 1983-10-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN JOAQUIN | CORROSION LEAK ON MAIN OPEN BELL HOLE AND SAME AS ABOVE. NOTE L#111 HAS WATER WITHIN THE PIPING SYSTEM.
70 | 81-50119-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1981-12-07 | 1981-12-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | LINE #111, DAMAGED BY D-9 K CAT WHILE SUB SOILING FOR FRESNO FARMS, 13 526 S.O. ELM, CARROTNERS. MAIN REPAIRED BY ABUTT WELDING 15' 9" OF .280 WALL, GRADE X-42 PIPE IN THE LINE. THE REPAIRED SECTION IS 124' SOUTH OF THE PIPELINE MARKER ON THE N/SIDE OF NEBRASKA.
70 | 83-30219-1 |  |  | 6 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1983-11-04 | 1984-03-23 | Other |  | Steel/Wrought Iron |  |  | FOUN DLEAK AT FLANGES ON VALVE F-03. REPAIRED BY TIGHTENING BOLTS AROUND FLANGE. PAINTED BOLTS + NUTS WITH PRIMER AND WRAPPED. COMPLETED 3-23-83.
70 | 93-30260-1 |  |  | 4 | Transmission |  | Valves |  |  | Material Failure |  | 1993-11-24 | 1994-10-05 | Other |  | Steel/Wrought Iron |  | FRESNO | LEAK FOUND ON 4" GAS TP VALVE. INSTALLED A 4" BALL VALVE FOR PERMANENT REPAIRS. DOWNGRADE TO 2. Y-87 VALVE NON-OPERATIONAL NEEDED TO BE REPLACED. INSTALLED (2) 4" LINE STOPPER FITTINGS H-17256 (CODE 02-2094) AND A 4" CARBON STEEL BALL VALVE WAS INSTALLED FOR REPAIRS. CONTROL FITTINGS WERE PRETESTED BEFORE BEING TAPPED OUT. WELDS WERE TESTED ALSO WITH SOAP. NO LEAKS.
70 | 94-50113-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Material Failure |  | 1994-07-12 | 1994-07-12 | Other |  | Steel/Wrought Iron |  | CLOVIS | H&R SET FOUND LEAKING. UNION FITTING & 3/4" GAS VALVE ON TP SIDE. TIGHTEN UNION FITTING & GAS VALVE FOR PERMANENT REPAIRS. SOAP TESTED NO LEAKS.
70 | 95-30077-1 |  |  | 6 | Transmission |  | Valves |  |  | Material Failure |  | 1995-02-14 | 1995-05-05 | Other |  | Steel/Wrought Iron |  | FRESNO | FOUND LEAK ON 6" TP F-08 VALVE. INSTALLED GREASE TO VALVE FOR PERMANENT REPAIRS; INSTALLED GREASED TO GAS T.P. VALVE F-08 FOR PERMANENT REPAIRS. SOAP TESTED VALVE NO LEAKS.
70 | 81-30434-1 |  |  | 4 | Transmission |  | Regulator |  |  | Construction Defect |  | 1981-06-02 | 1981-06-02 | Other |  | Steel/Wrought Iron |  | KARMAN | REPAIR 1 1/2 HPR 2ND STAGE. REPLACE DIAPH. BOTTS, RUSTED.
70 | 79-30151-1 |  |  |  | Transmission | [6 empty] | 1979-06-06
70 | 78-30260-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1978-07-20 | 1979-01-17 | Other |  | Steel/Wrought Iron |  | FRESNO | REPAIRED LEAK IN VALVE TAPE AT REG SET. IN REG BOX NEXT TO 2'" RISER AT 500B METER SET.
70 | 82-50044-1 |  |  | 12.38 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1982-07-01 | 1982-07-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | FRESNO | RE: GM 4314365.
70 | 80-30381-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1980-09-03 | 1980-09-12 | Other |  | Steel/Wrought Iron |  | FRESNO | TIGHTEN GREASE FITTING IN BYPASS VALVE. IN REG BOX IN FRONT OF 7896.
70 | 88-30200-1 |  |  | 0.75 | Transmission |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1988-08-19 | 1988-09-13 | Other |  | Steel/Wrought Iron |  | FRESNO | REDOPE MULDER CAP + TIGHTEN.
| 10-30186-1 |  |  | 0.25 | Transmission |  | Other |  | PLUG | Other | LOOSE PLUG | 2010-09-15 | 2010-10-10 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | FRESNO | REDOPED PLUG ON HPR. TIGHTENED & REDOPED 1/4" PLUG ON HPR SET SOAP TEST.
| 10-30186-1 |  |  |  | Transmission |  | Other |  | PLUG | Other | LOOSE PLUG | 2010-09-15 |  |  |  | Steel/Wrought Iron |  | FRESNO
| 88-30098-1 |  |  | 0.75 | Transmission |  | Regulator |  |  | Other |  |  | 1988-08-08 | Other |  | Steel/Wrought Iron |  |  | REPLACE PRIMARY AND DISTRIBUTION OF H.P.R.S.
| 91-30347-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1991-10-10 | 1991-10-15 | Other |  | Steel/Wrought Iron |  | CLOVIS | GREASE VALVE (2-1)
70 | 80-30377-1 |  |  | 12 | Transmission |  | Other |  |  | Other |  | 1980-09-10 | 1980-09-15 | Other |  | Steel/Wrought Iron |  | FRESNO | THREADS ON RELIEF VALVE LEAKING TIGHTENED C/OK.
70 | 80-30378-1 |  |  | 12 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1980-09-10 | 1980-09-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | FRESNO | IN REG BOX FOR SERVICE TO 1800. NUMEROUS FITTINGS LEAKING. REMOVED HPR-20. INSTALLED HPR-20 & FISHER H-202 RELIEF.
70 | 81-50106-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1981-11-08 | 1981-11-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | FRESNO | ISOLATED 5.85 MILES OF PIPE BY CLOSING VALVE 15.18+ 21.55 TO STOP GAS FLOW. PERM. REPAIRS MADE BY INSTALLING 3411" OF 12.750" PIPE ON 11-9-81.
70 | 92-30077-1 |  |  | 0.2 | Distribution Main |  | Other |  |  | Other |  | 1992-01-14 | 1992-04-02 | Other |  | Steel/Wrought Iron |  | FRESNO | INSPECTED TP VALVE FOUND NO LEAKS RESIDUAL FROM LEAK REPAIRED EAST OF THIS LOCATION.
70 | 77-50018-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Construction Defect |  | 1977-02-24 | 1977-02-24 | Other |  | Steel/Wrought Iron |  | FRESNO | 2-21-77. FRESNO COUNTY CONST. CREW WAS REGRADING SHOULDER OF ROAD WHEN MOTOR GRADER STUCK VALVE CASEING FORCEING IT INTO CURB VALVE AND BREAKING THREADS OF 3/4" PIPE AT CURB VALVE. REPAIRS WERE MADE BY CLOSING VALVE A TRANS WELDING IN A NEW 3/4" VALVE. 3-1-77. INSTALLED NEW VALVE CASING & CIVER. INSTALLED OIL DIRT AROUND VALVE CASING AND ALONG SHOULDER OFF ROAD SO THAT THE COUNTY WILL NOT HAVE TO REGRADE THIS AREA.
70 | 87-30140-1 |  |  | 8 | Transmission |  | Girth Weld |  |  | Corrosion |  | 1987-08-10 | 1987-08-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | FRESNO | FOUND CORROSION LEAK ON T/P #111E. INST. LEAK CLAMP FOR TEMP REPAIR. INST. (2) 8" PCF FITTING ON T/P#111E APPROX 500' & 574- W/P BLYTHE AND REPLACED APPROX. 14' OF 8" STL MAIN.
| 88-30102-1 |  |  | 8 | Transmission |  | Girth Weld |  |  | Corrosion |  | 1988-08-18 |  | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | FRESNO
70 | 72-00056-1 |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1972-03-15 | 1974-12-31 | Other |  | Steel/Wrought Iron |  |  | 85.% S/O NER OF W. FRANKLIN TESTED WITH FLAME IONIZATION ON SURFACE AS SHOWN IN ORANGE. GOT .3% AT VALVE VAULT. 12-26-74. PLUG ON 1 1/2" BLOW DOWN VALVE LEAKING GREASED VALVE & DOPED PLUG.
70 | 72-00056-1 | [10 empty] | 1972-03-14 | [5 empty] | FRESNO | RESTESTED 6-4-73). WITH HIGHEST READING TAKEN WAS 100% LEL IN THE AREA OL OLD 2" ABANDONED LINE. (SEE ATTACHED SHEET). WHICH INDICATES WE ARE STILL PICKING UP READINGS FROM OLD LINE.
70 | 83-30158-1 |  |  | 12 | Transmission |  | Valves |  |  | Other |  | 1983-09-15 | 1983-10-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | THIS LEAK REPAIRED (VALVE #17) SHOULD GET METER REPAIRED WITHIN THE WEEK.
70 | 90-30018-1 |  |  | 30 | Transmission |  | Girth Weld |  |  | Other |  | 1989-01-09 | 1990-05-16 | Replace Pipe |  | Steel/Wrought Iron |  | FRESNO | REPLACED 9FT OF 30" PIPE THAT CONTAINED HAD WELD (WO 430460). STRESS CORROSION CRACKING; ISOLATED SECTION AND BLEW DOWN.
70 | 85-70020-1 |  |  | 12 | Transmission |  | Other |  |  | Material Failure |  | 1985-03-22 | 1985-03-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CLOVIS | BODY CASTING ON 829 GROVE PILOT WAS CRACKED. REPLACED WIT NEW PART.
70 | 85-70021-1 |  |  | 12 | Transmission |  | Fitting |  |  | Other |  | 1985-03-22 | 1985-03-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CLOVIS | DOPE ON LINE TO GAGE BOX WAS DRY. RE-DOPED FITTINGS.
| 09-30968-1 |  |  | 0.75 | Single Service |  | Other |  | RISER THREADS | Construction Defect |  | 2009-07-29 | 2009-09-09 | Other | SKINNER PIPE JOINT CLAMP | Steel/Wrought Iron |  | FRESNO | SOAP TEST - OK. INSTALL SKINNER PIPE JOINT CLAMP.
70 | 91-30345-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1991-10-10 | 1991-10-15 | Other |  | Steel/Wrought Iron |  | FRESNO | GREASE (F-04)

## Descriptions
Coded Field Name | Definition
DISTRICTNUM | PG&E district number, as recorded on the document in the corresponding field
LEAKNUM | Leak number assigned to document, as recorded on the document in the corresponding field
LINENUM | Line number - PG&E transmission line number, as recorded on the document in the corresponding field
MILEPOINT | Mile Point - mile point along the PG&E line where the leak occured, as recorded on the document in the corresponding field
LINESIZE | Line Size - diameter of the line on which the leak occurred, as recorded on the document in the corresponding field
LINEUSE | Line Use - PG&E defined line use for the line on which the leak occurred, as recorded on the document in the corresponding field
OTH_LINEUSE | Additional data recorded on the document that appears to indicate line use information in addition to the prior field, as recorded on the document
LEAKSOURCE | Leak Source - the source component where the leak occurred, as recorded on the document in the corresponding field
LEAKSOURCE02 | Leak Source - additional data recorded on the document that appears to indicate leak source information in addition to the prior field, as recorded on the document
OTH_LEAKSRC | Hand written entry accompanying the selection of 'Other' in the Leak Source field, as recorded on the document
LEAKCAUSE | Leak Cause - the cause of the leak, as recorded on the document in the corresponding field
OTH_LEAKCAUS | Hand written entry accompanying the selection of 'Other' in the Leak Cause field, as recorded on the document
DATEFOUND | Date Found - the date the leak was discovered, as recorded on the document in the corresponding field
DATEREPAIRED | Date Repaired - the date the leak was repaired, as recorded on the document in the corresponding field
REPAIR_CODE | Repair Code - the translated PG&E code indicating the repair method, as recorded on the document in the corresponding field
REPAIR_OTHER | Hand written entry accompanying the selection of 'Other' in the Repair Code field, as recorded on the document
LINEMATERIAL | Line Material - the base material of the line on which the leak occurred, as recorded on the document
OTH_LINEMAT | Additional data recorded on the document that appears to indicate line material information in addition to the prior field, as recorded on the document
CITY | City in which the point on the line where the leak occurred is located
COMMENTS | Comments present in the comment or remarks field or written on/near the sketch of any other comment on the document