## Sheet1
DISTRICTNUM | LEAKNUM | LINENUM | MILEPOINT | LINESIZE | LINEUSE | OTH_LINEUSE | LEAKSOURCE | LEAKSOURCE02 | OTH_LEAKSRC | LEAKCAUSE | OTH_LEAKCAUS | DATEFOUND | DATEREPAIRED | REPAIR_CODE | REPAIR_OTHER | LINEMATERIAL | OTH_LINEMAT | CITY | COMMENTS
48 | 72-57002-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-11-18 | 1972-11-22 | Patch Welded |  | Steel/Wrought Iron |  |  | EXTERNAL CORROSION LEAK. HOLE SIZE 1/4" X 1/4" PERMANENT REPAIRS= 4" X 4" WLED PATCH .250 W.T.
72-57000-1
48 | 72-57000-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1972-07-08 | 1972-07-11 | Patch Welded |  | Steel/Wrought Iron
48 | 72-57001-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-09-08 | 1972-09-12 | Patch Welded |  | Steel/Wrought Iron |  |  | REPAIRED LEAK EXTERNAL CORROSION HOLE SIZE 1/16" X 1/16" IN CENTER OF 4" X 6" CORRODED AREA. PERMANENT REPAIRS WELD PATCH 8" X 10" .281 WALL API-5LX-GRX42
48 | 72-90001-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1972-03-28 | 1972-03-30 |  |  | Steel/Wrought Iron |  | RIO VISTA | 4" INSTALLED ON GM 146083-1959, REPLACED 12" OF 4" LINE.
48 | 72-90002-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1972-03-28 | 1972-03-30 |  |  | Steel/Wrought Iron |  | RIO VISTA | 4" INSTALLED ON GM 146083-1959, REPLACED 21" OF 4" LINE .188 API-SL GRB SMLS
48 | 72-90003-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-09-26 | 1972-09-27 | Patch Welded |  | Steel/Wrought Iron |  |  | HOLE SIZE 1/32" X 1/32"- CORRODED AREA 1" X 1". WELDED PATCH 3" X 3" .250 WALL ROUND CORNERS
48 | 72-90004-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-11-21 | 1972-12-06 | Patch Welded |  | Steel/Wrought Iron |  |  | EXTERNAL CORROSION LEAK HOLE SIZE 1/2: X 1/8"-7 O'CLOCK PERMANENT REPAIRS- 3" X 4" WELD PATCH .219 WALL
48 | 72-90006-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-12-01 | 1973-04-26 | Patch Welded |  | Steel/Wrought Iron |  |  | EXTERNAL CORROSION HOLE SIZE 1/16" X 1/8". CORRODED AREA 2" X 3" PERMANENT PATCH 7" X 9" .375 W.T., ROUND CORNERS, WELDED. LOCATION 6 O'CLOCK
48 | 72-90005-1 |  |  | 0.25 | Gathering |  | Tap Connection |  |  | Damage by outside Forces |  | 1972-11-08 | 1972-12-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | NIPPLE BROKEN OFF BY PRODUCER TANK.. REPLACE 1/4" NIPPLE 2" LINE
48 | 73-57000-1 |  |  | 0.75 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-03-02 | 1973-03-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | BUBBLING THROUGH GROUND; CUT OFF OLD 3/4" SERVICE TEE AND 17" OF 3/4" LINE. REPLACED WITH MUELLER 1/14" VALVE & 18" OF 3/4" LINE. OLD TEE AND LINE INSTALLED ON GM 120537-1952
48 | 73-90000-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1973-04-06 | 1973-04-09 | Patch Welded |  | Steel/Wrought Iron |  |  | 4" INSTALLED ON GM70811-1943
48 | 73-57001-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1973-04-06 | 1973-04-10 | Patch Welded |  | Steel/Wrought Iron
48 | 73-90001-1 |  |  | 6 | Gathering | [6 empty] | 1973-04-11 | 1973-04-12 |  |  | Steel/Wrought Iron |  |  | REMOVED 7'-1" OF OLD...AND INSTALED 7'-2" NEW 6" PIPE .API-SL GRB SMLS .188W.T. EXTERNAL CORROSION 3 O'CLOCK HOLE SIZE 1/8" X 1/8" CORRODED AREA 90% THROUGH PIPE ON TOP AREA REASON FOR REPLACING. 6" INSTALLED ON GM 53872-1937
48 | 73-57003-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion | ; | 1973-04-27 | 1973-05-02 | Patch Welded |  | Steel/Wrought Iron |  |  | BLOWING THROUGH
48 | 73-57003-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-04-27 | 1973-05-02 | Patch Welded |  | Steel/Wrought Iron |  |  | BLOWING THROUGH; EXTERNAL CORROSION HOLE SIZE 1/8" X 1/8" INSTALLED WELD PATCH .250 W.T. 2" X 2"
48 | 73-90002-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-10-03 | 1973-10-17 | Patch Welded |  | Steel/Wrought Iron |  |  | DEAD VEGITIATION; REPAIRED LEAK EXTERNAL CORROSION HOLE SIZE 1/16" X 1/8". TEMP REPAIRS WELD PATCH 3" X 3" ROUND CORNERS .281 WALL
48 | 73-57004-1 |  |  | 4 | Gathering |  |  |  |  | Corrosion | ; | 1973-10-16 | 1973-10-16 |  |  | Steel/Wrought Iron |  |  | SLIGHT BLOWING THROUGH GROUND; PERMAMENT REPAIRS: REPLACED 1 FORR OF 4" PIPE .188" API SL GRB SMLS
48 | 73-57005-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1973-10-19 | 1973-10-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | 3" C 4" HOLE IN PIPE PUNCTURED BY RIPPER TOOTH
48 | 73-57006-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1973-11-21 | 1973-12-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron
48 | 74-57000-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion | ; | 1974-01-31 | 1974-02-12 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | REPAIRED LEAK EXTERNAL CORROSION PERMANENT REPAIRS WELD SLEEVE-SPLIT .281 WALL API-SL GRB SMLS INSTALLED (2) PLB ANODES
48 | 73-57002-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion | [5 empty] | Steel/Wrought Iron
48 | 73-57002-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1973-04-19 | 1973-04-20 | Patch Welded |  | Steel/Wrought Iron |  |  | WEST THROHTON GAS FIELD. INSTERNAL CORROSION. PERMANENT PATCH 4" X 6" R.C. .250 W.T. ULTRASOUND CALIPHER TESTED PIPE WALL FOR POSITION OF PATCH BEFORE WELDING 4 O'CLOCK HOLE 1/16" X 1/8"
48 | 74-57002-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-07-13 | 1974-07-15 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | GAS BURNING ABOVE GROUND - STRAW STABLE WAS BURNT IN FIELD; WELDED SLEEVE .250 WALL EXT. CORR.
48 | 74-90000-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-08-07 | 1974-08-08 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | DEAD VEGITATION; EXT. CORR. HOLE 1/8" X 1/8" 5 O'CLOCK WELDED SLEEVE .250 W.T.
48 | 74-57001-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-10-03 | 1974-10-04 | Weld Over Sleeve or Can |  | Steel/Wrought Iron
48 | 74-57003-1 |  |  | 10 | [7 empty] | 1974-11-09
48 | 74-57004-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1974-11-25 | 1974-11-27 | Weld Over Sleeve or Can |  | Steel/Wrought Iron
48 | 74-57004-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-12-19 | 1974-12-20 | Weld Over Sleeve or Can |  | Steel/Wrought Iron
48 | 75-57002-1 |  |  | 0.5 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-08-26 |  | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Found 1/4" Hole in 1/2" pip elds to old style... Permanent repairs- Out off Mt. And welded 2" H.P. Cap over...
48 | 75-57003-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1975-09-08 | 1975-09-11 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Hole size 1/8" x 1/8" -Pitted...3/4" x 3/4" 7 o'clock- External corrosion. Permanent Repair- welding sleeve .188 wall.
48 | 75-90000-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1975-07-03 | 1975-07-09 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | External Corrosion- Location 7 o'clock. Hole size 1/16" x 1/4"- Corroded area installed .250 wall split sleeve 12" wide
48 | 75-57004-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1975-10-02 | 1975-10-08 | Patch Welded |  | Steel/Wrought Iron
48 | 75-57006-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1975-12-17 | 1975-12-18 | Patch Welded |  | Steel/Wrought Iron |  |  | Hole size 1/4" x 1/4" -10 o'clock External corrosion. Permanent Repairs = 3"x 3" Patch .219 wall, install 9lb....
48 | 75-57007-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1975-12-17 | 1975-12-18 | Patch Welded |  | Steel/Wrought Iron |  |  | Hole size 1/4" x 3/8" -8 o'clock External Corrosion. Permanent Repair = 3" x 4" Patch .219 wall install 9lbs ...
48 | 75-57005-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-11-26 | 1975-11-26 | Patch Welded |  | Steel/Wrought Iron |  |  | External corrosion- location 5 o'clock hole size 3/8" x 3/8" 35,000 S.M.Y.S. Welded on 3" x 5" permanent Patch .375 wall with round corners
48 | 76-57000-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-03-14 | 1976-03-15 | Patch Welded |  | Steel/Wrought Iron |  |  | External corrosion - hole size 1/8" x 1/8" -6 o'clock Permanent repairs- Weld patch 6" x 6" .375 weld with round corners
48 | 76-90000-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-07-06 | 1976-07-08 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | External corrosion -located 5:30 o'clock hole size 1/16" x 1/8"- Corroded Area 1/2" x 1/2" Permanent repairs .250 Salit sleeve
; ;
48 | 76-57002-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-08-16 | 1976-08-25 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | External corrosion. Location 5... O'clock hole size... corroded area 1/2" x 1/2" Permanent repaairs 4"x 4" .375 Patch
48 | 76-57001-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1976-08-04 | 1976-08-05 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Sleeve, leak at 4 o'clock
48 | 76-90001-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-12-08 | 1976-12-09 | Weld Over Sleeve or Can |  | Steel/Wrought Iron
48 | 76-57003-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-12-08 | 1976-12-10 | Weld Over Sleeve or Can |  | Steel/Wrought Iron
48 | 77-57001-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1977-03-02 | 1977-03-03 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Repaired with 10" sleeve 12" long W. T. .365
52 | 77-57000-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1977-01-31 |  |  |  | Steel/Wrought Iron |  |  | .....7:07....
48 | 77-57000-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1977-01-31 | 1977-12-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Line... on 1/31/77 at 7:07 pm. 10" line removed abandened on G.M. 187216. 12" pipe installed in...place and corrected to 16"...Oac 4..on G.M. 187216
48 | 77-57002-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1977-03-02 | 1977-03-08 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | 77-57006-1; 1/2" Dia. Dit. 1/32" hole, weld on a 5"x 5" Patch
48 | 77-57006-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1977-03-02 | 1977-03-08 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Inst. 6" of .250 w.t. pipe and a 10" sleeve 12" long w.t. 375 Pit 1/2"... 1 1/2" long several small pit at this location
48 | 77-57003-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1977-05-31 | 1977-05-31 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Hole size 1/8" x 1/4" 7 o'clock external corrosion permanent repairs installed 2'-5" of 8" steel pi... install 9lbs a...
48 | 77-57004-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1977-05-31 | 1977-06-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Hole size 1/4" x 1/4" 8 o'clock external corrosion permanent repairs install 11'-5" of 8" steel pi.. install 9lb. anode
48 | 77-57005-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1977-06-01 | 1977-06-03 | Patch Welded |  | Steel/Wrought Iron |  |  | Hole size 1/8" x 1/8" 8 o'clock external corrosion permanent repairs install a 4" x 4" weld Patch round corners .219 wall installed 9 lb. anode.
48 | 77-57007-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-06-07 | 1977-06-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | None
48 | 77-57008-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1977-06-13 | 1977-06-14 | Patch Welded |  | Steel/Wrought Iron |  |  | Leak cause external corrosion 5 o'clock 1/8" x 1/8" hole correded area 1 1/2" x 3/4" repairs 4" x 4" welded patch
48 | 77-90000-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1977-07-29 | 1977-08-02 | Patch Welded |  | Steel/Wrought Iron |  |  | Cause = external cor. location = 7 o'clock hole size 1/16" installed permanet repairs= 5" Dia. Patch .219 w.t.
48 | 77-90001-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1977-12-14 | 1977-12-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Replaced 8" installed on G.M. 73426- New Pipr insstalled from valve o.d. 8" installed on G.M. 451043 Rev. 12 o'clcok external corrosion- 1/4" x 1/4" hole permanent repairs installed 42" of new *" pi...
48 | 77-57011-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1977-11-28 | 1977-11-30 | Patch Welded |  | Steel/Wrought Iron
48 | 77-57012-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1977-02-04 |  |  |  | Steel/Wrought Iron |  |  | Field flooded with water could not get to rupture location until field dryed out on 4/11/1977 to...inspection
48 | 77-57012-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion | ; ; ; ; ; ; ; ; | 1977-02-04 | 1978-01-30 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | See G.M. 187579 for replacement of old 8" Line with new 8" line
48 | 77-90002-1 |  |  | 6 | Gathering | [6 empty] | 1977-12-20 | 1978-03-27 |  |  | Steel/Wrought Iron |  |  | Hole size 1/4" x 1/4" 6 o'clock 1-9lb anode external corrosion permanent repairs weld patch 4" x 4" . 188 wall with round corners
48 | 78-90003-1 |  |  | 8 | Transmission |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1978-01-10 | 1978-01-11 | Other |  | Steel/Wrought Iron
48 | 78-90004-1 |  |  | 6 | Gathering | [6 empty] | 1978-01-13 | 1978-04-24 |  |  | Steel/Wrought Iron |  |  | Hole size 1/8" 6 o'clock external corrosion- permanent repairs installed 3" x 3" weld patch. 188 wall installed 9 lb. anode
48 | 78-57000-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1978-02-17 | 1978-04-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Hole size 1/4" x 1/4" 7 o'clock permanent repaire installed 10' of .237 wall pipe 4" Dia pretested externnal corrosion
48 | 78-57001-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-08-25 | 1978-08-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Leak 3 o'clock punctured by plow permanent repairscut out damaded section and replace by 20" long piece...8" pipe. apl 5l grb.219 wall
52 | 78-57002-1 |  |  | 8 | Gathering | [5 empty] | ; | 1978-08-28 |  |  |  | Steel/Wrought Iron |  |  | Preliminary Report
52 | 78-57002-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1978-08-28 | 1981-01-30 | Clamp |  | Steel/Wrought Iron |  |  | Internal Corss. 6 o'clock installed 8" plideo split sleeve clamps over leaks 1000lb W.P. 2000 lb. shop test installed .n G.M. 19171... each leak hole 1/4" per divers report
48 |  |  |  | 10 | Transmission | [7 empty] | 1978-01-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | None
48 | 77-90002-1 |  |  | 6 | Gathering | [6 empty] | 1977-12-20 | 1978-03-27 |  |  | Steel/Wrought Iron |  |  | Hole size 1/4" x 1/4" 6 o'clock 1-9lb anode external corrosion permanent repairs weld patch 4" x 4" .188 wall with round corners
48 | 77-57009-1 |  |  | 10 | Transmission | [6 empty] | 1977-11-17 | 1978-04-19 |  |  | Steel/Wrought Iron |  |  | Location 6 o'clock hole size 1/2" installed 9 lb. anode cause evternal corrosion permanent repairs installed 5" x 5" welded patch .250 wall thickness eroded area 1" to 1 1/2" wide on bottom of pipe for the 20' of pipe exposed. side & top of pipe fair.
48 | 77-57010-1 |  |  | 10 | Transmission | [6 empty] | 1977-11-17 | 1978-04-19 |  |  | Steel/Wrought Iron |  |  | Location 6 o'clock- hole size 3/8" installed 9 lb. anode. Cause- external corrosion permanent repairs installed 5" x 5" welded patch .250 wall thickness eroded area 1" to 1 1/2" wide on bottom of pipe for the 40' of pipe exposed. Side and top of pipe fair
48 | 77-90004-1 |  |  | 6 | Gathering | [6 empty] | 1978-01-13 | 1978-04-24 |  |  | Steel/Wrought Iron |  |  | Hole size 1/8" -6 o'clock external corrosion- permanent repair installed 3" x 3" weld patch of .188 wall installed 9 lb. anode
48 | 78-90001-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1978-05-16 | 1978-05-17 |  |  | Steel/Wrought Iron |  |  | HOle size 1/16" x 1/16" -External Corrosion- Active- permanent repairs -3"x 4" welded patch .250 wall 6 o'clock 32lb. anode installed
48 | 78-90000-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1978-05-16 | 1978-05-17 |  |  | Steel/Wrought Iron |  |  | Hole size 1/8" x 1/8" -External corrosion- Active- Permanent repairs 4" x 4" wleded patch .250 wall 6 o'clocl 32 lb. Anoded installed
48 | 78-90005-1 |  |  | 10 | Gathering | [6 empty] | 1978-07-06 |  |  |  | Steel/Wrought Iron
48 | 78-90005-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1978-07-06 | 1978-12-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | 2488 feet of 10" 195 removed- Installed and replaced with 2488 feet of 3" steel pipe -G.M. 405138....
48 | 78-57003-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-11-09 | 1978-12-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Permanent repairs- Installed 39" of 6" pipe .188 wall -GR.B -smls and 11" of 6"pipe .188 wall gr.b-erw. Removed 50" old pipe see attached strength + est pressure report.
48 | 78-57003-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-11-09 |  |  |  | Steel/Wrought Iron |  |  | Pipe punctured by plow -3 o'clock permanent repairs - installed _" of 6" steel .___ wall-API
48 | 78-90006-1 |  |  | 8 | Gathering | [6 empty] | 1978-12-11 | 1978-12-13 |  |  | Steel/Wrought Iron
48 | 79-57000-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-02-12 | 1979-02-27 | Patch Welded |  | Steel/Wrought Iron |  |  | External corrosion- location 12 o'clock holesize 1/16" x/8". Permanent repairs- weld patch with rou... corners .250 wall- patch size 3'x4'
48 | 79-57001-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-02-12 | 1979-02-27 | Patch Welded |  | Steel/Wrought Iron |  |  | External corrosion- location 12 o'clock hole size 1/16" x 1/8" Permanent repairs- weld patch with round corners .250 wall patch size 3" x 5"
48 | 79-52002-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1979-04-04 | 1979-04-05 | Patch Welded |  | Steel/Wrought Iron |  |  | External corrosion 5 o'clcok 1/8" x 1/8" repairs 4" x 4" welded patch
48 | 79-90003-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1979-04-03 | 1979-04-04 | Patch Welded |  | Steel |  |  | Hole size 1/4''x1/4'' - 6 o'clocl, external corrosion - permanent repairs, weld on patch 4'x4' x .188 wall. Rosin corners, inst 1, 9LB anode
48 | 79-90000-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1979-02-23 | 1979-02-26 | Patch Welded |  | Steel/Wrought Iron |  |  | External Corrosion 6 o'clock permanent repairs- installed .219 wall 4" x 4" weld patch with round corners 1-9# anode
48 | 79-90001-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1979-02-23 | 1979-02-26 | Patch Welded |  | Steel/Wrought Iron |  |  | External corrosion 6 o'clock Permanent Repairs- installed .219 wall 4" x 4" weld patch with round corners
48 | 79-90002-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1979-02-23 | 1979-02-26 | Patch Welded |  | Steel/Wrought Iron |  |  | External Corrosion 7 o'clock permanent repairs- installed .219 wall 4 "x 4" weld patch with round corners 1-9# anode
o;
48 | 79-57003-1 |  |  | 0.5 | Transmission |  | Drip |  |  | Other |  | 1979-06-13 | 1979-06-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron
48 | 79-90004-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1979-08-08 | 1979-08-15 | Patch Welded |  | Steel/Wrought Iron |  |  | External corrosion 3 o'clock 1/8" x 1/8" repair leak with patch 4 x 5 x .219
o;
48 | 79-57004-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-11-02 | 1979-11-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Replaced 24" of pipe 0.188 6" permanent repair API 5 L GR B ERW
48 | 79-57005-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-11-08 | 1979-11-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Remove 3'6" of damaged 8" pipe. Installed 3'-6" of new 8" pipe API 5LX GRX42 ERW .172 wall FS 67+48.3 to FS 67+52._ Permanent repairs. Repairs on D & C 23163-C test Report Attched
48 | 79-90005-1 |  |  | 12 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1979-11-30 | 1979-11-30 | Patch Welded |  | Steel/Wrought Iron |  |  | Hole size 1/4" x 1/4", 6 o'clock external corrosion - temporay repairs of welded patch 4" x 4" .250 weld 12" line to be replaced in 1980
48 | 79-57006-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1979-12-18 | 1979-12-18 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | External corrosion- 6 o'clock permanent repairs weld sleeve. 250 wall hole size 1/4" x 1/4" installed (1) 9 lb. Anode
52 | 86-57007-1 |  |  | 0.5 | Gathering |  | Fitting |  |  | Digin |  | 1986-10-06 | 1986-10-06 | Other |  | Steel/Wrought Iron |  |  | Cut & cap 1/2" drip line below ground level
52 | 86-57006-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1986-09-30 | 1986-09-30 | Other |  | Steel/Wrought Iron |  |  | Replaced 2' of .154 4 pipe with 2' of .188 WT API 5LX 42 ERW on main acctivity 10-1-86
52 | 86-90003-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1986-09-22 | 1986-09-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Replaced 36" of 8" pipe on clearance 32-86 RV; External Corrosion
52 | 86-90002-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion | INTERNAL | 1986-08-11 | 1986-08-13 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Internal Corrosion Leak; Replace 3' of 6" pipe, wt .156
52 | 86-90000-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1986-08-01 | 1986-08-01 | Other |  | Steel/Wrought Iron |  |  | Internal corrosion leak; replaced 2446' of 6 & 8" pipe on GM 4540233 9/16/86
52 | 86-90001-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1986-08-08 | 1986-08-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Replace 36' of 4 " pipe, wt .141 to repair internal corrosion leak
52 | 86-57005-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion | EXTERNAL | 1986-06-15 | 1986-06-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | External leak. repair leak with 24" of 6" pipe, wt. .280
52 | 86-57004-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion | INTERNAL | 1986-06-13 | 1986-06-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Internal corrosion leak at 6 o'clock. Install 96" of 10" pipe wt 0.219
52 | 86-57003-1 |  |  | 0.75 | Gathering |  | Fitting |  |  | Other | Piping damaged by object floating in water while island was flooded | 1986-05-11 | 1986-07-17 | Replace Pipe |  | Steel/Wrought Iron |  |  | Replace 3/4" x 4" x-hvy nipple on anderson greenwood relief valve at tyler is. farms #9 gas well
52 | 86-57002-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion | INTERNAL | 1986-04-17 | 1986-04-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Install 26" of 6" pipe w.t. .188 with 2-6" sleeve, w.t. .375 ; IMT Corrosion leak
52 | 86-57001-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion | INTERNAL | 1986-03-08 | 1986-04-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Replace 26" of 6" .188 wt; Internal corrosion leak
52 | 86-57000-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion | EXTERNAL | 1986-02-18 | 1986-04-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Replace 26 1/4" of 6 " .280 wt. ; External Corrosion leak
52 | 80-57001-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-04-03 | 1980-04-04 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Permanent repairs made by welding a split sleeve .250 wall over 1/8" x 1/8" hole made by point of plow in pipe.; Farmer hit line on 4-3-80
52 | 80-57002-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-09-12 | 1980-09-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Permanent Repairs installed 2' of 4" steel pipe.
52 | 80-90000-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-01-29 | 1980-03-27 | Patch Welded |  | Steel/Wrought Iron |  |  | Hole 1/8" x 1/8" external corrosion - 6 o'clock isntalled permanent weld patch .188 Patch size 2" x 2" installed 32lb. annode.
52 | 80-90000-1 |  |  | 4 | Gathering | [6 empty] | 1980-01-29 |  |  |  | Steel/Wrought Iron
48 | 80-57000-1 |  |  | 8 | Gathering |  | Girth Weld |  |  | Construction Defect |  | 1980-01-19 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Weld open up 12 noon to 5pm due to strain on line. line jumped 7" up on valve #180 side. Installed piping as shown above.
52 | 80-57004-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-10-08 | 1980-10-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Permanent repair made installed 2'10" of 6" of stl. pipe .156 w & 45 degree welded ELL. Starting 6' above 57+47 on over head ditch crossing.
52 | 80-90001-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-03-27 | 1980-03-27 | Patch Welded |  | Steel/Wrought Iron |  |  | Hole 1/16" x 1/8" external corrosion 6 o'clock installed permanent weld patch .188 patch size 2" x 2"
52 | 80-90002-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-03-27 | 1980-03-27 | Patch Welded |  | Steel/Wrought Iron |  |  | Hole 1/16" x 1/4" External corrosion 6 o'clock installed permanent weld patch .188 w. patch size 2"x2"
52 | 80-90003-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-03-27 | 1980-03-27 | Patch Welded |  | Steel/Wrought Iron |  |  | Hole 1/4" x 1/4" external corrosion 6 o'clock installed permanent weld patch .188w. patch size 2 1/4" x 2 1/4"
52 | 80-90004-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-04-11 | 1980-04-14 | Patch Welded |  | Steel/Wrought Iron |  |  | Ext. Corr. Hole 1/8"x 1/8" -6 o'clcok ; Permanent repairs -weld patch .250w. 2"x2" size.
52 | 80-57002-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-09-15 | 1980-09-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Cut off 35' of 4 " old line replaced w/ 35'4" of .156 wall GRB ERW permanent repair.
48 | 80-57003-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-09-22 | 1980-10-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Permanent repairs replaced 29' of 2" of 8" .322 w. API SL SMLS steel pipe internal corrosion 9 o'clock
52 | 80-57005-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-10-17 | 1980-10-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Permanent repairs: Replace w/30" of 6" steel pipe. Hole 9 o'clock punctured by ripper.
52 | 80-90005-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-06-26 | 1981-03-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Removed old 4" pipe and replaced with 204' of API 5L GR.B- ERW- .156-3" pipe on G.M. 4234340
52 | 80-90006-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-06-26 | 1981-03-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Removed old 4" pipe and replaced with 204' of API 5L GR.B SMLS-.216-3" 2,830' of API 5L GR.B ERW -.156-3" pipe on GM.4234340
52 | 80-90007-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-06-26 | 1981-03-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Removed old 4" pipe and replaced with 204' of API 5L GR.B SMLS -.216-3" 2,830' of API 5L GR.B -ERW- .156-3" pipe on G.M. 4234340
52 | 81-90000-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1981-08-03 | 1981-08-04 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Permanent Repairs. Installed .250 wall split sleeve. Hole size 1/8" x 1/8" Locqation - 7 o'clock. External corrosion.
52 | 82-57001-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1982-01-16 | 1982-01-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Internal corrosion - One localized area at 5 o'clock-area 1 1/4" in diameter sloping to 1/16" x 1/4" hole. removed section of pipe and replaced with 24 3/8" section of tested 10 pipe. welds x-rayed and ok API 5LX GR. x 42 ERW PL tape
52 | 82-90000-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1982-02-17 | 1982-02-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | External corrosion- cut out 9'-8 1/4" of 4" pipe and replaced with 9'-8 1/2" of pretested API 5L-GR.B-SMLS .237 4 " pipe. Leak location 8 o'clock
52 | 82-57000-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1982-01-05 | 1982-02-23 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | External corrosion- Leak Location 5 o'clock ; Permanent Repairs- Split sleeve. -.250 wall patential to ground 690 m/v per P. Hanson. Installed two 30 LB. Anodes at each of bell hole on 10" line
52 | 82-57000-1 |  |  | 10 | Gathering | [6 empty] | 1982-01-05 |  |  |  | Steel/Wrought Iron
52 | 81-90001-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1981-11-30 | 1982-02-26 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | External Corrosion -5 o'clock leak location 1/4" x 1/16" hole - Permanent repair installed .219 wall split sleeve installed two 30lb anodes.
52 | 82-90001-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1982-03-15 | 1982-03-19 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Ext. Corrosion, Leak location at 6 o'clock. Permanent repair split sleeve. .181 wall
52 | 82-90002-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1982-03-18 | 1982-03-19 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Ext. Corrosion, leak location at 6 o'clock. permanent repairs= with split sleeve. .250
52 | 82-90003-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1982-03-18 | 1982-03-22 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Ext. Corrosion, Leak location at 5 o'clock. Permanent repairs with split sleeve. .250
52 | 82-57002-1 |  |  | 4 | Gathering |  | Girth Weld |  |  | Construction Defect |  | 1982-04-21 | 1982-04-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Replace 18" of 4" w.t. .237;
48 | 82-57004-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1982-10-11 | 1982-10-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Replace 24" of 6" w.t. .188 & 6" el...
52 | 82-57005-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1982-11-26 | 1982-12-01 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Ext. Corrosion 1/4" x 1/8" hole. Permanent repair installed .219 wall split sleeve. Installed 30 lb anode.
52 | 83-90000-1 |  |  | 0.75 |  |  | Other |  |  | Other |  | 1983-04-11 | 1983-04-14 | Other |  | Steel/Wrought Iron |  |  | Leak found on uprating L-168; Leaking Cap on mueller tee. for pres. tap; On riser at anna gamaal #1; Leak repaired by G.C. Dept. on 4-14-83
52 | 83-90000-1 |  |  | 0.75 |  |  | Other |  |  | Other |  | 1983-04-11 | 1983-04-14 | Other |  | Steel/Wrought Iron
52 | 83-57000-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-03-11 | 1983-04-15 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Repaired with full sleeve 10"x 12"x .375
52 | 83-57000-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-03-11 | 1983-04-15 | Weld Over Sleeve or Can |  | Steel/Wrought Iron
52 | 83-57002-1 |  |  | 12 | Transmission |  | Drip |  |  | Damage by outside Forces |  | 1983-06-30 | 1983-07-14 | Other |  | Steel/Wrought Iron |  |  | Repaired with 1" mueller tee & 10' of 3/4" pipe.
52 | 83-57001-1 |  |  | 0.75 |  |  | Body of Pipe |  |  | Corrosion |  | 1983-04-11 | 1983-09-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Repaired using 1/2" x 4" riser... from 3/4" Drip
52 | 83-57003-1 |  |  | 0.75 |  |  | Body of Pipe |  |  | Damage by outside Forces |  | 1983-07-29 | 1983-08-01 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | weld on 1" Sleeve 6" long
52 | 84-57001-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-05-02 | 1984-05-03 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Weld on .375" x 10" Full Circle Sleeve
52 | 84-57000-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1984-01-25 | 1984-09-13 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Replaced 30 13/16" of 8 " .219 pipe; Internal corrosion leak
52 | 84-90001-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1984-09-06 | 1984-09-06 | Patch Welded |  | Steel/Wrought Iron |  |  | External corrosion 3 o'clock 1/8" x 1/8" repair leak with 4"x5"x.219 patch
52 | 84-90002-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1984-10-23 | 1984-10-26 | Weld Over Sleeve or Can |  | Steel/Wrought Iron
52 | 84-90003-1 |  |  | 6 | Gathering |  | Longitudinal Weld |  |  | Corrosion |  | 1984-10-31 | 1984-11-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Repaired by replacing 22'-7'' of 6" pipe on CL-48-84 leak was in 6" by 4" reducer. External leak.
52 | 84-57002-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1984-06-14 | 1985-02-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Abandon 8" line form V-37 to tie point of WF3, install 185L' of 12" line on pres. reduction LOC# 10 GM 1938653. Ext. Leak
52 | 84-57003-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Damage by outside Forces |  | 1984-12-21 | 1985-01-30 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Installed 25" of 4" pipe with 2-4" sleeves 4 9/16"x1/4", A 516 GR 7C, 38000PSI
52 | 85-57000-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Damage by outside Forces |  | 1985-02-06 | 1985-02-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Replace 25' of 8" pipe-w.t. .219 API 5LX GR S-42 ERW
52 | 85-90000-1 |  |  | 0.5 | Transmission |  | Tap Connection |  |  | Damage by outside Forces |  | 1985-02-08 | 1985-02-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Install 1 1/4" dip tube and reinforcing ring. ; Leak caused by leeve movement
52 | 84-90000-1 |  |  | 12 | Transmission |  | Regulator |  |  | Other | Buried HPR. SCT | 1984-08-21 | 1985-04-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Permanent repairs, install 12" pipe wt .330 on GM 1933183
52 | 85-90002-1 |  |  | 12 | Transmission |  | Other |  | Service tee | Digin |  | 1985-04-11 | 1985-04-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Temp. Repairs, weld on 2" sav-A-Valve. Permanent Repairs, install 1.5' of 12" pipe wt. 330 on GM 1933183
52 | 85-57001-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1985-04-30 | 1985-05-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Install 12" of 8" pipe wt .219 API 5L-GR-X42 ERW. -out of emergency stock. Internal leak
52 | 85-90001-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion | INTERNAL | 1985-04-17 | 1985-05-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Replaced 30" of 6" pipe, wt.280 API-5L-GR-B-SMLS. Internal corrosion leak. at 11 o'clock looking north
52 | 85-57002-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion | INTERNAL | 1985-05-17 | 1985-06-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Replaced 19" of 8" pipe, wt .219 API-5K-X42 ERW. Internal leak at 5 o'clock
52 | 85-57003-1 |  |  | 12 | Transmission |  | Girth Weld |  |  | Other | Leeve movement | 1985-07-29 | 1985-10-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron
52 | 85-57003-1 |  |  | 12 | Transmission |  | Girth Weld |  |  | Other | Leeve movements | 1985-07-29 | 1985-10-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron
52 | 85-57005-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Other | Rusted out under wrap; | 1985-11-18 | 1985-11-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Replace 42 ft. of 4" pipe w.t. .337, API, 5L GR-B-SMLS
52 | 85-57006-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion | EXTERNAL | 1985-12-30 | 1986-01-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Install 27" of 6" .188wt. API-5LX-GR X42 ERW
52 | 85-90003-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion | INTERNAL | 1985-11-29 | 1986-01-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Replace 2023' of 10", API-5LX GR X42 ERW .281 W.T.
| 94-003-1 | 144 |  | 10 | Gathering |  | Other |  | Line still in ground | Other | Line still in ground; | 1994-05-12 | 1994-05-23 | Replace Pipe |  | Steel/Wrought Iron |  | County Solano | Instal. 67' of 6" pipe with dog leg instl. for ditch
| 94-002-1 | 200 |  | 10 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-04-19 | 1994-04-19 | Replace Pipe |  | Steel/Wrought Iron |  |  | Install 5' of 10" pipe and A 45 degree elbow
| 94-001-1 | 168 |  | 8 | Gathering |  | Girth Weld |  |  | Corrosion |  | 1994-03-08 | 1994-03-09 | Replace Pipe |  | Steel/Wrought Iron |  | County Sacramento | Installed 16' 6" of 8" pipe and 90 degree elbow
| 93-004-1 | 195 |  | 4 | Gathering |  | Other |  |  | Internal Corrosion |  | 1993-08-11 | 1993-08-19 | Replace Pipe |  | Steel/Wrought Iron |  | County Sacramento | Install 1'6" of 4" pipe and new 90 degree elbow
| 93-004-1 |  |  | 8.625 | [11 empty] | Steel
| 93-003-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Damage by outside Forces |  | 1993-07-28 | 1993-07-29 | Replace Pipe |  | Steel/Wrought Iron |  | Rio Vista | Round Contractor games construction for Amerada Hess Ripped into 4" Gas Line; Installed 17' of 4" pip for permanent repair
| 93-90002-1 | 195 |  | 6.625 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 1993-04-06 | 1993-04-07 | Replace Pipe |  | Steel/Wrought Iron |  | County Sacramento | Installed 4'-6.625 Wt .188 x-42 Pipe
| 93-90001-1 | 143 |  | 6.625 | Gathering |  |  |  |  | Other | C | 1993-01-25 | 1993-02-22 | Replace Pipe |  | Steel/Wrought Iron |  | Solano co | Replaced 21" of 6" .188wt.; 562' West of Belleaire 1-9 6" Line 143; Replaced 21" of 6" .188wt
| 92-90004-1 | 114 |  | 16 | Transmission |  | Body of Pipe |  |  | Digin |  | 1992-12-29 | 1992-12-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Sacto. Co. | Approx 1 mile north of state hwy 160 & Approx 2 miles north of the Antioch Bridge; Cut out 38" section of damaged pipe & Replaced with pipe from emergency stock. ...Dug Bell hole. Contractor filled Bell Hole line 114
| 92-90003-1 |  |  | 6.625 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-12-14 | 1992-12-16 | Replace Pipe |  | Steel/Wrought Iron |  | Solano Co. | 141 e/o Belleaire 5-9 6" Line 143; Replaced 38" of 6" wt.188 pipe
| 92-90002-1 | 143 |  | 6.62 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-03-11 | 1992-03-18 | Replace Pipe |  | Steel/Wrought Iron |  | Solano Co. | 378' East of Belleaire 5-9 6" line 143; Replaced 98 5/16" of 6" .188 Pipe
4.5
|  |  |  | 4.5 | [11 empty] | Steel
| 91-90000-1 | 195 |  |  | Gathering |  | Other |  |  | Other |  | 1991-03-26 | 1991-03-27 | Other |  | Steel/Wrought Iron |  | sacto co | Midland Fee #7 6" Line; Cut & Capped 6" line 195 and abandoned in place
| 90-57004-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1990-10-30 | 1990-10-30 | Replace Pipe |  | Steel/Wrought Iron |  | sacto co. | 750' SOuth of Tyler... #9 tie point; Replaced 8' of 4" .188 wall API 5lx GR x42 ERW
| 90-57003-1 | 182 |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1990-12-30 | 1990-12-31 | Replace Pipe |  | Steel/Wrought Iron |  | solano co. | West of v-34 on line 182, grizzly island; Replace 456" of 6" .280 on line 182
| 90-57002-1 | 143 |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1990-10-25 |  | Other |  | Steel/Wrought Iron |  | Dixon Area | 6' L-143 Between v-8 and H&C Union 1-1 well; Line isolated and to be abandoned with well
| 90-90000-1 |  |  | 6.625 | Gathering |  | Other |  |  | Corrosion |  | 1990-10-23 | 1990-10-24 | Replace Pipe |  | Steel/Wrought Iron |  | Solano Co | 786' West of Belleaire 1-9... 143 T.; Replace 25" of 6" .156 wall Pipe
| 90-57001-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Damage by outside Forces |  | 1990-10-18 | 1990-10-18 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | sacto co. | Repaired w/ split sleeve
| 90-57000-1 | 143 |  | 8.62 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1990-07-07 | 1990-07-09 | Replace Pipe |  | Steel/Wrought Iron |  | Unincorperated | Installed 23" x 42 .219 wt
| 89-57000-1 | 143 |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1989-04-19 | 1989-04-19 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Dixon | 6" Line -143 BTW Bellaire 1-9 + 2-9 Millar Field; I piece of pretested pipe
|  |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1989-08-06 |  | Replace Pipe |  | Steel/Wrought Iron |  | Isleton | Cut in 15'4" section of new 6" 156" retest; Note: this section of line 168 has had leaks in various locations
|  |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1989-08-01 | 1989-08-01 | Replace Pipe |  | Steel/Wrought Iron |  | Iselton | 54 n/e off A....#1 well pad'; 26" Can Hydro test x-key wrap & Backfill
|  | 220 |  | 10.75 | [11 empty] | Steel |  |  | Test failure due to external damage to pipe by unknown equipment. Install 10' 1'' - 10'' Gr 8.250
52 | 88-57004-1 |  |  | 8.625 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1988-05-05 | 1988-05-31 | Replace Pipe |  | Steel/Wrought Iron |  | Sacto. co | 107' South of 6" Riser at wtr. #2
52 | 88-90001-1 | 200 |  | 10.75 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1988-07-06 | 1988-07-15 | Replace Pipe |  | Steel/Wrought Iron |  | Solano Co. | 800' N. of M. Mccormick #5; Will replace approx. 300' of 10" line 200
52 | 88-57006-1 | 195 |  | 4 | Gathering |  | Body of Pipe |  |  | Damage by outside Forces |  | 1988-07-18 | 1988-07-19 |  |  | Steel/Wrought Iron |  | Rio Vista | 50' n/e Schnell #4 well; Replaced 10' of 4" line
52 | 88-57000-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1988-01-05 | 1988-01-07 | Other |  | Steel/Wrought Iron
| 88-90000-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion | ; | 1988-03-03 | 1988-03-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Dixon | Replaced 36" Segment with pretested 6.625 OD .156 Wall pipe
| 88-57001-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1988-04-11 | 1988-04-13 | Replace Pipe |  | Steel/Wrought Iron |  | Uninc. | RTW Schnell 1+6 Gas Wells; Cut out 54" section of bad pipe. Inst. 54" of pretested 6" pipe
| 88-57002-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1988-04-11 | 1988-04-13 | Replace Pipe |  | Steel/Wrought Iron |  | Uninc | RTW. Schnell 1+6 Gas Wells; Cut out 56" section of bad pipe. inst. 56" of pretested 6" pipe.
| 90-002-1 | 200 |  | 6.58 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1988-08-15 | 1988-08-19 | Replace Pipe |  | Steel/Wrought Iron |  | Solano Co. | 8,000" North of Cache SLU; Replaced approx. 36" of 6" line 200.
| 88-57003-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1988-04-25 | 1988-04-26 | Replace Pipe |  | Steel/Wrought Iron |  | Dixon | 1mm. e/o Robben Rd. on Well Rd/ Next A.T.T. #2 G.W.; Trenched V-11to operate Exposed local area made repairs.
52 | 88-57005-1 | 195 |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1988-07-25 | 1988-07-26 | Replace Pipe |  | Steel/Wrought Iron |  | Rio Vista | 150' N/ Mid. Fee-15; Replace 26" 8" line 195
52 | 86-57003-1 |  |  | 0.75 | Gathering |  | Fitting |  |  | Other | Piping damage by object floating in water while island was flooded | 1986-05-11 | 1986-07-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Replace 3/4" x 4" x-hwy nipple on Anderson Greenwood Relied Valve at Tyler Is. Farms #9 Gas Well.
52 | 86-57006-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion | INTERNAL | 1986-09-30 | 1986-10-01 | Other |  | Steel/Wrought Iron |  | Rio Vista | Replaced 2' of .154 4 pipe with 2' of .188 wt. API 5lx x 42 ERW on main acctivity 10-1-86
52 | 87-57000-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1987-01-14 | 1987-01-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron
52 | 87-57001-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1987-02-04 | 1987-02-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron
| 87-57002-1 |  |  | 4 | [7 empty] | 1987-02-04 | 1987-02-05 |  |  | Steel |  | Dixon | ACCT 3661-2040 Leak Repaired with 18" pipe of 4" Pretested pipe spects-5L-GR x 42
52 | 87-57002-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1987-02-04 | 1987-02-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron
52 | 87-57004-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1987-07-03 | 1987-07-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron
| 87-90001-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1987-02-09 | 1987-02-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron
52 | 87-90002-1 |  |  | 2 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1987-03-19 |  | Other |  | Steel/Wrought Iron
52 | 87-90005-1 |  |  | 4 | Transmission |  | Fitting |  |  | Other |  | 1987-08-12 | 1988-03-02 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Rio Vista Uninc | Tightened 3/4 Screwed elbow maint. Act. 6088/1020 3-2-88
52 | 87-90007-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1987-08-12 | 1988-03-02 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Rio Vista Uninc | Replaced section of 1/2" sensing line ou. maint. acct. 6088/1020
52 | 87-90006-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Other |  | 1987-08-12 | 1988-03-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Rio Vista Uninc | Tightened fitting on gage line
52 | 87-90005-1 |  |  | 4 | Transmission |  | Fitting |  |  | Other |  | 1987-08-12 | 1988-03-02 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Rio Vista Uninc | Tightened 3/4 Screwed elbow maint. act. 6088/1020 3-2-88
52 | 87-90007-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1987-08-12 | 1988-03-02 | Tighten Cap or Bolt |  | Steel/Wrought Iron
| 00-20001-1 | 200 |  |  | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2000-06-23 | 2000-07-06 | Other |  |  |  | Hasting island | Installed leak clamp
| 00-14301-1 | 143 |  | 6.25 |  |  | Body of Pipe |  |  | Internal Corrosion |  | 2000-07-13 | 2000-07-14 | ABANDON |  |  |  | Dixon
| 00-14501-1 | 145 |  |  | Gathering |  | Other |  | Carol test insulated union | Unknown |  | 2000-07-20 | 2000-07-22 | Welded Sleeve/Can - Weld |  |  |  | Dixon
| 00-14302-1 |  |  | 6.62 | Gathering |  | Body of Pipe |  |  | Other | Sent for analysis | 2000-08-20 | 2000-08-16 | Other | PIPE REPLACEMENT |  |  | Dixon/Solano Co. | 353' West of Wineman #5 TAP.; Install 48" of new 156 wall x 42 ERW 6" Pipe pretested emergency stock;
| 00-14303-1 |  |  | 6.62 | Gathering |  | Body of Pipe |  |  | Unknown |  | 2000-08-20 | 2000-09-24 | Other | New Dogleg |  |  | Dixon/Solano County | Sikes rd. & Delhi Rd.; Fabricate and install new dogleg over culvert; Installed 8' of 6" pipe
|  |  |  | 4 | Gathering | [6 empty] | 2000-10-13 | 2000-10-18 | Welded Sleeve/Can - Weld |  |  |  | Dixon/Solano County | 300' West of Zanehi #4 M.M.; Replaced 48" of 4" line; Site Pos. N. 38 Degrees 20.043'/ W. 121 Degrees 43.701'
| 00-20002-1 | 200 |  | 0.5 | Gathering |  | Drip |  |  | Damage by 3rd Party |  | 2000-11-06 | 2000-11-07 | Other | Inst. Valve |  |  | Rio Vista | 16" Line 200 1/2" Drip Line; Install new valve; Valve replaved with new 1/2" Valve
| 00-19501-1 | 195 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2000-10-06 | 2000-11-16 | Mechanical Repair Fitting - Fitting |  |  |  | Rio Vista | Line 195 Brannan is State Park; Installed leak clamp. Internal corrosion perforated pipe;
| 99-00001-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Damage by 3rd Party |  | 1999-04-16 |  | ABANDON |  | Steel/Wrought Iron |  | Isleton | Line 195 Brannan Island; Line was isolated and will be retired/abandoned
| 99-00002-1 | 114 | 7.29 | 16 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1999-07-15 | 1999-08-25 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | Sherman Island | L-114 m.p.7.29; New crosss tie valve installed from L-114 To stanpac 4 line, approx 800' of Line 114 retired
| 99-00003-1 | 131 |  |  | Transmission |  |  |  |  | Other | Weld defect | 1999-11-02 | 1999-12-01 |  |  |  |  | Sherman Isl. | Line 131; Installed new 4" blow down stack; Replace 3" blow dow
| 99-00004-1 | 143 |  | 6 | Gathering |  |  |  |  | Damage by 3rd Party | Digin | 1999-12-01 | [5 empty] | Dixon | Line 143 Sikes Rd. Line was Isolated for reparirs
| 98-006-1 | 200 |  | 8 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 1998-12-10 |  | Replace Pipe |  | Steel/Wrought Iron |  | Rio Vista | L-200 8" line east of liberty island RO 4/10 MI ... Well Rd.
| 98-004-1 | 200 |  | 6.25 | Gathering |  | Other |  | Dig-in | Damage by outside Forces |  | 1998-08-08 | 1998-08-11 | Replace Pipe |  | Steel/Wrought Iron |  | Rio Vista | Line 200 East of Liberty Island Road; Replace section of pipe
|  |  |  | 4 | [11 empty] | Steel/Wrought Iron
| 97-0005-1 | 108 | [9 empty] | 1997-10-15 | [5 empty] | South of Lodi
| 97-0003-1 |  |  | 4 | [5 empty] | Damage by outside Forces |  | 1997-07-16 | 1997-07-18 | Replace Pipe |  | Steel |  | Sacramento | Replace 58" of damaged main w/new pipe .237 wall GRD & SMLS pretested pipe back ground to specs
| 97-0002-1 | 200 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-01-25 |  | Replace Pipe |  | Steel/Wrought Iron |  | Rio Vista | L-200 8" LINS East of Liberty Island Rd. 4/10 MI on Well Rd.
| 97-0002-1 | 200 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-01-25 |  | Replace Pipe |  | Steel/Wrought Iron |  | Rio Vista; | L-200 8" LINS East of Liberty Island Rd. 4/10 MI on Well Rd.
| 97-0001-1 | 143 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-01-09 | 1997-01-10 | Clamp |  | Steel/Wrought Iron |  | Rio Vista | L-143 6" off of Levee Rd. Aprox. 30 Ft. at Toe of Levee 6/10MI North of Delhi Rd. In Yolo Bypass; Excavated and installed 6" plidco leak clamp
| 97-0001-1 | 143 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-01-09 | 1997-01-10 | Clamp |  | Steel/Wrought Iron |  | Rio Vista | L-143 6" off of Levee Rd. Aprox. 30 Ft. at toe of Levee 6/10 MI North of Delhi Rd. in Yolo Bypass; Excavated and installed 6" Plidco Leak Clamp
| 96-00081-1 | 195 |  | 8.62 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-11-08 |  | Other |  | Steel/Wrought Iron |  | Rio Vista | 8" Line 195 near gas well welch fee-3 3/10 MI East on Hwy 12 and 2/10MI So. In Field Aprox. 45' From v-227; Cut and cap line to remove leak area, abandon 1800' 8" L-195
| 96-0007-1 | 195 |  | 8.62 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 1996-08-12 |  | Replace Pipe |  | Steel/Wrought Iron |  | Rio Vista | L-195 8" Near Tiecherian -5 Gas Well Aprox. 6/10MI East of Hwy 12; Replace 31' 3/8" 8.625 .322 WT Pipe
| 96-00061-1 | 195 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-06-11 | 1996-06-16 | Replace Pipe |  | Steel/Wrought Iron |  | Rio Vista | L- 195 Near Gas Well WF-9 at curve 6" Gathering; Welded in can 46" Long
| 96-00051-1 | 143 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-06-05 | 1996-08-18 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Rio Vista | 1.2 MMI North on Sikes Rd. off of Swan Rd. the west on Well Rd. to Belair well 1-9 the 580' to leak location; replaced total length of run from 5-9 to 1-9 with 2" SCH #80 pope 18059
| 96-00041-1 | 143 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-03-29 |  | Replace Pipe |  | Steel/Wrought Iron |  | Dixon | Sikes & ...Rd. Dixon in drive way to mobil home on corner; weld in 41 Ft. of 6"
| 96-00031-1 | 210 |  | 0.75 | Transmission |  | Tap Connection |  |  | Other | No Description | 1996-03-01 | 1996-03-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Rio Vista | Rio Vista Wye L-210 16"; Tighten plug on service tap and replaced 3/4 line found with external corrosion aprox. 9" 3/4 pipe
| 96-00011-1 | 143 |  | 6.62 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  |  |  | Replace Pipe |  | Steel/Wrought Iron |  | Rio Vista Dixon | Sikes Rd. & Delhi Rd. Dixon near bellair G.W. 5-9
| 96-00021-1 | 200 |  | 16 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1996-01-31 | 1996-02-14 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Rio VIsta | Hwy 12 Near Rio Vista; See drawing on back page. See attached TES Report
| 95-00091-1 | 141 |  | 6 | Gathering |  | Tap Connection | Riser |  | Digin |  | 1995-11-30 |  | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Walnut Grove | Race Track Rd. & Tyler Island Rd. L 141 6"; Excavated and found 3/4" drip leg cut off by CAT. removed old 3/4" line and installed plug wraped and back filled
| 95-00081-1 | 200 |  | 4 | Gathering |  | Body of Pipe |  |  | Digin |  | 1995-10-05 | 1995-10-10 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Rio VIsta | L-200 4" 800' East of Hwy 12 and 400' North of Church Rd. near gas well marks -4 on Marks Ranch; Cut out damaged area and weld in 52" can.
| 95-0005-1 | 143 |  | 6 | Gathering |  | Valves |  |  | Material Failure |  | 1995-05-09 |  | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Dixon | V-21 L-143 on corner of G-Dixion and Rubbin Rds.; ADJ packing on Valve and stoped 90% of leakage
| 95-00071-1 | 200 |  | 8 | Gathering |  | Body of Pipe |  |  | Digin |  | 1995-06-14 |  | Other | Cut & Cap/ Isolate | Steel/Wrought Iron |  | Dixon | Aprox. 3MI East on Liberty Islandd Rd. in middle of flooded Island (See map); Line 200 cut & Capped 3' East of V-244 & 3' East V-8 on L143 to isolate liberty island system
|  |  |  | 42 | [11 empty] | Steel |  |  | To Abandon Line 145 & 200 across liberty island to valve 244
| 95-0006-1 | 143 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-05-18 | 1995-06-27 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Dixon | Sikes Rd. & Delhi Rd Dixon near bellair G.W. 5-9 Aprox 850' West between 1-9 & 5-9; Welded in 80' of new pipe to remove bad area with multiple repairs (Leak history)
| 95-0004-1 | 143 |  | 6.62 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-05-05 | 1995-05-16 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Rio Vista/Dixon | L-143 6"; Weld in 6'6" Can
| 95-0003-1 | 143 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-04-06 |  | Other |  | Steel/Wrought Iron |  | Dixon | 6" L-143; 4" L-143; Cut & Cap
| 95-0002-1 | 146 |  | 8 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 1995-03-13 |  | Other | Incert | Steel/Wrought Iron |  | Dixon | L-146 8"; Incerted 4" into old 8" as casin
| 95-0001-1 | 143 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-01-26 | 1995-03-28 | Replace Pipe |  | Steel/Wrought Iron |  | Dixon | Dixon Ave 1 MI e/o Robbens Rd. Dixon
| 95-0001-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  |  | 1995-03-28 | Replace Pipe |  | Steel/Wrought Iron |  | Dixon | Dixon Ave, 1 MI east of Robbens Rd. Dixon; Replace 24" of 6" STL Main Pretested on GM 1000728@ 1300PSI .280WT, 12/8/94
| 06-19501-1 | 195 |  | 6 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2006-02-16 | 2006-03-08 | Other | Plieco leak clamp | Steel/Wrought Iron |  | Rio Vista | L-195, Brannan Island; Installed 6" Plieco Leak Clamp
| 06-19502-1 | 195 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2006-04-08 | 2006-04-25 | Other | Plieco Leak Clamp | Steel/Wrought Iron |  | Isleton | Bottom of Pipe; Repaired leak using a 8" Plieco leak clamp
| 06-19503-1 |  |  | 10 |  |  | Body of Pipe |  |  | Internal Corrosion |  | 2006-04-17 | 2006-04-24 | Welded Sleeve/Can - Weld |  | Steel |  | Isleton | .4 MI s/o 2650 Twitchell Isl. Rd.
| 06-19504-1 | 195 |  | 6 |  |  | Body of Pipe |  |  | Internal Corrosion |  | 2006-04-26 | 2006-05-01 | Other | Plieco Leak Clamp | Steel |  | Rio Vista | Bottom of pipe; repaired leak using a 6" Plieco Clamp
| 06-19505-1 | 195 | [9 empty] | 2006-08-31 |  |  | Line sold to Rosetta up to V-119 |  |  | ISLETON
| 06-19506-1 |  |  | 6 | [7 empty] | 2006-10-11 |  |  | Line Retired 10/11/06 |  |  | ISLETON | LINE RETIRED 10-11-06
| 06-16801-1 |  |  | 6 |  |  | Body of Pipe |  |  | Internal Corrosion |  | 2006-01-09 | 2006-02-23 |  |  | Steel/Wrought Iron |  | Isleton | 900' West from Levey Rd. Installed Leak Clamp
| 06-20001-1 | 450 |  | 12 |  |  | Drip |  |  | Internal Corrosion |  | 2006-02-06 | 2006-02-10 | Other | Remove drip | Steel |  | Rio Vista | Montezuma Hills Rio Vista; repairs were made by removing drip sym @ leak location. Cover @ flange is 30'' +/-
| 06-20002-1 | 200 |  | 12 | Transmission |  | Mechanical Joint | Valves |  | Unknown |  | 2006-08-08 |  |  |  | Steel/Wrought Iron |  |  | 3/09- Valve to be retired & Removed 4/09?
| 06-33100-1 | [10 empty] | 2006-09-06 | [5 empty] | Vacaville
| 06-33100-1 | [10 empty] | 2006-09-06 | [5 empty] | Vacaville
| 06-33100-1 | [10 empty] | 2006-09-06 | [5 empty] | Vacaville
| 06-33100- | [10 empty] | 2006-09-06 | [5 empty] | Vacaville
| 06-33100- | [10 empty] | 2006-09-06 | [5 empty] | Vacaville
| 06-33100- | [10 empty] | 2006-09-06 | [5 empty] | Vacaville
| 07-19501-1 | 195 |  | 10 | [5 empty] | Internal Corrosion |  | 2007-10-18 | 2007-10-19 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | Isleton | Across from Kuhn 1 Well; Installed - Welded sleeve
| 07-19502-1 | 195 |  | 12 | Gathering |  |  |  |  | Internal Corrosion |  | 2007-10-25 | 2007-10-25 | SS Clamp w/Anode - Clamp |  | Steel |  | Isleton | Installed SS Clamp; Installed SS clamp and Wrapped
| 07-19503-1 | 195 | 79A | 10 | Gathering |  |  |  |  | Internal Corrosion |  | 2007-11-05 | 2007-11-29 | Welded Sleeve/Can - Weld |  | Steel |  | Isleton | Across from Kuhn 1 well site; Installed 20' Can Left deactivation for 3rd party sale; Left ... for 3rd party sale
| 07-19504-1 | 195 |  | 12 | Gathering |  |  |  |  | Internal Corrosion |  | 2007-11-05 |  |  |  | Steel/Wrought Iron |  | Isleton | 1/2MI s/o V-116 Twitchell Island; Datiuated pipleine for 3rd party sale; Deativated pipleine for 3rd party sale
| 07-19505-1 | 195 |  |  | Gathering |  | Fitting |  |  | Material Failure |  | 2007-11-29 | 2007-11-29 | Other | Removed broken fitting | Steel/Wrought Iron |  | Isleton | V-191; Removed broken grease fitting
| 07-19601-1 | 196 |  | 6 | [7 empty] | 2007-08-23 |  | Deactivate #TP Main |  | Steel/Wrought Iron |  | Thornton | N/A Retired in-Place; Pipeline Retired in place after cut off at woodbridge Rd.
| 07-20001-1 | 200 |  | 8 | [5 empty] | Internal Corrosion |  | 2007-01-24 |  |  |  | Steel |  | Rio Vista | N/A-Retired in Place Job#6102223 3-28-2007; Retired in place on Job #6102223
| 07-20002-1 | 200 |  | 10 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2007-05-07 |  |  |  | Steel/Wrought Iron |  | Rio Vista | Cut in corn.
| 08-19601-1 | 196 |  | 0.75 | Service | TRANSMISSION | Fitting |  |  | Damage by Natural Forces |  | 2008-01-19 |  |  |  | Steel/Wrought Iron |  | Isleton
| 08-16801-1 | 168 |  |  | Single Service |  | Fitting |  |  | Other |  | 2008-10-21 | 2009-05-22 | Other | Tightened Misc. Pipe Fitting | Steel/Wrought Iron |  | isleton | Tightened misc. pipe fitting on domestic odorizer/ Hi-Hi set. The in question piping will be removed.
| 08-19501-1 | 195-0151 |  | 8 | [7 empty] | 2008-08-11 | [5 empty] | Rio Vista
|  |  |  | 8.625 | [8 empty] | 2008-08-18 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  |  | Installed SS Clamp per Brian McCay and Niel Jenast
| 08-19502-1 | [5 empty] | Valves |  |  | Unknown |  | 2008-08-28 | 2008-11-26 |  |  | Steel/Wrought Iron |  |  | No Leak Found Oper. Valve; no Leak Found
| 08-19502-1 | 196 |  | 8 | Transmission |  | Valves |  |  |  |  | 2008-08-18 | [5 empty] | Rio Vista
| 08-19503-1 | 195-0151 |  | 8 | Gathering |  | Unknown |  | AT THIS TIME | Internal Corrosion |  | 2008-11-03 |  |  |  | Steel/Wrought Iron |  | Rio Vista | Get info from Jim Stack
| 08-19503-1 | 195-0151 |  | 8 | Gathering |  | Unknown |  | AT THIS TIME | Internal Corrosion |  | 2008-11-03 |  |  |  | Steel/Wrought Iron |  | Rio vista
| 08-19601-1 | 196 |  |  | Transmission |  | Valves |  |  | Unknown |  | 2008-08-28 | 2008-11-26 | Other | No Leak Found | Steel/Wrought Iron |  | Iselton | No leak Found
| 08-20001-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-01-26 | 2008-02-05 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | Rio Vista | Back ground .280 can 3' Long
| 08-20002-1 |  |  | 8 | Gathering |  |  |  |  | Internal Corrosion |  | 2008-04-21 |  |  |  | Steel/Wrought Iron |  | Rio Vista | Dug up leak location and identified problem. Cut out 3' of 8" steel pipe and installed new 8"pipe. (3 of .188 wall tested grade B seamless). Leak location was 405' south of V-288. GPS coord by Jerry Penick CGT supervisor N. 38degrees 14.924 Minutes W 131 Degrees 45.157 Minutes ( Leak was caused by Internal Corrosion)
| 08-20003-1 | 200 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-04-21 |  |  |  | Steel/Wrought Iron |  | Rio Vista | No Welding needed at leak location. Installed (2ea) 8" high presure Plidco repair leak clamp. Ser# SN2771023B & WP1000F 6 Ft. apart first clamp 123' south of Valve #228 2nd repair clamp 129' south of valve# 228
| 08-20004-1 | 200 |  | 8 | Gathering |  |  |  |  | Internal Corrosion |  | 2008-04-30 |  |  |  | Steel/Wrought Iron |  | Rio Vista | No Welding needed at leak location Installed (2ea) 8" high pressure Plido repaire leak clamp ser#SN2771023B & WP1000F. 6 feet apart first clamp 123' south of Valve #228, 2nd clamp 129' south of Vavle # 228
| 08-20005-1 | 200 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-07-01 | 2008-07-02 | Welded Sav-A-Valve - Weld |  | Steel/Wrought Iron |  | Rio Vista | Welded a 2" Save-a-valve over leak on back side of 8" tee
| 08-20006-1 | 200 |  | 10 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-08-21 | 2008-08-22 | Other | Plidco Clamp | Steel/Wrought Iron |  | Rio VIsta
| 08-20007-1 | 200 |  |  | Gathering |  | Fitting | Mechanical Joint |  |  |  | 2008-08-27 |  |  |  | Steel/Wrought Iron |  | Rio Vista
| 08-20007-1 | 200 |  |  | Gathering |  | Fitting | Mechanical Joint |  |  |  | 2008-08-27 |  |  |  | Steel/Wrought Iron |  | Rio Vista
| 08-20008-1 | 200 | Station | 24 | Transmission |  | Fitting | Physical/Mechanical Joint |  |  |  | 2008-08-27 | 06/00/2009 | Deactivate #TP Main |  |  |  | Rio VIsta | No Repair- Line was isolated, blown down and removed
|  | 200 | [16 empty] | Serpa Compressor Sta.. Notified Supervisor of leak location in Oriface vault; CL RV 39-28 Bypassed section of line. Valved off and taken out-of-service 10/23/2008; Line removed 06/09 on 30665197 CL RV 09-09
| 08-20008-1 | 200 | Station | 24 | Transmission |  | Fitting | Physical/Mechanical Joint |  |  |  | 2008-08-27 | 06/00/2009 | Other | Removed; |  |  | Rio Vista | No Repair-Line was isolated blown down and removed.; Serpa Compressor Sta. Notified Supervisor of leak location in oriface vault. CL RV 39-28 Bypassed section of line valved off and taken out-of- service 10/23/08. Line removed 06/09 on 30665197 CL. RV 9-09
| 08-40002-1 | 210 |  |  | Transmission |  | Other |  | Oriface fitting in Vault |  |  | 2008-08-29 | 2009-01-07 | Other | Tightened fitting | Steel/Wrought Iron |  | Dixon | Tightened misc. Fittings on meter
| 08-40003-1 | 400 | 269.48 | 36 | Transmission |  | Mechanical Joint | Valves |  |  |  | 2008-02-25 |  |  |  | Steel/Wrought Iron |  | Dixon
| 08-40004-1 |  |  |  | Transmission |  | Fitting |  |  | Unknown |  | 2008-08-29 | 2008-12-22 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | Winters | Repl. Tubing and fittings on pilots
| 08-40005-1 |  |  |  | Transmission |  | Fitting | Unknown |  | Unknown |  | 2008-08-29 | 2008-12-22 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | Winters | Replaced tubing and fittings on pilots
| 08-40101-1 | 401 |  |  |  |  | Valves |  |  |  |  | 2008-08-27 | [5 empty] | Isleton
| 08-40101-1 | 401 |  | 42 | Transmission |  | Fitting | Valves |  |  |  | 2008-08-27 | [5 empty] | Rio Vista | Notified supervisor, asked that vent piping be added to tap on valve to move hazard away from eye level
| 08-40301-1 | 403 |  | 4 | Transmission |  | Valves |  |  | Other |  | 2008-08-29 | 2008-09-22 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Dixon | Cleaned and tightened fittings. Greased and operated valve
|  |  |  | 0.08 |  |  | Body of Pipe |  |  | Internal Corrosion |  |  |  | SS Clamp w/Anode - Clamp | STAINLESS STEEL | Steel/Wrought Iron |  | Rio Vista | Tape Wrap and waxed wrap ss fitting. fitting was stainless steel fittings to 120psi; Pipeline sold to Rosetta Resources as part of Rio VIsta 30 psig gas gathering active pipeline sale on order #30604361 effective 01/01/2009
| 09-20005-1 | 200 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2009-10-10 | 2010-10-09 | Other | 8" PIidco Clamp Ser# 3062926 | Steel/Wrought Iron |  | Rio Vista
| 09-20005-1 | 200 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2009-10-10 |  |  |  | Steel/Wrought Iron |  | Rio VIsta | Tested @ line pressure
96 | 09-20005-1 | 200C1-3 |  | 8 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2009-10-10 | 2010-10-09 | Other |  |  |  | Rio Vista | Tested @ line pressure
96 | 09-20005-1 | 200C1-3 |  | 8 | [7 empty] | 2009-10-10 | [5 empty] | Rio VIsta
| 09-20006-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2009-10-10 | 2010-10-09 | Other | 8" Plidco clamp ser. 3092339 | Steel/Wrought Iron |  | Rio Vista | Leak was located and repaired. Crew installed a 8" plidco clamp repair was wraped and back filled. Soap tested @ line pressure
96 | 09-20006-1 | 200C2 | 0.45 | 8 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2009-10-10 | 2010-10-09 | Other |  | Steel |  | Rio Vista | INSTALLED A 8" PLIDCO CLANUP, WRAPED AND
| 09-20007-1 |  |  |  | Gathering |  | Fitting |  |  | Other | Loose fitting, tighten | 2009-10-12 | 2010-10-06 | Other | Greased | Steel/Wrought Iron |  | Rio VIsta | Tighten, Cleaned, greased fitting- checked for leak, check good. This is V-B a blown down valve 10-6-10 F. N.
96 | 09-20007-1 | BD |  | 4 | Gathering |  | Fitting |  |  | Other | No Description | 2009-10-12 | 2010-10-06 | Other |  |  |  | Rio Vista | Tightened, checked, greased fitting V-B
| 09-20008-1 | 200 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2009-10-12 | 2010-10-20 | Other | COMMENTS See pg 3 of 3 Line retired cut line to church 5 NEAR CHURCH | Steel/Wrought Iron |  | Rio Vista | 6" Dide will be tested at line pressure when piping is reinstalled @ Chruch 1
96 | 09-20008-1 | 200C4-5 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2009-10-12 | 2010-10-12 | Other |  | Steel |  | Rio Vista | Gas Lk repted, lk repr chged to N/O L-20
| 09-20009-1 | 200 |  |  | Gathering |  | Valves |  |  | Unknown |  | 2009-10-12 |  | Other | cut off | Steel/Wrought Iron |  | Rio Vista; | Well cut-off at church 1, retired pipe from church 1 to church 5 see leak 09-20008-1 for sketch of cut-off 10-13-10
96 | 09-20009-1 | 200C-6 |  | 6 | Gathering |  |  |  |  | Other |  | 2009-10-12 | 2010-10-13 | Deactivate #TP Main |  |  |  | Rio Vista | well cut off @ ch 1, retired pp fr ch 1
| 09-20004-1 |  |  | 3 | Gathering |  | Fitting |  |  | Equipment Malfunction |  | 2009-10-09 |  |  |  | Steel/Wrought Iron |  | Rio Vista
| 09-20004-1 |  |  | 3 | Gathering |  | Fitting |  |  |  |  | 2009-10-09 | 2009-10-10 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | Rio VIsta
| 09-20005-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2009-10-10 | 2010-10-09 | Other | 8" PLIDCO CLAMP | Steel/Wrought Iron |  | Rio Vista
| 09-20006-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2009-10-10 | 2010-10-09 | Other | 8" Plidco clamp ser. 3092339 | Steel/Wrought Iron |  | Rio Vista; | Leak was located and repaired. Crew installed a 8" Plidco Clamp. Repair was wraped and back filled. Soap tested and line pressure
| 09-20007-1 |  |  | 6 | Gathering |  | Fitting |  |  | Other | No Description | 2009-10-12 | 2010-10-06 | Other | Greased | Steel/Wrought Iron |  | Rio Vista | Tighten, cleaned, greased fitting. Checked for leak, check good. This is V-B a blown down valve 10-6-10 F.N.
| 09-20008-1 |  |  | 6 | [7 empty] | 2009-10-12 | 2010-10-12 | Other | See CommentS LAST PAGE of report page 3 of 3 |  |  | Rio Vista | Gas leak reported, leak repair changed to % (?) L-200 @ Church 1. Bell hole back fill per Joe C. Request
| 09-20009-1 |  |  | 26 | Gathering |  | Valves |  |  | Other | No Description | 2009-10-12 | 2010-10-13 |  |  | Steel/Wrought Iron |  | Rio Vista | Well Cut-Off at Church 1, retired pipe from church 1 to church 5, see leak 09-20008-1 for sketch of cut-off
| 09-13101-1 | [10 empty] | 2009-10-30 | [5 empty] | Rio VIsta
| 09-13101-1 | 131 | 9.08 | 12 | Transmission >= 20% SMYS |  | Unknown |  |  | Unknown |  | 2009-01-27 | 2009-02-19 | Mechanical Repair Fitting - Fitting |  |  |  | Oakley
| 09-18201-1 | 182 | 4.81 | 8 | Transmission |  | Other |  | Domestic Odorizer | Unknown |  | 2009-04-30 |  |  |  | Steel/Wrought Iron |  | Rio Vista
| 09-19601-1 | 196 |  | 1.56 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2009-03-17 | 2009-05-14 | Other | Retire line 196 | Steel/Wrought Iron |  | Lodi | Refer to stockton Div. Leak No. 09-02038-1, 3/17/2009
| 09-19601-1 | 196 |  | 1.56 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2009-03-17 | 2009-05-14 | Other | Retire Line 196 | Steel/Wrought Iron |  | Lodi | Refer to stockton div. leak no. 09-02-038-1, 3/17/2009
| 09-19601-1 | 196 |  | 1.56 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2009-03-17 | [5 empty] | Lodi | Refer to stockton Div. Leak no. 09-02038-1, 3/17/2009
| 09-19602-1 | [10 empty] | 2009-11-04 | [5 empty] | Walnut Grove
| 09-19603-1 | [10 empty] | 2009-11-04 | [5 empty] | Lodi
| 09-19604-1 | [10 empty] | 2009-11-04 | [5 empty] | Lodi
| 09-19605-1 | 196 |  | 1 | Gathering |  | Valves |  |  | Unknown |  | 2009-11-03 |  |  |  | Steel/Wrought Iron |  | Stockton
| 09-19606-1 | 196A |  | 12 | Transmission |  | Fitting |  |  | Unknown |  | 2009-10-30 |  |  |  | Steel/Wrought Iron |  | Isleton
| 09-19607-1 | 196 |  | 12 | Gathering |  | Fitting |  |  | Unknown |  | 2009-10-30 |  |  |  | Steel/Wrought Iron |  | Isleton
| 09-20001-1 | 200 |  | 2 |  |  | Valves |  |  |  |  | 2009-04-24 | [5 empty] | Rio VIsta | 2" Mueller Valve for feeder line to summerset regs.
| 09-20002-1 | 200 | [9 empty] | 2009-08-25 | [5 empty] | Rio VIsta
| 09-22003-1 | 220 |  | 10 |  |  | Unknown |  |  |  |  | 2009-10-05 | [5 empty] | DIXON
| 09-22003-1 | 220 |  | 10 | Transmission |  | Unknown |  |  | Unknown |  | 2009-10-05 |  |  |  | Steel/Wrought Iron |  | Dixon
| 09-20003-1 | 200 |  | 4 | Gathering |  | Valves |  |  | Unknown |  | 2009-10-09 |  |  |  | Steel/Wrought Iron |  | Rio VIsta
| 09-20004-1 |  |  | 3 | Gathering |  | Fitting |  |  | Equipment Malfunction |  | 2009-10-09 | 2009-10-10 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | Rio VIsta | Replaced insulating flauge kit & Gasket
| 09-20010-1 | [10 empty] | 2009-10-17 | [5 empty] | Rio Vista
| 09-40102-1 | [10 empty] | 2009-10-26 | [5 empty] | Vacaville
| 09-22001-1 | [10 empty] | 2009-10-02 | [5 empty] | Dixon
| 09-22002-1 |  |  | 3 |  |  | Valves |  |  |  |  | 2009-10-02 | [5 empty] | Dixon
| 09-20002-1 | 200 | [9 empty] | 2009-08-25 | [5 empty] | Rio Vista
| 09-22003-1 | 220 | [9 empty] | 2009-10-05 | [5 empty] | Dixon
| 09-19601-1 | 196 |  | 1.56 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2009-03-17 | 2009-05-14 | Other | Retire line 196 | Steel/Wrought Iron |  | Lodi | Refer to stockton Div. Leak No. 09-02038-1, 3/17/09
|  | 196 | [10 empty] | 2009-05-14 | Other | Retire line 196 | Steel/Wrought Iron |  |  | Refer to Stockton Div. Leak No. 09-02038-1, 3/17/2009
|  | 196 | [10 empty] | 2009-05-14 | Other | Retire line 196 | Steel/Wrought Iron |  |  | Refer to Stockton Div. Leak no. 09-02038-1, 3/17/09
96 | 11-23001-1 |  |  |  | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Material Failure |  | 2011-01-03 | [5 empty] | Lodi
|  |  |  | 12 | [7 empty] | 2001-03-25 | 2011-03-25 |  |  | Steel |  | Isleton | No Repair Needed inspection only; pitted area 4" x 4" max pitting; Pitting found just below valve #2. wire buff area measur 4'x4' max pitt measured .11''. Nick Jordan ran R-String calculations no repair needed. Turned in work request to repair coting.
|  |  |  | 12 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | External Corrosion |  | 2011-04-22 |  |  |  | Steel |  | Rio Vista | Inspection only; Found pitting measuring .050 all the way around the pipe at both walls. Wall thickness .424"
|  |  |  | 12 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | External Corrosion |  | 2011-04-22 |  |  |  | Steel |  | Rio Vista | Inspection Only; Found pitting measuring .060" 1/3 the way around the bottom of pipe. wall thickness .424"
|  | 182 |  | 10 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | External Corrosion |  | 2011-04-22 |  |  |  | Steel |  | Suisun | Inspection only; Sever pittig LIne 182 Upstream of valve 12.86
|  | 182 | 11.67 | 10.75 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2011-05-02 |  |  |  | Steel |  | Suisun | Inspection Only; Instpection Only
96 | 10-20002-1 | [10 empty] | 2010-08-10 | [5 empty] | Rio Vista
96 | 10-20004-1 | [10 empty] | 2010-08-10 | [5 empty] | Rio Vista
96 | 10-20004-1 | [10 empty] | 2010-08-10 | [6 empty] | Need to remove orrice meter McCoy
| 10-20001-1 | 200 |  |  | Gathering |  | Unknown |  |  | Unknown |  | 2010-06-22 | 2010-10-08 | Other | 8" Plidco Clamp Ser. 3092307 | Steel |  | Rio Vista | Soap Tested @ line Pressure
| 10-20001-1 | 200 |  |  | Gathering |  | Unknown |  |  | Unknown |  | 2010-06-22 | 2010-10-08 | Other | 8" Plidco Clamp ser. 3092307 | Steel |  | Rio Vista | Soap tested @ line pressure
96 | 10-20001-1 | 200C7-3 | 0.34 | 8 | Gathering |  | Unknown |  |  | Unknown |  | 2010-06-22 | 2010-10-08 | Other |  | Other |  | Fairfield | Soap tested @ line pressure
96 | 10-21001-1 | 1 |  | 12 | Transmission >= 20% SMYS |  |  |  |  | Material Failure |  | 2010-08-13 | [5 empty] | Dixon
| 10-21001-1 |  |  | 12 | Transmission |  | Valves |  |  | Material Failure |  | 2010-08-13 | 2010-10-22 | Mechanical Repair Fitting - Fitting | Replace stem seals JGCF | Steel/Wrought Iron |  | Dixon | Replaced stem seals CWF4
| 10-21001-1 |  |  | 12 | Transmission |  | Valves |  |  | Material Failure |  | 2010-08-13 | 2010-10-22 | Mechanical Repair Fitting - Fitting | Replace stem seals | Steel |  | Dixon | Replace stem seals CWF4
| 10-21001-1 |  |  | 12 | Transmission |  | Valves |  |  | Material Failure |  | 2010-08-13 | 2010-10-22 | Mechanical Repair Fitting - Fitting | Replace stem seal | Steel/Wrought Iron |  | Dixon | Replace stem seal
| 10-82008-1 | 196 | 0 |  |  |  | Regulator |  |  | Equipment Malfunction |  | 2010-09-24 | 2010-10-11 | Other | Repaired relay |  |  | Lodi | Replaced rubber goods inside & Modified porting to exhause to vent header of building
96 | 10-82008-1 | 108 | 43.49 | 6 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Equipment Malfunction |  | 2010-09-24 | 2010-10-11 | Other |  | Other |  | Lodi | Rebuilt pilot and ported vents
| 10-82008-1 | 196 | 0 |  |  |  | Regulator |  |  | Equipment Malfunction |  | 2010-09-24 | 2010-10-11 | Other | Repaired relay |  |  | Lodi | Replaced rubber goods inside & modified porting to vent exhaust to vent headed of building. Soap tested at the time of repair. OK. info not included in a form.
96 | 10-82035-1 | 202 | 3.49 | 0.75 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-03 | 2010-10-03 | Other |  | Other |  | Wheatland; | Sent to Dave Campbell 4/13/11; Rebuild Regulator
96 | 10-21001-1 | 1 |  | 0.75 | [7 empty] | 2010-08-13 | [5 empty] | Dixon;
| 10-21001-1 |  |  | 12 | Transmission |  | Valves |  |  | Material Failure |  | 2010-08-13 | 2010-10-22 | Mechanical Repair Fitting - Fitting | Replaced stem seals | Steel/Wrought Iron |  | Dixon | Replace stem seals
96 | 10-82035-1 | 202 | [9 empty] | 2010-10-03 | [5 empty] | Wheatland
96 | 10-82035-1 | 202 | 3.49 | 0.75 | Transmission |  | Other |  |  | Other |  | 2010-10-03 | 2010-10-03 | Other | Rebuild Regulator | Other |  | Wheatland
96 | 10-82035-1 | 202 | 3.49 | 0.75 | Transmission >= 20% SMYS |  | Other |  |  | Other | ; | 2010-10-03 | 2010-10-03 | Other | ; | Other |  | Wheatland
96 | 10-82008-1 | 108 | 43.49 | 6 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Equipment Malfunction |  | 2010-09-24 | 2010-10-11 | Other |  | Other |  | Lodi
96 | 10-88743-1 | 200C | 1 | 0.75 | Distribution Main <= 60 PSIG |  |  |  |  | Construction Defect |  | 2010-11-08 | 2011-01-07 | Other |  | Steel |  | Rio Vista | 1310 3/25/11 Called Wondy George (...) - Cott message 1310. Clay was the acting gus
96 | 10-88743-1 | 200C | 1 | 0.75 | Distribution Main <= 60 PSIG |  |  |  |  | Construction Defect |  | 2010-11-08 | 2011-01-07 | Other |  | Steel |  | Rio Vista
| 10-88743-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Construction Defect | Leak on Threads fitting | 2010-11-08 | 2011-01-07 | Other | Pipe Dope | Steel/Wrought Iron |  | Rio Vista | Re Doped Thread; Soap tested at line pressure (759Lbs)
| 10-10801-1 |  |  | 2 | Transmission |  | Valves |  |  | Other | Loose fitting tighten fitting | 2010-08-13 | 2010-09-05 | Other | Tighten fitting | Steel/Wrought Iron |  |  | Greased valve to stop leak. Removed Zin Plug, put pipe dope on plug anad installed and tightened; (On post it note) GTLS Entered repaired
96 | 10-10801-1 | 108 |  | 2 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-08-13 | 2010-09-05 | Other |  |  |  | Lodi | (On post-it note) Bud, you were looking for leak #10-10802-1 the bad number Wendy gave you. I found this in IGIS, leak # 10-10801-1 Could this be it? Brad.
| 10-10801-1 |  |  | 2 | Transmission |  | Valves |  |  | Other | Loose fitting tighten fitting | 2010-08-13 | 2010-09-05 | Other | Tighten fitting | Steel/Wrought Iron |  | Lodi
96 | 10-10801-1 | 108 | [9 empty] | 2010-08-13 | [5 empty] | Lodi
93 | 10-02491-1 |  |  |  | Distribution Main > 60 PSIG |  | Compression Coupling Stainless Steel | Fitting | REGULATOR/PILOT | Other | Loose fitting and replaced "O" Ring | 2010-11-01 | 2011-01-07 | Greased - Other | Tighten Cap/Bolt - Fitting |  |  | Lodi | Tighten fittings & Replaced "O" ring; All above ground piping tighten bolts & replaced O-Ring to repair; (On Post-It notes) Sent back to Stockton agter repairing 301's; Recieved 12-30-10
96 | 10-82010-1 |  |  | 6 | Distribution Main > 60 PSIG |  | Other Mechanical Joint |  |  | Other |  | 2010-09-24 | 2011-03-19 | Tighten Cap/Bolt - Fitting |  | Steel |  | Lodi | Retightened Bolts; Tightened bolts around flauge
96 | 10-22001-1 |  |  | 6 | Transmission >= 20% SMYS |  | Other Mechanical Joint |  |  | Other |  | 2010-08-13 | 2011-03-19 | Other |  | Steel |  | Dixon | Removed spool piece install new gaskets; Removed spool piece cleaned gasket faces and reinstalled spool piece with new gaskets. Blow down stack for valve A, L, J.
96 | 10-88739-1 | 200A-11 | 5.21 | 16 | Transmission >= 20% SMYS |  | Threads |  |  | Unknown |  | 2010-10-31 | 2011-03-19 | Tighten Cap/Bolt - Fitting |  | Steel |  | Rio Vista | Stem packing on orifice meter; Tightened stm packing and orifice plate door. Installed sealant and retightened plug on 1/2" gauge tap valve. Remove tubing and 1/2" valve and installed plug on down stream pressure tab.
96 | 10-20003-1 | 200 |  | 4 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-08-10 | 2011-03-12 | Mechanical Repair Fitting - Fitting |  | Steel |  | Rio Vista
96 | 10-20003-1 |  |  | 4 | Transmission >= 20% SMYS |  | Other |  | blowdown stack | Other | mech. joint | 2010-08-10 | 2011-03-12 |  |  |  |  | Rio Vista | Pulled joint apart cleaned o-ring grove and face of flange, Reinstalled o-ring with lithium greese; cap on top of blow down stack leaking at o-ring
96 | 10-88722-1 | 196A | 9.93 | [8 empty] | 2010-11-04 | [5 empty] | Isleton
96 | 10-88723-1 | 196A | 9.92 | 2011-01-02 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-11-04 | 2011-03-12 | Tighten Cap/Bolt - Fitting |  |  | steel |  | Tyler Is seperator station plug on v-4 gauge tap. Threads leading at plug removed plug install thread sealant reinstalled
96 | 10-88723-1 | 196A | 9.92 | 2011-01-02 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-11-04 | 2011-03-12 | Tighten Cap/Bolt - Fitting |  | Steel |  | Isleton | Threads lacking at plug, removed plug install therad sealant reinstalled; Removed plug installed thread sealant reinstalled plug
96 | 10-88738-1 | 200A11 | 2.52 | 12 | Transmission >= 20% SMYS |  | Other Mechanical Joint |  |  | Other |  | 2010-10-31 | 2011-04-23 | Other | Gasket | Steel |  | Rio Vista | See Attached; Removed blind flange cleaned gasket faces, installed new 12''x400 gasket and new studs,
96 | 10-88689-1 | 114 | [9 empty] | 2010-11-13 | 2011-05-02 |  |  |  |  | Rio Vista | repair location 100 from south shore San Joaquin River, No Leak Found
96 | 10-88692-1 | 130 | 0.49 | [8 empty] | 2010-11-12 | 2011-04-30 |  |  |  |  | Rio Vista | No leak found
96 | 10-88704-1 | 182 | 11.58 | [8 empty] | 2010-11-13 | 2011-05-02 |  |  |  |  | Rio Vista | No Leak Found
96 | 10-88755-1 | 400 | 0.03 | [8 empty] | 2010-11-15 | 2011-05-02 |  |  |  |  | Rio Vista | No leak found
96 | 10-88770-1 | 168 | 11.51 | [8 empty] | 2010-11-09 | 2011-04-29 |  |  |  |  | Rio Vista | No Leak Found
96 | 10-88771-1 | 168 | 11.5 | [8 empty] | 2010-11-09 | 2011-04-29 |  |  |  |  | Rio Vista | No Leak Found
96 | 10-88772-1 | 195A3-1 | 0.18 | [8 empty] | 2010-11-10 | [5 empty] | Isleton | No Leak Found
[13 empty] | 2011-05-02 | [5 empty] | This is a part of the previous A-form. No leak was found. ;
48 |  |  |  | 6 | Gathering | [6 empty] | 1972-01-19 |  |  |  | Steel
48 |  |  |  | 6 | Gathering | [6 empty] | 1972-01-19 |  |  |  | Steel
48 |  |  |  | 6 | Gathering | [6 empty] | 1971-05-27 |  |  |  | Steel
48 |  |  |  | 2 | Gathering | [6 empty] | 1971-07-13 |  |  |  | Steel |  |  | Installed on GM 164129 - 1966
48 |  |  |  | 6 | Gathering | [10 empty] | Steel |  |  | 4" installed on Gm 173444 1970. No PL sheet for saxon field.
48 |  |  |  | 16 | Gathering | [10 empty] | Steel
48 |  |  |  | 16 | Transmission | [10 empty] | Steel |  |  | Installed on GM 69800-1942. Lowered on G.M. 175372 - 4th lowering F.S 346+37 to 351+01. Seven patches welded on pitted holes at various location between F.S. 346+37 to F.S. 351+01. .520 wall material not available, .500 wall material used for patches. Pipe rewrapped where needed-tar&paper. Ultra sonic calipher test wall thickness.
48 |  |  |  | 16 | Transmission | [10 empty] | Steel |  |  | Installed on GM 69800. Lowered on GM 175372-3rd sect lowered.
48 |  |  |  | 16 | Transmission | [10 empty] | Steel |  |  | installed on GM 69800-1942. Lowered on GM 175372 2600 ft.-2nd section lowered.
48 |  |  |  | 3 | Gathering | [10 empty] | Steel
48 |  |  |  | 6 | Gathering | [10 empty] | Steel
48 |  |  |  | 4 | Gathering | [10 empty] | Steel |  |  | 4'' main installed on GM175450 year 3-22-1971. Main was cut & lowered across levee at F.S. 28 +82 & FS 29+03
48 |  |  |  | 8 | Gathering | [10 empty] | Steel |  |  | 6" main installed on GM 175017, 3" main installed on GM 175475
48 |  |  |  | 6 | Gathering | [10 empty] | Steel |  |  | 6" main installed on GM 175433 1970, 4" main installed on GM 175580 1971
s
48 |  |  |  | 16 | Transmission | [6 empty] | 1972-03-22 |  |  |  | Steel
48 |  |  |  | 16 | Transmission | [6 empty] | 1972-03-22 |  |  |  | Steel
48 |  |  |  | 16 | Transmission | [6 empty] | 1972-03-22 |  |  |  | Steel
48 |  |  |  | 16 | Transmission | [6 empty] | 1972-03-22 |  |  |  | Steel
48 |  |  |  | 16 | Transmission | [10 empty] | Steel
48 |  |  |  | 16 | Transmission | [6 empty] | 1972-03-22 |  |  |  | Steel
48 |  |  |  | 16 | Transmission | [6 empty] | 1972-03-22 |  |  |  | Steel
48 |  |  |  | 0.04 | Gathering | [10 empty] | Steel
48 |  |  |  | 4 | Gathering | [6 empty] | 1971-07-15 |  |  |  | Steel |  |  | Installed GM. 170334
48 |  |  |  | 6 | Gathering | [6 empty] | 1971-04-16 |  |  |  | Steel |  |  | 6" main installed on GM 174341 - 1970, 4" main installed on GM 175980 - 1971
48 |  |  |  | 3 | Gathering | [10 empty] | Steel |  |  | installed on GM 171451-1968
48 |  |  |  | 6 | Gathering | [10 empty] | Steel |  |  | 6" main to saxon fieeld installed on GM 173444 1970
48 |  |  |  | 8 | Transmission | [6 empty] | 1972-03-08 |  |  |  | Steel
48 |  |  |  | 8 | Transmission | [6 empty] | 1972-03-08 |  |  |  | Steel
48 |  |  |  | 2 | Gathering | [6 empty] | 1971-10-08 |  |  |  | Steel |  |  | Valvue 109 & mcCorwack #3. Tie-in Gm 174789 1979. McCorwack 5 tie-in on Gm 1767730 1971
48 |  |  |  | 4 | Gathering | [6 empty] | 1971-01-03 |  |  |  | Steel |  |  | 4'' main to P.E. #9 Installed on GM 175143 1970. P.E. #8 tie-in 6' from rised of P.E. #9
48 |  |  |  | 8 | Transmission | [6 empty] | 1973-09-11 |  |  |  | Steel
48 |  |  |  | 4 | Gathering | [10 empty] | Steel |  |  | Main to wist bell #1 installed on GM 165430 - 1966
48 |  |  |  | 6 | Gathering | [6 empty] | 1972-02-08 |  |  |  | Steel
48 |  |  |  | 6 | Gathering | [6 empty] | 1972-02-08 |  |  |  | Steel
48 |  |  |  | 8 | Gathering | [6 empty] | 1972-02-08 |  |  |  | Steel
48 |  |  |  | 8 | Gathering | [6 empty] | 1972-02-08 |  |  |  | Steel
48 |  |  |  | 6 | Gathering | [6 empty] | 1972-02-08 |  |  |  | Steel
48 |  |  |  | 6 | Gathering | [6 empty] | 1972-02-08 |  |  |  | Steel
48 |  |  |  | 6 | Transmission | [6 empty] | 1972-06-06 |  |  |  | Steel
48 |  |  |  | 4 | Transmission | [10 empty] | Steel
|  |  |  | 6 | Gathering | [6 empty] | 1972-06-07 |  |  |  | Steel
48 |  |  |  | 4 | Gathering | [10 empty] | Steel
48 |  |  |  | 4 | Gathering | [6 empty] | 1972-07-20 |  |  |  | Steel
48 |  |  |  |  | Gathering | [6 empty] | 1972-07-20 |  |  |  | Steel
48 |  |  |  | 4 | Gathering | [6 empty] | 1972-10-03 |  |  |  | Steel
48 |  |  |  | 4 | Gathering | [6 empty] | 1973-03-27 |  |  |  | Steel
48 |  |  |  | 4 | Gathering | [6 empty] | 1973-03-27 |  |  |  | Steel
|  |  |  | 4 | Transmission | [6 empty] | 1973-04-05 |  |  |  | Steel
48 |  |  |  | 4 | Transmission | [6 empty] | 1973-04-05 |  |  |  | Steel
48 |  |  |  | 12 | Transmission | [6 empty] | 1973-01-26 |  |  |  | Steel
back of A form, no front attached.
48 |  |  |  | 16 | Transmission | [6 empty] | 1973-04-03 |  |  |  | Steel
48 |  |  |  | 4 | Gathering | [6 empty] | 1973-12-11 |  |  |  | Steel
Back of A form, no front attached.
48 |  |  |  | 4 | Gathering | [6 empty] | 1974-01-30 |  |  |  | Steel
48 |  |  |  | 4 | Gathering | [6 empty] | 1974-01-31 |  |  |  | Steel
48 |  |  |  | 4 | Gathering | [10 empty] | Steel
48 |  |  |  | 4 | Gathering | [6 empty] | 1974-01-31 |  |  |  | Steel
48 |  |  |  | 4 | Gathering | [10 empty] | Steel
Back of A form, no front page attached.
48 |  |  |  | 4 | Gathering | [6 empty] | 1974-07-17 |  |  |  | Steel
48 |  |  |  | 4 | Gathering | [6 empty] | 1974-07-17 |  |  |  | Steel
48 |  |  |  | 3 | Gathering | [6 empty] | 1974-07-17 |  |  |  | Steel
48 |  |  |  | 4 | Gathering | [6 empty] | 1974-07-17 |  |  |  | Steel
48 |  |  |  | 12 | Gathering | [6 empty] | 1974-09-24 |  |  |  | Steel
48 |  |  |  | 6 | Gathering | [6 empty] | 1974-10-15 |  |  |  | Steel
48 |  |  |  | 6 | Gathering | [6 empty] | 1974-10-15 |  |  |  | Steel
A-Form missing first page.
48 |  |  |  | 6 | Gathering | [6 empty] | 1974-07-25 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1974-07-25 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 3 | Gathering | [6 empty] | 1974-07-24 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1974-07-24 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 3 | Gathering | [6 empty] | 1974-07-24 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 2007-07-24 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1974-07-26 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [10 empty] | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1975-03-11 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-03-11 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 3 | Gathering | [6 empty] | 1975-03-11 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [10 empty] | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [10 empty] | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [10 empty] | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-09-19 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-03-19 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1975-03-04 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1975-03-04 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 8 | Gathering | [6 empty] | 1975-03-04 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-03-04 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1975-03-04 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-09-16 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-09-16 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 6 | Gathering | [6 empty] | 1975-09-16 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 6 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | none
48 |  |  |  | 6 | Gathering | [6 empty] | 1975-03-04 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1975-03-04 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 8 | Gathering | [6 empty] | 1975-03-04 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-03-04 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1975-03-04 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1975-05-20 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [10 empty] | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1975-03-11 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-03-11 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 3 | Gathering | [6 empty] | 1975-03-11 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-03-19 |  |  |  | Steel
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-03-19 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-04-10 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [10 empty] | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [10 empty] | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [10 empty] | Steel/Wrought Iron
48 |  |  |  | 12 | Transmission | [6 empty] | 1975-06-11 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 10 | Transmission | [6 empty] | 1975-06-11 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-05-29 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 10 | Gathering | [6 empty] | 1975-05-29 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1975-05-14 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1975-05-14 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-05-14 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 10 | Gathering | [6 empty] | 1975-05-14 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 8 | Gathering | [6 empty] | 1975-05-27 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-05-27 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1975-05-28 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1975-05-28 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 12 | Transmission | [6 empty] | 1975-05-30 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 6 | Gathering | [10 empty] | Steel/Wrought Iron
48 |  |  |  | 3 | Gathering | [6 empty] | 1974-03-25 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 3 | Gathering | [10 empty] | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1974-04-24 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1975-09-02 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-09-02 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 8 | Gathering | [6 empty] | 1974-12-18 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 3 | Gathering | [6 empty] | 1975-01-20 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 3 | Gathering | [6 empty] | 1975-01-20 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 10 | Transmission | [6 empty] | 1976-02-24 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 12 | [7 empty] | 1976-03-10 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-04-15 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Transmission | [6 empty] | 1976-01-06 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 6 | Transmission | [6 empty] | 1976-01-06 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 4 | Transmission | [6 empty] | 1975-11-04 |  |  |  | Steel/Wrought Iron |  |  | Inspection cover valvue and lie in pointe
48 |  |  |  | 4 | Transmission | [6 empty] | 1975-11-04 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 3 | Transmission | [6 empty] | 1976-06-15 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  |  | Transmission | [6 empty] | 1976-06-15 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Transmission | [6 empty] | 1976-06-15 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1976-01-28 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 6 | Gathering | [6 empty] | 1976-04-22 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 10 | Transmission | [6 empty] | 1976-08-20 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 12 | Transmission | [6 empty] | 1976-08-20 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 12 | Transmission | [6 empty] | 1976-04-27 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 12 | Transmission | [6 empty] | 1976-05-05 |  |  |  | Steel/Wrought Iron |  |  | NONE
|  |  |  | 6 | [14 empty] | NONE
48 |  |  |  | 6 | Transmission | [6 empty] | 1976-02-10 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 12 | Transmission | [6 empty] | 1976-02-11 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 12 | Transmission | [6 empty] | 1976-02-19 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 8 | Transmission | [6 empty] | 1976-03-09 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 12 | Transmission | [6 empty] | 1976-03-09 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 12 | Transmission | [6 empty] | 1976-03-16 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 12 | Transmission | [6 empty] | 1976-03-16 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 12 | Transmission | [6 empty] | 1976-03-16 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 12 | Transmission | [6 empty] | 1976-03-16 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 8 | Gathering | [6 empty] | 1976-07-28 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1976-07-28 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 6 | Gathering | [6 empty] | 1976-07-28 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 8 | Gathering | [6 empty] | 1976-07-28 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1977-04-20 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 8 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | NONE
8
|  | 200 |  | 6.625 | Gathering
|  |  |  | 8.625 | [11 empty] | Steel
|  |  |  | 8.625 | [11 empty] | Steel
|  |  |  | 8.625 | [11 empty] | Steel
|  |  |  | 8.625 | [11 empty] | Steel
|  |  |  | 6.625 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 2.375 | [11 empty] | Steel
|  | 195 |  | 4 | [11 empty] | Steel |  |  | wrap looked good; no crop damage swamp area; wrap looked good;
|  | 195 |  | 12 | [11 empty] | Steel |  |  | wrap looked good; no crop damage swamp area
|  | 195 |  | 12 | [11 empty] | Steel |  |  | wrap looked good; no crop damage swamp area
|  | 195 |  | 4 | [11 empty] | Steel |  |  | wrap & pipe looked good. Wrap bonded to main good. no crop damage swamp area
|  | 195 |  | 12 | [11 empty] | Steel |  |  | wrap & pipe looked good & wrap bonded to pipe good. no crop damage swamp area
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Wrap & pipe looked real good wrap bonded to pipe good. no crop damage swamp area
|  | 195 |  | 4 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inspect pipe. Pipe & wrap in good shape. Wrap bonded to pipe good. 10'x10' clover damage
|  | 195 |  | 12 | [11 empty] | Steel |  |  | wrap looked good. Did not remove wrap because 12" main were about 1'' apart could not wrap.; 10'x10' clover damage
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Did not remove wrap because the 12" main were too close together about 1'' apart. wrap looked good.; 10'x10' clover pasture damage
|  | 195 |  | 4 | [11 empty] | Steel |  |  | wrap looked good.; 15'x15' clover pasture damage
|  | 195 |  | 12 | [11 empty] | Steel |  |  | wrap looked good.; 15'x15' clover pasture damage
|  | 195 |  | 12 | [11 empty] | Steel |  |  | wrap looked good.; 15'x15' clover pasters damage
|  | 195 |  | 4 | [11 empty] | Steel |  |  | Remove 18'' of tar wrap to longest pipe. wrap bonded to remain good.; 15'x15' clover damage pastures
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Removed 18'' after wrap to ... pipe. wrap bonded to main good.; 15'x15' clover pasture damage
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to deepest pipe. Wrap bonded to main good.
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Did not remove wrap. Wrap looked good. No crop damage
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Did not remove wrap. Wrap looked good.; No crop damage
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Removed 18" of tar wrap ... Pipe wrap bonded to pipe.; 15'x15' corn damage
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Removed 18'' tar wrap to inspect pipe, wrap bonded to main.; 15'x15' corn damage
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to ... pipe wrap bonded to pipe good. main's 12' apart.; 15'x15' corn damage
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to disp pipe. wrap bonded to pipe good. at this point mains are 12' apart.; 15'x15' corn damage
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Removed aprox 18'' of wrap to insp. pipe. wrap bonded to pipe good. used two 5'' water pumps to pump water from hole.; 20'x20' corn damage
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to insp. main. Wrap bonded to pipe good. Mains 9' apart.
|  | 195 |  | 12 | [14 empty] | Couldn't not find pipe of this location, to much water used two water pumps. corn damage 15'x15'
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inspect pipe. Wrap bonded to pipe good...; corn damage s15'x15'
|  | 195 |  | 8 | [11 empty] | Steel |  |  | wrap not bonded to main good. original primer no sign of water. no crop damage
|  | 195 |  | 8 | [11 empty] | Steel |  |  | Wrap no bonded to pipe. water under wrap. no crop damage
|  | 195 |  | 8 | [11 empty] | Steel |  |  | Removed wrap at weld wrap... Bonded to pipe good. Weld & Pipe looked good. 20'x20' corn mylo damage
|  | 195 |  | 4 | [11 empty] | Steel |  |  | Wrap bonded to main good. 4'x250' corn or mylo damage for rightway. 20'x20' corn or mylo dam
|  | 195 |  | 8 | [11 empty] | Steel |  |  | Wrap no bonded to main good. original primer no sign of water. no crop damage
|  | 195 |  | 8 | [11 empty] | Steel |  |  | Wrap no bonded to pipe water under wrap. no crop damage.
|  | 195 |  | 8 | [11 empty] | Steel |  |  | Removed wrap at weld wrap. Bonded to pipe good. Weld & Pipe looked good. 20'x20' corn or mylo damage
|  | 195 |  | 4 | [11 empty] | Steel |  |  | Wrap bonded to main good. 4'x250' corn or mylo damage for Rightway. 20'x20' corn or mylo damage
|  | 195 |  | 16 | [11 empty] | Steel |  |  | 20'x20' crop damage mylo. wrap bonded to pipe good.
|  | 195 |  | 16 | [11 empty] | Steel |  |  | 20'x20' crop damage mylo. wrap bonded to pipe good.
|  | 195 |  | 16 | [11 empty] | Steel |  |  | 20'x20' mylo crop damage. wrap bonded to pipe good.
|  | 195 |  | 16 | [11 empty] | Steel |  |  | 20'x20' mylo crop damage. wrap bonded to pipe good.
|  | 195 |  | 16 | [11 empty] | Steel |  |  | 20'x20' mylo crop damage. wrap bonded to main good.
|  | 195 |  | 16 | [11 empty] | Steel |  |  | 20'x20' mylo crop damage. Wrap bonded to main good.
|  | 195 |  | 16 | [11 empty] | Steel |  |  | 20'x20' crop damage Mylo. Wrap bonded to pipe good.
|  | 195 |  | 16 | [11 empty] | Steel |  |  | 20'x20' crop damage mylo. wrap bonded to pipe good.
|  | 195 |  | 16 | [11 empty] | Steel |  |  | 20'x20' mylo crop damage. Wrap bonded to pipe good.
|  | 195 |  | 16 | [11 empty] | Steel |  |  | 20'x20' mylo crop damage. Wrap bonded to pipe good
|  | 195 |  | 16 | [11 empty] | Steel |  |  | 20'x20' mylo crop damage. Wrap bonded to main good.
|  | 195 |  | 16 | [11 empty] | Steel |  |  | 20'x20' mylo crop damage. Wrap bonded to main good.
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wrap loose but not broken
|  | 195 |  | 6 | [11 empty] | Steel |  |  | tar wraps. wrap loose on pipe but not broken
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Tar wrap. Wrap sogging on bottom & broken on top. Water under wrap.
|  | 195 |  | 6 | [11 empty] | Steel |  |  | wrap loose but not broken. 4 holes 1 MD
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wrap loose but not broken
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Tar wrap. Wrap loose on pipe but no broken
|  | 195 |  | 6 | [11 empty] | Steel |  |  | tar wrap. wrap sogging on bottom & broken on top. Water under wrap.
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wrap loose but not broken. 4 hole 1 MD
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx 18'' of tar wrap to inspect pipe. Wrap bonded to main good.; Corn crop damage 15'x15'
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx 18'' of tor wrap to inspect pipe. Wrap not bonded to pipe. Water botween wrap & pipe.; Corn crop damage 15'x15'
|  |  |  | 10 | [11 empty] | Steel |  |  | Removed approx 18'' of tar wrap to inspect pipe. Wrap bonded to pipe good.; Corn crop damage 15'x15'
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed aprox. 18'' of tar wrap to inspect pipe. Wrap not bonded to main. Water between wrap & pipe.; Corn crop damage 15'x15'
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed about 18'' of tar wrap to inspect pipe. Wrap not bonded to pipe. Water between wrap & pipe.; Corn crop damage 15'x15'
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx 18'' of tar wrap to inspect pipe, part of wrap gone. ... water under Rest of wrap. Wrap not broken. ;Pasture no crop damage.
|  | 131 |  | 10 | [11 empty] | Steel |  |  | removed aprox. 18'' of tar wrap to inspect pipe. part of wrap good. From side of pipe water underneath rest of wrap. wrap not broken. pastures no crop damage.
|  | 131 |  | 10 | [14 empty] | Removed approx 18'' of tar wrap to inspect pipe. Part of wrap gone from sides of main. water underneath rest of wrap. wrap not bonded to pipe.; Pasture no crop damage.
|  | 131 |  | 10 | [14 empty] | Removed approx 18'' of tar wrap to inspe. pipe. Part of wrap gone from sides. Water underneath rest of wrap. Wrap not bonded to pipe.; Pasture no crop damage.
|  | 131 |  | 10 | [11 empty] | Steel |  |  | removed aprox 18'' of tar wrap to inspect pipe. Wrap half gone from pipe on top. Rest of wrap not bonded to pipe with water underneath wrap.
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Wrap on sides of main half gone. Rest of wrap not bonded to pipe with water between wrap & pipe.
|  | 131 |  | 10 | [14 empty] | This area flooded
|  |  |  | 10 | [14 empty] | Flooded
|  |  |  | 10 | [14 empty] | Flooded
|  |  |  | 10 | [14 empty] | Flooded
|  |  |  | 10 | [14 empty] | Flooded
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx. 18'' of tar wrap to inspect pipe. Wrap not bonded to pipe. no signs of water.; no crop damage
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx 18'' of wrap in drain. Detach to longest pipe's wrap half gone. This point 3' less than sta marked above.; No crop damage.
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx. 18'' of tar wrap to insp. pipe. Wrap not bonded to pipe. Water under wrap.; Corn damage 20'x20'
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx. 18'' of tar wrap to insp. pipe. Wrap not bonded to pipe on sides, water under wrap or bottom pited bad.; Corn damage 20'+20'
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx 18'' of tar wrap to insp. pipe. Wrap was not broken but not bonded to main good.; Corn damage 20'+20'
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx 18'' of tar wrap to insp. pipe. Wrap not bonded to main. Water under wrap.; Safflower damage 20'x20'
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx 18'' of tar wrap to insp. pipe. wrap not bonded to pipe. water under wrap.; Safflower 20'x20'
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx. 18'' of tar wrap to insp. pipe. Wrap not bonded to pipe. water under wrap.; Safflower 20'x20'
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx 18'' of tar wrap to insp. pipe. Wrap not bonded to pipe. Water under wrap.; Safflower 25'x25'
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx. 18'' of tar wrap to inspect pipe. Wrap not bonded to pipe. Water under wrap. Wrap not broken.; 15'x15' Satfflower damage
|  |  |  | 10 | [11 empty] | Steel |  |  | Removed Aprox 18" of tar wrap to inspect pipe, wrap not bonded, water under wrap. Wrap not broken
|  | 131 |  | 15 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inspect pipe. Wrap not bonded. Water under wrap, wrap not broken. 15'x15' Sotfflower damage
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inpsect pipe. wrap not bonded. water under wrap. wrap not broken. 15'x15' Sotfflower damage
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' tar wrap to inspect pipe. Wrap not bonded to pipe. Wrap is not broken. 15'x15' Safflower damage
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' tar wrap to inpsect pipe. Wrap not bonded to pipe. Water under wrap. 15'x15' Safflower damage
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inspect pipe. Wrap not bonded to pipe. Water under wrap. 15'x15' Safflower damage
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inspect pipe. wrap not bonded to main & half off main. Water under wrap that left on pipe. 15'x15' Safflower damage
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inspect pipe. Wrap not bonded to pipe. Water underneath wrap. 15'x15' Safflower damage
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to insp. pipe, wrap not bonded to main. Wrap is falling off main with dirt. Rewraped about 7''. signs of water. 15'x15' Safflower damage
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inspect pipe. Wrap not bonded to pipe. Water under wrap. 15'x15' Safflower
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inspect pipe. Wrap not bonded to pipe with water under wrap. Heavy scaley rust.; 15'x15' safflower damage
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to insp. pipe. Wrap not bonded to pipes. Water under wrap. Heavy scaley rust.; 15'x15' Safflower damage.
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to insp. pipe. Wrap not bonded to main. Water under wrap. Heavy scaley rust.; 15'x15' Safflower damage
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to insp. pipe. Wrap not bonded to pipe, water under wrap.; 15'x15' Safflower damage
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to insp. pipe. Wrap not bonded to pipe. water under wrap. Scaley rust.; grains has been harvested.
|  |  |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to insp. pipes. wrap not bonded to pipe. No water.; grain has been harvested
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to insp. pipe. Wrap not bonded to pipe. Broke off easy ; grain has been harvested.
|  | 195 |  | 8 | [11 empty] | Steel |  |  | Moisture under wrap. Wrap loose, broken. Primer spotty.
|  | 195 |  | 8 | [11 empty] | Steel |  |  | Wrap loose, broken, moisture under wrap. Rust scale extremely heavy.
|  | 195 |  | 8 | [11 empty] | Steel |  |  | Coating (tar) broken, moisture underneath. Rust scale heavy
|  | 195 |  | 8 | [11 empty] | Steel |  |  | Water under wrap. Coating broken. Primer rusted thru.
|  |  |  | 4 | [11 empty] | Steel |  |  | Tar Wrap, Two 4'' mains at this sta. Both mains checked out the same. Couldn't fixed 8''
|  |  |  | 4 | [11 empty] | Steel |  |  | Tar wrap. Wrap loose but not broken. Red Primer on part of pipe.
|  |  |  | 4 | [11 empty] | Steel |  |  | No crop damage. Wrap sogging on buttom & broken tap. water under wrap.
|  |  |  | 4 | [11 empty] | Steel |  |  | Tar wrap, wrap sogging on bottom & water between wrap + pipe.
|  | 195 |  | 8 | [11 empty] | Steel |  |  | Moisture under wrap. Wrap loose, broken. Primer spotty
|  | 195 |  | 8 | [11 empty] | Steel |  |  | Wrap loose, broken, moisture under wrap. Rust scale extremely heavy.
|  | 195 |  | 8 | [11 empty] | Steel |  |  | Coating (tar) borken, moisture underneath. Rust scale heavy
|  | 195 |  | 8 | [11 empty] | Steel |  |  | Water under wrap. Coating broken. Primer rusted thru.
|  |  |  | 4 | [11 empty] | Steel |  |  | Tar wrap. Two 4'' mains at the sta. Both main checked out the same. Couldn't find 8''
|  |  |  | 4 | [11 empty] | Steel |  |  | Tar wrap. Wrap loose but not broken. Red Primer on part of pipe.
|  |  |  | 4 | [11 empty] | Steel |  |  | No crop damage. Wrap sogging on bottom & broken tap. water under wrap.
|  |  |  | 4 | [11 empty] | Steel |  |  | Tar wrap. Wrap sogging on bottom & water between wrap & pipe.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Water next to main. No crop damage.
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | Water mext to main. No crop damage
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Wrap good. No water. no crop damage
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No crop damage
|  | 195 |  | 4 | [11 empty] | Steel |  | Rio Vista | No water under wrap. Rust. No crop damage.
|  | 195 |  | 4 | [11 empty] | Steel |  | Rio Vista | No water under wrap. No crop damage.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Heavy rust, lots of water. No pitting. No crop damage.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | No water under wrap. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | No water under wrap. No crop damage
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Lots of water under wrap. No crop damage
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | No water under wrap. No crop damage.
|  | 195 |  | 12 | [13 empty] | Rio Vista | Water under wrap. No pitt. No crop damage
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No pits. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Water under wrap. Main was dug up under road. That is why its so deep. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Water under main. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Water under main. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No crop damage.
|  | 195 |  | 12 | [13 empty] | Rio Vista | Water under wrap. No crop damage.
|  | 195 |  | 12 | [13 empty] | Rio Vista | Water under wrap. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | No water. No crop damage.
|  | 195 |  | 8 | [11 empty] | Steel |  | Rio Vista | No water. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | No water. No crop damage.
|  | 195 |  | 8 | [11 empty] | Steel |  | Rio Vista | No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | No water under wrap. No crop damage.
|  | 195 |  | 8 | [11 empty] | Steel |  | Rio Vista | No crop damage
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | No crop damage. No water under wrap.
|  | 195 |  | 8 | [11 empty] | Steel |  | Rio Vista | No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | No water under wrap. No crop damage.
|  | 195 |  | 8 | [11 empty] | Steel |  | Rio Vista | No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | No crop damage.
|  | 195 |  | 4 | [11 empty] | Steel |  |  | Wrap looked good.; 10'x10' corn damage
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Wrap looked good. ;10'x10' corn damage.
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Wrap looked good.; 10'x10' corn damage.
|  | 195 |  | 4 | [11 empty] | Steel |  |  | Wrap bonded to pipe good. Pipe looks good.; 10'x10' Corn Damage
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Wrap bonded to pipe good. Pipe looks good.; 10'x10' corn damaged.
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Wrap bonded to main good. Pipe looks good.; 10'x10' corn damage.
|  | 195 |  | 4 | [11 empty] | Steel |  |  | Wrap looked good.; no crop damage swamp area.
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Wrap looked good.; no crop damage swamp area
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Wrap looked good.; no crop damage. swamp area.
|  | 195 |  | 4 | [11 empty] | Steel |  |  | Wrap & pipe looked good. Wrap bonded to main good.; no crop damage. Swamp area.
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Wrap & pipe looked good & wrap bonded to pipe good.; No crop damage. Swamp area.
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Wrap & pipe looked real good. Wrap bonded to pipe good.; no crop damage. swamp area.
|  | 195 |  | 4 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inspect pipe. Pipe & wrap in good shape. Wrap bonded to pipe good.; 10'x10' clover damage.
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Wrap looked good. Did not remove wrap because 12'' main were about 1'' apart. Could not wrap.; 10'x10' clover damage.
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Did not remove wrap because the 12'' main was too close together. about 1'' apart. Wrap looked good.; 10'x10' clover damage.
|  | 195 |  | 4 | [11 empty] | Steel |  |  | Wrap looked good.; 15'x15' clover pasture damage.
|  | 195 |  | 12 | [11 empty] | Steel |  |  | wrap looked good.; 15'x15' clover pasture damage.
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Wrap looked good. ;15'x15' clover pasture damage.
|  | 195 |  | 4 | [11 empty] | Steel |  |  | Remove 18'' of tar, wrap to inspect pipe. Wrap bonded to main good.; 15'x15' clover damage pasture
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to insp. pipe. Wrap bonded to main good.; 15'x15' Clower pasture damage
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inspect pipe, wrap bonded to main good.
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Did not remove wrap. Wrap looked good. no crop damage
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Did not remove wrap. Wrap looked good.; No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  |  | removed 18'' of tar wrap to inspect pipe. Wrap bonded to pipe.; 15'x15' corn damage.
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Removed 18'' tar wrap to inspect pipe. Wrap bonded to main.; 15'x15' corn damage.
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to Insp. pipe wrap. Bonded to pipe good. Main's 12' apart. ;15'x15' corn damage.
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to insp. pipe, wrap bonded to pipe good. At that point mains are 12' apart.; 15'x15' corn damage.
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Removed approx. 18'' of wrap to insp. pipe. Wrap bonded to pipe good. used two 5'' water pumps to pump water for hole.; 20'x20' corn damage.
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inspect main. Wrap bonded to pipe good. main 9'' apart.; 25'x25' corn damage.
|  | 195 |  | 12 | [14 empty] | Couldn't not find pipe at this location, to much water used two water pumps.
|  | 195 |  | 12 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inspect pipe. Wrap bonded to pipe good.; Corn damage 15'x15'
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista
|  | 195 |  | 10 | [13 empty] | Rio Vista | Lot of little pits
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | Water under wrap.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Like new
|  | 195 |  | 10 | [11 empty] | Steel |  | Lincoln | Over head dog leg = mitered
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | Water under wrap
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | 10'' is mitered
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Water under wrap
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | Water under wrap
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | Water under wrap
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | Water under wrap
|  | 195 |  | 4 | [11 empty] | Steel |  | Rio Vista | Wrap was damage while digging ditch by farmer. Rewraped all the way across ditch.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Water under wrap
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | Lots of pitting. To small to measure
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista
|  | 195 |  | 10 | [13 empty] | Rio Vista | Lots of little pits
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | Water under wrap
|  | 195 |  | 10 | [11 empty] | Steel |  | Lincoln | Over head dog leg = mitered
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Like new
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | Water under wrap
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | 10'' is mitered
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Water under wrap
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | Water under wrap
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | Water under wrap
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | Water under wrap
|  | 195 |  | 4 | [11 empty] | Steel |  | Rio Vista | Wrap was damage while digging ditch by farmer. Rewraped all the way across ditch.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Water under wrap
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | Lots of pitting. To small to measure
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | No water. No crop damage
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | No water under wrap. No crop damage.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No crop damage.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No crop damage.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | No crop damage. Water under wrap.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista
|  | 195 |  | 10 | [13 empty] | Rio Vista | Lot of little pits
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | Water under wrap
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Like new
|  | 195 |  | 10 | [11 empty] | Steel |  | Lincoln | Over head dog leg = mitered
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | water under wrap
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | 10'' is mitered
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Water under wrap
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | Water under wrap
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | Water under wrap.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | Water under wrap
|  | 195 |  | 4 | [11 empty] | Steel |  | Rio Vista | Wrap was damage while digging ditch by farmer. Rewraped all the way across ditch.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Water under wrap
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | Lots of pitting. To small to measure
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx. 18'' of tar wrap to inspect pipe. Wrap bonded to main good.
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx. 18'' of tar wrap to inspect pipe. Wrap not bonded to pipe. Water between wrap & pipe.. Bill Cabral - Corn crop damage 15'x15'
|  |  |  | 10 | [11 empty] | Steel |  |  | Removed approx. 18'' of tar wrap to inspect pipe. Wrap bonded to pipe good.; Bill Cabral - Corn crop damage 15'x15'
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed appox. 18'' of tar wrap to inspect pipe. Wrap not bonded to main. Water between wrap & pipe.; Bill Cabral - corn crop damage 15'x15'
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed about 18'' of tar wrap to inspect pipe. Wrap not bonded to pipe. Water between wrap & pipe.; Bill Cabral - Corn crop damage 15'x15'
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx. 18'' of tar wrap to inspect pipe. Part of wrap gone from sides of pipe. Water under rest of wrap. Wrap not bonded.; Pasture no crop damage.
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx 18'' of tar wrap to inspect pipe. Part of wrap gone from sides of pipe. Water underneath part of wrap. Wrap wasn't...; Pasture no crop damage.
|  | 131 |  | 10 | [14 empty] | Removed approx 18'' of tar wrap to inspect pipe. Part of wrap gone from sides of main. Water underneath rest of wrap. Wrap not bonded to pipe.; Pasture no crop damage.
|  | 131 |  | 10 | [14 empty] | Removed approx. 18'' of tar wrap to insp. pipe. Part of wrap gone from sides. Water underneath rest of wrap. Wrap not bonded to pipe.; Pasture no crop damage.
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx. 18'' of tar wrap to inspect pipe. Wrap half gone from pipe on top. Part of wrap no bonded to pipe with water underneath wrap.
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Wrap on sides of main half gone. Rest of wrap no bonded to pipe with water between wrap & pipe.; Not planted.
|  | 131 |  | 10 | [14 empty] | This area flooded
|  |  |  | 10 | [14 empty] | Flooded
|  |  |  | 10 | [14 empty] | Flooded
|  |  |  | 10 | [14 empty] | Flooded
|  |  |  | 10 | [14 empty] | Flooded
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx. 18'' of tar wrap to inspect pipe. Wrap not bonded to pipes. No signs of water.; No crop damage.
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx. 18'' of wrap in main. Detach to inspect pipe wrap half gone. This point 3' less than sta marked above;. No crop damage
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx. 18'' of tar wrap to insp. pipe. Wrap not bonded to pipe. water under wrap.; Corn damage 20'x20'
|  | 131 |  | 10 | [11 empty] | Other Plastic |  |  | Removed approx. 18'' of tar wrap to insp. pipe. Wrap not bonded to pipe on sides. Water under wrap or bottom pited bad.; Corn Damage 20' x20'
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx. 18'' of tar wrap to insp. pipe. Wrap is not broken but not bonded to main good.; Corn damage 20'x20'
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx. 18'' of tar wrap to insp. pipe. Wrap not bonded to main. Water under wrap.; Safflower damage 20'x20'
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx. 18'' of tar wrap to inspt. pipe. Wrap not bonded to pipe. Water under wrap.; Safflower 20'x20'
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx. 18'' of tar wrap to insp. pipe. Wrap not flooded to pipe. Water under wrap.; Safflower 20'x20'
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx. 18'' of tar wrap to insp. pipe. Wrap not bonded to pipe. Water under wrap.; Safflower 25'x25'
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx. 18'' of tar wrap to inspect pipe. Wrap not bonded to pipe. Water under wrap. Wrap not broken. ;15'x15' safflower damage.
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed approx. 18'' of tar wrap to insp. pipe. Wrap not bonded. Water under wrap. Wrap not broken.; 15'x15' safflower damage
|  | 131 |  | 15 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inspect pipe. Wrap not bonded. Water under wrap, wrap not broken.; 15'x15' safflower damage.
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inspect pipe. Wrap not bonded. Water under wrap. Wrap not broken.; 15' x 15' Satfflower damage
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' tar wrap to inspect pipe. Wrap not bonded to pipe. Wrap is not broken.; 15'x15' Safflower damage
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 19'' tar wrap to inspect pipe. Wrap not bonded to pipe. Water under wrap.; 15'x15' Safflower damage
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inspect pipe. Wrap not bonded to pipe. Water under wrap.; 15'x15' safflower damage.
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inspect pipe. Wrap not bonded to main + half off main. Water under wrap that left on pipe.; 15'x15' safflower damage.
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inspect pipe. Wrap not bonded to pipe. Water underneath wrap.; 15' x 15' Safflower Damage
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to insp. pipe. Wrap not bonded to main. Wrap falling off main with dirt. Rewraped about 7'', Signs of water.; 15'x15' safflower damage.
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inspect pipe. Wrap not bonded to pipe. Water under wrap.; 15'x15' safflower.
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inspect pipe. Wrap not bonded to pipe with water under wrap. Heavy scaley rust.; 15'x15' safflower damage.
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inspect pipe. Wrap not bonded to pipes. Water under wrao, Heavy scaly rust.; 15'x15' safflower damage.
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to inspect pipe. Wrap not bonded to main. water under wrap. Heavy scaly rust. 15'x15' safflower damage.
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to insp. pipe. Wrap not bonded to pipe. Water under wrap.; 15'x15' safflower damage.
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Removed 18'' of tar wrap to insp. pipe. Wrap not bonded to pipe. Water under wrap. Scaley rust.; Grain has been harvested.
|  |  |  | 10 | [11 empty] | Steel |  |  | removed 18'' of tar wrap to insp. pipe. Wrap not bonded to pipe. No water.; Grain has been harvested.
|  | 131 |  | 10 | [11 empty] | Steel |  |  | Remove 18'' of tar wrap to insp. pipe. Wrap not bonded to pipe. Broken off easy...; Grain has been harvested.
|  | 196 |  | 12 | [11 empty] | Steel |  |  | Tar wrap on dog-leg. No water under wrap. Primer good. No crop damage.
|  | 196 |  | 12 | [11 empty] | Steel |  |  | No crop damage.
|  |  |  | 12 | [11 empty] | Steel |  |  | Near irrigation ditch. No crop damage.
|  |  |  | 12 | [11 empty] | Steel |  |  | No crop damage.
|  | 196 |  | 12 | [11 empty] | Steel |  |  | No crop damage.
|  | 196 |  | 12 | [11 empty] | Steel |  |  | No crop damage
|  | 196 |  | 12 | [11 empty] | Steel |  |  | No crop damage
|  | 196 |  | 12 | [11 empty] | Steel |  |  | Wrap & primer in excellent condition. No crop damage.
|  | 196 |  | 12 | [11 empty] | Steel |  |  | Wrap has been damaged. Area approx. 6'' x 8'' on top of pipe. Heavy scale limited to area damaged. Pipe exposed 10' each way from damaged area.
|  | 196 |  | 12 | [11 empty] | Steel
|  | 196 |  | 12 | [11 empty] | Steel
|  | 196 |  | 12 | [11 empty] | Steel
|  | 196 |  | 12 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel |  | Rio Vista | Removed approx/ 18" of ... wrap to inspect pipe. Wrap bonded tp pipe good
[18 empty] | Rio Vista | Removed approx. 18'' of tar wrap. Wrap not bonded to pipe. Water underneath wrap.
|  | 131 |  | 12 | [13 empty] | Rio Vista | Removed 18'' tar wrap to inspect pipe. Wrap bonded to pipe.
|  | 131 |  | 12 | [11 empty] | Steel |  | Rio Vista | Removed 18'' tar wrap to inspect pipe. Wrap bonded to pipe good.
|  | 131 |  | 10 | [11 empty] | Steel |  | Rio Vista | Removed 18'' of tar wrap to inspect pipe. Water under wrap. Wrap not bonded to pipe.
|  | 196 |  | 4 | [13 empty] | Rio Vista | Removed 18'' xtra cost wrap to inspect pipe. Wrap bonded to pipe like new.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to insp. pipe. Wrap bonded to pipe good.
|  | 131 |  | 10 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to insp. pipe. Wrap not bonded to pipe good. No signs of water.
|  | 131 |  | 12 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to inspect pipe. Wrap bonded to pipe good.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to inspect pipe. Wrap bonded to pipe good.
|  | 131 |  | 10 | [11 empty] | Steel |  | Rio Vista | Removed approx 18'' of tar wrap to inspect pipe. Wrap not bonded to pipe. Water underneath wrap.
|  | 131 |  | 12 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to inspect pipe. Wrap bonded to pipe good.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to inspect pipe. Wrap bonded to pipe good.
|  | 131 |  | 10 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' tar wrap to inspect pipe. Wrap not bonded to pipe. Water underneath wrap
|  | 131 |  | 12 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap. Wrap bonded to pipe good.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to inspect pipe. Wrap bonded to pipe good. Installed E.T.S. good.
|  | 131 |  | 10 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to inspect pipe. Wrap bonded to pipe good. Installed ETS leach
|  | 131 |  | 12 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to inspect pipe. Wrap bonded to pipe good. Installed E.T.S. leach.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to inspect pipe. Wrap bonded to pipe good.
|  | 131 |  | 10 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to inspect pipe. Wrap cracked & loose on main.
|  | 131 |  | 12 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' tor wrap to inspect pipe. Wrap bonded to pipe good.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Removed about 18'' of tar wrap to inspect pipe. Wrap bonded to pipe good.
|  | 131 |  | 10 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to inspect pipe. Wrap was bonded to main good.
|  | 131 |  | 10 | [11 empty] | Steel |  | Rio Vista | Removed 18'' tar wrap to inspect pipe wrap. Bonded to pipe good.
|  | 131 |  | 6 | [11 empty] | Steel |  | Rio Vista | Removed 18'' tar wrap to inspect pipe. Wrap bonded to main.
|  | 131 |  | 10 | [11 empty] | Steel |  | Rio Vista | Removed 18'' of tar wrap to inspect main. Wrap wrinkled
|  | 131 |  | 12 | [11 empty] | Steel |  | Rio Vista | Removed 18'' of tar wrap to inspect pipe. Wrap bonded to main.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap. Wrap bonded to main.
|  | 131 |  | 10 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap from main. Wrap bonded to main.
|  | 131 |  | 12 | [11 empty] | Steel |  | Rio Vista | Removed about 18'' of tar wrap. Wrap bonded to main
|  | 131 |  | 10 | [11 empty] | Steel |  | Rio Vista | Removed 18'' of tar wrap.
|  | 131 |  | 12 | [11 empty] | Steel |  |  | Removed approx. 18'' of tar wrap.
|  | 195 |  | 4 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of xtra coat wrap to inspect pipe wrap. Bonded to pipe good.
|  | 131 |  | 10 | [13 empty] | Rio Vista | Removed approx. 18'' of tar wrap. Wrap not bonded to pipe. Water underneath wrap.
|  | 131 |  | 12 | [13 empty] | Rio Vista | Removed 18" tar wrap to inspect pipe. wrap bonded to pipe. ; ; tar wrap to inspect pipe. Wrap bonded to pipe
|  | 131 |  | 12 | [11 empty] | Steel |  | Rio Vista | Removed 18'' tar wrap to inspect pipe. Wrap bonded to pipe good.
|  | 131 |  | 10 | [11 empty] | Steel |  | Rio Vista | Removed 18'' of tar wrap to inspect pipe. Water under wrap. Wrap not bonded to pipe.
|  | 196 |  | 4 | [13 empty] | Rio Vista | Removed 18'' xtra coat wrap to inspect pipe. Wrap bonded to pipe like new.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to insp. pipe. Wrap bonded to pipe good.
|  | 131 |  | 10 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to insp. pipe. Wrap not bonded to pipe good. No signs of water.
|  | 131 |  | 12 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to inspect pipe. Wrap bonded to pipe good.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to inspect pipe. Wrap bonded to pipe good.
|  | 131 |  | 10 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to inspect pipe. Wrap not bonded to pipe. Water underneath wrap.
|  | 131 |  | 12 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to inspect pipe. Wrap binded to pipe good.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to inspect pipe. Wrap bonded to pipe good.
|  | 131 |  | 10 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' tar wrap to inspect pipe. Wrap not bonded to pipe. Water underneath wrap.
|  | 131 |  | 12 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap. Wrap bonded to pipe good.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to inspect pipe. Wrap bonded to pipe good. Installed E.T.S. lead
|  | 131 |  | 10 | [11 empty] | Steel |  | Rio Vista | Removed approx 18'' of tar wrap to inspect pipe. Wrap bonded to pipe good. Installed ETS lead
|  | 131 |  | 12 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to inspect pipe. Wrap bonded to pipe good. installed E.T.S. Leads
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to inspect pipe. Wrap bonded to pipe good.
|  | 131 |  | 10 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to inspect pipe. Wrap cracked & loose on mains.
|  | 131 |  | 12 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' tar wrap to inspect pipe. Wrap bonded to pipe good.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Removed about 18'' of tar wrap to inspect pipe. Wrap bonded to pipe good.
|  | 131 |  | 10 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap to inspect pipe. Wrap was bonded to main good.
|  | 131 |  | 12 | [11 empty] | Steel |  | Rio Vista | Removed 18'' tar wrap to inspect pipe. Wrap bonded to pipe good.
|  | 131 |  | 6 | [11 empty] | Steel |  | Rio Vista | Removed 18'' tar wrap to inspect pipe. Wrap bonded to main.
|  | 131 |  | 12 | [11 empty] | Steel |  | Rio Vista | Removed 18'' of tar wrap to inspect pipe. Wrap bonded to main.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap. Wrap bonded to main.
|  | 131 |  | 10 | [11 empty] | Steel |  | Rio Vista | Removed approx. 18'' of tar wrap from main. Wrap bonded to main.
|  | 131 |  | 12 | [11 empty] | Steel |  | Rio Vista | Removed about 18'' of tar wrap. Wrap bonded to main.
|  | 131 |  | 10 | [11 empty] | Steel |  | Rio Vista | Removed 18'' of tar wrap.
|  | 131 |  | 12 | [11 empty] | Steel |  |  | removed approx. 18'' of tar wrap.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | No water. No crop damage
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | No water under wrap. No crop damage.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No crop damage.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No crop damage.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | No crop damage. Water under wrap.
48 |  |  |  | 4 | Gathering | [6 empty] | 1972-08-23 |  |  |  | Steel |  |  | Shut down
48 |  |  |  | 4 | Gathering | [6 empty] | 1971-05-15 |  |  |  | Steel
48 |  |  |  | 8 | Gathering | [6 empty] | 1972-05-15 |  |  |  | Steel
48 |  |  |  | 3 | Gathering | [6 empty] | 1972-08-31 |  |  |  | Steel
48 |  |  |  | 10 | Transmission | [6 empty] | 1972-10-25 |  |  |  | Steel |  |  | Tie-In
48 |  |  |  | 8 | Transmission | [6 empty] | 1973-05-03 |  |  |  | Steel
48 |  |  |  | 10 | Transmission | [6 empty] | 1973-05-03 |  |  |  | Steel
48 |  |  |  | 4 | Gathering | [6 empty] | 1978-10-16 |  |  |  | Steel |  |  | Shut down
52 |  |  |  | 4 | Gathering | [6 empty] | 1980-05-14 |  |  |  | Steel |  |  | Shut down; None
52 |  |  |  | 3 | Gathering | [6 empty] | 1980-05-14 |  |  |  | Steel |  |  | Shut down; Nonw
52 |  |  |  | 6 | Gathering | [6 empty] | 1980-05-07 |  |  |  | Steel |  |  | Shut down; None
52 |  |  |  | 8 | Gathering | [6 empty] | 1980-05-06 |  |  |  | Steel |  |  | Shut Down; None
52 |  |  |  | 4 | [7 empty] | 1980-09-04 |  |  |  | Steel |  |  | Shut down; None
52 |  |  |  | 3 | Gathering | [6 empty] | 1980-09-04 |  |  |  | Steel |  |  | Shut down; None
52 |  |  |  | 4 | Gathering | [6 empty] | 1980-09-04 |  |  |  | Steel |  |  | Shut down; None
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | No water. No crop damage.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | No water under wrap. No crop damage
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No crop damage
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | No crop damage. Water under wrap.
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wheat crop damage 22x20. No water under wrap. Wrap is tight on main.
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Install 32 LB anode. Wheat crop damage 23x19. Wrap is scoging. No water under wrap
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wheat crop damage 22x16. No water under wrap, wrap is scaging
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wrap tight on pipe. No water under wrap. Wheat damage 16'x22
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wrap tight on pipe. No water under wrap. Installed anode. What damage - 22'x24'
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wrap is loose on pipe. no water under wrap. Installed ETS leads. Wheat damage 10'x10'
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wrap loose & water underneath. Installed anode. Wheat damage 18'x29' - got stuck.
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wrap loose & water underneath. Scaley rust. no crop damage.
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wrap loose & water under wrap. No crop damage. Installed anode 32#
|  | 195 |  | 6 | [11 empty] | Steel |  |  | No crop damage. No water in wrap.
|  | 195 |  | 6 | [11 empty] | Steel |  |  | No crop damage. No water in wrap. Installed 32 LB anode.
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Water under wrap. No crop damage.
|  | 195 |  | 4 | [11 empty] | Steel |  |  | Wrap is tight on main. No crop damage. 4'' line no paralling Line 195
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Installed a 32 LB Anode. No crop damage.
|  | 195 |  | 4 | [11 empty] | Steel |  |  | 4'' line paralling line 195, installed a 32 lb Anode. No crop damage wrap tight. no water under wrap.
|  | 195 |  | 6 | [11 empty] | Steel |  |  | No crop damage. Wrap has no water under it.
|  | 195 |  | 4 | [11 empty] | Steel |  |  | 4'' is paralling line 195. No crop damage.
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Install 32 LB Anode. Wrap is tight on main. No crop damage, no water under wrap.
|  | 195 |  | 4 | [11 empty] | Steel |  |  | Install 32 LB Anode. no crop damage. No water under wrap. Wrap tight on main. 4'' line is paralling line 195
|  | 195 |  | 6 | [11 empty] | Steel |  |  | No crop damage. Pitting is about 11:00 o'clock
|  | 195 |  | 4 | [11 empty] | Steel |  |  | No crop damage, 4'' paralling line 195. No water under wrap, wrap tight on main
|  | 195 |  | 6 | [14 empty] | Install 32 LB Anode. Water under wrap, wrap is loose. Clover crop damage 32'x32'x8'x166'
|  | 195 |  | 4 | [11 empty] | Steel |  |  | Install 32 LB Anode, 4'' main paralling Line 195. Clover crop damage. see sheet #22A
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wrap is tight, no water under wrap. Corn crop damage 28'x26'x8'x53'
|  | 195 |  | 4 | [11 empty] | Steel |  |  | 4'' main paralling. crop damage see sheet #23 "A"
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wrap is loose. Water under wrap. Installed a 32 LB Anode. Scaley rust. No crop damage. Pits are about 11:00 o'clock.
|  | 195 |  | 4 | [11 empty] | Steel |  |  | 4'' paralling line 195. Install 32 LB Anode, no crop damage.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | No water. No crop damage
|  |  |  | 6 | [11 empty] | Steel |  | Rio Vista | No water under wrap. No crop damage.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No crop damage.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No crop damage
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | No crop damage. Water under wrap
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wheat crop damage 22x20. No water under wrap, wrap is tight on main.
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Install 32 LB Anode, wheat crop damage 23x19. Wrap is scoging, no water under wrap.
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wheat crop damage 22x16. No water under wrap, wrap is scaging
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wrap tight on pipe. No water under wrap. Wheat damage 16'x22'
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wrap tight on pipe. No water under wrap. Installed Anode. Wheat damage - 22'x24'
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wrap is loose on pipe. No water under wrap. Installed ETS Leads. Wheat damage 10'x10'
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wrap loose & water underneat. Installed Anode. Wheat damage 18'x29'. Got stuck
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wrap loose & water underneath. Scaley rust. No crop damage
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wrap loose & water under wrap. No crop damage. installed Anode 32#
|  | 195 |  | 6 | [11 empty] | Steel |  |  | No crop damage. No water in wrap.
|  | 195 |  | 6 | [11 empty] | Steel |  |  | No crop damage. No water in wrap. Installed 32 LB Anode.
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Water under wrap. No crop damage
|  | 195 |  | 4 | [11 empty] | Steel |  |  | Wrap is tight on main. No crop damage. 4'' line is paralling line 195
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Installed a 32 LB Anode. No crop damage
|  | 195 |  | 4 | [11 empty] | Steel |  |  | 4'' line paralling Line 195, Installed a 32 LB Anode. No crop damage. Wrap tight. No water under wrap.
|  | 195 |  | 6 | [11 empty] | Steel |  |  | No crop damage. Wrap has no water under it.
|  | 195 |  | 4 | [11 empty] | Steel |  |  | 4'' is paralling line 195. No crop damage.
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Install 32 LB Anode, wrap is tight on main. No crop damage, no water under wrap.
|  | 195 |  | 4 | [11 empty] | Steel |  |  | Install 32 LB Anode, no crop damage. No water under wrap, wrap tight on main. 4'' line is paralling line 195
|  | 195 |  | 6 | [11 empty] | Steel |  |  | No crop damage. Piting is about 11:00 O'Clock
|  | 195 |  | 4 | [7 empty] | 1980-02-12 |  |  |  | Steel |  |  | No crop damage, 4'' paralling line 195. No water under wrap, wrap tight on main.
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Install 32 LB Anode, water under wrap. Wrap is loose. Corn crop damage 32'x32'x8'166'
|  | 195 |  | 4 | [11 empty] | Steel |  |  | Install 32 LB Anode, 4'' main paralling line 195. (Corn crop damage. See sheet #22 "A")
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wrap is tight, no water under wrap. Corn crop damage 28'x26'x8'x53'
|  | 195 |  | 4 | [11 empty] | Steel |  |  | 4'' main paralling, crop damage. See sheet #23 "A"
|  | 195 |  | 6 | [11 empty] | Steel |  |  | Wrap is loose, water under wrap. Installed a 32 LB Anode, scaley rust. No crop damage. Pits are about 11:00 O'Clock
|  | 195 |  | 4 | [11 empty] | Steel |  |  | 4'' Paralling line 195. Install 32 LB Anode, no crop damage.
52 |  |  |  | 12 | Gathering | [6 empty] | 1980-06-03 |  |  |  | Steel |  |  | Mueller valve tee with 3/4'' pipe to center of 12'' line. To pick up dry gas from center of 12'' line.
48 |  |  |  | 4 | Gathering | [6 empty] | 1972-12-28 |  |  |  | Steel/Wrought Iron
|  | 195 |  | 4 | [11 empty] | Steel |  |  | Tar wrapped wrap bonded good to pipe. no water. Started #1 hole at weld fee #8
|  |  |  | 4 | [11 empty] | Steel |  |  | Tar wrap. Wrap bonded good on pipe. no water.
|  | 195 |  | 4 | [11 empty] | Steel |  |  | Plastic wrap. Wrap bonded to pipe good - no water. Tirin paint.
|  |  |  | 6 | [11 empty] | Steel |  |  | Tar wrap. Wrap bonded good to pipe.
|  |  |  | 6 | [11 empty] | Steel |  |  | Tar wrap. Wrap bonded good to pipe - no water.
|  |  |  | 04.00 or 05.00 | [11 empty] | Steel |  |  | Tar wrap. Wrap bonded good to pipe. No water under wrap.
|  |  |  | 04.00 or 05.00 | [11 empty] | Steel |  |  | Tar wrap. Wrap bonded good to main. No water under wrap.
|  |  |  | 04.00 or 05.00 | [11 empty] | Steel |  |  | Tar wrap. Wrap bonded good to pipe. No water under wrap. Started hole #1 at ... Blvd/
|  |  |  | 8 | [11 empty] | Steel |  |  | Tar wrap. Wrap not bonded to pipe. Water under wrap. Wrap very Brittle. Light Pitting not deep enough to guage.
|  |  |  | 8 | [11 empty] | Steel |  |  | Tar wrap. Wrap not bonded to pipe. Water under wrap. Heavy rust on bottom pipe. Light pitting not enough to guage.
|  |  |  | 8 | [11 empty] | Steel |  |  | Tar wrap. Wrap not bonded to pipe good. Heavy rust on bottom of pipe. water under wrap. Light pitting not enough to guage.
|  |  |  | 8 | [11 empty] | Steel |  |  | Tar wrap. Wrap not bonded to pipe good. Water under wrap. Heavy rust on bottom of pipe. Found askeu.
|  |  |  | 8 | [11 empty] | Steel |  |  | Leak
|  |  |  | 8 | [11 empty] | Steel |  |  | Tar wrap. Wrap not bonded to pipe. Water under wrap. Light rust on bottom of pipe.
|  | 195 |  | 8 | [11 empty] | Steel |  |  | Heavy rust & corrosion. Last hole approx 51' from valve. 66 direction N.W.
| 85-57003-1 |  |  | 12 | [7 empty] | 1985-07-29 | 1985-10-17 |  |  | Steel |  |  | Install 54'' of 12'' pipe. 330 unit. API 5 LX GR X-42 ERW. See DWG. Repaired on GM4469425
52 | 85-90003-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion | Internal | 1985-11-29 | 1986-01-16 | Replace Pipe and/or Service |  | Steel |  |  | Replace 20.23' of 10'', API-5LX GR. X42 FRW .281 W.T.
|  |  |  | 10 | [11 empty] | Steel
52 |  |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion | Internal | 1985-12-17 |  | Replace Pipe and/or Service |  | Steel
52 |  |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion | Internal | 1985-12-17 |  | Replace Pipe and/or Service |  | Steel
52 |  |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion | Internal | 1985-12-17 |  | Replace Pipe and/or Service |  | Steel
52 |  |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion | Internal | 1985-12-17 |  | Replace Pipe and/or Service |  | Steel
52 |  |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion | Internal | 1985-12-13 |  | Replace Pipe and/or Service |  | Steel
52 |  |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion | Internal | 1985-12-13 |  | Replace Pipe and/or Service |  | Steel
52 |  |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion | Internal | 1985-12-16 |  | Replace Pipe and/or Service |  | Steel
52 |  |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion | Internal | 1985-12-16 |  | Replace Pipe and/or Service |  | Steel
52 |  |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion | Internal | 1985-12-11 |  | Replace Pipe and/or Service |  | Steel
52 |  |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion | Internal | 1985-12-20 |  | Replace Pipe and/or Service |  | Steel
52 |  |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion | Internal | 1985-12-11 |  | Replace Pipe and/or Service |  | Steel
52 |  |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion | Internal | 1985-12-11 |  | Replace Pipe and/or Service |  | Steel
6.625
6.625
6.625
|  |  |  | 8.625 | [11 empty] | Steel
|  |  |  | 6.625 | [11 empty] | Steel
|  |  |  | 8 | [11 empty] | Stee
|  |  |  | 6.625 | [11 empty] | Steel
|  |  |  | 10.75 | [11 empty] | Steel
|  |  |  | 10.75 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel |  | S/O DIxon | Retest 4'' stl. C Recapitalize pipe & gas well
|  |  |  | 8.625 | [11 empty] | Steel
|  |  |  | 8 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 8.625 | [11 empty] | Steel
|  |  |  | 10 | [11 empty] | Steel
|  |  |  | 6.625 | [11 empty] | Steel
|  |  |  | 6.625 | [11 empty] | Steel
|  |  |  | 8 | [11 empty] | Steel
|  |  |  | 12 | [11 empty] | Steel |  |  | Wrap tight & well bonded. Pipe looked good. No water. Rust. Pits
| 84-57000-1 | [10 empty] | 1984-01-25
52 | 84-57000-1 |  |  | 8 | Gathering | [6 empty] | 1984-01-25 |  |  |  | Steel
|  | 143 |  | 6 | [11 empty] | Steel |  | Dixon | Refs to loc. #1 on MAP
|  | 143 |  | 6 | [11 empty] | Steel |  | Dixon | Ref to loc. #2
|  | 143 |  | 6 | [11 empty] | Steel |  | Dixon | Ref too loc. #3 of map
|  |  |  | 3.5 | [11 empty] | Steel |  | Rio Vista
|  |  |  | 3.5 | [11 empty] | Steel |  | Rio Vista
|  |  |  | 6.625 | [11 empty] | Steel |  | Rio Vista/South end
|  |  |  | 6.625 | [11 empty] | Steel |  | Rio Vista/North End
|  |  |  | 6.625 | [11 empty] | Steel |  | Rio Vista/South End
|  | 195 |  | 8.625 | [11 empty] | Steel |  | Rio Vista | Transferred recl. board gas well to 12'' 30# system
|  |  |  | 3 | [11 empty] | Steel |  | Dixon | Cut & remove 27'' to install 3'' tee.
|  |  |  | 10.75 | [11 empty] | Steel
|  |  |  | 10.75 | [11 empty] | Steel |  |  | Abandon main filled with 5 slum; 3/8 call grout
|  |  |  | 10.75 | [11 empty] | Steel |  |  | Abandon river crossing
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 2 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
4
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel |  | Rio Vista
|  |  |  | 8 | [11 empty] | Steel |  | Rio Vista
|  |  |  | 10 | [11 empty] | Steel |  | Rio Vista
6
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 8 | [11 empty] | Steel |  | Rio Vista
|  |  |  | 4 | [11 empty] | Steel |  | Rio Vista
|  |  |  | 8 | [11 empty] | Steel |  | Rio Vista
|  |  |  | 8 | [11 empty] | Steel |  | Rio Vista
|  | 168 |  | 8 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1989-08-06 |  | Replace Pipe |  | Steel |  |  | Note. This section of line 168 has had leaks in various loc.; Cut in 15'4" Section of new 6" 156" Retest.
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 08.00 & 06.00 | [7 empty] | 1989-07-28 |  |  |  | Steel |  | Isleton | Note: This section has had repair due to I.Corr. Valve #13 to Dehyd.
|  |  |  | 08.00 & 06.00 | [7 empty] | 1989-07-24 |  |  |  | Steel |  | Isleton
|  |  |  | 08.00 & 04.00 | [7 empty] | 1989-07-26 |  |  |  | Steel |  | Isleton
|  |  |  | 4 | [7 empty] | 1989-08-01 |  |  |  | Steel |  | Isleton
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 2 | [11 empty] | Steel
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 6 | [7 empty] | 1989-08-01 |  |  |  | Steel |  | Isleton
|  |  |  | 08.00 & 04.00 | [7 empty] | 1989-07-28 |  |  |  | Steel |  | Isleton
|  |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1989-08-01 | 1989-08-01 | Replace Pipe |  | Steel |  | Isleton | Bell Hole cut in 26" Hydro test x-key wrap @ Backfill
|  |  |  | 6 | [7 empty] | 1989-07-28 |  |  |  | Steel |  | Iselton
|  |  |  | 4 | [7 empty] | 1989-07-24 |  |  |  | Steel |  | Isleton
|  |  |  | 4 | [7 empty] | 1989-07-22 |  |  |  | Steel |  | Isleton
|  | 168 |  | 4 | [11 empty] | Steel |  |  | Corrison Inhibiliter Internal
|  | 168 |  | 4 | [11 empty] | Steel |  |  | Corrison Inhibitor Internal
|  | 168 |  | 6 | [11 empty] | Steel |  |  | Corrison Inhibitor Internal
|  | 168 |  | 8 | [11 empty] | Steel |  |  | Corrison inhibiter internal
|  | 168 |  | 8 | [11 empty] | Steel |  |  | Corrison inhibitor internal
|  | 168 |  | 8 | [11 empty] | Steel |  |  | Corrison Inhibitor Internal
|  | 168 |  | 8 | [11 empty] | Steel |  |  | Corrison Inhibitor Internal
|  |  |  | 6 | [11 empty] | Steel |  |  | Corrison Inhibitor Internal
|  |  |  | 8 | [11 empty] | Steel |  |  | Corrison Inihibitor Internal
|  |  |  | 4 | [11 empty] | Steel |  |  | Corrison inhibitor Internal
|  |  |  | 8 | [11 empty] | Steel |  |  | Corrison Inhibitor, sand, & water. Internal - test failed at 801# 8'' main abandon & replaced with 3'' man W045011-A
|  | 168 |  | 8 | [11 empty] | Steel |  | Isleton
|  |  |  | 6 | [11 empty] | Steel
|  | 168 |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1989-08-06 |  | Replace Pipe |  | Steel |  | Isleton | Cut in 15'4" section of new 6" 156" retest; Note: this section of line 168 has had leaks in various loc.
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 08.00 & 06.00 | [7 empty] | 1989-07-28 |  |  |  | Steel |  | Isleton | Note: This section has had repaire due to I. Corr. Valve #13 to dehyd.
|  |  |  | 08.00 & 06.00 | [7 empty] | 1989-07-24 |  |  |  | Steel |  | Isleton
|  |  |  | 08.00 - 04.00 | [7 empty] | 1989-07-26 |  |  |  | Steel |  | Isleton
|  | 168 |  | 4 | [7 empty] | 1989-08-01 |  |  |  | Steel |  | Iselton
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 2 | [11 empty] | Steel
|  |  |  | 3 | [11 empty] | Steel
|  | 168 |  | 6 | [7 empty] | 1989-08-01 |  |  |  | Steel |  | Iselton
|  | 168 |  | 08.00 & 04.00 | [7 empty] | 1989-07-28 |  |  |  | Steel |  | Iselton
|  |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1989-08-01 | 1989-08-01 | Replace Pipe |  | Steel |  | Isleton | Bell hole cut in 26" can hydro test x-key wrap @ backfill
|  |  |  | 6 | [7 empty] | 1989-07-28 |  |  |  | Steel |  | Iselton
|  | 168 |  | 4 | [7 empty] | 1989-07-24 |  |  |  | Steel |  | Isleton
|  |  |  | 4 | [7 empty] | 1989-07-27 |  |  |  | Steel |  | Isleton
|  | 168 |  | 4 | [11 empty] | Steel
|  | 168 |  | 4 | [11 empty] | Steel |  |  | Corrison Inhibiter Internal
|  | 168 |  | 6 | [11 empty] | Steel |  |  | Corrison Inhibiter Internal
|  | 168 |  | 8 | [11 empty] | Steel |  |  | Corrison inhibitor internal
|  | 168 |  | 8 | [11 empty] | Steel |  |  | Corrison inhibiter internal
|  | 168 |  | 8 | [11 empty] | Steel |  |  | Corrison Inhibiter Internal
|  | 168 |  | 8 | [11 empty] | Steel |  |  | Corrison Inhibitor Internal
|  |  |  | 6 | [11 empty] | Steel |  |  | Corrison Inhibitor Internal
|  |  |  | 8 | [11 empty] | Steel |  |  | Corrison Inhibitor Internal
|  |  |  | 4 | [11 empty] | Steel |  |  | Corrison Inhibitor Internal
|  |  |  | 3.5 | [11 empty] | Steel
|  |  |  | 8.625 | [11 empty] | Steel |  |  | Replaced pipe due to internal pitting
|  |  |  | 8.625 | [11 empty] | Steel |  |  | 15' of .322 wt 8'' replaced
|  |  |  | 12.75 | [11 empty] | Steel
|  |  |  | 12.75 | [7 empty] | 1990-04-24 |  |  |  | Steel
|  |  |  | 3.5 | [7 empty] | 1990-04-19 |  |  |  | Steel
|  |  |  | 16 | [11 empty] | Steel
|  | 195 |  | 8.625 | [11 empty] | Steel
|  | 195 |  | 16.75 | [11 empty] | Steel
|  | 143 |  | 6 | [7 empty] | 1989-09-07 |  |  |  | Steel |  | Dixon
|  |  |  | 6 | [7 empty] | 1989-09-06 |  |  |  | Steel |  | Dixon
|  | 143 |  | 6 | [7 empty] | 1989-09-07 |  |  |  | Steel |  | Dixon
|  | 143 |  | 4 | [7 empty] | 1989-09-07 |  |  |  | Steel |  | Dixon
|  |  |  | 6 | [11 empty] | Steel |  | Dixon
|  |  |  | 6 | [11 empty] | Steel |  | Dixon
|  |  |  | 6 | [11 empty] | Steel |  | Dixon
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel |  | Dixon
|  |  |  | 6 | [11 empty] | Steel |  | Dixon
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 10.75 | [11 empty] | Steel |  | Rio Vista
|  |  |  | 10.75 | [11 empty] | Steel |  | Rio Vista
|  |  |  | 3.5 | [11 empty] | Steel |  | Rio Vista | Cut out 16'' lc.
|  |  |  | 8.625 | [11 empty] | Steel |  | Rio Vista
|  |  |  | 4.5 | [11 empty] | Steel |  | Rio Vista | Cut 4'' from 8'' & caped for testing 8''
|  |  |  | 3.5 | [11 empty] | Steel |  | Rio Vista | Cut out 10'' AT PA 20; Cut out 10'' AT PA 38
|  |  |  | 6.625 | [11 empty] | Steel |  | Rio Vista | Cut out 30" Pc. AT U-113; Cut out 14" Pc ay PA-26 G/W
|  |  |  | 4.5 | [11 empty] | Steel |  | Rio Vista | Four tie-in cans are .156w Pipe
|  |  |  | 6.625 | [11 empty] | Steel |  | Rio Vista | Cut out 26'' tie point - cut out 30'' riser
|  |  |  | 6.625 | [11 empty] | Steel |  | Rio Vista | Cut out 1- 30'' Pc.; Cut out 1- 24'' Pc.
|  |  |  | 6.625 | [7 empty] | 1989-09-12 |  |  |  | Steel |  | Rio Vista | Cut 1- .30'' Pc.; Cut 1- 34'' Pc.; unable to test riser loc. due to tanks on replace
|  | 144 |  | 10 | [11 empty] | Steel |  | Dixon
|  | 144 |  | 10 | [11 empty] | Steel |  | Dixon
|  | 144 |  | 3 | [11 empty] | Steel |  | Dixon
|  | 144 |  | 6 | [11 empty] | Steel |  | Dixon
|  | 144 & 143 |  | 06.00 & 10.00 | [11 empty] | Steel |  | Dixon
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 04.00 & 06.00 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 04.00 & 06.00 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Other
|  |  |  | 6 | [11 empty] | Other
|  |  |  | 6 | [11 empty] | Other
|  |  |  | 6 | [11 empty] | Other
|  |  |  | 6 | [11 empty] | Other
|  |  |  | 6 | [11 empty] | Other
|  |  |  | 6 | [11 empty] | Other
|  |  |  | 6 | [11 empty] | Other
|  |  |  | 6 | [11 empty] | Other
|  |  |  | 3 | [11 empty] | Steel
|  | 182 |  | 8.625 | [11 empty] | Steel |  | Rio Vista
|  | 182 |  | 8.625 | [11 empty] | Steel |  | Rio Vista
|  | 182 |  | 8.625 | [11 empty] | Steel |  | Rio Vista
|  |  |  | 8.625 | [11 empty] | Steel
|  |  |  | 8.625 | [11 empty] | Steel
|  |  |  | 8.625 | [11 empty] | Steel
|  | 182 |  | 10.75 | [11 empty] | Steel
|  | 182 |  | 10.75 | [11 empty] | Steel
|  | 182 |  | 10.75 | [11 empty] | Steel
|  | 182 |  | 10.75 | [11 empty] | Steel
|  |  |  | 8.625 | [11 empty] | Steel
|  |  |  | 8.625 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  | 200 |  | 12
|  | 200 |  | 6
|  | 200 |  | 6
|  | 200 |  | 6
|  | 200 |  | 4
|  | 200 |  | 4
|  | 200 |  | 12
|  | 200 |  | 4
|  | 200 |  | 12
|  |  |  | 8.625 | [11 empty] | Steel |  | Rio Vista
|  |  |  | 6.625 | [11 empty] | Steel
|  |  |  | 8.625 | [11 empty] | Steel
|  |  |  | 12.75 | [11 empty] | Steel
|  |  |  | 6.625 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 6.625 | [11 empty] | Steel
|  |  |  | 6.625 | [11 empty] | Steel
|  | 200 |  | 12.75 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
6.625
6.625
12.75
12.75
|  |  |  | 10 | [7 empty] | 1990-05-07 |  |  |  | Steel |  | Iselton
|  |  |  | 12.75 | [11 empty] | Steel
|  |  |  | 12.75 | [11 empty] | Steel
|  |  |  | 3 | [7 empty] | 1990-04-19 |  |  |  | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 4.5 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 1990-04-11 | 1990-04-12 | Replace Pipe |  | Steel |  |  | Replaced 37'', using API 5L GRB ERW .156'' WT.
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 4.5 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 1990-04-11 | 1990-04-12 | Replace Pipe |  | Steel |  |  | Replaced 37'', using API 5L GRB ERW .156'' WJ.
|  |  |  | 8.625 | [11 empty] | Steel |  |  | Welded side tap no ipteccal. inspect or testing
|  |  |  | 6.625 | [11 empty] | Steel
|  |  |  | 8 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 8 | [11 empty] | Steel
|  |  |  | 8 | [11 empty] | Steel
|  |  |  | 8.625 | [11 empty] | Steel |  |  | Replaced pipe due to internal pitting
|  |  |  | 8.625 | [7 empty] | 1990-05-18 |  |  |  | Steel |  |  | 15' of .322 wt 8'' replaced
|  |  |  | 12.75 | [11 empty] | Steel
|  |  |  | 12.75 | [11 empty] | Steel
|  |  |  | 12.75 | [7 empty] | 1990-04-24 |  |  |  | Steel
|  |  |  | 3.5 | [11 empty] | Steel
|  |  |  | 16 | [11 empty] | Steel
|  | 195 |  | 8.625 | [11 empty] | Steel
|  |  |  | 16.75 | [11 empty] | Steel
|  |  |  | 16.75 | [7 empty] | 1991-04-24 |  |  |  | Steel
|  | 143 |  | 6 | [7 empty] | 1989-09-07 |  |  |  | Steel |  | Dixon
|  |  |  | 6 | [7 empty] | 1989-09-06 |  |  |  | Steel |  | Dixon
|  | 143 |  | 6 | [7 empty] | 1989-09-07 |  |  |  | Steel |  | Dixon
|  | 143 |  | 4 | [7 empty] | 1989-09-07 |  |  |  | Steel |  | Dixon
|  |  |  | 6 | [7 empty] | 1989-10-27 |  |  |  | Steel |  | Dixon
|  |  |  | 6 | [7 empty] | 1989-10-26 |  |  |  | Steel |  | Dixon
|  |  |  | 6 | [7 empty] | 1989-10-26 |  |  |  | Steel |  | Dixon
|  |  |  | 6 | [7 empty] | 1989-10-25 |  |  |  | Steel
|  |  |  | 4 | [7 empty] | 1989-11-06 |  |  |  | Steel |  | Dixon
|  |  |  | 6 | [7 empty] | 1989-11-06 |  |  |  | Steel |  | Dixon
|  |  |  | 6 | [7 empty] | 1989-11-06 |  |  |  | Steel
|  |  |  | 10.75 | [7 empty] | 1989-09-12 |  |  |  | Steel |  | Rio Vista
|  |  |  | 10.75 | [7 empty] | 1989-09-12 |  |  |  | Steel |  | Rio Vista
|  |  |  | 3.5 | [7 empty] | 1989-09-09 |  |  |  | Steel |  | Rio Vista | Cut out 16'' Ic.
|  |  |  | 8.625 | [7 empty] | 1989-09-13 |  |  |  | Steel |  | Rio Vista
|  |  |  | 4.5 | [7 empty] | 1989-09-13 |  |  |  | Steel |  | Rio Vista | Cut 4'' from 8'' & caped for testing 8''
|  |  |  | 3.5 | [7 empty] | 1989-09-12 |  |  |  | Steel |  | Rio Vista | Cut out 10''Pc. AT PA 20; Cut out 10''Pc. AT PA 38
|  |  |  | 6.625 | [7 empty] | 1989-09-12 |  |  |  | Steel |  | Rio Vista | cut out 30 Pc(?) at V-113, Cut out 14 Pc(?) at PA-26
|  |  |  | 4.5 | [7 empty] | 1989-09-12 |  |  |  | Steel |  | Rio Vista | Four tie in cans are .156w pipe
|  |  |  | 6.625 | [7 empty] | 1989-09-12 |  |  |  | Steel |  | Rio Vista | Cut out 26'' Tie Point - Cut out 30'' Riser -
|  |  |  | 6.625 | [7 empty] | 1989-09-12 |  |  |  | Steel |  | Rio Vista | Cut out 1- 30" pc, cut out 1-34 pc.
|  |  |  | 6.625 | [7 empty] | 1989-09-12 |  |  |  | Steel |  | Rio Vista | Cut 1-.30'' Pc., Cut 1-34'' Pc., unable to test riser loc. due to tanks on pipeline
|  | 144 |  | 10 | [7 empty] | 1989-09-08 |  |  |  | Steel |  | Dixon
|  | 144 |  | 10 | [7 empty] | 1989-09-09 |  |  |  | Steel |  | Dixon
|  | 144 |  | 3 | [7 empty] | 1989-09-14 |  |  |  | Steel |  | Dixon
|  | 144 |  | 6 | [7 empty] | 1989-09-14 |  |  |  | Steel |  | Dixon
|  | 144 & 143 |  | 6 & 10 | [7 empty] | 1989-09-14 |  |  |  | Steel |  | Dixon
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4 & 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4 & 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 3 | [11 empty] | Steel
|  | 182 |  | 8.625 | [11 empty] | Steel |  | Rio Vista;
|  |  |  | 8.625 | [11 empty] | Steel
|  | 182 |  | 8.625 | [11 empty] | Steel
|  |  |  | 8.625 | [11 empty] | Steel
|  |  |  | 8.625 | [11 empty] | Steel
|  |  |  | 8.625 | [11 empty] | Steel
|  | 182 |  | 10.75 | [11 empty] | Steel
|  | 182 |  | 10.75 | [11 empty] | Steel
|  | 182 |  | 10.75 | [11 empty] | Steel
|  | 182 |  | 10.75 | [11 empty] | Steel
|  |  |  | 8.625 | [11 empty] | Steel
|  |  |  | 8.625 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
[18 empty] | Rio Vista | IR 1A GM 4811345; 40' n/e of V-3@ Serpa Junction on 12" Line 200
[18 empty] | Rio Vista | 6" Pipe @ V-7 off 12" -200
[18 empty] | Rio VIsta | IP 3A GM 4811345; 6" Pipe @ V-9 off 12" line 200
[18 empty] | Rio Vista | IR 4A GM 4811345; 6" pipe @ V-10 off 12" Line 200
[18 empty] | Rio Vista | IR 5A GM4811345; 4" Pipe @ V-12 off 12" Line 200
[18 empty] | Rio VIsta | IR 6A GM 4811345; 4" Pipe @ V-14 off 12" line 200
[18 empty] | Rio Vista | IR 7A GM 4811345; 12" Pipe @ V-25 off 12" Line 200
[18 empty] | Rio Vista | IR 8A GM 4811345; 4" Pipe @ V-31 off 12" Line 200
[18 empty] | Rio Vista | IR 9A GM 4811345; 12" Cap @ End of 12" Line 200 @ Marks Station
|  |  |  | 8.625 | [11 empty] | Steel |  | Rio Vista
|  |  |  | 6.625 | [11 empty] | Steel
|  |  |  | 8.625 | [11 empty] | Steel
|  |  |  | 12.75 | [11 empty] | Steel
|  |  |  | 6.625 | [11 empty] | Aldyl A (Tan or Gray)
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 6.625 | [11 empty] | Steel
|  |  |  | 6.625 | [11 empty] | Steel
|  | 200 |  | 12.75 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
GM 4811345
GM 4811345
[18 empty] | Rio Vista | 12 West of V-2; GM 4811345
[18 empty] | Rio Vista | 6' West of V-2 Gm 4811345
|  |  |  | 10 | [11 empty] | Aldyl A (Tan or Gray) |  |  | 4' North of V-4 at Isleton Meter Station; IR#1
|  |  |  | 12.75 | [11 empty] | Steel
|  |  |  | 12.75 | [11 empty] | Steel
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 4.5 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 1990-04-11 | 1990-04-12 | Replace Pipe |  | Steel/Wrought Iron |  |  | Replaced 37", Using API 5L GRB ERW .156 wt
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 4.5 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 1990-04-11 | 1990-04-12 | Replace Pipe |  | Steel/Wrought Iron |  |  | Replaced 37", using API 5K GRB ERW .156wt.
|  |  |  | 3.625 | [11 empty] | Steel |  |  | Welding site tap to inspect or testing
6.625
|  |  |  | 8 | [11 empty] | Wrought Iron
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 8 | [11 empty] | Steel
|  | 199 |  | 8 | [11 empty] | Steel
48 |  |  |  | 10 | Transmission | [6 empty] | 1975-10-19 |  |  |  | Steel/Wrought Iron |  |  | None
|  |  |  | 10 | Transmission | [6 empty] | 1975-10-14 |  |  |  | Steel |  |  | NONE
48 |  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron
48 |  | 195 |  | 3 | Transmission | [6 empty] | 1976-09-07 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1976-06-14 |  |  |  | Steel/Wrought Iron |  |  | None
48 |  |  |  | 6 | Gathering | [6 empty] | 1976-06-14 |  |  |  | Steel/Wrought Iron |  |  | None
48 |  |  |  | 8 | Transmission | [6 empty] | 1977-04-19 |  |  |  | Steel/Wrought Iron |  |  | None
48 |  |  |  | 8 | Transmission | [6 empty] | 1977-04-19 |  |  |  | Steel/Wrought Iron |  |  | None
48 |  |  |  | 8 | Transmission | [6 empty] | 1977-09-16 |  |  |  | Steel/Wrought Iron |  |  | None
48 |  |  |  | 8 | Transmission | [6 empty] | 1977-09-16 |  |  |  | Steel/Wrought Iron |  |  | None
48 |  |  |  | 12 | Transmission | [6 empty] | 1977-09-16 |  |  |  | Steel/Wrought Iron |  |  | None
48 |  |  |  | 12 | Transmission | [6 empty] | 1977-09-16 |  |  |  | Steel/Wrought Iron |  |  | None
| 95-0002-1 | 146 | [9 empty] | 1995-03-15 | [5 empty] | Dixon
| 95-00061-1 | 143 |  | 6.625 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-05-18 | 1995-06-27 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Dixon | Welded in 80' of new pipe to remove bad area with multipe repairs (leak history)
|  |  |  | 8 | [11 empty] | Steel
|  |  |  | 8 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 8 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 3.5 | [11 empty] | Steel/Wrought Iron
|  |  |  | 6.62 | [11 empty] | Steel/Wrought Iron
|  |  |  | 6.62 | [11 empty] | Steel/Wrought Iron
|  |  |  | 6.62 | [11 empty] | Steel/Wrought Iron
|  |  |  | 8.62 | [11 empty] | Steel/Wrought Iron
|  |  |  | 8.62 | [11 empty] | Steel/Wrought Iron
|  | 196 |  | 6.625 | [11 empty] | Steel/Wrought Iron |  |  | Tie in hole @ Jackson well line 196, Removed aprox 6' of .156GM
Steel/Wrought Iron
|  | 400 | 280.24 | [15 empty] | L-400 MP 280.24 Casing replaced and aprox 60 feet striped and re-coated. Light Googes repaired by gringing see attached sheet
|  | 400 | 280.24 | [15 empty] | Casing replaced and aprox. 60 Feet striped and re-coated. Light googes repaired by grinding see attached sheet/
|  | 210B |  | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Dixon area Solano County
|  |  |  | 6.62 | Transmission | [10 empty] | Steel |  |  | Dixon area Solano County
|  |  |  | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Dixon Area Solano County
|  |  |  | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | Dixon | Tie in reactivated 6" Pipe in Denverton valve lot south of North Fence line; Dixon area solano
|  |  |  | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | Dixon | Tie in Reactivated 6" pip in denverton valve lot north of south fence line; Dixon area solano county
|  |  |  | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | Dixon | Dixon area Soloano County
|  |  |  | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | Dixon | 6" Tie in to reactivated pipeline north at Railroad tracks; Dixon area Solano County
|  |  |  | 3.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | Dixon | 3" to 6" Tie in North of Rail Road tracks; Dixon area Soloano County
|  |  |  | 3.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | Dixon | 3" to 6" Tie in south of railroad tracks reactivated pipelines; Dixon area Solano County
|  |  |  | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | Dixon | 6" Tie in to reactivated pipeline south of railroad tracks; Dixon area Soloano County
|  |  |  | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | Dixon | 6" Reactivated pipeline North Conection to V-1 south of Cal Pines North Fence line; Dixon area Solonao County
|  |  |  | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | Dixon | 6" Reactivated pipeline south conection to V-1 South at Cal Pines North Fence line; Dixon area Solano County
|  |  |  | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | Dixon | 6" Reactivated pipeline segment reconnection south of Cal Pine's North Fence line; Dixon area Solano County
|  |  |  | 6.25 | Transmission | [10 empty] | Steel/Wrought Iron |  | Dixon | 6" Reactivated pipeline segment reconnection South of Cal Pine's North Fence Line; Dixon area Solano County
|  |  |  | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | Dixon | 6" Reactivate pipeline connection to new pipe to meter set South of Cal Pine's North Fence line; Dixon area Solano County
|  |  |  | 32 | Transmission | [10 empty] | Steel/Wrought Iron |  | Diixon | Dixon area Solano County. Goose Haven Power Plant Tap location
|  |  |  | 32 | Transmission | [10 empty] | Steel/Wrought Iron |  | Dixon | Dixon area Solano county. Creed Power Plant Hot Tap Location
|  |  |  | 10.75 | [11 empty] | Steel/Wrought Iron
|  |  |  | 6.625 | [11 empty] | Steel/Wrought Iron
|  |  |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 10.75 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 2.375 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron
[5 empty] | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 8.625 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 8.625 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 10.5 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 6.625 | [11 empty] | Steel/Wrought Iron
|  |  |  | 12.75 | [11 empty] | Steel/Wrought Iron
|  |  |  | 6.625 | [11 empty] | Steel/Wrought Iron
|  |  |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron
[5 empty] | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 12.75 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron
16
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 6.625 | Gathering
|  |  |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  |  | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 8.625 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 0.04 | Transmission | [10 empty] | Steel/Wrought Iron |  | Ryde
|  |  |  | 0.03 | Transmission | [10 empty] | Steel/Wrought Iron |  | Rio Vista | Instal Riser c/o riser at well...
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 196 |  | 3.5
|  | 196 |  | 3.5 | [14 empty] | Valve location GPS cordinates: N 38o 05. Old' W121o 25.452'/ Installed line marker and ETS at 6' feet west of valve, buried in yellow fiber glass box
|  | 196 |  | 6.625
|  | 196 |  | 6.625 | [14 empty] | Valve loctation GPS Cordinates N38 degrees 05.061' W 121 Degrees 25.452' Installed Line Marker and ETS at 6' feet west of valve, buried in yellow fiber glass box
|  |  |  | 2.375 | Gathering | [10 empty] | Steel/Wrought Iron
| 05-20002-1 |  |  | 6.625 | Gathering |  |  |  |  | Internal Corrosion |  | 2005-02-16 |  |  |  | Steel/Wrought Iron |  | Rio Vista | Retired 396 feet 6" Main to Neil Hamilton #4 Gas Well
| 05-20002-1 |  |  | 6.625 | Gathering |  |  |  |  | Internal Corrosion |  | 2005-02-16 |  |  |  | Steel/Wrought Iron |  | Rio Vista | Retired 396 feet 6" Main to Neil Hamilton #4 Gas Well
| 05-20002-1 |  |  | 6.625 | Gathering |  |  |  |  | Internal Corrosion |  | 2005-02-16 |  |  |  | Steel/Wrought Iron |  | Rio Vista | Retired 396 feet 6" Main to Neil Hamillton #4 Gas Well
[16 empty] | Steel/Wrought Iron |  |  | L-400 MP 286.68 N 38 10.210' W 131 48.486'
Steel/Wrought Iron
Steel/Wrought Iron
Steel/Wrought Iron
| 98-004-1 | 200 |  | 6.25 | Gathering |  | Other |  | DIG-IN | Damage by outside Forces |  | 1998-08-08 | 1998-08-11 | Replace Pipe |  | Steel/Wrought Iron |  | Rio Vista | Replace Section of pipe
| 98-004-1 | 200 |  | 6.25 | Gathering |  | Other |  | DIG-IN | Damage by outside Forces |  | 1998-08-08 | 1998-08-11 | Replace Pipe |  | Steel/Wrought Iron |  | Rio Vista | Replaced section of pipe
| 99-55031- |  |  | 4.5 | Gathering |  |  |  |  | Digin |  | 1999-06-14 | 1999-06-15 |  |  | Steel/Wrought Iron |  | West Sarfo
| 99-00004-1 | 143 |  | 6.625 | Gathering | [6 empty] | 1999-12-01 | 1999-12-03 |  |  | Steel/Wrought Iron |  | Dixon | Installed 50" pf 6" .x42 ERW .156 Wall and 2" save valve rolled 4 degrees toward Sikes Rd.
| 99-00004-1 | 143 |  | 6.625 | Gathering | [6 empty] | 1999-12-01 | 1999-12-03 |  |  | Steel/Wrought Iron |  | Dixon | Removed damaged pipe and reinstalled 50" of emergency sctock pipe 6" ERW .156wt; Installed 50" of 6" .X42 ERW .156 wall and 2" save valve rolled 45 Degrees toward Sikes Rd.
|  | 195 |  | 4 | Gathering | [6 empty] | 2001-07-10 | 2001-07-16 | Welded Sleeve/Can - Weld |  |  |  |  | Installed Repair sleeve; Install 4' Sleeve
|  | 195 |  | 4 | Gathering | [6 empty] | 2001-07-10 | 2001-07-16 | Welded Sleeve/Can - Weld |  |  |  |  | Installed Repair Sleeve; Install 4' Sleeve
|  | 195 |  | 4 | Gathering | [6 empty] | 2001-07-10 | 2001-07-16 | Welded Sleeve/Can - Weld |  |  |  |  | Installed Repair Sleeve; Install 4' Sleeve
|  | 195 |  | 4 | Gathering | [6 empty] | 2001-07-10 | 2001-07-16 | Welded Sleeve/Can - Weld |  |  |  |  | Installed Repair Sleeve; Install 4' Sleeve
|  |  |  | 12.75 | [11 empty] | Steel/Wrought Iron |  |  | Tar Wrap appear in fair Condition for... found no real problems
[16 empty] | Steel/Wrought Iron |  |  | Somastic Pipe wrap appeared to be in excellect shape in this area no holiday cracks or nicks
[16 empty] | Steel/Wrought Iron |  |  | Somastic Pipe Wrap appeared to be in excellent shape in this area no holiday cracks or nicks
|  |  |  | 12.75 | [11 empty] | Steel/Wrought Iron |  |  | Very Shallow pipe this location DCVG Prior-O...UTM B3 616007, 4222542
|  |  |  | 10.62 | [8 empty] | 2001-05-11 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  |  | Air tested sleeve
| 00-20002-1 | 200 |  | 0.5 | Gathering |  | Drip |  |  | Damage by 3rd Party |  | 2000-11-06 | 2000-11-07 | Other | Inst. Valve |  |  | Rio Vista; | Install new valve; Vavle replaced with new 1/2" valve
| 00-20002-1 | 200 |  | 0.5 | Gathering |  | Drip |  |  | Damage by 3rd Party |  | 2000-11-06 | 2000-11-07 | Other | Inst. Valve |  |  | Rio Vista | Install new Valve; Valve replaced with new 1/2" Valve
|  | 145 |  | 4 | Gathering | [6 empty] | 2000-10-13 | 2000-10-18 | Welded Sleeve/Can - Weld |  |  |  | Dixon | Replaced 48'' of 9' line
|  |  |  | 4 | Gathering | [6 empty] | 2000-10-13 | 2000-10-18 | Welded Sleeve/Can - Weld | ; |  |  | Dixon | Replaced 48'' of 9' line
145
|  |  |  | 6.625 | [5 empty] | Internal Corrosion |  |  | 2000-09-11 | Other | Installed new dog leg | Steel/Wrought Iron
|  |  |  | 6.625 | [5 empty] | Internal Corrosion |  |  | 2000-09-11 | Other | Installed new dog leg | Steel/Wrought Iron
|  | 195 |  | 16 | Gathering | [10 empty] | Steel/Wrought Iron
|  | 195 | [13 empty] | Steel/Wrought Iron
|  | 195 |  |  | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 8.625 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 8.625 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | Inspection
|  |  |  | 8.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | Inspection
[5 empty] | Gathering | [10 empty] | Steel/Wrought Iron |  |  | Inspection 1275"OD .354" Wt. 39" C. Inspection 8.625"OD 0.219WT 41" C.
[5 empty] | Gathering | [10 empty] | Steel/Wrought Iron |  |  | Inspection
|  |  |  | 8.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | Inspection
[5 empty] | Gathering | [10 empty] | Steel/Wrought Iron |  |  | Inspection 36" C. 12.15"OD .375"WT. Inspection 4.50" OD .188" 60"C.
[5 empty] | Gathering | [10 empty] | Steel/Wrought Iron |  |  | Removed metering equipment and riser from well pad digged lines of ... and insert with air installed redwood.... Job #8056739 Loc Retirement of Isleton Community #1 Gas Well. 84" Inspection. 6" line 195 retired to valve 34. retirement included valve 36 see sheet 2 of 3 of as builts. Installed locating wire and line marker at 4" Cap Installed 4" Cap.
|  |  |  | 2.375 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | Job 38056739 Loc Removal od check valve 51 AsBuilt. Installed wires to keep CP on line...Installed 2" Flange and 3/4 Piping on valve 50 for future digging and to...pressure until retirement. 6" Line from ///LangHart spreckles gas well is flat but not digged of production fluids or ....Job in future for retirement per Brian
[5 empty] | Gathering | [10 empty] | Steel/Wrought Iron |  |  | Inspection.. Removed V-36 1ea. 4" Valve 2ea 4" Glanges 2ez. 90" ...
[5 empty] | Gathering | [10 empty] | Steel/Wrought Iron |  |  | Inspection
[5 empty] | Gathering | [10 empty] | Steel/Wrought Iron |  |  | Inspection
[5 empty] | Gathering | [10 empty] | Steel/Wrought Iron |  |  | Inspection
|  |  |  | 20 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | Inspection
[5 empty] | Gathering | [10 empty] | Steel/Wrought Iron |  |  | Inspection
[5 empty] | Gathering | [10 empty] | Steel/Wrought Iron |  |  | Inspection @ V-225
[5 empty] | Gathering | [10 empty] | Steel/Wrought Iron |  |  | Inspection
[5 empty] | Gathering | [10 empty] | Steel/Wrought Iron |  |  | Inspection.
|  |  |  | 6.25 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | Inspection
|  |  |  | 3.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | Inspection
|  |  |  | 6.25 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | Inspection
|  |  |  | 3.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | Inspection
|  | 114 |  | 16 | Transmission |  | Body of Pipe |  |  | Digin |  | 1992-12-29 | 1992-12-30 | Weld Over Sleeve or Can |  | Steel |  | Sherman Island | cut out 38" section of damaged pipe & replaced with pipe from emergency stock. Encon dug bell hole. contractor filled bell hole. line 114.
48 |  |  |  | 10 | Transmission | [6 empty] | 1971-09-21 |  |  |  | Steel/Wrought Iron |  |  | 10'' Install on Gm 150292-1961. New valve #16 installed on wo H0 40-A 1971
48 |  |  |  | 16 | Transmission | [6 empty] | 1971-09-21 |  |  |  | Steel/Wrought Iron |  |  | 16'' Installed on Gm 150292. Tied-in on w.o. 4040-A-1971
48 |  |  |  | 4 | [7 empty] | 1972-05-18 | [6 empty] | Retic union Pet #1 to original existant. Rison installed on Gm 158278 10-30-64
48 |  |  |  | 4 | Gathering | [6 empty] | 1973-06-14 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1973-08-03 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 10 | Transmission | [6 empty] | 1973-10-17 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 12 | Transmission | [6 empty] | 1973-10-17 |  |  |  | Steel/Wrought Iron | `
48 |  |  |  | 4 | Gathering | [6 empty] | 1973-10-17 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 10 | Transmission | [6 empty] | 1973-10-03 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 10 | Transmission | [6 empty] | 1973-10-17 |  |  |  | Steel
48 |  |  |  | 12 | Transmission | [6 empty] | 1973-10-17 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1973-10-17 |  |  |  | Steel/Wrought Iron
48 | 73-90002-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-10-03 | 1973-10-17 | Patch Welded |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1974-07-02 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1974-07-02 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Transmission | [6 empty] | 1973-11-06 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1974-01-29 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1974-01-29 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1974-01-29 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1974-01-29 |  |  |  | Steel/Wrought Iron
|  |  |  | 4 | Gathering | [6 empty] | 1971-04-13 |  |  |  | Steel/Wrought Iron |  |  | Dirty pipe: mud 1'' deep bottom opf pipe: job no. w.o. 4143 A-1124
48 |  |  |  | 6 | Gathering | [6 empty] | 1976-11-18 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1976-11-18 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  |  | Gathering | [6 empty] | 1976-11-18 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 6 | Gathering | [10 empty] | Steel/Wrought Iron
48 |  |  |  | 12 | Gathering | [6 empty] | 1974-05-09 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1974-10-03 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-03-20 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-03-20 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-04-16 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 2 | Gathering | [6 empty] | 1975-07-15 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-07-07 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-06-13 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 16 | Transmission | [6 empty] | 1975-07-28 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 16 | Transmission | [6 empty] | 1975-07-28 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-09-25 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 2 | Gathering | [6 empty] | 1975-11-11 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 3 | Gathering | [6 empty] | 1975-11-11 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-11-11 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Transmission | [6 empty] | 1975-11-07 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Transmission | [6 empty] | 1975-11-07 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1975-11-18 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 4 | Gathering | [6 empty] | 1975-11-18 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 6 | Gathering | [6 empty] | 1975-11-18 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 6 | Gathering | [6 empty] | 1975-12-02 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 10 | Gathering | [6 empty] | 1976-11-30 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1978-07-13 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 4 | Gathering | [6 empty] | 1978-07-13 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 4 | Gathering | [6 empty] | 1978-07-13 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 6 | Gathering | [6 empty] | 1978-03-01 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 4 | Gathering | [6 empty] | 1977-12-20 |  |  |  | Steel/Wrought Iron |  |  | None
48 |  |  |  | 4 | Gathering | [6 empty] | 1977-12-20 |  |  |  | Steel/Wrought Iron |  |  | NONE
[12 empty] | 1977-06-09 | [6 empty] | Back page of A-form, missing front.
48 |  |  |  | 6 | Gathering | [6 empty] | 1977-06-09 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1977-06-09 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 16 | Transmission | [6 empty] | 1976-10-26 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Transmission | [6 empty] | 1976-12-08 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1976-12-08 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | [7 empty] | 1976-12-08 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Transmission | [6 empty] | 1976-12-23 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Transmission | [6 empty] | 1976-12-23 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Transmission | [6 empty] | 1976-12-24 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Transmission | [6 empty] | 1976-12-24 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 3 | Gathering | [6 empty] | 1976-11-11 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 8 | Gathering | [6 empty] | 1977-04-29 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1977-04-29 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 8 | Gathering | [6 empty] | 1977-04-29 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Transmission | [6 empty] | 1976-10-15 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1977-04-28 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1977-02-02 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 3 | Gathering | [6 empty] | 1977-02-08 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1978-12-06 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1977-04-07 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 2 | Gathering | [6 empty] | 1977-04-07 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1977-04-07 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 3 | Gathering | [6 empty] | 1977-04-07 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1977-04-21 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 4 | Gathering | [6 empty] | 1977-04-21 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 6 | Gathering | [6 empty] | 1977-03-25 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | [7 empty] | 1977-05-06 |  |  |  | Steel/Wrought Iron |  |  | NONE
|  |  |  | 4 | Gathering | [6 empty] | 1977-05-23 |  |  |  | Steel/Wrought Iron |  |  | NONE
|  |  |  | 4 | Gathering | [6 empty] | 1977-05-23 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 3 | Gathering | [6 empty] | 1977-10-05 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 10 | Transmission | [6 empty] | 1977-12-06 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1977-06-22 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1977-06-22 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1977-11-04 |  |  |  | Steel/Wrought Iron |  |  | 1,869 feet of 4'' installed on G.M. 'A 133473 & 128050 removed from ground at owner's request as shallow pipe interfered with his farming operations
48 |  |  |  | 6 | Gathering | [6 empty] | 1977-09-01 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 4 | Gathering | [6 empty] | 1978-08-02 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 10 | Transmission | [6 empty] | 1978-08-02 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 6 | Gathering | [6 empty] | 1977-10-06 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1977-09-29 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1978-03-29 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 8 | Transmission | [6 empty] | 1977-11-10 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 4 | Gathering | [6 empty] | 1978-06-20 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Transmission | [6 empty] | 1978-08-10 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 6 | Transmission | [6 empty] | 1978-08-10 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 6 | Transmission | [6 empty] | 1978-08-09 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 6 | Transmission | [6 empty] | 1978-08-08 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 4 | Transmission | [6 empty] | 1978-08-08 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 6 | Transmission | [6 empty] | 1978-08-09 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 6 | Transmission | [6 empty] | 1978-08-10 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1978-11-29 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1978-11-07 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1978-07-20 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 16 | Transmission | [6 empty] | 1978-12-26 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 4 | Gathering | [6 empty] | 1978-11-08 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 10 | Transmission | [6 empty] | 1978-12-18 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 4 | Gathering | [6 empty] | 1978-10-24 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1979-03-15 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 3 | Gathering | [6 empty] | 1979-03-15 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1979-03-15 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1979-03-15 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 3 | Gathering | [6 empty] | 1979-03-15 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1979-03-15 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 8 | Gathering | [6 empty] | 1978-12-20 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 3 | Gathering | [6 empty] | 1979-03-15 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1979-03-15 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1979-03-15 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1979-06-05 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 8 | Gathering | [6 empty] | 1979-05-03 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1978-12-21 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 3 | Gathering | [6 empty] | 1979-02-01 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 3 | Gathering | [6 empty] | 1980-02-12 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1980-02-12 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1979-05-01 |  |  |  | Steel/Wrought Iron |  |  | Welded 3'' Cape on 3''x4'' reducers on triple gone users-cut off 3'' valves and motes sets - dual skid.
48 |  |  |  | 3 | Gathering | [6 empty] | 1979-05-16 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1979-05-02 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 3 | Gathering | [6 empty] | 1979-05-02 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1979-05-02 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1979-05-15 |  |  |  | Steel/Wrought Iron |  |  | Cut 6'' risers 1' above ground and installed 6'' cape. E.T.S. wire lead in way: Will remove resine malbondment of A.T. 47 some time in future.
48 |  |  |  | 4 | Gathering | [6 empty] | 1979-05-22 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1979-12-14 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1979-12-14 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1979-05-10 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1979-05-10 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1979-08-09 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1979-05-08 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1979-07-11 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 6 | Gathering | [6 empty] | 1979-07-10 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 6 | Gathering | [6 empty] | 1979-07-10 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 4 | Gathering | [6 empty] | 1979-07-10 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 4 | Gathering | [6 empty] | 1980-01-04 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 8 | Gathering | [6 empty] | 1980-01-04 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1980-01-04 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1980-01-04 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1979-07-30 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1980-02-28 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1980-02-28 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 10 | Gathering | [6 empty] | 1979-12-11 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 10 | Gathering | [6 empty] | 1979-12-11 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1979-09-12 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1979-09-11 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1979-09-11 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 5 | Gathering | [6 empty] | 1979-09-11 |  |  |  | Steel/Wrought Iron |  |  | Pipe specification from D.E.R. Report No. 5973-66-APRIL 4,1966 on section of 5'' pipe sent in for physical test.
48 |  |  |  | 6 | Gathering | [6 empty] | 1979-09-11 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1979-09-11 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1979-09-11 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1979-09-06 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1979-09-06 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1980-02-27 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1980-02-27 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1979-09-12 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1979-09-12 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1979-08-15 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 8 | Gathering | [6 empty] | 1979-08-15 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1979-08-15 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 | 79-90004-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1979-08-08 | 1979-08-15 | Patch Welded |  | Steel/Wrought Iron |  |  | External corrosion 3 o'clocl 1/8'' x1/8''. Reprimer with patch 4x5x.219
48 |  |  |  | 10 | Gathering | [6 empty] | 1980-01-21 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 8 | Gathering | [6 empty] | 1980-01-21 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 8 | Gathering | [6 empty] | 1980-01-21 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 2 | Gathering | [6 empty] | 1979-12-13 |  |  |  | Steel/Wrought Iron |  |  | none
52 |  |  |  |  | Gathering | [6 empty] | 1980-04-29 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 6 | Gathering | [6 empty] | 1980-04-29 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 8 | Gathering | [6 empty] | 1980-04-29 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 10 | Transmission | [6 empty] | 1980-09-08 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 10 | Transmission | [6 empty] | 1980-09-08 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 10 | Transmission | [6 empty] | 1980-09-09 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 10 | Transmission | [6 empty] | 1980-09-09 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 10 | Transmission | [6 empty] | 1980-09-09 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 10 | Transmission | [6 empty] | 1980-09-09 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1980-08-27 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 8 | Gathering | [6 empty] | 1980-07-24 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 10 | Gathering | [6 empty] | 1980-07-24 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 8 | Gathering | [6 empty] | 1980-07-24 |  |  |  | Steel/Wrought Iron |  |  | Remove valves "A" & #5
52 |  |  |  |  | Gathering | [10 empty] | Steel/Wrought Iron
48 |  |  |  | 8 | Transmission | [6 empty] | 1978-11-15 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 10 | Gathering | [6 empty] | 1978-12-07 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1978-12-07 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 4 | Gathering | [6 empty] | 1979-12-12 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 3 | Gathering | [6 empty] | 1979-12-12 |  |  |  | Steel/Wrought Iron |  |  | 3'' is part of riser installed bypg8e on G.M 189132 Adv. to meter set on producers platform of capitol - swanston #2 well
52 |  |  |  | 4 | Gathering | [6 empty] | 1980-08-22 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 4 | Gathering | [6 empty] | 1980-10-30 |  |  |  | Steel/Wrought Iron
52 |  |  |  | 4 | Gathering | [6 empty] | 1980-10-30 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 8 | [14 empty] | Installed on GM 169153 1967 valve 51 Inst on Gm 169153
48 |  |  |  | 8 | [14 empty] | Installed on Gm 68787 1942
48 |  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 6'' - line 141 installed on Gm 145816-1969 install new 6'' valve GM 460288-1971 Job-27-71
48 |  |  |  | 4 | [11 empty] | Steel/Wrought Iron
48 |  |  |  |  | Transmission | [6 empty] | 1971-03-10 |  |  |  | Steel/Wrought Iron |  |  | 4'' installed on GM175097-1970. Transfer north isleton unit #1 gas well to lowline GM 462990-71
48 |  |  |  | 6 | Transmission | [6 empty] | 1971-03-10 |  |  |  | Steel/Wrought Iron |  |  | 6'' installed on GM 100755 - wall thickness & type - see dept of engineering research report no. 4439-63. Sept. 9, 1963. Transfer north isleton unit #1 gas well lowline GM 462990-71
48 |  |  |  | 4 | Transmission | [6 empty] | 1971-03-09 |  |  |  | Steel/Wrought Iron |  |  | 4'' line abandoned was installed on GM159113 - abandoned on GM462991-71
48 |  |  |  | 4 | Gathering | [6 empty] | 1971-09-28 |  |  |  | Steel/Wrought Iron |  |  | 4'' installed on G.M. 133715-1951. River Island #5 rises & line cut off - G.M. 464298
48 |  |  |  | 6 | Gathering | [6 empty] | 1971-09-28 |  |  |  | Steel/Wrought Iron |  |  | 6'' installed on G.M. 134246-1956. Brandt #3 riser cut off and 2'' union dial to line cut off on G.M. 464298-1971
48 |  |  |  | 2 | Gathering | [6 empty] | 1971-09-28 |  |  |  | Steel/Wrought Iron |  |  | 2'' installed on G.M. 447389-1968 2'' check valve remove3d on G.M. 464298-1971. 2'' union oil to line cut off on G.M. 464298-1971
48 |  |  |  | 4 | Gathering | [6 empty] | 1971-11-09 |  |  |  | Steel/Wrought Iron |  |  | Installed on G.M. 110255 - 1950
48 |  |  |  | 6 | Gathering | [6 empty] | 1971-11-09 |  |  |  | Steel/Wrought Iron |  |  | Installed on G.M. 110755 1950
48 |  |  |  | 3 | Gathering | [6 empty] | 1973-06-06 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1973-05-18 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1973-05-18 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1973-05-18 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1973-05-18 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1973-05-18 |  |  |  | Steel/Wrought Iron
|  |  |  | 6 | Transmission | [6 empty] | 1973-07-12 |  |  |  | Steel/Wrought Iron
[5 empty] | Transmission | [6 empty] | 1973-07-10 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 3 | Gathering | [6 empty] | 1973-05-29 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1973-05-29 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1974-04-10 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 3 | Gathering | [6 empty] | 1974-04-10 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1974-04-10 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1974-04-10 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1974-04-10 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 3 | Gathering | [6 empty] | 1974-04-10 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1974-04-10 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1974-03-13 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1974-03-13 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1974-07-11 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1974-07-11 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1974-07-11 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1974-09-18 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1974-09-18 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 12 | Transmission | [6 empty] | 1974-05-02 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 12 | Transmission | [6 empty] | 1974-05-02 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1974-09-05 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1974-09-05 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1974-12-11 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1974-12-11 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1974-12-11 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 3 | Gathering | [6 empty] | 1974-12-11 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 4 | Gathering | [6 empty] | 1974-12-12 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 6 | Gathering | [6 empty] | 1974-12-12 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 8 | Gathering | [6 empty] | 1975-04-11 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 12 | Transmission | [6 empty] | 1975-03-31 |  |  |  | Steel/Wrought Iron
48 |  |  |  | 12 | Transmission | [6 empty] | 1975-03-31 |  |  |  | Steel/Wrought Iron
52 |  |  |  | 4 | Gathering | [6 empty] | 1980-10-15 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 6 | Gathering | [6 empty] | 1980-10-15 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 4 | Gathering | [6 empty] | 1980-10-15 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 | 80-57003-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-09-22 | 1980-10-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Permanent repairs. Replaced R9'-2' of 8''. .322WQ. API 5L GR.B smls steel pipe. Internal corrosion 6 o'clock
52 |  |  |  | 6 | Gathering | [6 empty] | 1980-10-14 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 6 | Gathering | [6 empty] | 1980-10-14 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 6 | Gathering | [6 empty] | 1980-10-14 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 | 80-57003-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-09-22 | 1980-10-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Permanent repairs. Replaced 29'-2'' or 8''. .322W. API 5L GR.B SMLS steel pipe. Internal corrosion - 6 o'clock
52 |  |  |  | 6 | Gathering | [10 empty] | Steel/Wrought Iron
52 |  |  |  | 4 | Gathering | [6 empty] | 1980-11-05 |  |  |  | Steel/Wrought Iron
52 |  |  |  | 2 | Gathering | [6 empty] | 1980-12-02 |  |  |  | Steel/Wrought Iron
|  | 195 |  | 6 | [7 empty] | 1988-06-03 |  |  |  | Steel |  | Rio Vista | Wrap loose with voids and water between wrap and pipe. Hit water at 36".
|  | 195 |  | 6 | [7 empty] | 1988-06-03 |  |  |  | Steel |  | Rio Vista | Wrap loose with voids and water between wrap and pipe, hit water at 60"
|  | 195 |  | 6 | [7 empty] | 1988-06-03 |  |  |  | Steel |  | Rio Vista | wrap good, hit water at 60 inches
|  | 195 |  | 6 | [7 empty] | 1988-06-03 |  |  |  | Steel |  | Rio Vista | wrap good no water
|  | 195 |  | 6 | [7 empty] | 1988-06-03 |  |  |  | Steel |  | Rio Vista | wrap good, hit water at 60"
|  | 195 |  | 10 | [7 empty] | 1988-10-20 |  |  |  | Steel
|  | 131 |  | 10 | [7 empty] | 1988-10-20 |  |  |  | Steel
|  | 195 |  | 10 | [7 empty] | 1988-10-20 |  |  |  | Steel
|  | 131 |  | 10 | [7 empty] | 1988-10-20 |  |  |  | Steel
|  | 195 |  | 8.625 | [11 empty] | Steel |  | Rio Vista | lowered pipe in place
|  | 195 |  | 8.625 | [11 empty] | Steel |  | Rio Vista | lowered pipe in place
|  | 195 |  | 8.625 | [11 empty] | Steel |  | Rio Vista | lowered pipe in place
|  |  |  | 8.625 | [7 empty] | 1987-05-07 |  |  |  | Steel |  | Dixon | GM454049-8 Master Meter Tube (6") new amerada compresser site.
|  |  |  | 6.625 | [7 empty] | 1987-03-16 |  |  |  | Steel |  | Rio Vista
|  |  |  | 4.5 | [7 empty] | 1987-10-15 |  |  |  | Steel |  | Isleton
|  |  |  | 6.5 | [7 empty] | 1987-11-30 |  |  |  | Steel
|  |  |  | 8 | [7 empty] | 1987-11-12 |  |  |  | Steel
Steel
|  |  |  | 6.625 | [7 empty] | 1988-12-07 |  |  |  | Steel |  | Dixon Area | Internal Corrosion, this section of piping should be replaced! @ 600ft. +or-
|  |  |  | 6.625 | [7 empty] | 1988-12-06 |  |  |  | Steel |  | Dixon area | looking for leak
|  |  |  | 6.625 | [7 empty] | 1988-11-15 |  |  |  | Steel |  | Dixon area | looking for leak
|  |  |  | 6.625 | [7 empty] | 1988-12-01 |  |  |  | Steel |  | Dixon Area | this section was cut out to isolate 16194 of l-200 looking for a leak
|  |  |  | 6.625 | [7 empty] | 1988-11-15 |  |  |  | Steel |  | Dixon
|  |  |  | 3.5 | [7 empty] | 1988-10-18 |  |  |  | Steel
|  |  |  | 4 | [7 empty] | 1988-10-18 |  |  |  | Steel |  | Rio Vista
|  |  |  | 6 | [7 empty] | 1988-10-18 |  |  |  | Steel |  | Rio Vista
|  | 200 |  | 3.5 | [7 empty] | 1989-01-23 |  |  |  | Steel |  | Rio Vista
|  |  |  | 6.625 | [7 empty] | 1989-01-23 |  |  |  | Steel
|  | 200 |  | 6.625 | [7 empty] | 1989-01-23 |  |  |  | Steel |  | Rio Vista
|  |  |  | 8.625 | [11 empty] | Steel |  | Rio Vista | Testing L-200 GM
|  | 200 |  | 8.625 | [7 empty] | 1989-01-23 |  |  |  | Steel |  | Rio Vista
|  | 200 |  | 4 & 6 | [7 empty] | 1989-01-23 |  |  |  | Steel |  | Rio Vista
|  | 200 |  | 6.625 | [7 empty] | 1989-01-23 |  |  |  | Steel |  | Rio Vista
|  |  |  | 8.625 | [7 empty] | 1988-11-08 |  |  |  | Steel |  | Rio Vista
|  |  |  | 8.625 | [7 empty] | 1988-11-08 |  |  |  | Steel |  | Rio Vista | Tested H+H gas service tee. + Dist. Reg. Pin-off tee also.
|  |  |  | 8.625 | [7 empty] | 1988-11-08 |  |  |  | Steel
|  |  |  | 8.625 | [7 empty] | 1988-11-08 |  |  |  | Steel |  |  | New pipe
|  |  |  | 8.625 | [7 empty] | 1988-11-08 |  |  |  | Steel |  | Rio Vista
|  |  |  | 8.625 | [7 empty] | 1988-12-05 |  |  |  | Steel |  | Rio Vista
|  |  |  | 8.625 | [7 empty] | 1988-12-05 |  |  |  | Steel
|  |  |  | 6.625 | [7 empty] | 1988-12-05 |  |  |  | Steel
|  |  |  | 3.5 | [7 empty] | 1988-12-05 |  |  |  | Steel
|  |  |  | 3.5 | [7 empty] | 1988-12-05 |  |  |  | Steel
|  |  |  | 6.625 | [7 empty] | 1988-12-05 |  |  |  | Steel |  | Dixon
|  |  |  | 6.625 | [7 empty] | 1988-12-06 |  |  |  | Steel |  |  | Looking for leak
|  |  |  | 4 | [7 empty] | 1988-07-05 |  |  |  | Steel |  | Isleton
|  |  |  | 4 | [7 empty] | 1988-07-05 |  |  |  | Steel |  | Isleton
|  |  |  | 6.625 | [7 empty] | 1988-08-11 |  |  |  | Steel |  | Rio Vista
|  |  |  | 6.625 | [7 empty] | 1991-02-01 |  |  |  | Steel
|  |  |  | 10.75 | [7 empty] | 1991-02-13 |  |  |  | Steel
|  |  |  | 10.75 | [7 empty] | 1991-02-13 |  |  |  | Steel
|  |  |  | 4.5 | [7 empty] | 1991-04-11
|  |  |  | 4.5 | [7 empty] | 1991-04-11
|  |  |  | 8 | [7 empty] | 1991-05-03
|  |  |  | 8 | [7 empty] | 1991-05-03 |  |  |  | Steel
|  |  |  | 16 | [7 empty] | 1991-12-17 |  |  |  | Steel
|  |  |  | 6 | [7 empty] | 1991-12-17 |  |  |  | Steel
|  | 200 |  | 10 | [7 empty] | 1991-12-17 |  |  |  | Steel
|  |  |  | 4 | [7 empty] | 1991-11-05
|  |  |  | 4 | [7 empty] | 1991-11-05
|  | 200 |  | 6 | [7 empty] | 1991-09-19 |  |  |  | Steel
|  |  |  | 6 | [7 empty] | 1991-10-13 |  |  |  | Steel
|  |  |  | 10.75 | [7 empty] | 1991-11-25
|  | 200 |  | 16 | [7 empty] | 1991-12-09 |  |  |  | Steel
|  |  |  | 3 | [11 empty] | Steel
|  | 200 |  | 3.5 | [7 empty] | 1991-12-17 |  |  |  | Steel
|  | 200 |  | 3.5 | [7 empty] | 1991-12-19 |  |  |  | Steel
|  |  |  | 2 | [7 empty] | 1999-10-15 | [6 empty] | Vega G/W-Sherman IS. 2" valve #!
|  |  |  | 6.625 | [7 empty] | 2000-05-23 | [6 empty] | loc #6025004, loc at 6" tee from valve 26
|  |  |  | 6.625 | [7 empty] | 2000-05-23 | [6 empty] | loc #6025004. Loc at north cut off point.
|  |  |  | 6.625 | [14 empty] | Loc #6025004, loc at 6" tee from valve
6.625
|  |  |  | 12.75 | [7 empty] | 1998-12-01
|  |  |  | 10.75 | [7 empty] | 1999-11-23 | [6 empty] | loc #6028163 10" main at valves 102& 104 line 131 installed on GM 187216 between fs 284+80 and fs 284+88
|  |  |  | 3.5 | [7 empty] | 2000-04-01 | [6 empty] | loc#603804 location at riser fs 0+0
|  |  |  | 4.5 | [7 empty] | 2000-04-04
|  |  |  | 3.5 | [7 empty] | 2000-04-05 | [6 empty] | loc#6031804 location south side canal crossing. FS 12+51
|  |  |  | 4.5 | [7 empty] | 2000-04-05 | [6 empty] | job #6031804. Location at canal crossing. FS 13+93 detail #2 north side of canal
|  |  |  | 8.625 | Gathering | [6 empty] | 2000-06-22
|  |  |  | 8.625 | Gathering | [6 empty] | 2000-06-22
|  |  |  | 16 | [11 empty] | Steel/Wrought Iron
|  |  |  | 32 | [7 empty] | 2000-11-04 |  |  |  | Steel/Wrought Iron
|  |  |  | 4.5 | [7 empty] | 2001-03-21 |  |  |  | Steel/Wrought Iron
|  |  |  | 8.625 | [7 empty] | 2000-10-12 |  |  |  | Steel/Wrought Iron
|  |  |  | 8.625 | [7 empty] | 2000-10-12 |  |  |  | Steel/Wrought Iron |  |  | Exposed where 4'' x-tie was cut out
|  |  |  | 8.625 | [7 empty] | 2000-10-12 |  |  |  | Steel/Wrought Iron |  |  | Exposed where 4'' x-tie was cut out
|  |  |  | 8.625 | [7 empty] | 2000-10-12 |  |  |  | Steel/Wrought Iron |  |  | exposed where 4" x-tie was cut out.
|  |  |  | 6.62 | [7 empty] | 2000-12-19 |  |  |  | Steel/Wrought Iron
|  |  |  | 16 | [7 empty] | 2001-02-07 |  |  |  | Steel/Wrought Iron |  |  | pipe was ultra soniced for walll tihs in weld areas of 3" nipple and reinforcing ... by ties see atached letter from Chris Neary
16
[12 empty] | 2001-03-13 |  |  |  | Steel/Wrought Iron
|  |  |  | 3.5 | [7 empty] | 2001-02-14 |  |  |  | Steel/Wrought Iron
|  |  |  | 8.62 | [7 empty] | 2001-05-03 |  |  |  | Steel/Wrought Iron
|  |  |  | 12.75 | [7 empty] | 2001-04-23 |  |  |  | Steel/Wrought Iron
|  |  |  | 4.5 | [7 empty] | 2001-05-04 |  |  |  | Steel/Wrought Iron
|  |  |  | 8.62 | [7 empty] | 2001-05-04 |  |  |  | Steel/Wrought Iron
|  |  |  | 6.625 | [7 empty] | 2001-05-30 |  |  |  | Steel/Wrought Iron
|  |  |  | 6.625 | [7 empty] | 2001-05-30 |  |  |  | Steel/Wrought Iron
|  |  |  | 6.625 | [7 empty] | 2001-05-31 |  |  |  | Steel/Wrought Iron
|  |  |  | 8.625 | [11 empty] | Steel/Wrought Iron
|  |  |  | 6.625 | [7 empty] | 2001-06-07 |  |  |  | Steel/Wrought Iron
|  |  |  | 4.5 | [7 empty] | 2001-06-01 |  |  |  | Steel/Wrought Iron
|  |  |  | 10.75 | Gathering | [6 empty] | 2002-02-20 |  |  |  | Steel/Wrought Iron |  |  | 10'' valve
|  |  |  | 6.25 | Gathering | [6 empty] | 2002-02-21 |  |  |  | Steel/Wrought Iron
|  |  |  | 6.25 | Gathering | [6 empty] | 2002-02-21 |  |  |  | Steel/Wrought Iron
|  |  |  | 10.75 | Gathering | [6 empty] | 2002-02-20 |  |  |  | Steel/Wrought Iron |  |  | 10'' valve
|  |  |  | 12.75 | [11 empty] | Steel/Wrought Iron
|  |  |  | 32 | [11 empty] | Steel/Wrought Iron
|  |  |  | 6.625 | [11 empty] | Steel/Wrought Iron
|  |  |  | 16 | [11 empty] | Steel/Wrought Iron
|  |  |  | 6 | [7 empty] | 1997-10-14 |  |  |  | Steel |  | Dixon
|  |  |  | 10 | [7 empty] | 1997-10-02
|  |  |  | 6 | [7 empty] | 1997-04-08 |  |  |  | Steel
|  | 200 |  | 8.625 | [7 empty] | 1997-02-05 |  |  |  | Steel
|  |  |  | 4 | [7 empty] | 1997-03-11
|  | 200 |  | 8.625 | [7 empty] | 1997-02-05 |  |  |  | Steel
|  |  |  | 4 | [7 empty] | 1997-03-10 |  |  |  | Steel |  |  | Pressure taps appear to be off of bottom of pipe & valve tees. 0 to old hi to hi set per as built see attached
|  |  |  | 4 | [7 empty] | 1997-03-11
|  |  |  | 4 | [7 empty] | 1997-03-10 |  |  |  | Steel
|  | 200 |  | 8.625 | [7 empty] | 1997-02-05 |  |  |  | Steel
|  |  |  | 6 | [7 empty] | 1998-05-14 |  |  |  | Steel
|  |  |  | 6 | [7 empty] | 1998-05-07 |  |  |  | Steel
|  |  |  | 6 | [7 empty] | 1998-05-14 |  |  |  | Steel
|  |  |  | 4 | [7 empty] | 1998-05-06 |  |  |  | Steel
|  |  |  | 6 | [7 empty] | 1998-05-07 |  |  |  | Steel
|  |  |  | 6 | [7 empty] | 1998-05-06 |  |  |  | Steel
|  |  |  | 6 | [7 empty] | 1998-05-06 |  |  |  | Steel
|  |  |  | 4 | [7 empty] | 1998-05-08 |  |  |  | Steel
|  |  |  | 6 | [7 empty] | 1998-05-14 |  |  |  | Steel
|  |  |  | 6 | [7 empty] | 1998-05-14 |  |  |  | Steel
|  |  |  | 6 | [7 empty] | 1998-05-06 |  |  |  | Steel
|  |  |  | 4 | [7 empty] | 1998-05-06 |  |  |  | Steel
|  |  |  | 4 | [7 empty] | 1998-05-08 |  |  |  | Steel
|  |  |  | 6 | [7 empty] | 1998-05-07 |  |  |  | Steel
|  |  |  | 4 | [7 empty] | 1998-05-06 |  |  |  | Steel
|  |  |  | 6 | [7 empty] | 1998-05-07 |  |  |  | Steel
48 |  |  |  | 6 | Gathering | [6 empty] | 1979-12-14 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 8 | Gathering | [6 empty] | 1979-12-14 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 8 | Gathering | [6 empty] | 1980-01-21 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 8 | Gathering | [6 empty] | 1980-01-21 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 10 | Gathering | [6 empty] | 1980-01-21 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 2 | Gathering | [6 empty] | 1979-12-13 |  |  |  | Steel/Wrought Iron |  |  | none
52 |  |  |  |  | Gathering | [6 empty] | 1980-04-29 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 6 | Gathering | [6 empty] | 1980-04-29 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 8 | Gathering | [6 empty] | 1980-04-29 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 10 | Transmission | [6 empty] | 1980-09-08 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 10 | Transmission | [6 empty] | 1980-09-08 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 10 | Transmission | [6 empty] | 1980-09-09 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 10 | Transmission | [6 empty] | 1980-09-09 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1980-08-27 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 8 | Gathering | [6 empty] | 1980-07-24 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 10 | Gathering | [6 empty] | 1980-07-24 |  |  |  | Steel/Wrought Iron |  |  | NONE
52 |  |  |  | 8 | Gathering | [6 empty] | 1980-07-24 |  |  |  | Steel/Wrought Iron |  |  | Remove valves "A" & #5
52 |  |  |  |  | Gathering | [10 empty] | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 8 | Transmission | [6 empty] | 1978-11-15 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 8 | Transmission | [6 empty] | 1978-11-15 |  |  |  | Steel/Wrought Iron |  |  | none
48 |  |  |  | 10 | Gathering | [6 empty] | 1978-12-07 |  |  |  | Steel/Wrought Iron |  |  | NONE
48 |  |  |  | 6 | Gathering | [6 empty] | 1978-12-07 |  |  |  | Steel/Wrought Iron |  |  | NONE
| 09-40004-1 | 400 | 16.26 | 0.36 | Transmission |  | Other |  | Bonnet | Other | Gasket | 2009-05-26 | 2010-10-14 | Other | Clamps & packing | Steel/Wrought Iron |  | Tulelake
| 09-40004-1 | 400 | 16.26 | [8 empty] | 2009-05-26 | [5 empty] | Tulelake
| 09-40005-1 | 400 | 97.66 | [8 empty] | 2009-05-26
| 03-40007-1 | 400 | 115.26 | 36 | Transmission |  | Fitting | Other | Flange bolts | Equipment Malfunction |  | 2003-05-05 | 2009-09-17 | Other | TRP-3117 | Steel/Wrought Iron |  | Burney
| 03-40007-1 |  | 115.26 | [8 empty] | 2003-05-05 |  |  |  |  | ; | Burney
| 03-40007-1 |  | 115.26 | 36 | Transmission |  | Fitting | Valves |  |  |  | 2003-05-05 | [5 empty] | Burney
| 08-80076-1 | DFM |  | 0.75 | Transmission |  | Valves |  |  | Other | GREASE | 2008-06-23 | 2009-07-20 | Other | GREASE VALVE | Steel/Wrought Iron |  | GLENBURN | GREASED VALVE
| 09-80041-1 | DFM |  | 0.75 | Transmission |  | Other |  | Cap on pin off TEE | Other | Loose CAP | 2009-05-07 |  |  |  | Steel/Wrought Iron |  | MCARTHUR
| 09-80044-1 | 401/400 | 80.94 | 2 | Transmission |  | Fitting |  |  | Other | Loose | 2009-05-14 | 2009-05-15 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Johnson Park | ReDoped & Retightened. 2^ BTTM. Tap CAP. Bottom Tap feed Johnson Park DRs.
| 09-80044-1 | 401 | 80.94 | [8 empty] | 2009-05-07 | [5 empty] | Johnson Park
| 09-80105-1 | DFM | 32.8 | 6 | Transmission |  | Valves |  |  | Unknown |  | 2009-05-23 | 2010-06-14 | Other | OPERATION | Steel/Wrought Iron |  | Shasta Lake City | Soap test
| 09-80105-1 | DFM | 32.8 | 3 | [7 empty] | 2009-05-23 | [5 empty] | Shasta Lake City
| 09-80107- | 402 | 30.68 | 4 | Transmission >= 20% SMYS |  | Line Valve |  |  | Equipment Malfunction |  | 2009-05-26 | 2010-11-18 | Replace Dist Main < 100 ft |  | Steel |  | Redding | Replaced 118" 4" STL Valve 250 Installed Insolator & 8'4" 10" stl Main
| 09-80110-1 | 402/DFM | 16.73 | 0.25 | Transmission |  | Valves |  |  | Other | Loose Metric | 2009-05-03 | 2009-11-19 | Other | TIGHTEN FITTING | Steel/Wrought Iron |  | Redding | Tightened Metric Valve Core; Soap tested ok CXCP
| 09-80111-1 | 402/DFM | 21.41 | 6 | Transmission |  | Valves |  |  | Other | Grease | 2009-06-03 | 2010-01-14 | Other | GREASE | Steel/Wrought Iron |  | Redding
| 09-80116-1 | 402/DFM | 23.99 | 3 | Transmission |  | Valves |  |  | Other | No Description | 2009-06-03 | 2010-06-10 | Other | GREASED | Steel/Wrought Iron |  | Redding | Soap Test
87 | 10-88039-1 | 402 | 34.47 | 0.75 | Distribution Main >60 PSIG and <20% SYMS |  | Other Mechanical Joint |  |  | No/Deteriorated Pipe Dope |  | 2010-10-18 | 2011-02-28 | Other | Welded Caps | Steel |  | Redding | c/o Bypass to eliminate leak on high to high set; Welded 3/4" and 1" caps on high to high set (aboveground set) to eliminate leak
| 10-88001-1 | 1042-01 | 0.01 | 0.75 | Transmission |  | Valves |  |  | Other | Loose gauge tap | 2010-10-14 | 2011-01-25 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Fall River | Soap test ok step
| 10-80186-1 | 402/SVC | 38.15 | 8 | Transmission |  | Valves |  |  | Unknown |  | 2010-05-20 | 2010-06-10 | Other | GREASED | Steel/Wrought Iron |  | Mountain Gate | Soap test
| 10-80186-1 | 402/SVC | 38.15 | [8 empty] | 2010-05-20 | [5 empty] | Mountain Gate
| 10-80188-1 | 402 | 27.98 | 10 | Transmission |  | Valves |  |  | Other | Needed Grease | 2010-05-25 | 2010-05-26 | Other | GREASE | Steel/Wrought Iron |  | Redding | Bridal Valve Cluster for hilltop TAP, Soap Test
| 10-80189-1 | 402 | 27.98 | 10 | Transmission |  | Valves |  |  | Other | Needed Grease | 2010-05-25 | 2010-05-26 | Other | GREASE | Steel/Wrought Iron |  | redding | Bridal Valve Cluster for hilltop and pepper tree, soap test
| 10-80203-1 | 402/SVC | 38.15 | 8 | Transmission |  | Valves |  |  | Other | Need Grease | 2010-05-20 | 2010-06-15 | Other | GREASE VALVE | Steel/Wrought Iron |  | Mountain Gate | Grease Valve; Sopa test after valve greasing
| 10-80203-1 | 402/SVC | 38.15 | [8 empty] | 2010-05-20 | [5 empty] | Mountain Gate | ;
87 | 10-80496-1 | 402/DFM | 16.09 | 6 | Transmission >= 20% SMYS |  | Line Valve | Fitting |  | Other Natural Forces |  | 2010-12-16 | 2010-12-17 | Greased - Other |  | Steel |  | Anderson | Greased and Operated Valve
87 | 10-81201-1 | DREG5485 | 0.51 | 6 | Transmission >= 20% SMYS |  | Other |  | Grease Fitting | Other | Lack of Grease | 2010-10-13 | 2011-01-07 | Greased - Other |  | Steel |  | Shasta Lake City | Grease fitting wa. leaking, crew greased valve; Grease fitting in valve # 253 was leaking. Valve was greased, sopa test applied
87 | 11-80003-B | 402/DFM | 16.09 | 6 | Transmission >= 20% SMYS |  | Other |  |  | Other | Failed Thermal Check valve | 2011-01-20 | 2011-02-08 | Tighten Cap/Bolt - Fitting |  | Steel |  | Anderson | Removed thermal expansion plug & replaced with a solid plug Isolated & Blew down valve. Plug was on body of valve;
87 | 74-00025-1 |  |  | 10 | Transmission |  | Fitting |  |  | Material Failure |  | 1974-05-29 | 1974-08-16 | Other | redope and tighten cap | Steel/Wrought Iron |  |  | Found leakage around cap on gauge live tie. Repairs by redoping and tightening caps
87 | 74-00063-1 |  |  | 8 | Transmission |  | Valves |  |  | Other |  | 1974-06-24 | 1974-07-01 | Other |  | Steel/Wrought Iron
87 | 75-00015-1 |  |  | 2 | Distribution Feeder Main |  | Longitudinal Weld |  |  | Construction Defect |  |  | 1975-01-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Insert 2-2" P.C. F with 3/4" bypass and replace leaking weld with 2' of pipe and 2-45 degree welding
13 | 81-00050-1 |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1981-11-24 | 1981-11-24 | Other |  | Steel/Wrought Iron |  | Redding
13 | 82-00038-1 |  |  | 0.5 | Distribution Main |  | Other |  |  | Material Failure |  | 1982-11-05 | 1982-11-08 | Replace Pipe and/or Service |  | Plastic |  | Redding | Inserted Risser leaking internally
87 | 82-00023-1 |  |  | 0.75 | Transmission |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1982-04-29 | 1982-07-22 | Other |  | Steel/Wrought Iron |  | Mt. Gate | REPAIRED
87 | 79-00050-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-03-06 | 1979-03-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Burney
87 | 79-00040-1 |  |  | 1.25 | Other |  | Meter |  |  | Other |  | 1979-02-16 | 1979-03-20 | Other |  | Steel/Wrought Iron |  | Redding | Found leak at swival connection or out let side of meter, repaired by tightening swival
87 | 77-00007-1 |  |  | 2 | M |  | Fitting |  |  | Construction Defect |  | 1977-01-17 | 1978-04-20 | Other |  | Steel/Wrought Iron |  | Redding | Found leakage around P.C.F cap repaired by redoping and tightening cap
87 | 77-00078-1 |  |  | 10 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 1977-07-28 | 1977-07-28 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Anderson | A lot of moisture under wrap and in 16" caseing. Installed bottom vent
87 | 83-00012-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-02-17 | 1984-05-24 | Other |  | Steel/Wrought Iron |  | Pine Grove
87 | 83-00019-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Material Failure |  | 1983-04-22 | 1983-05-03 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Red Bluff | Weld full wedding band 24"
87 | 83-00020-1 |  |  | 12 | Transmission | [6 empty] | 1983-04-22 |  |  |  | Steel/Wrought Iron |  | Red Bluff
87 | 83-00050-1 |  |  | 1 | Distribution Main |  | Tap Connection |  |  | Construction Defect |  | 1983-11-22 | 1983-11-22 | Other |  | Plastic |  | Redding | Leak @ tap connection
87 | 83-00028-1 |  |  | 10 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 1983-03-16 | 1984-06-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Redding; | Repaired with Sleeve
13 | 83-00025-1 |  |  | 0.75 |  |  | Fitting |  |  | Construction Defect |  | 1983-05-10 | 1983-05-13 | Other |  | Steel/Wrought Iron |  | Anderson | Reparied leak by tightening cap on Static Line
10 | 91-00021-1 |  |  | 1 | Transmission |  | Fitting |  |  | Other | No Description | 1991-04-25 | 1991-04-25 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Redding | Over P.C.F. Fitting. Found savor cap not tightened. Re-doped and tightened
87 | 91-00022-1 | 402 |  | 0.75 | Transmission |  | Other Welds |  |  | Construction Defect |  | 1991-05-09 | 1991-05-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Redding | Line 402 Dogleg S. End of Bridge at Creek. Repaired leak on 3/4" Coupling with 3/4 stl. Plug welded in was leaking, welded 3" nipple with saver valve
87 | 73-38- |  |  | 1.25 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1973-08-29 | 1973-08-29 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Shingletown | Soap test ok. Stand up pressure test, ok
| 10-70010- | 177A | 48.85 | [8 empty] | 2010-03-27 | [5 empty] | Red Bluff | at 3rd State reg sta 119, no leakage found delete
85 | 10-70017-1 | 177A | 85.73 | 0.75 |  |  | Fitting |  |  | Other | Loose | 2010-04-23 |  |  |  | Steel/Wrought Iron |  | Platina | 1st. Stage box at gauge tap no leak found
| 09-70026-1 | 177 | 88.8 | 0.75 | Transmission |  | Fitting |  |  | Other | Loose fitting | 2009-05-13 |  |  |  | Steel/Wrought Iron |  | Harrison Gulch
| 09-70027-1 | 177 | 88.8 | 0.75 | Transmission |  | Fitting |  |  | Other | loose fitting | 2009-05-13 | 2009-05-14 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | Harrison Gulch
| 09-70028-1 | 177 | 88.8 | 0.75 | Transmission |  | Fitting |  |  | Other | loose cap | 2009-05-13 | 2009-05-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Harrison Gulch | A-form for leak number 09-70028-1 are included in concordance image
| 09-70029-1 | 177 | 88.8 | 0.75 | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-05-13 | 2009-05-14 | Other | OPERATE VALVE | Steel/Wrought Iron |  | Harrison Gulch
| 09-70030-1 | 177 | 85.73 | 0.75 | Transmission |  | Fitting |  |  | Other | Loose fitting | 2009-05-13 | 2009-05-14 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | Platina
| 09-70031-1 | 177 | 85.73 | 0.75 | Transmission |  | Fitting |  |  | Other | Loose fitting | 2009-05-13 | 2009-05-14 | Other | TIGHTENED FITTINGS | Steel/Wrought Iron |  | Platina
| 09-70032-1 | 177 | 78.21 | 0.75 | Transmission |  | Fitting |  |  | Other | Loose fitting | 2009-05-13 | 2009-05-15 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Platina
| 05-70009-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 2005-04-28 | 2005-04-28 | Mechanical Repair Fitting - Fitting |  | Aldyl A (Tan or Gray) |  | Red Bluff | Install Dead end 28" below ground
| 03-70019-1 | 177 | 38.89 | 0.75 | Transmission |  | Fitting |  |  | Other | Loose plug | 2003-08-23 | 2004-02-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Red Bluff | Tighten valve plug
| 03-70020-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other | Loose fiting | 2003-08-23 | 2003-10-22 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | Red Bluff | Tightened fitting
| 04-80005-1 | 402 | 17.89 | 0.75 | Transmission |  | Fitting |  |  | Construction Defect |  | 2004-01-09 | 2004-01-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Anderson | Caps on both pin off tees leaking, used teflon taape retighten
| 04-80007-1 | 402 | 17.39 | 0.75 | Transmission |  | Regulator |  |  | Material Failure |  | 2004-01-09 | 2004-01-13 | Other | REBUILT REGULATOR | Steel/Wrought Iron |  | Anderson | Reg Blowing out of vent, rebuilt reg
| 04-80024-1 | 402 | 17.39 | 0.75 | Transmission |  | Regulator |  |  | Other | diaphragm froze | 2004-03-03 | 2004-03-10 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Anderson | Tightened bolts on diaphragm housing
| 04-80122-1 | 402 | 19.31 | 0.75 | Transmission |  | Regulator |  |  | Equipment Malfunction |  | 2004-10-08 | 2010-04-27 | Other | NEW REG | Steel/Wrought Iron |  | Anderson | Repair AEG; Soap test rem, left 7 day reloader
| 03-80050-1 | DFM |  | 0.75 | Transmission |  | Valves |  |  | Other | Dried out grease | 2003-06-18 | 2004-02-11 | Other | GREASE VALVE | Steel/Wrought Iron |  | McArthur | Above groung valve on 3/4" pipe leaking greased valve
| 03-80049-1 | Fall River Feeder |  | 0.75 | Transmission |  | Fitting | Valves |  | Other | Threads | 2003-06-18 | 2003-09-24 | Deactivate #TP Main | Replace TP Main, Replace Valve < 2 inch | Steel/Wrought Iron |  | McArthur | Tightened plug & Replaced 3/4" V-511 + 8 of 3/4" T.P. Pipe
| 03-80058-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2003-06-24 | 2003-09-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | McArthur | Cap on 3/4" Pin off tee, re-doped and tightened
| 03-80059-1 | DFM |  | 0.75 | Transmission |  | Valves |  |  | Other | Grease | 2003-06-24 | 2004-07-15 | Other | GREASE VALVE | Steel/Wrought Iron |  | McArthur | Greased & Operated valve. Replaced buttonhead
| 03-80061-1 | DFM |  | 0.75 | Transmission |  | Other |  | Relief Valve | Other | REG Failure | 2003-06-24 | 2004-07-22 | Other | REBUILT REG | Steel |  | McArthur | Rebuilt 141 REG @ First Stage
| 03-80081-1 | [10 empty] | 2003-07-23 | [5 empty] | Burney | NO LEAKAGE
| 02-80016-1 |  |  | 3 | Transmission |  | Valves |  | Tap Connection | Other | Grease fitting | 2002-03-13 | 2002-03-14 | Other | GREASE FITTING | Steel/Wrought Iron |  | Redding | Greased Valve
20 | 75-00166-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1975-07-28 | 1976-05-21 | Other |  | Steel/Wrought Iron |  | Rosev. | Greased valve= tested entire intersection with combustable tester. No leaks.
20 | 77-00210-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-12-29 | 1977-12-29 | Replace Pipe and/or Service |  | Plastic |  | Auburn | Replaced 1/3" Plastic Tee & Damaged 1/2" pipe
20 | 77-00209-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-12-20 | 1977-12-20 | Replace Pipe and/or Service |  | Other Plastic |  | Auburn
20 | 77-00208-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-12-20 | 1977-12-20 | Replace Pipe and/or Service |  | Plastic |  | Auburn | Connection made with 1" plastic AMP-fitt coupling (2)
20 | 77-00195-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-11-30 | 1977-11-30 | Replace Pipe and/or Service |  | Plastic |  |  | Connection made wih 2-2" plastic coupling
20 | 77-00187-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-11-17 | 1977-11-17 | Replace Pipe and/or Service |  | Plastic |  | Bowman
20 | 77-00186-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-11-16 | 1977-11-16 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Auburn | Installed can over damage area 11-17-77, Installed permanent Clamp 11-16-77
20 | 77-00134-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-09-21 | 1977-09-21 | Replace Pipe and/or Service |  | Plastic |  | Auburn | Installed 1-1" Clamp fitting, Installed 1-1" plastic coupling
20 | 77-00129-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-09-10 | 1977-09-10 | Replace Pipe and/or Service |  | Plastic |  | Auburn | Replace 1 1/2" of Damage 1/2" plastic. Connection made with 2-1/2" Plastic Coupling
20 | 77-00123-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-08-26 | 1977-08-26 | Replace Pipe and/or Service |  | Plastic |  | Loomis | Inst. 2-2" Plastic Elbow
20 | 77-00119-1 |  |  | 0.5 | Service |  | Fitting |  |  | Damage by outside Forces |  | 1977-08-05 | 1977-08-05 | Replace Pipe and/or Service |  | Plastic |  | Loomis | Replace 1/2" Plastic Coupling; Backhoe operator pulled 1/2 plastic pipe from coupling. Repair was made by Replacing 1/2" coupling.
22 | 77-00115-1 |  |  |  | Other | [6 empty] | 1977-08-12 |  |  |  | Steel/Wrought Iron |  | Grass Valley | Line use: "O"= Other; Area Clear; Soap tested manifold. SM. found no leakage
20 | 77-00099-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1977-07-06 | 1977-07-07 | Clamp |  | Steel/Wrought Iron |  | Roseville | Inst. 2- Skin a Clamp, to Repair 2 Gas Leak.; Inst. 2-Skinner clamp to repair 2 gas leak soap tested OK
20 | 77-00092-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-06-23 | 1977-06-23 | Replace Pipe and/or Service |  | Plastic |  | Auburn | Connection made with 2-1/2" plastic coulping
20 | 77-00080-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-05-23 | 1977-05-23 | Replace Pipe and/or Service |  | Plastic |  | Roseville | Connection made with 2-2" plastic coupling
20 | 77-00078-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-05-21 | 1977-05-21 | Replace Pipe and/or Service |  | Plastic |  | Rocklin | Connection with 1/2" plastic 1/2" plastic coupling
15 | 77-00054-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Damage by Natural Forces |  | 1977-04-05 | 1977-04-05 | Replace Pipe and/or Service |  | Plastic |  | Roseville | Connection made with 2- 1/4" plastic coupling
20 | 77-00049-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-03-29 | 1977-03-29 | Replace Pipe and/or Service |  | Plastic |  | Auburn
15 | 79-00158-1 |  |  | 0.34 | Service |  | Fitting |  |  | Damage by outside Forces |  | 1979-09-06 | 1979-09-06 | Patch Welded |  | Steel/Wrought Iron |  | Grass Valley | Main in this area is going to be lowered. Hanson Brothers are grading street in this area. Pulled off serv. tee in the process.
20 | 79-00105-1 |  |  | 0.75 | Service |  | Fitting |  |  | Construction Defect |  | 1979-06-27 | 1980-10-21 | Other |  | Steel/Wrought Iron |  | Roseville | Replaced leaking cap on service tee.
20 | 79-00013-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-03-10 | 1979-03-10 | Replace Pipe and/or Service |  | Plastic |  | Roseville | Connection made with 2-1/2" AMP-fit coupling
20 | 80-165-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-08-11 | 1980-08-11 | Replace Pipe and/or Service |  | Plastic |  | Loomis | Connection made with 2-1/2" AMP-fit coupling
20 | 80-163-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-08-09 | 1980-08-09 | Replace Pipe and/or Service |  | Plastic |  | Rocklin | Connection made with 2 -1/2" AMP-fit Coupling
20 | 80-137-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-07-21 | 1980-07-21 | Replace Pipe and/or Service |  | Plastic |  | Roseville | Connection made with 2 -1/2" AMP-fit Coupling
20 | 80-136-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-07-21 | 1980-07-21 | Replace Pipe and/or Service |  | Plastic |  | Roseville | Connection made with 2 -1/2" AMP-fit Coupling
20 | 80-135-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-07-18 | 1980-07-18 | Replace Pipe and/or Service |  | Plastic |  | Roseville | Connection made with 2 -1/2" AMP-fit Coupling
20 | 80-131-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-07-15 | 1980-07-15 | Replace Pipe and/or Service |  | Plastic |  | Roseville | Connection made with 2 -1/2" AMP-fit Coupling
20 | 80-130-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-07-15 | 1980-07-15 | Replace Pipe and/or Service |  | Plastic |  | Roseville | Connection made with 2 -1/2" AMP-fit Coupling
20 | 80-105-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-06-18 | 1980-06-18 | Replace Pipe and/or Service |  | Plastic |  | Rocklin | Connection made with 2 -1/2" AMP-fit Coupling
20 | 80-00050-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-04-19 | 1980-04-19 | Replace Pipe and/or Service |  | Plastic |  | Auburn | Connection made with 2 -1/2" AMP-fit Coupling
20 | 80-00014-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-02-08 | 1980-02-08 | Replace Pipe and/or Service |  | Plastic |  | Roseville | Connection made with 2 -1/2" AMP-fit Coupling
15 | 82-48-1 | 202 |  | 6 | Transmission | [6 empty] | 1982-06-16 |  |  |  | Steel/Wrought Iron |  | Penn Valley | Area Clear; *Found while checking main for depth *Recheck found no leakage-P.P. 11-2-83. Copy sent to G.K. 1-3-84 for 15 month chk. (w.r.). 2d.=2-8-84 Retrurned to check with pilly.
20 | 87-00060-1 |  |  | 0.75 | Distribution Main |  | Other Welds |  |  | Other |  | 1987-04-23 | 1987-04-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Loomis | Leak on weld at Hi-Hi Set R-54, Welded on new riser with arc. Leak repaired
20 | 88-00114-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1988-10-25 | 1989-02-22 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Rocklin | Greased Valve
11 | 81-00074-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion | Internal | 1981-01-22 | 1981-01-22 | Clamp | REPLACE PIPE AND/OR SERVICE | Steel/Wrought Iron |  | Sutter Co. | PR, on 12/14/1983, G.C. Repaired Date 12-14/1983; Found small pin hole on bottom of pipe (5 O'clock). Approx. 1 1/2" to 2" from welded joint. Installed 5' of pretested pipe.
11 |  |  |  | 6 | Transmission | [10 empty] | Steel |  | Yuba City | c/o line 121 & installed. transfered to new 2" PC. H.P. Main
11 |  |  |  | 6 | Transmission | [10 empty] | Steel |  | Sutter Co.
11 |  |  |  | 6 | Transmission | [10 empty] | Steel |  | Sutter Co
|  | 121 |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 121 |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron
12 |  | 121 |  | 6.5 | Transmission |  | Other |  |  | Other |  | 1974-03-15 |  | Other |  | Steel/Wrought Iron |  |  | Refer to GM182218
11 |  |  |  | 6 | Transmission | [6 empty] | 1972-09-29 |  |  |  | Steel/Wrought Iron
12 |  |  |  | 6 | Transmission | [6 empty] | 1972-05-15 |  |  |  | Steel/Wrought Iron |  |  | 6" L-121
12 |  |  |  | 6 | Transmission | [6 empty] | 1972-05-15 |  |  |  | Steel/Wrought Iron |  |  | 6" L-121
|  | 121 |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Sutter Co.
11 |  |  |  | 6 | Transmission | [6 empty] | 1972-09-23 |  |  |  | Steel/Wrought Iron
[5 empty] | Transmission | [10 empty] | Steel/Wrought Iron
11 | 80-60003-1 | 50 |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion | External | 1980-01-21 | 1980-03-10 | Patch Welded |  | Steel/Wrought Iron |  | Marysville | Ref. to 79-20159-1 #3; Leak 1' n/o Serv. on top of line 50 R. Lutz 3-5-80
11 | 73-40079-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-11-15 | 1973-12-13 | Patch Welded |  | Steel/Wrought Iron |  | Marysville | Apparently the joint has never been wrapped. Numerous Corrosion pits.
11 | 73-20094-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-12-18 | 1973-12-20 | Patch Welded |  | Steel/Wrought Iron |  | Marysville | Welded half sole patch
11 | 75-00007-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-04-02 | 1975-06-26 | Patch Welded |  | Steel/Wrought Iron |  | Marysville
13 | 73-00091-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-12-05 | 1979-04-19 | Patch Welded |  | Steel/Wrought Iron |  | Live Oak | Leak in main on Highway 9 30' n/o mailbox 11400 eastside of raod marked yellow X
11 | 76-40024-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-05-20 | 1978-01-24 | Patch Welded |  | Steel/Wrought Iron |  | Live Oak
11 | 71-60016 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-06-21 | 1971-06-24 | Replace Pipe |  | Steel/Wrought Iron |  | Marysville | Replaced 12' 8" Main
11 | 71-60015 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1971-06-25 | 1971-06-28 | Patch Welded |  | Steel/Wrought Iron |  | Marysville | Welded patches over pits 3' east of leak and 4' west of leak;
13 | 72-00079-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-06-23 | 1972-10-24 | Patch Welded |  | Steel/Wrought Iron |  | Live Oak | Changed to Grade 2 Leak; Leak on bottom, installed welded patch 14" x 18"
|  |  |  | 8 | Transmission | [6 empty] | 1975-03-11 |  |  |  | Steel |  | Live Oak
11 |  |  |  | 8 | Transmission | [10 empty] | Steel |  | Live Oak | No Leak Uncovered Main to pluf off service.
13 |  | 50 |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron
11 |  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | Yuba City
12 |  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | Marysville
13 |  | 50 |  | 8 | [7 empty] | 1973-06-14 |  |  |  | Steel/Wrought Iron
11 |  |  |  | 8 | Transmission | [6 empty] | 1973-07-02 |  |  |  | Steel/Wrought Iron
13 |  | 50 |  | 8 | Transmission | [6 empty] | 1975-06-13 |  |  |  | Steel/Wrought Iron
11 |  | 50 |  | 8 | Transmission | [6 empty] | 1973-12-13 |  |  |  | Steel/Wrought Iron |  | Marysville
11 |  | 50 |  | 8 | Transmission | [6 empty] | 1973-12-13 |  |  |  | Steel/Wrought Iron |  | Marysville
11 |  | 50 |  | 8 | Transmission | [6 empty] | 1973-12-12 |  |  |  | Steel/Wrought Iron |  | Marysville | Inspected for a distance of 65'
11 |  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | Yuba City
11 |  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | Yuba City
22 | 83-165-1 | 202 |  | 6 | Transmission |  | Fitting |  |  | Construction Defect |  | 1983-10-24 | 1984-10-08 | Other |  | Steel/Wrought Iron |  | Grass Valley | Repaired leaking cap on 2" sava valve found threads on cap leaking, redoped & replaced cap
20 | 83-162-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other |  | 1983-10-28 | 1983-12-14 | Other |  | Steel/Wrought Iron |  | Roseville | Removed HPR. Plugged service riser & Capped house line
20 | 83-104-1 |  |  | 8 | Transmission |  | Tap Connection |  |  | Other |  | 1983-05-26 | 1983-05-26 | Other |  | Steel/Wrought Iron |  | Rocklin | Found leak on cap of 8" fitting. Reversed gasket & Tightened to stop leak.
20 | 83-3-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1983-01-13 | 1983-01-15 | Patch Welded |  | Steel/Wrought Iron |  | Roseville | Patch welded over corrosion leak, permanent repair clamps over leaks.
20 | 85-00198-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1985-11-09 | 1985-12-09 | Other |  | Steel/Wrought Iron |  | Loomis | Greased valve 12-5-85, Checked again with leak indicator 12-9-95.
20 | 85-191-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Digin |  | 1985-11-05 | 1985-11-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Loomis | Inst. 3' of 2" Pl Pipe, 1-Couple & 1 AMP repair Cpling. for repair D&C
20 | 76-00098-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-06-28 | 1976-06-28 | Replace Pipe and/or Service |  | Other Plastic |  | Auburn | Replaced 3'-1" PLC with 2'-1" coupling
22 | 76-00068-1 |  |  | 0.75 |  |  | Regulator |  |  | Construction Defect |  | 1976-05-27 | 1976-07-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Grass Valley | Line Source indicated "O" = Other; Small leak in screwed fittings, in regulator pit (cannot tighten); Remove screwed piping and replaced with welded pipimg, Reg Pit
20 | 78-00190-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-11-09 | 1978-11-09 | Replace Pipe and/or Service |  | Plastic |  | Loomis | Connection made with 2 -1/2" AMP-fit Coupling
20 | 78-00168-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-10-09 | 1978-10-09 | Replace Pipe and/or Service |  | Plastic |  | Roseville | Connection made with 2-1/2" plastic AMP-fit Coupling
20 | 78-00139-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1978-07-15 | 1978-07-21 | Clamp |  | Steel/Wrought Iron |  | Auburn
20 | 78-00115-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-08-05 | 1978-08-05 | Replace Pipe and/or Service |  | Plastic |  | Rocklin | Connection made with 2-1/2" AMP Fit Coupling
20 | 78-00112-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-07-20 | 1978-07-20 | Replace Pipe and/or Service |  | Plastic |  | Auburn | Connection made with 2-1/2" AMP fit coupling
20 | 78-00105-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-06-24 | 1978-06-24 | Replace Pipe and/or Service |  | Plastic |  | Loomis; | Connection made with 2-1/2" AMP fit coupling
20 | 78-00104-1 |  |  | 0.75 | Service |  | Fitting |  |  | Damage by outside Forces |  | 1978-06-23 | 1978-06-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Rocklin | Ray Chiaratti back over his gas meter set with AN Pick-up. Repair by st... out the gas riser
20 | 78-00101-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-06-27 | 1978-06-27 | Replace Pipe and/or Service |  | Plastic |  | Roseville | Connection made with 2-1/2" AMP fit coupling
20 | 78-00100-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-07-13 | 1978-07-13 | Replace Pipe and/or Service |  | Plastic |  | Roseville | Connection made with 2-1/2" AMP fit coupling
20 | 78-00099-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-07-13 | 1978-07-13 | Replace Pipe and/or Service |  | Plastic |  | Roseville | Inst. 1-1/2" AMP fit Coupling
20 | 78-00095-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-07-08 | 1978-07-08 | Replace Pipe and/or Service |  | Plastic |  | Rocklin | Connection made with 2-1/2" AMP fit coupling
20 | 78-00089-1 |  |  | 0.75 | Other |  | Meter |  |  | Corrosion |  | 1978-06-19 | 1979-03-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Loomis | Meter was leaking in body change meter and eliminated leakage. SOAP Tested OK.; Line Use indicated "o"= other.
20 | 78-00087-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-06-12 | 1978-06-12 | Replace Pipe and/or Service |  | Plastic |  | Rocklin | Connection made with 2-1/2" plastic AMP fit coupling
20 | 78-00047-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-05-15 | 1978-05-15 | Replace Pipe and/or Service |  | Plastic |  | Auburn | Connection made with 2-1/2" plastic AMP fit coupling
20 | 78-00032-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-04-03 | 1978-04-03 | Replace Pipe and/or Service |  | Plastic |  | Auburn | Connection made with 2-1" AMP fit coupling
| 97-00107-1 | 50 |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1997-06-06 | 1997-06-06 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Yuba City | Installed. 8"ODx12L 50,000 SMYS sleeve
| 95-00014-1 | 50 |  | 8 | Transmission |  | Other |  | No Description | Construction Defect |  |  | 1996-06-11 | Replace Pipe |  | Steel/Wrought Iron |  | Live Oak | Installed 2 -8" SER. 30 BT mullers w/8" dog leg .322wall/ Replaced 9'6" of .250wall 8" pipe and 12" tap
| 01-00152-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | No Grease | 2001-06-27 | 2001-06-27 | Other | Greased valve | Steel/Wrought Iron |  | Penryn | Extended grease plug, greased valve & Installed F&C; Installed F&C 18" from 6" main.
| 01-00260-1 |  |  | 1.25 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2001-10-10 | 2001-10-26 | Other | Replaced leaking transition | Aldyl A (Tan or Gray) |  | Grass Valley | Replaced leaking PC. TU. STZ. transition
| 02-00048-1 |  |  | 1.25 | Distribution Main |  | Fitting |  | Physical/Mecahnical Joint | Damage by 3rd Party |  | 2002-08-30 | 2002-08-30 | Other | 1 1" X 8" NIPPLE | Steel/Wrought Iron |  | Marysville | above grd hpr - straighten set & install 1 1" x 8" Nipple; Install 1 8" Nipple; Above Grd. HPR- Straighten set and install 1 1"x8" mipple- ENG Should decide if set needs to be repaired due to service blonding from truck hitting it.
| 03-00330-1 |  |  | 6 | Transmission |  | Valves |  |  | Material Failure |  | 2003-10-06 | 2003-11-10 | Other | REPOCK VALVE | Steel/Wrought Iron |  | Marysville | Closed V-15 on 10/06/03 -Repacked on 11/10/03
| 03-00378- |  |  | 8 | Transmission |  | Valves |  |  | Other | Needed Grease | 2003-11-08 | 2003-11-12 | Other | Grease Valve | Steel/Wrought Iron |  | Yuba City | Grease Valve
| 03-00379- |  |  | 12 | Transmission |  | Valves |  |  | Other | Needed Grease | 2003-11-08 | 2003-11-12 | Other | Grease Valve | Steel/Wrought Iron |  | Yuba City | Grease Valve
| 03-00380- |  |  | 16 | Transmission |  | Valves |  |  | Other | Need Grease | 2003-11-08 | 2003-11-12 | Other | Grease Valve | Steel/Wrought Iron |  | Yuba City | Grease Valve
| 03-00381- |  |  | 6 | Transmission |  | Valves |  |  | Other | Needed Grease | 2003-11-08 | 2003-11-12 | Other | Grease Valve | Steel/Wrought Iron |  | Yuba City | Grease Valve
| 03-00411-1 |  |  | 8 | Transmission |  | Valves |  |  | Other | Needs Grease | 2003-11-05 | 2004-01-19 | Other | Greased; | Steel/Wrought Iron |  | Grass Valley | Greased Valve Stem; Greased Valve Stem.
| 04-00225- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Digin |  | 2004-08-31 | 2004-08-31 | Service Partially Replaced |  | Steel/Wrought Iron |  | Yuba City | Replaced; Shut Valve off replaced 2 SMLS 00.75 pipe that was hit by ripper.
| 04-00313-1 |  |  | 6 | Transmission |  | Valves |  |  | Other | Valve | 2004-11-08 | 2005-05-19 | Other | Reset; | Steel/Wrought Iron |  | Newcastle | Reset relief valve
| 05-00037-1 |  |  | 0.75 | Single Service |  | Regulator |  |  | Other | Loose; | 2005-02-01 | 2010-04-28 | Other | Replace Reg. | Steel/Wrought Iron |  | Yuba City | Leak on outlet of reg. replaced reg & relief valve
| 05-00092-1 | [10 empty] | 2005-03-26 | 2005-05-19 |  |  |  |  | Roseville | Grease valve with leaking stem, no leaks. "O" ring
| 05-00092- | [10 empty] | 2005-03-26 | [5 empty] | Roseville
| 05-00188-1 | 55 |  | 8 | Transmission |  | Other |  | NUT | Construction Defect |  | 2005-07-29 | 2005-07-30 | Other |  | Steel/Wrought Iron |  | Yuba city | Tighten Nut
| 05-00189- | 55 |  | 1.25 | Transmission |  | Valves |  |  | Other |  | 2005-07-29 | 2005-07-30 | Other | Grease; | Steel/Wrought Iron |  | Yuba City | Grease Valve
| 05-00192-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | Loose threads | 2005-07-29 | 2010-04-30 | Other | R & R; | Steel/Wrought Iron |  | Yuba City | Dissasembled & Reopened, grease and reassemble
| 05-00207-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Digin |  | 2005-08-10 | 2005-08-10 | Other | Replace <100' trans. Main | Steel/Wrought Iron |  | Yuba City | Replace 42" of 6" steel pipe
| 05-00257-1 | 173 | 5.5 | 6 | Transmission |  | Mechanical Joint |  |  | Construction Defect |  | 2005-09-22 | 2005-10-11 | Other | Weld Elbow | Steel/Wrought Iron |  | Rocklin | Weld Fitting
|  | DFM |  | 6.625 | Transmission | [7 empty] | 2005-11-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | Yuba City | Repaired gauge by installing a 29" long Sleeve.; Removed 42" of damaged 06.625"OD x 42 .188WT. pipe and installed pre-tested emergency 06.625OD x 42 .299 WT. pipe. see attached test report
|  |  |  | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | Roseville | Exposed future use DFM for signs of damage in 2 spots at water crossing - No damage to pipe found.
|  |  |  | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | Beale AFB
|  |  |  | 6 | Transmission | [6 empty] | 2006-02-07 |  |  |  | Steel/Wrought Iron |  | Rocklin | Note: Condition not checked off-unknown
|  |  |  | 6 | Transmission |  | Other |  | GOUGE | Damage by 3rd Party |  | 2005-11-21 | 2005-11-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | Yuba City | Installed 6" weld sleeve; Installed 6" weld sleeve
|  | DFM |  | 4 | Transmission | [6 empty] | 2005-09-26 |  |  |  | Steel/Wrought Iron |  | El Dorado Hills
|  |  |  | 4 | Transmission | [6 empty] | 2005-08-15 |  |  |  | Steel/Wrought Iron |  | Lincoln | Install water service Xing over 4" DFM Gas Line
|  | DFM |  | 6 | Transmission | [6 empty] | 2005-07-11 |  |  |  | Steel/Wrought Iron |  | Rocklin
|  | DFM |  | 4 | Transmission | [6 empty] | 2005-07-05 |  |  |  | Steel/Wrought Iron |  | Lincoln | 5' Slurry backfill on Pipe
|  | DFM |  | 6 | Transmission | [6 empty] | 2005-04-29 |  |  |  | Steel/Wrought Iron |  | Rocklin
|  | DFM |  | 10 | Transmission | [6 empty] | 2005-06-03 |  |  |  | Steel/Wrought Iron |  | El Dorado
|  | DFM |  | 10 | Transmission | [6 empty] | 2005-06-03 |  |  |  | Steel/Wrought Iron |  | El Dorado | Storm drain crosses 15" above DFM
|  |  |  | 10 | Transmission | [6 empty] | 2005-05-31 |  |  |  | Steel/Wrought Iron |  | El Dorado Hills
|  | DFM |  | 6 | Transmission | [6 empty] | 2005-03-28 |  |  |  | Steel/Wrought Iron |  | Lincoln
|  |  |  | 6 | Transmission | [6 empty] | 2005-03-28 |  |  |  | Steel/Wrought Iron |  | Lincoln
|  |  |  | 6 | Transmission | [6 empty] | 2005-03-25 |  |  |  | Steel/Wrought Iron |  | Lincoln
|  |  |  | 6 | Transmission | [6 empty] | 2005-03-25 |  |  |  | Steel/Wrought Iron |  | Lincoln
|  |  |  | 6 | Transmission | [6 empty] | 2005-03-25 |  |  |  | Steel/Wrought Iron |  | Lincoln
|  |  |  | 6 | Transmission | [6 empty] | 2005-03-25 |  |  |  | Steel/Wrought Iron |  | Lincoln
|  |  |  | 6 | Transmission | [6 empty] | 2005-03-25 |  |  |  | Steel/Wrought Iron |  | Lincoln
|  | DFM |  | 6 | Transmission | [6 empty] | 2005-04-07 |  |  |  | Steel/Wrought Iron |  | Lincoln
|  | DFM |  | 6 | Transmission | [6 empty] | 2005-02-22 |  |  |  | Steel/Wrought Iron |  | Lincoln | Boreing Xing over 6" DFM Gas Main. Sage Trl. Com. ___ "Brett Barry" 26w. Dry Crk. Cir. St. 190 Littleton Ca. 916-640-1350 "Ron" 303-210-4713 "For" Surewest Broaadbald "Luke Wallace" Inspector.
|  | DFM |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | LIncoln | Boreing -Xing over 6" DFM Gas Main.
|  | DFM |  | 6 | Transmission | [6 empty] | 2005-02-22 |  |  |  | Steel/Wrought Iron |  | Lincoln | Boring over 6" Gas DFM
|  | DFM |  | 6 | Transmission | [6 empty] | 2005-02-10 |  |  |  | Steel/Wrought Iron |  | Rocklin
|  | DFM |  | 6 | Transmission | [6 empty] | 2005-02-09 |  |  |  | Steel/Wrought Iron |  | Rocklin
|  | DFM |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Lincoln | No Sched. Stand by Insp Durinig routine USA work found sage communication boreing over 6" DFM Gas Main. Work being done for" Sure west inspector for surewest Luke Wallave Ph # 916-879-1894
|  | DFM |  | 6 | Transmission | [6 empty] | 2004-11-15 |  |  |  | Steel/Wrought Iron |  | Lincoln
|  | DFM |  | 4 | Transmission | [6 empty] | 2004-08-11 |  |  |  | Steel/Wrought Iron |  | Roseville | Stand by only
|  | DFM |  | 6 | Transmission | [6 empty] | 2004-08-04 |  |  |  | Steel/Wrought Iron |  | Rocklin | Stand by only
|  | 124 |  | 16 | Transmission | [6 empty] | 2005-02-08 |  |  |  | Steel/Wrought Iron |  | Lincoln | @ Depths to final grade
|  | 124 |  | 16.00 & 08.00 | Transmission | [6 empty] | 2004-12-16 |  |  |  | Steel/Wrought Iron |  | Lincoln | Teichert Const. Working lime into soil. ;
|  | 124 |  | 16 | Transmission | [6 empty] | 2005-01-20 |  |  |  | Steel/Wrought Iron |  | Lincoln | 7' ft. deep from finish grade
11 |  | 124 |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron
11 |  | 124 |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Lincoln
11 |  | 124 |  | 16 | [11 empty] | Steel/Wrought Iron |  |  | No Leakage, Main inspection report only
11 |  | 124 |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Lincoln;
11 |  | 124 |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Lincoln
11 |  | 124 |  | 16 | Transmission | [6 empty] | 1973-08-28 |  |  |  | Steel/Wrought Iron |  | Sutter Co.
|  |  |  | 16 | Transmission | [6 empty] | 1972-10-17 |  |  |  | Steel/Wrought Iron |  | Oroville | Refer to WO4088
|  |  |  | 16 | Transmission | [6 empty] | 1972-08-04 |  |  |  | Steel/Wrought Iron |  | Yuba City | Roots cutting into wrap
11 |  |  |  | 16 | Transmission | [6 empty] | 1973-01-16 |  |  |  | Steel/Wrought Iron
|  | 124 | 25.98 | 16 | [7 empty] | 2000-09-29 |  |  |  | Steel/Wrought Iron |  | Yuba City | Inspection only
|  | 124 | 25.98 | 16 | [7 empty] | 2000-09-29 |  |  |  | Steel/Wrought Iron |  | Yuba City | Inspection only
| 06-00215-1 |  |  | 2 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 2006-09-26 | 2006-09-26 | Patch Weld - Weld |  | Steel/Wrought Iron |  | Marysville | Lowered pressure and re-welded around Tee; Re-welded tap tee
| 06-00262-1 | 1502-01 | [9 empty] | 2006-11-21 | [5 empty] | Marysville | *need to recheck in six mounths-Ground was wat on 11-21-06
| 06-00438-1 |  |  | 3 | Transmission |  | Valves |  |  | Construction Defect |  | 2006-03-15 | 2008-12-08 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Penryn | Torqued stem bolt
| 06-00438-1 |  |  | 3 | Transmission |  | Valves |  |  | Construction Defect |  | 2006-03-15 | 2008-12-08 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Penryn | Torqued stem bolt
| 06-00464-1 |  |  | 4 | Distribution Main |  | Other |  | SS Tubing Fittings & Plug or Fitter Lid | Other | wear | 2006-12-19 | 2008-06-02 | Soap and/or Tape - Other |  | Steel/Wrought Iron |  | Roseville | Installed new SS tubing and fittings on reg. & taped & doped plug
| 07-00129-1 | 121 |  | 6 | Transmission |  | Unknown |  |  | Unknown |  | 2007-08-01 | 2007-08-01 | Deactivate #TP Main |  | Steel/Wrought Iron |  | W/O Sutter Co. | Deactivated approx. 105' of 6", 4", 2" STL on line 120 from T-203 to valve #5 in Sutter Creek Valve lot.; Deactivated approx. 105' of 6", 4", 2" STL of line 120 from T-203 to valve #5 in Sutter Creek Valve lot, see attached sheet
| 07-00209-1 |  |  | 6 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 2007-12-23 | 2007-12-23 | Patch Weld - Weld |  | Steel/Wrought Iron |  | Sutter | Re-welded 2" tee on 6" main
| 08-00022-1 | 124 |  | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2008-01-27 | 2008-01-28 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | Marysville | G.C. to repair line/install sleeve/ x-ray welds
| 08-00023-1 | 123 | [9 empty] | 2008-01-02 | [5 empty] | Lincoln
| 08-00121-1 | 123 | [9 empty] | 2008-01-02 | [5 empty] | Lincoln | ;
| 08-00023-1 | 123 | [9 empty] | 2008-01-02 | [5 empty] | Lincoln | 6/13/2008 11:30 ; 1,500 PPm Valve at walkway; 3,000 PPM Reg Vault/vent
| 08-00023-1 | 123 | [9 empty] | 2008-01-02 | [5 empty] | Lincoln
| 08-00058-1 | 202 |  | 8 | Transmission |  | Fitting |  |  | Other | No Description | 2008-03-18 | 2008-04-01 | Other | No Description | Steel/Wrought Iron |  | Grass Valley
| 08-00085-1 | 1501-01 |  | 0.75 | Transmission |  | Tap Connection |  |  | Incorrect Operation |  | 2008-04-24 | 2008-04-25 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Yuba City | Tightened cap on 00.75 fitting only
| 08-00121-1 | 123 |  | 6 | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2008-06-13 | 2008-12-12 | Replace Main Valve < 2-inch |  | Steel/Wrought Iron |  | Lincoln
| 08-00165-1 | [10 empty] | 2008-09-10 | [5 empty] | Marysville
| 08-00202-1 |  |  | 2 | Transmission |  | Valves |  |  | Other | Valve stem leak | 2008-11-25 | 2008-11-25 | Other | Lube Valve | Steel/Wrought Iron |  | Penryn | Lube Valve / stem seals to stop leak, N/A -No pipe installed
| 08-00226-1 |  |  | 4 | Transmission |  | Other |  | 4" B.T. | Material Failure |  | 2008-12-30 | 2009-01-07 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | Marysville | Installed new 4" Completion on bottom tap; Spring in 4" COmpletion plug leaking- replaced with new completion plug; Sring in 4" completion plug leaking- replaced with new completion plug
| 08-00226-1 | [10 empty] | 2008-12-30 | [5 empty] | Marysville
| 08-10045-1 | 124 | [9 empty] | 2008-05-05 | [5 empty] | Wheatland
| 08-10151-1 | 123 |  | 0.25 | Single Service |  | Fitting |  |  | Other | Dry Dope | 2008-04-28 | 2008-05-21 | Other | Re-doped tighten fitting | Steel/Wrought Iron |  | Lincoln
| 08-00565-1 | 173 | [9 empty] | 2008-03-10 | [5 empty] | Ophir
| 08-00566-1 | 173 | [9 empty] | 2008-03-10 | [5 empty] | Penryn
| 08-00568-1 | 173 |  | 4 | Transmission |  | Fitting |  |  | Other |  | 2008-03-11 | 2008-04-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Loomis
| 08-00569-1 | 1519-04 |  | 12 | Transmission |  | Valves |  |  | Other | No Description | 2008-03-12 | 2008-04-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Rocklin
| 08-00570-1 | 173 |  | 3 | Transmission |  | Valves |  |  | Other | Leaking @ Stem | 2008-03-12 | 2008-05-23 | Other | Tightened stem bolt | Steel/Wrought Iron |  | Rocklin | Tightened stem bolt
| 08-00572-1 | 173 |  | 8 | Transmission |  | Valves |  |  | Other | leaking fitting (thread) | 2008-05-13 | 2008-05-22 | Other | 1. Grease fitting; 2. Re-welded gauge tap | Steel/Wrought Iron |  | Rocklin | Greased & Re-welded
|  | DREG4861 | [9 empty] | 2008-03-13 | 2008-06-25 | Other | Relocated main and installed new valve at new location |  |  | Rocklin | Leak Eliminated!! Valve removed on PM 30604384; Delete Leak!
| 08-00574-1 | DREG8724 |  | 0.5 | Distribution Main |  | Valves |  |  | Other | Metric Valve partially open | 2008-03-14 | 2008-05-28 | Other | Tightened valve and re-secure plug | Steel/Wrought Iron |  | El Dorado Hills | Tightened Valve & re-secured plug
| 08-00575-1 | 123 |  | 4 | Transmission |  | Valves |  |  | Other | No Description | 2008-03-17 | 2008-03-17 | Other | Regreased and acctivated; | Steel/Wrought Iron |  | Roseville
| 08-00576-1 | 1523-01 |  | 0.5 | Transmission |  | Valves |  |  | Other | No Description | 2008-03-18 | 2008-04-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Lincoln
| 08-00577-1 | 1523-01 |  | 8 | Transmission |  | Valves |  |  | Construction Defect |  | 2008-03-18 | 2008-08-05 | Other | Redoped plug on valve | Steel/Wrought Iron |  | Lincoln | Loose plug- redoped tightened
| 08-00578-1 | 123 |  | 16 | Transmission |  | Valves |  |  | Other | No Description | 2008-03-18 | 2008-04-04 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Lincoln
| 08-00686-1 | DFM |  | 2 | Transmission |  | Regulator |  |  | Construction Defect |  | 2006-09-21 | 2008-12-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Roseville | Tightened plug on filter (pilot) right side mon.
| 08-00687-1 | 123 |  | 0.75 | Transmission |  | Valves |  |  | Construction Defect |  | 2008-09-21 | 2008-12-18 | Other | Fully opened valve | Steel/Wrought Iron |  | Roseville | Open valve tee all the way
| 08-00693-1 |  |  | 8 | Transmission |  | Other |  | Gauge tap caps | Other | Loose caps | 2008-09-21 | 2009-07-07 | Tighten Cap or Bolt |  | Steel |  | Lincoln | Tightened caps; Soap test
| 08-00693-1 | [10 empty] | 2008-09-21 | [5 empty] | Lincoln
| 08-00694-1 |  |  | 6 | Transmission |  | Fitting |  |  | Construction Defect |  | 2008-09-20 | 2008-12-17 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | El Dorado Hills | Shut in sides of station, blew down, resealed leaking fitting
| 08-00697-1 | 173 |  | 2 | Transmission |  | Valves |  |  | Other | Greased Valve | 2008-10-29 | 2010-04-19 | Other | Greased | Steel/Wrought Iron |  | Roseville | Greased & Accuated
| 08-00746-1 | 173 |  | 0.75 | Transmission |  | Fitting |  |  | Material Failure |  | 2008-11-25 | 2010-01-11 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Penryn | Run pin down on pin off tee, rebuild tee
| 09-01147-1 | DFM |  | 0.75 | Single Service |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2009-10-12 | 2010-12-21 | Tighten Cap/Bolt - Fitting |  | Steel |  | Yuba City | Re-doped & Tighted Bushing; Soap Test after repair , ok
| 09-02160-1 | 173 |  | 0.75 | Transmission |  | Valves |  |  | Other | required grease | 2009-11-03 | 2010-08-31 | Other | Greaed valve and operated valve | Steel/Wrought Iron |  | Auburn | Grease & Operated Valve
| 09-02161-1 | 173 |  | 0.75 | Transmission |  | Valves |  |  | Other | Greased | 2009-11-03 | 2010-01-22 | Other | Greased; | Steel/Wrought Iron |  | Newcastle | Greased
| 09-02162-1 | [10 empty] | 2009-11-03 | [5 empty] | Newcastle | Leak eliminated by repair on 41132104 valve replaced BJBQ 1-25-10
| 09-02163-1 | 173 |  | 0.75 | Transmission |  | Valves |  |  | Other | Greased | 2009-11-03 | 2010-01-22 | Other | Greased | Steel/Wrought Iron |  | Penryn
| 09-02164-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | O-ring | 2009-11-03 | 2010-01-27 | Other | Replaced O-rings and cap on V-tee | Steel/Wrought Iron |  | Penryn | Replaved V-tee cap and O-Rings; Soap tested cap @ line pressure / replaced cap and O-Rings in V-tee cap
| 09-02165-1 | 173 |  | 0.25 | Transmission |  | Valves |  |  | Other | plug | 2009-11-03 | 2010-01-22 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Rocklin | Greased plug and tightened
| 09-04387-1 | 173 |  | 6 | Transmission |  | Valves |  |  | Other | Added Grease | 2009-11-03 | 2010-01-15 | Other | Added Grease; | Steel/Wrought Iron |  | Loomis | Added Grease
| 09-04571-1 | 123 |  | 12 | Transmission |  | Other |  | Pin-Off tee | Unknown |  | 2009-11-10 | 2010-06-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Roseville | Tightened Pin-Off Tee
| 09-04572-1 | 123 |  | 6 | Transmission |  | Other |  | Pin-Off Tee | Unknown |  | 2009-11-10 | 2010-06-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Roseville | Tightened Caps on Pin-Off Tee
| 09-04573-1 | 123 |  | 12 | Transmission |  | Other |  | Pin-Off Tee | Unknown |  | 2009-11-10 | 2010-06-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Roseville | Tightened Pin-Off Tee
| 09-04574-1 | 123 |  | 16 | Transmission |  | Other |  | Pin-Off Tee | Unknown |  | 2009-11-10 | 2010-06-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Roseville | Tighten Pin-Off 01:00 Tee
| 09-20027-1 |  |  | 0.5 | Single Service |  | Plastic Tee Cap |  |  | Plastic Crack Failure |  | 2009-11-17 | 2009-11-17 | Aldyl A Overcap - Plastic |  | Aldyl A (Tan or Gray) |  | Auburn | Inst. ..."ALDYL-A CUEB...; Sopa Test; Excavated to expose SVC Tee to 413 Golo St. Found SVC TEE to 410 Golo St. 91/2" away from SVC Tee to 413 Golo St. SVC tee cap to 410 also leaking, installed Aldyl-A electro fusion over cap to 410 Golo St. SVC tee.
| 09-00101-1 |  |  | 0.75 | Single Service |  | Regulator |  |  | Material Failure |  | 2009-01-08 | 2009-01-08 | Other | Replaced with fisher 627 regulator | Steel/Wrought Iron |  | Yuba city | Rebuilt regulator
| 09-00125-1 |  |  | 2 | Transmission |  | Other |  | S/S fitting | Other | Loose; | 2009-04-17 | 2009-04-17 | Other | S.S. Fitting | Other | S. Steel | Live oak
| 09-00128-1 |  |  | 0.75 | Single Service |  | Other |  | Reg-Blow off | Equipment Malfunction |  | 2009-05-20 | 2009-05-21 | Other | Repair HPR Reg. | Steel/Wrought Iron |  | Yuba City | Rebuild Reg.; Call T&R Agter reg set was unearthed to determine where the actual leak was. set Reg. rebuilt and new H-Series relief valve installed.
| 09-00129-1 |  |  | 0.5 | Single Service |  | Body of Pipe |  |  |  |  | 2009-05-30 | 2009-05-30 | Deactivated Partial Service |  | Aldyl A (Tan or Gray) |  | Yuba City | Replaced 15" 1/2PL
| 09-00207-1 |  |  | 4 | Transmission |  | Other |  | Station Filters | Other | Gaskets | 2009-03-28 | 2009-03-28 | Other | Replaced Gaskets | Steel/Wrought Iron |  | El Dorado Hills | Replaced Station filter Gasket; Replaced inlet station filter gaskets. Soap tested after repairs were made.
| 09-93378-1 |  |  | 0.5 | Single Service |  | Plastic Tee Cap |  |  | Construction Defect |  | 2009-11-13 | 2009-11-13 | Replace Plastic Tee Cap - Plastic |  | PE2406 (Yellow or Orange) |  | Rocklin | Install new Tee Cap; Soap test new tee cap
| 09-00137-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2009-07-08 | 2009-07-17 | Other | Leak Clamp | Steel/Wrought Iron |  | Live Oak | Install 8" Leak Clamp/ BC weld out; INstall 8" - 6 Bolt leak clamp over pit area / OC weld out Clamp on 7-17-09
96 | 10-88548-1 | 302-072 | 0.47 | [8 empty] | 2010-10-20 | [5 empty] | Grimes
20 | 11-11039-1 |  |  | 0.25 | Distribution Main |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-02-07 | 2011-02-09 | Tighten Cap/Bolt - Fitting |  | Steel |  | Newcastle | Removed plug, doped plug, tighten/re-installed plug; Soap test OK
|  | 123 |  | 12 | Transmission | [6 empty] | 2006-06-08 | [5 empty] | Roseville
|  |  |  | 0.16 | [11 empty] | Steel/Wrought Iron |  | Roseville
|  | 123 |  | 12 | Transmission | [6 empty] | 2005-06-27 |  |  |  | Steel/Wrought Iron |  | Lincoln | Work dove for PG&E by Rockford/Delaney ... Boreing for new 16" L-123 replacing "old" 12" L-123 from 300 N of Moore Rd. Going S. 2000'
|  | 123 |  | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | Roseville
|  | 123 |  | 16 | Transmission | [6 empty] | 2005-06-19 |  |  |  | Steel/Wrought Iron |  | Rosville
|  | 123 |  | 12 | Transmission | [6 empty] | 2005-05-04 |  |  |  | Steel/Wrought Iron |  | Roseville
|  | 123 |  | 12 | Transmission | [6 empty] | 2005-04-05 |  |  |  | Steel/Wrought Iron |  | Roseville | Tree roots are into pipe wrap
|  | 173 |  | 12 | Transmission | [6 empty] | 2005-04-19 |  |  |  | Steel/Wrought Iron |  | Roseville
|  | 123 |  | 12 | Transmission | [6 empty] | 2005-04-22 |  |  |  | Steel/Wrought Iron |  | Roseville | Pipe wrap is in excellent condition
|  | 123 |  | 12 | Transmission | [6 empty] | 2005-04-22 |  |  |  | Steel/Wrought Iron |  | Roseville | Pipe wrap is in excellent condition
|  | 173 |  | 12 | Transmission | [6 empty] | 2005-08-01 |  |  |  | Steel/Wrought Iron |  | Roseville
|  | 173 |  | 16 | Transmission | [6 empty] | 2005-07-27 |  |  |  | Steel/Wrought Iron |  | Roseville
|  | 173 |  | 12 | Transmission | [6 empty] | 2005-07-27 |  |  |  | Steel/Wrought Iron |  | Roseville
|  | 173 |  | 8 | Transmission | [6 empty] | 2005-07-27 |  |  |  | Steel/Wrought Iron |  | Roseville
|  | 173 |  | 16 | Transmission | [6 empty] | 2005-08-01 |  |  |  | Steel/Wrought Iron |  | Roseville
|  | 173 |  | 6 | Transmission | [6 empty] | 2005-12-21 |  |  |  | Steel/Wrought Iron |  | Newcastle
|  | 173 |  | 6 | Transmission | [6 empty] | 2005-10-10 | [5 empty] | Newcastle | South-side OPHIR, Filled all pot holes with sand.
|  | 173 |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Auburn | Stand by only;Exposed 6" line 173 at A-196, Never saw 12" Line 173. ;
|  | 173 |  | 8 | Transmission | [6 empty] | 2005-06-21 |  |  |  | Steel/Wrought Iron |  | Roseville
|  | 173 |  | 12 | Transmission | [6 empty] | 2005-06-21 |  |  |  | Steel/Wrought Iron |  | Roseville
|  | 173 |  | 16 | Transmission | [6 empty] | 2005-06-17 |  |  |  | Steel/Wrought Iron |  | Roseville
|  | 173 |  | 6 | Transmission | [6 empty] | 2005-07-07 |  |  |  | Steel/Wrought Iron |  | Penryn
|  | 173 |  | 8 | Transmission | [6 empty] | 2008-06-17 |  |  |  | Steel/Wrought Iron |  | Roseville | @ 40" Deep to final grade
|  | 173 |  | 12 | Transmission | [5 empty] | ; ; ; | 2005-06-17 |  |  | @ 46" Deep to final grade | Steel/Wrought Iron |  | Roseville
|  | 173 |  | 16 | Transmission | [6 empty] | 2005-06-17 |  |  |  | Steel/Wrought Iron |  | Roseville
|  | 173 |  | 16 | Transmission | [6 empty] | 2005-06-17 |  |  |  | Steel/Wrought Iron |  | Roseville
|  | 173 |  | 16 | Transmission | [6 empty] | 2005-06-17 |  |  |  | Steel/Wrought Iron |  | Roseville
|  | 173 |  | 8 | Transmission | [6 empty] | 2005-04-19 |  |  |  | Steel/Wrought Iron |  | Roseville
|  | 173 |  | 8 | Transmission | [6 empty] | 2005-04-26 |  |  |  | Steel/Wrought Iron |  | Roseville
|  | 123 |  | 12 | Transmission | [6 empty] | 2005-04-26 |  |  |  | Steel/Wrought Iron |  | Roseville
|  | 173 |  | 12 | Transmission | [6 empty] | 2005-04-04 |  |  |  | Steel/Wrought Iron |  | Rocklin
|  | 173 |  | 12 | Transmission | [6 empty] | 2005-04-04 |  |  |  | Steel/Wrought Iron |  | Rocklin
|  | 173 |  | 12 | Transmission | [6 empty] | 2005-04-04 | [5 empty] | Rocklin
|  | 173 |  | 12 | Transmission | [6 empty] | 2005-04-04 |  |  |  | Steel/Wrought Iron |  | Rocklin
|  | 173 |  | 6 | Transmission | [6 empty] | 2005-02-02 |  |  |  | Steel/Wrought Iron |  | Penryn | Re-Dig Back fill compaction not to PG&E standards
|  | 173 |  | 8 | Transmission | [6 empty] | 2005-02-10 |  |  |  | Steel/Wrought Iron
|  | 173 |  | 6 | Transmission | [6 empty] | 2004-07-02 |  |  |  | Steel/Wrought Iron |  | Penryn
|  | 173 |  | 6 | Transmission | [6 empty] | 2004-07-02 |  |  |  | Steel/Wrought Iron |  | Penryn
|  | 173 | 16.58 | 6.625 | Transmission | [13 empty] | Installed Pressure gauge
|  | 173 |  | 2.375 | Transmission | [12 empty] | Newcastle
| 96-00091-1 |  |  | 8 | Transmission |  | Fitting |  |  | Construction Defect |  | 1996-05-14 | 1996-05-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Rocklin | Tightened bolts at fitting
20 | 89-00324-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1989-10-20 |  | Other |  | Steel/Wrought Iron |  | Rocklin | ;
15 | 90-00451-1 |  |  | 6 | Transmission |  | Physical/Mechanical Joint |  |  | Other | NO description | 1990-10-23 | 1990-10-24 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Grass Valley | Tightened bolts on flange to stop leak
15 | 90-00204-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1990-07-23 | 1990-07-23 | Replace Pipe |  | Other Plastic |  | Nevada City | Replaced 4' of 2" plastic with new 2" plastic pipe connection made with 2-2" plastic coupling
20 | 91-00255-1 |  |  | 12 | [7 empty] | 1991-11-22 | 1991-11-22 |  |  | Steel |  | Roseville | No leak- scratch on main only, repaired with full encirclement sleeve;
20 | 91-00176-1 |  |  | 6 | Distribution Feeder Main |  | Fitting |  |  | Other | No description | 1991-10-30 | 1991-10-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Rocklin | Shut down that side, remove cover, replace, and grease gasket, replace cover and test.
20 | 91-00163-1 | [10 empty] | 1991-08-27 | 1991-11-20 |  |  |  |  | El Dorado Hills | Those valves had just been operated by M&C this may have cleared any leakage.
20 | 91-00137-1 |  |  | 6 | Transmission |  | Other Welds |  |  | Other | No description | 1991-10-09 | 1992-01-27 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | Newcastle | Weld on 6" tip main leaking, weld sleeve over bad weld- hrd welds x-rayed
20 | 92-00040-1 |  |  | 0.75 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1992-09-15 | 1993-03-30 | Other | No decription | Steel/Wrought Iron |  | Roseville | Cut off service at Hi - Hi at valve left new valve frame and cover, greased valve- stopped leak.
20 | 92-00041-1 |  |  | 8 | Transmission |  | Valves |  |  | Other | No description | 1992-09-16 | 1992-11-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Rocklin | Tightened grease fitting (Above ground).
20 | 92-00042-1 | 123 |  | 2 | Service |  | Valves |  |  | Other | No description | 1992-09-17 | 1992-11-30 | Other | No description | Steel/Wrought Iron |  | Roseville | Greased valve (above ground)
20 | 92-00043-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other | no description | 1992-09-17 | 1992-10-26 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Roseville | Tighten Plug-redoped (Above Ground)
20 | 92-00044-1 |  |  | 2 | Service |  | Valves |  |  | Other | No description | 1992-09-17 | 1992-10-26 | Other | No description | Steel/Wrought Iron |  | Roseville | Greased 2 valves (above ground)
20 | 92-00045-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other | No description | 1992-09-25 | 1992-11-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Rocklin | Tightened grea fitting (above ground)
20 | 92-00046-1 |  |  | 2 | Service |  | Valves |  |  | Other | No decriptions | 1992-09-29 | 1992-10-26 | Other | No description | Steel/Wrought Iron |  | Loomis | Greased valve (above ground)
20 | 92-00047-1 |  |  | 6 | Transmission |  | Valves |  |  | Other | No description | 1992-10-02 | 1992-11-30 | Other | No description | Steel/Wrought Iron |  | El Dorado Hills | Greased valve (above ground)
22 | 92-00051-1 |  |  | 4 | Transmission |  | Other Welds |  |  | Other | No description | 1992-10-12 | 1993-11-03 | Patch Welded |  | Steel/Wrought Iron |  | Grass Valley | Arc welded around base of fitting
22 | 92-00052-1 |  |  | 4 | Transmission |  | Other Welds |  |  | Other | No description | 1992-10-12 | 1992-11-19 | Patch Welded |  | Steel/Wrought Iron |  | Grass Valley | Repaired weld
22 | 92-00053-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | No description | 1992-10-12 | 1992-11-19 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Grass Valley | Re-doped and tightened plug
22 | 92-00054-1 |  |  | 0.75 | Distribution Main |  | Regulator |  |  | Material Failure |  | 1992-10-13 | 1992-11-18 | Other | No description | Steel/Wrought Iron |  | Penn Valley | Rebuilt relief valve and reset regulator
22 | 92-00055-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Other | No description | 1992-10-13 | 1992-11-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Penn Valley | Re-doped and tightened cap
22 | 92-00056-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other | No description | 1992-10-15 | 1992-11-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Rough and Read | Tightened valve
22 | 92-00057-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other | No description | 1992-10-15 | 1992-11-18 | Other | No description | Steel/Wrought Iron |  | Penn Valley | Re-set regulator and relief valve
20 | 92-00088-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Other | No description | 1992-10-14 | 1992-11-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Auburn | Re-doped and tightened cap
20 | 92-00093-1 |  |  | 1 | Distribution Main |  | Physical/Mechanical Joint |  |  | Corrosion |  | 1992-11-05 | 1993-01-12 | Replace Pipe |  | Aldyl A (Tan or Gray) |  | Roseville | Replaced 4'1" plastic fused tap 1" coupling. Removed 4'1" plastic T... Mechincal fittings
21 | 93-00058-1 |  |  | 6 | Distribution Main |  | Other |  | No description | Other | No description | 1993-03-18 | 1993-03-31 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | El Dorado Hills | Dope and tighten plug
21 | 93-00059-1 |  |  | 6 | Distribution Feeder Main |  | Other |  | No description | Other | No description | 1993-03-18 | 1993-03-31 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | El Dorado Hills | Dope and tighten plug
2 | 93-00161-1 |  |  | 0.75 | Service |  | Other |  | No description | Other | No description | 1993-05-19 | 1993-07-07 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Roseville | Tighten nipple at top of srv. valve
20 | 93-00183-1 |  |  | 0.5 | Service |  | Tap Connection |  |  | Material Failure |  | 1993-06-21 | 1994-02-15 | Other | No description | Steel/Wrought Iron |  | Roseville | Over- cap put on
20 | 93-00247-1 |  |  | 0.25 | Distribution Main |  | Fitting |  |  | Other | No Description | 1993-10-07 | 1994-01-26 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Rocklin | Reg Pit, Tightened plug
20 | 93-00248-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other | No description | 1993-10-07 | 1993-12-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Rocklin | At valve, tightened static tap
20 | 93-00249-1 | [10 empty] | 1993-10-07 | 1993-12-29 |  |  |  |  | Rocklin | No leak found, checked w/ gas trace, no trace found
20 | 93-00250-1 |  |  | 0.25 | Service |  | Fitting |  |  | Other | No description | 1993-10-07 | 1993-12-20 | Other | No description | Steel/Wrought Iron |  | Rocklin | Tightened plug
20 | 93-00251-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other | No description | 1993-10-07 | 1993-12-20 | Other | No description | Steel/Wrought Iron |  | Rocklin | Tightened plug
20 | 93-00252-1 |  |  | 4 | Transmission |  | Fitting |  |  | Other | No description | 1993-10-07 | 1994-01-31 | Other | No description | Steel/Wrought Iron |  | Roseville | Greased Valve
20 | 93-00253-1 |  |  | 2 | Service |  | Valves |  |  | Other | No description | 1993-10-05 | 1995-04-04 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Rocklin | Operated valve, leak stopped (check Valve)
20 | 93-00254-1 |  |  | 0.75 | Service |  | Valves |  |  | Other | No description | 1993-10-05 | 1993-10-22 | Other | No description | Steel/Wrought Iron |  | Rocklin | Greased valve
20 | 93-00255-1 |  |  | 0.75 | Service |  | Valves |  |  | Other | No description | 1993-10-05 | 1993-10-22 | Other | No description | Steel/Wrought Iron |  | Rocklin | Greased Valve
20 | 93-00256-1 |  |  | 8 | Transmission |  | Other |  | No description | Other | No description | 1993-10-05 | 1994-01-29 | Other | No description | Steel/Wrought Iron |  | Rocklin | Greased Valve
20 | 93-00257-1 |  |  | 12 | Transmission |  | Fitting |  |  | Other | No description | 1993-10-05 | 1993-12-20 | Other | No description | Steel/Wrought Iron |  | Rocklin | Greased Valve
20 | 93-00258-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Other | No description | 1993-10-06 | 1994-04-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Roseville | Greased valve
20 | 93-00259-1 |  |  | 12 | Transmission | [6 empty] | 1993-10-06 | 1993-11-09 |  |  | Steel/Wrought Iron |  | Roseville | Rechecked w/flame...No herd of cows- no readins of gas; No leak on the check
20 | 93-00260-1 |  |  | 0.5 | Transmission |  | Fitting |  |  | Other | No description | 1993-10-06 | 1994-01-26 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Roseville | Tightened plug
20 | 93-00261-1 |  |  | 4 | Distribution Main |  | Other |  | No description | Other | No description | 1993-10-06 | 1993-12-20 | Other | No description | Steel/Wrought Iron |  | Roseville | Greased valve
20 | 93-00262-1 |  |  | 0.25 | Transmission |  | Fitting |  |  | Other | No description | 1993-10-13 | 1993-10-26 | Tighten Cap or Bolt |  | Other Plastic |  | Rocklin | Tightened plug
20 | 93-00263-1 |  |  | 6 | Distribution Main |  | Fitting |  |  | Other | No description | 1993-10-13 | 1993-10-26 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Rocklin | Tightened plug on fitter
20 | 93-00264-1 |  |  | 6 | Distribution Main | [6 empty] | 1993-10-13 | 1993-10-26 |  |  | Steel/Wrought Iron |  | Rocklin | No leak found
21 | 93-00265-1 |  |  | 0.25 | Distribution Main |  | Fitting |  |  | Other | No description | 1993-10-19 | 1993-12-22 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | El Dorado hills | Tightened plug
21 | 93-00266-1 |  |  | 0.5 | Distribution Main |  | Fitting |  |  | Other | No description | 1993-10-19 | 1993-12-22 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | El Dorada Hills | Tightened plug
21 | 93-00267-1 |  |  | 8 | Distribution Feeder Main |  | Other |  | Tighten Caps Test Valves | Other | Tighten Caps Test Valves | 1993-10-19 | 1994-02-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | El Dorado Hills | End of 8" 57L Main Tightened caps to stop leak
21 | 93-00268-1 |  |  | 8 | Distribution Main |  | Fitting |  |  | Other | No description | 1993-10-19 | 1994-01-29 | Other | No description | Steel/Wrought Iron |  | Rocklin | Greased valve
10 | 93-00269-1 | 176 |  | 6 | Transmission |  | Tap Connection |  |  | Material Failure |  | 1993-10-20 | 1993-10-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Auburn | Removed cap replaced "O" ring redoped cap stopped leak
20 | 93-00270-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Other | No Description | 1993-10-20 | 1993-12-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Ophir | Tightened plug
20 | 93-00271-1 |  |  | 0.75 | Service |  | Physical/Mechanical Joint |  |  | Other | No Description | 1993-10-25 | 1994-04-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Ophir | Tightened cap on pin off tee
20 | 93-00272-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Other | No Description | 1993-10-25 | 1993-12-20 | Other | No Description | Steel/Wrought Iron |  | Ophir | Greased Valve
22 | 93-00273-1 |  |  | 4 | Distribution Main |  | Fitting |  |  | Other | No Description | 1993-10-12 | 1993-11-03 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Grass Valley | Tightened plug on safety device
22 | 93-00274-1 |  |  | 4 | Distribution Main |  | Fitting |  |  | Other | No Description | 1993-10-12 | 1993-11-03 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Grass Valley | Tightened fitting
22 | 93-00275-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Other | No Description | 1993-10-13 | 1993-11-08 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Penn Valley | Tightened Union
20 | 93-00337-1 |  |  | 2 | Service |  | Fitting |  |  | Damage by Natural Forces |  | 1993-11-24 | 1994-03-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Rocklin | Bypassed set and repaired plug
20 | 94-00380-1 |  |  | 4 | Transmission |  | Regulator |  |  | Other | No Description | 1994-08-31 | 1995-07-09 | Other | No Description | Steel/Wrought Iron |  | Lincoln | Rebuilt static ... regs
22 | 94-00346-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Damage by Natural Forces |  | 1994-10-26 | 1996-05-04 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Penn Valley | Tightened Union
20 | 94-00290-1 | [10 empty] | 1994-09-21 | [5 empty] | Roseville | Same Lk. 93-00253
20 | 94-00291-1 |  |  | 0.75 | Service |  | Valves |  |  | Damage by Natural Forces |  | 1994-09-21 | 1995-10-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Roseville | Tightened plug
20 | 94-00292-1 |  |  | 0.75 | Service |  | Valves |  |  | Damage by Natural Forces |  | 1994-09-26 | 1995-04-10 | Other | No Description | Steel/Wrought Iron |  | Roseville | Greased valve
20 | 94-00293-1 |  |  | 2 | Distribution Feeder Main |  | Valves |  |  | Damage by Natural Forces |  | 1994-09-26 | 1995-02-23 | Other | No Description | Steel/Wrought Iron |  | Roseville | Greased valve
20 | 94-00294-1 | 173 |  | 8 | Transmission |  | Fitting |  |  | Damage by Natural Forces |  | 1994-09-27 | 1995-04-05 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Rocklin | Found leak on 1/4" ...line- repaired same
20 | 94-00295-1 |  |  | 2 | Service |  | Regulator |  |  | Material Failure |  | 1994-09-27 | 1995-04-10 | Other | No Description | Steel/Wrought Iron |  | Rocklin | Replaced Diaphram on monitor rey
20 | 94-00296-1 |  |  | 4 | Service |  | Valves |  |  | Damage by Natural Forces |  | 1994-09-27 | 1995-04-10 | Other | No Description | Steel/Wrought Iron |  | Rocklin | Greased valve
20 | 94-00298-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Damage by Natural Forces |  | 1994-09-29 | 1995-04-04 | Other | No Description | Steel/Wrought Iron |  | Rocklin | Greased valve
20 | 94-00299-1 |  |  | 6 | Transmission |  | Valves |  |  | Damage by Natural Forces |  | 1994-09-29 | 1995-10-13 | Other | No Description | Steel/Wrought Iron |  | Rocklin | greased valve
20 | 94-00300-1 |  |  | 4 | Distribution Main |  | Valves |  |  | Damage by Natural Forces |  | 1994-10-06 | 1996-01-20 | Other | No Description | Steel/Wrought Iron |  | Rocklin | Greased valve
20 | 94-00301-1 |  |  | 2 | Distribution Main |  | Tap Connection |  |  | Material Failure |  | 1994-10-11 | 1996-01-04 | Other | No Description | Aldyl A (Tan or Gray) |  | Loomis | Installed over cap
20 | 94-00302-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Damage by Natural Forces |  | 1994-10-17 | 1995-09-25 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Penryn | Tightened Union
20 | 94-00303-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Damage by Natural Forces |  | 1994-10-17 | 1995-09-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Penryn | Tightened packing nut
20 | 94-00304-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Material Failure |  | 1994-10-18 | 1994-10-28 | Other | No Description | Steel/Wrought Iron |  | Newcastle | Replaced relief valve
20 | 94-00305-1 |  |  | 0.75 | Transmission |  | Regulator |  |  | Damage by Natural Forces |  | 1994-10-18 | 1995-09-21 | Other | No Description | Steel/Wrought Iron |  | Auburn | Repaired relief valve
20 | 94-00306-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Damage by Natural Forces |  | 1994-10-18 | 1995-11-02 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Auburn | Tightened fitting
21 | 94-00307-1 |  |  | 0.75 | Distribution Feeder Main |  | Fitting |  |  | Damage by Natural Forces |  | 1994-10-19 | 1995-10-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | El Dorado Hills | Tightened fitting
20 | 95-00038-1 |  |  | 0.75 | Service |  | Physical/Mechanical Joint |  |  | Other | No Description | 1995-04-11 | 1995-04-11 | Replace Pipe |  | Steel/Wrought Iron |  | Newcastle | Replaced 3' of 3/4" seamless tested pipe. Threads were leaking at valve.; Replaced 3' of 3/4" seamless tested pipe with 3/4" socket weld couplings to fix leakage at threads going into curb valva, cleared with load control to weld.
22 | 95-00041-1 |  |  | 0.75 | Service |  | Fitting |  |  | Damage by Natural Forces |  | 1995-04-06 | 1995-09-15 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Grass Valley | Tightened cap re-doped
22 | 95-00042-1 | [10 empty] | 1995-04-06 | [5 empty] | Grass Valley | 3/7/96 0 Delete Leak 3
22 | 95-00063-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Damage by Natural Forces |  | 1995-02-21 | 1995-09-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Grass Valley | Re-doped cap and tightened union
22 | 95-00064-1 |  |  | 0.75 | Transmission |  | Other |  | No Description | Corrosion |  | 1995-02-25 | 1996-06-20 | Other | No Description | Steel/Wrought Iron |  | Grass valley | On fire valve stem, replaced "O" rings on pin-off tee cap
22 | 95-00065-1 | [10 empty] | 1995-02-25 | [5 empty] | Grass Valley | 4/18/97 50PPM In fire valve box; 3/15/96 50PPM
22 | 95-00066-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Other | No Description | 1996-02-25 | 1997-03-24 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Grass Valley | Re-doped ...cap. on key
22 | 95-00067-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Damage by Natural Forces |  | 1995-02-25 | 1995-09-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Grass Valley | Re-doped cap
22 | 95-00070-1 | [10 empty] | 1995-07-10 | [5 empty] | Penn Valley | Leak on Fire valve in street down grade leak single source...
20 | 95-00089-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Other | No Description | 1995-10-03 | 1996-04-19 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Roseville | Tighten 1/2" Plug
20 | 95-00090-1 | [10 empty] | 1995-10-03 | [5 empty] | Roseville | Delete
20 | 95-00091-1 | [10 empty] | 1995-10-03 | [5 empty] | Roseville | Delete
20 | 95-00092-1 |  |  | 4 | Transmission |  | Valves |  |  | Other | No Description | 1995-10-04 | 1996-03-08 | Other | No Description | Steel/Wrought Iron |  | Rocklin | Grease valve
20 | 95-00093-1 |  |  | 8 | Transmission |  | Valves |  |  | Other | No Description | 1995-10-04 | 1996-01-28 | Other | No Description | Steel/Wrought Iron |  | Rocklin | Greased valve, leaking through valve stem
20 | 95-00094-1 |  |  | 8 | Transmission |  | Valves |  |  | Other | No Description | 1995-10-04 | 1996-01-28 | Other | No Description | Steel/Wrought Iron |  | Rocklin | Greased valve, leaking though grease extension
20 | 95-00095-1 | [10 empty] | 1995-10-04 | [5 empty] | Rocklin | Deleted
20 | 95-00096-1 | [10 empty] | 1995-10-05 | [5 empty] | Rocklin | Deleted
20 | 95-00097-1 | [10 empty] | 1995-10-11 | [5 empty] | Rocklin | Deleted
20 | 95-00098-1 |  |  | 2 | Transmission |  | Valves |  |  | Damage by Natural Forces |  | 1995-10-11 | 1996-07-06 | Other | No Description | Steel/Wrought Iron |  | Rocklin | Greased valve
20 | 95-00099-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1995-10-13 | 1997-03-17 | Replace Pipe |  | Steel/Wrought Iron |  | Rocklin | Inserted 1/2" plastic
20 | 95-00100-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1995-10-13 | 1997-03-17 | Replace Pipe |  | Steel/Wrought Iron |  | Rocklin | Inserted 1/2" plastic
20 | 95-00101-1 | [10 empty] | 1995-10-16 | [5 empty] | Loomis | Deleted
20 | 95-00102-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | No Description | 1995-10-18 | 1996-04-19 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Loomis | Dope and retighten 1/2 Plug. In let press tap
20 | 95-00103-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Other | No Description | 1995-10-18 | 1996-03-08 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Loomis | Tighten plug on metric valve
20 | 95-00104-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Other | No Description | 1995-10-18 | 1996-04-19 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Auburn | Tighten union D/S of reg's
21 | 95-00106-1 | [10 empty] | 1995-10-26 | [5 empty] | El Dorado Hills | Deleted
20 | 96-00091-1 |  |  | 8 | Transmission |  | Fitting |  |  | Corrosion |  | 1996-05-14 | 1996-05-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Rocklin | Tightened bolts at fittings
22 | 96-00300-1 |  |  | 6 | Transmission |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1996-11-21 | 1997-06-12 | Other | No Description | Steel/Wrought Iron |  | Grass Valley | Tightened plug and fittings on V-112- Installed new bolts and insalation kit to repair flange
22 | 97-00402-1 |  |  | 1 | Service |  | Fitting |  |  | Construction Defect |  | 1997-10-30 | 1997-11-17 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Penn Valley | Replaced "O" rings on unions
22 | 97-00403-1 |  |  | 0.75 | Service |  | Fitting |  |  | Damage by Natural Forces |  | 1997-10-30 | 1997-12-19 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Penn Valley | Tightened Union
22 | 97-00404-1 | [10 empty] | 1997-11-04 | [5 empty] | Grass Valley | Deleted, Above ground leak convert to service tag
22 | 97-00406-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Damage by Natural Forces |  | 1997-11-04 | 1998-09-24 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Grass valley | Tightened Metric valva
20 | 97-00463-1 | [10 empty] | 1997-11-24 | [5 empty] | Rocklin | Dellete
21 | 97-00482-1 | [10 empty] | 1997-12-15 | [5 empty] | El Dorado Hills | Deleted
21 | 97-00483-1 | [10 empty] | 1997-12-15 | [5 empty] | El Dorado Hills | Deleted, Above ground leak convert to svc. tag, delte
21 | 97-00484-1 | [10 empty] | 1997-12-15 | [5 empty] | El Dorado Hills | Deleted, Above ground leak convert to svc. tag delte 1-22-98
20 | 97-00504-1 | [10 empty] | 1997-11-03 | [5 empty] | Penryn | Deleted, Above ground leak convert to svc. tag, delete 1-22-98
20 | 97-00505-1 |  |  | 1 | Service |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1997-10-30 | 1999-04-29 | Replace Pipe |  | Aldyl A (Tan or Gray) |  | Roseville | Inserted 1/2" PL service in 1" casing
20 | 97-00506-1 | [10 empty] | 1997-10-30 | [5 empty] | Roseville | Deleted, Above ground leak convert to svc. tag delete 1-22-98
20 | 97-00507-1 | [10 empty] | 1997-10-30 | [5 empty] | Lincoln | Deleted, Above ground leak convert to svc. tag delete 1-22-98
20 | 97-00508-1 | [10 empty] | 1997-10-30 | [5 empty] | Lincoln | Deleted, above ground leak convert to svc. tag delete 1-22-98
20 | 97-00509-1 | [10 empty] | 1997-10-30 | [5 empty] | Roseville | Deleted, Above ground leak convert to svc. tag delete 1-22-98
20 | 97-00539-1 | [10 empty] | 1997-11-03 | [5 empty] | Roseville | Deleted
22 | 98-00116-1 | [10 empty] | 1998-10-12 | [5 empty] | Penn Valley
22 | 98-00118-1 | [10 empty] | 1998-10-13 | [5 empty] | Penn Valley
20 | 98-00066-1 |  |  | 6 | Transmission |  | Physical/Mechanical Joint |  |  | Damage by Natural Forces |  | 1998-07-08 | 1998-07-08 | Replace Pipe |  | Steel/Wrought Iron |  | Rocklin | Replaced. greased lines
20 | 98-00094-1 | 173 |  | 6 | Transmission |  | Valves |  |  | Other | No Description | 1998-09-02 | 1999-09-17 | Other | No Description | Steel/Wrought Iron |  | Newvcastle | Greased valve
20 | 98-00095-1 | [10 empty] | 1998-09-02 | [5 empty] | Newvcastle | Deleted
20 | 98-00097-1 | [10 empty] | 1998-09-10 | [5 empty] | Rocklin | Deleted
20 | 98-00098-1 | [10 empty] | 1998-09-11 | [5 empty] | Lincoln | Deleted, above ground leak converted to svc. tag
20 | 98-00099-1 |  |  | 0.38 | Distribution Main |  | Tap Connection |  |  | Damage by Natural Forces |  | 1998-09-10 | 1998-09-29 | Other | No Description | Steel/Wrought Iron |  | Rocklin | Repaired leaking static lines
22 | 98-00117-1 |  |  |  | Distribution Main |  | Valves |  | Fittings | Other | No Description | 1998-10-12 | 1998-12-22 | Tighten Cap or Bolt | & Service Valve | Steel | Stainless Steel | Grass Valley | Repaired leaking valve and static lines
| 99-00002-1 |  |  | 2 | Transmission |  | Valves |  |  | Damage by 3rd Party |  | 1999-01-06 | 1999-01-06 | Other | Repair valve ext. | Steel/Wrought Iron |  | Roseville | Blowing in valve frame repaired valve. Repair tightened extension and grease extension to valve; Repair high head extension, grease ext. grease valve and exercise
| 99-00207-1 |  |  | 2 | Transmission |  | Fitting |  |  | Construction Defect |  | 1999-05-25 | 2000-10-18 | Other | Fitting | Other | TR 418 | Roseville | Replaced leaking 2" ... (plastic)
20 | 99-00207-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 1999-05-25 | 2000-10-18 | Replace Pipe |  | Other Plastic |  | Roseville | Replaced leaking 2" Pl. elbow at PLX STL transition fitting
| 99-00383-1 | [10 empty] | 1999-10-18 | [5 empty] | Roseville
| 99-00398-1 |  |  | 4 | Distribution Main |  | Valves |  |  | Other | Valve | 1999-11-15 | 1999-12-08 | Other | Repair valve | Steel/Wrought Iron |  | New Castle | Repaired leak at valve. Please Bar Test (Crew) Prospect reg. pit. leak on metric valve.
| 99-00411-1 | [10 empty] | 1999-10-09 | [5 empty] | Edh | Delete Above ground leak svc. tag
| 99-00414-1 |  |  | 12 | Transmission |  | Valves |  |  | Other | Needed Grease | 1999-10-25 | 2000-03-10 | Other | Grease | Steel/Wrought Iron |  | Roseville | at lid to reg station. Rep by greasing valve S. Nakashima
| 99-00415-1 |  |  | 8 | Transmission |  | Other |  | No Description | Other | No Description | 1999-10-25 | 2000-03-13 | Other | No Description | Steel/Wrought Iron |  | Linc | Normal Operations. At reg vent. Sam Nakashima venting reg
| 00-00023 |  |  | 4 | Transmission |  | Fitting |  |  | Construction Defect |  | 2000-02-04 | 2000-02-04 | Other | No Description | Steel/Wrought Iron |  | Roseville | Greased Valve; reg pit do not number
| 00-00368-1 |  |  | 0.5 | Transmission |  | Other |  | Filter | Construction Defect |  | 2000-12-11 | 2001-01-11 | Other | Tightened nipples | Steel/Wrought Iron |  | Newcastle | Tar doped and tightened 1/2" nipple for valve on fitting
|  |  |  | 4.5 | Gathering | [7 empty] | 1999-09-23 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  |  | Cut-cap @ V-26 to retire ...
19 | 94-10001-1 | [10 empty] | 1994-10-21 | [5 empty] | Gridley | Downgraded 12/94; 12-5-94 2% at valve ;
|  | 169 |  | 4 | Gathering | [7 empty] | 2002-04-29 |  |  | Other | GRB SLMS |  | Cut cap L-169; Soap cap save valve @ 100PSI
|  |  |  | 4.5 | [8 empty] | 2002-04-26 |  |  | Other | GRB SLMS |  | Remove old valve 16 tie-in with new line; Soap @ 100 PSI
|  |  |  | 3.5 | Transmission | [5 empty] | ; ; |  | 2002-04-26 |  |  | Other | SMLS |  | Remove old valve piping install new stuff; Soap test @100 PSI; Cut off at spragne 1-A
[16 empty] | Steel/Wrought Iron |  |  | .250 w.t.
[16 empty] | Steel/Wrought Iron |  |  | Cut off wood plug
[16 empty] | Steel/Wrought Iron |  |  | 18" Cant sava, cut capp, wood plug
Cut and cap valve 21 line 193
Steel/Wrought Iron
|  | 193 | [13 empty] | Steel/Wrought Iron |  |  | C/o at road to retire 12-1 and leak. Uprated 6" to TP pressure to feed high-high set.
[16 empty] | Steel/Wrought Iron |  |  | Cut and cap sava 6" abandon
|  |  |  | 6 | [11 empty] | Steel/Wrought Iron |  |  | 4" Abandon remove riser; c/o 6" 193 w/o malton 4-1 and cap 6" 163 crossing RoHH to west for Hi to hi Set.; Light oil internally; Didn"t expose main
|  |  |  | 8 | [8 empty] | 1990-06-19 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  |  | 1" valve tee cap leak. Re-doped, retightened, 3/4" feed to HPR set..
| 09-60080-1 | 50 |  | 0.75 | Transmission |  | Fitting |  |  | Other | Fitting | 2009-06-16 | 2009-06-26 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Gridley
| 09-60081-1 |  |  | 08.00 & 04.00 | Transmission |  | Fitting |  |  | Construction Defect |  | 2009-06-17 | 2009-07-08 | Replace TP Main |  | Steel/Wrought Iron |  | Oroville | Replaced 42+/- ft. 8" & 4" steel; Replaced 42+ft. T/P Pressure pipe 8" & 4"
| 09-60090-1 | 50A |  | 0.75 | Transmission |  | Other |  | Grease fitting in fire valve | Construction Defect |  | 2009-06-24 | 2009-12-17 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | Gridley
| 09-60091-1 |  |  | 0.75 | Distribution Main >60 PSIG and <20% SYMS |  | Other Mechanical Joint |  | Threads | No/Deteriorated Pipe Dope |  | 2009-06-24 | 2010-12-02 | Tighten Cap/Bolt - Fitting |  | Steel |  | Gridley | Repaired leaks on threaded fittings on HPR boxl Tightened threads- stopped leaks, repaired leaks on threaded fittings in HPR box.
| 09-60096-1 | 50 |  | 0.75 | Transmission |  | Other |  | No Description | Construction Defect |  | 2009-07-16 |  |  |  | Steel/Wrought Iron |  | Gridley
13 | 09-60135-1 | 167 |  | 2 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2009-11-19 | 2011-05-10 | Tighten Cap/Bolt - Fitting |  | Steel |  | Gridley | Re-tighten valve; Tightened body bleed valve
| 08-60081-1 |  |  | 3 | Transmission |  | Valves |  |  | Construction Defect |  | 2008-11-04 | 2008-11-04 | Other | Grease | Steel/Wrought Iron |  | Biggs | *Employees on site when reported by 3rd party at site; Ryan Brandon greased leaking 3" valve and repaired leaks.
| 08-60041-1 |  |  | 2 | Distribution Main |  | Valves |  |  | Other | Dry Grease | 2008-09-11 | 2009-05-08 | Other | Grease | Steel/Wrought Iron |  | Oroville
| 08-60042-1 |  |  | 2 | Distribution Main |  | Other Welds |  |  | Unknown |  | 2008-09-11 | 2009-05-08 | Fill Weld - Weld |  | Steel/Wrought Iron |  | Oroville | Leak repaired with weld @1/4" nipple
| 02-52336-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Digin |  | 2002-05-22 | 2002-05-22 | Replace Dist Main < 100 ft |  | Aldyl A (Tan or Gray) |  | Gridley | Spliced in 8' of 2" TR-418 plastic pipe
| 04-52436-1 | Oroville DFM |  | 6.62 | Transmission |  | Fitting | Other | WELD | Construction Defect |  | 2004-01-23 | 2004-03-15 | Replace Dist Main < 100 ft |  | Steel/Wrought Iron |  | Oroville | Replaced 97' of 6" (TP) DFM; Replaced 97' of 6.625" x42 .188wt. and 2PCF's to repair leak
13 | 97-52067-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Digin |  | 1997-05-19 | 1997-05-19 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Gridley | Temporarilly squeezed and welded up 3/4" trans svc.; Temp c/o 3/4" line until G.C. makes permanent replacement Repairs of Pipe.
13 | 97-52067-1 |  |  | 0.75 | [7 empty] | 1997-05-19 |  |  |  | Steel |  | Gridley | GSR 50-184; Bored and installed 90ft of 3/4" GRB SMLS steel pipe to replace damaged 3/4" steel pipe installed in 1952
19 | 96-10005-1 |  |  | 6.62 | Distribution Feeder Main |  | Other |  |  | Other |  | 1996-12-02 | 1998-10-22 | Other |  | Steel/Wrought Iron |  | Oroville | Replaced main 6N91196-98
| 96-10005-1 |  |  | 6 | [11 empty] | Steel |  | Oroville | Tie-in location Pomona ave
|  |  |  | 6 | [13 empty] | Oroville | Tie-in loc. Feather River Blvd.
19 | 96-10004-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1996-12-02 | 1998-09-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Oroville | Tightened flauge nuts grased and operated
|  |  |  | 4 | [11 empty] | Steel |  | Oroville | Replaced leaking valve V-16 Placed grease stem. John Rossi re-packed valve as per Larry straple.
| 95-50976-1 |  |  | 2 | Transmission |  | Other |  |  | Other |  | 1995-10-23 | 1995-11-06 | Other |  | Steel/Wrought Iron |  | Biggs | Repaired leak on pilot regs; Both reg pits front veteran's builder.
10 | 95-50971-1 |  |  | 8 | Transmission |  | Fitting |  |  | Other |  | 1995-10-14 | 1996-04-10 | Other |  | Steel/Wrought Iron |  | Orovillle | Greased valve
13 | 95-50943-1 |  |  | 0.75 | Distribution Main |  | Regulator |  |  | Other |  | 1995-03-19 | 1997-12-31 | Other |  | Steel/Wrought Iron |  | Butte Co. | Rebuilt regulator replaced small leak on diaghram revieved tag 12-30-97
13 | 95-50434-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1995-02-10 | 1996-08-26 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Oroville | Exposed valve greased and tightened gland
13 | 95-50434-1 | [10 empty] | 1995-02-10 | [5 empty] | Oroville
13 | 94-50422-1 |  |  | 6 | Transmission |  | Fitting |  |  | Construction Defect |  | 1994-10-19 | 1996-05-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Oroville | Doped and retightened 3/4" stee plug on 6" pressure control fitting
13 | 85-00188-1 |  |  | 6 | Distribution Main |  | Valves |  |  | Other |  | 1985-12-04 | 1985-12-16 | Other |  | Steel/Wrought Iron |  | Oroville | Greased main line valve
13 | 85-00185-1 |  |  | 2 | Transmission |  | Regulator |  |  | Other |  | 1985-12-03 | 1986-01-31 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Gridley | Tighten nuts on reg diaphragm chamber on pilot reg, left normal.
13 | 85-00137-1 | [10 empty] | 1985-10-21 | [5 empty] | Oroville | Duplicate
13 | 85-00173-1 | [10 empty] | 1987-09-23 | [5 empty] | Oroville
13 | 85-00173-1 | [10 empty] | 1985-10-21 | [5 empty] | Oroville
13 | 85-00122-1 | [10 empty] | 1987-09-23 | [5 empty] | Oroville
13 | 85-00122-1 | [10 empty] | 1985-09-12 | [5 empty] | Oroville
13 | 85-00120-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1985-09-12 | 1985-12-06 | Other | Replace Reg. | Steel/Wrought Iron |  | Oroville | Replaced leaking H-202 Relief valve
13 | 85-00117-1 |  |  | 0.75 | Service |  | Fitting |  |  | Construction Defect |  | 1985-09-11 | 1986-02-03 | Other | No Description | Steel/Wrought Iron |  | Oroville | Tightened union inside H.P.H. box and greased valve
13 | 85-00116-1 |  |  | 4 | Distribution Main |  | Valves |  |  | Other |  | 1985-09-11 | 1986-01-05 | Other | Grease valve | Steel/Wrought Iron |  | Oroville | Found ML valve leaking slightly, greased same & left normal
13 | 85-00065-1 |  |  | 3 | Distribution Main |  | Other |  |  | Corrosion |  | 1985-05-23 | 1986-04-30 | Clamp |  | Steel/Wrought Iron |  | Richvale | Leak upgraded changed leak No. From GRD-3 83-00024 to GRD-2; Installed leak clamp
13 | 85-00017-1 |  |  | 2 | Transmission |  | Regulator |  |  | Other |  | 1985-01-30 | 1985-02-27 | Other |  | Steel/Wrought Iron |  | Gridley | Tighten bolt on reg.
13 | 85-00016-1 |  |  | 2 | Transmission |  | Regulator |  |  | Other |  | 1985-01-30 | 1985-02-27 | Other |  | Steel/Wrought Iron |  | Gridley | Tighten fitting on Reg.
13 | 85-00206-1 |  |  | 2 | Transmission |  | Regulator |  |  | Other |  | 1985-12-03 | 1986-01-31 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Gridley | Tighten nuts on Reg. Diaphragm chamber on pilot Reg., Left normal
13 | 84-00145-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Other |  | 1984-09-14 | 1988-05-04 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Oroville | Tightened metric valve plug
13 | 83-00193-1 |  |  | 0.75 | Other |  | Physical/Mechanical Joint |  |  | Other |  | 1983-11-30 | 1983-12-22 | Other | Tighten Union | Steel/Wrought Iron |  | Oroville | Line Use- "O"= Other; Found small bubble at Union repaired same.
13 | 82-00028-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1982-05-02 | 1982-05-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Biggs | Meter was hit and broke off the serv. valve, repaired with new riser.
13 | 81-00142-1 |  |  | 0.25 | Other |  | Valves |  |  | Other |  | 1981-10-20 | 1981-10-30 | Other |  | Steel/Wrought Iron |  | Oroville | Line Use- "O"=Other ;.032% not enough gas to run on my gas scope. Found very very very small leak on 1/4" metric plug, tightened same.
13 | 81-00141-1 |  |  | 0.25 | Other |  | Valves |  |  | Other |  | 1981-10-20 | 1981-10-30 | Other |  | Steel/Wrought Iron |  | Oroville | Line Use "O"= Other; Found metric leaking at plug, turned off and tightened same
13 | 80-20038-1 |  |  | 0 |  |  | Body of Pipe |  |  | Corrosion |  | 1981-09-10 | 1981-09-10 | Other |  | Steel/Wrought Iron |  | Oroville | Line Use "O"= Other; meter leak code 3; Removed meter manifold and replace 1A curb meter leaking through dial cover.
13 | 80-20038-1 | [10 empty] | 1980-09-10 | [5 empty] | Oroville | Called in leak to KME 220 (Oroville) #1- Ordone in air
13 | 80-40013-1 |  |  | 2 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-06-04 | 1980-06-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Live Oak | Line Use = "O" = Other; Not reportable; 1/4" metric valve was broken off of large volume meter set. Rewelded 1/4" nipple onto 2" house line to repair
13 | 80-40012-1 | 167 |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-05-28 | 1980-05-30 | Other | Abandoned - 4488A | Steel/Wrought Iron |  | Gridley | Leak St = Line 167; Abonded 4488A
13 | 79-20160-1 |  |  |  | Other |  | Other |  |  | Other |  | 1979-07-02 | 1979-07-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Oroville | Line Use "O" = Other; Meter leak not entered computer for file 8-24-79; 30 PPM under house 50-70 1 ft. in front of riser. Replaved gas meter; Found 5B Gas meter leaking at seam
13 | 79-20026-1 | [5 empty] | Fitting |  |  | Construction Defect |  | 1979-04-04 | [5 empty] | Palermo | ; Line Use "O" = Other; Grade 3; Customers equipment . Costomer notified - will make repairs- leak is in open area- no hazards very small.
13 | 78-20001-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-03-14 | 1978-08-10 | Clamp |  | Steel/Wrought Iron |  | Richvale | One pit only leaking, main in generally good condition. Installed 3" x 4" Skinner clamp no Anode Installed.
13 | 76-40055-1 |  |  | 0.75 |  |  | Body of Pipe |  |  | Corrosion |  | 1976-12-14 | 1976-12-15 | Other | No Description | Steel/Wrought Iron |  | Gridles | Line Use "O" = Other; Ref. No. 77-60000-1; Mapped: RFM; Additional leakage new leak number 77-60006-1; Cut and test 36' of 3/4" ser. Cut off this part of ser. to repair leak. Thransfer to main on S.Side. Instpection and repair.
13 | 76-40038-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-08-12 | 1976-08-12 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | s.w. Gridley | See DWG. Attached; Ripper cut hole in 16" L-167
13 | 76-40012-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-02-10 | 1976-02-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Palermo | Clear; Pipe was cut by loader blade added 36" of 3/4" STL pipe and lovered 8'
13 | 76-60107-1 |  |  | 0.75 |  |  | Other |  |  | Other |  | 1976-08-17 | 1978-02-10 | Other |  | Steel/Wrought Iron |  | Oroville | Line Use "O" = Other; Soaped all fittings, repaired Fuzz Leak on Meter
13 | 76-60106-1 | [5 empty] | Meter |  |  | Construction Defect |  | 1976-08-17 | 1977-11-09 | Other |  | Cast Iron |  | Oroville | Line use "O" = Other; Found leak at point where meter head connected to body- Tightened all screws
13 | 75-00039-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1975-04-09 | 1975-05-23 | Other |  | Steel/Wrought Iron |  | Gridley
13 | 75-00038-1 |  |  |  | Transmission | [6 empty] | 1975-04-09 | [5 empty] | Gridley | .01% 4-9-80, 0% 4-1-81, Delete 4/14/81; All area's marked in "X" leaking about 6' off the road; All area's marked in"X" leaking about 6' off the road. .02 3-23-79 F.M.
13 | 75-00036-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Material Failure |  | 1975-04-09 | 1978-05-25 | Weld Over Sleeve or Can | CAN 2" MAIN | Steel/Wrought Iron |  | Live Oak | Can 2" main, same leak as 74-00182-1 Code 3; Install permanent clamp for temp. use. 1" crack on bottom of main, Install 6" can on 2" main; Additonal leakage found just west of original leak- new leak sheet made out 6-15-78
Found leak 1" crack on bottom of 2" trans main 4-26-78 R.L.
13 | 75-20026-1 |  |  | 0.75 |  |  | Body of Pipe |  |  | Corrosion |  | 1975-11-04 | 1975-11-13 | Patch Weld - Weld |  | Steel/Wrought Iron |  | Oroville | Line Use "O" = Other, Ref. No. 74-20160-1, Clear; Cap on M-2 Fitting was leaking repaired by tightening the cap, 3/4" gas line under sidewalk to blow off. Valve was leaking, repaired leak by squeezing off the line and welding off cut 3/4" line at curb line
13 | 75-20014-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  |  | 1975-01-15 | Patch Welded |  | Steel/Wrought Iron |  | Gridley | Leak upgraded, Changed leak no. from 74-00135-1 to 75-20014-1; Leak in Reg. Between st. and building yellw "X" leak on 8" main
13 | 74-00182-1 | [10 empty] | 1974-06-25 | [5 empty] | Live Oak | Two forms: Leak, same leak to 75-00036-1; Leak in main n/side rd. 20' e/o drive way to Live Oak High School parking lot. 10% L.E.L 4-16-75
13 | 74-00182-1 | [10 empty] | 1974-04-26 | [6 empty] | 6-25-74 F.M. Chage to #3; Leak in main n/side of road 20' e/o drive way to Live Oak High School parking lot
13 | 74-20204-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1974-10-03 | 1975-08-11 | Other |  | Steel |  | Thermaito | 8-2-75 .3% Gas 9-17-75; 35% Lev. at H.P.R. both sides of box are clear. Leak as green plug lubricated valve- 2 small small fuzz leaks of no significance, still leaking 9-2-75 3% 9-17-75. Repaired gas leak by tightening the fitting in the H.P.R Box.
12 | 74-20134-1 |  |  | 1.25 |  |  | Other |  | No Description | Corrosion |  | 1974-09-13 |  | Other | No Description | Steel/Wrought Iron |  | Oroville | Line Use "O" = Other, Cut off leaking customers pipe. (Unsused). Aerated earth around building with compressed air - for 35 minutes. No gas indication around grounds or in building. Customers pipe; Cut and plugged line at stop cock; leak in 1/2" customers pipe in this area.
13 | 74-20073-1 |  |  | 2 |  |  | Body of Pipe |  |  | Corrosion |  | 1974-09-04 | 1975-05-01 | Clamp |  | Steel/Wrought Iron |  | Oroville | Line Use "O" = Other; 30% Gas in water valve. Installed skinner repair calmp and 9 LB zinc Anode
13 | 74-20073-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-09-04 | 1975-05-01 | Clamp |  | Steel/Wrought Iron |  | Oroville | Installed 2" Skinner permanent repair clamp and 9lb Anode., Pit on top of Main
13 | 74-20020-1 |  |  | 0.75 |  |  | Other |  |  | Other |  | 1974-08-28 | 1974-08-29 | Other |  | Steel/Wrought Iron |  | Oroville | Line Use "O" = Other; Soap tested and found leak in Ser. cock and where it services on to riser. Shut off gas, tighten fittings and reassembled, called for light up
13 | 74-40027-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-06-21 | 1974-06-21 | Other | Temporary repairs by valving off damaged section @ 1558HR. 6/21/74; State Hwy 162 334' West of 14th str. Oroville, Butte County | Steel/Wrought Iron |  | Oroville | Valved off by T&R Dept.
13 | 74-40027-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-06-21 |  | Replace Pipe |  | Steel/Wrought Iron
13 | 73-00094-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1973-12-06 | 1973-12-14 | Other |  | Steel/Wrought Iron |  | Sutter Co. | Leak in P.G.& E. Reg. on Encinal Rd. Between Hwy 99 and williston Rd. Northside of Rd. Marked yellow "X". ; Still Leaking 1-7-74, In same union that was repaired.
13 | 73-00082-1 |  |  | 0.75 | Other |  | Other |  |  | Construction Defect |  | 1973-11-21 | 1974-06-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Line Use "O" = Other; Clear 7-10-74- Lowe.; Leak in PG&E box on road with no name off Kirk Rd. 57' of Kirk Rd. Marked Yellow "X"; Leak in Reg Box in Butte co. housing Kirk Rd. OFf east Gridley Rd.
13 | 73-20075-1 |  |  | 0.75 | Service |  | Bell Joint |  |  | Other |  | 1973-06-11 | 1973-08-27 | Other |  | Steel/Wrought Iron |  | Gridley | Repair reg and made up fittings
13 | 72-00079-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-06-23 | 1972-10-24 | Patch Weld - Weld |  | Steel/Wrought Iron |  | Live Oak | Changed to Grade 2 Leak; Leak on bottom. Installed welded patch 14" x 18"
13 | 72-00079-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-06-23 | 1972-10-24 | Patch Welded |  | Steel/Wrought Iron
13 | 71-40048-1 |  |  | 2 | Other |  | Fitting |  |  | Construction Defect |  | 1971-01-17 | 1971-01-19 | Other |  | Steel/Wrought Iron |  |  | Line Use "O" = Other; leak in Oroville Reg. Pit.
13 | 71-40028-1 |  |  | 0.75 | Service |  | Fitting |  |  | Corrosion |  | 1971-06-29 | 1971-06-29 | Other |  | Steel/Wrought Iron |  | Gridley | Repaired leaks in regulator pitt; Threads leaking on HP. Side of regulator, Replaced 3/4" nipple to complete repair
13 | 71-40007-1 |  |  | 8.5 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1971-01-14 | 1971-01-18 | Patch Welded |  | Steel/Wrought Iron |  |  | Roots have cut into wrapping and pipe is badly corroded
| 09-40002-1 | 128 |  | 0.75 | Transmission |  | Other |  | 3/4" Valve | Material Failure |  | 2009-03-19 | 2010-08-06 | Other | Abandon 3/4" valve | Steel/Wrought Iron |  | Willows | Installed 4" of 3/4" pipe- 2 3/4" Elbow; Welds Soap tested at 460 PSI ok.
| 08-16901-1 | 169 | 2.08 | 12.75 | Transmission |  | Body of Pipe |  |  |  |  | 2008-03-31 | 2008-04-01 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | Glenn | Installed Sleeve over punctured hole in pipe; Farmer was digging out bottom of ... a V-ditcher plow when he struck steel main causing the leak.
96 | 10-82013-1 | 303 | 30.88 | 0.75 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other | Valve stem leaking stem packing deteriorated | 2010-09-24 | 2011-02-04 | Replace Valve < 2 inch |  | Steel |  | Livermore | Replace 3/4" Valve; Shut off gauge line @ Mueller valve tee... Blow down 3/4 gauge line and replace 3/4" valve @V-6 (L303@M.P. 30.88)
96 | 10-82014-1 | 303 | 30.88 | 1 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other | Valve stem leaking stem packing deteriorated | 2010-09-24 | 2011-02-04 | Replace Valve < 2 inch | Replace 1" valve on B/D Stack | Steel |  | Livermore | Blow down header and replace 1" valve
98 | 10-30301-B | 303 | 7.8 | 0.75 | Transmission >= 20% SMYS |  | Line Valve |  |  | Equipment Malfunction |  | 2010-11-04 | 2010-11-24 | Deactivated Partial Service |  | Steel |  | Brentwood | Removed Chromatograph Probe and closed valve and installed plug
98 | 10-81261-B | 2408-01 | 0.01 | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Construction Defect |  | 2010-10-06 | 2010-10-28 | Tighten Cap/Bolt - Fitting |  | Steel |  | Livermore | Isabel Red. Station Yellow flag multiple leaks; Isabel station L131 MP 34
98 | 10-88883-A | 303 | 30.88 | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Material Failure |  | 2010-10-22 | 2010-11-27 | Tighten Cap/Bolt - Fitting |  | Steel |  | Livermore | At base of valve M.P. 30.88 in center and 18' from gate A/G on valve base; Foleys Ranch L-303 @M.P. 30.88
96 | 10-22201-1 | 222 | 0 | 3.5 | Transmission >= 20% SMYS |  | Other |  |  | Unknown |  | 2010-05-19 | 2010-05-25 | Other | ; | Other |  | Tracy
| 10-88903-1 | 316 | [9 empty] | 2010-10-21 | [5 empty] | Tracy | John Harris G&S 925-595-6440
| 10-88834-1 | 57B | [9 empty] | 2010-10-25 | [5 empty] | Tracy
| 10-30301-1 | 303 | 7.8 | 0.75 | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2010-11-04 | 2010-11-24 | Deactivated Entire Service | Remove chromatoagraphy probe close valve install plug |  |  | Brentwood
24 | 10-81041-1 | 5438/303 | 0.3 | [8 empty] | 2010-10-09 | [5 empty] | Livermore
24 | 10-88002-1 | 303 | 25.53 | [8 empty] | 2010-10-28 | [5 empty] | Livermore
| 09-31601-1 | 316A | 1.02 | 4 | Gathering |  | Tap Connection | Valves |  | Unknown |  | 2009-11-10 |  |  |  | Steel/Wrought Iron |  | Oakley (Jersey Island)
24 | 10-88002-1 | 303 | 25.53 | 0.5 | Transmission >= 20% SMYS |  | Other |  | Grease fitting | Other | Loose grease fitting cap | 2010-10-28 | 2011-03-04 | Tighten Cap/Bolt - Fitting |  | Steel |  | Livermore | Tighten cap; Tighen cap on grease button head fitting, Livermore Jct.
24 | 10-81041-1 | 5438/303 | 0.3 | [8 empty] | 2010-10-09 | [5 empty] | Livermore | Go Dave Kuryla Tracy;
| 10-11401-1 | [5 empty] | Unknown |  |  | Unknown |  | 2010-04-05 |  |  |  | Steel/Wrought Iron |  | Brentwood
| 10-82014-1 | 303 | [9 empty] | 2010-09-24 | [5 empty] | Livermore
Do not use other-Unless no other choice fits. If other is used- write in reason.; Do not use other choice; If Replaced Pipe, LANID
| 10-82013-1 | 303 | [9 empty] | 2010-09-24 | [5 empty] | Livermore
| 10-88893-1 | 304 | 7.2 | [8 empty] | 2010-10-20 | [5 empty] | Tracy | Attn Dave Kuryla 603Y673, Don Stocxfisch D35K From Stockton M & C. Pretty good. Leak at valve. Please send copy of A-form when completed
| 10-05701-1 |  |  |  | Transmission |  | Valves |  |  | Unknown |  | 2010-12-27 | [5 empty] | Brentwood | Waiting for return phone call from Wendy/Ray with leak number info
| 10-88001-1 | 3010/303 |  | 12 | Transmission |  | Regulator |  |  | Other | Internal | 2010-10-28 | 2010-10-28 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | Livermore
96 | 86-19501-1 | 195 | 4.73 | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1986-06-05 | 1986-06-17 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Line blown down 6-5-86 Repairs made 6-17-86
96 | 86-19502-1 | 195 | 5.47 | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1986-08-25 | 1986-09-04 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Line Blown down on 8/25/86 Repairs made 9-4-86
96 | 80-19505-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-11-19 |  | Clamp |  | Steel/Wrought Iron |  | Bradford Isl. | Gas bubbling in water over line when leak was repaired water raised over pipe. Found OK; See attached sketch
96 | 80-19604-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-11-19 |  | Clamp |  | Steel |  | Bradford Isl | Pipe clamp failed same leak remove; Gas bubbling in water over line when leak was repaired water raised over pipe found ok.
96 | 80-19503-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-04-18 |  | Clamp |  | Steel/Wrought Iron |  | Bradford Isl. | Gas bubbling in water over line. When repaired water level raised over line found leak.
96 | 80-19502-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-04-18 |  | Clamp |  | Steel/Wrought Iron |  | Bradford Isl. | Gas bubbling in water over line. When leak repaired waer raised over pipe, found leak
96 | 80-19501-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-01-15 |  | Clamp |  | Steel/Wrought Iron |  |  | Repaired on above date with temp. 4" repair clamp
96 | 79-19501-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1979-01-11 | 1979-01-16 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Bradford Isl. | From Valve B.C. #3 to leak 130' 7"
96 | 77-19501-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1977-01-29 | 1977-01-31 | Clamp |  | Steel/Wrought Iron |  | Bradford Isl.
96 | 75-19501-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1975-08-21 | 1975-09-30 | Patch Welded |  | Steel/Wrought Iron
96 | 72-19501-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1972-11-19 | 1972-11-20 | Patch Welded |  | Steel/Wrought Iron |  | Brandford Is | Heard leak blowing from road 3/16" hole 1/2" dia. Pit. on bottom of pipe. Blew gathering line down 11/19/72 & made repair 11/20/72 Patch at 1/2" x 4 1/2"
|  | 303 | 1.67 | 36 | [13 empty] | ANTIOCH | 18" cover over main 303; DuPont nitrogen & Oxygen are over 303 with a cover of 18". Main 303 with a cover at this crossing.
|  |  |  | 4 | [11 empty] | Steel |  | Bradford is. | 4" line has many don't within 6' long (dents range from 1/4" to 11/4" deep).
|  |  |  | 4 | [13 empty] | Bradford Isl. | 4" Collection line from JD#6 to K-7 compressor.
|  |  |  | 4 | [11 empty] | Steel |  | Bradford Isl. | 4" Collection line from JD#4 to K-7 compressor
|  |  |  | 4 | [11 empty] | Steel |  | Bradford Isl. | 4" Collection line from Bradford BC#2 well to K-7 compressor
|  | 114 |  | 22 | [11 empty] | Steel |  |  | Repair wrap
|  |  |  | 16 | [14 empty] | Main 114 was exposed for installation of 12" bypass main 400 to main 131 terminal Yard
96 | 72-11401-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-02-22 | 1972-03-06 | Weld Over Sleeve or Can |  | Steel |  | Tracy | Full Sleeve welded over leak; 1/16" hole in 1 1/10" pit Ht. 6 O'Clock 18" long full encirclement sleeve installed over leak.
96 | [18 empty] | GM-179627, 1124, 0316
96 | 72-11401-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-02-22 | 1972-03-06 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Tracy | Full Sleeve weld over leak; 1/16" hole in 1 1/10" pit at 6 O' Clock 18" long full encirclement sleeve installed over leak.
|  | 114 | 9.5 | 22 | [11 empty] | Steel |  | Oakley | Install 3" plastic drain;
|  | 114 | 10.4 | 22 | [11 empty] | Steel
|  | 114 | 12.5 | 22 | [11 empty] | Steel |  |  | Install test lead
|  | 114 | 12.5 | 22 | [11 empty] | Steel |  | Brentwood | Install drain P.PE & Box
|  | 114 | 12.53 | 22 | [11 empty] | Steel |  | Brentwood | Gen. Constr. Installing 3" Tap Valve; Install 3" Tap M.P. 12.53;
|  | 114 | 10.43 | 22 | [11 empty] | Steel |  | Antioch
|  | 114 | 10.65 | 22 | [11 empty] | Steel |  | Antioch | ;
|  | 114 | 10.57 | 22 | [11 empty] | Steel |  | Antioch
|  | 114 | 10.5 | 22 | [11 empty] | Steel |  | Antioch
|  |  |  | 22 | [11 empty] | Steel |  |  | Installed two 2" mueller taps 360' to first tap 488' to second tap from center of Oakley Rd.
|  | 114 |  | 22 | [11 empty] | Steel |  |  | Repair wrap
11 | 87-19500-1 | 195 |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1987-01-09 | 1987-01-13 | Weld Over Sleeve or Can |  | Steel |  | Branford Isl. | Line blown down 1-09-87 Reapirs made with full encirclement sleeve 1-13-87
|  |  |  | 6.625 | [11 empty] | Other Plastic |  | Brentwood
|  |  |  | 12.75 | [11 empty] | Other | GR-X-52, ERW | Brentwood | Wall thickness tested with ultrasonic thickness gage Paranatric's model 26 ny G.L.G's antioch
11 |  | 316 |  | 8.62 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1996-04-24 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Brentwood
11 |  | 316 |  | 8.62 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1996-04-24 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Brentwood | ;
|  | 303 | 32.5 | 36 | [8 empty] | 2000-12-28 | Weld Over Sleeve or Can |  |  |  |  | Welded sleeve PPC#10889030, 36485"I.D. 1/2WT., X-60, 60,000 SYMS (Back Beveled
98 | 11-50001-A |  |  |  | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-11 |  |  |  | Steel |  | Byron
98 | 11-50002-A |  |  |  | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-11 |  |  |  | Steel |  | Byron
98 | 11-50003-A |  |  |  | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-11 |  |  |  | Steel |  | Byron
98 | 11-50004-A |  |  |  | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-11 |  |  |  | Steel |  | Byron
98 | 11-50005-A |  |  |  | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-11 |  |  |  | Steel |  | Byron | ;
98 | 11-50006-A |  |  |  | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-11 |  |  |  | Steel |  | Byron
98 | 11-50007-A |  |  |  | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-11 |  |  |  | Steel |  | Byron
98 | 11-50008-A |  |  |  | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-11 |  |  |  | Steel |  | Byron
98 | 11-50009-A |  |  |  | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-11 |  |  |  | Steel |  | Byron
98 | 11-50010-A |  |  |  | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-11 |  |  |  | Steel |  | Byron
98 | 11-50011-A |  |  |  | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-11 |  |  |  | Steel |  | Byron
98 | 11-50012-A |  |  |  | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-11 |  |  |  | Steel |  | Byron
98 | 11-50013-A |  |  |  | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-11 |  |  |  | Steel |  | Byron
98 | 11-50001-A |  |  |  | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-11 |  |  |  | Steel |  | Byron
98 | 11-50002-A |  |  |  | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-11 |  |  |  | Steel |  | Byron
98 | 11-50003-A |  |  |  | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-11 |  |  |  | Steel |  | Byron
98 | 11-50004-A |  |  |  | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-11 |  |  |  | Steel |  | Byron
| 10-00201-1 |  |  |  | Transmission |  | Regulator |  |  | Unknown |  | 2010-04-01 |  |  |  | Other | Stainless | Santa Nella
98 | 11-A | 2 | 68.6 | 3 | Distribution Main > 60 PSIG |  | Line Valve |  |  | Material Failure |  | 2011-03-08 |  |  |  | Steel
| 11-A | 2 | 68.6 | 1 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-08 |  |  |  | Steel
| 11-A | 2 | 68.6 | 1 | Transmission >= 20% SMYS |  | Threads |  |  | Incorrect Operation |  | 2011-03-08 |  |  |  | Steel
| 11-00000-A | 2 | 68.6 | 2 | Distribution Main > 60 PSIG |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-08 |  |  |  | Steel
| #NAME? | 2 | 68.6 | 2 | Distribution Main > 60 PSIG |  | Fitting |  |  | Incorrect Operation |  | 2011-03-08 |  |  |  | Steel
| 11-A | 2 | 68.6 | 2 | Distribution Main > 60 PSIG |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-08 |  |  |  | Steel
98 | 11-50014-1 | 2 | 142.5 | 26 | Transmission >= 20% SMYS |  | Fitting |  |  | Material Failure |  | 2011-03-11 |  |  |  | Steel |  | Tracy
98 | 11-50015-1 | 2 | 142.5 | 26 | Transmission >= 20% SMYS |  | Line Valve |  |  | Unknown |  | 2011-03-11 |  |  |  | Steel |  | Tracy
98 | 11-50016-1 | 2 | 142.5 | 26 | Transmission >= 20% SMYS |  | Fitting |  |  | Equipment Malfunction |  | 2011-03-11 |  |  |  | Steel |  | Tracy
98 | 11-50017-1 |  | 2 | 142.5 | Transmission >= 20% SMYS |  | Unknown |  |  | Unknown |  | 2011-03-11 |  |  |  | Steel |  | Tracy
98 | 11-50018-1 | 2 | 142.5 | 26 | Transmission >= 20% SMYS |  | Line Valve |  |  | Unknown |  | 2011-03-11 |  |  |  | Steel |  | Tracy
98 | 11-50019-1 | 2 | 142.5 | 26 | Transmission >= 20% SMYS |  | Line Valve |  |  | Unknown |  | 2011-03-11 |  |  |  | Steel |  | Tracy
98 | 11-50020-1 | 2 | 142.5 | 26 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-03-11 |  |  |  | Steel |  | Tracy
98 | 11-50021-1 | 2 | 142.5 | 26 | Transmission >= 20% SMYS |  | Line Valve |  |  | Unknown |  | 2011-03-11 |  |  |  | Steel |  | Tracy
98 | 11-50023-1 | 2 | 142.5 | 26 | Transmission >= 20% SMYS |  | Line Valve |  |  | Unknown |  | 2011-03-11 |  |  |  | Steel |  | Tracy
| 08-00205-1 | [10 empty] | 2008-02-26 | [5 empty] | Tracy
| 08-00205-1 | 162 | [9 empty] | 2008-08-26 | 2009-03-02 | Other | Mooney spring case; ; |  |  | Tracy
| 08-00206-1 | [10 empty] | 2008-08-26 | [5 empty] | Tracy
| 08-00204-1 | [11 empty] | 2006-09-15 | Tighten Cap or Bolt |  |  |  | Tracy
| 08-00204-1 | [16 empty] | Tracy
| 08-00203-1 | [10 empty] | 2008-08-26 | [5 empty] | Tracy
| 08-00203-1 | [11 empty] | 2008-09-15 | Tighten Cap or Bolt |  |  |  | Tracy
| 08-00201-1 | [10 empty] | 2008-08-26 | 2008-09-15 | Tighten Cap or Bolt |  |  |  | Tracy
| 08-00201-1 | [10 empty] | 2008-08-26 | [5 empty] | Tracy
| 08-00202-1 | [10 empty] | 2008-08-26 | 2008-09-15 | Tighten Cap or Bolt |  |  |  | Tracy
| 08-00202-1 | [10 empty] | 2008-08-26 | [5 empty] | Tracy
| 08-10701-1 | 107 | 15.27 | 22 | Transmission |  | Other |  | Presser coupling | Material Failure |  | 2008-03-10 | [5 empty] | Livermore
| 08-13101-1 | 131 | 33.95 | 24 | Transmission |  | Fitting | Valves |  |  |  | 2008-06-12 | [5 empty] | Livermore | 06-12-08 Notified supervisors of leak at location in valve yard. Grade 3 at this time. To set up for recheck. DJMR/DFRI
| 08-13102-1 | 131 | 26.63 | 24 | Transmission |  | Valves |  |  | External Corrosion |  | 2008-11-05 |  |  |  | Steel/Wrought Iron |  | Livermore
| 09-00202-1 | [10 empty] | 2009-03-09 | [5 empty] | Tracy
| 09-00201-1 | [10 empty] | 2009-03-09 | [5 empty] | Tracy
| 09-00203-1 | [10 empty] | 2009-03-09 | [5 empty] | Tracy
| 09-00204-1 | [10 empty] | 2009-04-06
| 09-13101-1 | 131 | [9 empty] | 2009-01-27 | 2009-02-19 |  |  |  |  | OAKLEY
| 09-13101-1 | [10 empty] | 2009-01-27 | [5 empty] | OAKLEY
| 10-11403-1 | 114 | 27.76 | [8 empty] | 2010-09-29
| 08-00203-1 | [10 empty] | 2008-08-26 | 2008-09-15 | Tighten Cap or Bolt |  |  |  | Tracy
| 08-00203-1 | [10 empty] | 2008-08-26 | [5 empty] | Tracy
| 08-00204-1 | [11 empty] | 2008-09-15 | Tighten Cap or Bolt |  |  |  | Tracy
| 08-00204-1 | [16 empty] | Tracy
| 08-00204-1 | [10 empty] | 2008-08-26 | [5 empty] | Tracy
| 10-30004-1 | 300B | 457.28 |  |  |  | Regulator |  |  |  |  | 2010-09-19 | [5 empty] | Hollister
|  | 2 | [9 empty] | 2010-10-12 | [5 empty] | Santa Nelle
|  | 114 | 14.69 | [15 empty] | 10-8-10 Kirk Buster A105, 1015 10-8\442-1 320 Fairview Ave. Brentwood. M.P. 14.69, 41% Gas in median in front of address map3005 B12 Line 114 HCA-Yes Grade 2
| 10-81443-1 | 2 | 88.4 | [8 empty] | 2010-10-11 | [5 empty] | Santa Nella
| 09-31601-1 | 316A | 1.02 | 4 | Gathering |  | Tap Connection | Valves |  | Unknown |  | 2009-11-10 |  |  |  | Steel/Wrought Iron |  | OAKLEY
| 08-00203-1 | [10 empty] | 2008-08-26 | [5 empty] | Tracy
|  | 304 | 9.97 | 12.75 | [8 empty] | 2010-01-08 | Grinding - Other |  | Steel/Wrought Iron
| 08-00203-1 | 2 |  | 6 | Transmission |  | Fitting |  |  | Other | Loose Fitting | 2008-08-26 | 2008-09-15 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Tracy
| 10-81081-1 | STANPAC2 | [15 empty] | Modesto
| 10-31601-1 | 316-20 | 0.77 |  | Transmission |  | Fitting |  |  | Other | Loose Plug | 2010-05-03 | 2010-05-24 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Brentwood
| 10-81221-1 | 401 | 34.45 | 0.75 | Transmission |  | Valves |  |  |  |  | 2010-10-06 | 2010-10-20 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | Westley
| 06-30401-1 | 304 | 3.11 | 12 | Gathering |  | Valves |  |  |  |  | 2006-04-06 | 2008-12-09 | Other | Replace grease stem |  |  | Tracy
| 10-11402-1 | 114 | 26.25 | 22 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2010-05-25 | 2010-07-01 | Replace TP Main |  | Steel/Wrought Iron |  | Livermore | Replace 4' 4" TP Mail
96 | 08-13101-1 | 131 | 33.95 | 1 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2008-06-12 | 2010-10-28 | Tighten Cap/Bolt - Fitting |  | Steel |  | Livermore | Mueller valve tee for gauge tap cap leaking
| 10-31801-1 | 316-20 | 0.77 | 16 | Transmission |  | Other |  |  | Other |  | 2010-05-03 |  |  |  | Other |  | Brentwood
| 10-31601-1 | 316-20 | 0.77 | [8 empty] | 05/03/0200 | [5 empty] | Brentwood
| 10-82013-1 | 303 | 30.88 | [8 empty] | 2010-10-24 | [5 empty] | Livermore
| 10-82014-1 | 303 | 30.88 | [8 empty] | 2010-10-24 | [5 empty] | Livermore
| 10-82012-1 | 303 | 30.88 | [8 empty] | 2010-10-24 | [5 empty] | Livermore
| 10-82013-1 | 303 | 30.88 | [8 empty] | 2010-10-24 | [5 empty] | Livermore
| 10-82014-1 | 303 | 30.88 | [8 empty] | 2010-10-24 | [5 empty] | Livermore
| 10-81261-1 | 2408-01 | 0.01 | 0.75 | Transmission |  | Fitting |  |  | Construction Defect |  | 2010-10-06 | 2010-10-28 | Tighten Cap or Bolt |  |  |  | Livermore
| 10-88883-1 | 303 | 30.88 | 0.75 | Transmission |  | Fitting |  |  | Material Failure |  | 2010-10-22 | 2010-11-27 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Livermore
| 10-81443-1 | 2 | 88.4 | 0.75 | Transmission |  | Valves |  |  | Material Failure |  | 2010-10-11 | 2010-10-18 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | Santa Nella
| 10-81443-1 | 2 | 88.4 | 0.75 | Transmission |  | Valves |  |  | Material Failure |  | 2010-10-11 | 2010-10-18 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | Santa Nella
98 | 10-88903-1 | 316A | 2.3 | 0.5 | Gathering |  | Fitting |  |  | Compression Coupling |  | 2010-10-21 | 2011-01-26 | Tighten Cap/Bolt - Fitting |  | Other |  | Tracy
| 10-81081-1 | STANPAC2 |  |  | Transmission |  | Fitting |  |  | Other | Loose | 2010-10-02 | 2010-10-07 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Modesto | Loose cap on grease filling on Valve 111.90; Tightened loose cap on grease fitting
| 09-00201-1 | [10 empty] | 2009-03-09 | 2009-07-03 | Other | Gas supply regulator gasket and tubing fitting |  |  | Tracy | Repaired 7/3/09; 11/19/08-Other tighten stem packing
| 08-10701-1 | 107 | 15.27 | 22 | Transmission |  | Other |  |  | Material Failure |  | 2008-03-10 | 2009-11-07 | Replace TP Main |  | Steel/Wrought Iron |  | Livermore | Removed MLV bridle in pit w. dresser cou
| 08-00203-1 | [10 empty] | 2008-08-26 | 2008-09-15 | Tighten Cap or Bolt |  |  |  | Tracy
| 09-05703-1 | 57B | 16.57 | 0.75 |  |  | Fitting |  |  |  |  | 2009-04-20 | [5 empty] | BRENTWOOD
| 09-00201-1 | [10 empty] | 2009-03-09 | [5 empty] | TRACY
| 08-10701-1 | 107 | 15.27 | 22 | Transmission |  | Other |  | Leaking dresser coupling | Material Failure |  | 2008-03-10 | 2008-11-07 | Replace TP Main |  | Steel/Wrought Iron |  | Livermore | Remove MLV Bridle in pit w/ dresser couplings
| 08-00205-1 | 2 |  | 6 | Transmission |  | Unknown |  |  | Unknown |  | 2008-08-26 | 2009-03-02 | Tighten Cap or Bolt |  | Other |  | Thornton
| 09-00202-1 | 2 |  | 0.75 | Transmission |  | Fitting |  |  | Other | Loose fitting | 2009-03-09 | 2009-04-20 | Tighten Cap or Bolt | SOAP AND/OR TAPE | Steel/Wrought Iron |  | Tracy
| 08-13102-1 | 131 | 26.98 | 24 | Transmission |  | Valves |  |  | External Corrosion |  | 2008-11-05 | 2008-11-08 | Other | Installed new plug | Steel/Wrought Iron |  | Livermore
| 08-00206-1 | 2 | [9 empty] | 2008-08-26 | 2008-11-19 | Other | Tighten stem packing |  |  | Tracy
| 08-00204-1 |  | 2 | 6 | Transmission |  | Fitting |  |  | Other | Loose fitting | 2008-08-26 | 2008-09-15 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Tracy
| 09-00204-1 | [10 empty] | 2009-04-06 | 2009-07-03 | Other | Stem packing |  |  |  | Repaired 7/3/09; Valve is leaking around stem packing tightened packing and greased valve stopped leak
| 08-10701-1 | 107 | 15.27 | 22 | Transmission |  | Other |  | Presser coupling | Material Failure |  | 2008-03-10 | [5 empty] | Livermore | L-107 M.P. 15.27 Arroyo Rd. Livermore
| 09-00203-1 | [10 empty] | 2009-03-09 | 2009-07-03 | Other | SENOR ORIFICE METER GREASE FITTING AND ORIFICE PLATE GASKET |  |  | Tracy | Repaired 7/3/09; Senior orifice meter grease fitting and orifice plate gasket
| 10-22201-1 | 222 | 0 | 3.5 | Transmission |  | Other |  |  | Unknown |  | 2010-05-19 |  |  |  | Other |  | Tracy
98 | 09-05704-3 | 57A | 16.64 | 16 | Transmission >= 20% SMYS |  | Unknown |  |  | Material Failure |  | 2009-04-20 | 2010-12-23 | Mechanical Repair Fitting - Fitting |  | Cast Iron |  | Brentwood | Brentwood terminal Meter Tube 11; Replaced upper housing of meter tube
| 09-05704-1 | [5 empty] | Unknown | Other | Loose SR fitting |  |  | 2009-04-20 | [5 empty] | Brentwood
| 10-22201-1 | 222 | 0 | [8 empty] | 2010-05-19 | 2010-05-25 | Other | Grease fitting leaking Greased fitting stopped leak | Steel/Wrought Iron |  | Tracy
98 | 10-88903-1 | 316A | 2.3 |  | Gathering |  | Fitting |  |  |  |  | 2010-10-21 | 2011-01-26 | Tighten Cap/Bolt - Fitting |  | Steel |  | Tracy | Tightened fittings 1/2" & 3/4"
| 09-05702-1 | [5 empty] | Unknown |  |  | Other | Leaky fitting | 2009-04-20 | 2009-07-08 | Tighten Cap or Bolt |  |  |  | Brentwood | Repaired 7/9/09; disassembled power gas pipe fittings and cleaned threads and reassembled with teflon tape and pipe dope
98 | 10-30301-1 | 303 | 7.8 | 0.75 | Transmission >= 20% SMYS |  | Line Valve |  |  | Equipment Malfunction |  | 2010-11-04 | 2010-11-24 | Deactivated Partial Service |  | Steel |  | Brentwood | Removed Chromatograph probe closed vlv.ins.
98 | 09-05704-1 | 57A | 16.64 | 16 | Transmission |  | Unknown |  |  | Material Failure |  | 2009-04-20 | 2010-12-03 | Mechanical Repair Fitting - Fitting |  | Cast Iron |  | Brentwood; | Replaced upper housing of meter tube
98 | 10-88883-1 | 303 | 30.88 | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Material Failure |  | 2010-10-22 | 2010-11-27 | Tighten Cap/Bolt - Fitting |  | Steel |  | Livermore | None
96 | 10-11402-1 | 114 |  | 22 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | External Corrosion |  | 2010-05-25 | 2010-07-01 | Replace TP Main |  |  |  | Livermore | replaced 11' of 4" TP main
96 | 10-31601-1 | 316-20 | 0.77 | 16 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-05-03 | 2010-05-24 | Tighten Cap/Bolt - Fitting |  | Other |  | Brentwood | Tighten pipe plug
| 06-30401-1 | 304 | 3.11 | 12 | Gathering |  | Valves |  |  | Other |  | 2006-04-06 | 2008-12-09 | Other |  | Other |  | Tracy
|  | 114 | 30.73 | 36 | [11 empty] | Steel |  | Tracy | Excavated line to eliminate metallic contact between pipe and casing W.O. 4403G
96 | 82-10703-1 | 107 | 16.7 | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1982-11-16 | 1982-11-23 | Replace Pipe and/or Service |  | Steel |  | Livermore | Leak repaired by Replacing pipe on w.o.45521; Line 107 M.P. 16.70, Gas blowing in creek pond and surrounding
96 | 85-10702-1 | 107 | 4.9 | 3.5 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-06-05 | 1985-06-19 | Other |  | Steel/Wrought Iron |  |  | Removed drip on w.o. 40043A 6-14-85; Line 107 M.P. 04.90
|  | 107 | 5.3 | 22 | [11 empty] | Steel |  |  | Remove 3" drip w.o.40043A
|  | 107 | 6.6 | 22 | [11 empty] | Steel |  |  | Remove 3" Drip w.o. 40043A
LB |  | SP-2 | 53.76 | 26 | Transmission |  | Other |  |  |  |  | 1981-01-27 |  | Weld Over Sleeve or Can |  | Steel |  | Los Banos | Excavated, sandblasted & double wrapped 115 ft. Light pitting located 3:00 to 9:00 position thru out exposed pipe. Installed test lead and line marker @FS 2838+89. P/S. S40.w.o. 3688;
|  | SP-2 | 59.39 | 26 |  |  |  |  | SP-2 | [6 empty] | Steel |  |  | Installed sleeve GS&S A-60 over 0.110 Depth gouge FS 3135+80 Repaired wrap and lowered '26" main FS
|  | SP-2 | 72.72 | 26 | [11 empty] | Steel |  | Los Banos | Lowered 650' SP-2 main to a min. 30" depth. Found minor dents FS 384+18 @ 12:00 position. Spot wrapped all disturbance of rust coating caused by excavation
|  | SP-2 | 72.72 | 26 | [11 empty] | Steel |  | Los Banos | Lowered 650' SP-2 main to a min. 30" depth. Found minor dents FS 384+18 @ 12:00 position. Spot wrapped all disturbance of rust coating caused by excavation
|  |  | 128.3 | 26 | [11 empty] | Steel |  | Los Banos | Repaired 0.05 depth gouge damage. Double wrapped with polykin & installed 60# zink Anode. Backfilled all portions of dump within right of way P/S.520
|  | SP-2 | 98.26 | 26 | [11 empty] | Steel |  | Los Banos | Sp-2 exposed adjacent to ripper damage on 18" Chevron main with in right-of-way, for inspection of possible damage and removal of oil containated soil by property owner. Their was no damage to SP-2
|  | SP 2 | 51.33 | 26 | [11 empty] | Steel |  | Los Banos | Inspected FS. 2711+25 to FS. 2711+50 doublewrapped, sand blasted, and isntalled 60# zink Anode. Indecations of active corrosion. P/S 280mv.
|  | SP2 | 41.06 | 22 | [11 empty] | Steel |  | Los Banos | Sand blasted, double wrap and 60# zinc anode installed P/S .270 Corrosion active
|  | SP2 | 40.47 | 22 | [11 empty] | Steel |  | Los Banos | SandBlasted, double wrap and 60# zinc anode installed P/S .490
|  | SP2 | 40.47 | 22 | [11 empty] | Steel |  | Los Banos | Sand blasted, double wrap and 60# zinc anode installed P/S .210 Corrosion Active
|  | SP2 | 87.4 | 26 | [11 empty] | Steel |  |  | Installation of 10" transite water main crossing Sp-2, 60' from center line of Hwy 33 12" clearance below SP2
|  | SP2 | 87.4 | 26 | [11 empty] | Steel |  |  | Installation of 10" transite water main crossing SP2, 60' from center line of hwy 207
|  | SP2 | 87.4 | 26 | [11 empty] | Steel |  |  | Installation of 10" transite water main crossing SP2, 60' from center line of hwy 207 -12" clearance below SP2
|  | SP2 | 124.21 | 26 | [11 empty] | Steel |  |  | Sand blasted, wrapped and 60# zink anode installed. P/S .410 limited access due to almond trees. WO/SP 3531
|  | SP2 | 124.21 | 26 | [11 empty] | Steel |  |  | Sand blasted, wrapped & 60# zink anode installed. P/S .400 limited access due to almond trees. WO/SP 3531
|  | SP2 | 127.4 | 26 | [11 empty] | Steel |  |  | Pipe was not inspected due to condition of wrap. Repaired wrap where hoe bucket caused damage WO/SP3531 P/S .400
|  | SP2 | 123.77 | 26 | [11 empty] | Steel |  |  | Pipe sand blasted, wrapped and 60# zink anode installed P/S .410 WO/SP 3531 corrosion active
|  | SP2 | 121.31 | 26 | [11 empty] | Steel |  |  | Limited access due to almond trees pipe sand blasted, wrapped and 60# zink anode installed P/S/ .500 WO/SP3531
|  | SP2 | 42.23 | 22 | [11 empty] | Steel |  |  | Pipe sand blasted, wrapped and 60# zink anode installed P/S .250 WO/Sp 3531
|  | SP2 | 107.49 | 26 | [11 empty] | Steel |  |  | Lowered 350' SP#2 M.P. 107.49 SP 3525-1000-1502 Installed 11 Zinc annodes spaced 25' on bare pipe. SP 3525-2000-1124
|  | SP2 | 119.22 | 26 | [11 empty] | Steel |  |  | WO/SP 3531 Pipe sand blasted, inspected, polyken... wrap applied and 60#zink anode installed. P/S .250 all pitting located @ 5:00 to 7:00 position
|  | SP2 | 107.49 | 26 | [11 empty] | Steel |  |  | Lowered 350' SP#2 M.P. 107.49 SP 3525-1000-1502 Installed 11 zinc annodes spaced 25' on bare pipe SP3525-2000-1124
|  | SP2 | 120.9 | 26 | [11 empty] | Steel |  | Westley
|  | SP2 | 12.4 | 26 | [11 empty] | Steel |  | Westley | In almond orchard exposed to install sprinkler system
|  | 316 | 5.2 | 12 | [11 empty] | Steel |  | Antioch | Pot hole check depth
|  | 316 | 1.4 | 10.75 | [11 empty] | Steel
|  | 316 |  | 6 | [11 empty] | Steel |  |  | Line was exposed to abandon section of line going to Murphy #1 on Gm 4360483
|  | 316 |  | 6 | [11 empty] | Steel |  | Brentwood | 28" Storm drain crossing 6" PG&E pipe line
|  | 316 |  | 6 | [11 empty] | Steel |  | Brentwood | 8" Sewer Line crossing 6" PGE line
|  | 316 |  | 6.625 | [11 empty] | Steel |  |  | Murphy's #1 gas well
|  | 316 |  | 6.625 | [11 empty] | Steel |  |  | Enos nunn gas well #1
|  | 316 |  | 6.625 | [11 empty] | Steel |  |  | Gas well 10-3
|  | 316 |  | 6.625 | [11 empty] | Steel |  |  | Gas well 10-1
|  | 316 |  | 12.75 | [11 empty] | Steel |  |  | Gas well 8-3
|  | 316 |  | 4.5 | [11 empty] | Steel |  |  | Gas Well 1-3
|  | 316 |  | 12 | [11 empty] | Steel |  | Brentwood | Reference drawing 427931 sheet 1 of 2. 1/8 mile from Brentwood dehi...
|  | 316 |  | 6.25 | [11 empty] | Steel |  |  | 6" line is 4' downstream of 4"
|  | 316 |  | 6.25 | [11 empty] | Steel |  |  | 06.00 Line is 4' downstream of 4"
|  | 316 |  | 6.25 | [11 empty] | Steel |  |  | 6" line is 4' downstream of 4"
|  | 316 |  | 6.25 | [11 empty] | Steel |  |  | 6" line is 4' downstream of 4"
|  | 316 | 2 | 10 | [11 empty] | Steel |  |  | 14" steel sewer line crossed over main 316 M.P. 02.00
|  | 316 |  | 4 | [11 empty] | Steel |  |  | 10ft north of Nunn #2 meter fence
|  | 114 |  | 24 | [14 empty] | Dupont nitrogen and oxygen line are under main 114 with 13" of cover. Main 114 is cased at this crossing
|  | 316 | 3.75 | 12 | [11 empty] | Steel |  | Oakley | Several small gouges from .020" to .040" in depth in conjunction with a longitudinal scratch approx. 2' long starting on ..
|  | 316 | 4.95 | 12 | [11 empty] | Steel |  |  | Main 316 M.P. 04.95. 790ft west of valve 4.80 21" vitrified clay sewer line perpendicular to main 316
|  | 316 | 3.6 | 4 | [11 empty] | Steel
|  | 316 | [13 empty] | Steel |  |  | Baldwin Const. Installing 2-4" PVC pipe incased in concrete and is installed 15" over main 316
|  | 316 |  | 12 | [11 empty] | Steel |  |  | Dupont oxygen-Nitrogen are under Main 316 with 13" of cover. Main 316 is cased at this crossing
|  | 316 |  | 4 | [11 empty] | Steel |  |  | GM189919;
|  | 316 | 2.5 | 8 | [11 empty] | Steel |  |  | 14" Steel sewer line crossed over main 316 M.P. 2.5;
|  | 316 | 2.92 | 4 | [11 empty] | Steel |  |  | 14" Steel sewer line crossed under line 316
|  | 316 | 2.8 | 6 | [11 empty] | Steel |  |  | 14" Steel Sewer line crossed over main 316
|  | 316 |  | 4 | [11 empty] | Steel |  |  | See attached sketch; 316 collection nunnally line on Laurel Rd. No M.P.
|  | 316 |  | 4 | [11 empty] | Steel |  |  | 316 Collection, nunnally line on Laurel Rd. No M.P.; See attached sketch
|  | 316 |  | 4 | [11 empty] | Steel |  | Oakley | DDS Const. Installing A 10" force feed sewer line across line 316 north edge sypress rd. Approx 300' S. of V-19. Contractor did not contact when he started const.
|  |  |  | 8 | [11 empty] | Steel |  | Bradford Isl. | Valve 124 removed 4" wall thickness .148 4" G.R. B. SMLS 04.50" o.d.
96 | 75-19501-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1975-08-21 | 1975-09-30 | Patch Welded |  | Steel
|  | 195 |  | 08.00, 04.00, & 03.00 | [11 empty] | Steel |  |  | Drawing attached 4" all thickness .148 3" thickness .188
|  |  |  | 8 | [11 empty] | Steel |  | Bradford Isl. | Drawing attached 4" GR. B. SMLS 04.50od.
|  | 195 |  | 8 | [11 empty] | Steel |  |  | Drawing attached 4" GR. B. 04.50 O.D.
|  | 195 |  | 8 | [11 empty] | Steel |  | Bradford Isl. | Approx. 5 feet of fill to be added over exisiting ground level
96 | 80-19501-1 | 195 |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-01-15 |  | Clamp |  | Steel |  | Bradford Isl.
|  | 195 |  | 4 | [11 empty] | Steel |  | Bradford Isl. | Line 195
96 | 72-19501-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1972-11-19 | 1972-11-20 | Patch Welded |  | Steel |  | Bradford Isl. | Heard leak blowing from roard 3/16" hole 1/2" Dia. Pit. on bottom of pipe. Blew gathering line down 11/19/2 and made repair 11/20/72. Patch 4 1/2" x 4 1/2"
|  | 195 |  | 4.5 | [11 empty] | Steel |  | Bradford Isl. | Line 195 Tie-in Loc #4 bradford Island; 4" pipe at this location needs to be replaced
|  | 195 |  | 4 | [11 empty] | Steel |  | Bradford Isl. | 4" Collection line from Bradford BC#2 well to K-7 Compressor
|  | 195 |  | 4 | [13 empty] | Bradford Isl. | 4" Collection line form JD#6 to K-7 Compressor
96 | 79-00195-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1979-01-11 | 1979-01-16 | Weld Over Sleeve or Can |  | Steel |  | Bradford Isl. | From valve B.C. #3 to leak 103' 7"
|  | 195 |  | 4.5 | [11 empty] | Steel |  | Bradford Isl. | Line 195 Tie-in Loc#1
|  | 195 |  | 4.5 | [11 empty] | Steel |  | Bradford Isl. | 4" pipe at this location needs to be replaced
|  | 195 |  | 4.5 | [11 empty] | Steel |  | Bradford Isl. | Line 195 Tie-in Loc#3; 4'' pipe at this location needs to be replaced
|  | 303 |  | 36 | [11 empty] | Steel |  |  | DuPont Nitrogen and Oxygen are over 303 with a cover of 18". Main 303 is cased at this crossing
|  | 303 | 1.38 | 36 | [11 empty] | Steel |  | Antioch
|  | 303 |  | 36 | [11 empty] | Steel |  | W/O 41552-1124-5-303 Install test leads Line 303
|  | 303 | 1.59 | 36 | [11 empty] | Steel |  | Antioch
|  | 303 | 1.53 | 36 | [11 empty] | Steel |  | Antioch
|  | 303 | 1.45 | 36 | [11 empty] | Steel |  | Antioch
|  | 131 | 13.33 | 24 | [11 empty] | Steel |  |  | Install 6" Tap (Shell Oil)
Tracy;
|  | 114 | 15.98 | [12 empty] | Steel/Wrought Iron |  | Brentwood | Line114, M.P. 15.98 1/2 mile north of concord ave.
|  | 114 | 13.5 | [12 empty] | Steel/Wrought Iron |  | Brentwood | Line 114 M.P. 13.50 Fairview Ave 1162 South of Apricot way
|  | 114 | 10.64 | [12 empty] | Steel/Wrought Iron |  | Oakley | Line 114, M.P. 1064 50' North of Laurel Rd. West of Neroly
|  | 114 | 10.64 | [12 empty] | Steel/Wrought Iron |  | Oakley | Line 114 M.P. 10.64 250' North of Laurel Rd. West of Neroly
|  | 114 | 10.64 | [12 empty] | Steel/Wrought Iron |  | Oakley | Line 114 M. P. 10.64 395' North of Laurel Rd. West of Neroly
|  | 114 | 9.03 | [12 empty] | Steel/Wrought Iron |  | Antioch | Line 114 M.P. 9.03 + 600' East Bridgehearded Rd.
|  | 114 | 9.03 | [12 empty] | Steel/Wrought Iron |  | Antioch | Line 114, M.P. 9.03+ 600' east of Bridgehearded Rd.
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | Antioch gas Terminal Area 12, Oakley; Contra Costa County.; 16" blowdown stack just outside fence at Antioch terminal.
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 16" above ground station piping 2'-4" above V-125; Antioch gas terminal area 2C oakley contra costa county
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 16" Station piping between L191 and V206; Antioch gas terminal area 2C Oakley; contra costa coutny
|  |  |  | 3.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 3" Steel pipe that is tied to 4" blowdown line; 1'-5' west of 4" pipe; Antioch gas terminal area 2D Oakley; contra costa county
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 16" station piping 6'6" N/o V-89 fitting; Antioch gas terminial Area2D; Oakley; Contra costa county
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 16" station piping 1'-4" e/o V-80 Area 12 Antioch, gas terminal 2D Oakley contra costa county
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 16" station piping on M7 run between V-47 and 174; Antioch gas Terminal Oakley' Contra Costa County
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 16" station pipting on M7 run between V-57 & V-174; Antioch Gas Terminal oakley; Contra Costa County
|  |  |  | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 12" Station piping between M15 & V-56; Antioch Gas Terminal oakley; contra costa county
|  |  |  | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 20" station piping between M-7 and Valve 158; Antioch Gas Terminal Oakley; Contra Costa County
|  |  |  | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 20" station piping between M-7 and valve 158; Antioch Gas Terminal Oakley; Contra Costa County
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 12" station piping between V-57 and V-175; Antioch Gas Terminal Oakley; Contra Costa County
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 16" station piping = 84' 0" west of Valve 1 and east of V-14; Antioch Gas Terminal Oakley; Contra Costa County
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 16" Station Piping 131'0" west of Valve 1 and east of V-14; Antioch Gas Terminal Oakley; Contra Costa County
|  |  |  | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 12" station piping installed cap 13'-4" west of V-2; Antioch Gas Terminal Oakley; Contra Costa County
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 16" station piping between V-86 and V-167; Antioch Gas Terminal Oakley; Contra Costa County
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 16" station piping between master meter and V-85
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 16" station piping between V-85; 3' 1" V-86; Antioch Gas Terminal Oakley; Contra Costa County
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 16" Station piping between V-85 and V-86, 5'1" n/o V-86; Antioch Gas Terminal Oakley; Contra Costa County
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 16" station piping beteen V-60; Antioch Gas Terminal Oakley; Contra Costa County
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 16" station piping between M25 and V85; Antioch Gas Terminal Oakley; Contra Costa County
|  |  |  | 16 | [11 empty] | Steel/Wrought Iron |  | Oakley | 16" station piping between V-45 and V-173
|  |  |  | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 12" station piping between V175 amd 156; Antioch Gas Terminal Oakley; Contra Costa County
|  |  |  | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 12" station piping between v175 and v-155; Antioch Gas Terminal Oakley; Contra Costa County
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | 16.00 Station piping between V-45 and V156; Antioch Gas Terminal Oakley; Contra Costa County
|  |  |  | 6.62 | Gathering | [10 empty] | Steel/Wrought Iron |  | Jersey Island | 6316 13' N/o valve 1 west of Jersey Isl. Station; Jersey Island Contra Costa County, 20' West of Jersey Island Rd. and around 1/2 north Jersey Island bridge
|  | 131 |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | Byron | L 131 35North of Valve 18.78; Marsh creek rd. and Camino Diablo Blvd. 2' west of Byron; Contra Costa County
|  | 114 |  | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  | Byron | Line 114 45' north of valve, 18.62; Marsh Creek Rd. and Camino Diablo Blvd. +/- 2 west of Byron; Contra Costa County
|  | 304 | 6.59 | 12.75 | [14 empty] | Specific order #7043593
|  |  |  | 16 | [10 empty] | ; ; ; | Steel |  |  | 2340' South est of V-4.59 Vernalis mix station;
|  | 131 |  | 3.5 | [6 empty] | ; ; |  |  |  |  | Steel |  | Brentwood | 311 tap at line 131 T-14.14 +- 3/4 mile west of meados way line with San Jose Ave it extended
|  | 303 | 2.71 | 36 | Transmission | [6 empty] | 2000-06-06 |  |  |  | Steel/Wrought Iron |  | Antioch | Line 303 @ M.P. 02.71
|  | 303 | 2.76 | 36 | Transmission | [6 empty] | 2000-06-06 |  |  |  | Steel/Wrought Iron |  | Antioch | Line 303 @ M.P. 2.76; Antioch: Contra Costa County. ;
|  | 316 |  | 8.625 | [11 empty] | Other | GR X-46 | Oakley
|  | 316 |  | 6.625 | [11 empty] | Other | GR X-42 | Oakley
|  | 316 |  | 6.625 | [11 empty] | Other | GR X-42 | Oakley
|  |  |  | 12.75 | [11 empty] | Other | APISL G.X-5L
|  |  |  | 12.75 | [11 empty] | Other | APISL G.X-5L
|  | 401 | 330 | 36 | Transmission | [7 empty] | 1996-09-28 | Welded Sleeve/Can - Weld |  |  |  |  | Replaced 14' of 36" pipe
96 | 10-82012-1 | 303 | 30.88 | 0.75 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other | Valve stem leaking stem packing deteriorated | 2010-09-24 | 2011-02-04 | Replace Valve < 2 inch |  | Steel |  | Livermore | Pinned off meuller tee and replaced valves; Shut off gauge lines @ mueller valve tee blow-down 3/4 line and replace 3/4 vavles u/s and d/s of MLV 30.88;
98 | 10-88834-1 | 057B | 5.81 | [8 empty] | 2010-10-25 | [5 empty] | Tracy
24 | 10-81041-1 | 5438/303 | 0.3 | [8 empty] | 2010-10-09 | [5 empty] | Livermore
98 | 10-88868-1 | DREG7864 | 0 | [8 empty] | 2010-10-22 | [5 empty] | Livermore | Sent to Jim Rechtin this seems to be his
98 | 10-88884-1 | 303 | [9 empty] | 2010-10-24 | [5 empty] | Livermore
98 | 10-88893-1 | 304 | 7.2 | [8 empty] | 2010-10-20 | [5 empty] | Tracy
96 | 10-88893-1 | 304 | 7.2 | [8 empty] | 2010-10-20 | [5 empty] | Tracy
96 | 10-88904-1 | 316N | 37 | [8 empty] | 2010-10-21 | [5 empty] | Brentwood
96 | 09-31601-1 | 316A | 1.02 |  | Transmission >= 20% SMYS |  |  |  |  | Unknown |  | 2009-11-10 | [5 empty] | Oakley
| 09-40103-1 | 401 | 197.8 |  | Transmission |  | VALVES |  |  |  | VALVE STEM | 2009-06-02 |  |  |  | Steel/Wrought Iron |  | Maxwell
| 09-40103-1 | [10 empty] | 2005-06-24 | [5 empty] | Maxwell
| 05-40103-1 | 401 | 197.8 | [8 empty] | 2005-06-24 | 2006-05-05 |  |  |  |  | Maxwell | Leak is undetectable at this time. Valve was installed & seal greased.
| 09-40108-1 | [10 empty] | 2005-06-24 | [5 empty] | Maxwell
| 00-40001-1 | 400 | 197.83 | 36 |  |  | MECHANICAL JOINT |  |  |  | GASKET | 2000-05-01 | [5 empty] | Maxwell | W.R. #164429 in system for repair.
| 00-40001-1 | 400 | 197.83 | 36 | Transmission |  | PHYSICAL/MECHANICAL JOINT | Valves | VALVES | UNKNOWN |  | 2004-06-04 | [6 empty] | Leak seem to be show more sign wr#139046
| 00-40001-1 | 400 | 197.83 | 36 | Transmission |  | PHYSICAL/MECHANICAL JOINT | Valves |  | UNKNOWN |  | 2004-06-04 | [5 empty] | Maxwell | Test unit Heath Detecto Pak III model - DPIII S/N 10173
| 04-40002-1 | 400 | 197.8 | 36 | [7 empty] | 2004-06-04 | 2006-05-05 |  |  |  |  | Delevan | Tightened seals & Leak is gone
| 01-40002-1 | 400 | 197.83 | 36 | Transmission |  | PHYSICAL/MECHANICAL JOINT | Valves |  |  |  | 2001-06-07 | [5 empty] | Delevan
| 01-40002-1 | 400 | 197.83 | 36 | Transmission |  | VALVES | Unknown |  |  |  | 2001-06-07 |  |  |  | Steel/Wrought Iron |  | Delevan
| 01-40003-1 | 400 | 197.83 | 2 | Transmission |  | PHYSICAL/MECHANICAL JOINT | Valves |  |  |  | 2001-06-07
| 01-40003-1 | 400 | 197.8 | 36 | Transmission |  | VALVES | Unknown |  |  |  | 2001-06-07 |  |  |  | Steel/Wrought Iron |  | Delevan | Out of service drip tank check and monitor only out of service 'drip tank
| 00-40001-1 |  | 197.83 |  | Transmission |  | PHYSICAL/MECHANICAL JOINT | Valves |  | UNKNOWN |  | 2000-05-01 | [6 empty] | *waiting for clarification from system integrity as to whether or not this is a grade 2 or 3 5/30/000
| 00-40001-1 | 400 | 197.83 | 36 | Transmission |  | PHYSICAL/MECHANICAL JOINT | Valves |  | UNKNOWN |  | 2000-05-01 | [6 empty] | TEST UNIT HEATH DETRCRO-PAC III MODEL-DPIII SERIAL #10173
| 00-40001-1 |  | 197.83 |  | Transmission |  | PHYSICAL/MECHANICAL JOINT | Valves |  | UNKNOWN |  | 2000-05-01 | [6 empty] | HOV-152; MONITOR & CHECK ONLY; MONITOR & CHECK ONLY; MONITOR & CHECK ONLY
| 03-40002-1 | 400 | 233.87 | 36 | Transmission |  | UNKNOWN |  |  | UNKNOWN |  | 2003-06-13 |  |  |  | Steel/Wrought Iron |  | Dunnigan | MLV 233.87 (STEP TO OPERATOR)
| 03-17701-1 | 177 |  | 0.12 |  |  | OTHER |  | HINGE PACHING SEALS | UNKNOWN |  | 2003-06-13 | 2005-09-27 |  |  | Steel/Wrought Iron |  | Gerber | L-177 CHECK VALVE #23 VAULT ; GCS; GC REMOVED CHECK VALVE & BACKFILLED HOLE.
| 03-40001-1 | 400 | 149.18 | 0.75 | Transmission |  | UNKNOWN |  |  | UNKNOWN |  | 2003-08-13 | 2003-06-27 |  |  | Steel/Wrought Iron |  | Gerber | GAUGE LINE FOR MLV 149.18; GCS; VALVE NO LONGER LEAKING AFTER GREASING PRIMARY SEAL
|  | 400 | 150.7 | 36 | Transmission |  |  |  |  | DAMAGE BY 3RD PARTY | DIG IN | 2003-10-03 | 2003-10-06 | OTHER | BLENDED AND STAL WRAPPED | Steel/Wrought Iron |  |  | L400 MP150.70 (ELDER CREEK); Blended (filko) rogrs, mag particle testro and wrapped
|  |  |  | 36 | [8 empty] | 2003-06-09 | OTHER |  |  |  | Red Bluff | B; BOTTOM OF PIPE (5 TO 7 O'CLOCK); Blended damaged area w/60 geit pad.
|  | 400 | 152 | 36 | [14 empty] | 50' of M-400 was exposed in Thomas Creek. Pipe was cleaned, buffed and re-wrapped.
| 00-40101-1 | 401 | 129.37 | 42 | Transmission |  | UNKNOWN |  |  |  |  | 2000-03-13 | [5 empty] | Red Bluff | OP. MAP #384504 #2; OP. IA. #384506; DIA. SHEET #385200
| 00-40101-1 |  | 129.37 | 42 | Transmission |  | UNKNOWN |  |  |  |  | 2000-03-13 | [5 empty] | Red Bluff | Operating Map #364504 #2; Operating Diagram #384506; Plat Sheet #385200; *After review of this site I changed the grade to grade 3. Little or no detection of gas with jw sniffer.
| 00-40101-1 |  | 129.37 | 42 | Transmission |  | UNKNOWN |  |  |  |  | 2000-03-13 | [5 empty] | Red Bluff | after review of this site I changed the grade to grade 3. Little or no detection of gas with/ jw sniffer.
| 00-40101-1 |  | 129.37 | 42 | Transmission |  | UNKNOWN |  |  |  |  | 2000-03-13 | [5 empty] | Red Bluff | Op. Map #384504 #2; Op. Dia. #384506; DIA Sheet #385200
|  | 400 | 155.5 | [9 empty] | 2000-11-07 | OTHER | REPAIR WRAP AND COVER WITH ERCON MAT |  |  |  | WRAP REPAIRS THOMAS CREEK L-400 MP 155.5; Installed new star wrap on bare section of L-400. Bare pipe cleaned by hand, then installed new star wrap per instructions - ercon back filled pipe prior to installation of concrete blanket over L-400 at trouble area.
| 01-40001-1 | 400 | 180.74 |  | Transmission |  | VALVES |  | STEM SEAL | UNKNOWN |  | 2001-01-09 | [5 empty] | Willows | STEM LEAK - NON GREASABLE
| 10-40102-1 | 401 | 197.8 |  |  |  | VALVES |  |  | Other | VLV STEM | 2010-10-27 |  |  |  | Steel/Wrought Iron |  | Maxwell | work request made out each time to grease to stop leak.
| 10-40102-1 | 401 | 197.8 |  | Transmission |  | VALVES |  |  | OTHER | VLV STEM | 2010-06-28 |  |  |  | Steel/Wrought Iron |  | Maxwell | LEAK #10-40101-1; RETIRED ON 9-10-10; NEW LEAK #10-40102-1 ON 10-27-10; W.R. made out to grease awd repair valve gas leak.
| 00-40001-1 | 400 | 197.83 | 36 |  |  | MECHANICAL JOINT |  |  | OTHER | GASKET | 2000-05-01
| 09-40104-1 |  | 197.8 |  | Transmission |  | VALVES |  |  | OTHER | VALVE STEM | 2009-06-02 |  |  |  | Steel/Wrought Iron |  | Maxwell
| 09-40103-1 | 401 | 197.8 |  | Transmission |  | VALVES |  |  | OTHER | VALVE STEM | 2009-06-02 |  |  |  | Steel/Wrought Iron |  | Maxwell
| 06-40001-1 | 400 | 149.19 |  |  |  | VALVES |  |  | OTHER | STEM SEAL | 2006-06-07 |  |  |  | Steel/Wrought Iron |  | Gerber
| 08-40102-1 | 401 | 233.88 | 1 | Transmission |  | VALVES |  |  |  |  | 2008-06-04 | [5 empty] | Dunnigan | BUCKEYE PLS; BUCKEYE PLS; BUCKEYE PLS;
| 09-40104-1 |  | 197.8 |  | Transmission |  | VALVES |  |  | OTHER | VALVE STEM | 2009-06-02 |  |  |  | Steel/Wrought Iron | ; | Maxwell
| 05-40001-1 | 401 | 197.8 | [8 empty] | 2005-06-24 | 2006-05-05 |  |  |  |  | Delevan | DCS (401 SUCTION); Leak is undetectable at this time. Valve was installed & seal greased.
| 05-40001-1 | 401 | 197.8 | [8 empty] | 2005-06-24 | 2006-05-05 |  |  |  |  | Maxwell | W.R. #88714; GOV-1B; PRIMARY SEAL - GOV - 1B; REPAIRED. SEE BELOW; NOTHING FOUND OR DETECT; NO LEAK DETECTED.; DCS (401 SUCTION); Leak is undetectable at this time. Valve was installed & seal greased.
| 04-40001-1 | 400 | 197.8 | 36 |  |  | PHYSICAL/MECHANICAL JOINT |  | VALVES | UNKNOWN |  | 2004-06-04 | 2006-05-05 | OTHER | GREASE |  |  | Delevan | See Below; LEAK REPAIRED. DJMR OVER; Leak is currently undetectable. Contractor made repair of leak and checked with Gas Ranger. Leak is at zero. D. MacLean 4-15-10; TEST UNIT; HEATH; DETECTO - PAK iii; MODEL - DP III; SN 10173
| 00-40001-1 | 400 | 197.83 | 36 |  |  | PHYSICAL/MECHANICAL JOINT |  |  | OTHER | GASKET | 2000-05-01 | [5 empty] | Maxwell | LEAK A+ VALVE BODY; LEAK HAS GOTTEN WORSE; LEAK WROTE #2 W.R.; FLANGE, CHECK & MONITOR; ANNUAL RECHECK.; LEAK SEEMS TO SHOW MORE SIGN W.R. 139046 CLOSED CORRENT W.R. 164429
| 06-40001-1 | 400 | 149.19 |  |  |  | VALVES |  |  | OTHER | STEM SEAL | 2006-06-07 |  |  |  | Steel/Wrought Iron |  | Gerber
| 09-40009-1 | 400 | 149.19 |  |  |  | VALVES |  |  | OTHER | STEM SEAL | 2006-06-07 |  |  |  | Steel/Wrought Iron |  | Gerber
14 | 81-00002-1 | 400A | 177.86 | 36 | Service |  | OTHER |  |  | OTHER |  | 1981-04-30 | 1987-04-02 | OTHER |  | Steel/Wrought Iron |  |  | Main 400 was exposed to check 3/4" muller tee service tap. found the cap loose & gas leaking. Removed cap & cleaned threads. Resealed using teflon tape. sope tested for leaks.
14 | 81-00002-1 | 400A | 177.86 | 36" | Service |  | OTHER |  |  | OTHER |  | 1981-04-30 | 1987-04-02 | OTHER |  | Steel/Wrought Iron |  |  | REPAIR BY 7-11-86; G91136; Main 400 was exposed to check 3/4" muller tee service tap. Found cap loose removed cap & cleaned threads. Resealed using teflon tape, sope tested for leaks.; 02-16-83 F; 01-05-84 F; 01-02-85 F; 2-11-86F
|  | 401 | 255 | 42 | [7 empty] | 1995-11-19 |  |  |  | Other | X-60 |  | Main 401 was exposed to install a hot tap tee for smudd service a final report will be put into file with the finish grade or depth of m-401. this location will be a reg. station for service to SMUDD.
|  | 400B | 192.88 | 36 | [7 empty] | 1989-10-14 |  |  |  | Steel |  |  | M-400-B exposed to install a 12" water line under M-400 water line 8' deep.
|  | 400B | 197.72 | 36 | [7 empty] | 1988-02-26 |  |  |  | Steel |  |  | Pipe was exposed to farify wll thickness & piping arrangement in this area for "B" main suction valve replacement.
|  | 400B | 197.72 | 30 | [7 empty] | 1988-02-26 |  |  |  | Steel |  |  | Pipe exposed to verif wall thickness & piping arrangement in this area for "B" Main suction valve replacement.
|  | 400B | 185.75 | 36 | [7 empty] | 1985-10-30 |  |  |  | Steel |  | Willows | installing 24" water line across A&B line 200 feet north of tower 59/401A
|  | 400B | 184.45 | 36 | [7 empty] | 1985-10-30 |  |  |  | Steel |  | Willows | installing 24" water line across a & b line, 150' north of tower 58/398
|  | 400B | 180.78 | 36 | [11 empty] | Steel |  |  | main 400 B exposed for a 5' concrete waterline to be installed under main 400, rewrapped 20' due to small nicks in wrap GM
|  | 400B | 197 | 36 | [7 empty] | 1981-04-06 |  |  |  | Steel |  |  | Main 401 exposed to install a current span on north side of station yart outside of fenced area.
|  | M400B | 192.37 | 36 | [7 empty] | 1980-07-11 |  |  |  | Steel |  |  | Wrap was slightly damaged with now damage to pipe. Repaired wrap as neccessary.
|  | M400B | 190.86 + 19' | 36 | [11 empty] | Steel |  |  | main 400 b was exposed to install a 16 inch mater line across main 400A+B R/W for Kanawha water district. (JOINT, FIELD WRAP).
|  | 400 | 253.33 | 36 | [7 empty] | 1998-07-15 |  |  |  | Other | X-52
|  | 400 | 219.3 | 36 | [11 empty] | Steel |  |  | INFORMED ENGINEERING ABOUT M-400 AT CORTINA CREEK. PIPE IS EXPOSED ALSO AREA WITH ERCON MAT IS EXPOSED. AREA EXPOSED IS NORTH OF THEIR PALASANE SYSTEM REPAIRS TO BE MADE IN 1998
|  |  |  | 36 | [7 empty] | 1997-10-22 | [6 empty] | exposed M.400 at Salt Creek. GC crew doing work. M.P. 229.40 DEPTH VERIFICATION & EROSION WORK; M-400 EXPOSED TO VERIFY DEPTH IN CREEK.
|  | 400 | 156.67 | 36 | [7 empty] | 1997-03-13 |  |  |  | Other | X-52 |  | WALL THICKNESS VERIFICATION; M-400 EXPOSED FOR VERIFICATION OF WALL TAKINESS FOR TAP INSTALLATION. KA 3-17-97
|  | 400 | 246 | 36 | [7 empty] | 1996-08-06 |  |  |  | Steel |  |  | Note: Ercon to check erosion & give PG&E an estimate for repairs
|  | 400 | 139 | 36 | [7 empty] | 1996-08-06 |  |  |  | Steel |  |  | Note: Contacted piping engineer George Karkasis. on 8-6-96 George to get estimates from G.C Gas & ERCON for erosion repairs. Also the areas wrap is missing see attached sketch wrap will be repaired during erosion repairs.
|  |  | 255 | 36 | [7 empty] | 1996-01-22 |  |  |  | Other | X-52 |  | FINAL COVER AFTER NEW GRADING IS COMPLETE WILL BE APPROX 7' 10" INSTALLATION OF SMLED TAP 11-18-95
|  | 400 | 255 | 36 | [7 empty] | 1995-11-19 |  |  |  | Other | X-52 |  | Main 400 was exposed to install hot tap tee for SMUDD service. A final inspection teport will be put into file with the finish grade or depth of m-400 this location will be a reg station for service to SMUDD.
|  | 400 | 229.4 | 36 | [7 empty] | 1994-08-15 |  |  |  | Steel
|  | 400 | 176.86 | 36 | [7 empty] | 1994-07-07 |  |  |  | Other | Somastic
|  |  |  | 36 | [7 empty] | 1994-05-25 |  |  |  | Steel |  |  | MAIN 400 IS EXPOSED IN THOMES CREEK. DUE TO EROSSION PG&E INSTALLED A PACISAGE SYSTEM. THIS IS TO PREVENT FURTHER BANK EROSION & WILL EVENTUALLY SILT IN THE EXPOSED AREA. ERCON DEVELOPMENT CO. FABRICATED & INSTALLED THE PACISAGE & WILL MONITOR THE CREEK EROSION. PG&E WILL CONTINUE TO MONITOR.
|  | 400 | 139.81 | 36 | [7 empty] | 1996-07-07 |  |  |  | Steel |  |  | M-400 & service line was exposed to verify location of both lines & service tee.
|  | 400 | 201.8 | 36 | [7 empty] | 1992-05-07 |  |  |  | Steel |  |  | SEE DWG. ON BACK
|  | 400 | 206 | 36 | [7 empty] | 1992-06-11 |  |  |  | Steel |  |  | SEE SKETCH ON BACK
|  | 400 | 215.38 | 36 | [7 empty] | 1992-05-18 |  |  |  | Steel |  |  | SEE SKETCH ON BACK
|  | 400 |  | 36 | [7 empty] | 1992-08-21 |  |  |  | Steel |  | SEE SKETCH ON BACK
|  | 400 | 217.13 | 36 | [7 empty] | 1992-05-19 |  |  |  | Steel |  | SEE DWG ON BACK
|  | 400 | 218 | 36 | [7 empty] | 1992-05-21 |  |  |  | Steel |  |  | SEE ATTACHED DWG.
|  | 400 | 227.8 | 36 | [7 empty] | 1992-06-16 |  |  |  | Steel |  | SEE ATTACHED DWG.
|  | 400 | 232.85; 232.95; 233.0 | 36 | [7 empty] | 1992-06-22 |  |  |  | Steel |  |  | SEE SKETCH ON BACK
|  | 400 | 233.89 | 36 | [7 empty] | 1992-04-17 |  |  |  | Steel |  |  | SEE SKETCH ON BACK
|  | 400 | 236.35 | 36 | [11 empty] | Steel |  |  | SEE DWG ON BACK
|  | 400 | 240 | 36 | [7 empty] | 1992-10-12 |  |  |  | Steel
|  | 400 | 245 | 36 | [7 empty] | 1992-11-09 | [6 empty] | SEE SKETCH ON BACK
|  |  | 129.4 | 36 | [7 empty] | 1992-05-26 |  |  |  | Steel
|  | 400 | 164.36 | 36 | [7 empty] | 1990-04-06 |  |  |  | Steel |  | Corning | Line was exposed to pin off service tees on 3/4" risers. replaced rusted areas on risers & replaced 3/4" service valve down stream of MLV 164.36.
|  | 400 | 164.36 | 36 | [7 empty] | 1990-05-02 |  |  |  | Steel |  | Corning | line was exposed to pin off service tees on 3/4" risers. Replaced rusted areas of 3/4" pipe & to replaced 3/4" service valve down stream of MLV 164.36
|  | 400 | 142.91 | 26 | [7 empty] | 1990-04-06 |  |  |  | Steel |  | Red Bluff | Line exposed to pin off service tees on 3/4" riser. Replaced rusted areas of 3/4" pipe and to replace 3/4" service valves down stream of MLV 142.91
|  | 400 | 142.91 | 26 | [7 empty] | 1990-04-06 |  |  |  | Steel |  | Red Bluff | Line exposed to pin off service tee on 3/4" risers. Replaced rusted areas of 3/4" service valves down stream of MLV 142.91
|  | 400 | 192.88 | 36 | [7 empty] | 1989-10-14 |  |  |  | Steel |  | Glenn Co | M-400 exposed for installation of 12" water line. Under M-400 depth 42" deep new water line 8' deep.
|  | 400 | 179.86 | 36 | [7 empty] | 1989-06-26 |  |  |  | Steel |  | Artois | Line exposed to connect rextifier lead & A test station for pipe to soil readings.
|  | 400 | 142.61 | 26 | [7 empty] | 1989-01-20 |  |  |  | Steel |  | Red Bluff | Line exposed to pin off service tees on 3/4" risers. Replaced rusted areas of 3/4" pipe & to replace 3/4" service valves down stream of MLV 142.61
|  | 400 | 142.61 | 36 | [7 empty] | 1989-01-19 |  |  |  | Steel |  | Red Bluff | Line exposed to pin off service te on 3/4" riser. Replace rusted areas of 3/4" pipe & to replace 3/4" service valve upstream of MLV 142.61
|  | 400 | 142.61 | 36 | [7 empty] | 1989-01-19 |  |  |  | Steel |  | Red Bluff | line exposed to pin off service tee on 3/4" riser. Replace rusted areas of 3/4" service valves up stream of MLV 142.6
|  | 400 | 142.61 | 26 | [7 empty] | 1989-01-18 |  |  |  | Steel |  | Red Bluff | Line exposed to pin off service tees on 3/4" risers. Replace rusted areas of 3/4" pipe & to replace 3/4" service valves up&down stream of MLV 142.62
|  | 400 | 233.87 | 36 | [7 empty] | 1988-12-13 |  |  |  | Steel |  | Dunnigan | Line exposed for installtion of current spans-gm 4666111-CAD weldeed #10 wire (2) 3 locations south of MLV 233.87
|  | 400 | 197.72 | 36 | [7 empty] | 1988-12-05 |  |  |  | Steel |  | Delevan | line exposed for installation of current span - GM 4666111 - CAD welded #10 wire (2) 3 locations north of MLV 197.87
|  | 400 | 197.72 | 36 | [7 empty] | 1988-12-05 |  |  |  | Steel |  | Delevan | Line exposed for installation of current span GM 4666111. CAD welded # 10 wire (2) 3 locations north of GOV #4
|  | 400 | 149.18 | 36 | [7 empty] | 1988-11-22 |  |  |  | Steel |  | Gerber | Line Exposed for installation of current span GM-4666111 CAD welded #10 wire (2) in 3 locations north of MLV 149.18
|  | 400 | 129.36 | 36 | [7 empty] | 1988-11-17 |  |  |  | Steel |  | Red Bluff | Line exposed for installation of current spans. GM 4666111 cap welded # 10 wire (2) in 3 locations south of MLV 129.36
|  | 400 | 166.86 | 36 | [7 empty] | 1988-11-17 |  |  |  | Steel |  | Orland | line exposed to connect 3" existing tap to Houghton #1 gas well.
|  | 400 | 256.8 | 36 | [7 empty] | 1988-09-29 |  |  |  | Steel |  | Winters | pipe exposed to disconnect the clyde baker/rominger #1 gas well to line 400 in the pleasant creek gas field.
|  | 400 | 214.8 | 36 | [7 empty] | 1988-09-09 |  |  |  | Steel |  | Williams | Relocate tap from MP 215.3 to 214.8 (per cathy bennett - colgate div) removed 12"x12" area of coating. Repaired with poly-wrap.
|  | 400 | 215.3 | 36 | [7 empty] | 1988-09-03 |  |  |  | Steel |  | Williams | Installed 1" service tee w/5/8" hole. removed 12"x12" area of coating. Repaired with poly-wrap. 9-3-88
|  | 400A | 256.8 | 36 | [7 empty] | 1988-05-09 |  |  | PIPE EXPOSED TO CONNECT THE CLYDE BAKER ROMINGER #1 GAS WELL TO LINE 400 IN THE PLEASANT CREAK GAS FIELD. | Steel |  | Winters | Pipe exposed to connect the clyde baker rominger # 1 gass well to line 400 in the pleasant creek gas field.
|  | 400 | 149.18 | 36 | [7 empty] | 1988-02-29 |  |  |  | Steel |  | Gerber | PIPE EXPOSED TO VARIFY WALL THICKNESS & PIPING ARRANGEMENT IN THIS AREA FOR MAIN LINE VALVE REPLACEMENT.
|  | 400 | 197.83 | 36 | [7 empty] | 1988-02-26 |  |  |  | Steel |  | Delevan | Pipe exposed to verify wall thickness & piping arrangment in this area for main line valve replacement & installation of a new monitoring valve.
|  | 400 | 197.83 | 36 | [7 empty] | 1988-02-26 |  |  |  | Steel |  | Delevan | Pipe exposed to varify wall thickness & piping arrangement in this area for station suction valve replacement
|  | 400 | 197.83 | 30 | [7 empty] | 1988-02-26 |  |  |  | Steel |  | Delevan | Pipe exposed to verify wall thickness & piping arrangment in this area for station suction valve replacement.
|  | 400 | 221.26 | 36 | [7 empty] | 1987-11-18 |  |  |  | Steel |  | Williams | Exposed area is side of pipe below concrete slab. see letter to Mr. Kalfsheek dated 10-20-80. Sand bagged exposed pipe area, top layer used a cement&sand mixed in burlap
|  | 400A | 239 | 36 | [7 empty] | 1988-09-22 |  |  |  | Steel |  | Southwest of Dunnigan | Main 400 was exposed for installation of AT&T conduit for new fiber optic line.
|  | 400A | 233.87 | 36 | [7 empty] | 1987-06-18 |  |  |  | Steel |  | West of Dunnigan | Main 400 was exposed for installation of AT&T conduit for new fiber optic line.
|  | 400A | 252.31 | 36 | [11 empty] | Steel |  | Esparto - Yolo County | Installed 1" service tee w/ 1/4" hole. Removed 12"x12" area of coating. Repaired with Poly-wrap.
|  | 400A | 252.31 | 36 | [7 empty] | 1987-06-23 |  |  |  | Steel |  | Southwest of Esparto - Yolo County | Will instal 1" service tee when gas control will give clearance.
|  | 400A | 250.6 | 36 | [7 empty] | 1987-04-29 |  |  |  | Steel |  |  | Installed service tee (1") w/ 3/16" hole. Removed 12"x12" area of wrap. Repaired wrap with poly.wrap.
14 | 81-00002-1 | 400A | 177.86 | 36 | Service |  | OTHER |  |  | OTHER |  | 1981-04-30 | 1987-04-02 | OTHER |  | Steel/Wrought Iron |  | Rural Glenn Co. | Main 400 was exposed to check 3/4" muller tee service tap. Found the cap loose & gas leaking. Removed cap & cleaned threads. Resealed using teflon tape. Soap tested for leaks.
|  | 400A | 185.75 | 36 | [7 empty] | 1985-10-30 |  |  |  | Steel |  | Willows | Installed 24" transite water main under main 200 ft. north of tower 59/401A.
|  | 400A | 184.45 | 36 | [7 empty] | 1985-10-30 |  |  |  | Steel |  | Willows | Installed 24" transite water main 150 ft. north of tower 58/398.
|  | 400 | 229.07 | 36 | [7 empty] | 1983-06-03 |  |  |  | Steel |  | West of Arbuckle | Wrap damage to seven locations. Three locations have pioe damage. Depth of pipe damage - two .030" deep & one .010" deep. Used somastic & tar to repair wrap.
|  | 400A | 180.78 | 36 | [7 empty] | 1981-07-20 | [6 empty] | Main 400 A exposed for a 5' concrete water line to be installed under main 400. Rewrapped field joint, due to buble in wrap.
|  | 400A | 167.95 | 36 | [7 empty] | 1981-04-02 |  |  |  | Steel |  | Stoney Creek | exposed main 400 was backfilled to a depth of approx 6'.
|  | 400A | 159.87 | 36 | [7 empty] | 1981-04-07 |  |  |  | Steel |  |  | Main 400 exposed to install a current span. on North side of Garcia's pond.
|  | 400A | 192.37 | 36 | [7 empty] | 1980-07-11 |  |  |  | Steel
|  | M400A | 191.5 | 36" | [7 empty] | 1980-06-19 |  |  |  | Steel |  |  | KANAWHA WATER DISTRICT CROSSED UNDER MAIN WITH 32" TRANSITE PIPE HAD 15" CLEARANCE BETWEEN PIPES. WRAP WAS UNDAMAGED.
|  | 400B | 191.5 | 36 | [7 empty] | 1980-06-19 |  |  |  | Steel |  |  | Kanawha water distric crossed under main with 32" transite pipe. Had 17" of clearane between pipe. Wrap was undamaged.
|  | 400A | 190.86 + 19' | 36 | [7 empty] | 1980-05-08 |  |  |  | Steel |  | Rural Glenn Co. | Main 400A was exposed to install a 16 inch water line across main 400 A & B R/W for Kanawha water district
|  | 400A | 219.86 + 316' | 36 | [7 empty] | 1980-05-09 |  |  |  | Steel |  | Colusa Co. | Main 400 was exposed to install a 6" water line across main 400 R/W.
|  | 400 | 200.86 | 36 | [7 empty] | 1979-08-31 |  |  |  | Steel |  |  | Uncover main to take 1" tee out of service.
|  | 400 | 159.5 | 36 | [7 empty] | 1979-08-30 |  |  |  | Steel |  |  | Chipped wrap with backhoe while checking depth, no damage to pipe, repaired wrap.
|  | 400 | 213.85 | 36 | [7 empty] | 1978-11-09 | [5 empty] | Willows | Calif. coordinate no. T15NR4WMDB+M
|  | 400 | 217.08 | 36 | [7 empty] | 1979-06-14 |  |  |  | Steel |  | Willows | Calif. coordinates no. T15NR3WMDB+M
|  | 400 | 143.55 | 36 | [7 empty] | 1979-05-30 |  |  |  | Steel |  | Willows | Original with 4509.G. Calif. coordinate no. T26NR3WMOB+M
|  | 400 | 259.86 | 36 | Transmission | [6 empty] | 1974-09-14 |  |  |  | Steel/Wrought Iron |  | Winters | Reference Job: MR 4718-F
|  | 400 | 261.26 | 36 | Transmission | [6 empty] | 1974-09-14 |  |  |  | Steel/Wrought Iron |  | Winters | Reference Job: MR 4718-F
|  | 401 |  | 42 |  |  | LINE VALVE |  |  | OTHER | WRONG VALVE | 2011-04-26 | 2011-04-26 | DEACTIVATE #TP MAIN | REPLACE #TP < 50 FT, WELDED SAV-A-VALVE - WELD | Steel |  | Maxwell | Delevan conpressor station. cut in 42" can on line 401.
96 | 11-21001-1 | 400 | 197.83 | 12 | Transmission >= 20% SMYS |  | OTHER MECHANICAL JOINT |  |  | EQUIPMENT MALFUNCTION |  | 2011-01-25 | 2011-01-26 | MECHANICAL REPAIR FITTING - FITTING |  | Steel |  | Maxwell | HOV-152 Leak is at flange of valve. V-152 was injected with sealant by team industrial services. HOV-152 E-1 GAS COOLER DISCH. VALVE
96 | 11-21002-1 | 400 | 242.85 | 0.75 | Transmission |  | LINE VALVE |  |  | MATERIAL FAILURE |  | 2011-02-03 | 2011-02-04 | OTHER | SENSING LINE VALVE | Steel |  | Capay | Replace 3/4" u/s sensing line valve on tap to cache creek casino. Closed pin-off tee on main installed new 3/4" valve.
96 | 10-88942-1 | 400 | 224.52 | [8 empty] | 2010-10-26 | [5 empty] | Arbuckle
9 | 10-00292-1 | 400 |  | 0.75 | Single Service |  | THREADS |  |  | OTHER |  | 2010-01-08 | 2010-12-02 | Tighten Cap/Bolt - Fitting |  | Steel |  | Arbuckle | Leak on downstream union on 1st stage. tightened union.
| 10-88934-1 | 209 | 0.01 | 0.75 | Transmission |  | FITTING | Other | PRESSURE LINE | OTHER | CUT OFF | 2010-10-18 | 2010-11-05 | MECHANICAL REPAIR FITTING - FITTING | 3/4" STL. PIPE. | Steel |  | Willows
| 10-88939-1 | 400 | 193.84 | 2 | Transmission |  | FITTING | Other | BODY BLEED | OTHER | THREAD FITTING | 2010-10-21 | 2010-11-06 | MECHANICAL REPAIR FITTING - FITTING | 2.0" STL. CAP | Steel |  | Willows | Removed, doped 1/2" threaded pipe reinstalled piping.
| 10-88959-1 | 401 | [9 empty] | 2010-10-26 | [5 empty] | Arbuckle | 859 Frenzen RD. In PGE farm tap. L-400
| 10-88939-1 | 400 |  | 2 | [7 empty] | 2010-10-21 | 2010-11-06 |  |  |  |  | Willows
| 10-40002-1 | 400 | 164.4 | 36 | Transmission |  |  |  |  | Unknown |  | 2010-08-27 |  |  |  | Steel/Wrought Iron |  | Orland | This leak is under ground next to M.L. valve and piping for blowing out drips or "P.L. fluids." Can't find info on year valve was put into service.
36 | 71-00911-1 | NULL | NULL | 0.75 | Service |  | Fitting |  | NULL | Construction Defect |  | 1971-12-31 | 1971-12-31 | OTHER | NULL | Steel/Wrought Iron
35 | 72-10120-1 | NULL | NULL | 0.5 |  |  | Valves |  | NULL | Damage by outside Forces |  | 1972-09-19 | 1972-09-19 | OTHER | REMOVED PIPE | Steel/Wrought Iron
36 | 72-20055-1 | NULL | NULL | 1.14 |  |  | Body of Pipe |  | NULL | Corrosion |  | 1972-10-09 | 1972-10-09 | OTHER | NULL | Steel/Wrought Iron
36 | 72-20055-1 | NULL | NULL |  |  |  | Body of Pipe |  | NULL | Corrosion |  | 1972-08-21 |  | CLAMP | NULL | Steel/Wrought Iron
36 | 72-20055-1 | NULL | NULL | 1.25 |  |  | Body of Pipe |  | NULL | Corrosion |  | 10/09/0972 | 1975-05-20 | REPLACE PIPE AND/OR SERVICE | NULL | Steel/Wrought Iron |  | Eureka
36 | 72-20158-2 | NULL | NULL | 1.25 |  |  | Fitting |  | NULL | Material Failure |  | 1972-11-15 | 1972-11-15 | OTHER | INSTALLED NEW CAP | Steel/Wrought Iron |  | Eureka
36 | 72-30207-1 | NULL | NULL | 0.34 |  |  | Fitting |  | NULL | Construction Defect |  | 1972-07-19 | 1972-07-26 | REPLACE PIPE AND/OR SERVICE | NULL | Steel/Wrought Iron |  |  | Repaired service cock-reffited meter set.
36 | 72-30331-1 | NULL | NULL | 1.25 |  |  | METER |  | NULL | Other |  | 1972-07-27 | 1977-02-16 | OTHER | NULL | Steel/Wrought Iron |  | Eureka
36 | 72-30392-1 | NULL | NULL | 4 | Service |  | Girth Weld |  | NULL | Construction Defect |  | 1972-11-27 | 1973-03-12 | OTHER | REWELD | Steel/Wrought Iron |  | Eureka
36 | 72-30392-1 | [10 empty] | 1972-11-27 |  |  |  | Steel |  | Eureka
36 | 72-30484-1 | [5 empty] | Meter |  |  | OTHER |  | 1972-11-29 | 1973-04-12 | Other | Replaced Meter | Steel/Wrought Iron
36 | 73-10158-1 | NULL | NULL | 0.75 | Service |  | BODY OF PIPE |  | NULL | Damage by outside Forces |  | 1973-11-30 | 1973-11-30 | REPLACE PIPE AND/OR SERVICE | NULL | Steel/Wrought Iron
37 | 73-10206-1 | NULL | NULL | 0.75 | Distribution Feeder Main |  | Body of Pipe |  | NULL | Corrosion |  | 1973-12-04 | 1973-12-04 | OTHER | NULL | Steel/Wrought Iron
36 | 73-30086-1 |  | NULL |  |  |  | Fitting |  | NULL | Material Failure |  | 1973-12-26 | 1974-01-09 | OTHER | NULL | Steel/Wrought Iron
35 | 74-10063-1 | NULL | NULL | 0.75 | Service |  | Body of Pipe |  | NULL | Corrosion |  | 1974-04-09 | 1974-04-10 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron
37 | 74-20022-1 | NULL | NULL | 2 |  |  | Body of Pipe |  | NULL | Corrosion |  | 1974-06-12 | 1974-06-13 | CLAMP | NULL | Steel/Wrought Iron
36 | 74-30090-1 |  | NULL | 0.75 | Service |  | Fitting |  | NULL | Construction Defect |  | 1974-01-29 | 1974-01-30 | OTHER | NULL | Steel/Wrought Iron
37 | 76-10074-1 | NULL | NULL | 0.75 | Service |  | Fitting |  |  | Damage by outside Forces | Small Tractor | 1976-05-26 | 1976-05-26 | OTHER | REPLACE REGULATION | Steel/Wrought Iron
35 | 76-30164-1 | NULL | NULL | 2 |  |  | Fitting |  | NULL | CONSTRUCTION DEFECT |  | 1976-10-08 | 1977-01-03 | OTHER | NULL | Steel/Wrought Iron
36 | NULL | NULL | NULL | 1.14 |  |  | Body of Pipe |  | NULL | Corrosion |  | 1978-01-10 | 1978-01-11 | CLAMP | NULL | Steel/Wrought Iron
35 | 78-10098-1 | NULL | NULL | 2 | Distribution Feeder Main |  | Body of Pipe |  | NULL | Damage by outside Forces |  | 1978-06-05 | 1978-06-05 | REPLACE PIPE AND/OR SERVICE | NULL | Steel/Wrought Iron |  | Fortuna
36 | 78-30335-1 | NULL | NULL | 0.75 | Distribution Feeder Main |  | Regulator |  | NULL | OTHER |  | 1978-12-14 | 1979-06-05 | OTHER | GM 403117 REPLACE REGS | Steel/Wrought Iron |  | Eureka; Eureka
36 | 79-30163-1 | NULL | NULL | 4 | Transmission |  | Valves |  | NULL | OTHER |  | 1979-12-07 | 1980-01-11 | OTHER | INST. GREASE FITTING | Steel/Wrought Iron |  | Eureka | Inst. grease fitting stem & greased valve.
37 | 79-30127-1 | NULL | NULL | 0.75 |  |  | Fitting |  | NULL | OTHER |  | 1979-08-15 | 1979-08-23 | OTHER | NULL | Steel/Wrought Iron |  | Arcata
37 | 79-30133-1 | NULL | NULL | 2 |  |  | Girth Weld |  | NULL | Construction Defect |  | 1979-08-27 | 1979-09-19 | REPLACE PIPE AND/OR SERVICE | NULL | Steel/Wrought Iron |  | Blue Lake | Did a PMC & installed new pipe spool, replacing spool that was leaking, 9-19-79
36 | 80-30072-1 | NULL | NULL | 6 |  |  | Valves |  | NULL | OTHER | NO MAINTANCE | 1980-06-02 | 1980-10-22 | OTHER | NULL | Steel/Wrought Iron |  | Eureka
36 | 80-30148-1 | NULL | NULL | 6 | Transmission |  | Valves |  | NULL | CONSTRUCTION DEFECT |  | 1980-10-24 | 1981-04-15 | OTHER | NULL | Steel/Wrought Iron |  | Eureka | 4-13-81 Bell dug, no leak found metric valce open. no plug in threads @outlet pit.
36 | 80-30178-1 | NULL | NULL | 4 | Transmission |  | Valves |  | NULL | OTHER | ; | 1980-11-26 | 1981-04-30 | OTHER | NULL | Steel/Wrought Iron |  | Humbolt Hill | Downgrade to 3 & recheck in 6 mos
36 | 80-30179-1 | NULL | NULL | 4 | Transmission |  | Valves |  | NULL | OTHER |  | 1980-11-26 | 1980-12-23 | OTHER | NULL | Steel/Wrought Iron |  | Humbolt Hill
36 | 81-10007-1 |  |  | 2 |  |  | Tap Connection |  |  | CONSTRUCTION DEFECT |  | 1980-01-19 | 1980-01-19 | Other | Arc Weld | Steel/Wrought Iron |  | Eureka | LEAK AT TEE. POOR WELD AT TEE ON MAIN. ARC WELD REPAIRS.
37 | 81-30084-1 | NULL | NULL | 4 | Transmission |  | Valves |  |  | Other | No Grease | 1981-09-21 | 1982-01-05 | OTHER | NULL | Steel/Wrought Iron |  | Arc
36 | 81-30112-1 | NULL | NULL | 6 | Transmission |  | VALVES |  | NULL | OTHER |  | 1981-10-20 | 1981-10-26 | OTHER | NULL | Steel/Wrought Iron |  | Eureka
36 | 82-10091-1 |  |  | 4 | Transmission |  | Longitudinal Weld |  | NULL | Construction Defect |  | 1982-08-03 | 1982-08-03 | Other | 6" can weld | Steel/Wrought Iron
36 | 82-10091-1 | NULL | NULL | 4 | Transmission |  | Longitudinal Weld |  | NULL | Construction Defect |  | 1982-08-03 | 1982-08-03 | PATCH WELDED | NULL | Steel |  | Eureka
36 | 82-10114-1 | NULL | NULL | 0.25 |  |  | OTHER |  | NULL | Damage by outside Forces |  | 1982-10-21 | 1982-10-21 | OTHER | NULL | Steel/Wrought Iron
36 | 83-10015-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 02/19/0983 | 1983-02-19 | Clamp |  | Steel/Wrought Iron |  | Eureka
36 | 83-10041-1 | NULL | NULL | 0.5 | Distribution Feeder Main |  | Body of Pipe |  | NULL | Damage by outside Forces |  | 1983-07-16 | 1983-07-16 | OTHER | NULL | Steel/Wrought Iron |  | Eureka
36 | 83-30191-1 | NULL | NULL | 1.25 |  |  | Body of Pipe |  | NULL | Corrosion |  | 1983-11-29 | 1984-01-15 | REPLACE PIPE AND/OR SERVICE | NULL | Steel/Wrought Iron |  | Eureka
Steel/Wrought Iron
36 | 84-10035-1 |  |  | 0.5 |  |  | Body of Pipe |  |  | Corrosion |  | 1984-04-23 | 1984-04-23 | Other | Weld over pit | Steel
36 | 84-30007-1 | NULL | NULL | 4 | Transmission |  | Girth Weld |  | NULL | Construction Defect |  | 1984-01-19 | 1984-05-04 | OTHER | NULL | Steel/Wrought Iron |  | Eureka | Bad weld on Main, installed can.
36 | 84-30012-1 |  |  | 6 | Transmission |  | Fitting |  |  | Construction Defect |  | 1984-01-25 | 1984-05-15 | Patch Welded |  |  |  | Eureka
36 | 85-30123-1 | [10 empty] | 1985-11-26 | [5 empty] | Eureka
37 | 85-30160-1 |  |  | 0.78 | Transmission |  | Other Welds |  |  | Construction Defect |  | 1985-12-09 | 1987-06-23 | Patch Welded |  | Steel/Wrought Iron |  | For
37 | 85-30160-1 | [10 empty] | 1985-12-09 | [5 empty] | For
35 | 85-30182-1 | NULL | NULL | 0.25 | Distribution Feeder Main |  | Body of Pipe |  | NULL | Corrosion |  | 1985-12-18 | 1986-06-02 | REPLACE PIPE AND/OR SERVICE | NULL | Steel/Wrought Iron |  | Loleta
35 | 85-30182-1 | NULL | NULL |  |  |  | OTHER |  | NULL | Corrosion |  | 1985-12-18 | 1986-04-01 | OTHER | NULL |  |  | Loleta
37 | 86-10011-1 | NULL | NULL | 0.5 | Service |  | Body of Pipe |  | NULL | Damage by outside Forces |  | 1986-02-18 | 1986-03-04 | REPLACE PIPE AND/OR SERVICE | NULL | Steel/Wrought Iron |  | Blue Lake
35 | 86-30002-1 | NULL | NULL | 0.25 | Distribution Main |  | VALVES |  | NULL | OTHER |  | 1986-01-07 | 1986-01-27 | OTHER | NULL |  |  | Fortuna
36 | 86-30003-1 | NULL | NULL | 2 | Distribution Feeder Main |  | Physical/Mechanical Joint |  | NULL | OTHER |  | 1986-01-07 | 1986-03-28 | OTHER | NULL |  |  | Eureka | REPLACED 2 1/2 PIPE PLUGS AND REPAIRED LEAK IN VALVE. SMALL LEAK.
36 | 86-30009-1 | NULL | NULL | 4 | Transmission |  | OTHER |  | NULL | OTHER |  | 1986-01-27 | 1986-11-05 | OTHER | NULL |  |  | Eureka
37 | 86-30221-1 | NULL | NULL | 2 |  |  | Regulator |  | NULL | OTHER |  | 1986-09-30 | 1987-04-03 | OTHER | NULL |  |  | Arcata
36 | 86-30228-1 |  |  | 4 | Transmission |  | Other Welds |  |  | CONSTRUCTION DEFECT |  | 1986-09-30 | 1988-05-10 | Patch Welded |  | Steel |  | Arcata
37 | 86-30243-1 |  | NULL | 1.25 |  |  | Body of Pipe |  | NULL | Corrosion |  | 1986-10-02 | 1987-03-24 | Clamp | NULL | Steel/Wrought Iron |  | Arcata
36 | 86-30276-1 | NULL | NULL | 0.75 | Service |  | Valves |  | NULL | CONSTRUCTION DEFECT |  | 1986-10-13 | 1988-04-20 | OTHER | NULL | Steel/Wrought Iron |  | Eureka
36 | 86-30315-1 | [10 empty] | 1986-11-13
36 | 86-30315-1 | NULL | NULL | 0.75 | Service |  | Body of Pipe |  | NULL | Corrosion |  | 1986-11-13 | 1987-02-17 | REPLACE PIPE AND/OR SERVICE | NULL | Steel/Wrought Iron |  | Eureka
36 | 88-30050-1 | [10 empty] | 1988-04-11 | [5 empty] | EUR
36 | 88-30190-1 | [10 empty] | 1988-10-21
36 | 88-30185-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Other |  | 1988-10-25 | 1989-02-07 | Other |  | Aldyl A (Tan or Gray) |  | Eureka | replaced broke 1/2" pc dead end
| 86-10038-1 | [16 empty] | EUR
| 89-10033-1 | NULL | NULL | 0.75 | Service |  | Fitting |  | NULL | Construction Defect |  | 1989-05-10 | 1989-05-10 | Weld Over Sleeve or Can | Tighten Cap or Bolt | Steel/Wrought Iron |  | Eureka | Leaking cap on TP suc. and dist. meter set; repaired leaking farm tap cap, 5-9-89. Repaired riser. Replaced service cock and meter set, 5-10-89.
36 | 89-30236-1 | NULL | NULL | 3 |  |  | Body of Pipe |  | NULL | Corrosion |  | 1989-12-27 | 1990-03-21 | CLAMP | NULL | Steel/Wrought Iron |  | Eureka | Leak Clamp
| 91-10050-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Digin |  | 1991-06-15 | 1991-06-15 | Replace Pipe |  | Steel/Wrought Iron |  | Eureka | cut out 2' of bad pipe & reweld piece of new 4" pipe in
36 | 93-30054-1 | NULL | NULL | 3 | Service |  | Fitting |  | NULL | DAMAGE BY NATURAL FORCES |  | 1993-04-05 | 1993-05-13 | REPLACE PIPE AND/OR SERVICE | NULL | Steel/Wrought Iron |  | Eureka | Replaced 4" x 4" x 3" tee & 3" fire valve.
36 | 93-30238-1 | NULL | NULL | 2 | Service |  | Body of Pipe |  | NULL | Corrosion |  | 1993-05-13 | 1993-06-08 | CLAMP | NULL | Steel/Wrought Iron |  | Eureka | Leak Clamp
36 | 93-30419-1 | NULL | NULL | 2 | Service |  | Fitting |  | NULL | CORROSION |  | 1993-06-18 | 1993-09-02 | Replace Pipe | NULL | Steel/Wrought Iron |  | Eureka | cut out leaking control fitting - replaced S&R to 1100 vista
36 | 93-30537-1
36 | 93-30732-1 |  |  | 3 | Service |  | Other |  | Seam | Other |  | 1993-11-04 | 1993-12-22 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Eureka | Weld seam
36 | 92-30089-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1992-05-22 | 1996-01-29 | Other |  | Steel/Wrought Iron |  | Eureka | Greased valve 6.39 to stop leakage on valve.
35 | 92-30249-1 | NULL | NULL | 1 |  |  | Body of Pipe |  | NULL | Construction Defect |  | 1992-11-12 | 1993-04-17 | Other | NULL | Steel/Wrought Iron |  | Fortuna | replaced 1" X 1/2" stab fitting
37 | 94-30247-1 |  |  | 2 |  |  | Body of Pipe |  |  | Construction Defect |  | 1994-05-06 | 1994-05-25 | Other |  | Steel/Wrought Iron |  | Bayside | weld leak on fitting. fiting 2' from sertee to 4210 brookwood
36 | 94-30248-1 | [10 empty] | 1994-05-06 | 1994-06-23 |  |  |  |  | Eureka | Greased
37 | 94-30261-1 | [10 empty] | 1994-05-10 | [5 empty] | Arcata
37 | 94-30417-1 |  |  | 4 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 1994-07-07 | 1995-07-29 | Patch Welded |  | Steel/Wrought Iron |  | Arcata | re-welded tee on main
37 | 94-30417-1 | [10 empty] | 1994-07-07
36 | 94-30510-1 | [10 empty] | 1994-08-08 | [5 empty] | Eureka
36 | 94-30539-1 | NULL | NULL | 6 | Transmission |  | Valves |  | NULL | Other |  | 1994-11-07 | 1995-04-05 | Other | NULL | Steel/Wrought Iron |  | Eureka | greased valve
36 | 95-10025-1 | NULL | NULL | 2 | Transmission |  | Valves |  | NULL | Other |  | 1995-11-02 | 1995-11-27 | Other | GREASED AND OPERATED VALVE | Steel/Wrought Iron |  | Eureka | greased & operated valve
36 | 95-10027-1 |  |  |  | Transmission |  | Valves |  |  | Other |  | 1995-11-08 | 1996-01-29 | Other |  | Steel/Wrought Iron |  | Eureka | 1/4" plug leaking - redoped & tightened
36 | 95-30066-1 |  |  | 6 | Transmission |  | Tap Connection |  |  | Other |  | 1995-06-12 | 1996-06-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Eureka | tightened bolt on 6" T.P. muller line stopper
19 | 95-30106-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1995-10-03 | 1995-10-03 | Patch Welded |  | Steel/Wrought Iron |  | Arcata | installed patch and save-a-valve nipple 1"
37 | 95-30114-1 |  |  | 10 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 1995-10-12 | 1995-10-16 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Arcata | Installed a band over a defective weld
| 95-30134-1 | NULL | NULL | 0.75 | Transmission |  | Regulator |  | NULL | Other |  | 1995-12-19 | 1996-01-11 | REPLACE PIPE | NULL | Steel/Wrought Iron |  |  | Installed new HPR set
37 | 96-10010-1 | NULL | NULL | 4 | Transmission |  | Tap Connection |  | NULL | Construction Defect |  | 1996-09-10 |  | PATCH WELDED | NULL | Steel/Wrought Iron |  | Arcata | Patch weled leaks on g/o tee & on weld on renforcing patch on main
37 | 96-10013-1 | [10 empty] | 1996-09-11 | [5 empty] | Arcata
37 | 96-10014-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1996-09-12 | 1996-09-25 | Other |  | Steel/Wrought Iron |  | Arcata | replace SEL valve no leak found on high to high set
37 | 96-10016-1 | NULL | NULL | 1 | Distribution Main |  | Fitting |  | NULL | Material Failure |  | 1996-09-12 | 1997-10-09 | REPLACE PIPE | NULL | Cast Iron |  | Eureka
37 | 96-10018-1 | NULL | NULL | 0.75 | Transmission |  | Valves |  | NULL | Other |  | 1996-09-12 | 1996-09-27 | Other |  | Steel/Wrought Iron |  | Eureka
36 | 96-10027-1 | NULL | NULL | 4 | Distribution Main |  | Valves |  | NULL | Other |  | 1996-10-14 | 1995-12-09 | Other | NULL | Steel/Wrought Iron |  | Eureka | greased valve lead in reg station
36 | 96-10037-1 |  | NULL | 4 | Transmission |  | Fitting |  |  | Other |  | 1996-11-09 | 1997-05-02 | Other | NULL | Steel/Wrought Iron |  | Eureka | leaking at 2nd ..... valve nipple- pulled plug + .... .... .... cap
36 | 96-10037-1 | [10 empty] | 1996-11-09
36 | 92-30089-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1992-05-22 | 1996-01-29 | Other |  | Steel/Wrought Iron |  | Eureka | greased valve 6.39 to stop leakage on valve
36 | 96-10038-1 | NULL | NULL | 0.75 | Transmission |  | BODY OF PIPE |  | NULL | Corrosion |  | 1996-11-09 | 1997-03-04 | Replace Pipe | NULL | Steel/Wrought Iron |  | Eureka | leak located at reinforcing tab holding 3/4" line for gauge tap on V00.00
| 96-30012-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1996-02-03 | 1996-02-03 | Clamp |  | Steel/Wrought Iron |  | Arcata | Installed temp ss leak clamp
| 96-30072-1 |  |  | 1.25 |  |  | Body of Pipe |  |  | DIGIN |  | 1996-07-30 | 1996-07-30 | Replace Pipe |  | Aldyl A (Tan or Gray) |  | Eureka | replace 3' feet of 1 1/4" pc main - ......
35 | 96-50016-1 | [10 empty] | 1996-04-03 | [5 empty] | Alton
| 96-50017-1 | [10 empty] | 1996-04-03 | [5 empty] | Fortuna
35 | 96-50037-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1996-04-22 | 1996-08-13 | Other |  | Steel/Wrought Iron |  | Dinsmore | inst. new grease fitting dre-greased valve to stop leak
| 96-50038-1 | [10 empty] | 1996-04-22 | [5 empty] | Dinsmore
| 96-50044-1 | [10 empty] | 1996-04-23 | [5 empty] | Mad River
| 97-10014-1 | [10 empty] | 1997-09-22
| 97-10026-1 | NULL | NULL | 6 | Transmission |  | Other |  | Bolted flange |  |  | 1997-11-05 | 2001-10-01 | Tighten Cap or Bolt | TIGHTEN BOLTS ON EXISTING FLANGE | Steel/Wrought Iron |  | Eureka
36 | 97-10026-1 | NULL | NULL | 6 | Transmission |  | Fitting |  | NULL | Other |  | 1997-11-05 | 2001-03-25 | TIGHTEN CAP OR BOLT | NULL | Steel/Wrought Iron |  | Eureka | Tightened flange bolts
36 | 95-30066-1 | NULL | NULL | 6 | Transmission |  | Tap Connection |  | NULL | Other |  |  | 1996-06-01 | TIGHTEN CAP OR BOLT | NULL | Steel/Wrought Iron
| 97-10031-1 | [10 empty] | 1997-11-12 | [5 empty] | Eureka
36 | 97-10032-1 | [10 empty] | 1997-11-12
36 | 96-10028-1 | [10 empty] | 1996-10-14
36 | 97-50008-1 |  |  | 6 | Transmission |  | Valves |  |  | Material Failure |  | 1997-03-13 | 1997-10-09 | Replace Pipe |  | Steel/Wrought Iron |  | Eureka | replace leaking button head fitting & greased valve
36 | 97-50071-1 |  |  | 0.25 | Transmission |  | Fitting |  |  | Other |  | 1997-05-01 | 1997-10-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Eureka | tightened & redoped plug in metric
| 97-50094-1 | [10 empty] | 1997-05-27 | [5 empty] | Eureka
36 | 97-50095-1 | [10 empty] | 1997-05-27 | [5 empty] | Eureka
| 98-10001-1 | 137 | 1.77 | 10 | Transmission |  | OTHER WELDS |  | NULL | CONSTRUCTION DEFECT |  | 1998-09-03 | 1998-09-04 | Welded Sleeve/Can - Weld | NULL | Steel/Wrought Iron |  | Arcata
| 98-10007-1 |  |  | 0 | [7 empty] | 1998-10-06 | [5 empty] | Eureka
| 98-10010-1 | [10 empty] | 1998-10-06 | [5 empty] | Eureka
| 98-10019-1 | NULL | NULL | 6 | Transmission |  | Other Welds |  | NULL | Construction Defect |  | 1998-11-03 | 1999-03-18 | PATCH WELDED | NULL | Steel/Wrought Iron |  | Eureka | welded up leak on weld on sav-a-valve nipple
36 | 98-30008-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1998-02-10 | 1998-02-10 | Clamp |  | Steel/Wrought Iron |  | Eureka | installed clamp/ reduce pressure to 35 psig
| 98-30055-1 | NULL | NULL | 4 | Transmission |  | Body of Pipe |  | NULL | Digin |  | 1998-07-24 | 1998-07-27 | Replace Pipe | NULL | Steel/Wrought Iron |  |  | replaced 27" of damaged pipe
| 98-30055-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Digin |  | 1998-07-24 | 1998-07-27 |  |  | Steel/Wrought Iron |  | Fortuna
36 | 98-50018-1 |  |  | 4 |  |  | Valves |  |  | Material Failure |  | 1998-03-09 | 1998-04-15 | Other |  | Steel/Wrought Iron |  | Eureka | Greased valve
| 01-10023-1 | [10 empty] | 2001-10-02 | [5 empty] | Eureka
| 99-30039-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Atmospheric Corrosion |  | 1999-05-20 | 1999-10-07 |  |  | Steel/Wrought Iron |  | Loleta
| 99-50031-1 | 4"L137C | NULL |  | Distribution Main |  | Other |  | NULL | Other | CAP AND PLUG | 1999-04-13 | 2010-04-08 | OTHER | REPLACED 3/4 CAP AND 3/4 PLUG | Steel/Wrought Iron |  | Eureka | replaceed 3/4 x 3/4 cap in old reg pit
| 00-10004-1 | NULL | NULL | 3 | Distribution Main |  | BODY OF PIPE |  | NULL | Damage by 3rd Party |  | 2000-08-08 |  |  | NULL | Steel/Wrought Iron |  | Arcata
| 00-10015-1 | [10 empty] | 2000-09-20 | [5 empty] | Eureka; Eureka
| 00-30020-1 | L178A | NULL | 0.75 | Distribution Main |  | Fitting |  | NULL | Material Failure |  | 2000-05-25 | 2000-05-25 | Other | REPLACE REG. | Steel/Wrought Iron |  | Arcata
| 01-10003-1 | 10L137D | 297 | 0.75 | Transmission |  | Valves |  | NULL | Other | plug valve dry | 2001-08-07 | 2001-08-14 | Other | greased valve | Steel/Wrought Iron |  | Arcata | valve to high-to high at. Greased valve to stop small leak
| 01-10008-1 | [10 empty] | 2001-09-06 | [5 empty] | Eureka
| 01-10022-1 |  |  | 2 | Transmission |  | Valves |  |  | Material Failure |  | 2001-10-02 | 2003-10-30 | Other |  | Steel/Wrought Iron |  | Eureka | Greased valve T-64
| 01-10024-1 | 126B | 6.39 | [8 empty] | 2001-10-03 | [5 empty] | Eureka
| 01-30008-1 | 137C | 1.65 | 4 | Transmission |  | Body of Pipe |  | NULL | EXTERNAL CORROSION |  | 2001-02-13 | 2001-02-13 | Welded Sleeve/Can - Weld | NULL | Steel/Wrought Iron |  | Eureka | final repair welded 4" can.
| 01-40022-1 | 1374C | 2.66 | 0.75 | Transmission |  | Body of Pipe |  | NULL | Digin |  | 2001-07-18 | 2001-07-18 | SERVICE PARTIALLY REPLACED | NULL | Steel/Wrought Iron |  | Eureka | Replaced damaged pipe
| 01-50003-1 | DFM | NULL | 0.75 | Service |  | Fitting |  | NULL | Other | PIPE THREAD | 2001-05-07 | 2001-05-07 | Other | RE DOPE THREADS | Steel/Wrought Iron |  | Alton | redoped and tightened
| 01-50044-1 | 177 | 17389 | 12 | Transmission |  | Valves |  | NULL | Other | dry pipe dope | 2001-07-09 | 2001-07-23 | Other | REPACED 1/4" METRIC | Steel/Wrought Iron |  |  | replaced 1/4" metric valve with new one on blowdown flange
| 01-50057-1 | 126B | 44 | 0.75 | Service |  | Fitting |  | NULL | External Corrosion |  | 2001-07-14 | 2006-05-17 | Replace Partial Service | NULL | Steel/Wrought Iron |  | Fortuna | replaced HPR & relief w/associated fittings on service.
| 03-40016- | NULL | NULL | 2 | Distribution Main |  | Body of Pipe |  | NULL | Digin |  | 2003-08-06 | 2003-08-06 | Mechanical Repair Fitting - Fitting | REPLACE DIST MAIN < 100 FT |  | TR 41B | McKinleyville | Repaired dig-in w/(1) 2" amprit clamp
| 04-30001-1 |  |  | 6 | Gathering |  | Unknown |  |  | Unknown |  | 2004-01-01 | 2004-01-10 | Other | closed valve | Steel/Wrought Iron |  | Fortuna | Closed valve 36, 32, 112, 72, 29, & 25
| 04-30042- | 137 | 4.92 | 4 | Transmission |  | Girth Weld |  | NULL | Construction Defect |  | 2004-12-09 | 2004-12-14 | Welded Sleeve/Can - Weld | NULL | Steel/Wrought Iron |  | Eureka | Repairs made w/ 4" wrinkle band sleeve
| 05-10012-1 | 137 | 2.75 | 6" | Transmission |  | Other Welds |  | NULL | Construction Defect |  | 2005-09-12 | 2006-02-15 | Welded Sleeve/Can - Weld | NULL | Steel/Wrought Iron |  | Eureka | welded 6" can & rewrapped main
| 05-10017-1 | 126 | 4.97 | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2007-02-15 | 2007-02-15 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | Eureka | Onstalled 4" T.P. Clamp
| 05-30012- | NULL | NULL | 6 | Transmission |  | Body of Pipe |  | NULL | INTERNAL CORROSION |  | 03/00/0026 | 2005-04-02 | Other | BLEW DOWN PIPE | Steel/Wrought Iron |  | Fortuna | Blew down pipe
| 05-30046-1 | 125 | NULL |  |  |  | DRIP |  | NULL | EXTERNAL CORROSION |  |  | 2005-11-09 | Welded Sleeve/Can - Weld | NULL
| 06-10010-1 | 126-4 | 9.95 | 4 | Transmission |  | Fitting |  | NULL | Unknown |  | 2010-03-26 | 2010-03-26 | Tighten Cap or Bolt | NULL | Steel/Wrought Iron |  | Eureka | tightened bolts on 4" line stopper, repaded 3/4" plug. Taped and rigged 2" save-a-valve cap. Soap test Ok.
| 06-30029-1 | 177 | 124 | 12 | Transmission |  | Body of Pipe |  | NULL | Construction Defect | DAMAGE BY NATURAL FORCES | 2006-08-19 | 2006-08-20 | Replace TP Main | NULL | Steel/Wrought Iron |  | Mad River | Replaced 16' of 12" stl pipe
| 06-30038-1 | 4L126B | 4.13 | 4 | Transmission |  | Body of Pipe |  | NULL | External Corrosion |  | 2006-12-22 | 2006-12-22 | Other | Pletco clamp | Steel/Wrought Iron |  | Eureka | Install 4" pletco clamp
35 | 06-50032-1 | [10 empty] | 2006-04-05
| 07-30004-1 | 4L137C | 4.36 | 4 | Transmission |  | Body of Pipe |  | NULL | External Corrosion |  | 2007-01-18 | 2007-01-18 | Mechanical Repair Fitting - Fitting | NULL | Steel/Wrought Iron |  | Bayside | Installed 4" plidco clamp
| 07-30033-1 | NULL | NULL | 0.75 | Service |  | Valves |  | NULL | External Corrosion |  | 2007-11-23 | 2007-11-27 | REPLACE VALVE < 2 INCH | REBUILET SET | Steel/Wrought Iron |  | Loleta | Corrosion leak on high to high set/plugged off rebuilt set.
| 07-30035- | L-125 | [9 empty] | 2007-12-14
| 07-30035-1 | 3L125 | NULL | 2 | Gathering |  | Body of Pipe |  | NULL | Atmospheric Corrosion |  | 2007-12-14 | 2008-01-15 | Replace Dist Main < 100 ft | NULL | Steel/Wrought Iron |  | Fortuna
| 07-30035-1 | 3L125 | NULL | 2 | Transmission |  | Body of Pipe |  | NULL | External Corrosion |  | 2007-12-14 | 2008-01-15 | Replace Dist Main < 100 ft | NULL | Steel/Wrought Iron |  | Fortuna
| 08-20002-1 | NULL | NULL | 0.25 | Transmission |  | Valves |  | NULL | Other | LOOSE VALVE | 2006-07-07 | 2008-07-11 | Other | Tighten valve & plug | Steel/Wrought Iron |  | Eureka | tighten valve and plug
| 08-20003-1 | 126A6 | NULL | 6 | Transmission |  | Valves |  | NULL | Other | grease stem | 2008-07-07 | 2008-07-11 | Other | greased valve | Steel/Wrought Iron |  | Eureka | Greased valve
| 08-20004-1 | 4L126B | NULL | 0.75 | Service |  | Body of Pipe |  | NULL | Atmospheric Corrosion |  | 2008-07-14 | 2009-05-23 | Other | REPLACED HPR | Steel/Wrought Iron |  | Eureka | Replaced HPR set
| 08-20006-1 | 4L126B | [9 empty] | 2008-07-14 | [5 empty] | Eureka
| 08-20009-1 | [10 empty] | 2008-07-07 | [5 empty] | Eureka
| 08-20010-1 | [10 empty] | 2008-07-17 | [5 empty] | Eureka
| 08-20012-1 | 4L126B | 10.57 | 2 | Transmission |  | Valves |  | NULL | Construction Defect |  | 2008-11-10 | 2010-07-24 | Tighten Cap or Bolt | NULL | Steel/Wrought Iron |  | Eureka | Tightened flange
| 08-20013-1 | NULL | 10.57 | 3/8" | Transmission |  | Other |  | SST COMPRESSION FTG. | Other | FTG LOOSE | 2008-11-10 | 2010-01-21 | Other | TIGHTEN SST FTGS. | Other | 316 SST | Eureka
| 08-20015-1 | [10 empty] | 2008-11-14
| 08-30009-1 | L189 | 0.01 | 0.75 | Transmission |  | Body of Pipe |  | NULL | Atmospheric Corrosion |  | 2008-04-01 | 2008-05-29 | Welded Sleeve/Can - Weld | NULL | Steel/Wrought Iron |  | Eureka | Welded coupling replaced valve
| 08-30009- | L189 | NULL | 0.75 | Transmission |  | Body of Pipe |  | NULL | Atmospheric Corrosion |  | 2008-04-01 |  |  | NULL | Wrought Iron |  | Eureka
| 08-30025-1 | NULL | NULL | 0.75 | Transmission |  | Body of Pipe |  | NULL | Construction Defect |  | 2008-07-15 | 2008-10-01 | OTHER | REPAIRED WELD | Steel/Wrought Iron |  | Arcata | Welded up
| 08-30030-1 | NULL | NULL | 0.75 | Single Service |  | Riser |  | NULL | External Corrosion |  | 2008-07-23 | 2008-07-23 | Other | C/O AND RETHREADED RISER | Steel/Wrought Iron |  | McKinleyville
| 08-30033-1 | 177 | [9 empty] | 2008-08-28
| 08-30038-1 | 8L137B | 7.22 | 8.625 | Transmission |  | Girth Weld |  | NULL | Weld Failure |  | 2008-09-17 | 2009-02-15 | Patch Weld - Weld | NULL | Steel/Wrought Iron |  | Arcata | Ground out and repaired weld
| 08-30039-1 | 10L137D | 0.17 | 10 | Transmission |  | Girth Weld |  | NULL | Weld Failure |  | 2009-09-17 | 2009-03-18 | Mechanical Repair Fitting - Fitting | Pledco clamp | Steel/Wrought Iron |  | Arcata
| 08-30039-1 | 137D |  | 10 | [7 empty] | 2008-09-17 | [5 empty] | Arcata
| 08-30040-1 | [10 empty] | 2008-09-29
| 08-30057-1 | L177 | NULL | 0.25 | Transmission |  | Tap Connection |  | NULL | Other | loose cap | 2008-12-17 | 2008-12-18 | Tighten Cap or Bolt | NULL | Steel/Wrought Iron |  | Alton/Fortuna | 1/4" plug leak on pipe tap/tightened
| 08-40012-1 | 4"L137C | 3.12 | 3.12 | Transmission |  | Body of Pipe |  | NULL |  |  | 2008-07-21 | 2008-07-22 | Replace TP Main | NULL | Steel/Wrought Iron |  | Arcata
| 08-40018- |  |  | 0.75 | Single Service |  | Body of Pipe |  |  |  |  | 2008-10-01 | 2008-10-01 | Replace Partial Service |  | Steel/Wrought Iron |  | Arcata
| 09-20001-1 | L1310-01 | 1.26 | [8 empty] | 2009-05-13
| 09-20003-1 | [10 empty] | 2009-05-23
| 09-20004-1 | [10 empty] | 2009-05-30
| 09-30008-1 | 6L126A | NULL | 6 | Transmission |  | Body of Pipe |  | NULL | External Corrosion |  | 2009-02-19 |  |  | NULL | Steel/Wrought Iron |  | Eureka
| 03-30008-1 | 6L126A | NULL | 6 | Transmission |  | Body of Pipe |  | NULL | External Corrosion |  | 2009-02-19 | 2009-02-20 | OTHER | PLEDCO CLAMP | Steel/Wrought Iron |  | Eureka | clamp temp. need to weld can on in Aug.
| 09-30011-1 | NULL | NULL | 2 | Single Service |  | Body of Pipe |  | NULL | Atmospheric Corrosion |  | 2009-03-21 | 2009-03-21 | Other | SHUT OF CURB VALVE | Steel/Wrought Iron |  | Loleta
| 09-30015-1 | 10"137D | 0.15 | 10 | Transmission |  | Girth Weld |  | NULL | Weld Failure |  | 2009-03-26 | 2009-03-27 | Other | Ground out entire girth weld and re-welded | Steel/Wrought Iron |  | Arcata | repaired girth weld
| 09-30030-1 | 6"L126a | 10.78 | [8 empty] | 09/30/0030 | [5 empty] | Eureka
36 | 10-20001-1 | 12L177 | 19191 | [8 empty] | 2010-05-24 | [5 empty] | Eureka
| 10-30045- | L1309-01 | 4.19 | 0.5 | Transmission |  | Mechanical Joint |  | NULL | Construction Defect |  | 2010-06-22 | 2010-06-22 | Mechanical Repair Fitting - Fitting | NULL | Steel/Wrought Iron |  | Rio Dell | Tighten sense line. Reg station leak on sense line.
| 10-81022-1 | 126A | NULL | 2 | Distribution Main |  | Valves |  | NULL | Other | low grease | 2010-10-02 | 2010-10-07 | Other | grease 2" valve | Steel/Wrought Iron |  | Eureka | Greased 2" valve to stop leak
| 10-81023- | 126B | NULL | 0.5 | Distribution Main |  | FITTING |  | NULL | Other | loose | 2010-10-02 | 2010-10-04 | Other | TIGHTENED FITTING | Steel/Wrought Iron |  | Eureka | tightened fitting
| 10-81101-1 | 137C | 5075 | 5075 | [7 empty] | 2010-10-02 | [5 empty] | Arcata
35 | 10-81101-1 | 1309-01 | 3.3 | 0.75 | Single Service |  | Threads |  | NULL | No/Deteriorated Pipe Dope |  | 2010-10-09 | 2011-03-09 | Other | RE DOPE THREADS | Steel |  | Rio Dell | Redope threads-fitting
| 10-81101-1 | 1309-01 | 3.3 | [8 empty] | 2010-10-09
| 10-81102- | 177A | 158.23 | 12 | Transmission |  | Girth Weld |  | NULL | Construction Defect |  | 2010-10-11 | 2010-10-15 | Welded Sleeve/Can - Weld | NULL | Steel/Wrought Iron |  | Elevation 2438 | welded sleeve
| 10-81102- | 137C | NULL | 4 | Transmission |  | OTHER WELDS |  | NULL | Construction Defect |  | 2010-10-02 | 2010-11-11 | Patch Weld - Weld | NULL | Steel/Wrought Iron |  | Bayside | weld repair
| 10-81103- | 137D |  | 0.75 | Single Service |  | Other |  | relief | Equipment Malfunction |  | 2010-10-02 | 2010-10-04 | Other | replaced relief | Steel/Wrought Iron |  | Arcata | replaced leaking relief
| 10-81141-1 | 1 | [9 empty] | 2010-10-02 | [5 empty] | Fortuna
| 10-81200-1 | 137B | 3.69 | [8 empty] | 2010-10-03 | [5 empty] | Eureka
| 10-81201-1 | 11111111 | [9 empty] | 2010-10-03
| 10-60012-1 | 6L126B | 0.01 | 6 | Transmission |  | Fitting |  | NULL | Other | loose flange bolts on PFC | 2010-01-10 | 2010-01-15 | Tighten Cap or Bolt | NULL | Steel/Wrought Iron |  | Eureka
35 | 11-30009-B | 125 | NULL |  |  |  | Girth Weld |  |  | Internal Corrosion |  | 2011-03-21 | 2011-03-22 | Fill Weld - Weld | NULL | Steel/Wrought Iron |  | Fortuna | repair weld
96 | 10-88016-1 | 057B | 2.02 | 22 |  |  | Other |  |  | Other |  | 2010-10-15 | 2011-03-18 | Other | NULL | Steel |  | Stockton | Not company gas; PLM work request 173791: Per ATS mobile gas chromatograph, not likely natural gas due to absence of ethane, propane and butane
96 | 10-82081-1 | 057A | 0.32 | 0.5 | Transmission |  | Other |  |  | Other |  | 2010-09-18 | 2011-03-17 | Other |  | Steel |  | Holt | tightened fittings and replaced section of SS. Tubing with fittings; all repairs made on PLM work request #173783;
96 | 10-82086-1 | 057-M125 | 0.24 | 2 | Transmission |  | Other |  |  | Other |  | 2010-09-18 | 2011-03-15 | Other |  | Steel |  | Holt | Replaced O-ring; Multiple leaks repaired by PLM work Request. (Total of 4); WR 173581: Replaced O-Ring. No leak found w/soap after repressured; WR 173580: 0% gas tested with CGI (No leak found); WR 173582: Resealed threaded joints. No leaks found w/soalp after repressured; WR 173719: Replaced O-Ring. No leak found w/soap after repressured
96 | 10-82083-1 | 057A-MD1 | 1.13 | 4 | Transmission >= 20% SMYS |  | Line Valve |  | NULL | Other |  | 2010-09-18 | 2011-03-10 | Greased - Other | NULL | Steel |  | Holt | Injected stem packing; Multiple leaks repaired by PLM Work Request (Total of 7); WR 173430: Injected stem packing. No Leak found with saop test (V-15); WR 173429: 0% gas tested with CGI. (No leak found); WR 168449: No leak found by Hxgb. (Same as WR 173429); WR 173431: Resealed threaded joint. No leak found after repressured; WR 168450: Duplicate of WR 173431; WR 173428: Replaced 2" Union (No leak found after repressures); WR 168448: Duplicate of WR 17328
96 | 10-82089-1 | 057A-M11 | 0.2 | 4 | Transmission >= 20% SMYS |  | Line Valve |  | NULL | Other |  | 2010-09-18 | 2011-03-14 | Greased - Other | NULL | Steel |  | Holt | Injected Stem Packing; Multiple leaks repaired by PLM work requests (total of 10); WR 173435: Injected stem packing-no leak found with soap test (V-10); WR 173440: Replaced O-ring. Soap test ok after repressured; WR 173633: Replaced O-ring. Soap test ok after represssured; WR 173442: Injected stem packing. No leak found with soap test; WR 173445; Cleared and reassembled. Soap test ok after repressured; WR 173577: Tightened loos Union. Soap test ok after repressured; WR 173436: Tightened Union (WR 168440) Soap test ok; WR 173443: Found to be normal opperating conditions.(See WR 168440); WR173444: Found to be normal opperating conditions. (see WR 168440); WR: 168440: Duplicate of WR 173436, WR 173443, WR 173444
96 | 10-82088-1 | 057A-M13 | 0.11 | 4 |  |  | Line Valve |  | NULL | Other |  | 2010-09-18 | 2011-03-17 | Greased - Other | NULL | Steel |  | Holt | Injected stem packing; Multiple leaks repaired by PLM work requests (toal of 8); WR 173449: Injected stem packing, No leak found, soap test (V-15); WR 168511: Duplicate to WR 173449; WR 173446 replace seel = O-ring, soap test ok; WR173447: Cleaned and reassemble-retorqued, No leak, soap test; WR173448: Injected stem packing. No leak found, soap test (V-10); WR: 168509: Duplicate of WR 173448; WR 173450: Found to be normal operating conditions; WR 168512: Duplicate of WR168512
96 | 10-82090-1 | 057A-M15 | 0 | 6 |  |  | Line Valve |  | NULL | Other |  | 2010-09-18 | 2011-03-14 |  | NULL | Steel |  | Holt | Injected grease replaced bolton head; Multipl leaks repaired by PLM Work requests (total of 6); WR 168437: Replaced button head- No leak after soap rest; WR168435: Duplicate of WR 168437; Wr 168516: Replaced regulators soap test ok; WR168438: Injected stem packing, Soap test ok (V-4); WR 168439: replaced button head, no leak after soap test (V-A); WR 173675: Shaffer tool tightened bolts. No leak after soap test.
96 | 10-82065-1 | 057A-Mt | 0.35 | 0.75 |  |  | Threads |  | NULL | No/Deteriorated Pipe Dope |  | 2010-09-18 | 2011-03-14 | Tighten Cap/Bolt - Fitting | NULL | Steel |  | Holt | Redoped and tightened; Redoped and tightened threaded plug on drip line valve, soap test ok after repair
96 | 10-82093-1 | 057A-12 | 0.05 | 3 |  |  | Other Mechanical Joint |  | NULL | Other |  | 2010-09-18 | 2011-03-17 | Greased - Other | NULL | Steel |  | Holt | Replaced O-ring; Multiple leaks repaired by PLM work request (total 5); WR17368: Replaced O-ring. Soap test ok.; WR173639: Replace O-ring, Soap test ok; WR173640: Injected stem packing, Soap test ok; WR173641: Opened and cleaned tighten back up, soap test ok; WR 173643: Replace O-Ring, Soap test ok.
96 | 10-82091-1 | 056A | NULL | 3 |  |  | Other Mechanical Joint |  | NULL | Other |  | 2010-09-18 | 2011-03-17 | Tighten Cap/Bolt - Fitting | NULL | Steel |  | Holt | Cleaned and Resealed; Multiple leaks repaired by PLM Work request (total of 8); WR173650: Cleaned and retightened. Soap test ok after repressured; WR173651: Repaired on 2010 Inspection, soap test ok; WR:173637: Packing injected by shaffer oil tools. Soap test ok; WR173652: Repaired on 2010 inspection . soap test ok; WR173655 repaired on 2010 Inspection. soap test ok; WR 173656: Repaired 2010 Inspection. Soap test ok; WR 173657: 3-14-11, No leak found w/ soap; WR 173659: repaired by shaffer oil tools. Soap test ok
96 | 10-82087-1 | 057A-M10 | 0 | 3 |  |  | Line Valve |  | NULL | Other |  | 2010-09-18 | 2011-03-17 | Greased - Other | NULL | Steel |  | Holt | Injected stem packing; Multiple leaks repaired by PLM Work Requests (Total of 5); WR: 173645: Injected stem packing, soap test ok (V-10); WR: 173646: Injected stem packing, soap test ok (V-15); WR: 173647: Inspected Re-lube O-ring, soap test ok F¦M11 fitter; WR: 173648: Cleaned threads resealed threads, tightened up. soap test ok; WR: 173649: Replace O-ring tighten-up, soap test ok
96 | 10-82087-1 | 057A-M10 | 0 | 3 |  |  | Line Valve |  | NULL | Other |  | 2010-09-18 | 2011-03-17 | Greased - Other | NULL | Steel |  | Holt | Injected stem packing; Multiple leaks repaired by PLM Work Request (total of 5); WR: 173645: Inject stem packing, soap test ok (V-10); WR: 173646: Inject stem packing, soap test ok (V-15); WR: 173647: Inspect Re-lube O-ring soap test ok F¦M11 Fitter; WR: 173648: Cleaned threads resealed threads tightened up soap test ok; WR: 173649 Replace o-ring tighten-up soap test ok
96 | 10-82064-1 | 057A-T2 | 0 00 | 4 |  |  | Other Mechanical Joint |  | NULL | Other |  | 2010-09-18 | 2011-03-17 | Other |  | Steel |  | Holt | No Leak detected with soap; Multiple leaks repaired by PLM work request (total of 3); WR 173784: No leak detected at this field pressure; WR 173785: Replace filtz housing O-Ring soap test ok; WR 173786: Injected stem packing, soap test ok
|  | 057A-wt | 0.59 |  | Transmission | [7 empty] | 2010-01-26 | Other | REPAIRED DAMAGED PIPE WRAP | Steel/Wrought Iron |  |  | Re-wrapped 36" section of main
| 09-35002-1 |  |  | 0.75 | Transmission |  | Other |  | Cap | Other | LOOSE CAPS | 2009-06-11 | 2010-05-28 | Other | REMOVE CAP REDOPE RETIGHTEN | Steel/Wrought Iron |  | Williams | Faxed 6-4-10, Valve (V-2) on Meyers Rd., On V-2, V-2, V-2 (repaired); Retighten. Re-doped caps; Soap test, remove caps redope & tighten; Remove caps on 2 ea. pinoff tees, redope & retighten
| 09-35002-1 | [10 empty] | 2009-08-11 | [5 empty] | Williams | Valve (V-2) on Meyers Rd., On V-2, V-2, V-2
| 09-35002-1 | [10 empty] | 2009-08-11 | [5 empty] | Williams | Valve (V-2) on Meyers Rd., On V-2, V-2
| 09-35004-1 |  |  | 0.75 | Single Service |  | Valves |  |  | Other | Valve open plug leaking | 2009-06-09 | 2010-03-08 | Other | CLOSE METRIC - DOPE & TIGHTEN PLUG | Steel/Wrought Iron |  | Meridian | Faxed 3-9-10, S/O HWY 20 100' E/O Tarke Rd., In HPR Box. Marked in yellow. leak in HPR bx; Close valve, dope & tighten plug; Soap test, Close metric, dope & tighten plug, H202 metric loose, close metric dope & tighten plug
| 09-21015- |  |  | 6 | Transmission |  | Valves |  |  | Other | VALVE NEEDED GREASED | 2009-01-25 | 2009-02-02 | Other | Greased valve core | Steel/Wrought Iron |  | Sacramento | See leak # 09-21228, PM 41044000, T&R Dept, No excavation required, At valve B-34, Valve Lid, Valve Lid; Soap tested 6" D.P. Valve - B34 at line press. Found valve B34 to be leaking - repaired LK. by greasing it. Please recheck 30-45 days to ensure valve still not leaking. Found 6" V-B34 LKing. -greased to stop LK.
| 09-21138-1 |  |  | 1 | Transmission |  | Other |  | CAP ON PIN OFF TEE | Other | O-RINGS IN CAP | 2009-06-04 | 2009-07-28 | Other | Replaced cap on pin off tee | Steel/Wrought Iron |  | Sacramento | No evacuation required, Roseville Rd Reg sta, At G-5 box next to Valve G; Replaced cap on 1'' pin off tee; soap tested after repairs made, see attached map
| 09-21154- |  |  | 0.75 | Transmission |  | Other |  | Grease fitting | Other | Needed grease | 2009-06-12 | 2009-06-12 | Other | Greased | Steel/Wrought Iron |  | Sacramento | PM#41101070, 103866589, At valve B-21, Delete Leak Repaired; Greased to stop bubbles
| 09-21160-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | Grease fitting | 2009-06-11 | 2009-12-14 | Other | greased fittings | Steel/Wrought Iron |  | Sacramento | At V-24 outside of station, V-24; Repair leak at grease fitting; Soap tested after repair
| 09-21228-1 |  |  | 0.5 | Transmission |  | Valves |  |  | Other | Pipe thread on valve | 2009-06-25 | 2009-06-25 | Other | Tightened plug | Steel/Wrought Iron |  | Sacramento | 103885677, PM#41108405, Previous LK. 09-21015, 08-21114, No excavation required, At valve B-34 in (HCA), T&R crew called. Delete leak, rechecked, after repairs made; Soap tested after repair, 1) source of leak indentified as: threads on 1/2'' gauge tap, 2) date of source determination: 6/25/09, 3) prompt repairs required? Y/N: Yes
52 | 10-21359-1 | 119 |  | 20 | Transmission >= 20% SMYS |  | THREADS |  |  | Other |  | 2010-06-25 | 2011-05-06 | Tighten Cap/Bolt - Fitting |  | Steel |  | Sacramento | Unscrewed fittings & taped & doped& tightened; Repaired leaks on V-12 - 15. 1 on screw fitting on body ..., 1 on plug on body of valve, 1 on gauge tape pin off tee cap. Soaped after repaires were made no more leaks found
| 09-20238-1 | DFM |  | 6 | Transmission |  | Fitting |  |  | Construction Defect |  | 2009-05-01 | 2009-06-22 | Other | TIGHTENED 3/4 PLUG | Steel/Wrought Iron |  | Sacramento | Doped and tightened 3/4" plug on lid to 6" BT Mueller fitting; Tightened 3/4" plug on lid to 6" BT at PCF. Did not know pressure of this DFM
| 10-21456-1 | DFM |  | 0.75 | Transmission |  | Other |  | REGULATOR DIAPHRAGM | Other |  | 2010-06-21 | 2010-06-21 | Other |  | Steel/Wrought Iron |  | Sacramento | Rebuilt HPR type rig and reset Relief; rebuilt HPR type reg & reset relief, soaped ok
52 | 10-21454-1 | DFM |  | 4 | Transmission >= 20% SMYS |  | Line Valve |  | REG STATION VALVE INSIDE VAULT | Other | 1/2" plugs | 2010-06-21 | 2011-04-04 | Greased - Other | VALVES + DOPED PLUGS | Steel |  | Sacramento; | Found two leak;
| 10-21397-1 | DFM |  | 2 | Transmission |  | Valves |  |  | Unknown |  | 2010-06-12 | 2010-08-26 | Other | GREASED + OPERATED | Steel/Wrought Iron |  | Sacramento | Greased and operated 2" plug value soaped ok
| 10-21392-1 | DFM | [9 empty] | 2010-06-01 | [5 empty] | Folsom
52 | 10-22617-1 | 108 | 66.14 | 0.75 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-11-17 | 2010-11-18 | Tighten Cap/Bolt - Fitting |  | Steel |  | Sacramento | Re-Doped and tightened 3/4" plug on valve; Re-doped and tightened 3/4" plug on 3/4 valve soap tested after repair no leaks
52 | 10-22582-1 | DFM |  | 8 | Transmission |  | Line Valve |  |  | Other |  | 2010-06-07 | 2011-03-10 | Greased - Other |  | Steel |  | Sacramento | Grease valve
52 | 10-22621-1 | 119 |  | 2 | Transmission |  | THREADS |  |  | Other |  | 2010-11-12 | 2011-01-18 | Soap and/or Tape - Other |  | Steel |  | Sacramento | Removed valve. Raped and doped threads and re-tightened valve
| 09-53106-1 | 150 | 8.95 | 6.63 | Transmission |  | Body of Pipe |  |  |  |  | 2009-09-01 | 2009-09-01 | Replace #TP Main >= 50 ft |  | Steel/Wrought Iron |  | Dixon | Replace 78" of existing damaged pipe w/ pre-tested emergency pipe; see gas events 10 161;
| 09-53056-1 | DFM |  | 6 | Transmission |  | Valves |  |  | Other | LACK OF GREASE | 2009-02-04 | 2009-04-01 | Other | Greased and operated valve | Steel/Wrought Iron |  | Dixon | Leak on 6" plug valve- greased and operted to stop leake vave I/D-01
| 09-53057-1 |  |  | 0.75 | Transmission |  | Other |  | GAUGE TAP | Other |  | 2009-02-04 | 2009-05-05 | Other | TIGHTEN GAUGE TAP | Steel/Wrought Iron |  | Dixon | Tighten gauge tap valve; soap test after repair
| 08-21133-1 | 123 |  | 2 | Transmission |  | Valves |  |  | Other | Loose fitting | 2009-06-08 | 2009-10-06 | Tighten Cap or Bolt | GREASE FITTING | Steel/Wrought Iron |  | Sacramento | Tighten fitting on tubing for grease; T & R tighten nut on tubing for grease valve
| 10-35332-1 | DFM |  | 0.25 | Transmission |  | Other |  | Nipple | Other |  | 2010-09-04 | 2010-11-19 | Other | Tighten nipple | Steel/Wrought Iron |  | Esparto | Fixed leak at nipple on inlet of meter serv.; Fixed leak at nipper at 1/4" tap
50 | 10-35336-1 | 119 |  | 0.75 | Single Service |  | THREADS |  |  | Other |  | 2010-09-10 | 2011-02-16 | Other | TAPE AND DOPE SCREW FITTING, CLEAN AND GREASE UNIONS. | Steel |  | Davis | Tape and doped screw fitting clean and grease union
| 10-35023-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other | Loose | 2010-05-04 | 2010-06-30 | Other | TIGHTENED H202-SOAP TESTED NO LEAKS | Steel/Wrought Iron |  | Woodland | Tightened H202 soap tested no leaks; doped and re-tightened H202 ... Soap tested no leaks
| 10-35042-1 | 116 |  | 0.75 | Service |  | Regulator |  |  | Equipment Malfunction |  | 2010-05-11 | 2010-08-31 | Deactivated Partial Service |  | Steel/Wrought Iron |  | Davis | Single service off, removed hi to hi, capped end, soap tested piping no leaks found; removed hi to hi- Reg/Relief. Pin off tee is pinned off and plugged
| 10-35036-1 | 220 |  | 4 | Service |  | Valves |  |  | Other | Loose bolt | 2010-05-13 | 2010-08-04 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Davis | Tightened flange bolts @ down stroam bypass valve; tightened flane bolts on 4" downstream bypass valve for meter
| 10-35027-1 | 220 |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2010-05-07 | 2010-06-30 | Other | GREASED VALVE. SOAP TESTED NO LEAKS. | Steel/Wrought Iron |  | Woodland | Greased valve soap tested no leaks; greased nordstrow 3/4" valve soap tested no leaks
| 10-35029-1 | 220 |  | 6 | Service |  | Valves |  |  | Other |  | 2010-05-07 | 2010-08-04 | Other | Greased and Operated | Steel/Wrought Iron |  | Woodland | Greased and Operated;Greased and operated 6" downstream valve- soap teseted no leakage
52 | 11-21000-1 | 0605-03 | 2.64 | 6 | Transmission >= 20% SMYS |  | Other |  | Steel cap | No/Deteriorated Pipe Dope |  | 2011-01-06 | 2011-04-04 | Tighten Cap or Bolt |  | Steel |  | Galt | Re-doped and tightened cap; Re-doped and tightened cap on tee for gauge tap
| 09-21139-1 |  |  | 0.75 | Transmission |  | Other |  | Elbow | Other | Loose fitting | 2009-06-04 | 2009-12-14 | Other | Tighten elbow fitting | Steel/Wrought Iron |  | Citrus Heights | repair leak at body bleed elbow fitting
| 09-21161-1 |  |  |  | Transmission >= 20% SMYS | [6 empty] | 2009-06-11 | [5 empty] | Sacramento
| 09-21177-1 | 119B |  | 0.75 | Transmission |  | Valves |  |  | Other | THREADS LEAKING | 2009-06-15 | 2009-12-21 | Other | Re-doped threads; | Steel/Wrought Iron |  | Sacramento | Removed, redoped and tightened valve
| 09-21167-1 |  |  | 0.5 | Transmission |  | Other |  | Cap | Other | Loose Cap | 2009-06-12 | 2009-12-14 | OTHER | GG FITTING CAP TIGHTEN | Steel/Wrought Iron |  | Sacramento | Repair leak @ grease fitting caps; soap tested after repairs
| 10-35028-1 | 220 |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2010-05-07 | 2010-06-30 | Other | GREASED INCOT VALVE, OPERATED-SOAP TESTED | Steel/Wrought Iron |  | Woodland | Greased inlet valve- operated- soap tested; greased and operated 3/4" nordstrow valve soaptested no leaks
| 10-35021-1 |  |  | 1 | Transmission |  | Regulator |  |  | Other |  | 2010-05-01 | 2010-08-05 | Other | REMOVED REPLACED FITTING, REPLACED DIAPHRAM | Steel/Wrought Iron |  | Woodland | Removed, replaced fitting, replaced diaphram; re doped and taped threads @ pri-cut-rog. Replaced diaphram...reg
| 10-35005-1 | 116 |  | 1 | Transmission |  | Valves |  |  | Other | Loose; | 2010-03-10 | 2010-06-09 | Other | TIGHTENED BODY BLEED RELIEF | Steel/Wrought Iron |  | Davis | Tightened body bleed for relief; tightened plug on body bleed for V-63, soap tested no leaks
| 10-53161- | 210B | 18.65 | 16 | Transmission |  | Other |  | CAP ON A BOND AND SERVICE | Unknown |  | 2010-10-29 | 2010-11-03 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Fairfield | ; Cap on service tee... leaking also cap on savor valve was leaking fitting coming off side of main- redoped and reinstalled cap. soap test under pressure (savor valve on 3/4 steel)
| 10-55104- | DFM |  | 6 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2010-10-26 | 2010-10-27 | Other | PLIDCO 6 | Steel |  | Yolo | Soap tested at line pressure 318335 viton seal 1000 maop 6" plidco
| 10-55111- | 172A |  | 0.75 | Transmission >= 20% SMYS |  | Fitting |  | MULLER TEE (PIN-OFF) | Other | LOOSE FITTINGS | 2010-11-22 | 2011-02-10 | Tighten Cap/Bolt - Fitting | TIGHTENED UNION, RE-DOPED + TIGHTENED MUELLER PIN-OFF TEE CAP | Steel |  | Zamora | Tightened union, re-doped and tightened mueller pin off tee cap; Repaired leaks @ 1st stage union and muieller tee cap painted union and mueller pin-off tee, soaped, no leaks; see attached plat.
| 09-35027-1 | 0646-01 |  | 1 | Transmission |  | Fitting |  |  | Other |  | 2009-06-01 | 2010-08-04 | Other | TIGHTENED NIPPLE | Steel/Wrought Iron |  | Yolo | Removed Reg. Cleaned threads - taped and doped; Repaired leak @ threads on downstream side of regulator
| 10-54005-1 | 167 |  | 1 | Transmission |  | Fitting |  |  | Other | Loose fitting | 2010-08-06 | 2010-09-22 | Other | Tighten Union | Steel/Wrought Iron |  | Butte City | Tighten Union; Soap test ok
| 09-56003-1 |  |  | 200 | Transmission |  | Body of Pipe |  |  |  |  | 2009-03-19 | 2009-03-20 | Replace #TP Main < 50 ft |  | Steel |  | Arbuckle | Installed 7' of 2" and 4' of 3" steel pipe and new 3" valve; digging on N/S of V-1 to determine position of valve stem after emergency. Call of valve operation failure, and pressure drop @ reg. station. See AS-Binds for repair information completed by GC Gas Rocklin.
| 09-38001-1 | 172 |  | 0.25 | Transmission |  | Fitting |  |  | Other | Loose; | 2009-06-11 | 2009-08-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Williams | O.P. Map384019-1zz; Tignten gauge tap plug ...
| 10-22430- | DFM |  | 0.75 | Transmission |  | Tap Connection |  |  | Other | Cap needed Dope | 2010-10-14 | 2010-10-14 | OTHER | Re-doped cap | Steel/Wrought Iron |  | Citrus Heights | Re-doped cap on station line 3/4" tee. It backfilled w/ native soil. I backfilled 100% sand. Tested at line pressure
| 10-21362- |  |  | 0.75 | Transmission |  | Fitting |  |  | Other | Valve | 2010-06-05 | 2010-06-05 | OTHER | Grease valve | Steel/Wrought Iron |  | Rancho Cordova | Tightened fitting and greased By-Pass valve
| 10-21361- |  |  | 0.75 | Transmission |  | Fitting |  |  | Other | Valve | 2010-06-05 | 2010-06-05 | Other | REGULATOR | Steel/Wrought Iron |  | Rancho Cordova | Found Foreign material under reg. seat. Replaced reg. seat.
| 10-21290- | 119 |  | 2 | Transmission |  | Valves |  | VALVE | Other | LOOSE FITTINGS | 2010-05-24 | 2010-05-24 | Other | TIGHTENED VALVE | Steel/Wrought Iron |  | Folsom | Threaded pipe... outlet 1/2" by-pass valve; Soap tested afrer repair, ok.
| 10-20274- |  |  | 8 | Transmission |  | FITTING |  |  | Construction Defect |  | 2010-08-18 | 2010-08-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Sacramento | Tightened brass plug. doped and tightened cap; Soap Tested
| 09-21832-1 |  |  | 4 | Transmission |  | Valves |  |  | Other | Needed grease | 2009-11-09 | 2009-11-09 | Other | GREASED VALVE | Steel/Wrought Iron |  | Sacramento | Greased leaking plug valve, soap tested, no leaks on By-Pass
| 09-21832-1 | DFM | [9 empty] | 2009-08-26 | [5 empty] | Sacramento
| 09-21717- | DFM |  | 0.75 | Transmission |  | Other |  | PIN-OFF TEE | Other | Dried pipe dope | 2009-08-25 | 2009-08-28 | Other | REDOPE & TIGHTEN CAP | Steel/Wrought Iron |  | Antelope | Took line pressure down flat, removed cap, re-doped fitting and re-installed cap; soap tested after repairs
| 09-21224 |  |  | 0.75 | Transmission |  | Other |  | Cap | Material Failure |  | 2009-06-30 | 2009-06-30 | Other | CAP-O-RINGS BAD | Steel/Wrought Iron |  | Sacramento | 1.) Source of leaking identified as: O-rings in cap of Mueller: pin-off tee; 2.) Date of source determination: 6/30/09; 3.) Prompt repaires required y/n: Yes- Replaced cap w/ new
| 10-22524-1 | 1 |  | 24 | Transmission |  | Valves |  |  | Other | Loose plug | 2010-10-12 | 2010-11-17 | Tighten Cap or Bolt | ; | Steel/Wrought Iron |  | Sacramento | Tightened plug on valve body; Tightened plug on valve body. Soap test - no leak. See attached plat sheet 2525 and attached OP. Diagram 385/86
| 10-22524-1 | [10 empty] | 2010-10-12 | [5 empty] | Sacramento
52 | 11-21308-B |  |  | 0.75 | Transmission >= 20% SMYS |  | Other Welds |  |  | Construction Defect |  | 2011-05-03 | 2011-05-04 | Fill Weld - Weld |  | Steel |  | Sacramento | At base of transduer cabinet; Leaking elbow re-welded; Leaking 3/4" STL elbow leaking rewelded by K. Flynn-KLF7. Soap tested @ line-pressure
52 | 11-21305-b |  |  | 6 | Transmission >= 20% SMYS |  | Fitting |  |  | Construction Defect |  | 2011-04-19 | 2011-04-22 | Tighten Cap/Bolt - Fitting |  | Steel |  | Sacramento | Over D.F.M. next to valve B-34 in patch; Tightened bolts- re-doped 3/4" plug and tightened; Slow going 42" of slurry over TP> GM hand dig and spade- In street checking 6" M24 Sinc tee (old c/o) by valve B-34. found 3/4" plug on top of cap was leaking we re-doped and tightened and snugged bolts on cap. no leak on c/o attached ACR Monitor sheet and tact board
52 | 11-21302-B | 0617-08 |  | 0.75 | Transmission >= 20% SMYS |  | Threads |  | EAES | No/Deteriorated Pipe Dope |  | 2011-04-13 | 2011-04-13 | Mechanical Repair Fitting - Fitting |  | Steel |  | Fair Oaks; Soap test ok | At valve D-34 (east bound bike lane); @ Grease fitting north side of valve D34
52 | 11-21301-B | 119 |  | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-04-12 | 2011-04-12 | Tighten Cap/Bolt - Fitting |  |  |  | Sacramento | Over 16" T.P. gas main in front of Reg. Station; Doped and tightened cap on 1" 04-12-11 Pin off tee gauge tap.; 1.) source of leak identified as: pinched off, Doped and tightened cap on 1" 2.) date of source determination: 4/12/11 soap tested at line pressure 5cc 3.) Prompt repairs required y/n: yes;
52 | 11-21272- | 0617-06 |  |  | Transmission >= 20% SMYS |  | Threads |  |  | Other | Loose | 2011-04-06 | 2011-05-04 | Tighten Cap/Bolt - Fitting |  | Steel |  | Sacramento | At valve D-109 in park parking lot; Unsrewed plug taped and doped and re-tightened;
| 09-53019- | 210 |  | 2 | Transmission |  | Valves |  |  | Unknown |  | 2009-01-21 | 2009-01-22 | Other | Greased valve; | Steel/Wrought Iron |  | Fairview | Greased valve
| 09-53012- |  |  | 3 | Transmission |  | Valves |  |  | Other | Stem Seal | 2009-01-08 | 2009-01-13 | Other | Replace stem seal | Steel/Wrought Iron |  | Dixon | Replaced stem seal on 3" cameron ball valve
| 09-33112- |  |  | 12 | Transmission |  | Tap Connection |  | LEAK @ 3/4 TAP WELD | Weld Failure |  | 2009-05-14 | 2009-05-14 | Fill Weld - Weld |  | Steel/Wrought Iron |  | Suisun City | Blew down 40' of line. Welder fixed pinhole leak, repressured line to 100 psi- soap test ok. Equalized line soap testok. Revalued for normal operation
| 09-33025- | VV57 DFM |  | 2 | Transmission |  | Valves |  |  | Unknown |  | 2010-03-24 | 2010-03-25 | Other | Tighten packing | Steel/Wrought Iron |  | Vacaville | T & R tightened packing on Valve
| 09-53026-1 | DFM |  | 4 | Transmission |  | Valves |  |  | Other | No grease | 2009-02-04 | 2009-04-01 | Other | Greased and operated valve | Steel/Wrought Iron |  | Dixon | ...Valve V-2 in monitor vault R-20 Dixon greased and operated
| 09-53026-1 | [10 empty] | 2009-02-04 | [5 empty] | Dixon
| 10-35031-b |  |  | 0.75 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2011-04-22 | 2011-04-29 | Tighten Cap/Bolt - Fitting |  | Steel |  | Woodland | At multiple G-5 boxes marked with yellow X; Redoped threads and soap tested; Soap tested at line pressure
| 10-53161- | 210B | 18.65 | 16 | Transmission |  | Other |  | CAP ON A BOND AND SERVICE | Unknown |  | 2010-10-29 | 2010-11-08 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Fairfield | Cap on service Tee (A-bound) leaking. Also cap on savor valve was leaking. Fitting coming off side of main- Redoped and reinstalled cap. Soap test under pressure (Savor value on 3/4" steel)
|  |  |  | 16 | [11 empty] | Steel/Wrought Iron |  | Antelope | Abandoned Reg. station cut off and capped 3/4" Stl.
|  | 123 |  | 16 | [11 empty] | Steel/Wrought Iron |  | Antelope
| 10-55105-1 | DFM |  | 1 | Transmission |  | Fitting |  | REGULATOR, VALVE | Other | DRIED OUT DOPE | 2010-11-03 | 2010-11-03 | Other | TAPED + DOPED, PIPING + FITTINGS + REBUILD REGS | Steel/Wrought Iron |  | Davis | See Comment Sect.; Multiple leaks on 1st stage reg. diaphram head bolts, and @ threads to reg. valve. Multiple leaks on monitor threads to body and @ threads to valve. Multiple leaks on reg. Threads to body and @ threads to union and @ threads to valve. Rebuilt all regs. (1st cut & Red.) IxG4 11-3-10, Soaped hi to hi, no leaks found; See attached plat.
50 | 10-55111-B | [10 empty] | 2010-11-22 | [5 empty] | Zamora | At hi to hi set that way back behind this prperty near markers
50 | 11-55030-B |  |  | 0.75 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2011-04-29 | 2011-04-29 | Tighten Cap/Bolt - Fitting |  | Steel |  | Woodland | High pressure pin off tee far static union; Redoped threads and soap tested; Soap tested at line pressure
| 09-35001-1 |  |  | 2 | Transmission |  | Valves |  |  | Other | Grease | 2009-03-18 | 2009-03-18 | Other | Greased valve | Steel/Wrought Iron |  | Davis | Greased and operated valve; Found V-2 to be leaking due to lack of grease. repaired by greasing and perating valve
| 09-35002- |  |  | 1.25 | Transmission |  | Other |  | GREASE FITTING | Unknown |  | 2009-03-18 | 2009-03-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Davis | Found fitting on valve to be leaking- tightened same to repair leak
| 09-20010- | 0614-13 | 0.01 | 6.62 | Transmission |  | Valves |  |  | Material Failure |  | 2009-01-05 | 2009-01-06 | Replace #TP Main < 50 ft |  | Steel/Wrought Iron |  | Sacramento
| 10-21287-1 | 116 |  | 1 | Transmission |  | Valves |  |  | Other | dried out O-ring | 2010-05-13 | 2010-12-06 | Other | REPLACED O-RINGS | Steel/Wrought Iron |  | Sacramento | Replaced O-rings in caps; replaced O-rings in caps and soap tested for leaks. No more leaks
| 10-92169-1 | DFM |  | 16 | Transmission |  | Valves |  |  | Other | Stem seal | 2010-03-09 | 2010-05-10 | Other | REPLACE STEM SEAL | Steel/Wrought Iron |  | Sacramento | Replaced stem seal
| 10-92169- | [5 empty] | Valves |  |  |  |  | 2010-03-09 | [5 empty] | Sacramento
| 05-21065-1 |  |  | 0.5 | Transmission |  | Other |  | 1/2" Pipe threads | Other | Dry pipe dope | 2005-08-31 | 2010-12-03 | Replace Valve < 2 inch | Replaced 1/2" valve on body bleed, soaped ok | Steel/Wrought Iron |  | Folsom | D-52-E Fair Oaks & Madison, D-52-E Fair Oaks Bl & Madison Ave, same, D-52-E, Valve D-52-E in sidewalk; Replaced 1/2" valve on body bleed, soaped ok; replaced 1/2" ball valve on body bleed for valve #D52E, repair location inside valve casing
| 12-20190-1 |  |  | 0.75 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2010-04-29 | 2010-05-05 | Deactivated Entire Service |  | Steel/Wrought Iron |  | North Highlands | 104675532, 51 hook, PM#41312133, on service external corrosion, on service; Deactivated entire service
52 | 10-21392-1 | DFM |  | 4 | Transmission >= 20% SMYS |  | Other Mechanical Joint |  | MUELLER CAP | No/Deteriorated Pipe Dope |  | 2010-06-01 | 2011-01-25 | Tighten Cap/Bolt - Fitting | CAP | Steel |  | Folsom | @ V-109, NE intrsctn blue ravine&sibley, @ V-109, NE intersctn blue revine& silbe, V-109, @ V-109, V-109, NE intrsctn blue ravine & sibley; Redoped and tightened cap; Redoped & tightened mueller cap
| 10-21426-1 | DFM | [9 empty] | 2010-06-14 | [5 empty] | Sacramento | leak @ V-1, leak @ V-1, Soaped no leak found
| 10-21456-1 | DFM |  | 0.75 | Transmission |  | Other |  |  | Other |  | 2010-06-21 | 2010-06-21 | Other |  | Steel/Wrought Iron |  | Sacramento | @ hi-to-hi set in bx (press. vlv), @ hi-to-hi set in box (press. vlv); Rebuilt HPR type Reg & Reset relief
| 10-21586-1 | DFM |  | 6 | Transmission |  | Fitting |  |  | Other | Redoped Cap | 2010-07-14 | 2010-10-01 | Other | Redoped Cap | Steel/Wrought Iron |  | Galt | Galt DFM gauge tap fitting in casing by valve A-42, galt DFM gauge tap fitting in casing by, same; Redoped cap on guage tap; redoped cap - tested line pressure & soap - backfilled w/sand
52 | 10-22620-1 | 119 |  | 4 | Single Service |  | Other |  |  | Other |  | 2010-11-12 | 2011-01-18 | Tighten Cap/Bolt - Fitting |  | Steel |  | Sacramento | At Reg #300 Mooney Filter. Marked yellow Zip Tie, At reg #300 Mooney filter; Tighten reg bolts and allen bolt on filter
52 | 10-22628-1 | DREG4119 | 0.01 | 0.5 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-11-12 |  |  |  | Steel |  | Sacramento | Call city inspector # John 804-8363, at N/E corner of Truxel rd and Gateway Park Blvd Next to Chiles, Valve, @ valve V-1 on gauge tap
52 | 10-22640-B | 119 | [9 empty] | 2010-10-10 | [5 empty] | Sacramento | At valve in casing (marked with yellow X), at valve V-1
9 | 10-90292-1 | 400 |  | 0.75 | Single Service |  | Threads |  |  | Other |  | 2010-01-08 | 2010-12-02 | Tighten Cap/Bolt - Fitting |  | Steel |  | Arbuckle | PGE bx @ SE end of drive, leak found PG&E box at s/e end of drive; Tightned union; soap test o.k.
| 10-33014-1 | 210 | [9 empty] | 2010-04-07 | [5 empty] | Suisun | V-7 NE side of HWY12 (HCA), V-7 NE side of HWY12 (approx. 140'E of E, Valve removed on 4/27/10; Leak eliminated
| 10-33015-1 | 210 |  | 6 | Transmission |  | Valves |  |  | Other |  | 2010-04-07 | 2010-07-06 | Other |  | Steel/Wrought Iron |  | Suisun | V-1 (wheel vlv) NW of Intersctn. (HCA), V-1 (wheel vlv) NW of intersctn (HCA); Greased valve and partially operated; Greased and partially operated - soap tested - clear - checked with CGI wo roads
| 10-33017-1 | 210 | [9 empty] | 2010-04-09 | [5 empty] | Suisun | V-4.88 - B, North side, V-4.88 - B, N or creed rd., Downgrade to 2
| 10-33020-1 | 143 | [9 empty] | 2010-04-23 | [5 empty] | Dixon | @ V-1', @ V-1, Downgrade
| 10-33036-1 | 150 | [9 empty] | 2010-05-12 | [5 empty] | Dixon | hi-to-hi box to mtr#60759813, hi-to-hi bx to mtr#60759813
50 | 10-55124- |  |  | 2 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | Digin/Excavation | OTHER - NOT MARKED | 2010-09-03 | 2010-09-03 | Deactivate Dist Main =>1 foot | MECHANICAL REPAIR FITTING - FITTING | PE2406/2708 (Yellow) |  | Woodland | not # 105256743, at stub on the south side of Branisan, on main (stub); Shorten stub away from new joint trench (4'); contractor dug into 2" stub. Install dead end on main
| 10-35007-1 |  |  | 0.25 | Service |  | Fitting |  |  | Other | LOOSE | 2010-04-04 | 2010-06-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Woodland | Cache Creek Meter Station. Capay Valley, at gauge tap above main vlv.; Tightened 1/4'' nipple for gauge tap.; Tightened 1/4" fitting for gauge tap on inlet of meter sot.
| 10-54002-1 | 172 | [9 empty] | 2010-04-19 | [5 empty] | Williams | USA# 116984 4-30-10, Faxed 6-4-10, leak on valve 3 in driveway at address (N, No leak found, leak @ pinoff tee's to valve #2 (09-35002-1)
| 10-54002- | [10 empty] | 2010-04-19 | [5 empty] | Williams | Leak on valve 3 in O.W. of address.
| 10-54003-1 | DFM |  | 0.75 | Single Service |  | Regulator |  |  | Other | NO LOCKUP | 2010-05-30 | 2010-08-05 | Other | Replaced reg/relief | Steel/Wrought Iron |  | Colusa | Hi to hi set 25' n/road, Hi to hi set 25' n/road; Put in new 627 & H202
| 10-54004-1 | DFM | [9 empty] | 2010-06-06 | [5 empty] | Colusa | In reg st. V-6 mwyellow zip tie, in reg sta. V-6, marked with yellow pain, soap test no leaks found; No leak found @ V-6
| 10-56009- | L172 |  | 0.75 | Single Service |  | Body of Pipe |  |  |  |  | 2010-10-20 | 2010-10-22 | Replace Partial Service |  | Steel/Wrought Iron |  | Colusa | EM installed @ Pin off tee location
[5 empty] | Transmission | [10 empty] | Steel/Wrought Iron |  | Butte City | Installed E.T.S., Instaled locate ball curr main at point where wires are tied to main.
9 | 79-40018-1 | 152 |  | 6 | Gathering |  | Other |  |  | Corrosion |  | 1979-03-06 | 1979-04-16 | PATCH WELDED |  | Steel/Wrought Iron |  | Glenn Co. | Obtain measurement from odorizer station so leak and repairs can be mapped
| 03-35000-1 | 151 |  | 0.75 | Transmission |  | Other |  | Relief Valve | Construction Defect | RELIEF VALVE | 2003-05-12 | 2004-06-21 | Other | Repair relief | Steel/Wrought Iron |  | Butte City | Repaired relief;
| 92-35044-1 | [10 empty] | 1992-07-22 | 1993-01-20 |  |  |  |  | Princeton | Soapped set- Couldn't find any leaks
| 03-35002-1 |  |  | 3 | Transmission |  | Valves |  |  | Other |  | 2003-05-12 | 2004-06-14 | Other | grease valve | Steel/Wrought Iron |  | Princeton | Grease valve stoped leak
| 92-35041-1 |  |  |  | Transmission |  | Valves |  |  | Other |  | 1992-07-22 | 1993-01-26 | Other |  | Steel/Wrought Iron |  | Prinsceton | Greased and turned valve- soaped out cound't find any leaks
| 92-35043-1 |  |  | 0.25 | Transmission |  | Valves |  |  | Other |  | 1992-07-22 | 1993-01-27 | Other |  | Steel/Wrought Iron |  | Princeton | Repaired leak on d/s cap
| 03-35004-1 |  |  |  | Transmission |  | Valves |  |  | Construction Defect |  | 2003-05-15 | 2004-07-06 | Replace Main Valve < 2-inch |  | Steel/Wrought Iron |  | Alton | replaced leaking 3/4" ball valve @ fire valve to set
9 | 96-35003-1 | [10 empty] | 1996-05-28 | [5 empty] | Princeton
9 | 92-35015-1 | 400 |  | 2 | Distribution Feeder Main |  | Other |  |  | Material Failure |  | 1992-07-13 | 1993-01-25 | Other |  | Steel/Wrought Iron |  | Maxwell | Rebuilt pilot regulator diaphrams and seat
9 | 92-35016-1 |  |  | 0.75 | Distribution Feeder Main |  | Fitting |  |  | Material Failure |  | 1992-07-13 | 1993-01-25 | Other |  | Other Plastic |  | Maxwell | Repair leak on Union on HPR Reg. Set
5 | 87-00069-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1987-07-10 | 1988-02-20 | Other | Tighten inner plug and cap | Steel/Wrought Iron |  | Maxwell | repaired leak by tightening inner pin off plug and cap 2/20/88 R. Lutz.
| 03-35013-1 | [10 empty] | 2003-05-21 | [5 empty] | Maxwell
| 06-56010-1 |  |  | 0.5 | Single Service |  | Body of Pipe |  |  |  |  | 2006-10-02 | 2006-10-02 | Replace Partial Service |  | Other | TR 418 | Maxwell | Replaced 1'ft. 1/2" pipe; replace 1'Ft. 1/2 "in. PL Pipe
| 03-35012-1 |  |  | 0.75 | Single Service |  | Regulator |  |  | Equipment Malfunction |  | 2003-05-23 | 2008-10-06 | Other | REPLACED LEAKING FISHER 627 - REPAIRED LEAKS ON SCREWED | Steel/Wrought Iron |  | Maxwell | Replaced leaking fisher 627-Replaced leaks on sleeve
9 | 92-35017-1 |  |  |  | Distribution Feeder Main |  | Valves |  |  | Other |  | 1992-07-13 | 1992-11-07 | Other | GREASED & OPERATED VALVE | Steel/Wrought Iron |  | Maxwell | Greased and operated valve
9 | 87-00344-1 | [10 empty] | 1987-12-17 | [5 empty] | Maxwell | S-side 641' W/Elm st. @ Fire Valve;
9 | 77-20047-1 |  |  | 2 | Service |  | Valves |  |  | Other |  | 1977-08-08 | 1980-05-08 | Other |  | Steel/Wrought Iron |  | Maxwell | Leak on top of valve...gound
| 99-35022-1 | [10 empty] | 1999-12-08 | [5 empty] | Maxwell
9 | 92-35025-1 |  |  |  | Transmission |  | Valves |  |  | Other |  | 1992-07-16 | 1993-01-27 | Other | GREASED & TURNED V-1 COULD FIND NO LEAK  GREASED 3/4 VALVE ON BLOWDOWN STACK | Steel/Wrought Iron |  | Princeton | Greased and turned V-A could find no leaks- greased 3/4" valve on blow down stack
9 | 87-00077-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1987-07-17 | 1988-05-09 | Other | GREASED VALVE REMOVED BLOW-OFF CAP AND GREASED | Steel/Wrought Iron |  | Princeton | Grased valve remoed Blow-off cap and greased
| 98-35006-1 | [10 empty] | 1998-06-01 | [5 empty] | Alton
9 | 87-00372-1 | 167 |  | 6 | Gathering |  | Body of Pipe |  |  | CORROSION |  | 1987-11-07 | 1987-11-07 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Colusa | Replaced 3.5 ft. of 6" pipe
|  |  |  | 18 | [11 empty] | Steel
| 96-56007-1 | 172 |  | 18 | Transmission |  | Body of Pipe |  |  | DAMAGE BY OUTSIDE FORCES |  | 1996-09-28 | 1996-09-28 | REPLACE PIPE |  | Steel/Wrought Iron |  | Coulusa | Exposed and replaced 30ft of 18" pipe.
| 04-56000-1 | 172 |  | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2004-02-19 | 2004-02-20 | Patch Weld - Weld |  | Steel |  | Colusa | Welded 2" sav-a-valve over corrosion pit; Sopa test firring @ 100PSIG and NOP of 225 PSIG (no leaks)
9 | 87-00083-1 |  |  | 4 | Distribution Feeder Main |  | Regulator |  |  | Other |  | 1987-07-20 | 1988-05-13 | Other |  | Steel/Wrought Iron |  | Colusa | Rebuilt Red. Replaced; Dow...Greased to #3 ...
|  |  |  | 6 | [11 empty] | Cast Iron
9 | 88-90004-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | CORROSION |  | 1988-05-05 | 1988-05-11 | Replace Pipe |  | Steel/Wrought Iron |  | Meridian | Replaced 68ft. of 6" L-302 with 3" pipe at well 81183 See WO 48615
9 | 74-00042-1 |  |  | 2 | Distribution Main |  | OTHER |  |  | Other |  | 1974-03-26 | 1974-04-10 | Other |  | Steel/Wrought Iron |  | Williums | Repaired leak in Regulator
9 | 92-38014-1 |  |  | 2 | Transmission |  | Fitting |  |  | Other |  | 1992-07-07 | 1997-02-10 | Other |  | Steel/Wrought Iron |  | Arbuckle | In Reg. vault area rd. and lonestar, repaired leak on 2" axial relief
9 | 72-60050-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-08-10 | 1972-09-19 | PATCH WELDED |  | Steel/Wrought Iron |  | Culsa | External Corr. at a 80cc lock, welded perm patch on line 12" long.
9 | 92-35059-1 |  |  |  | Distribution Feeder Main |  | Valves |  |  | Other |  | 1992-08-05 | 1992-11-07 | Other |  | Steel/Wrought Iron |  | Colusa | Greased valve- stopped leak
9 | 89-00122-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1989-04-19 | 1989-06-26 | PATCH WELDED |  | Steel/Wrought Iron |  | Colusa | Installed 1/2" sleeve patch
9 | 80-40009-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-04-27 | 1980-04-27 | Other | SEE 4489A | Steel/Wrought Iron |  | Merdian | Instection @ point cap was installed
9 | [11 empty] | 1992-12-23
9 | 76-40057-1 | 302 |  | 1 | Transmission >= 20% SMYS |  | Drip |  |  | Damage by outside Forces |  | 1976-12-03 | 1976-12-03 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  |  | Line was blown down on 12-3-76 to elminate hazard and repairs were made next morning
9 | 76-40051-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-10-25 | 1976-10-25 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  |  | Line was shut down on 10/25/76 until permanent repairs could be made on 10-26-76
9 | 75-40086-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | CORROSION |  | 1975-06-07 | 1975-06-12 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  |  | Internal corrosion leak #8 pipe replaced on WO4761
9 | 82-00130-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | CORROSION |  | 1982-09-24 | 1982-09-27 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron
9 | 82-00131-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | CORROSION |  | 1982-09-27 | 1982-09-30 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron
9 | -35002 | [10 empty] | 1992-06-18 | [5 empty] | Meridian
|  |  |  | 4.5 | [11 empty] | Steel
9 | 86-00161-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1986-06-14 | 1986-06-16 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Sutter Co.
9 | 86-00119-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | CORROSION |  | 1986-05-27 | 1986-05-27 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  |  | Pipe is very bad condition and should be replaced
9 | 85-00197-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1985-12-03 | 1985-12-03 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | INSTALLED 4" WELD SLEEVE. WELDING BY G.C.
9 | 85-00205-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | CORROSION |  | 1985-12-03 | 1985-12-03 | WELD OVER SLEEVE OR CAN |  | Steel/Wrought Iron |  |  | 1/8" hole in bottom of pipe
9 | 86-00064-1 | 302 |  | 4 | Gathering |  | BODY OF PIPE |  |  | CORROSION |  | 1986-05-09 | 1986-05-12 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Meridian | hecked with flaine pack after repair found 0%; ;
9 | 82-00132-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | CORROSION |  | 1982-12-29 | 1982-12-29 | WELD OVER SLEEVE OR CAN | 2 SLEEVES AND 4FT OF PIPE | Steel/Wrought Iron |  | Meridian | Repaired a leak. Cut out and replaced 4' section with new pipe...main in this area is very bad and should be replaced
9 | 83-00012-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | CORROSION |  | 1983-02-14 | 1983-02-16 | REPLACE PIPE AND/OR SERVICE | GM 4332763 | Steel/Wrought Iron |  |  | Repair gas leak this location temporary patch weld, Internal corrosion leak
9 | 82-00129-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | CORROSION |  | 1982-06-18 | 1982-06-22 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  |  | Replaced 6ft. of 6" pipe to repair leak
9 | 83-00036-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | CORROSION |  | 1983-03-21 | 1983-03-22 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Meridian
9 | 77-20021-1 | [10 empty] | 1977-07-12 | [5 empty] | NeridianLeaking from HPR box
9 | 89-00145-1 | 302 | 14.61 | 24 | Gathering |  | Body of Pipe |  |  | CORROSION |  | 1989-05-02 | 1989-05-03 | REPLACE PIPE |  | Steel/Wrought Iron |  | Merdian | Cut out 2' of 4" pipe and replaced with 2' of new 4" pipe
9 | 83-00013-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | CORROSION |  | 1983-02-14 | 1983-02-15 | REPLACE PIPE AND/OR SERVICE | REPLACE 2 FT OF PIPE | Steel/Wrought Iron |  |  | Repair gas leak this location replaced 2ft of pipe
9 | 79-40037-1 | 302 |  | 6 | Transmission |  | Body of Pipe |  |  | CORROSION |  | 1979-08-02 | 1979-08-16 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Meroni and Drexcier Rd | Replaced 2' section 6" pipe with new pipe and leak was in middle of piece taken out. Both ends old pipe leaked good.
9 | 82-00041-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | CORROSION |  | 1982-06-11 | 1982-06-11 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Meridian | 400 n/o valve 59 5' replaced
9 | 88-90065-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | CORROSION |  | 1988-09-16 | 1988-09-27 | REPLACE PIPE |  | Steel/Wrought Iron |  | Meridian | Replaced 3ft of .188 ERW 6" pipe
9 | 88-90007-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | CORROSION |  | 1988-06-30 | 1988-06-30 | REPLACE PIPE |  | Steel/Wrought Iron |  | Meridian | Replaced 2ft section of 4" line FS6+03
9 | 88-90003-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | CORROSION |  | 1988-04-26 | 1988-04-26 | REPLACE PIPE |  | Steel/Wrought Iron |  | Meridian | Replaced 12" of 6" pipe
9 | 88-90001-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | CORROSION |  | 1988-03-26 | 1988-03-27 | REPLACE PIPE |  | Steel/Wrought Iron |  | Meridian | Installed 6" of pipe line, need to be replaced due to internal corrosion
9 | 83-00220-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | CORROSION | INTERNAL | 1983-12-16 | 1983-12-16 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron
9 | 83-00220-1 |  |  | 6 | Gathering |  | OTHER |  |  | CORROSION | INTERNAL | 1983-12-16 | 1983-12-16 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron
|  |  |  | 6 | Transmission |  | Body of Pipe |  |  | CORROSION | INTERNAL | 1983-12-16 | 1984-03-22 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron
9 | 83-00219-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | CORROSION | INTERNAL | 1983-12-16 | 1983-12-16 | CLAMP | REPLACE PIPE AND/OR SERVICE | Steel/Wrought Iron
9 | 83-00219-1 |  |  | 6 | Gathering |  | OTHER |  |  | CORROSION | INTERNAL | 1983-12-16 | 1983-12-16 | Clamp |  | Steel/Wrought Iron
|  | 172 |  | 18 | [11 empty] | Steel
|  | 172 |  | 18 | [11 empty] | Steel
9 | 81-00204-1 | 174 |  | 6 | Gathering |  | Body of Pipe |  |  | CORROSION | INTERNAL | 1981-03-12 | 1981-04-15 | REPLACE PIPE AND/OR SERVICE | WO 41827 | Steel/Wrought Iron |  | Arbuckle
9 | 78-40053-1 | 174 |  | 6 | Gathering |  | Body of Pipe |  |  | CORROSION | INTERNAL | 1978-10-30 | 1978-11-16 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron
9 | 75-60048-1 | 174 |  | 6 | Gathering |  | Body of Pipe |  | INTERNAL | CORROSION |  | 1975-08-23 | 1975-09-02 | PATCH WELDED |  | Steel/Wrought Iron |  | Colusa Co | No gas leak
9 | 75-60048-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | CORROSION |  | 1975-08-23 | 1975-09-02 | PATCH WELDED |  | Steel/Wrought Iron |  | Colsua Co. | Internal corrosion
9 | 83-00006-1 | 174 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1983-01-04 | 1983-01-13 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Arbuckle
9 | 73-70075-1 |  |  | 2 | Gathering |  | Other |  |  | Corrosion |  | 1973-10-20 | 1973-10-24 | Clamp |  | Steel/Wrought Iron |  | Arbuckle | Leak in 1" gathering line 100 years n/o wiggins no. 3., no leakage on PG & E line belonging to gulf oil co. Gulf oil co. to make repairs
9 | 83-00105-1 |  |  | 0.75 | Gathering |  | Valves |  | 3/4 VALVE ON DRIP REG. | Other |  | 1983-07-22 | 1984-06-01 | Other |  | Steel/Wrought Iron |  | Arbuckle | Crew was called out 6/1/84 10:00Am F.Y. Grased valve @ Drip ... leak
9 | 83-00106-1 | 174 |  | 6 | Gathering |  | Other |  |  | Other |  | 1983-07-22 | 1984-05-23 | Other | ABANDONED PIPE ON WO43549 | Steel/Wrought Iron |  | Arbuckle
| 05-56008- |  |  | 0.75 | Service |  | Valves |  |  | Digin |  | 2005-07-28 | 2005-07-28 | Service Partially Replaced |  | Steel/Wrought Iron |  | Arbuckle | Replace 6" of 3/4" Stl
| 97-35012-1 | [10 empty] | 1997-12-29 | [5 empty] | Williamss
9 | 97-35012-1 | [10 empty] | 1997-12-29 | [5 empty] | Arbuckle
9 | 87-00376-1 |  |  | 12 | Gathering |  | Body of Pipe |  |  | CORROSION | INTERNAL | 1987-10-15 | 1987-10-15 | REPLACE PIPE |  | Steel/Wrought Iron |  | Grimes | Replaced pipe on GM4659017
9 | 87-00376-1 | 302 |  | 12 | Gathering |  | Body of Pipe |  |  | CORROSION | INTERNAL | 1987-10-15 | 1987-10-15 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Grimes | 12" L-302 w/V-96 E/DR4 slough; Plat L-302-20
9 | 85-00022-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | CORROSION | INTERNAL | 1985-01-30 | 1985-01-30 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Sutter Co. | ; ; ;
9 | 87-00335-1 | 302 |  | 8 | Gathering |  | Valves |  |  | Other |  | 1987-12-07 | 1988-04-18 | Other |  | Steel/Wrought Iron |  | Grimes | 8" L-302 abandoned and 8" valve removed on GM4659090
9 | 87-00335-1 | 302 | [9 empty] | 1987-12-07 | [5 empty] | Grimes | 4/15/88 valve was removed pipe line abandened
9 | 85-00164-1 |  |  | 2 | Transmission |  | Valves |  |  | Other |  | 1985-10-24 | 1985-10-28 | Other |  | Steel/Wrought Iron |  | Grimes | Greased valve
9 | 86-00390-1 |  |  |  | Transmission | [6 empty] | 1986-11-10 | [5 empty] | Grimes | ... Thi smain has been cut off
9 | 83-00221-1 | 302 |  | 6 | Gathering |  | Other |  |  | CORROSION | INTERNAL | 1983-12-14 | 1983-12-15 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Grimes
9 | 85-00204-1 | 302 |  | 2 | Gathering |  | Fitting |  |  | Other |  | 1985-12-23 | 1986-01-03 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  |  | Replaced tee with 2" pipe and valve
9 | 86-00001-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | CORROSION | INTERNAL | 1986-01-06 | 1986-01-06 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  |  | Pipe is in very bad shape 05 farback inside... we can see approx. 16' suggest that this pipe be replaced
| 08-30203-1 | 302-040 | 0.54 | 12 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-07-02 | 2008-07-16 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | Meridian | Install 70" can with Sav-A-Valve; X-ray install 70" can with Sav-A-Valve, pre tested emergency pipe
9 | 85-00047-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | CORROSION | INTERNAL | 1985-03-19 | 1985-03-20 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Sutter Co.
9 | 84-00068-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | CORROSION | INTERNAL | 1984-05-27 | 1984-05-29 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Sutter Co. | 1 bad pit in pipe
9 | 86-00218-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | CORROSION | INTERNAL | 1986-08-07 | 1986-08-07 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Sutter Co.
|  |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1986-08-07 |  | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron
9 | 78-40064-1 | 302-040 |  | 20 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-09-28 | 1978-09-28 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron
9 | 88-90006-1 |  |  | 2 | Gathering |  | Body of Pipe |  |  | CORROSION | INTERNAL | 1988-05-29 | 1988-06-02 | REPLACE PIPE |  | Steel/Wrought Iron |  | Arbuckle | abandonen white rd. drip and installed new section of line
9 | 86-00118-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | CORROSION | INTERNAL | 1986-05-27 | 1986-05-28 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Arbuckle | Repaired with 4" pretested 8" pipe
9 | 71-00042-1 | 302-040 |  | 6 | Gathering |  | Body of Pipe |  |  | CORROSION |  | 1971-09-03 | 1971-09-30 | PATCH WELDED |  | Steel/Wrought Iron |  | Arbuckle
| 05-56004- | 20-172 |  | 0.75 | Service |  | Fitting |  |  | Digin |  | 2005-05-27 | 2005-05-27 | Replace Main Valve >= 2-inch |  | Steel/Wrought Iron |  | Dunnigan | Removed 1/4" metric valve w/ 3/4" inline shut off valve; Did not remove wrap on L-172. Removed wrap from 1" Serv. Tap and 3/4" Stl. Serv.
9 |  |  |  | 0.75 | Distribution Main |  | Physical/Mechanical Joint |  |  | Other |  | 1992-06-30 | 1996-12-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Dunnigan | All 3 STGS of HPR farm tap, rebuilts 3 regs and re-doped and installed all screw joints on all 3 stages of regulation
9 | 86-00422-1 | 302 |  | 0.75 | Transmission |  | Other |  |  | Other |  | 1986-11-07 | 1986-11-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Dunnigan | Removed, doped pin-off tee cap and reinstalled. Tightened packing nut on metric valve. First Stage Reg.
9 | 86-00423-1 | 302 |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1986-11-07 | 1986-11-20 | Other |  | Steel/Wrought Iron |  | Dunnigan | Lube bypass valve stopped leak on third stage rrg.;
9 | 87-00337-1 |  |  |  | Transmission | [6 empty] | 1987-12-08 | [5 empty] | Dunnigan
|  | 302 |  |  | Transmission | [6 empty] | 2008-06-18 |  |  |  | Steel/Wrought Iron
9 | 85-00163-1 | 302 |  | 0.75 | Transmission |  | Fitting |  |  | Other |  | 1985-10-24 | 1985-10-28 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Dunnigan | Found union leaking
9 | 77-60001-1 | 302 |  | 12 | Transmission |  | Valves |  |  | Other |  | 1977-01-03 | 1978-04-21 | Other | GM 187674 | Steel/Wrought Iron |  | Dunnigan | ; ; ; ;
|  |  |  | 0.75 | Service | [6 empty] | 2001-06-06 |  |  |  | Steel/Wrought Iron |  | Duniigan | Installed valve frame and cover
9 | 71-00086- | 174 |  | 6 | Transmission |  | Valves |  |  | Other |  | 1971-08-31 | 1972-05-31 | Other |  | Steel/Wrought Iron |  | Arbuckle | Valve greased to stop leak
9 | 71-00076-1 | [10 empty] | 1971-03-31
9 | 71-00088-1 | 174 |  | 6 | Transmission |  | Valves |  |  | Other |  | 1971-08-31 | 1972-05-31 | Other |  | Steel/Wrought Iron |  | Arbuckle | Valve greased to stop leak
9 | 71-00088-1 | [10 empty] | 1971-03-31
9 | 89-00141-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1989-06-15 | 1989-06-16 | REPLACE PIPE |  | Steel/Wrought Iron |  | Arbuckle | Removed 38" and replaced with new pipe
9 | 87-00037-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | CORROSION | INTERNAL | 1987-04-03 | 1987-04-03 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  |  | Replaced 3' of pipe with 6 5/8" ...V-188 X42 ERW pipe
| 96-56005-1 | 172 |  | 20 | Transmission |  | Other |  |  | Digin |  | 1996-07-22 | 1996-07-23 | REPLACE PIPE |  | Steel/Wrought Iron |  | Dunnigan | Replaved 20' of 20" main .350 w/ Emergency stock team sacto florin...
| 04-35007- | [16 empty] | Arbuckle
| 02-35001-1 |  |  | 6 | Transmission |  | Fitting |  |  | Other | NEEDED GREASE | 2002-04-08 | 2003-08-23 | Other | Grease valve | Steel/Wrought Iron |  | Arbuckle | Grease valve
| 83-35044-1 | [10 empty] | 2003-10-18 | [5 empty] | Yolo
| 86-85003-1 |  |  | 0.75 | Gathering |  | OTHER |  | NONE | OTHER | NONE | 1986-04-08 |  | OTHER | NONE | Steel/Wrought Iron |  | Woodland | Leak survyed gas service and found 50PPM behind sidewalk. ...
50 | 93-55015-1 |  |  | 2 | Transmission |  | Fitting |  |  | Damage by outside Forces |  | 1993-04-09 | 1993-04-09 | Other |  | Steel/Wrought Iron |  | Woodland | Shut down broken metric nipple on high side of Reg. and helped M s/c install new metric and nipple ... and cover self
|  | 220 |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Woodland | Stand-by to install ETS leaks on L-220 8"
| 99-35004-1 |  |  | 0 | Transmission |  | Fitting |  | PHYSICAL/MECHANICAL JOINT, REGULATOR | Unknown |  | 1999-03-03 | 2000-07-15 | Mechanical Repair Fitting - Fitting | SOAP AND/OR TAPE |  |  | Woodland | Found and repaired severl leaks on equipment
50 | 82-85016-1 |  |  | 0.5 | Distribution Feeder Main |  | Tap Connection |  |  | Other |  | 1982-09-23 | 1982-12-28 | Other | REMOVED CAP, REDOPED THREADS, RETIGHTENED CAP. | Steel/Wrought Iron |  | Woodland | Found very small leak. Cap of tap connection ... Chart line. ...
50 | 72-35009-1 |  |  |  | Distribution Feeder Main |  | Valves |  |  |  |  | 1972-08-01 | 1972-12-10 | Other |  | Steel/Wrought Iron |  | Woodland
50 |  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1974-04-29
| 86-35009-1 | [10 empty] | 1986-03-11 | [5 empty] | Woodland | This is a pit refer to regulation
| 86-35022-1 | [10 empty] | 1986-03-12 | [5 empty] | Woodland | Both Reg pits leaking
50 | 95-35017-1 |  |  | 2 | Distribution Main |  | Physical/Mechanical Joint |  |  | Other |  | 1995-03-14 | 1996-05-07 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Woodland | Found leak on Flange and on pilots
50 | 72-35010-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1972-08-01 | 1972-12-11 | OTHER |  | Steel/Wrought Iron |  | Woodland | See: Gibson Rd. Reg. Pit Dwg. M2460-I2, Leak repaired in primary pit @ Valve #1
| 99-35003- | [10 empty] | 1999-03-03 | [5 empty] | Woodland
50 | 95-35069-1 |  |  | 2 | Transmission |  | Valves |  |  | Other |  | 1995-05-02 | 1998-04-02 | Other |  | Steel/Wrought Iron |  | Woodland | Replaced missing 1/4" plug in fitting gauge valve- greased and turned both valve on w/s 101
50 | 95-35069-1 | [10 empty] | 1998-05-02 | [5 empty] | Woodland | Tony acorp was sent T & R at... leak center 3/31
50 | 82-85000-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1982-02-05 | 1982-02-16 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  |  | GC shut down main and replaced 2' of 4" main
50 | 78-15008-1 |  |  | 4 | Transmission |  |  |  |  | Other | Found no leak or Indication | 1978-06-28 |  |  |  | Steel/Wrought Iron |  | Davis
50 | 95-35070-1 | [10 empty] | 1995-05-03 | [5 empty] | Davis
| 98-85006-1 |  | 65.31 | [8 empty] | 1998-08-01 | [5 empty] | Woodland
50 | 96-35042-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Material Failure |  | 1996-03-20 | 1996-11-13 | Other |  | Steel/Wrought Iron |  | Davis | Greased...valve
50 | 50-35945-1 | [10 empty] | 1990-03-22 | [5 empty] | Winters
50 | 98-85005-1 | [10 empty] | 1998-03-26 | [5 empty] | Yolo
50 | 96-35019-1 |  |  | 1 | Service |  | Valves |  |  | Other |  | 1996-02-15 | 1996-11-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Winters | Repaired leaks on V.T. caps and threads on both regs and mon. m. s. run
| 93-15025-1 | [10 empty] | 1993-03-24 | [5 empty] | Yolo
50 | 93-15025-1 | [10 empty] | 1993-03-24 | [5 empty] | Yolo
|  |  |  | 4 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party |  | 2007-11-25 | 2007-11-06 | REPLACE TP MAIN |  | Steel/Wrought Iron |  | West Sacramento | Replaced
|  |  |  | 4 | Distribution Main | [6 empty] | 2007-11-05 | 2007-11-06 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | West Sacramento | Cut in 4" can. Installed bypass and r' 4" line stoppers
50 | 91-55005-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1991-03-07 | 1991-03-07 | Replace Pipe |  | Steel/Wrought Iron |  | Davis | Shut down ... and installed 18" of new 3/4" stl pipe
50 | 91-55031-1 |  |  | 0.75 | Service |  | Valves |  |  | Other | VALVE | 1991-11-16 |  | Other | Greased valve | Steel/Wrought Iron |  | Woodland | Valve between main and dist. reg. sets, greased valve
50 | 72-35009-3 | [5 empty] | Valves |  |  |  |  | 1972-08-01 | 1972-12-10 | Other
50 | 72-35009-2 | [5 empty] | Valves |  |  |  |  | 1972-08-01 | 1972-12-10 | Other
50 | 75-35108-1 |  |  |  | Gathering |  | Regulator |  |  | Material Failure |  | 1975-09-22 | 1976-01-22 | Other |  | Other |  | Winters | Pin at reg. was leaking
50 | 75-15069-1 |  |  | 4 | Distribution Feeder Main | [6 empty] | 1975-07-15 |  |  |  | Steel/Wrought Iron |  | Davis | No leak found. Stripped 10' of pipe and rewrapped. Tested soil each way in hole w/comb. Gas Ind. and readings were zero.; On 12-16-7 The flamg ionization valt from sacto survevered the line from fairfield kwells tap to a point at 1000 ft. east and found only one indication as noted on attached sketch. G.C. excavated and found no leakage on 12-29-95 at this location. M. Ames Checked on 12-8-75 with probe holes and gas indicator and found no indication.
50 | 76-35021-1 |  |  | 4 | Distribution Feeder Main | [6 empty] | 1976-08-16 |  |  |  | Steel/Wrought Iron |  | Davis | 1-7-77 Check with flang ionization unit borrowed from Sacto. no indication of leakage; Bar tested over line 127 at location. Indicated above 10% level in ...
|  |  |  | 8 | Transmission |  | OTHER |  |  | OTHER |  |  |  | OTHER |  | Steel |  | Citrus Heights
|  |  |  | 8 | Transmission |  | OTHER |  |  | OTHER |  |  |  | OTHER |  | Steel/Wrought Iron |  | Citrus Heights
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | citrus heights
|  |  |  | 6.62 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Sacramento
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1974-08-26 |  |  |  | Steel/Wrought Iron
52 |  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1974-08-26 |  |  |  | Steel/Wrought Iron
52 | 82--1 |  |  | 6 | Distribution Feeder Main |  | Valves |  | WOULD NOT TURN |  | Not leaking | 1982-07-01 | 1982-07-12 | Other |  | Steel/Wrought Iron |  | Sacramento | Greased valve valve 4
|  |  |  | 12.75 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Foot Hill
52 |  |  |  | 12 | Transmission |  |  |  | NONE |  | NONE | 1972-05-11 | 1972-05-11 |  | NONE | Steel/Wrought Iron |  | Sacramento | Rewrapped main
| 02-20185- | [11 empty] | 2002-09-10 | OTHER | GREASE |  |  | Citrus Heights | Greased valve leak stopped 0%
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | Sacramento
52 | 85-40044-1 |  |  | 0.75 | Transmission |  | Regulator |  |  | Damage by Electrical Defect |  | 1985-04-03 | 1985-04-03 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Sacramento | Repaired Regulator
52 | 90-40084-1 |  |  | 0.75 | Transmission |  | Other Welds |  |  | Construction Defect |  | 1990-05-18 | 1990-05-15 | Other |  | Steel/Wrought Iron |  | N. Highlands | Cut out and welded and rewelded 3/4" Stl. Serv.. Added 3"-3/4" stl. pipe to replace cut out weld
52 |  |  |  | 6 | Transmission | [6 empty] | 1972-02-10 |  |  |  | Steel/Wrought Iron
52 |  |  |  | 12 | Transmission | [6 empty] | 1972-02-10 |  |  |  | Steel/Wrought Iron
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Installed 2" plastic main
| 07-20308-1 | 119 |  | 0.75 | Transmission |  | Fitting |  | VALVE | Material Failure | Unknown | 2007-10-31 | 2008-03-05 | Deactivated Partial Service | Other | Steel/Wrought Iron |  | Sacramento | Soap Tested c/o; Cut 3/4" line off 16" main
| 07-20308-1 | 119 |  | 0.75 | Transmission |  | Fitting |  |  | Material Failure |  | 2007-10-31 | 2008-03-05 | Deactivated Entire Service |  | Steel/Wrought Iron |  | Sacramento
52 |  |  |  | 6 | Transmission | [6 empty] | 1972-03-07 |  |  |  | Steel/Wrought Iron
52 |  |  |  | 6 | Distribution Main | [6 empty] | 1970-12-10 |  |  |  | Steel |  | Sacramento
52 |  |  |  | 6 | Transmission | [6 empty] | 1972-07-05 |  |  |  | Steel/Wrought Iron |  | North Nile
| 03-21067-1 | [10 empty] | 2003-06-24 | [5 empty] | Antelope
20 | 84-223-1 |  |  | 6 | Distribution Main |  | Valves |  |  | Other |  | 1984-10-09 | 1984-10-17 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Citrus Heights | Ref. W.O. 43702-1224-9
20 | 83-161-1 |  |  |  | Distribution Feeder Main | [6 empty] | 1983-10-25 | [5 empty] | Citrus Heights | Area clear; Bar tested mains found no leak with gas soap... had f/Survey re check found no leakage 6-12-84
52 |  |  |  | 6 | Transmission | [6 empty] | 1972-04-21 |  |  |  | Steel/Wrought Iron |  | North highlands | 6" 150 16 line main inspection hole
52 |  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1972-05-24 |  |  |  | Steel/Wrought Iron |  | Rio Linda
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | Roseville
52 |  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1972-12-22 |  |  |  | Steel/Wrought Iron
52 |  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1981-04-08 |  |  |  | Steel/Wrought Iron |  | Rio Vista
52 |  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1972-07-06 |  |  |  | Steel/Wrought Iron |  | Sacramento
52 |  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1980-05-07 |  |  |  | Steel/Wrought Iron |  | Sacramento | Exposed to Inst. New Svs.
52 | 80-60315-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-08-01 | 1980-08-01 | REPLACE PIPE AND/OR SERVICE |  | Other Plastic |  | Sacramento | Backhoe case, operated by owner Ray Henerson Traching for electrical conduit hit 1" PL. Gas Serv. 1" plastic serv. 12" deep.
|  |  |  | 8 | [8 empty] | 1997-09-13 |  |  | Steel |  | Sacramento | Inst. 1-32" Mag. Anode
52 |  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1981-04-09 |  |  |  | Steel/Wrought Iron |  | Sacramento
52 |  |  |  | 10 | [7 empty] | 1986-02-21 | 1986-02-21 |  |  | Steel/Wrought Iron
|  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel |  | Sacramento | Installed ETS on feeder main
52 |  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1986-02-25 |  |  |  | Steel/Wrought Iron |  |  | Exposed to check wall thichness on both main at tee
52 |  |  |  | 10 | Distribution Feeder Main | [6 empty] | 1974-03-19 |  |  |  | Steel/Wrought Iron |  | Sacramento
52 |  |  |  | 8 | [11 empty] | Steel |  | Sacramento
52 |  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1986-02-24 |  |  |  | Steel/Wrought Iron
52 |  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1986-02-24 |  |  |  | Steel/Wrought Iron
52 | 79-20640-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Material Failure |  | 1979-05-23 | 1980-07-17 | Other |  | Steel/Wrought Iron |  | Sacramento | Had to redope and retighten 2" PCF cap to stop leak...
52 | 79-20639-1 | [10 empty] | 1979-05-23 | [5 empty] | Sacramento
|  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
52 |  |  |  | 8 | [7 empty] | 1991-03-25 |  |  |  | Steel |  | Sacramento | TBM 338 B4
|  |  |  | 8 | [11 empty] | Steel |  |  | I used the old valve frame and cover that thots over the old service for a new RTS station
52 |  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1993-09-16 |  |  |  | Steel/Wrought Iron |  |  | Wrap on pipe is in excellent condition did not expose any steel
| 03-21085-1 | [10 empty] | 2003-07-24 | [5 empty] | Sacramento
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1989-08-14 |  |  |  | Steel |  |  | Installed a 4" DFM valve on feeder main 8-14-89
|  |  |  | 8 | [11 empty] | Steel |  |  | Exposed main to turn main valve
|  |  |  | 04.00 to 12.00 | [11 empty] | Steel |  |  | Replaced broken 4" H.P. gate valve
52 |  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1984-06-20 |  |  |  | Steel/Wrought Iron |  | Sacramento
52 | 79-20512-1 | [10 empty] | 1979-04-04 | [5 empty] | Sacramento
52 |  |  |  | 4 | [7 empty] | 1989-05-25 |  |  |  | Steel |  | Sacramento
52 | 89-40060-1 |  |  | 6 | Distribution Feeder Main |  | Fitting |  |  | Damage by outside Forces |  | 1989-03-24 | 1989-03-24 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Sacramento | Installed weld can over valve for old gas svr.
52 | 90-60175-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1990-06-12 | 1990-06-12 | PATCH WELDED |  | Steel |  | Sacramento | welded three (3) patches on scraped 16"Trans Main- no leaks
52 |  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1986-03-21 | 1986-03-21 |  |  | Steel/Wrought Iron |  | Sacramento
52 |  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Sacramento
52 |  |  |  | 12.00 & 06.00 | Gathering | [6 empty] | 1986-02-21 | 1986-02-21 |  |  | Steel/Wrought Iron |  |  | Exposed both main for thickness of wall size
52 | [15 empty] | Steel |  | Sacramento
52 |  |  |  | 6 | [11 empty] | Steel |  | Sacramento
|  |  |  | 2 | [8 empty] | 1990-08-09 |  |  | Steel |  |  | W.O. 40085-C
|  |  |  | 6 | [11 empty] | Steel |  |  | Installed M.P. Pin off svc Tee
52 |  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1987-03-09 | 1987-03-09 |  |  | Steel |  | Sacramento | Exposed to c/o 3/4 Hi ti Hi Svs
52 |  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Sacramento | Exposed tp c/o 3/4 Hi to Hi svs
52 |  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1971-12-23 |  |  |  | Steel/Wrought Iron |  | Sacramento | 800' W/of leidesdorff Street. Pipe is suspeneded on bridge crossing by steel pipe hangers
52 |  |  |  | 16 | Distribution Feeder Main | [7 empty] | 1986-03-28 |  |  | Steel/Wrought Iron
52 | 98-20323-1 | [10 empty] | 1998-05-15
52 | 91-60526-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1991-11-25 | 1991-11-25 | PATCH WELDED |  | Steel/Wrought Iron |  | Elf Grove | Installed 8" half sole 24" long repaired gauge 8" feeder
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
52 | 76-00051-1 | [10 empty] | 1976-06-10 | [5 empty] | Sacramento | .03% in valve; neg.; Area 34 next scheduled routine 5-year leak survey 1979
|  |  |  | 4.5 | Transmission | [6 empty] | 1986-10-16 |  |  |  | Steel/Wrought Iron
|  |  |  | 6.62 | Distribution Feeder Main | [6 empty] | 1986-10-16 |  |  |  | Steel/Wrought Iron
52 | 88-20014-1 | 108 | [9 empty] | 1988-01-22
52 | 78-20735-1 | [10 empty] | 1978-05-05 | [5 empty] | Elk Grove | 650 PPM in gas valve; Sche'd for survey 1979
52 | 76-00052-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-06-14 | 1977-04-19 | PATCH WELDED |  | Steel/Wrought Iron |  | Elk Grove | Pithole at 6 O'Clock. Arc welded 8" x 8" patch over corrosion on 4" -150lb feeder main here.
52 | 81-20119-1 | [10 empty] | 1981-06-03 | [5 empty] | Elk Grove | Valve A-16 1000PPM; From old leak #7820735
52 | 74-60111-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Construction Defect |  | 1974-04-19 | 1974-04-22 | Other |  | Steel/Wrought Iron |  |  | Plug on 4" P.C.F. leaking, redoped and retightened packing stopping leak.
|  | 334 |  | 4 | [11 empty] | Steel |  |  | Cut-in 4'' tee & installed #32 anode
|  | 334 & 108 |  | 4 | [11 empty] | Steel |  |  | cap & sav-or-valve plus #32 anode installed
52 | 88-20192-1 | [10 empty] | 1988-11-08 | [5 empty] | Sacramento
52 | 88-20193-1 | [10 empty] | 1988-11-08 | [5 empty] | Sacramento
|  | 108 |  | 16 | [7 empty] | 1991-08-21 |  |  |  | Steel |  |  | GM 4856571, 357-C5, 26, GM 4856571, Line 108
|  |  |  | 4 | [7 empty] | 1997-04-23 |  |  |  | Steel
|  |  |  | 4 | [7 empty] | 1997-04-23 |  |  |  | Steel
[16 empty] | Steel |  | Elk Grove | Installed E.T.S. in a stub marker in the faucet line
52 | 97-60081-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1997-05-17 | 1997-05-17 | Replace Pipe |  | Steel/Wrought Iron |  | Elk Grove | Replaced 5' of 4" .237 wt. pipe. Installed one 2" sav a valve & one 1" sav a valve
52 | 98-20366-1 |  |  | 8 | Transmission |  | Valves |  |  | CONSTRUCTION DEFECT |  | 1998-04-16 | 1998-06-15 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Elk Grove | Repaired leak on valve stem value (3/4") leak at 4' deep; did not dig down to main.
52 | 99-20248-1 |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | CONSTRUCTION DEFECT |  | 1994-04-26 | 2000-11-14 | Replace Pipe |  | Steel |  | Sacramento | (720-7152) Gateway leaks George Karkazis; W/O RR, S/O Elliot Ranch, Rd., flame-out, odor in air, same as above
| 99-20248-1 |  |  | 6 | [7 empty] | 1999-03-16 |  |  |  | Steel/Wrought Iron |  | Elk Grove | Franklin Rd. S/of Elliott Ranch Rd., In pit @ W/side of Franklin Rd S/of Elli, In pit @ W/side of Franklin Rd S/of Elli, w/o RR, s/o Elliott Ranch
48 | 72-13002-1 |  |  | 6 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1972-04-14 | 1972-11-21 | Other |  | Steel/Wrought Iron |  | Dixon | Leak on N/S 'A' St. 15' E/O mail box 713 marked yellow X
48 | 72-33000-1 |  |  | 6 | Distribution Feeder Main |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1972-08-14 | 1972-11-22 | Other |  | Steel/Wrought Iron |  | Dixon | Substructure on north edge of road 50 yds east of Doyle ln.
48 | 74-33064-1 |  |  | 0.75 | Distribution Feeder Main |  | Physical/Mechanical Joint |  |  | Other |  | 1974-05-07 | 1974-05-09 | Other |  | Steel/Wrought Iron |  | Dixon | Downgrade from 1; Leaking below service cock. Rethreaded pipe - installed new service cock.
48 | 75-53034-1 |  |  | 0.75 | Distribution Feeder Main |  | Valves |  |  | Damage by outside Forces |  | 1975-06-23 | 1975-06-23 | Other |  | Steel/Wrought Iron |  | Dixon | Farmer working near drip riser in concrete box ran over box and knock riser valve off replaced riser valve box will be replaced. First installation of blow-off see wo.4354-F'49
48 | 76-33025-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-06-25 | 1976-10-29 | Patch Welded |  | Steel/Wrought Iron |  | Dixon | Weld 4"x5" patch ... c/o leak. Installing 32# ... anode
48 | 77-53054-1 |  |  | 6 | Distribution Feeder Main |  | Fitting |  |  | Damage by outside Forces |  | 1977-08-27 | 1977-08-27 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Dixon | Dummy 12-13-77; Pipe to be wrapped on 8-29-77 w/ inspection report
48 | 79-33067-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1979-07-23 | 1982-02-04 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Dixon | Deleted; Checked area received, LeL reading but it would air out immediately, we also exposed high pressure riser and low pressure riser neg leaks - it is apperant that it was only a gas pocket. Required leaks on H.P.R leak somewhere on service. Could not find.
48 | 79-33061-1 | [10 empty] | 1979-07-23 | [5 empty] | Dixon | Deleted; Please delete "0" readings
48 | 79-33062-1 |  |  | 0.75 | Distribution |  | Other |  |  | Material Failure |  | 1979-07-23 | 1979-12-05 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Dixon | Bob Conrad gave me this leak 2-22-80 to report to computer. Leak is HP. Reg. in box. Repaired HPR - tighten fig's & placed back in service.
48 | 79-33063-1 |  |  | 0.34 | Service |  | Physical/Mechanical Joint |  |  | Corrosion |  | 1979-07-23 | 1980-07-30 | Other |  | Steel/Wrought Iron |  | Dixon | LEAK ON RING. LEAK ON ELBOW.
48 | 79-33064-1 |  |  | 0.75 | Service |  | Fitting |  |  | Corrosion |  | 1979-07-23 | 1982-01-28 | Other |  | Steel/Wrought Iron |  | Dixon | Dummy 10-28-81; Overhauled first stage reg replaced second stage relief with H-202 fisher relief
48 | 79-33065-1 |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1979-07-23 | 1979-11-15 | Other |  | Steel/Wrought Iron |  | Dixon | Line use: regulation; broke down set & repaired all leaks in fittings, leak in H.P. box, leak is on handle of metric and on 3/4" elbow
48 | 79-33066-1 | [10 empty] | 1979-07-23 | [5 empty] | Dixon | Deleted; Regulator making noise, Delete "0" readings
48 | 79-33068-1 | [10 empty] | 1979-07-23 | [5 empty] | Dixon | Deleted
48 | 82-33032-1 |  |  | 0.25 | Distribution Feeder Main |  | Other |  |  | Other |  | 1982-05-03 | 1984-06-20 | Other |  | Steel/Wrought Iron |  | Dixon | Delete computer will not accept 16 noted 8/24/84; repaired leak on metric ....
48 | 82-33033-1 |  |  | 0.75 | Distribution Feeder Main |  | Regulator |  |  | Material Failure |  | 1982-05-03 | 1983-01-21 | Other |  | Steel/Wrought Iron |  | Dixon | Replaced regulator
48 | 82-33034-1 |  |  | 0.75 | Distribution Feeder Main |  | Regulator |  |  | Material Failure |  | 1982-05-03 | 1983-01-21 | Other |  | Steel/Wrought Iron |  | Dixon | Replaced regulator
48 | 82-33036-1 |  |  | 0.75 | Service |  | Fitting |  |  | Corrosion |  | 1982-05-03 | 1984-05-03 | Other |  | Steel/Wrought Iron |  | Dixon | Redoped threads refitting installed relief valve tester 202 repaired leaks. Soap tested. Put ... back into ...
48 | 83-33002-1 | [10 empty] | 1983-04-28 | [5 empty] | Dixon | Delete "0" read
48 | 83-33003-1 | [10 empty] | 1983-04-28 | [5 empty] | Dixon | Delete no reading
48 | 83-33004-1 | [10 empty] | 1983-04-28 | [5 empty] | Dixon | Deleted
48 | 83-33005-1 | [10 empty] | 1983-05-02 | [5 empty] | Dixon | Deleted
48 | 83-33006-1 | [10 empty] | 1983-05-02 | [5 empty] | Dixon | Deleted
48 | 83-33007-1 | [10 empty] | 1983-05-02 | [5 empty] | Dixon | Delete; Delete no reading
48 | 83-33008-1 | [10 empty] | 1983-05-02 | [5 empty] | Dixon | Delete; Delete no reading
48 | 83-33016-1 | [10 empty] | 1983-05-05 | [5 empty] | Fair. | Deleted; soap tested all hpr's and fittings throughly could not find any leaks, Primer delete "0" readings.
48 | 84-33000-1 | [10 empty] | 1984-04-05 | [5 empty] | Dixon | Delete; Delete No reading
48 | 84-33001-1 | [10 empty] | 1984-04-05 | [5 empty] | Dixon | Delete; delete no reading
48 | 84-33002-1 | [10 empty] | 1984-04-05 | [5 empty] | Dixon | Delete; Delete no reading
48 | 80-33016-1 |  |  | 0.75 | Service |  | Physical/Mechanical Joint |  |  | Corrosion |  | 1980-07-14 | 1980-07-30 | Other |  | Steel/Wrought Iron |  | Dixon | Remove fitting & dope. Retighten fitting's soap tested ok
| 75-33044-1 | [10 empty] | 1975-09-26 | [5 empty] | Dixon | Deleted; area survey didn't find leak. Deleted 12-4-78; 7-14-77 leak surveyed area did not find leak. 1977 annual survey see reports
48 | 78-33040-1 | [10 empty] | 1978-09-01 | [5 empty] | Dixon | Deleted
48 | 79-33060-1 | [10 empty] | 1979-07-19 | [5 empty] | Dixon | Deleted; Delete "0" readings
48 | 84-53024-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1984-11-05 | 1984-11-05 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Dixon | Service HPT by ditch grader installed neon socket weld ecc and 2 ft. new, pre-tested, SO 6715-H 3/4" SML's pipe
48 | 84-80009-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1984-05-03 | 1984-05-03 | Other |  | Steel/Wrought Iron |  | Dixon | Bob scaned out to pass for repair, return when repaired, refer to MFC leak on HPR., Repacked leaking valve, repaired leaking nipples, & removed stem relief
48 | 85-33000-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1985-05-09 | 1985-09-11 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Dixon | Replaced ser.
48 | 85-33014-1 | [10 empty] | 1985-06-11 | [6 empty] | By 1/3/90
48 | 85-33015-1 | [10 empty] | 1985-06-11
48 | 85-53009-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | DAMAGE BY OUTSIDE FORCES |  | 1985-06-11 | 1985-06-13 | REPLACE PIPE AND/OR SERVICE |  | Aldyl A (Tan or Gray) |  | Dixon | Repair broken 1/2" PL service, broken service was capped 6-11-85, permanant repairs made 6-13-85, inst 2 perfection leakings and 1' piece of 1/2" plastic pipe
48 | 86-33002-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1986-05-05 | 1987-07-09 | OTHER |  | Steel/Wrought Iron |  | Dixon | Replaced nipple on Hi to Hi
48 | 86-33003-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1986-05-05 | 1987-02-11 | Other |  | Other |  | Dixon | Replaced diaphragm in leaking regs & repaired leaking nipples.
48 | 86-33004-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1986-05-05 | 1986-05-05 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Dixon | Tighten ... on 6" ..., tighten 1/4" metric valves ... & 2" screwed ...
48 | 86-33006-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1986-05-05 | 1987-07-09 | Other |  | Steel/Wrought Iron |  | Dixon | Replaced nipples in hi to hi box
48 | 86-33007-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1986-05-05 | 1981-07-14 | Other |  | Steel/Wrought Iron |  | Dixon | Repair leaking nipple & tighten
48 | 86-33008-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1986-05-05 | 1987-07-02 | Other |  | Steel/Wrought Iron |  | Dixon | Repaired threads on inlot
48 | 89-33056-1 | [10 empty] | 1989-05-03 | [5 empty] | Dixon | Delete 0%
48 | 89-33057-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1989-05-03 | 1989-10-18 | Other |  | Steel/Wrought Iron |  | Dixon | Removed reg & re-tighten fittings
48 | 89-33058-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1989-05-03 | 1989-10-18 | Other |  | Steel/Wrought Iron |  | Dixon | Remove reg & re-tighten fittings
48 | 89-33060-1 | [10 empty] | 1989-05-05 | 1991-08-26 |  |  |  |  | Dixon | Delete - no gas reading; Deleted.
48 | 89-33055-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1989-05-03 | 1991-07-30 | Other |  | Steel/Wrought Iron |  | Dixon
48 | 87-33005-1 | [10 empty] | 1987-05-14 | [5 empty] | Dixon | Deleted; Delete no/gas reading
48 | 87-33003-1 | [10 empty] | 1987-05-13 | [5 empty] | Dixon | Deleted 10/2/91, Delete, Ref to 90-33000 Leak no., Delete +; Delete, Refer to new leak 90-33000
48 | 87-33004-1 |  |  | 0.75 | Service |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1987-05-13 | 1988-06-16 | Other |  | Steel/Wrought Iron |  | Dixon | Regulator set was replaced by G.C. on 3/88 should not be leaking.
48 | 88-33043-1 | [10 empty] | 1988-05-24 | [5 empty] | Rio Vista
48 | 88-33045-1 | [10 empty] | 1988-05-24 | [5 empty] | Dixon
48 | 90-33002-1 |  |  | 2 | Transmission |  | Valves |  |  | Other |  | 1990-05-09 | 1991-10-03 | Other |  | Steel/Wrought Iron |  | Dixon | Greased valve, replaced brushing & plug in valve
| 90-33002-1 | [10 empty] | 1990-05-09 | [5 empty] | Dixon | Duplicate
48 | 90-33015-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1990-05-05 | 1991-08-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Dixon | Tighten relief nipple
48 | 87-33006-1 | [10 empty] | 1987-05-14 | [5 empty] | Dixon | Deleted; Repaired on leak rep. 90-33015-1, 8-13-91
48 | 90-33016-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1990-05-15 | 1991-08-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Dixon | Deleted - cannot enter repair report, Tighten nipples 3/4"; At hi to hi set one on right, 301 on 1/4" nipple weld & regs
48 | 90-33017-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1990-05-16 | 1991-08-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Dixon | Deleted leak cannot enter repair report, Tighten nipples on relief and regs; Same reading out of both hi to hi sets, 301 on regs
48 | 90-33017-1 | [10 empty] | 1990-05-16 | 1991-04-15 |  |  |  |  | Dixon | Replaced by lab Refer ... delete leak; 6/13/91 Bob, Deleted these leaks & each one needs to be file with closed out lab.
48 | 90-33018-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1990-05-16 | 1991-08-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Dixon | Tighten joints
48 | 89-33061-1 | [10 empty] | 1989-05-05 | [5 empty] | Dixon | Deleted 8-13-91, 2648-C8-6 or 2648-A8-1
48 | 90-33026-1 |  |  | 2 | Distribution Main |  | Physical/Mechanical Joint |  |  | Other |  | 1990-05-30 | 1991-10-30 | Other |  | Steel/Wrought Iron |  | Vacaville | This leak report was deleted per ENGR. dept.; Repaired leaks on control and gage lines, repaired leaking reg, status deleted - couldn't enter repair, print
48 | 91-33001-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1991-05-02 | 1992-05-28 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Dixon | Tighten leaking union
48 | 91-33023-1 |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1991-06-06 | 1992-06-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Vaca. | Retighten & resealed leaking plug
48 | 91-33023-1 | [10 empty] | 1991-06-06 | [5 empty] | Vaca.
6 | 92-80006-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1992-01-23 | 1992-02-27 | Other |  | Steel/Wrought Iron |  | Fairfield | Refer to GM 4977328, Replaced 6" valve
48 | 91-33029-1 | [5 empty] | REGULATOR |  |  | MATERIAL FAILURE |  | 1991-06-07 | 1992-03-26 | OTHER |  |  |  |  | Repaired on leak #92-80011
9 | 92-33000-1 | [10 empty] | 1992-05-06 | [5 empty] | Dixon | 5/8 1992 leak survey - annual; hi to hi set box
9 | 92-33001-1 | [10 empty] | 1992-05-07 | [5 empty] | Dixon | Delete - refer to leak 94-33102; hi to hi set, hi to hi set box, refer to leak 94-33102
48 | 93-33002-1 | [10 empty] | 1993-05-13 | [5 empty] | Dixon | Delete leak - refer to Leak #94-33108
48 | 94-33052-1 | [10 empty] | 1994-04-14 | [5 empty] | Dixon
48 | 94-33053-1 | [10 empty] | 1994-04-14 | [5 empty] | Dixon
48 | 94-33054-1 | [10 empty] | 1994-04-14 | [5 empty] | Dixon
48 | 94-33055-1 | [10 empty] | 1994-04-14 | [5 empty] | Dixon
| 94-33056-1 | [10 empty] | 1994-04-14 | [5 empty] | Dixon | Annual, at hi to hi box, at hi to hi box, at hi to hi box, at hi to hi box, same, see next
48 | 94-33056-1 | [10 empty] | 1994-04-14 | [5 empty] | Dixon | hi to hi set box, hi to hi set box, same, same, delete leak
48 | 94-33056-1 | [10 empty] | 1994-04-14 | [5 empty] | Dixon
| 94-33058-1 | [10 empty] | 1994-04-14 | 2006-08-15 |  |  |  |  | Dixon | SVC. #4 Annual, At hi to hi set box, at hi to hi set box, back of fence, same, same, see next, Replace with new reg; same, same, same, same, replace with new reg.
48 | 94-33058-1 | [10 empty] | 1994-04-14 | [5 empty] | Dixon | Hi to hi box - back of fuse, hi to hi box, hi to hi, same, same
48 | 94-33058-1 | [10 empty] | 1994-04-14 | [5 empty] | Dixon | Filed 2648-A8-2
| 94-33058-1 |  |  |  | Service |  | Other |  |  | Atmospheric Corrosion |  | 1994-04-14 | 2006-09-07 | OTHER |  | Steel/Wrought Iron |  | Dixon | At Hi to Hi set box, same, same, Hi to Hi, back of fence, see next page, Found nipple corroded & leaking, rebuilt set & installed new box
| 94-33100-1 | [10 empty] | 1994-05-04 | [5 empty] | Dixon | Annual, 50' S/O Vaughn Rd. on Robben Rd. out of, 50' S/O Vaughn Rd. on Robben Rd. out of, vault, same, see next page; vault, same, same, vault; at valve, no leak found, delete
48 | 94-33100-1 | [10 empty] | 1994-05-04 | [5 empty] | Dixon | Same location (vault), vault, vault, vault, vault
| 94-33101-1 | [10 empty] | 1994-05-04 | [5 empty] | Dixon | SVC.#3 ANNUAL, @ hi to hi set box, @ hi to hi set box, hi to hi, same, See next page; same, same, same, same; At hi to hi box, no leak found, delete
48 | 94-33101-1 | [10 empty] | 1994-05-04 | [5 empty] | Dixon | Annual; Hi to hi set box, hi to hi set box, hi to hi, hi to hi, same
48 | 94-33101-1 | [10 empty] | 1994-05-04 | [5 empty] | Dixon
| 94-33102-1 | [10 empty] | 1994-05-04 | [5 empty] | Dixon | annual, @ hi to hi set box, @ hi to hi set box, hi to hi box, same, same, see next page
48 | 95-33018-1 | [10 empty] | 1995-03-31 | [5 empty] | Vaca\Dixon | same
48 | 95-33019-1 | [10 empty] | 1995-03-31 | [5 empty] | Vaca\Dixon
| 98-33004-1 | [10 empty] | 1998-03-27 | [5 empty] | Dixon | SVC. #2, annual, 301 at hi to hi box(N), 10' back of pavement, 301 at hi to hi box (N), 10' back of pav, 201 at hi to hi box (N), 10' back of pav, hi to hi box, same, see next page; hi to hi box, same, same; hi to hi box, hi to hi box, no leak found, delete
48 | 98-33004-1 | [10 empty] | 1998-03-27 | [5 empty] | Dixon | Annual; Hi to hi box, hi to hi, hi to hi
48 | 98-33007-1 | [10 empty] | 1998-04-02 | [5 empty] | Vacaville | Annual; GVB, delete leak
48 | 98-33010-1 | [10 empty] | 1998-04-02 | [5 empty] | Dixon | Annual; same
| 98-33011-1 | [10 empty] | 1998-04-01 | [5 empty] | Dixon | SVC. #2, Annual, hi to hi set, hi to hi set, hi to hi set, same, see next page; hi to hi, same, same, same, see next page; hi to hi, hi to hi box, no leak found, delete
48 | 98-33011-1 | [10 empty] | 1998-04-01 | [5 empty] | Dixon | Hi to hi set, hi to hi set, same
| 98-33012-1 | [10 empty] | 1998-04-01 | [5 empty] | Dixon | SVC. #1, annual, Hi to hi set, hi to hi set, hi to hi set, same, see next page; Hi to hi set, same, same, same, see next page; high to hight, hi to hi box, no leak found, delete
48 | 98-33012-1 | [10 empty] | 1998-04-01 | [5 empty] | Dixon | Annual; hi to hi set, hi to hi set, same
| 00-33002-1 |  |  | 0 | [7 empty] | 2000-03-08 | [5 empty] | Dixon | Annual, valve #1422 A in Dixon reg station, same, delete leak
48 | 94-33099-1 | [10 empty] | 1994-05-04 | [5 empty] | Dixon | Duplicate of #00-33002; same, same
| 00-33004-1 |  |  | 0.75 | Service |  | Fitting |  | FITTING SCREWED | Other | THREAD ON SCREWED FITTINGS | 2000-03-06 | 2001-06-29 | Other | REPLACED SERVICE | Steel/Wrought Iron |  | Dixon | Annual, over service near hi to hi set, over suc 3' back from ..., same, same, Inserted new service
| 01-33001-1 | [10 empty] | 2001-03-05 | [5 empty] | Vacaville | Annual, at reg sta #43 chart box, same, same, delete
| 01-33002-1 | [10 empty] | 2001-03-05 | [5 empty] | Vacaville | Annual, at valve #VV-09, same, same, delete
| 01-33086-1 | [10 empty] | 2001-05-22 | 2006-10-20 | DEACTIVATED ENTIRE SERVICE |  |  |  | Dixon | 600' w/o Currey Rd., Hi to Hi, 600' W/Currey Rd., Mete set is off, customer is on electric, remove bad reg, plug both sides
| 01-33086-1 | [10 empty] | 2001-05-22 | [5 empty] | Dixon | MOVE TO ANNUAL. REPAIRE 10/20/2006, hi to hi box, 1973 west of pedrick rd., hi to hi 600' w of currey rd.
| 01-33087-1 | [10 empty] | 2001-05-22 | [5 empty] | Dixon | Move to annual, hi to hi box
| 01-33089-1 | [10 empty] | 2001-05-22 | [5 empty] | Dixon | 5 Yr., hi to hi box, delete
| 01-33090-1 | [10 empty] | 2001-05-22 | [5 empty] | Dixon | 5 Yr., Hi to hi box, delete
| 01-33091-1 |  |  | 0.75 | Service |  | Regulator |  |  | Unknown |  | 2001-05-22 | 2007-01-16 | Other | REBUILD REG & BLOWOFF | Steel/Wrought Iron |  | Dixon | 5 Yr, hi to hi box on Robben Rd, 949' North of Midway Rd., rebuild regs & blow-offs in boxes
| 02-33004-1 | [10 empty] | 2002-04-10 | [5 empty] | Solano Unc | Annual SVC. #1, hi to hi box, same, delete
| 02-33005-1 | [10 empty] | 2002-04-12 | [5 empty] | Dixon | Annual SVC. #1, hi to hi set, hi to hi set, delete leak
| 02-33007-1 | [10 empty] | 2002-04-12 | [5 empty] | Dixon | Annual SVC. #2. hi to hi set, same, same, same, see next page; at hi to hi set, no leak found, delete
| 09-53106-1 | 150 | 8.95 | 6.63 | Transmission |  | Body of Pipe |  |  |  |  | 2009-09-01 | 2009-09-01 | Replace TP Main |  | Steel/Wrought Iron |  | Dixon | Replaced 78" of existing damaged main w/ pretested emergency main. Tested @ 2200 psig @ A-1342-01; -See Attached-; Farmer performing ripping of existing tomatoe field for future walnut orchard struck 6"00 L-150 transmission main, rapturing pipeline and causing downstream customer outages. Operator was not injured. No USA called. Operator claimed he was not aware of presence of pipeline. Equipment = D8 cut w/ 42" ripper blades.
| 08-33137-1 | [10 empty] | 2008-09-18 | [5 empty] | Dixon | on Sparkling Ln s/o Tremont Rd., on Reg first stage next to valve R-56, on reg first stage next to valve R-56, downgrade per T&R supervisor, On sparkling by line markers 100' S/O Tr, On sparkling by line markers 100' S/O Tremont, R-56
| 06-33100-1 | [10 empty] | 2006-09-06 | [5 empty] | Vacaville | Valve 269.5 at the Meridian Vaca Dixon sub station, valve 269.5 at the meridian vaca, same, same
| 06-53150- |  |  | 4 | Distribution Main |  | Body of Pipe |  |  |  |  | 2006-09-13 | 2006-09-13 | Deactivate #TP Main | Replaced Dist Main < 100 ft., Deactivated Partial Service, Replaced Partial Service | TR 418 |  | Dixon | Original, Cutout & spliced new section of plastic; At approx 11:30 Chillotti Cousta was digging to set a water box (valve) when backhoe dug up 4" plastic gas main
48 | 91-33009-1 |  |  | 0.75 | Distribution Feeder Main |  | Other |  |  | Other |  | 1991-05-29 | 1991-11-01 | OTHER |  | Steel/Wrought Iron |  | Vaca | Dummy; Cannot enter check date 11/19 after date permanently repaired.
48 | 98-33014-1 | [10 empty] | 1998-04-06 | [5 empty] | Vacaville | Same, clear
48 | 90-33034-1 |  |  | _.00 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1990-06-05 | 1991-11-22 | Replace Pipe |  | Steel/Wrought Iron |  | Vaca. | Removed & replaced section of feeder main
52 |  |  |  | 6 | Distribution Feeder Main | [8 empty] | OTHER |  | Steel/Wrought Iron |  | Sacto | Had to grease 6" valve ...
| 09-33310- |  |  | 0.5 | Transmission |  | Valves |  |  | Construction Defect |  | 2009-09-24 | 2009-09-24 | TIGHTEN CAP OR BOLT | CLOSE 1/2" BALL VALVE FOR GAUGE TAP. | Steel/Wrought Iron |  | Dixon | At valve VD-03, T&R crew called; Closed 1/2" ball valve for gauge tap and tightened plug. Soap tested no leakage. Replaced gauge. Leak surveyor re-checked and found no leakage.
| 08-33013-1 | [10 empty] | 2010-09-20 | [5 empty] | Vacaville | Over Gas main by valve, 24' back of curb; HCA Information 1) Source of leak identifified as: 2) Date of source determination: 3) Prompt repairs required: Y/N, Coments: Arived for Grade 1 in high consequence area T and R says this line was dist preasure T amd R greased valve. 8 gas @ 8 percent. Should recheck by Oct. 15.
| 08-33136-1 | 150 |  | 0.75 | Transmission |  | Valves |  |  | Other | Grease | 2009-03-19 |  |  |  | Steel/Wrought Iron |  | Dixon | R-36; Soap tested. 3/4" steel valve leaking - greased and operated valves - re-checked after scruicing valve with ranger & 112-2 and found 0% gas leak repaired @ v-1
| 07-53037- |  |  | 2 | Transmission |  | Valves |  |  | Material Failure |  | 2007-04-17 | 2007-04-18 | Other | REPLACED VALVE | Steel/Wrought Iron |  | Vacaville | 2" Broken valve off of L-400 Vaca/Reg, Replaced failed 2" valve; Vaca/Dixon sub - L-400 ; 2" to reg pit
| 08-33008- | [10 empty] | 2008-05-20 | [5 empty] | Dixon | Over street valve (V-1) campbell soup plant, valve (v-1), no leak detected, used CGI, Soap & operated valve; Use CGI, soap tested no leak detected operated valve
| 08-33005- |  |  | 0.75 |  |  | Valves |  |  | Other | DRY GREASE | 2008-05-19 | 2008-05-29 | Other | GREASED VALVE REPAIR LEAK ON HI-HI REG | Steel/Wrought Iron |  | Dixon | Scanned 5/20/08 No excavation required, at curb valve (8' back of road), valve; Found HPR fire valve to be leaking repaired by greasing valve
| 00-53133-1 | 210A | 18.08 |  |  |  | BODY OF PIPE |  |  | DIGIN |  | 2000-12-26 | 2000-12-26 | OTHER | REPLACE 30' OF PIPE | Steel/Wrought Iron |  | Cordelia | main, 30' of 32" A-1333-01 Emerg. stock X-60 hyp rod used to repair & pre-heat; 30' of pre-test emer. stock 32" A 1333/01 x 60 .500 .w x-ray tie-in weld #182 good cmt (925)250-2606 Robert Morales
|  |  |  | 8 | [7 empty] | 2004-11-16 |  |  |  | Steel/Wrought Iron |  | Elk Grove | Inspection only (stand by), 8" H.P. steel feeder main, installed directly under, 6" H.P. plastic gas main. 21" separation between top and bottom of 8" and 6" mains.
|  |  |  | 6 | [7 empty] | 2002-10-01 |  |  |  | Steel/Wrought Iron |  | Galt | Dept Inspection; GM Inspection only (depth check)
|  |  |  | 6 | Transmission | [6 empty] | 2002-10-01 |  |  |  | Steel/Wrought Iron |  | Galt | Dept check on G.M.; Dept check on GM
|  |  |  | 6 | Transmission | [6 empty] | 2002-10-02 |  |  |  | Steel/Wrought Iron |  | Galt | Depth check; Dept check only
|  |  |  | 1.25 | [11 empty] | Steel/Wrought Iron |  | Sacramento
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | Sacramento
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  |  | 10 | Transmission | [6 empty] | 2005-03-09 |  |  |  | Steel/Wrought Iron |  | Sacramento | Stand By
|  | 123 |  | 12.75 | [8 empty] | 2000-05-23 |  |  |  |  | Sacramento | repair wrap damaged by tiegert const. while potholeing
|  | 123 |  | 12.75 | [8 empty] | 2000-05-23 |  |  |  |  | Sacramento | Repair wrap - damaged by tiegert const while potholing
|  | 123 |  | 12.75 | [8 empty] | 2000-05-23 |  |  | Steel/Wrought Iron |  | Sacramento | Repair wrap damaged by tiegert const while potholeing
|  |  |  | 12.5 | [8 empty] | 2000-05-23 |  |  | Steel/Wrought Iron |  | Sacramento | repair wrap damaged by tiegert const while potholeing
|  | 123 |  | 12.75 | [8 empty] | 2000-05-23 |  |  | Steel/Wrought Iron |  | Sacramento | Repair wrap damaged by tiegert const. while potholeing
|  | 123 |  | 12.75 | [8 empty] | 2000-05-23 |  |  | Steel/Wrought Iron |  | Sacramento | Repair wrap damaged by tiegert const. while potholeing
|  | 123 |  | 12.75 | [8 empty] | 2000-05-23 |  |  | Steel/Wrought Iron |  | Sacramento | Repair wrap damaged by tiegert const. while potholeing
|  | 123 |  | 12.75 | [8 empty] | 2000-05-23 |  |  | Steel/Wrought Iron |  | Sacramento | Repair wrap - damaged by tiegert const. while potholeing
|  | 123 |  | 12.75 | [8 empty] | 2000-05-23 |  |  | Steel/Wrought Iron |  | Sacramento | Repair pipe wrap - damaged when potholed by tiegert const.
| 00-60037-1 | DFMA |  | 0.75 | Transmission |  | Fitting |  |  | Digin |  | 2000-03-22 | 2000-03-22 | Other | New Valve | Steel/Wrought Iron |  | N. Highlands | Blowing & shut down by T&R elevl - 175 lbs of pressure, Repairs made by T&R crevis we just assisted; T&R repaired - gas T&D just cut, threaded & installed a new valve + frame
| 01-55046-1 | 6-064601 | 7 |  | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-06-25 | 2001-07-12 | Mechanical Repair Fitting - Fitting | Plideo clamp | Steel/Wrought Iron |  | Woodland | At man
|  | 158 |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Woodland/Yolo Town | Stand-by to install ETS leads on L-158 Bob Miller
| 05-55095- |  |  | 0.75 | Transmission |  | Fitting |  | Regulator | Unknown |  | 2005-09-19 | 2005-09-19 | Other | Replaced Hi to Hi set | Steel/Wrought Iron |  | Woodland | At Hi to Hi set, Replaced Hi to Hi set by T&R installed new #2 box
| 00-35002- | [10 empty] | 2000-03-06 | [5 empty] | Woodland | Leak deleted, annual, Reg station, 0 Reading Delet Leak
| 01-35018- | 172 |  | 18 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2001-10-18 | 2001-10-22 | Welded Sleeve/Can - Weld | SAVE A VALVE | Steel/Wrought Iron |  | Davis | Line #116 & #119 uprate survey (2nd step), north side of dirt road, Weld 1-18" O.D. x 18" long sleeve over 1 leak ext corr. Weld 2 - 2" save-a-valve over 2 other leaks; 1 sleeve + 2 ea. 2" save a valve over series of pits, sleeve info 52,000 0.375" W.T. 18" O.D. 18" long
|  | 116 |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Yolo county | Line-116 1 mi east of swingle sta; Stand-by on L-166 Bob Miller
|  | 119 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | Yolo County | L-119 1 mile east of Swingle Sta, Stand-by L-119 Bob Miller
|  | 172 |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Yolo County | Line-172 1 Mile east of Swingle Sta; Stand-by on L-172 Bob Miller
|  | 116 |  | 0.16 | Transmission | [10 empty] | Steel/Wrought Iron |  | W. Sac - Davis
|  | 172 |  | 0.12 | Transmission | [10 empty] | Steel/Wrought Iron |  | W. Sac. - Davis
|  | 116 |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Yolo County | L-116 1.7 miles east of the west levee of the yolo by pass; Stand-by L-116 Bob Miller
|  | 119 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | Yolo county | L-119 1.7 miles east of the west levee of Yolo by-pass; Stand-by L-119 Bob Miller
|  | 172 |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Yolo County | L-172 1.7 miles east of the west levee of Yolo by-pass; Stand-by L-172 Bob Miller
|  | 172 |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Yolo County | L-172 .4 mile east of the west levee of Yolo by pass; Stand-by L-172 Bob Miller
|  | 119 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | Yolo County | L-119 .4 mile east of the west levee of the yolo by pass; standy-by L-119 Bob Miller
|  | 116 |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Yolo County | L-116 .4 mile east of the west levee of the Yolo by pass; Stand-by L-116 Bob Miller
| 07-20307- | [10 empty] | 2007-10-31 | [5 empty] | Sacramento | Valve #B (back side of the station), T&R Greased, valve #B, Leak repaired, Delete Leak
|  |  |  | 6 | Transmission | [6 empty] | 2010-08-11 |  |  |  | Steel/Wrought Iron |  | Sacto | We cut out existing 6" PCF. We were unable to complete the make up of fitting. Had shaving in the threads. Still leaked. Replaced with a straight piece of pipe that was tested. Put a 2'' valve is when we plugged down the existing fitting.
|  |  |  | 6 | Transmission | [6 empty] | 2010-08-11 |  |  |  | Steel/Wrought Iron |  |  | Put a 6" PCF on 6'00 main. So we could cut out exisiting PCF. That was unable to complete due to shaving in threads. Was leaking. Was leaking when exposed in the begining. Completion plug was not down in the fitting.
| 08-21153- |  |  | 0.75 | Transmission |  | Valves | Other | ON 3/4" NUT ON 3/4" VALVE | Other | 3/4" VALVE & NUT LEAKING | 2008-06-09 | 2008-06-25 | TIGHTEN CAP OR BOLT | SOAP AND/OR TAPE; RE-TIGHTENED NUT ON VALVE, RE-TAPED & DOPED PLA ON 3/4" VALVE ON STEM | Steel/Wrought Iron |  | Citrus Heights | No excavation or USA required, on valve D119; Re-tightened nut on 3/4" valve, re-taped & doped plug on 3/4" valve
|  |  |  | 8 | Transmission |  | Other |  | Inspection | Other | No leak | 2010-11-04 | 2010-11-05 | Other | Inspect | Steel/Wrought Iron |  | Davis | Inspection, 2nd bell hole sav-a-valve only, inspect; Weld on 2" Sav-A-Long inspect only.
| 08-35059- | 172 |  | 1 | Transmission |  | Valves |  |  | Unknown |  | 2008-05-14 | 2008-05-14 | Other | Operated Pin-off tee. | Steel/Wrought Iron |  | Woodland | Scanned 5/15/08, various ground valves in reg station, delete leak, leak repaired; Lk. repaired by operating "pin-off" tee. Sketch no provided by T&R.
| 08-35071- |  |  | 0.75 | Transmission |  | Other |  | PIN-OFF TEE. | Other | LOOSE CAP | 2008-05-26 | 2008-07-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Yolo | No excavation or USA required, valve #2, valve #2; Soap tested pin-off tee at line pressure after re-tightening the cap. Tightened cap on steel pin tee - soap tested no leaks detected. Excavated by R Cavello of GC Vaca.
| 08-35073- |  |  | 0.75 | Transmission |  | Other |  | PIN-OFF TEE. | Other | LOOSE CAP | 2008-05-26 | 2008-07-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Yolo | No excavation or USA req., valve #1, valve #1; soap tested pin-off tee after re-tightening at line pressure, tightened cap on steel pin tee - soap tested no leakage detected. excavated by R. Lavolle of GC Vava.
|  | 400 |  | 36 | Transmission | [12 empty] | Colusa | Dug up pin-off tee on line 400
| 08-21400-1 |  |  | 8 | Transmission |  | Valves |  |  | Construction Defect |  | 2008-11-18 | 2009-03-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Citrus Heights | Scanned to mapping 11/20/08, PM#41013064, At valve Antelope rd 200' (west of Rolling wood), V-D12; Soap tested before & after repairs. Found V-D121 to be leaking at gauge taps - pinnec off gauge tap tees - re-doped and tightened gauge taps to repair leak.
| 08-21400-1 | [10 empty] | 2008-11-18 | [5 empty] | Sacramento | Valve D-121, at valve D-121-200' west of Rolling Wood; Leak on valve D-121 41033298, Need to have dug-up to replace upstream & downstream gauge taps, valve is in bike lane used traffic control
| 06-35019- |  |  | 0.75 | Transmission |  | Unknown |  |  | Unknown |  | 2006-10-04 | 2006-10-25 | Other | Rebuilt reg | Steel/Wrought Iron |  | Davis | At PGE #1 box, on G/S, Rebuilt reg, fixed all leaks, reset relief. Sent back for corrections 11-13-06
|  | 116 | 3.77 | 12.75 | Transmission |  | Body of Pipe |  |  |  |  | 2006-07-17 | 2006-07-19 | Other | Install (3) clock springs | Steel/Wrought Iron |  |  | 8/31/06 CC: Mike Necton, Vacaville, Fax'd CC Dave Prewitt 8/31/06 9:30 A, Installed (3) 12" clock springs to repair 24" long gouge in pipe; A PG&E contractor struck and damaged 12" L-116 while digging a hole to replace an exisiting rotted pole. The TP gas line was not properly marked, so the contractor will not be billed. The auger caused a gouge ~ 24" long @ 1:00 to 2:30 o'clock area on the pipe. The auger struck the 12" L-116 38' west of the pipeline marker angle point. There was no gas loss.
| 01-55046-1 | 6-064601 | 7 | 6 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2001-06-25 | 2001-07-12 | Mechanical Repair Fitting - Fitting | PLIDEO CLAMP | Steel/Wrought Iron |  | Woodland | Used 6" lepl repair clamp
| 07-55064- | 155 |  | 6 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2007-11-13 | 2008-02-07 | Replace TP Main | 4" steel | Steel/Wrought Iron |  | Woodland | Sent to Terry M. 11-3-07 CD, Leak of 45" weld bend on DFM, on DFM
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | Sac
| 08-21123-1 |  |  | 6 | Transmission |  | Valves |  |  | Unknown | OTHER | 2008-06-08 | 2008-06-25 | Other | GREASED & OPERATED VALVE | Steel/Wrought Iron |  | Sac | No excavation or USA required; Greased & operated valve
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | Sacto | Cut out existing 4" valves. And replaced them with new ones. Valve 1# PUV 1378983 300 Seri Ball valve, Valve 2# PUV 1344483 300 Seri Ball valve.
|  |  |  | 8.625 | Transmission |  | Valves |  |  | Material Failure |  |  | 2003-09-16 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | Sacto. | Replaced 3/4" ball valve, replaced 12' of 3/4" STL. Pressure Tap; Note: Distribution Mains not shown. Valve A49. Leaking 3/4" valve. Replaced 3/4" valve, raised Pressure tap valve to grade.
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Galt
| 01-20268-1 |  |  | 4 | Transmission |  | Valves |  |  | Unknown |  | 2001-09-17 | 2001-12-19 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Rancho Cordova | cy to mapping 8/19/2001, Found a leak on the bottom of a ball valve - No hazzard out in sidewalk PIE, Plug leak repaired on bottom of bad valve 4" feeder main; Soap tested fitting
|  |  |  | 10 | Distribution Feeder Main | [6 empty] | 2001-07-21 |  |  |  | Steel/Wrought Iron |  | Sacramento
| 05-20164- | [10 empty] | 2005-05-04 | [5 empty] | Antelope | Transmission semi-annual, Cy to mapping 5/5/0, Outside station ground too wet to get M&C truck in to grease valve, will grease when ground dries, delete leak
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | Sacto
| 99-20249- |  |  | 6 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 1994-04-23 | 1999-04-27 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Elk Grove | At 6" GM valve 23, Tightened completion plug on 6" PCF
52 | 99-20249-1 | [10 empty] | 1994-04-23 | 1999-03-26 |  |  |  |  | Elk Grove | Checked out leak odor of valve, soaped all parts. No leak found, non-greasable valve. need to dig up; S/S Elk Grove Blvd, 100' E/O, Big Horn Blvd. Valve 23
|  |  |  | 8.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | Sacto. County | TBM 358 E-5 WM/PS 2654 F8 8 Laguna Area Sacramento County. Cleared contact with PacBell ground rod. No damage to TP main.
[5 empty] | Transmission | [10 empty] | Steel/Wrought Iron |  | Elk Grove
|  |  |  | 4 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Elk Grove
|  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Elk Grove
52 |  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1974-03-27 |  |  |  | Steel/Wrought Iron
52 |  |  |  | 1.25 | Branch Service | [6 empty] | 1972-02-11 |  |  |  | Steel/Wrought Iron
52 |  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Sacto
52 | 79-60318-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-07-13 | 1979-07-13 | Other | AMP- | Plastic
52 |  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1972-08-15 |  |  |  | Steel/Wrought Iron |  | Orangevale
52 |  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
52 |  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
52 | 76-20488-1 |  |  | 0.75 | Other |  | Other |  |  | Other |  | 1976-05-03 | 1976-05-26 | Other |  | Steel/Wrought Iron |  | Fair Oaks
52 |  |  |  |  | Other |  | Body of Pipe |  |  | Corrosion |  | 1976-10-04 | 1976-10-05 | Other |  | Steel/Wrought Iron |  | Sacto. | Not entered into computer! house line. See reverse side; Made temp repairs with taps only. Call ... dept. for time check. School will repair!
52 | 80-60046-1 |  |  | 1 | Service |  | Other |  |  | Damage by outside Forces |  | 1980-02-07 | 1980-02-07 | Replace Pipe and/or Service |  | Plastic |  | Sacto
52 | 80-60042-1 |  |  | 1 | Service |  | Other |  |  | Damage by outside Forces |  | 1980-02-05 | 1980-02-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Sacto
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | Fair Oaks
20 | 75-00139-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-05-22 | 1975-05-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron
20 | 78-00039-1 |  |  | 1.25 | Distribution |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-04-28 | 1978-04-28 | Replace Pipe and/or Service |  | Plastic |  | Citrus Hts
|  |  |  | 4 | Other | [10 empty] | Steel/Wrought Iron |  | Citrus Heights
20 | 78-00114-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-08-05 | 1978-08-05 | Replace Pipe and/or Service |  | Plastic |  | Citrus Hts | Connection made with 2-1/2" plastic ampfit coupling
20 | 78-00113-1 |  |  | 2 | Distribution |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-07-31 | 1978-07-31 | Replace Pipe and/or Service |  | Plastic |  | Roseville
20 | 77-00124-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-08-28 | 1977-08-28 | Replace Pipe and/or Service |  | Plastic |  | Roseville | Replace damage section & connection made with 2-1/2" plastic coupling
20 | 77-00082-1 |  |  | 1.25 | Distribution |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-05-26 | 1977-05-26 | Replace Pipe and/or Service |  | Plastic |  | Cit. Hit.
20 | 78-00128-1 |  |  | 00.50 + 3/4" steel | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-08-22 | 1978-08-23 | Replace Pipe and/or Service |  | Plastic | Steel | Orangevale | Lower 35' of 3/4" steel + 1/2" plastic
20 | 78-00142-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-09-17 | 1978-09-17 | Replace Pipe and/or Service |  | Plastic |  | Orangevale | Connection made with 2-1/2" amp-fit fitting coupling
20 | 77-00022-1 |  |  | 4 | Distribution Main |  | Fitting |  |  | CONSTRUCTION DEFECT |  | 1977-01-11 | 1977-01-11 | Patch Welded |  | Steel/Wrought Iron |  | Orangevale | LEAK IN CAP.
20 | 77-00021-1 |  |  | 4 | Distribution |  | Body of Pipe |  |  | Corrosion |  | 1977-01-07 | 1977-01-24 | Clamp |  | Steel/Wrought Iron |  | Orangevale
52 | 81-60236-1 |  |  | 2 | Distribution |  | Body of Pipe |  |  | Damage by outside Forces |  | 1981-09-15 | 1981-09-15 | Replace Pipe and/or Service |  | Plastic |  | Sacto.
| 05-20229- |  |  | 16 | Transmission |  | Valves |  |  | Unknown |  | 2005-08-31 | 2005-08-31 | Other | Greased valve | Steel/Wrought Iron |  | Orangevale | Folsom uprate, DFM valve (D-35), Greased valve & replaced 1/4" plug; Greased valve -D.35- no exposed pipe.
| 00-20109- |  |  | 8 | Transmission |  | Valves |  |  | Unknown |  | 2000-03-01 | 2000-03-03 | Other | GREASED VALVE & FITTING | Steel/Wrought Iron |  | Orangevale | Valve leak - grease, Injected grease and tightened fittings at various taps and buttons
|  |  |  | 8 | Distribution Feeder Main | [6 empty] | 2004-10-15 | 2004-10-15 | Other | wrapped pipe | Steel/Wrought Iron |  | Orangevale | Re-wrapped 8" H.P. Feeder as main; rewrap only
| 05-21064-1 |  |  | 0.5 | Transmission |  | Other |  | 1/2" PRESSURE TAP ON MAINLINE VALVE | Other | Dry pipe dope on pipe threads | 2005-08-31 | 2010-11-03 | Other | CLEANED THREADS BELOW 1/2" VALVE, DOPED & TIGHTENED VALVE. SOAPED OK | Steel/Wrought Iron |  | Folsom | D-52-D Fair Oaks & Madison, Fair Oaks & Madison Ave- D-52-D, same, D-52-D, Valve D-52-D in Sidewalk; Doped threads & tightened 1/2" valve, soaped OK; Doped threads, tightened 1/2" valve, soaped OK, All repairs performed inside valve frame of cover, unable to see gas main for inspection.
52 | 72- |  |  | 8 | Distribution Feeder Main | [6 empty] | 1972-08-08 |  |  |  | Steel/Wrought Iron |  | Orangevale | all stations tested with Davis gas leak, tester show no gas readings now. This service broken when pressure was raised, service was repaired.
52 |  |  |  | 8 | Transmission | [6 empty] | 1984-07-03 |  |  |  | Steel/Wrought Iron |  | Sacto
52 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
52 | 79-40181-1 |  |  | 0.75 | Service |  | BODY OF PIPE |  |  | CORROSION |  | 1979-07-12 | 1979-07-12 | OTHER |  | Steel/Wrought Iron |  | Fair Oaks | Re-newed service, 16' inserted with 1/2" PL 24' of 1/2" PL direct buried 64' of 3/4" STL.
52 |  |  |  | 2 | [11 empty] | Other Plastic |  | Carmichael
[13 empty] | 1990-10-22 |  |  |  |  | Folsom | Comment 1 page 1: c/o 3/4" hi to hi serv. at main using pin off tee + 3/4" weld cap
2004-04-03
52 | 90-20219-1 |  |  | 8.65 | Distribution Feeder Main |  | Other Welds |  |  | Construction Defect |  | 1990-11-02 | 1990-11-07 | Replace Pipe |  | Steel/Wrought Iron |  | Folsom | Installed 2" 8" B.T. + 15' of .188 8" pipe
[13 empty] | 1990-11-02 | [5 empty] | Comment 1 page 1: Replace hi to hi reg set.
52 | 90-20034-1 |  |  | 8 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1990-01-11 | 1991-02-07 | Other |  | Steel/Wrought Iron |  | Folsom | Comment 1 page 1: greased valve #D09
52 |  |  |  | 4.5 | Distribution Main > 60 PSIG | [6 empty] | 1972-11-07 |  |  |  | Steel/Wrought Iron |  | Folsom
52 |  |  |  | 4 | Distribution Main > 60 PSIG | [8 empty] | Other |  | Steel/Wrought Iron |  |  | Comment 1 page 2: See above sketch.
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | Orangevale
| 08-21116-1 |  |  | 12 | Transmission |  | Other |  | threaded fitting | Unknown |  | 2008-06-04 | 2008-06-25 | TIGHTEN CAP OR BOLT | TIGHTEN CAP/BOLT; SOAP AND/OR TAPE; RE-TAPED & DOPED FITTING & TIGHTENED | Steel/Wrought Iron |  | Folsom | Comment 1 page 3: Re-taped + doped thread + re-tightened 1/2" valve onstem.
52 | 90-20069-1 |  |  | 4 | Transmission |  | Valves |  |  | Construction Defect |  | 1990-08-15 | 1995-04-05 | Other |  | Steel/Wrought Iron |  | Folsom | Comment 1 page 1: Greased leaking fire valve to dist. reg station
|  |  |  | 2 | [11 empty] | Steel/Wrought Iron |  |  | Comment 1 page 1: inst. 1" plastic svs
52 | 75-21794-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  |  |  | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Folsom
52 |  |  |  | 1.25 | [11 empty] | Steel/Wrought Iron |  | Folsom
52 | 81-60200-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1981-08-27 | 1981-08-27 | Other |  | Steel/Wrought Iron |  | Folsom TBM 22C6 | Comment 1 page 2: Time tested house line to wash room with 10cb air pressure Did service main shut + locked meter here.
[16 empty] | Steel/Wrought Iron |  | Folsom | Comment 1 page 1: ETS BOW S/S Riley 149' E/O Wales Dr.
52 | 91-20229-1 |  |  | 10 | Distribution Feeder Main |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1991-08-29 | 1991-08-29 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Folsom | Comment 1 page 1: Redoped threads
| 00-20152- |  |  | 6 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 2000-03-08 | 2000-03-15 | TIGHTEN CAP OR BOLT |  | Steel/Wrought Iron |  | Folsom | Comment 1 page 1: Repaired two small leaks on guage tops
| 08-21148-1 |  |  | 8 | Other |  | Fitting |  | THREADED | Unknown |  | 2008-06-05 | 2008-09-02 | OTHER | TIGHTENED THREADED PIPE. | Steel/Wrought Iron |  | Folsom | Comment 1 page 2: tightend threaded pipe
| 08-21117-1 |  |  | 0.75 | Transmission |  | Other |  | 3/4 CAP/PLUG ON THREADS | Other | fitting thread | 2008-06-05 | 2008-06-25 | TIGHTEN CAP OR BOLT | TIGHTEN CAP/BOLT; SOAP AND/OR TAPE; RE-TAPED & DOPED FITTING & TIGHTENED | Steel/Wrought Iron |  | Folsom | Comment 1 page 3: Re-taped + doped 3/4" plug re-tightened plug; Comment 2 page 3: No sketch required sketch is with static drawings
52 | 93-20426-1 |  |  | 12 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1993-04-16 | 1994-05-04 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Folsom | Comment 1 page 1: permanent repair made by tightening 1/2" steel coupling & 1/2" steel nipple for grease fitting.
| 94-60278-1 | [5 empty] | BODY OF PIPE | [5 empty] | 1994-10-21 | REPLACE PIPE
52 | 90-60155-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Digin | ; | 1990-07-03 | 1990-07-03 | Replace Pipe |  | Other | TR 418 | Folsom | Repaired 1 1/4" p main w/ two TR+18 coupling and 15" of 1 1/4" gas main
52 | 89-60449-1 |  |  | 2 |  |  | Body of Pipe |  |  | Digin |  | 1989-12-12 | 1989-12-12 | Replace Pipe |  | Steel/Wrought Iron |  | Folsom | replaced 2" pipe and 2" fittings
[18 empty] | Folsom | Comment 1 page 3: Performed standby at this location A form for depth only.
| 02-60340-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Digin | BORE MACHINE | 2002-09-12 | 2002-09-12 | REPLACE TP MAIN |  | Steel/Wrought Iron |  | Sacramento | Comment 1 page 1: Instal 2 4" PCF service 30 & 119 of 4" steel pipe .237wt; Comment 1 page 2: See attached sketch.
| 08-20068- |  |  | 1.25 | Single Service |  | Body of Pipe |  |  | Construction Defect |  | 2008-01-26 | 2008-02-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron | coated steel | Sacramento | Comment 1 page 2: Tighten bolts on hi to hi set.
| 05-20276- |  |  |  | Transmission |  | Regulator |  |  | Construction Defect |  | 2005-10-25 |  |  |  | Steel/Wrought Iron |  | Sacramento | Comment 1 page 1: Delete leak - Reg sation
| 03-21079-1 | [10 empty] | 2003-07-08 | [5 empty] | Sacramento | Comment 1 page 1: high to high set deleted.
[16 empty] | Steel/Wrought Iron |  | Sacto | Comment 1 page 3: Standby @ this location 3/12/10 - filled out A-Form per Scott Farrell
| 07-20334- | [10 empty] | 2007-11-19 | 2007-11-29 |  |  |  |  | Sacramento | Comment 1 page 1: Found no leaks might be on line outside of station
| 08-21152-1 | [10 empty] | 2008-06-09 | [5 empty] | Sacto
| 08-21154-1 | [10 empty] | 2008-06-09 | [5 empty] | Sac
| 08-21154 | [10 empty] | 2008-06-09 | [5 empty] | Sac
| 08-21401- |  |  | 8 | Transmission |  | Fitting |  |  | Unknown |  | 2008-11-19 | 2008-11-19 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Sacramento | Comment 1page 3: tightened fitting on valve top or valve 12,15 Barandas Dr. Sacramento
52 |  | 119 |  | 12 | Transmission | [6 empty] | 1972-08-22
| 03-21080-1 | [10 empty] | 2003-07-08
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | Sacramento
52 | 79-40303-1 |  |  | 0.75 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-11-02 | 1979-11-02 | Replace Pipe |  | Steel/Wrought Iron |  | Sactramento
| 07-20136-1 | 500 |  | 8 | Transmission >= 20% SMYS |  | Valves |  |  | Other |  | 2007-04-19 | 2007-10-18 | Other |  | PE2406 (Yellow or Orange) |  | Sacramento | valve will have to be dug up
| 07-20136-1 | [10 empty] | 2007-04-19
| 07-20136-1 | [10 empty] | 2009-04-19 | [6 empty] | Per Steve Reiswig: leak reported as GR 1 falls in CGT red zone as must be worked as a GR 1. If you choose to downgrade the leake you must enter teh appropriate grade & leak read in the "readings" section. Steve won't downgrade. Turned in memo # 249826 valve will have to be dug up PV 5-1-07
| 07-20136-1 |  |  | 8 | Transmission |  | Valves |  | VALVE BODY | Other | Fittings | 2007-04-19 | 2007-10-18 | Other | Tightened valve threads |  |  | Sacramento | turned in memo #24826 Valve will have to be dug up.
52 | 83-40126-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1983-07-26 | 1983-07-26 | Other |  | Steel/Wrought Iron |  | Sacto
| 08-21087-1 |  |  | 4 | Transmission |  | Other |  | Fitting on valve | Other | Valve | 2008-04-05 | 2008-06-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  |  | Tighten plugs in valve frame & cover
| 08-21172-1 | 119 | 13.39 | 16 | [7 empty] | 2008-06-18 |  |  |  | Steel/Wrought Iron |  | SAC | 0% on gas ranger-no bubble found in valve frame & cover. Greased & operated valve.
| 08-21169- |  |  | 0.5 | Transmission |  | Other |  |  | Weld Failure |  | 2008-06-18 | 2008-09-15 | REPLACE VALVE < 2 INCH |  | Steel/Wrought Iron |  | Sacramento | REPLACED 1/2" VALVE WITH NEW VALVE.
| 08-21171-1 |  |  | 0.5 | Transmission |  | Valves |  |  | Unknown |  | 2008-06-18 | 2008-09-15 | REPLACE VALVE < 2 INCH |  | Steel/Wrought Iron |  | Sacramento
| 08-21171-1 | 119 | 13.39 | 6 | Transmission | [6 empty] | 2008-07-03 | 2008-07-03 | Other | GREASED FITTING | Steel/Wrought Iron |  | Sac
| 08-21170- |  |  | 0.75 |  |  | Valves |  |  | Other | Plug | 2008-06-18 | 2008-06-18 | Other | Tighten plug | Steel/Wrought Iron |  | Sacramento
52 |  |  |  | 12 | Distribution Feeder Main | [6 empty] | 1981-07-21 | [5 empty] | Sacto
| 03-21076-1 | [10 empty] | 2003-07-07
52 |  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1971-12-23 |  |  |  | Steel/Wrought Iron
|  |  |  | 12 | Transmission
|  |  |  | 20 | [11 empty] | Steel/Wrought Iron
52 |  |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  |  | 1974-06-13 | Weld Over Sleeve or Can |  | Steel/Wrought Iron
52 | 96-20203-1 |  |  | 3 |  |  | Body of Pipe |  |  | Corrosion |  | 1996-05-01 | 1996-05-01 | Clamp |  | Steel/Wrought Iron |  | Sacto | Replaced 18" 3" stl pipe on 5/2. 5/1/96 installed clamp for temp.
52 | 76-60317-1 |  |  | 2 | Other |  | Other Welds |  |  | Construction Defect |  | 1976-09-09 | 1976-09-10 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | shut by pass off 9-9-76 to stop leak.
52 | 81-60035-1 |  |  | 0.75 | Other |  | Fitting |  |  | Material Failure |  | 1981-02-06 | 1981-02-06 | Other |  | Steel/Wrought Iron |  | Sacto city
52 | 73-00056-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-06-25 | 1973-07-03 | PATCH WELDED |  | Steel/Wrought Iron |  | Sacto | had to acr weld a 6" x 8" steal patch over leaking pitt also had to acr weld a 3" x 4" over a small pitt (not leaking) patches ..250 also used 1 1" save-a-valve
52 | 95-20174-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1995-04-19 | 1996-02-23 | Other |  | Steel/Wrought Iron |  | sac | Greased & operated V-20
52 | 74-40281-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1974-11-11 | 1974-11-12 | Other |  | Steel/Wrought Iron |  | Sacti city
52 | 75-40358-1 |  |  | 6 | Distribution Feeder Main |  | Other Welds |  |  | Construction Defect |  | 1975-12-03 | 1975-12-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Sacramento | arc welded a 1" sace-a-valve over pinhole like to rc-
52 | 79-40266-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-09-28 | 1979-09-28 | REPLACE PIPE AND/OR SERVICE |  | Other | Plastic
52 | 95-20185-1 |  |  | 0.5 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1995-04-19 | 1996-02-22 | Tighten Cap or Bolt |  | Other |  | Sac | permanent repair made by dopping and re-tightening 1/2" plug on valve # D85.
52 | 96-60199-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Digin |  | 1996-08-15 | 1996-08-15 | Replace Pipe |  | Steel/Wrought Iron |  | Sacramento | exposed and replaced approx 5' ft. of 12" pipe
52 | 71-00019- | 119 |  | 8 | Distribution Feeder Main |  | BODY OF PIPE |  |  | CORROSION |  | 1971-05-13 | 1971-05-18 | PATCH WELDED |  | Steel/Wrought Iron |  | N/ Sacto | arc welded a 6" x 20" steel patch over a 6" x 1", 1" x 1" electrolysis pitt to 8" beeder 150 lbs gas main here. This is line # 119.
52 | 90-20023-1 |  |  | 12 | Transmission |  | Fitting |  |  | Other |  | 1993-12-13 | 1993-12-17 | Replace Pipe |  | Steel/Wrought Iron |  | Sacramento
52 |  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1981-04-03 |  |  |  | Steel/Wrought Iron |  | N. Sacto
|  |  |  | 12 | Transmission | [6 empty] | 2010-10-10 |  |  |  | Steel/Wrought Iron |  | Sacramento | inspected 12" gas main 34' W/E/L 7th st & 93' N/N/L F St
52 | 78-60087-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  | 1978-03-28 | 1978-04-11 | Other |  | Steel/Wrought Iron |  | Sacto
52 | 77-40065-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Material Failure |  | 1977-02-15 | 1977-03-11 | CLAMP |  | Steel/Wrought Iron |  | Sacto
52 | 74-21291-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Material Failure |  | 1974-06-18 | 1974-06-26 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron
| 02-20138-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Other | Ding in pipe | 2002-04-09 | 2003-08-12 | Other | Sleeve | Steel/Wrought Iron |  |  | welded sleeve + 2" save-a-valve over bad spaon on Trans Main
52 | 74-21549-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-07-12 | 1974-08-16 | Other |  | Steel/Wrought Iron
52 |  |  |  | 12 | Distribution Feeder Main | [6 empty] | 1974-01-24 |  |  |  | Steel/Wrought Iron
52 | 75-60191-1 |  |  | 0.75 | Other |  | Fitting |  |  | Damage by outside Forces |  | 1975-07-11 | 1975-07-11 | Other |  | Steel/Wrought Iron |  | Sacto
52 | 74-60087-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-04-03 | 1974-04-03 | PATCH WELDED |  | Steel/Wrought Iron |  | Sacto | found an electrolysis leak in a 12" feeder main. Made permanent repairs, welded a 6" x 6" patch over leak. Made patch from .250 pipe5L x 42 backfilled bellhole with fill sand.
52 |  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Sacramento | remove wrap from 12" feeder main at this ???? and checked condition of main & wrap. Backfilled bellhole with fill sand.
|  |  |  | 3 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | cut off 3/4" Hp.svs removed reg set + abandoned 3/4" set in place 3" main @ 40" cover.
52 | 75-40239-1 |  |  | 1 | Gathering |  | Tap Connection |  |  | Material Failure |  | 1975-08-05 | 1975-08-07 | Other |  | Steel/Wrought Iron
52 |  |  |  | 12 | Transmission | [6 empty] | 1973-11-01 |  |  |  | Steel/Wrought Iron
52 | 75-60043-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1975-04-03 | 1975-04-03 | Other |  | Steel/Wrought Iron |  | Sacto | arc welded 1" sava valve nipple over 9/32 drill hole in w 12" HP main.
52 | 73-20383-1 |  |  | 1.25 | Other |  | Valves |  |  | Material Failure |  | 1973-12-10 | 1974-02-11 | OTHER | TIGHTENED PACKING NUT ON CURB GATE VALVE. | Steel/Wrought Iron |  | Sacto | Repaired a gas leak on a 1 1/4" Lp. Curb valve, tightened packing nut on valve
52 | 76-60462-1 |  |  | 1 | Other |  | BODY OF PIPE |  | DRIP | Corrosion |  | 1976-12-14 | 1976-12-15 | Other |  | Steel/Wrought Iron
52 | 83-60061-1 |  |  | 2 | Other |  | Body of Pipe |  |  | Corrosion |  | 1983-04-06 | 1983-04-06 | Other |  | Steel/Wrought Iron
52 | 74-21325-1 |  |  | 1 | Other |  | Drip |  |  | Corrosion |  | 1974-06-19 | 1974-07-02 | Other |  | Steel/Wrought Iron
|  |  |  | 12 | Distribution Main > 60 PSIG |  | Other |  | DAMAGED WRAP ONLY. | Damage by 3rd Party |  |  | 2011-02-01 | Rewrapped Pipe - Other |  | Steel |  | sAC | cleaned existing wrap (w/water) primered and rewrapped
|  |  |  | 12 | Distribution Main > 60 PSIG |  | Other |  | DAMAGED WRAP ONLY. | Damage by 3rd Party |  |  | 2011-02-01 | Rewrapped Pipe - Other |  | Steel |  |  | found wrap damaged -cleaned w/ water, primered and rewrapped
52 | 76-60190-1 |  |  | 1 | Gathering |  | Drip |  |  | Corrosion |  | 1976-06-02 | 1976-06-02 | Other | CUT DRIP OFF AT MAIN | Steel/Wrought Iron |  | Sacto. | Found old 1" Homemade drip leaking, made permanent repairs, cut drip off at main.
52 | 77-21086-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Corrosion |  | 1977-12-06 | 1979-01-16 | Other |  | Steel/Wrought Iron |  | Sacramento | Had to abandon unused 1 1/4" LP stub at main to repair leak here.
52 | 74-20013-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-01-10 | 1974-01-15 | Other | Cut off at main | Steel/Wrought Iron |  | Sacramento | Found old 1" pipe leaking near curb, pipe not in use, abandoned, 1" tap at bottom of 4" CI. main.
|  |  |  | 6 | [7 empty] | 1990-07-28 |  |  |  | Cast/Ductile Iron |  |  | c/o stl sus
[16 empty] | Steel/Wrought Iron |  | W. Sac | Comment 1 page 2: cut off 3/4" of, svs. Exposed svc. tee only. Comment 2 page 2: used pin off tee to shut down svc. gas flow.
52 |  |  |  | 2 | Transmission | [6 empty] | 1974-05-30
52 | 89-60197-1 |  |  | 8 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1989-06-14 | 1989-06-15 | TIGHTEN CAP OR BOLT |  |  |  |  | Dug up 8" valve. Had reg dep grease valve.
52 | 80-40086-1 |  |  | 12 | Gathering |  | Drip |  |  | Corrosion |  | 1980-04-02 | 1980-04-03 | Other | LOWERED DRIP PIPE TO MAIN | Steel/Wrought Iron |  | Sacto. | Page 2 comment 1: Cut drip off at main chocked each side of drip pot with T.L.V detector, did not expose bell joints.
52 | 93-20025-1 |  |  | 12 | Distribution Feeder Main |  | Girth Weld |  |  | Material Failure |  | 1993-01-13 | 1993-01-14 | Replace Pipe |  | Steel/Wrought Iron |  | Sacto | Page 1 comment 1: Replaced 3' of 12" stl made 1 butt weld and 1 sleeve
52 |  |  |  | 12 | Transmission | [6 empty] | 1977-06-21 |  |  |  | Steel/Wrought Iron
| 08-21110-1 |  |  | 1 | Transmission |  | Valves |  |  | Other | 1" Valve | 2008-05-28 | 2008-06-05 | REPLACE VALVE < 2 INCH | TIGHTENED PACKING NUT. | Steel/Wrought Iron |  | Sacto | Comment 1 from page 3: Found 1" Ball valve for body bleed to be leaking-tightened packing nut and stopped leak. Soap tested found no further leak.
52 | 74-21537-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-07-12 | 1974-09-13 | Other |  | Steel/Wrought Iron
| 09-21220-1 | [10 empty] | 2009-06-24 | [5 empty] | Sacramento
52 | 80-60436-1 |  |  | 6 | Other |  | BODY OF PIPE |  |  | Damage by outside Forces |  | 1980-10-16 | 1980-10-16 | Other | DRIP RISER | Cast/Ductile Iron
52 | 75-20417-1 |  |  | 1 | Other |  | Drip |  |  | Corrosion |  | 1975-07-30 | 1976-02-25 | Other |  | Steel/Wrought Iron
52 | 76-20374-1 |  |  | 4 | Distribution Main |  | BELL JOINT |  |  | Other | BOLTS LOOSE + CLAMP OLD. | 1976-04-15 | 1977-04-21 | Bell Joint Clamp |  | Cast/Ductile Iron |  | Sacramento | Comment 1 from page 2: Fo8und a 4" CI bell joint blowing gas, made permanent repairs, replaced 4" leak clamp. Exposed 9ft. of main, did not find a drip where D. Palmer abandoned a 1" riser from, on leak #75204171
52 | 75-20417-1 |  |  | 1 | Other |  | Drip |  |  | Corrosion |  | 1975-07-30 | 1976-02-25 | Other |  | Steel/Wrought Iron |  | Sacramento
52 | 80-60437-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-10-14 | 1980-10-14 | Other | Drip c/o at main | Steel/Wrought Iron |  | Sacto
52 | 74-60093-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-04-05 | 1974-04-08 | Other |  | Steel/Wrought Iron
52 | 74-22441-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-06-14 | 1975-01-17 | Other |  | Steel/Wrought Iron |  | Sacto | 1" LP drip had corrosion leak here, cut off 1" drip at 6" ci LP main drip pot.
52 | 77-20043-1 |  |  | 2 | Other |  | Body of Pipe |  |  | Corrosion |  | 1977-01-19 | 1979-05-18 | Other |  | Steel/Wrought Iron |  | Sacramento | Comment 1 from page 2: Abandoned 2" LP drip at 4" CI main to stop leak here.
52 | 74-40136-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-05-13 | 1974-05-15 | Other |  | Steel/Wrought Iron |  | sacto. inc. | found 21" drip riser leaking made permanent repairs, lowered drip riser to main.
52 | 79-40149-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Corrosion |  | 1979-05-19 | 1979-05-22 | OTHER |  | Steel/Wrought Iron |  | Sacto City inc. | Comment 1 from page 1: made temp. repairs 5-21-79. Comment 1 from page 2: Abandoned 1 1/4" stub at main to stop leak here.
52 | 82-20031-1 |  |  |  | Other |  | Body of Pipe |  |  | Corrosion |  | 1982-03-22 | 1982-10-01 | Other |  | Steel/Wrought Iron |  | Sacto | Found leak on 2" old drip. Cut drip off at 4" c.i. main all so 4" c.i.b.j clamp 154" N of NPL of hsi.
52 | 75-60115-1 |  |  | 1 | Other |  | Drip |  |  | Corrosion |  | 1975-05-29 | 1975-06-04 | Other |  | Steel/Wrought Iron |  | Sacto | Comment 1 page 1: leak discovered by crew foreman & repared while on customer call in leak 75-40164.
52 | 74-40248-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-09-04 | 1974-09-09 | Other |  | Steel/Wrought Iron |  | Sacto. Inc. | Comment 1 from page 2: Found an old 1 1/4" LP. drip pipe leaking, (blowing gas) drip tied to 6' WI. main, with bottom tap screwed tee. Made permanent repairs, cut drip pipe at main, removed tee, and plugged hole with 1 1/4" screwed plug.
52 | 79-20120-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  | 1979-01-24 | 1980-01-04 | Other | cut off at main | Steel/Wrought Iron |  | Sacramento | Comment 1 page 2: Cut off leaking 1" drip line at main.
52 | 77-40086- |  |  | 0.75 | Other |  | Other |  |  | Damage by outside Forces |  | 1977-04-01 | 1977-04-01 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Sacto | reweld nipple on manifold gas serv. not damage.
52 | 80-60406-1 |  |  | 1.25 | Other |  | Drip |  |  | Damage by outside Forces |  | 1980-10-06 | 1980-10-06 | Other | Cut off at main | Steel/Wrought Iron |  | Sacto city | Comment 1 page 2: cut off old drip line at main.
52 | 79-60192-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  | 1979-05-25 | 1979-05-29 | Other | cut off at main | Steel/Wrought Iron |  | Sacto city | Comment 1 page 2: Made permanent repairs by cutting off drip at main.
52 | 75-40258-1 |  |  | 4 | Distribution Main |  | Drip |  |  | Damage by outside Forces |  | 1975-08-30 | 1975-08-30 | Other |  | Cast/Ductile Iron
52 | 80-20316-1 |  |  | 1.25 | Other |  | BODY OF PIPE |  |  | Corrosion |  | 1980-07-28 | 1981-01-07 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Sacramento | WELDED OVER CORRODED BODY... 4" H.P....
52 | 81-40173-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1981-12-04 | 1981-12-04 | Clamp |  | Steel/Wrought Iron |  | Sacto
52 | 76-40252-1 |  |  | 1 | Other |  | OTHER |  |  | Damage by outside Forces |  | 1976-08-06 | 1976-08-06 | Other |  | Steel/Wrought Iron
52 | 74-21156-1 |  |  | 1 | Other |  | Fitting |  |  | Material Failure |  | 1974-06-10 | 1974-09-17 | Other |  | Steel/Wrought Iron
52 | 71-00311-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1971-10-18 | 1971-12-06 | PATCH WELDED |  | Steel/Wrought Iron
52 | 71-00248-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1971-10-18 | 1971-12-06 | Patch Welded |  | Steel/Wrought Iron |  |  | ARC WELDED 6" X 12"...
52 | 74-21883-1 |  |  | 0.75 | Other |  | Fitting |  |  | Corrosion | CPA65 | 1974-08-07 | 1974-12-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1975-11-26 |  |  |  | Steel/Wrought Iron
52 | 78-60369-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Corrosion |  | 1978-09-15 | 1978-09-15 | OTHER |  | Steel/Wrought Iron |  | Sacto. | Comment 1 page 1: date corrections made by clerk. The dates written in by foreman were incorrect as they are same dates as lk. #7820242. Comment 1 page 2: Abandoned 1 1/4" stub at main to stop leak here.
52 | 79-20237-1 |  |  | 0.75 | Other |  | Other |  | Cap on drip | DAMAGE BY OUTSIDE FORCES | CAP ON DRIP | 1979-02-01 | 1979-02-01 | REPLACE PIPE AND/OR SERVICE | Replaced cap | Steel/Wrought Iron |  | Sacto city | comment 1 page 2: Repaired leaking drip cap in lawn at edge of gutter by replacing cap.
52 | 80-60339-1 |  |  | 1 | Other |  | Body of Pipe |  | DRIP | Damage by outside Forces |  | 1980-08-15 | 1980-08-15 | Other |  | Steel/Wrought Iron |  |  | Abandoned 1" drip below ground level (caped) to make temp. repair here!
52 |  |  |  | 4 | Other | [6 empty] | 1980-08-19 | 1980-08-19 | Other |  | Steel/Wrought Iron |  | Sacto City, Inc. | Installed a 1 1/4" PGE + abandoned old drip at 4" g main
|  |  |  | 4 | [14 empty] | Inst 1/2 plastic hp svs c/o
52 | 93-20108-1 |  |  | 4 |  |  | Body of Pipe |  |  | Corrosion |  | 1993-02-24 |  | OTHER |  |  |  | Sacramento
52 | 82-60117-1 |  |  | 1 | Other |  | BODY OF PIPE |  |  | DAMAGE BY OUTSIDE FORCES |  | 1982-04-14 | 1982-04-14 | Other |  | Steel/Wrought Iron |  | Sacto. city inc. | Comment 1 page 2: abandoned 1" drip at main.
52 | 82-60187-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Corrosion |  | 1982-11-02 | 1982-11-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Sacto. | Removed 1 1/4" drip leaking
| 08-21114- |  |  | 10 | Transmission |  | Valves | Unknown | VALVE | Unknown | [5 empty] | Steel/Wrought Iron |  | Sacramento | Greased & operated valve. No gas odor found - no bubble present w/ soapy water. Ground in valve casing is white & stinky
52 | 72-40083-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  | 1972-04-03 | 1972-04-12 | OTHER |  | Steel/Wrought Iron |  | Sacto
52 |  |  |  | 16 | Distribution Main > 60 PSIG | [6 empty] | 1979-03-24 |  |  |  | Steel/Wrought Iron |  | Sacramento
52 |  |  |  | 06.00 + 10" mains | Distribution Main > 60 PSIG | [6 empty] | 1981-04-08 |  |  |  | Steel/Wrought Iron |  |  | Mains on side's of DryCreek rd share location both
6 |  |  |  | 10 | Distribution Main > 60 PSIG | [6 empty] | 1982-05-17 |  |  |  | Steel/Wrought Iron |  |  | Raised 10" feeder main to 6" storm drain. Exposed 29' 22'
52 |  |  |  | 10 | Distribution Main > 60 PSIG | [6 empty] | 1974-02-13 |  |  |  | Steel/Wrought Iron
52 |  |  |  | 1000 | [7 empty] | 1973-12-06 |  |  |  | Steel/Wrought Iron |  | Sacto
52 |  |  |  | 10 | Distribution Main > 60 PSIG | [10 empty] | Steel/Wrought Iron |  | Sacto
52 |  |  |  | 6 | Distribution Main > 60 PSIG | [6 empty] | 1971-12-23 |  |  |  | Steel/Wrought Iron
52 |  |  |  | 10 | Distribution Main > 60 PSIG | [6 empty] | 1970-07-05 |  |  |  | Steel/Wrought Iron |  | Sacto
52 |  |  |  | 10 | Distribution Main > 60 PSIG | [6 empty] | 1970-07-05 |  |  |  | Steel/Wrought Iron |  | Sacto
52 |  |  |  | 6 | Distribution Main > 60 PSIG | [6 empty] | 1972-07-03 |  |  |  | Steel/Wrought Iron |  | Sacto
52 |  |  |  | 6 | Distribution Main > 60 PSIG | [6 empty] | 1972-07-03 |  |  |  | Steel/Wrought Iron |  | Sacto
52 |  |  |  | 10 | Distribution Main > 60 PSIG | [6 empty] | 1971-12-23 |  |  |  | Steel/Wrought Iron |  | Sacto
52 | 77-20293-1 |  |  |  | Other |  | Body of Pipe |  |  | Corrosion |  | 1977-05-17 | 1977-05-17 | Other |  | Steel/Wrought Iron |  | Sacto city inc | Comment 1 page 1: Houseline leak not entered into computer. Comment 1 page 2: Found house line leaking! had serviceman shut gas off! Customer will repair!
| 99-60257- |  |  |  | Other |  | Body of Pipe |  |  | Digin |  | 1999-10-12 | 1999-10-12 | Patch Weld - Weld
52 | 83-40200-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  | 1983-11-04 | 1983-11-04 | Other |  | Steel/Wrought Iron |  | Sacto
| 05-60283- |  |  | 0.5 | Gathering |  | Body of Pipe |  |  | Digin |  | 2005-09-23 | 2005-09-23 | Service Partially Replaced |  | Other | TR 418 | Sacramento | Replaced 18" of 1/2" plastic pipe with two 1/2" pefection couplings
52 |  |  |  | 6 | Transmission | [6 empty] | 1975-10-01 |  |  |  | Steel/Wrought Iron |  | Sacto. Inc.
52 |  |  |  | 1.25 | Distribution Feeder Main | [6 empty] | 1984-11-21 |  |  |  | Steel/Wrought Iron |  | Sacto.
52 | 71-00183-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Corrosion |  | 1971-09-29 | 1972-09-28 | Other |  | Steel/Wrought Iron |  | Sacramento | Repairs made by abandoning 1 1/4" drip, removed old pipe and installed 1 1/4" plug in
52 | 78-60366-1 |  |  | 2 | Gathering |  | Fitting |  |  | Corrosion |  | 1978-02-25 | 1978-09-05 | Other | Cut drip off at main | Steel/Wrought Iron |  | Sacto. Inc. | Comment 1 page 2; After Bill Becker renew service at this address, A. Day still pick up gas readings under Garage, Becker could not locate drip connection, we dug out same bell hole, and dug around main, we found drip connection 8 inches south of service tee. Made permanent repair, cut drip cleaned rust of main. Wrapped main.
|  |  |  | 4 | Transmission | [13 empty] | Comment 1page 1; Inst 1/2 plastic svs.
52 |  |  |  | 6 | Distribution Main > 60 PSIG | [6 empty] | 1981-04-07 |  |  |  | Steel/Wrought Iron |  | N. Sacto
52 |  |  |  | 6 | Distribution Main > 60 PSIG | [6 empty] | 1981-04-07 |  |  |  | Steel/Wrought Iron |  | N. Sacto
52 |  |  |  | 6 | Service | [6 empty] | 1981-04-07 | [5 empty] | N. Sacto
52 |  |  |  | 6 | Distribution Main > 60 PSIG | [6 empty] | 1981-04-07 |  |  |  | Steel/Wrought Iron
52 |  |  |  | 6 | Distribution Main > 60 PSIG | [6 empty] | 1972-06-29 |  |  |  | Steel/Wrought Iron
[16 empty] | Steel/Wrought Iron |  |  | Inst 1/2 plastic
52 | 92-20369-1 |  |  | 6 | Distribution Main |  | Fitting |  |  | Corrosion |  | 1992-08-14 | 1993-06-23 | Other |  | Steel/Wrought Iron |  | Sacramento | Replaced gasket + cap 6" control fittings
52 | 93-20501-1 |  |  | 6 | Distribution Feeder Main |  | Fitting |  |  | CONSTRUCTION DEFECT |  | 1993-05-26 | 1993-06-23 | OTHER | REPLACE GASKET + CAP CONTROL FITTING | Steel/Wrought Iron |  | Sacramento | Comment 1 page 1: replaced gasket and cap on 6" control fitting
52 | 82-40152-1 |  |  | 0.75 | Other |  | Valves |  |  | Material Failure |  | 1982-11-23 | 1982-11-23 | Other |  | Steel/Wrought Iron |  | Sacto City inc 37A1 | Comment 1 page 1: GM4233102 to replace old main!; Comment 2 page 1: 3/4" drip riser valve on 2" main - not a service;
52 | 71-00293-1 |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1971-11-10 | 1972-03-27 | Other |  | Steel/Wrought Iron |  | Sacto. Sub | Comment 1 page 2: Repoved cap + welded 3/4" stub sut to repair leak here
52 | 80-60459-1 |  |  | 0.75 | Service |  | Physical/Mechanical Joint |  |  | Damage by outside Forces |  | 1980-10-27 | 1980-10-27 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | North Highlands TBM35D6 | Comment 1page 2: Made temp. repairs by shutting off H.p. mueller valve tee at inlet to high to high bc. 29 oct 80 replaced 10' of 3/4" stl. svc. Svc pipe tested weld inspected weld by T. R. Smith
6 | 83-60182-1 |  |  | 2 | Distribution Main |  | Other |  |  | Damage by outside Forces |  | 1983-08-02 | 1983-08-02 | Replace Pipe and/or Service |  | Other Plastic
52 |  |  |  | 10 | Distribution Main > 60 PSIG | [6 empty] | 1972-06-29 |  |  |  | Steel/Wrought Iron |  | Sacto
52 |  |  |  | 6 | Distribution Main > 60 PSIG | [10 empty] | Steel/Wrought Iron
52 |  |  |  | 10 | Distribution Main > 60 PSIG | [6 empty] | 1922-06-29 | [5 empty] | Sacto
52 |  |  |  | 6 | Distribution Main > 60 PSIG | [6 empty] | 1972-06-30 |  |  |  | Steel/Wrought Iron |  | Sacto
52 |  |  |  | 10 | Distribution Main > 60 PSIG | [6 empty] | 1972-12-26 |  |  |  | Steel/Wrought Iron
52 |  |  |  | 6 | Distribution Main > 60 PSIG | [6 empty] | 1972-06-30 |  |  |  | Steel/Wrought Iron |  | Sacto
| 00-20570- | 65187 |  | 6.25 | Transmission |  | Other Welds |  |  | Construction Defect |  | 2000-12-05 | 2000-12-06 | Other | REWORK GAUGE TAP | Steel/Wrought Iron |  | Sac | Comment 1 page 1: Gauge tap was to high causing frame and tp push down on 3/4" pipe (broke at bottom weld)
52 |  |  |  | 10 | Distribution Main > 60 PSIG | [6 empty] | 1973-12-13
|  |  |  | 2 | [11 empty] | Aldyl A (Tan or Gray)
6 | 83-60179-1 |  |  | 0.5 | Service |  | Other |  |  | Damage by outside Forces |  | 1983-07-28 | 1983-07-28 | Replace Pipe and/or Service |  | Other Plastic |  | Sacto
52 | 72-20068-1 |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1972-02-23 | 1972-04-05 | Other |  | Steel/Wrought Iron |  | Sacto. City. | Comment 1 page 2: Found no leak c/o at spout near house with leak was under houst at houseline = repaired by 4-5-72.
52 | 77-20470-1 |  |  | 2 | Other |  | OTHER |  |  | Other |  | 1977-08-11 | 1977-09-02 | Other |  | Steel/Wrought Iron |  | North, Sacramento, Calfornia | abandon 2" main due to be used as state highway.
52 |  |  |  | 12 | Transmission | [6 empty] | 1972-02-24 |  |  |  | Steel/Wrought Iron
|  |  |  | 12 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party |  | 2001-05-10 | 2001-05-10 | Other | REWRAPED PIPE | Steel/Wrought Iron |  | Sac | Comment 1page 1under "LOCATION REMARKS": Scratched feeder main + damaged wrap - called super Jerry Robertson; Comment 2 page 1 under "REPAIR REMARKS": Re-wrapped pipe; Comment 1 page 2 under "Comments": Rewraped trans. Line# 119.
52 | 72-60074-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-05-03 | 1972-05-04 | Patch Welded |  | Steel/Wrought Iron |  |  | Comment 1 page 1: Deleted. trans. lline #119 leak. original form A forward to division.
00-20400-
52 |  |  |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron
52 |  |  |  | 12 | Distribution Main > 60 PSIG | [6 empty] | 1976-09-29 |  |  |  | Steel/Wrought Iron |  | Sacto
6 |  |  |  | 6 | Transmission |  |  |  |  | Digin |  | 1987-08-19 | 1987-09-15 |  |  | Steel/Wrought Iron |  |  | Comment 1 page 2: Sleeve was welded on and welds were x-rayed
|  | 119E |  |  | Transmission | [10 empty] | Steel/Wrought Iron |  | Sacramento | Boned 3 mains and brought up into ETS on line.
52 |  |  |  | 12 | Distribution Main > 60 PSIG
52 |  |  |  | 8 | Distribution Main > 60 PSIG | [6 empty] | 1981-04-02 | [5 empty] | N. Sacto
52 | 72-20056-1 |  |  | 8 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | Corrosion |  | 1972-02-18 | 1972-05-06 | PATCH WELDED |  | Steel/Wrought Iron |  | Sacto.
52 |  |  |  | 8 | Distribution Main > 60 PSIG | [6 empty] | 1973-11-19 |  |  |  | Steel/Wrought Iron |  | Sacto
52 | 72-20253-1 |  |  | 4 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | Corrosion |  | 1972-08-18 | 1972-10-06 | PATCH WELDED |  |  |  | Sacto. Inc. | Comment 1 page 2: It was necessary to arc weld a steel patch over 2 electrolysis leaks here. Also installed a 9lb anode here.
|  |  |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron
52 |  |  |  | 8 | Transmission |  |  |  | NONE |  | NONE | 1972-05-10 | 1972-05-11 |  | NONE | Steel/Wrought Iron |  | Sacto.
52 | 72-00113-1 |  |  | 4 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | Corrosion |  | 1972-08-04 | 1972-08-08 | Patch Welded |  | Steel/Wrought Iron |  | N. Sacto | ARC WELDED 4" X 4" PATCH OVER ELECTROLYSIS LEAK ON #4 HP FEEDER MAIN HERE. INSTALLED 9 LB MAGNESIUM ANODE HERE. Comment 1 page 2: Send this report to Mike Windsor.
52 |  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1984-02-09 |  |  |  | Steel/Wrought Iron |  | Sacti, City inc 34E3
52 | 71-00251- |  |  | 2 |  |  | VALVES |  |  | OTHER |  | 1971-10-13 | 1971-10-14 | OTHER |  |  |  | Sacto City inc. | Comment 1 page 2: Stopped leak at 2" nord valve by greasing! This valve is buried!
[18 empty] | Sacramento | Comment 1 page 1: Never saw pipe - only wrap!
52 | 74-20158-1 |  |  | 8 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | Corrosion |  | 1974-06-03 | 1974-06-07 | Patch Welded |  | Steel/Wrought Iron |  | N. Sacto
52 | 73-20074-1 |  |  | 4 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | Corrosion |  | 1973-02-27 | 1973-03-02 | PATCH WELDED |  | Steel/Wrought Iron |  | Sacto City inc. | Comment 1 page 2: Arc welded a 6" x 4" steel patch over pitts + leak here. Installed a 9LB anode here.
52 | 78-60439-1 |  |  | 4 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | Corrosion |  | 1978-10-17 | 1978-10-17 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron
52 |  |  |  | 4 | Distribution Main > 60 PSIG | [6 empty] | 1978-10-18 |  |  |  | Steel/Wrought Iron |  | North Sacto
52 | 72-00117-1 |  |  | 4 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | Corrosion |  | 1972-08-04 | 1972-08-08 | Patch Welded |  | Steel/Wrought Iron |  | No. Sacto.
52 | 72-20243-1 |  |  | 4 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | Corrosion |  | 1972-09-06 | 1972-09-21 | Patch Welded |  | Steel/Wrought Iron |  | Sacto. City inc.
52 |  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Comment 1 page 2: Had to insulate 4" + 8" main at point of contact here.
52 |  |  |  | 8 | Distribution Main > 60 PSIG | [6 empty] | 1972-07-26 |  |  |  | Steel/Wrought Iron |  | No. Sacto.
52 | 71-00118- |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  |  |  | OTHER |  | Steel/Wrought Iron |  | Sacto City | Comment 1 page 2: Leak not found at this point, leak was in the intersection of Boxwoods st. readings related to leak #71-00153 - 9-20-71.
52 |  |  |  | 6 | Transmission | [6 empty] | 1972-07-20 | 1972-07-20 | Other |  | Steel/Wrought Iron |  | Sacto | Comment 1 page 2: water serv. contract
52 | 77-60049-1 |  |  | 1 | Other |  | Fitting |  |  | Material Failure |  | 1977-02-17 | 1977-02-17 | Other |  | Steel/Wrought Iron |  | Sacto. city inc. | Comment 1 page 2: Abandoned old 1" drip! Retightened leaking fittings to stop leak + caped!
52 | 73-40179-1 |  |  | 4 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | Corrosion |  | 1973-04-30 | 1973-05-02 | Patch Welded |  | Steel/Wrought Iron |  | Sacto. city inc. | Comment 1 page 2: Arc welded 2 steel patches (3 1/2" x 5" + 4" x 5") over leak + pitts here.
| 09-93436-1 | DFM |  | 16 | Transmission |  | Valves |  |  | Unknown |  | 2009-12-18 | 2009-12-22 | Other | Greased & operated valve | Steel/Wrought Iron |  | Sacramento | Comment 1 page 2 under "Repair Remarks":Greased & Operated Valve; Comment 1page 3 under "Comments": Valve D-55 located in vault. Greased and operated. No leak after repair.
52 |  |  |  | 1.25 | Other |  | Body of Pipe |  |  | Corrosion |  | 1977-09-02 | 1977-09-02 | Clamp |  | Steel/Wrought Iron |  | Sacto. Sub uninc | Comment 1 page 2 under "Other pertinent information": Used 2-1 1/4" clamp to make temp repairs only!
52 | 74-40302-1 |  |  |  | Other | [6 empty] | 1974-10-09 | 1974-10-09 | Other |  | Other |  | Sacto | Comment 1 page 2: Found leak on tube to pilot control on boiler shut
|  |  |  | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Comment 1 page 2: Performed standby inspection from T.O.P only. Potholed by Gdm construction.
| 01-21069-1 | [10 empty] | 2001-06-11 | [5 empty] | Sacramento
52 | 71-00019-1 |  |  | 8 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | Corrosion |  | 1971-05-13 | 1971-05-18 | Patch Welded |  | Steel/Wrought Iron
6 | 83-60018-1 |  |  | 2 | Distribution Main |  | Valves |  |  | Material Failure |  | 1983-02-09 | 1983-02-09 | Other |  | Steel/Wrought Iron
52 | 82-40170- |  |  | 6 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | Corrosion |  | 1982-10-20 | 1983-02-23 | Patch Welded |  | Steel/Wrought Iron |  | Sacti City inc. | MADE TEMP REPAIRS (CLAMPED) 10-20-1982. NEG JR. CHAMBERED; ARC WELDED AT 6" X 14" STEEL PATCH WITH 1" SERVICE VALVE HERE. ARC WELDED A 6" X 27" STEEL PATCH WITH 1" SAW A-VALVE HERE. INSTALLED A ETS 47' FROM PL...
52 | 82-40- |  |  | 6 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | Corrosion |  | 1982-10-20 | 1982-10-20 | Clamp |  | Steel/Wrought Iron |  | Sacto. city inc | Comment 1 page 2: 6-11-84 1901 Del Paso Blvd. 1000ppm at base of riser & 1905 Del Paso Blvd. 1000 ppn below ro valve
52 |  |  |  | 6 | Distribution Main > 60 PSIG | [9 empty] | INST. ETS H | Steel/Wrought Iron |  | Del Paso Blvd N/Sacto 34D5
52 | 77-20099-1 |  |  | 0.75 | Other |  | Other |  |  | Material Failure |  | 1977-02-23 | 1977-02-23 | Other |  | Steel/Wrought Iron |  | Sacto City inc. | Comment 1 page 1: Called service dept. to clock meter + found house line to 2311 Cambridge leaking badly cement! Shut gas off + customer notified!
52 | 76-00053-1 |  |  | 6 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | Corrosion |  | 1976-06-16 | 1976-06-21 | Patch Welded |  | Steel/Wrought Iron |  | No Sacto
52 | 72-20251-1 |  |  | 4 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | Corrosion |  | 1972-10-02 | 1972-10-04 | Patch Welded |  | Steel/Wrought Iron |  | Sacto. City inc. | Comment 1 page 2: Had to arc weld a 5" x 6"steel patch over leak + 2 pitts here. Also installed a 9lb anode here.
52 | 74-60312-1 |  |  | 3 | Distribution Main > 60 PSIG |  | Valves |  |  | Other |  | 1974-08-05 | 1974-08-06 | Other |  | Steel/Wrought Iron |  | Sacto City | Comment 1 page 2: Had to grease valve in order to stop leaks here.
52 | 75-20016-1 |  |  | 4 | Distribution Main > 60 PSIG |  | Valves |  |  | Material Failure |  | 1975-01-06 | 1975-02-20 | Other |  | Steel/Wrought Iron |  |  | Comment 1 page 2: Had to grease 4" of curb. Valve to stop leak here.
52 | 75-60139-1 |  |  | 4 | Distribution Main > 60 PSIG |  | Valves |  |  | Material Failure |  | 1975-06-09 | 1975-06-16 | Other |  | Steel/Wrought Iron |  | Sacto City inc. | Comment 1 page 2: Greased valve to stop leak here. Could not remove grease fitting in order to install extension fitting.
52 | 79-60509-1 |  |  | 8 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-10-16 | 1979-10-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Sacto
52 | 76-20190-1 |  |  | 2 | Other |  | Body of Pipe |  |  | Corrosion |  | 1976-02-02 | 1976-02-03 | Other |  | Steel/Wrought Iron |  | Sacramento | Comment 1 page 2: Had to abandon 2" hy dw steel stub at 6" feeder main to stop leaks here.
52 | 79-40063-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1979-02-27 | 1979-02-27 | Clamp |  | Steel/Wrought Iron |  | Sacto | Comment 1 page 2: Found rock against pipe with deep corrosion pit blowing gas Repaired with 2" skinner clamp + wrapped gas main.
52 | 80-30206-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1980-05-28 | 1981-06-08 | Clamp |  | Steel/Wrought Iron
52 | 75-21085-1 |  |  | 0.75 | Other | [6 empty] | 1975-05-29 |  | OTHER |  |  |  | Sacto Sub uninc | comment 1 page 2: Leak surveyed service with flame ionization indicator (A. day) + found 3/4" lg. Service not leaking here! Had P.G.&E service man (Mr. Tomes) clock meter + found a 4 qu. ft hr leak in house line. Shut customer off. Customer will repair + call co. for relite.
52 | 81-60224-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1981-09-15 | 1981-09-15 | Replace Pipe and/or Service |  | Other Plastic |  | Sacto TBM3706
52 |  |  |  | 8 | Distribution Main > 60 PSIG | [10 empty] | Steel/Wrought Iron |  | Sacto uninc
52 |  |  |  | 1.25 | Distribution Main > 60 PSIG | [12 empty] | Sacto uninc
52 | 78-40042-1 |  |  | 1.25 | Distribution Main |  | Physical/Mechanical Joint |  |  | CONSTRUCTION DEFECT |  | 1978-01-25 | 1978-01-25 | Clamp |  | Other Plastic |  | Sacto | Comment 1 page 2: Plastic sleeve was not properly installed on service tee. Cause break between service tee & 1/2" plastic . Permanent repairs were made by replacing tee & putting proper sleeve in place.
52 | 76-60142-1 |  |  | 1 | Other |  | Drip |  |  | Corrosion |  | 1976-04-29 | 1976-04-30 | Other |  | Steel/Wrought Iron |  | Sacto | Comment 1 page 2: Screw joint leaking on drip pip, and corrosion leaks. Permanent repairs made by abandoning drip pipe; Comment 2 page 2: See leak report # 75-21600-1.
52 |  |  |  | 1 | Other | [6 empty] | 1975-08-20 |  |  |  | Steel/Wrought Iron |  | Sacto
|  |  |  | 8.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | Sacramento
Comment 1 page 2: I inst a ets 3' s/o orange grove blvd on 8" stl main.
52 | 82-60014-1 |  |  | 0.5 | Other | Pig Tail | Body of Pipe |  |  | Damage by outside Forces |  | 1982-02-03 | 1982-02-03 | Replace Pipe and/or Service |  | Other Plastic |  | Sacto. Sub uninc 36E6 | Comment 1 page 2: Used one 1/2" amp fit bead end to repair neat here.
52 |  |  |  | 2 | Distribution Main | [6 empty] | 1973-06-22 | 1973-06-22 |  |  | Steel/Wrought Iron |  | Carm
52 | 79-60106-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-04-04 | 1979-04-04 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Sacto. subn uninc 39A6 | Comment 1 page 2: Had to plug old abandoned 3/4" Mueller service tee + weld damaged end up to replace leak here.
| 02-60070-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 2002-03-13 | 2002-03-13 | SERVICE PARTIALLY REPLACED |  | Aldyl A (Tan or Gray) |  | Calm | Installed 6' of 1/2" plastic TR418 pipe and 2 ea. 1/2" perfection coupling; Inspection repair
52 | 76-60010-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-01-13 | 1976-01-13 | Patch Welded |  | Steel/Wrought Iron |  | Carmichael | Weld 12" x 12" patch and sav. valve.
|  |  |  | 2 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Carmichael
52 | 79-60378-1 |  |  | 0.5 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-08-29 | 1979-08-29 | REPLACE PIPE AND/OR SERVICE |  | Other Plastic |  | Sacramento | Replaced 1/2" PL dead...Coupling head
52 |  |  |  | 2 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Carmichael
52 | 79-40048-1 |  |  | 1.25 | Other |  | Valves |  | OFF RISER | Damage by outside Forces |  | 1979-02-20 | 1979-02-21 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Carmichael | Damage riser by unknown. Broke swidge nipple off riser. Replaced 1 1/4" riser ... Meter by Metal riser 1 1/4
52 | 76-20913-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1976-11-04 | 1976-11-04 | Other |  | Steel/Wrought Iron |  | Sacramento | Houseline, not entered into computer, see reverse side; ...
| 01-21068-1 | [10 empty] | 2001-06-08 | [5 empty] | Sacramento
52 | 79-40219-1 |  |  | 2 | Other |  | Body of Pipe |  |  | Corrosion |  | 1979-08-16 | 1979-08-20 | Other | Made temp. repairs to leaking 2" house lines & notifyed maintenance man. Plumber will repair soon. | Steel/Wrought Iron |  | Sacramento | See reverse side; Made temp repair to leaking 2" houseline and notifyed maintenance...plumber will repair ...; Found 2" LP houseline leaking under...service main
52 | 78-60267-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-07-17 | 1978-07-17 | REPLACE PIPE AND/OR SERVICE |  | Other Plastic |  | Sacramento | So #775528 Main 2"
52 | 96-20392-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1996-09-20 | 2001-09-05 | Other |  | Steel/Wrought Iron |  |  | Greased Valve and doped; T&R Greased and operated to repair leak!
52 |  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1973-12-31 |  |  |  | Steel/Wrought Iron |  | Sacramento
52 |  |  |  | 4 | Other | [10 empty] | Steel/Wrought Iron
52 | 78-40311-1 |  |  | 2 | Other |  | Valves |  |  | Damage by outside Forces |  | 1978-08-04 | 1978-08-07 | Other | Cut off | Steel/Wrought Iron |  | Fair Oaks | Made temp repair 08/04/78; Replaced service 4/19/79 see G.S.R. for details; Found corrosion leak were storm drain went through and damaged 3/4 serv.
52 | 77-60442-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-10-10 | 1977-10-10 | Other |  | Steel/Wrought Iron |  | Carmichael
| 02-20033- |  |  | 0.75 | Service |  | Physical/Mechanical Joint |  |  | Unknown |  | 2002-02-07 |  |  |  | Steel/Wrought Iron |  | Rancho Cordova | Escavated fire valve, valve leaking; needs to be cut-out and replaced.
| 03-20265- |  |  | 0.75 | Transmission |  | Valves |  |  | Material Failure |  | 2003-10-30 | 2003-10-30 | Other | REBUILT THE VALVE | Steel/Wrought Iron |  | Sacramento | Rebuilt the valve; (Rebuilt the valve) Soap test valve.
52 | 79-60562-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-11-16 | 1979-11-16 | REPLACE PIPE AND/OR SERVICE |  | Other Plastic |  | Faustino | Made permanent repair, To 1/14" main with 4' of pipe and 2 1/4" AMP. ...
52 |  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1973-09-19 |  |  |  | Steel/Wrought Iron |  | Sacramento
52 | 83-20151-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1983-09-09 | 1983-09-09 | REPLACE PIPE AND/OR SERVICE |  | Other Plastic |  | Sacramento
52 | 79-60234-1 |  |  | 0.5 | Other |  | Other |  |  | Damage by outside Forces |  | 1979-06-19 | 1979-06-19 | Other | Fusion Connection | Other Plastic |  | Sacramento | 1/2" blow off on end of 2" PL. Main (Plate Shows 1 1/8" PL. Main); ...
52 | 79-20738-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  | 1978-04-19 | 1979-06-18 | Other |  | Steel/Wrought Iron |  | Sacramento | Drip line; Permanent repair made by abandoning 1" drip., ...4" main in bad condition....
52 | 74-21613-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-07-18 | 1974-10-17 | OTHER |  | Steel/Wrought Iron |  | Sacramento
52 | 75-60382-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  | 1975-11-07 | 1975-11-07 | Other |  | Steel/Wrought Iron |  | Sactramento | Drip line
52 | 73-60112-1 |  |  | 0.75 | Other |  | Valves |  |  | Damage by outside Forces |  | 1973-04-25 | 1973-04-25 | Other |  | Steel/Wrought Iron |  | Sacramento | All Neg. Thompson; 3/4" Nord valve broken off 3/4" HP drip riser, squeezed off riser, this 3/4" HP drip will be cut off of main at a later date
6 |  |  |  | 0.75 | Service |  | BODY OF PIPE |  |  | CORROSION |  | 1981-10-14 | 1981-10-14 | OTHER |  | Steel/Wrought Iron |  | Sacramento | For file only, House line leaking- PGE responsibility
52 | 76-40098-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-03-20 | 1976-03-28 | Other |  | Steel/Wrought Iron |  | Sacramento
|  |  |  | 12 | Distribution Feeder Main | [6 empty] | 2004-05-28 | 2004-05-28 |  | Wrapped 12" feeder main | Steel/Wrought Iron |  | Rancho Cordova | Wrapped 12" feeder main
52 |  |  |  | 16 | Transmission | [6 empty] | 1973-10-03 |  |  |  | Steel/Wrought Iron |  | Sacramento | W16" HP Transmission main inspection hole.
52 |  |  |  | 10 | Distribution Feeder Main | [6 empty] | 1978-11-10 |  | Other |  | Steel/Wrought Iron |  | Sacramento | Used 1 Gal. of ... TAR to cover ... to 10' HP...Main...
52 |  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron
| 08-21167-1 |  |  | 1.25 | Transmission |  | Other |  | Grease fitting | Unknown |  | 2008-06-17 | 2008-07-07 | OTHER | Plugged grease fitting | Steel/Wrought Iron |  | Sacramento | 0% gas 0% lel when done fixing leak. Grease fitting on ball valve (V-3) body leakig took off- Plugged leak w/ 1/4" metric w/ plug
52 | 73-00054-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-06-22 | 1973-10-09 | Clamp |  | Steel/Wrought Iron |  | Sacramento | All Neg., Thompson; Installed 4" x 6" skinner seal clamp over deep eleclrolysis pitted area on 4" HP main here.; Installed 4" x 6" skinner seal clanp over eleclrolysis leak on 4"HP main here. Leak at 2 o'clock
52 |  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Sacramento | Exposed 6" main, while checking for leak on 10" main; Checked condition of main and wrap at this location. 6" main over 10" main see leak report on 10" main.
52 | 73-20235-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-07-21 | 1973-04-11 | Patch Welded |  | Steel/Wrought Iron |  | Sacramento | Second leak No.: 73-20235-1; All Neg. Thompson; Found electrolysis leak at 10" gas main, made permanent repairs. Welded 2 7" x 10" patch over leak.; Welded 2 7" x 10" patch over leak
52 | 73-20235-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-07-21 | 1973-04-11 | Patch Welded |  | Steel/Wrought Iron
52 | 72-40138-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-06-29 | 1972-06-30 | Patch Welded |  | Steel/Wrought Iron |  | Sacramento | All neg., Thompson; found electrolysis leak...10" feeder main. Made permanent repairs, wleded 2 5" x 5" patch over....main.; Permanent 6" patch over ... leak, installed area...main
52 |  |  |  | 0.5 | Transmission |  | Other |  |  | Other |  |  |  | Other |  | Other Plastic |  | Sacramento | Made P/L cut off 6' in property. Service should have been cut off.
52 | 75-20516-1 |  |  | 0.5 | Other |  | Fitting |  |  | Other | Curb frame and cover setting on 1/2" plastic, PL. Broken near tree | 1975-09-25 | 1975-10-08 | Other |  | Other Plastic |  | Sacramento | Found 2 1/2" self tap tee, 1/2" plastic connection for by pass, 4" from Nord curb valve. Frame and cover setting on top of 1/2" PL. Line, 1/2" plastic blowing, shut off plug in tee was not completing shut off, made permanent repair shut tee off, installed dead end on PL. and set frame cover with concrete slab under curb valve.; This leak should have been reported 1st grade 1 leak for the record purpose.
| 03-20302- |  |  | 10.75 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2003-10-08 | 2003-12-09 | WELDED SLEEVE/CAN - WELD |  | Steel/Wrought Iron |  | Sacramento | Installed full encirclement sleeve over corrosion leak; repair location. installed full encirclement sleeve. 10.75' ID. steel ASTM A-516 Grade to 35,000 SMYS .500 W.T. os per GS & E A-60
52 | 74-60010-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-01-22 | 1974-01-23 | Patch Welded |  | Steel/Wrought Iron |  | Sacramento | Leak at 6 o'clock. Arc welded 8" x 8" patch over electrolysis leak and bad spots on 10" HP feeder main. Installed 9lb magnesium anode here.
52 | 79-00023-1 |  |  | 6 | Other |  | Other |  |  | Other |  | 1977-05-08 | 1980-02-07 | Other |  | Steel/Wrought Iron |  | Sacramento | Repaired leak in 6" gas filter distribution Reg. Station.
52 |  |  |  | 10 | Distribution Feeder Main | [6 empty] | 1975-10-04 |  |  |  | Steel/Wrought Iron |  | Sacramento | Cleared contact with water main.
| 03-20302- |  |  | 10.75 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2003-12-08 | 2003-12-09 | WELDED SLEEVE/CAN - WELD |  | Steel/Wrought Iron |  | Sacramento | Installed full encirclement sleeve over corrosion leak; Repair location, installed full encirclement sleeve 10.75" Ib. Steel ASTM A-516 grade to 35,000 SMYS .500 W.T. os per GS&S A-60
| 03-20302- |  |  | 10.75 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2003-12-08 | 2003-12-09 | WELDED SLEEVE/CAN - WELD |  | Steel/Wrought Iron |  | Sacramento | Installed full encirclement sleeve over corrosion leak. Repair location, Installed full encirclement sleeve. 10.75" ID. Steel ASTM A-516 grade to 35,000 SMYS .500 W.T. os per GS&S A-60
52 | 80-60322-1 |  |  | 0.5 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-08-11 | 1980-08-11 | REPLACE PIPE AND/OR SERVICE |  | Other Plastic |  | Sacramento | Clear crips piazza; Leak...Exposed by...
52 |  |  |  | 10 | Distribution Feeder Main | [6 empty] | 1974-05-08 |  |  |  | Steel/Wrought Iron
| 03-21081-1 | [10 empty] | 2003-07-18 | [6 empty] | Delete leak
52 |  |  |  | 10 | Distribution Feeder Main | [6 empty] | 1974-04-02 |  |  |  | Steel/Wrought Iron
[12 empty] | 1976-01-06 |  |  |  | Steel/Wrought Iron
52 | 78-20645-1 |  |  | 0.5 | Other |  | Body of Pipe |  |  | Corrosion |  | 1978-06-02 | 1979-04-12 | Other |  | Steel/Wrought Iron |  | Sacramento | Found leak in gas line svc. line, ... line
52 | 79-20602-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-05-08 | 1979-06-04 | Clamp |  | Steel/Wrought Iron |  | Sacramento | Found corrosion P.T. leaking on bottom of 3/4" HP Steel gas service. Installed skinner clamp and wrapped service pipe; found corrosion pit leaking on bottom of 3/4" HP Steel gas service pipe; Found corrosion pit leaking on bottom of 3/4" HP steel gas service.
52 |  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1974-01-07 |  |  |  | Steel/Wrought Iron |  | Sacramento
52 |  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1974-01-07 |  |  |  | Steel/Wrought Iron |  | Sacramento
| 03-21082-1 | [10 empty] | 2003-07-18 | [6 empty] | Delete leak
| 03-21083-1 | 108 |  | 24 | Transmission |  | Valves |  |  | Unknown |  | 2003-07-18 | 2005-07-12 | Other | Greased valve #6 | Steel/Wrought Iron |  | Sacramento | Greased valve #6 on line 108 11:30; Soap test: Pete Velasquez 7/12/05
| 03-21083-1 | [10 empty] | 2003-07-18 | [5 empty] | Sacramento
| 02-21062-1 |  |  | 24 | Transmission |  | Valves |  |  | Other | Greased Valve | 2002-05-29 | 2003-05-13 | Other | GREASED VALVE | Steel/Wrought Iron |  | Sacramento | Greased Valve; Soap test valve 5-13-03 Joe Dona
| 08-21186-1 | 108 |  | 24 | Transmission |  | Valves |  |  | Unknown |  | 2008-06-18 | 2008-09-16 | Other | Greased Valve | Steel/Wrought Iron |  | Sacramento | Greased valve
| 08-21187-1 | 108 |  | 24 | Transmission |  | Valves |  |  | Construction Defect |  | 2008-06-18 | 2009-08-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Sacramento | Tighten blow off cap; Found blow off/ Gauge taps on valve B004- Found 1 to have Its cap leaking
52 | 91-20104-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1991-03-29 | 1991-03-29 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Sacramento | Installed 2" Sav-A-Valve on Pin- Hole corrosion leak
| 92- 279-1 |  |  | 2 | [5 empty] | Construction Defect |  | 1992-05-07 | 1992-05-07 | Other |  | Other Plastic
52 | 80-60014-1 |  |  | 2 | Distribution Main |  | Other |  |  | Damage by outside Forces |  | 1980-01-22 | 1980-01-22 | REPLACE PIPE AND/OR SERVICE |  | Other Plastic
52 | 91-60198-1 |  |  | 0.5 | Transmission |  | Physical/Mechanical Joint |  |  | Damage by outside Forces |  | 1991-05-25 | 1991-05-25 | Replace Pipe |  | Other Plastic |  | Sacramento | Repair 1/2" PL SVC
52 | 79-20737-1 | 108 |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-06-22 | 1979-06-22 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Sacramento | For Record Puposes only.; Found electrolysis leak on a 16" transmission 108 main, made permanent repair, welded a 16" Sleeve 12" wide around gas main, by G.C. Welders
52 | 90-60213-1 |  |  | 2 | Distribution Main |  | Other |  |  | Digin |  | 1990-07-20 | 1990-07-20 | OTHER |  | Other | TR-418 | Sacramento | Repaired 2" HR Plastic main with ... coupling
52 | 90-60221-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1990-07-27 | 1990-07-27 | Replace Pipe |  | Other | TR-418 | Sacramento | Repair 1/2 PL service, 2 couplings and 16" PL pipe
52 |  |  |  | 10 | Distribution Feeder Main | [6 empty] | 1979-12-03 |  |  |  | Steel/Wrought Iron |  | Sacramento | Hard pan; Linde Tap Feeder
52 |  |  |  | 10 | Distribution Feeder Main | [6 empty] | 1979-12-03 |  |  |  | Steel/Wrought Iron |  | Sacramento | Limde Tap Feeder
52 |  |  |  | 10 | Distribution Feeder Main | [6 empty] | 1979-12-03 |  |  |  | Steel/Wrought Iron |  | Sacramento | Limde tap feeter
52 | 75-40190-1 |  |  | 1 | Gathering |  | DRIP |  |  | Other | Leak at threads on cap | 1975-06-19 | 1975-09-09 | Other |  | Steel/Wrought Iron |  | Sacramento | Lowered 1" drip riser, Re ... cap, installed frame and cover, on South P/L
52 |  |  |  | 2 | [7 empty] | 1972-02-08 |  |  |  | Steel/Wrought Iron |  | Sacramento | Installed 2 magnisum anodes on 2" main
52 | 81-40154-1 |  |  | 2 | Distribution Main |  | OTHER |  | COMPRESSOR COMPONENTS | Construction Defect |  | 1981-11-02 | 1981-11-02 | Other |  | Other Plastic |  | Sacramento | Leak at service tee compression nut was loose
52 |  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1974-03-21 |  |  |  | Steel/Wrought Iron |  | Sacramento
52 |  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1974-03-20 |  |  |  | Steel/Wrought Iron
52 | 86-60 |  |  | 12 | Distribution Feeder Main |  | OTHER |  |  | OTHER |  | 1986-04-28 | 1986-04-28 |  |  | Other | Casing
52 | 77-20392-1 |  |  | 1.25 | Other |  | Tap Connection |  |  | Material Failure |  | 1977-07-06 | 1977-09-13 | Other |  | Steel/Wrought Iron |  | Sacramentio | Permanent repair made by tightening caps and stopping leaking
52 | 75-20677-1 |  |  | 0.75 | Other |  | Other |  |  | Material Failure |  | 1975-12-11 | 1976-04-01 | Other |  | Steel/Wrought Iron |  | Sacramento
52 | 75-21402-1 |  |  |  | Distribution Feeder Main | [6 empty] | 1975-07-17 | [5 empty] | Sacramento
52 | 77-60255-1 |  |  | 2 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-05-30 | 1977-05-30 | Other |  | Steel/Wrought Iron |  | Sacramento | ... 2" H.P. gas main
52 | 87-20390-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-09-15 | 1987-09-15 | Patch Welded |  | Steel/Wrought Iron |  | Sacramento
[16 empty] | Steel |  | Sacramento
52 | 74-22343-1 |  |  | 0.5 | Other |  | Fitting |  |  | Material Failure |  | 1974-12-18 |  |  |  | Steel/Wrought Iron |  | Sacramento
52 |  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1972-12-04 |  |  |  | Steel/Wrought Iron |  | Sacramento
52 | 78-20482-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Material Failure |  | 1978-04-21 | 1978-12-18 | Other | Redope cap | Steel/Wrought Iron |  | Sacramento | Curb box found 3/4 cap. on L.P. Drip leaking
52 | 78-60249-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-07-03 | 1978-07-03 | Other |  | Steel/Wrought Iron |  |  | Broken 3/4" steel service. Replaced with new steel.
[5 empty] | Distribution Main | [6 empty] | 03/00/0000
Distribution Feeder Main
Distribution Main
52 |  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1986-02-26 | 1986-02-26 |  |  | Steel/Wrought Iron |  |  | Exposed to check wall thichness
52 | 78-60356-1 |  |  | 0.75 | Other |  | Tap Connection |  |  | Damage by outside Forces |  | 1978-09-08 | 1978-09-08 | Clamp |  | Steel/Wrought Iron |  | Sacramento | Teichert construction Co. pitted a 3/4" service tee off a 2" WHP main. Made permanent repair, installed 1 2" skinner temp can... in main.
52 |  |  |  | 8 | Distribution Feeder Main |  | OTHER |  |  | OTHER | [5 empty] | Steel/Wrought Iron |  | Sacramentio
[5 empty] | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
|  |  |  | 6 | [7 empty] | 1998-04-23 |  |  |  | Steel |  | Vacaville
|  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1982-12-07 |  |  |  | Steel/Wrought Iron |  | Vacaville | Installed signal lights, steiny poored cement over 6" gas main. Approx 8" sand between gas main and cement
48 |  |  |  | 3 | Distribution Feeder Main |  |  |  |  | OTHER | NO LEAKS |  | 1975-10-15 |  |  | Steel/Wrought Iron |  | Vacaville | Installed 2 ETS stations at this location. Please post to maps.
48 | 82-33081-1 |  |  | 14 | Transmission |  | Valves |  |  | Other | Cap leak | 1982-05-13 | 1983-06-30 | Other | Redoped | Other | Hi- to- HI
48 | 85-33011-1 |  |  | 3 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1985-05-22 | 1986-04-18 | Other |  | Other
48 | 85-33010-1 |  |  | 3 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1985-05-20 | 1986-04-18 | Other |  | Steel/Wrought Iron |  |  | .. (3")
48 | 85-33008-1 |  |  | 0.25 | Distribution Feeder Main |  | Other |  |  | Other |  | 1985-05-20 | 1986-04-18 |  |  | Steel/Wrought Iron |  |  | ...1/2" weld...
48 | 85-33009-1 |  |  | 0.25 | Gathering |  | Other |  | VALVE | Other |  | 1985-05-20 | 1986-04-18 | Other |  | Steel/Wrought Iron |  |  | Repaired leaking...Vault
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1972-09-14 |  |  |  | Steel/Wrought Iron |  | Vacaville
40 | 89-53049-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1989-06-13 | 1989-06-13 | Replace Pipe |  | Steel/Wrought Iron |  | vacaville | Replaced 4" tested @1200 PSIG and 3/4" static line tested @120PSIG ...
48 | 89-53057-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1989-06-20 | 1989-06-21 | Other |  | Steel/Wrought Iron |  | Vacaville | Replaced 4" valve
| 98-53076-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1998-08-13 | 1998-08-13 | Clamp |  | Steel/Wrought Iron |  | vacavlle | Installed 4" clamp and wrapped pipe. G.P. replaced pipe
48 | 76-53026-1 |  |  | 0.75 | Service |  | Valves |  |  | Material Failure |  | 1976-07-14 | 1976-07-15 | Other | Greased & tightened valve core. | Steel/Wrought Iron |  | Vacaville
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1972-05-02 |  |  |  | Steel/Wrought Iron |  | Vacaville
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1972-06-23 |  |  |  | Steel/Wrought Iron |  | Vacaville
48 |  |  |  | 4 | Distribution Feeder Main |  |  |  |  | OTHER | None |  | 1975-10-14 |  |  | Steel/Wrought Iron |  | Vacaville | Installed ETS station at this location please post to maps
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1973-12-06 | 1973-12-06 | OTHER |  | Steel/Wrought Iron |  | Vacaville
|  |  |  | 4 | Distribution Feeder Main | [7 empty] | 1977-04-27 | PATCH WELDED | ; | Steel/Wrought Iron |  | Vacaville | No Leak; G.C. Welder installed 24" half sole patch over gouge made by Noe-CHL Plurroing Back hoe on 4/13/77
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1977-04-13 | 1977-04-13 | OTHER |  | Steel/Wrought Iron |  | Vacaville | Pipe had damage from back hoe
48 | 78-33139-1 |  |  | 2 | Distribution Feeder Main |  | Fitting |  |  | Material Failure |  | 1978-10-23 | 1982-01-27 | Other |  | Steel/Wrought Iron |  | Vacaville | Shut down regulators and replaced leaking fittings
48 | 73-53044-1 |  |  | 1 | Service |  | Fitting |  |  | Material Failure |  | 1973-07-25 | 1973-07-25 | Other | Replaced fitting | Steel/Wrought Iron |  | Vacaville | Houseline; Note: Leak found by PGE crew. Leak repaired by medical facility crew PGE facilities found inc. excellent contition
48 | 79-33104-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1979-08-16 | 1979-09-14 | Other |  | Steel/Wrought Iron |  | Vacaville | Installed weld repair can over An-hole leaking. Weld @ +/- 30 degrees ELL. 8" x 12" can-pipe= API 5LX GRD. X42 W.T. .188- 9/14/79
48 | 72-33014-1 |  |  | 0.25 | Other | [6 empty] | 1972-08-14 |  | Other | Turned off valve to gas light | Steel/Wrought Iron |  | Vacaville | Gas Light
48 | 72-33012-1 |  |  | 0.25 | Other |  |  |  |  | Corrosion |  | 1972-08-14 |  | Other | Clocked for 10 found less than 1 cutt per hr. customer will change line; | Steel/Wrought Iron |  | Vacaville | Gas Light
48 | 87-33016-1 |  |  | 4 | Distribution Feeder Main |  | Other Welds |  |  | Construction Defect |  | 1987-05-26 | 1992-02-19 |  |  | Steel/Wrought Iron |  | Vacaville | Found leak w/ weld on 4" feeder main, repaired by isolating section of pipe, add re-welded pipe.
48 | 73-13032-1 |  |  | 4 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1973-07-18 | 1976-01-06 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Vacaville | replaced leaking cap on HP service tee
48 | 72-13043-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1972-04-28 | 1972-10-17 | Other |  | Steel/Wrought Iron |  |  | Replaced valve
48 | 76-33136-1 |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1976-09-14 | 1977-03-21 | Other |  | Steel/Wrought Iron |  | Vacaville | Repaired leak by tightening fittings on HPR Reg. Srt. SO120834
48 | 76-33135-1 |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1976-09-04 | 1977-03-21 | Other |  | Steel/Wrought Iron |  | Vacaville | SO 179261 Tightened fittins on H.P.R. Reg. Srt. Leak stopped 3/21/77 R.S.
48 | 80-33059-1 | [10 empty] | 1980-08-20 | [5 empty] | Vacaville
48 | 80-33060-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1980-08-20 | 1981-02-05 | Other |  | Steel/Wrought Iron |  | Vacaville | Greased..., do not believe leak was stopped
6 | 77-53017-1 |  |  | 0.5 | Service |  | Tap Connection |  |  | Construction Defect |  | 1977-04-26 | 1977-04-26 | Other |  | Other Plastic |  | Vacaville | Cap on service tee was leaking. Topper wasn't down far enough.
[16 empty] | Steel |  | Vacaville
|  |  |  | 3 | [11 empty] | Steel |  | vacaville
|  |  |  | 3 | [11 empty] | Steel |  | Vacaville
|  |  |  | 3 | [11 empty] | Steel |  | Vacaville
|  |  |  | 6 | [11 empty] | Steel |  | Vacaville
|  |  |  | 6 | [11 empty] | Steel |  | Vacaville
|  |  |  | 3 | Distribution Feeder Main | [6 empty] | 1972-12-27 | 1972-12-27 |  |  | Steel/Wrought Iron |  |  | Rewrap Main
| 08-33002- |  |  | 4 | Transmission |  | Valves |  |  | Unknown |  | 2008-05-17 | 2008-05-17 | OTHER | GREASED VALVE AT GREASE FITTING | Steel/Wrought Iron |  | Fairfield
| 09-33312- |  |  | 12 | Transmission |  | Mechanical Joint |  |  | Other | Flattened "O" Ring | 2009-10-05 | 2009-10-05 | Other | REPLACED "O" RING ON LID | Steel/Wrought Iron |  | Suisan City | SOAP TEST AFTER REPAIR. REPLACED FLATTENED "O" RING. MADE NEW "O" RING, TESTED WITH LINE PRESSURE - NO LEAKS. LEAK WAS ON THE LID OF THIS STACK.
48 | 91-33003-1 |  |  | 0.75 | Distribution Feeder Main |  | OTHER |  |  | Other |  | 1991-05-24 | 1991-11-01 | Other |  | Steel/Wrought Iron |  | Vacaville
48 | 87-534-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1987-01-14 | 1987-01-14 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Vacaville | Replaced 1 section 3" stl. pipe.
48 | 91-33003-1 |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  | 1991-05-24 | 1991-11-01 | Other |  | Steel/Wrought Iron |  | Vacaville | Tested RES
6 | 77-53021-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-04-30 | 1977-04-30 | REPLACE PIPE AND/OR SERVICE |  | Other Plastic |  | Fairfield
48 | 78-53093-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-10-20 | 1978-10-20 | REPLACE PIPE AND/OR SERVICE |  | Other Plastic |  | Fairfield | Installed 2...coupling
48 | 78-53004-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1977-01-09 | 1977-01-09 | Clamp |  | Steel/Wrought Iron |  | Fairfield | Installed two 2" clamps.
48 | 75-53057-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-11-03 | 1975-11-04 | Clamp |  | Steel/Wrought Iron |  | Fairfield | Repaired leak by permanent clamp 11-4-75
48 | 73-33060-1 |  |  | 2 | Distribution Main |  | Other |  |  | Construction Defect |  | 1973-10-04 | 1975-01-30 | Other |  | Steel/Wrought Iron |  | Fairfield | ...Leak below service tee at base of weld on tee by arc welding over...
48 | 73-33075-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-10-05 | 1973-10-05 | Other | Clamp | Steel/Wrought Iron |  | Fairfield
48 | 73-33075-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-10-05 | 1973-10-06 | Clamp |  | Steel/Wrought Iron |  | Fairfield
6 | 77-80009-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Other |  | 1977-12-13 | 1977-12-13 | Other |  | Steel/Wrought Iron |  | Fairfield | Redoped 2" cap on central fitting and stopped leak
48 | 75-53010-1 |  |  | 0.75 | Service |  | Other Welds |  | SERVICE TEE | CONSTRUCTION DEFECT |  | 1975-02-11 | 1975-03-04 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Fairfield | Renewed service to #733 Madison St. with a 1/2" plastic insert using a powell Riser bonded...and casing to main.
48 | 78-53007-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1978-01-16 | 1978-01-16 | Clamp |  | Steel/Wrought Iron |  | Fairfield | Installed permanent clamp
| 97-53034-1 |  |  | 1.25 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1997-03-06 | 1997-03-06 | Other |  | Steel/Wrought Iron |  | Fairfield | Repaired stem on valve to eliminate leakage. Caution: see gas ENGN. About this valve tee.; Change to 2" because of PC Program.
48 | 78-53005-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1978-01-09 | 1978-01-10 | Clamp |  | Steel/Wrought Iron |  | Fairfield | Installed permanent clamp on 3/4" steel service
48 | 75-53047-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1975-08-11 | 1975-08-13 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Fairfield | Renewed and lowered 28' of 2" steel gas main; Lowered 28' of 2" gas main
48 | 74-53027-1 |  |  | 2 | Distribution Main |  | Other Welds |  | 45 DEGREE ANGLE | Corrosion |  | 1974-04-05 | 1974-04-08 | Clamp | PERMANENT REPAIR REPLACE PIPE AND/OR SERVICE | Steel/Wrought Iron |  | Fairfield
48 | 78-53002-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1978-01-05 | 1978-01-11 | Clamp |  | Steel/Wrought Iron |  | Fairfield | Installed two 4" permanent clamps
48 | 78-33093-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-09-21 | 1978-10-17 | Patch Welded |  | Steel/Wrought Iron |  | (FFLD) | *One pit was leaking installed 2" Save-A-Valve nipple over leak
48 | 75-80014-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-04-09 | 1975-04-10 | REPLACE PIPE AND/OR SERVICE | PLASTIC INSERT | Steel/Wrought Iron |  | Suisun | Renewed plastic instert. Bonded risers to casing and casing to main
|  |  |  | 6.58 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  |  | 6" feeder altered on D&C 22/62-C to clear box culvert construction.
48 | 78-80000-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1978-01-10 | 1978-01-18 | Other |  | Steel/Wrought Iron |  | Fairfield | Installed a 24" can over a clamp
48 | 78-80005-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1978-03-15 | 1978-03-21 | Clamp |  | Steel/Wrought Iron |  | Fairfield | Installed 2" permanent clamp
48 | 74-80004-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-03-18 | 1974-04-10 | Clamp |  | Steel/Wrought Iron |  | Fairfield
48 | 73-13001-1 |  |  | 1.25 | Distribution Main |  | Other |  | None | Other | NO INDICATION OF GAS. | 1973-06-12 |  | Other | None | Steel/Wrought Iron |  | Fairfield | Leak in P.G. & E. P at 2516 Beaufort Ct. East side of St. Marked Yellow X; Bar tested every 10' no indication of Ca. Evidence of work done here at earlier date.
48 | 77-53007-1 |  |  | 0.75 | Other | [6 empty] | 1977-02-02 |  |  |  | Steel/Wrought Iron |  |  | Cust. turned off. Leaking houseline customer #1740 turned off
48 | 76-53037-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-08-31 | 1976-08-31 | REPLACE PIPE AND/OR SERVICE |  | Other Plastic |  | Fairfield | Cut pipe and installed...
48 | 76-33117-1 |  |  | 6 | Other |  | Valves |  |  | Other |  | 1976-09-07 | 1977-03-07 | Other |  | Steel/Wrought Iron |  | FFLD
6 | 78-53089-1 |  |  | 0.05 | Service |  | Body of Pipe |  |  | Construction Defect |  | 1978-10-11 | 1978-10-11 | REPLACE PIPE AND/OR SERVICE |  | Other Plastic |  | Suisun
48 | 77-53046-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-09-12 | 1977-09-12 | REPLACE PIPE AND/OR SERVICE |  | Other Plastic |  | Suisun
48 | 99-33071-1 |  |  | 2 | Transmission |  | Valves |  |  | Other |  | 1999-03-11 | 2000-07-12 | Other |  | Steel/Wrought Iron |  | Fairfield | Worked and greased valve
48 | 77-53056-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-10-08 | 1977-10-08 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Suisun
| 08-33007- |  |  | 0.75 |  |  | Other |  | Relief Valve | Unknown |  | 2008-05-17 | 2008-05-20 | Other | REPLACED RELIEF | Steel/Wrought Iron |  | Vacaville | Replaced relief; Replced relief, soap tested. No leaks
48 | 81-33047-1 |  |  | 0.75 | Distribution Feeder Main |  | Regulator |  |  | Other |  | 1981-06-17 | 1982-05-07 | Other |  | Steel/Wrought Iron |  | Vacaville | Leaking in Reg. Pit.
48 | 80-33061-1 |  |  | 2 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1980-08-26 | 1981-03-02 | Other |  | Steel/Wrought Iron |  | Fairfield | Greased valve to stop leak
48 | 80-33117-1 |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1980-10-17 | 1983-03-23 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  |  | Soap tested leak at...top...stop leak.; Leak above valve on service. Repaired by Servicemen
48 | 88-53056-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1988-05-18 | 1988-05-18 | Replace Pipe |  | Steel |  |  | Replaced a section of pipe
48 | 88-53056-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1988-05-18 | 1988-05-18 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  |  | Valved by...-Permanent repairs to be made 5-19-88. Temp Repairs made 5-18-88.
| 06-33104- | [10 empty] | 2006-10-03 | 2006-10-17 |  |  |  |  | Vacaville | Greased valve-JLT9 10-17-06
48 | 81-33036-1 |  |  | 1.25 | Distribution Feeder Main |  | Regulator |  |  | Other |  | 1981-06-16 | 1982-05-07 | Other |  | Other |  | Fairfield | Part order, not hazzard vent to Atmisfair will Rep. When parts come in
|  |  |  | 0.75 | [11 empty] | Steel |  | Fairfield
48 | 78-33000-1 | 210 |  | 0 | Other |  | Valves |  |  | Other |  | 1978-04-11 | 1979-04-16 | Other |  | Steel/Wrought Iron |  |  | Inlet valve fix Reg. Sta. gas valve off line
48 | 78-33001-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1978-04-11 | 1979-04-16 | Other |  | Steel/Wrought Iron |  |  | Reg Station Leaksat ... Valve
|  |  |  | 4 | Distribution Main |  | BODY OF PIPE |  |  | CORROSION |  | 1977-08-30 | 1977-08-31 | OTHER |  | Steel/Wrought Iron |  | Isleton | Canned tee and main.
48 | 76-33048-1 |  |  | 2 | Distribution Main |  | Tap Connection |  | ABANDONED TEE LEAKING | Corrosion |  | 1976-07-13 | 1976-07-20 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Rio Vista | Repaired leaking. Abandoned service Tee by Weld over Sleeve 7-20-76
48 | 75-53048-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-08-14 | 1975-08-15 | REPLACE PIPE AND/OR SERVICE | PLASTIC INSERT | Steel/Wrought Iron |  | Rio VIsta | Insert 1/2 Plastic...; Plastic Insert USPD Powell Riser
52 | 78-20044-1 |  |  | 0.75 | Other |  | Fitting |  |  | Corrosion |  | 1978-01-19 | 1978-01-20 | Other |  | Steel/Wrought Iron |  | Sacramento | Installed a 2" line stopper at main, abandoned badly leaking 3/4" drip, 3/4" service stub and 10' of 2" W steel main to stop leaking at this point.
52 |  |  |  | 0.75 | Other |  | OTHER |  |  | OTHER |  | 1975-07-31 | 1975-08-01 |  |  | Steel/Wrought Iron |  | Bryte | Found leak on customer's houseline. Made temp repaires...
52 | 80-20049-1 |  |  | 0.75 | Other |  | Fitting |  |  | Other | Service Tee Cap loose | 1980-03-06 | 1980-04-08 | Other | Tightened Cap | Steel/Wrought Iron |  | Sacramento | Found a 3/4" service tee cap leaking, cap loose, service tee is abandoned service, not in use. Removed all three tee caps redopped and tightened, aslo removed all wrap from main in this bell hole. Did not find P.C.F. as shown on Plat sheet.
52 | 73-60390-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1973-09-21 | 1973-09-21 | Patch Welded |  | Steel/Wrought Iron
50 | 97-55009-1 |  |  | 0.75 | Transmission |  | Body of Pipe |  |  | Digin |  | 1997-03-18 | 1997-03-18 | Replace Pipe |  | Steel/Wrought Iron |  | W. Sacranento | Located service and main opened a 4 x 5 hole over the gas tee and pluged off the service. There was no U.S.A. marks
52 |  |  |  | 3 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | W. Sacramento | Checked condition of main here at this location. Replaced curb valve on service. See Report.
|  |  |  | 0.03 | Transmission | [10 empty] | Steel/Wrought Iron |  | West Sacramento
| 00-55021- |  |  | 0.75 | Transmission |  | Body of Pipe |  |  | Digin |  | 2000-05-12 | 2000-05-12 | Other | REPLACE PIPE (MAINTENANCE: <100' FOR DIST., <50' FOR TRANS.) | Steel/Wrought Iron |  | West Sacramento | Replaced 29' Pipe 3/4; 3/4 STL. Tested @ 1200 psi for 73 min.
50 | 95-35083-1 |  |  | 6 | Transmission |  | Fitting |  |  | Other |  | 1995-05-08 | 1997-03-19 | Tighten Cap or Bolt |  |  |  | W. Sacramento | Tighten 1/4" plug on Gauge...
| 99-35008-1 |  |  | 1.25 | Transmission |  | Valves |  |  | Material Failure |  | 1999-03-18 | 2000-05-13 | OTHER | ABANDON | Steel/Wrought Iron |  | W. Sacramento | Valve removed 5-13-00
52 | 81-60220-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1981-09-15 | 1981-09-15 |  |  | Other Plastic |  | Sacramento | Installed to 700... hold couplings
| 08-35076-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Unknown |  | 2008-05-27 |  |  |  | Steel/Wrought Iron |  | West Sacramento
| 99-35006-1 |  |  | 2 | Transmission |  | Valves |  |  | Material Failure |  | 1999-03-16 | 2000-05-12 | Other | GREASED VALV | Steel/Wrought Iron |  | W. Sacramento | Greased Valve.
| 08-35069-1 |  |  |  | Transmission |  | Valves |  |  | Unknown |  | 2008-05-26 |  |  |  | Steel/Wrought Iron |  | West Sacramento | Ball valve for body bleed was leaking
| 99-35001- | 172 |  | 0.75 | Service |  | Body of Pipe |  |  | Unknown |  | 1999-03-18 | 1999-03-18 | OTHER | REPLACE PIPE (CAPITAL) | Steel/Wrought Iron |  | W. Sacramento | Insert service
| 99-35007- |  |  | 0.75 | Transmission |  | Fitting |  |  |  |  | 1999-03-16 | 1999-06-03 | Other | Hi to Hi | Steel/Wrought Iron |  | W. Sacramento | Redoped mueller cap
|  |  |  | 16 | Transmission | [6 empty] | 2005-11-03 |  |  |  | Steel/Wrought Iron |  | W. Sacramento
52 | 73-20267-1 |  |  | 2 | Other |  | Tap Connection |  |  | Construction Defect |  | 1972-09-13 | 1972-09-13 | Patch Welded |  | Steel/Wrought Iron
50 | 95-35030-1 |  |  | 0.75 | Service |  | VALVES |  |  | CORROSION |  | 1995-03-21 | 1995-09-20 | Other |  | Steel/Wrought Iron |  | Winters | Greased valve on 3/4" STL. Service
50 |  |  |  | 3 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Winters | Lower feeder main & Rewrapped main to clear new storm drain
50 | 93-15026-1 | [10 empty] | 1993-03-24 | [5 empty] | Winters | 5-23-94 No leak found
| 81-55000-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | CONSTRUCTION DEFECT |  | 1981-01-30 | 1981-02-03 | Other |  | Other Plastic |  | Davis | Repaired 2 Plastic gas main with 2 Ampfit couplings. Removed leaking service tee.
50 | 81-55020-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1981-09-09 | 1981-09-11 | Clamp |  | Steel/Wrought Iron |  | Davis | Leak is in sidewalk and grass by tree on main.
50 | 95-35074-1 | [10 empty] | 1995-05-03 | [5 empty] | Winters
50 |  |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-12-26 | 1972-12-26 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | HOLE WELDED SHUT.; ;
| 99-55031- | 203 |  | 4 | Gathering |  | Body of Pipe |  | SAV-A-VALVE | Digin |  | 1999-06-14 | 1999-06-15 | OTHER | REPLACE PIPE (MAINTENANCE: <100' FOR DIST., <50' FOR TRANS.) |  |  | W. Sacramento | Dig in on line 203 at 500# pressure; Replaced 4 ft. of main
9 | 74-00039-1 |  |  | 4 | Distribution Main |  | Other |  |  | Other |  | 1974-03-22 | 1974-04-03 | Other |  | Steel/Wrought Iron |  | Colusa | Leak in Reg. N/E...First St....
9 | 74-00039-1 | [10 empty] | 1974-03-22 | [5 empty] | Colusa
9 | 96-35010-1 |  |  | 0.75 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1996-07-31 | 1996-12-19 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Colusa | Repaired plug on top of alcohol pot- only leaks found.
9 | 87-00147-1 |  |  | 2 | Distribution Main |  | Valves |  |  | Other |  | 1987-08-16 | 1988-05-09 | Other |  | Steel/Wrought Iron |  | Colusa | Greased valve (stopped leak)
9 | 87-00147-1 | [10 empty] | 1987-08-18 | [5 empty] | Colusa
| 08-35083-1 |  |  | 0.75 | Transmission |  | Other |  | Valve Tee | Material Failure |  | 2008-05-29 | 2008-08-28 | Other | Replace "O" Rings | Steel/Wrought Iron |  | Davis | Repaired 3 3/4" Mueller valve tee's by removing caps and replacing 2 internal "O" rings on each cap. Soap tested no leaks observed.
| 02-35037-1 | 150 |  | 0.75 |  |  | Regulator |  |  | Other |  | 2002-03-25 | 2002-05-14 | Other | RELIEF | Other |  | Davis | Rebuilt leaking relief. Rebuilt Reg. also.
| 06-35018- |  |  | 0.75 | Transmission |  | Unknown |  |  | Unknown |  | 2006-10-04 | 2006-10-25 | Other | Tighten plug | Steel/Wrought Iron |  | Davis | One side, Spool other side, inlet pressure 150 down grade in 2004
| 09-35081-1 | 116 |  | 1 | Transmission |  | Other |  | Pin off Tee | Other | Bad O-rings | 2009-10-16 | 2009-12-29 | Other | Replaced O-rings | Steel/Wrought Iron |  | Davis | Replaced O-rings in cap; replaced O-rings in cap of pin off tee
| 09-35082-1 | 116 |  | 1 | Transmission |  | Other |  | Pin off tee | Other | Bad O-rings | 2009-10-16 | 2009-12-29 | Other | Replaced O-rings | Steel/Wrought Iron |  | Davis | Replaced O-rings in cap; Replaced O-rings in cap of pin off tee
50 | 95-35076-1 | [10 empty] | 1995-05-03 | [5 empty] | Davis | 4/15/1995 No leak found
50 | 95-35075-1 | [10 empty] | 1995-05-03 | [5 empty] | Davis | 4/15/95 No leak found
| 08-13813-1 |  |  |  | Transmission | [6 empty] | 2008-03-18 | 2008-11-19 | Other | PCF (WELDED) NOT TAPPED MUELLER - ANSI 150# | Steel/Wrought Iron |  | Sonoma | ANSI 150 Muller used to report the leak, not tapped because corrision pit was 6" long & a leak clamp is only 5" long. A PCF is 9" long
| 08-12971-1 | 21E |  |  | Distribution Main |  | Valves |  |  | Other | Grease | 2008-01-30 | 2008-02-22 | Other | GREASED VALVE | Steel/Wrought Iron |  | Cloverdale | Pintpoint and exposed leak on 6" stl.; Leak on valve, 2" SPL D.F.; We just had out R. Peters to grease valve, after we uncover it.
44 | 72-18001-1 |  |  | 2 | Distribution Main |  | Fitting | Fitting |  | Other |  | 1972-04-14 | 1972-04-14 | Other |  | Steel/Wrought Iron |  |  | Repaired with small piece of plastic and coupling.
44 | 72-18002-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-04-27 | 1972-04-27 | Clamp |  | Steel/Wrought Iron |  | Cotati
44 | 72-18021-1 |  |  | 1.25 | Other |  | Tap Connection |  |  | Construction Defect |  | 1972-08-18 | 1973-01-24 | Replace Pipe and/or Service |  | Other Plastic |  | Cotati | Replaced section of main install new sec. tee. (G.C. proformed).
44 | 72-38016-1 |  |  | 0.75 | Service |  | Fitting |  |  | Material Failure |  | 1972-09-11 | 1973-02-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Found H.P.R. leaking on high pressure side. Turn-over to mechanic.
44 | 72-58010- |  |  | 0.5 | Service |  |  |  |  | Material Failure |  | 1972-01-07 | 1972-01-07 | Other |  | Copper |  | Petaluma | Install partial piece of plastic in service line.
44 | 72-58012- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-01-31 | 1972-01-31 | Clamp |  | Steel/Wrought Iron |  | Petaluma | Temp leak clamp.
44 | 72-58013-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-02-02 | 1972-02-02 | Clamp |  | Steel/Wrought Iron
44 | 72-58015-1 |  |  | 2 | Distribution Main |  | Body of Pipe | Physical/Mechanical Joint | Physical/Mechanical Joint | Corrosion |  | 1972-02-14 | 1972-02-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Petaluma | Refer to job order #M-9945.
44 | 72-58021- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-03-03 | 1972-03-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Cotati | Renewed srvice with 1/2" PL. 3/6/72, no leaks in area at this time; Replaced 3/4" service with 1/2" plastic insert, 3-6-72.
44 | 72-58022-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  |  | 1972-04-10 | Patch Welded |  | Steel/Wrought Iron |  | Petaluma | Inserted plastic. Welded coupling over pit.
44 | 72-58023-1 |  |  | 4 | Distribution Main |  | Girth Weld |  |  | Corrosion |  | 1972-05-26 | 1972-05-26 | Clamp |  | Steel/Wrought Iron |  | Penngrove | Main is pitted badly in this area. (2) 4" temp leak clamp.
44 | 73-38029-1 |  |  | 2 | Other |  | Other |  |  | Other |  | 1973-08-10 | 1973-08-10 | Other |  | Steel/Wrought Iron |  |  | Leak is high presure house line found leak and disconnected. Owner will have it repaired.
44 | 73-78035-1 |  |  | 0.75 | Other |  | Fitting |  |  | Construction Defect |  | 1973-08-03 | 1974-04-30 | Other |  | Steel/Wrought Iron |  | Petaluma | This leak was on meter. I replaced outlet. Ellbow and nilon bushing.
44 | 74-38004-1 |  |  | 16 | Transmission |  | Valves |  |  | Material Failure |  | 1974-06-14 | 1974-07-30 | Other |  | Steel/Wrought Iron |  | Petaluma | Grease Leaking Valve
44 | 75-18002-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-03-14 | 1977-09-25 | Patch Welded |  | Steel/Wrought Iron |  | Penngrove
44 | 75-18006-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-03-17 | 1976-06-11 | Patch Welded |  | Steel/Wrought Iron |  | Petaluma/Pemmgrove
44 | 75-18061-1 |  |  | 8 | Transmission |  | Tap Connection |  |  | Other |  | 1975-03-28 | 1976-05-06 | Patch Welded |  | Steel/Wrought Iron |  |  | Patched hole where old service saddle was leaking
44 | 75-38004-1 |  |  | 6 | Transmission |  | Fitting | Fitting |  | Other |  | 1975-11-17 | 1975-11-17 | Other |  | Steel/Wrought Iron |  | Petaluma
44 | 75-58019-1 |  |  | 0.75 | Other |  | Fitting |  |  | Damage by outside Forces |  | 1975-05-08 | 1975-05-08 | Other |  | Steel/Wrought Iron |  | Penngrove | Old Drip 3/4 broken by county, cut pipe at main.
44 | 75-58062-1 |  |  | 0.7 | Other |  | Body of Pipe |  |  | Corrosion |  | 1975-10-29 | 1976-07-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron
44 | 75-19023-1 |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1975-04-03 | 1976-07-31 | Other |  | Steel/Wrought Iron |  |  | Sonoma
44 | 75-19034-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-04-03 | 1977-06-17 | Clamp |  | Steel/Wrought Iron |  |  | Found Leak in 6" I's of stor. Install 1 6x6 leak clamp. This should have a can welded on it.
44 | 75-19035-1 |  |  | 6 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 1975-04-03 | 1976-07-15 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Found leak on 6" plastic, leak at weld, installed can over.
44 | 75-19071-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Other |  | 1975-04-29 | 1976-05-07 | Other |  | Steel/Wrought Iron |  |  | Found Muller cap leaking in the N/W. Took cap off redo & tighten up
44 | 75-59019-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-12-29 | 1975-12-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | sONOMA | On 12/23/1975 I found a leak in service 2" from riser, repaired by inserting 1/2" PL. S.D. #6106 AP.
44 | 75-59020-1 |  |  | 0.5 | Service |  | Fitting |  |  | Construction Defect |  | 1975-10-27 | 1975-10-28 | Other |  | Other Plastic |  | Sonoma | 10/28/1975 Found leak in service on plastic fitting due to inproper melting on plastic repaired by installer. New fitting rechecked 11/17/75 ok.
44 | 76-39019-1 |  |  | 6 | Other |  | Valves |  |  | Material Failure |  | 1976-11-17 | 1978-03-14 | Other |  | Steel/Wrought Iron |  | Sonoma
44 | 76-39034-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-11-23 | 1978-09-15 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Sonoma | Install 8" can over leaking 6" main 9/15/75.
44 | 76-39036-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1976-11-23 | 1977-11-23 | Other |  | Steel/Wrought Iron |  | Sonoma | Grease Valve 11/23/77 DYE
25 | 76-59008-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1976-08-30 | 1976-08-30 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Found corrosion leak in service.
44 | 77-39005-1 |  |  | 6 | Distribution Feeder Main |  | Fitting |  |  | Corrosion |  | 1977-05-10 | 1978-05-23 | Other |  | Steel/Wrought Iron |  |  | Welded a 6" can on a leaky service tee.
44 | 77-59009-1 |  |  | 2 | Transmission |  | Valves |  |  | Material Failure |  | 1977-09-15 | 1978-09-20 | Other |  | Steel/Wrought Iron |  |  | Greased 2" valve on blow off on 6" transmission main. The valve greased comes off the bottom of the 6" refer to field book 110 pg. 16. Re-checked 12/29/1975 no reading
44 | 78-59013-1 |  |  | 8 | Transmission |  | Valves |  |  | Other |  | 1978-03-28 | 1978-07-12 | Other |  | Steel/Wrought Iron |  |  | Greased valve on 8'" transmission pipe was able to stop all leakage.
44 | 78-59031-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1978-10-28 | 1978-10-28 | Other |  | Steel/Wrought Iron |  | Sonoma | Found corrosion leak.
44 | 80-59001-1 |  |  | 0.75 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-08-04 | 1980-08-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Sonoma | Demartini const broke our 3" high pressure line. 2" from HPR box supplying Linda Dr.
44 | 76-20275-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1976-11-12 | 1977-07-05 | Clamp |  | Steel/Wrought Iron |  | Sebastopol | Clear
44 | 76-40016-1 |  |  | 8 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1976-02-23 | 1976-03-08 | Other | Greased Valves | Steel/Wrought Iron |  | Sebastopol | Two leak. one 12"
44 | 76-40104-1 |  |  | 0.34 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-08-14 | 1976-08-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Sebastopol | Replaced 2' 3/4" steel service
4 | 76-40128-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-09-15 | 1976-09-17 | Clamp |  | Steel/Wrought Iron |  | Healdsburg | Leak one foot South of service tee to 828. Installed 2"x3" clamp 9 Anode.
44 | 76-18005-1 |  |  | 8 | Transmission |  | Valves |  |  | Other |  | 1976-05-04 | 1981-05-12 | Other | GREASED VALVE | Steel/Wrought Iron |  | Petaluma | Valve #5 Repaired
44 | 76-58005-1 |  |  | 8 | Transmission |  | Valves |  |  | Other |  | 1976-02-12 | 1976-02-17 | Other |  | Steel/Wrought Iron |  | Petaluma | Greased valve & tightened flange on 8" H.P. valve stoping leak. Backfilled with & Reset marker #76
44 | 76-58018-1 |  |  | 2" | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-03-24 | 1976-03-25 | Clamp |  | Steel/Wrought Iron |  | Petaluma | Clamped leak on 2" main.
44 | 76-58024-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-03-05 | 1976-04-06 | Patch Welded |  | Steel/Wrought Iron |  | Petaluma | Weld vent patch at 5:00 o'clock position on 12" (HP) gas main
44 | 76-58025-1 |  |  | 0.5 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-03-23 | 1976-03-23 | Other |  | Other Plastic |  | Penngrove | 1/2" PL stub service in 3/4" casing broken by Penngrove water dept. stub was not in. So I abandoned at 2" steel main-80" North of Rosheimer Rd.
44 | 76-58026-1 |  |  | 0.75 | Other |  | Fitting |  |  | Damage by outside Forces |  | 1976-03-22 | 1976-03-22 | Other |  | Steel/Wrought Iron |  | Petaluma | Contractor broke 3/4" stub at service tee. I removed service tee and slid 2" leak clamp over 1/2" tap hole and cut off bolts wrapped.
44 | 76-58040-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-03-29 | 1977-01-31 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Petaluma | Insert 322' of 2" Plastic into 3" steel main per attached sketch no. 4322-F SD# 56243. Tested new main and 2" running up McDowell with 100 lbs air for 1/2 hr. Held ok.
44 | 76-58054-1 |  |  | 12 | Transmission |  | Other |  |  | Construction Defect |  | 1976-07-17 | 1976-07-20 | Other |  | Steel/Wrought Iron |  | Petaluma | Tighten leaking insulating flangeon 12" trans main.
44 | 76-58066-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-04-10 | 1976-05-18 | Patch Welded |  | Steel/Wrought Iron |  | Petaluma | Weld 16" long half sole.
44 | 76-58067-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-04-10 | 1976-05-18 | Patch Welded |  | Steel/Wrought Iron |  | Petaluma | Welded 24" long half sole for repair
44 | 77-38053- |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1977-04-21 | 1977-09-29 | Patch Welded |  | Steel/Wrought Iron |  |  | NEED FLAME PAK, 8-12-77; ARC WELDED PATCH ON 8" MAIN.
44 | 77-38095- |  |  | 8 | Transmission | [6 empty] | 1977-05-19 |  |  |  | Steel/Wrought Iron |  | Penngrove | 05% both sides of drain marked yellow; No Ind, of gas 4/19/79
44 | 77-38027-1 |  |  | 8 | Transmission |  | Fitting |  |  | Material Failure |  | 1977-02-23 | 1977-06-24 | Other |  | Steel/Wrought Iron |  | Petaluma | Valve leaking.
44 | 77-38040-1 |  |  | 8 | Distribution Feeder Main |  | Drip |  |  | Corrosion |  | 1977-04-15 | 1978-09-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Penngrove | Replaced on W.D. 4914-F 6-50152
44 | 77-38046- |  |  | 8 | Transmission | [6 empty] | 1977-04-19 |  |  |  | Steel/Wrought Iron |  | Penngrove | Down grade (785-0001)
44 | 77-38099- |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1977-05-20 | 1977-11-10 | Patch Welded |  | Steel/Wrought Iron |  | Penngrove
44 | 77-20001-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1977-02-10 | 1978-04-06 | Clamp |  | Steel/Wrought Iron |  | Santa Rosa | Found 6" main on Geurville Hwy 184' west of Marlow. Repairs made by installing 1"-6" flange clamp & 1 leak clamp. 5" lb installed on each clamp. 5 of main was uncover & checked. Fitting was connected to a 178" section. Pin hole was upper at the 5 o'clock position. Heavy fitting on leak section/ pits appear to be inactive.
44 | 77-40004-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-02-25 | 1977-02-25 | Other |  | Other Plastic |  | Santa Rosa | Dig-In Joe Lunardi Electric Co. Received call 10:17 AM job site.
44 | 78-38049-1 |  |  | 0.5 | Other |  | Body of Pipe |  |  | Corrosion |  | 1978-03-10 | 1978-03-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Petaluma | Found 3/4" steel riser leaking. Replaced with powell riser
44 | 78-58000-1 |  |  | 1.25 | Distribution Main | [6 empty] | 1978-01-09 |  |  |  | Steel/Wrought Iron
44 | 78-58032-1 |  |  | 2 | Other |  | Fitting |  |  | Other |  | 1978-05-05 | 1978-05-05 | Other |  | Steel/Wrought Iron |  |  | Install 2" top-tap. Abandon 20" of 2" main
44 | 79-58036-1 |  |  | 12 | Transmission |  | Valves |  |  | Material Failure |  | 1979-09-24 | 1979-09-26 | Other |  | Steel/Wrought Iron |  |  | Repaired 9/26/79. Sleased Valve
4 | 80-40228-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-12-30 | 1980-12-30 | Other |  | Steel/Wrought Iron |  | Santa Rosa
44 | 81-58011-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1981-03-02 | 1981-03-02 | Patch Welded |  | Steel/Wrought Iron |  | Petaluma | Lowered pressure on transmission main to repair 3/28/1981 and vent made final repair on 3/3/1981
44 | 81-58012-1 |  |  | 0.75 | Other |  | Regulator |  |  | Material Failure |  | 1981-03-12 | 1981-03-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Cotati
44 | 81-40072-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1981-05-04 | 1981-06-05 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Windsor
44 | 81-40072-1 | [10 empty] | 1981-05-04 | [5 empty] | Windsor | Leak apears to be over 150# G< area painted yellow
4 | 81-40090-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1981-05-28 | 1981-05-28 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Santa Rosa | Dig-In to the dip in the intersection at 5th & E st repairs made by replacing damaged section with 3/4" steel pipe
4 | 81-40093-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1981-06-01 | 1981-06-01 | Other |  | Other Plastic |  | Geyserville
4 | 81-40098-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1981-06-10 | 1981-06-10 | Other |  | Steel/Wrought Iron |  | Santa Rosa | Old service to c/o at main when road crew is clear of area 6/12/1981
44 | 81-40112-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1981-06-17 | 1981-07-01 | Patch Welded |  | Steel/Wrought Iron |  | Windsor | Leak apears tp be over 6" GM, 4" from house, DF.
44 | 81-40115-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1981-07-20 | 1981-09-22 | Clamp |  | Steel/Wrought Iron |  | Santa Rosa | This leak was graded #2 because of ahigh reading, and people complaining in area. DFpipe in very poor shape, installed 2-6" Clamp. Should be replaced ASAP
|  |  |  | 0.2 | Other | [6 empty] | 1986-03-05 |  |  |  | Steel/Wrought Iron |  | Sonoma | No reading in area with JW, Area has been repaved
44 | 81-19006-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1981-03-10 | 1981-04-27 | Other |  | Steel/Wrought Iron |  | Sonoma | Found 2" blown off leaking, permanent repaires made by cutting off 2" pipe & installing can over 2" valve. Made existing valve box into a ETS station. 2 Distribution ("') away from (6") at a depth of (18")
44 | 86-00013-1 | [10 empty] | 1986-05-12 | [5 empty] | Healds
44 | 82-38008- |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-06-30 | 1982-07-01 | Replace Pipe and/or Service |  | Copper |  | Petaluma | Repaired leaking 1" copper coupling 3" from service tee
44 | 82-38021-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1982-06-21 | 1983-09-02 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Petaluma | Leak was repaired on 12" line 21 by welding 12" sleve on the main-soap test-ok main is in very bad shape!
44 | 85-00000-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1985-01-22 | 1985-02-04 | Clamp |  | Steel/Wrought Iron |  | Santa Rosa | Install 3 leak clamps on main to stop leakage
44 | 85-00013-1 |  |  | 0.75 | Distribution Main |  | Regulator |  |  | Other |  | 1985-08-09 | 1986-01-21 | Other |  | Steel/Wrought Iron |  | Santa Rosa
44 | 85-00013-1 |  |  | 75 | Distribution Main |  | Regulator |  |  | Other |  | 1985-08-09 | 1986-01-21 | Other |  | Steel/Wrought Iron |  | Santa rosa
44 | 85-40030-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1985-03-11 | 1986-08-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Santa Rosa | Large section of pipe being place by G.C.
44 | 85-40031-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1985-03-07 | 1985-03-08 | Clamp |  | Steel/Wrought Iron |  |  | Installed 2 8" leak clamps
44 | 84-00005-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-01-30 | 1984-02-06 | Patch Welded |  | Steel/Wrought Iron |  | Healdsburg | Wrap on the bottom is in very poor condition
44 | 84-40036-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1984-03-20 | 1984-05-31 | Clamp |  | Steel/Wrought Iron |  | Santa Rosa | To be replaced
44 | 84-40038-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1984-03-20 | 1985-03-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Graton | Main replaced on GM 440115403/15/85
44 | 84-40080-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1984-05-16 | 1984-05-16 | Patch Welded |  | Steel/Wrought Iron
44 | 85-58023-1 |  |  | 0.2 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1985-04-17 | 1985-06-26 | Patch Welded |  | Steel/Wrought Iron |  | Petaluma | Main in very bad condition
4 |  |  |  |  | Transmission |  | Valves |  |  | Other |  | 1986-07-25 | 1986-07-25 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Petaluma | Repaired leaking metric valve & 1 1/4" cap on tee in reg pit
44 | 84-00005-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-01-30 | 1984-02-06 | Patch Welded |  | Steel/Wrought Iron |  | Healdsburg | Wrap in the bottom is in very poor condition
44 | 84-40036-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1984-03-20 | 1984-05-31 | Clamp |  | Steel/Wrought Iron |  | Santa Rosa
44 | 84-40038-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1984-03-20 | 1985-03-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Graton
44 | 84-40080-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1984-05-16 | 1984-05-16 | Patch Welded |  | Steel/Wrought Iron
44 | 86-00013-1 | [10 empty] | 1986-05-13 | [5 empty] | Healds
44 | 87-38001-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-03-13 | 1987-03-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Leaking-numerous pits to dephts of .250. 1 hole. Replaced 5' 12" pipe
44 | 87-58004-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-03-11 | 1987-03-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Leaking numerous pits to dephts of .250. 3 holes. Replaced 7'12" pipes
44 | 87-00001-1 |  |  | 0.75 | Service |  | Regulator |  |  | Construction Defect |  | 1987-01-16 | 1987-05-13 | Other |  | Steel/Wrought Iron |  | Santa Rosa | Found H.P.R. leaking
44 | 87-00002-1 |  |  | 6 | Distribution Feeder Main |  | Longitudinal Weld |  |  | Construction Defect |  | 1987-01-16 | 1987-05-13 | Patch Welded |  | Steel/Wrought Iron |  | Santa Rosa
44 | 87-00003-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1987-01-16 | 1987-04-09 | Clamp |  | Steel/Wrought Iron |  | Santa Rosa | Repaired 2 leaks on the 2" steel main
44 | 87-40033-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1987-04-12 | 1987-04-12 | Replace Pipe and/or Service |  | TR 418
SR | 88-19001-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1988-04-05 | 1988-04-05 | Patch Welded |  | Steel/Wrought Iron |  | Sonoma | Weld 1 patch on 6" main over corrosion leak
44 | 89-19000-1 |  |  | 8 | Distribution Feeder Main |  | Fitting |  |  | Material Failure |  | 1989-02-17 | 1989-08-03 | Other |  | Other |  | Glenn Ellenwall | Relief valve on HPR leaking (repaired)
44 | 89-19003-1 |  |  | 2000-02-01 | Distribution Main |  | Fitting |  |  | Other |  | 1989-02-23 | 1989-08-04 | Other |  | Steel/Wrought Iron |  | Sonoma | Found leak on muller cap redoped amd tighten cap
| 90-19001-1 |  |  | 12.75 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1990-02-12 | 1991-03-15 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Sonoma | Found leak on 12" flange. Gave work to G.C. Flange was cleaned up and bolts tightened.
44 | 90-19000-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1990-02-12 | 1990-03-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Sonoma Glen Ellen | Found leak under bridge. G.C. repaired leak by replacing 6" HP main with 8" HP main across bridge
44 | 90-59004-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Other | D | 1990-04-25 | 1990-04-25 | Patch Welded |  | Steel/Wrought Iron |  | Sonoma | Welded half sole 1sav-a-valve over leak
44 | 91-19000-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1991-01-31 | 1991-02-25 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Sonoma | Welded can over valve. Abandon 2" across hwy
44 | 91-19000-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1991-01-31 | 1991-02-25 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Sonoma | Welded can over valve. Abandon 2" across hwy
44 | 91-19001-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1991-02-25 | 1991-03-05 | Clamp |  | Steel/Wrought Iron |  | Boyes | Installed two 3"x2" s. steel leak clamp.
44 | 92-39000-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1992-11-02 | 1993-01-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Sonoma | G.C. installed two 6" bottom taps and cut out leaking valve and flanges
| 90-58061-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Digin |  | 1990-10-25 | 1990-10-25 | Replace Pipe and/or Service |  | TR 418 |  | Petaluma | Replace 2" sectionpf 2' pl
44 |  |  |  | 2 | Distribution Feeder Main |  | Fitting |  |  | Construction Defect |  | 1988-01-14 | 1988-02-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Santa Rosa | Found cap leaking on 2" side tap feeding valve #1. Repairs made by tightining up cap
44 | 88-00001-1 |  |  | 6 | Distribution Feeder Main |  | Fitting |  |  | Material Failure |  | 1988-01-14 | 1988-02-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Santa Rosa | Found karotest leaking
44 | 88-00021-1 | [10 empty] | 1988-01-20 | [5 empty] | Santa Rosa | This leak graded class I beacause of reading near bldg. DF
44 | 88-40005-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Damage by outside Forces |  | 1988-01-08 | 1988-01-13 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Cloverdale | Replaced 2-leaking HPR
44 | 88-40036-1 |  |  | 8 | Distribution Main |  | Other Welds |  |  | Other |  | 1988-02-05 | 1988-02-08 | Other |  | Steel/Wrought Iron |  | Healds | This leak graded class I because of reading's over 150# line 5' from house. DF welded leak on can.
44 | 88-40091-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1988-06-17 | 1988-06-17 | Other |  | Steel/Wrought Iron |  | Sebastopol | SUC. rusted thru threads below stop cock
44 | 88-40160-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1988-11-30 | 1988-12-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Sebastopol | Had M&C replace, leaking H.P.R.
44 | 89-00002-1 |  |  | 8 | Transmission |  | Other Welds |  |  | Construction Defect |  | 1989-01-18 | 1989-03-15 | Patch Welded |  | Steel/Wrought Iron |  | Santa Rosa | Pressured leak on old patch. Weld leaking.
44 | 89-00009-1 |  |  | 8 | Distribution Feeder Main |  | Fitting |  |  | Construction Defect |  | 1989-02-07 | 1989-03-02 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Sebastopol | Tighten cap on 3/4" valve on 8" 150# main.
| 89-00013-1 |  |  | 12.75 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 1989-03-03 | 1989-10-03 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Geyser | Pinned Tee, Rewelded
44 | 89-40027-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1989-03-10 | 1989-05-15 | Clamp |  | Steel/Wrought Iron |  | Windsor | Installed 2 leak clamps on 6" HP main. 1 piece and 1 full circle stainless steel clamp
44 | 89-40143-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1989-08-04 | 1989-08-09 | Other |  | Steel/Wrought Iron |  | SEB | Replaced leaking relief to H.P.R.
44 | 89-40151-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Digin |  | 1989-08-19 | 1989-08-19 | Other |  | Steel/Wrought Iron |  | Windsor
| 89-40149-1 | [17 empty] | See Sketch
44 | 89-58034-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1989-07-19 | 1989-07-19 | Other |  | Steel/Wrought Iron |  | Penngrove | Removed leaking HPR
44 | 89-58054-1 |  |  | 12 | Transmission |  | Other |  |  | Other |  | 1989-11-03 | 1989-11-04 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Petaluma | C/O 1" drip and weld 2" save-a-valve over.
44 | 90-00000-1 |  |  | 0.75 | Service |  | Regulator |  |  | Corrosion |  | 1990-01-10 | 1990-01-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Santa Rosa | Replace HPR and fittings.
44 | 90-40049-1 |  |  | 2 | Distribution Main |  | Tap Connection |  |  | Construction Defect |  | 1990-02-26 | 1990-02-28 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Santa Rosa | Tighten cap on 2" split main fittings.
44 | 90-40058-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1990-04-19 | 1990-10-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Santa Rosa | Note: no HPR in bolts.
44 | 90-40059-1 |  |  | 4 | Distribution Feeder Main |  | Other Welds |  |  | Other |  | 1990-05-10 | 1990-05-23 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Santa Rosa | Repaired old can on tee.
44 | 90-40147-1 | 2 |  | 12 | Transmission |  | Body of Pipe |  |  | Digin |  | 1990-05-14 | 1990-05-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Geyserville | replaced 10" of 12" steel main.
44 | 90-40190-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Digin |  | 1990-07-23 | 1990-07-23 | Other |  | Steel/Wrought Iron |  | Windsor | C/O 3/4" HPR set
| 90-58061-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Digin |  | 1990-10-25 | 1990-10-25 | Replace Pipe |  | TR 418 |  | Petaluma | Replace 2" section of 2" pl. Try 8"-main. Repaired leak
44 | 91-58042-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1991-11-12 | 1991-11-12 | Clamp |  | Steel/Wrought Iron |  | Petaluma | Installed 8" skinned radar clamp (3 bolts) on 8" DFM
4 | 91-00007-1 |  |  | 8 | Other |  | Other |  |  | Other |  | 1991-11-06 | 1991-03-27 | Replace Pipe |  | Steel/Wrought Iron |  | Santa Rosa | GC replaced the 150# and the distribution in this area! 3/28/91 G.R.C.
4 | 91-40152-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other | MATERIAL FAILURE | 1991-07-25 | 1991-07-25 | Replace Pipe |  | Steel/Wrought Iron |  | Windsor | Replaced HPP or HPR.
44 | 91-58042-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1991-11-12 | 1991-11-13 | Clamp |  | Steel/Wrought Iron |  | Petaluma | replaced 8" skinner redar clamp (3 bolt) on 8" DFM
44 | 92-00004-1 |  |  | 2 | Other |  | Body of Pipe |  |  | Corrosion |  | 1992-01-24 | 1992-08-24 | Replace Pipe |  | Steel/Wrought Iron |  | Cloverdale | House Line replaced by owner
44 | 92-00004-1 | [10 empty] | 1992-01-24 | [5 empty] | Cloverdale
4 | 92-40142-1 |  |  | 0.75 | Service |  | Valves |  |  | Digin |  |  | 1992-06-19 | Other |  | Steel/Wrought Iron |  | Santa Rosa | Abandon old HPR will also have main abandon
44 | 92-58011-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1992-03-25 | 1992-03-25 | Patch Welded |  | Steel/Wrought Iron |  | Cotati | Welded Patch
44 | 93-40070-1 |  |  | 1.25 | Distribution Main |  | Valves |  |  | Other |  | 1993-03-01 | 1993-03-16 | Other |  | Steel/Wrought Iron |  | Santa Rosa | Fixed leak on HPR and raised box and greased buried. HP valve 15' away and installed new casing & box.
44 | 93-40164-1 |  |  | 3 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1993-09-01 | 1993-09-01 | Other |  | Steel/Wrought Iron |  | Healdsburg | Tighten up greased valve
44 | 94-00001-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1994-03-01 | 1994-07-13 | Replace Pipe |  | Steel/Wrought Iron |  | Santa Rosa | Found Corrosion leak on 8" HP. Replaced 12" of main.
4 | 94-40198-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1994-12-05 | 1994-12-05 | Other |  | Steel/Wrought Iron |  | Sonoma | Greased and operate valve
44 | 95-58052-1 | 21 |  | 0.75 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1995-11-02 | 1995-11-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Petaluma | Repair corrosion leak at gauge riser on N/S valve 2.54 (3/4"). Replaced 18" of 3/4" Seamless pipe w/same. Plugged off existing mueller. H.P. plug tee. 11/2/1995
44 | 95-00016-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe | Body of Pipe |  | Corrosion |  | 1995-03-07 | 1996-07-25 | Replace Pipe |  | Steel/Wrought Iron |  | Santa Rosa | 850' to the south. Abandon old 8" main and install new 8".
44 | 95-00019-1 |  |  | 0.75 | Distribution Feeder Main |  | Fitting |  |  | Corrosion |  | 1995-03-16 | 1995-04-03 | Patch Welded |  | Steel/Wrought Iron |  | Sonoma | Service tee leaking at weld. Leak welded up byG.C. with wire welder.
44 | 95-00020-1 |  |  | 6 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1995-03-16 | 1995-04-05 | Patch Welded |  | Steel/Wrought Iron |  | Sonoma | Welded up leaking tees. 1'1/4" valve tee and 3/4" service tee by G.C. with wire welder
44 | 95-00021-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 1995-03-16 | 1995-04-10 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Sonoma | redeoped and tightened service tee cap to dist. reg. #639
44 | 95-40066-1 |  |  | 8 | Transmission |  | Valves |  |  | Material Failure |  | 1994-12-29 | 1995-02-10 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Sonoma | Greased and tightened bolts on 8" valve.
44 | 95-40075-1 |  |  | 1 | Transmission |  | Fitting |  |  | Construction Defect |  | 1995-03-24 | 1995-04-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Santa Rosa | Tightened cap on 1" HP tee (service).
44 | 95-40138-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1995-08-23 | 1995-09-18 | Clamp |  | Steel/Wrought Iron |  | Healdsburg | Installed 4-full circle leak clamps
44 | 95-40138-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1995-08-23 | 1995-09-18 | Other |  | Steel/Wrought Iron |  | Healdsburg | replaced all main and service in area 8/2/96
44 | 95-40138-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1995-08-23 | 1995-09-18 | Clamp |  | Steel/Wrought Iron |  | Healdsburg | Replaced 4-full cirlcle leak clamps.
44 | 95-40224-1 |  |  | 0.75 | Distribution Main |  | Other |  |  | Damage by outside Forces |  | 1995-10-12 | 1995-10-12 | Other |  | Steel/Wrought Iron |  | Sebastopol | Closed valves and plugged
44 | 96-00004-1 | [10 empty] | 1996-03-21 | [5 empty] | Sonoma | Down Grade
44 | 96-00004-1 | [10 empty] | 1996-03-21 | [5 empty] | Sonoma
44 | 96-38012-1 |  |  | 0.75 | Service |  | Fitting |  |  | Material Failure |  | 1996-03-28 | 1996-04-01 | Replace Pipe |  | Steel/Wrought Iron |  | Cotati | Replaced leaking valve & re thread high pressure. Replace dist service with 1/2" PL Insert
44 | 96-58075-1 |  |  | 1.5 | Transmission |  | Valves |  |  | Other |  | 1996-07-31 | 1996-07-31 | Other |  | Steel/Wrought Iron |  | Penngrove | Greased 11/2" HP valve. Redoped 11/2" plug
44 | 96-58105- |  |  | 0.75 | Transmission |  | Regulator |  |  | Damage by outside Forces |  | 1996-12-23 | 1996-12-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Petaluma
44 | 97-40010-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Corrosion |  | 1997-01-28 | 1997-01-28 | Replace Pipe | TIGHTEN CAP OR BOLT | Steel/Wrought Iron |  | Healdsburg | Replace 3/4" & 1/2" nipples on HPR set.
44 | 97-38003-1 |  |  | 3 |  |  | Valves |  |  | Other |  | 1997-05-01 | 1997-06-18 | Other |  | Steel/Wrought Iron |  | Petaluma | Greased valves amd removed leaking recorder.
44 | 98-20027-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1998-03-24 | 1998-04-14 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Santa Rosa | On main (8" DFM) witch welded 2" sav-a-valve over pit and collar.
44 | 98-40028-1 |  |  | 0.75 | Service |  | Fitting |  |  | Digin |  | 1998-03-25 | 1998-03-25 | Other |  | Steel/Wrought Iron |  | Graton | Rewrap, service and repair HPR.
44 | 99-40050-1 |  |  | 6 | Distribution Feeder Main |  | Fitting |  |  | Digin |  | 1999-01-15 | 1999-01-15 | REPLACE PIPE |  | Steel/Wrought Iron |  | Windsor | Replaced all main & service in area.
44 | 99-40062-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1999-02-19 | 1999-05-05 | Other |  | Steel/Wrought Iron |  | Windsor | On 4" Kerotest valve replaced. Parking vendor assisted repair.
44 | 99-40065-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1999-02-26 | 1999-04-20 | Replace Pipe |  | Steel/Wrought Iron |  | Windsor | Replaced all main and services.
| 99-40065-1 | [10 empty] | 1999-02-26 | [5 empty] | Windsor | Drilled holes and vented
| 99-58019-1 | [5 empty] | Tap Connection |  |  | Digin |  | 1999-03-10 | 1999-03-10 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | Sonoma | Weld plug at outlet of abandoned mueller tee.
| 00-40070-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2000-04-10 | 2000-10-07 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | Santa Rosa | Marked with stakes bubbles on DFM.
| 00-40070-1 |  |  | 0.06 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  |  | 2000-10-07 | Clamp |  | Steel/Wrought Iron |  | Santa Rosa | Installed 6" clamp on DFM. Line found two bad pits in pipe leaking.
| 00-40191-1 |  |  | 3 | Transmission |  | Valves |  |  | Other | Dried grease | 2000-10-13 | 2001-02-21 | Other | Grease valve | Steel/Wrought Iron |  | Sebastopol | Repair CK ok. 0 read at valve. Greased valve
| 00-58081-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Material Failure |  | 2000-12-20 | 2000-12-30 | Other | Greased valve | Steel/Wrought Iron |  | Sonoma | 3/4" 150# Valve to Dist. Reg. #571No inspection greased valve only.
| 01-40098-1 |  |  | 0.75 | Service |  | Riser |  |  | Digin |  | 2001-05-21 | 2001-05-21 | Service Partially Replaced |  | Steel/Wrought Iron |  | Sebastopol | At H.P.R. Replaced service HPR
| 01-40101-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Digin |  | 2001-10-22 | 2001-10-22 | Service Partially Replaced |  | Steel/Wrought Iron |  | Healdsburg | Over dig-in, squeezed off, repaired. Moved H.R.P. to short side of the street. Inserted service across the street.
| 01-40244-1 | 21 | 57.73 | 12 | Transmission |  |  |  |  | Digin |  | 2001-12-16 | 2001-12-16 | Replace TP Main | OTHER | Steel/Wrought Iron |  | Windsor | 450# blowing gas. By pass & replace 12" line
| 01-38007-1 | 21 |  | 12 | Transmission |  | Valves |  |  | Material Failure |  | 2001-04-11 | 2002-02-22 | Other | REPLACE VALVE BODY BLEED OFF | Steel/Wrought Iron |  | Cotati | Found 1/2" street ell for valve body. Bleed off cracked-replaced.
| 02-58013-1 | 21 | 43.37 | 12 | Transmission |  | Valves |  |  | Other |  | 2002-02-22 | 2002-02-22 | Other |  | Steel/Wrought Iron |  | Cotati | Valve 43.37 cheacking old leak 0138007-1. replace valve body bleed off.
| 01-38007-1 | [10 empty] | 2001-04-11 | [5 empty] | Cotati | Deleted tag. Original should be in Petaluma
| 01-38007-1 | 21 |  | 12 | Transmission |  | Valves | Valves |  | Material Failure |  | 2001-04-11 | 2002-02-22 | Other | REPLACE VALVE BODY BLEED OFF | Steel/Wrought Iron |  | Cotati | at Valve 43.37 body bleed off. Found 1/2" street ell for valve body bleed off cracked replaced
| 01-38007-1 | 21 | 43.37 | 12" | Transmission |  | Valves |  |  | Material Failure | OTHER | 2001-04-11 | 2002-02-22 | Other | Replace valve body bleed off | Steel/Wrought Iron |  | Cotati | At valve 43.37 body bleed off. Found 1/2" street ell for valve body bleed off cracked-replaced.
| 01-58011-1 | 21 | 35.22 | 12 | Transmission |  | Fitting |  |  | Construction Defect |  | 2001-02-27 | 2001-03-20 | Other | TIGHTEND COMPLETION PLUG | Steel/Wrought Iron |  | Petaluma | Outside pit. Tightend completion plug on 2" sav-a-valve
| 02-20001-1 | [10 empty] | 2002-01-29 | [5 empty] | Santa Rosa | Op. 082485 downgrade to grade 3
| 02-40115-1 | DFM |  | 6 | Transmission |  | Fitting | Physical/Mechanical Joint | Physical/Mechanical Joint | Construction Defect |  | 2002-07-10 | 2002-07-11 | Replace TP Main |  | Steel/Wrought Iron |  | Sebastopol | Removed leaking dresser fitting. Welded in 2' of 6" pipe
| 02-40193-1 |  |  | 0.5 | Service |  | Plastic Tee Cap |  |  | Construction Defect |  | 2002-12-17 | 2003-01-17 | Tighten Cap/Bolt - Fitting |  | TR 418 |  | Santa Rosa | Replaced damaged cap. Explanation- we responded to this leak on the day it was called in 12/17/02. We got the gas away from the buildingand were able to downgrade it. It was difficult to pinpoint, but we kept going back until we got it cleared beacuse there was still odor and customer was concerned.
| 02-58013-1 | 21 | 43.37 | 12 | Transmission |  | Valves |  |  | Other |  | 2002-02-22 | 2002-02-22 | Other |  | Steel/Wrought Iron |  | Cotati | Valve 43.37 checking old leak 01-380071
| 02-58013-1 | 21 | 43.37 | 12 | Transmission |  | Valves |  |  | Other |  | 2002-02-22 | 2002-02-22 | Other |  | Steel/Wrought Iron |  | Cotati | Valve 43.37 checking old leak 01-380071
| 02-58023-1 |  |  | 1.25 | Service |  | Other |  | HPR | Other | UNIONS | 2002-05-02 | 2002-05-02 | Service Entirely Replaced | Replace HPR | Steel/Wrought Iron |  | Sonoma | Found buried HPR leaking. Replace buried HPR, box, and entire service
| 03-40082-1 | 1305-01 |  | 8 | Transmission |  | Body of Pipe |  |  | Digin |  | 2003-10-25 | 2003-10-25 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | Santa Rosa | On now. Installed (2) 8" repairs leaks x.500wt.
| 03-40192-1 | [10 empty] | 2003-11-19 | [5 empty] | Santa Rosa | Reissued new# for LK. 03-20182 that was worked as svc rerun. Need T&R to locate mains in area using tinker beacause of bad signal & possible contacts.
| 03-40192-1 | [10 empty] | 2003-11-19 | [5 empty] | Santa Rosa | Reissued new# for LK. 03-20182 that was worked as service rerun. Need T&R to locate mains in area using tinker because of bad signal & possible contacts. make package for adrian to work this leak tag & map. Use this as plug foam.
| 03-00001-1 | 1305-01 |  | 6 | Transmission |  | Other | Clamp | Clamps | Construction Defect |  | 2003-10-15 | 2004-11-10 | Replace TP Main |  | Steel/Wrought Iron |  | Santa Rosa | 15" s/o scada shack over main. 15" n/o shack over main in parking. Replaced 7' of pipe.
| 03-00002-1 | 1303-01 |  | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2003-10-15 | 2003-10-16 | Deactivate #TP Main |  | Steel/Wrought Iron |  | Santa Rosa | Pit let loose during upgrade. Cut out section of pipe & installed 8" dead-end cap
| 03-00002-1 | [10 empty] | 2003-10-15 | [5 empty] | Santa Rosa | 15' FR S?W corner
| 03-00003-1 | 1303-01 |  | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2003-10-15 | 2003-10-16 | Deactivate #TP Main |  | Steel/Wrought Iron |  | Santa Rosa | Multiple pitts cut & cap main. Weld on 8" dead end cap.
| 03-00003-1 | [10 empty] | 2003-10-15 | [5 empty] | Santa Rosa | At main off-set
| 03-00004-1 |  |  | 8 | Transmission |  | Valves |  |  | Construction Defect |  | 2003-10-15 | 2003-10-23 | Replace Valve >= 2 inch |  | Steel/Wrought Iron |  | Santa Rosa | Replaced leaking valve 8" kerotest.
| 03-20182-1 |  |  | 0.75 | Service |  | Unknown |  |  | Unknown |  | 2003-10-15 | 2003-11-19 | Service Entirely Replaced |  | Steel/Wrought Iron |  | Santa Rosa | At gutter at edge of concrete and AC S/E COR Montgomery Dr. and Sotoyome. Rerun gas service with 1/2" PL insert
[5 empty] | Branch Service | [10 empty] | Steel/Wrought Iron |  | Sonoma
|  |  |  | 6 | [11 empty] | Steel/Wrought Iron |  | Sonoma
| 03-58034-1 | 1305-01 |  | 0.6 | Transmission |  | Fitting |  |  | Damage by 3rd Party | DIG-IN | 2003-07-10 | 2003-07-11 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | Sonoma | Welded sleeve A0824-01/02
|  |  |  | 6 | Transmission |  | Body of Pipe | Body of Pipe |  | Digin |  |  | 2003-07-10 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | Sonoma | Installed sleeve #A0824-01/02 6"/16" x .500 wall
| 03-58034-1 | 1305-01 |  | 6 | Transmission |  | Fitting |  |  | Digin |  | 2003-07-10 | 2003-07-11 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | Sonoma | 9' FR. W/PL Broadway and Newcome
|  |  |  | 2 | [11 empty] | Steel/Wrought Iron |  | Santa Rosa
| 03-58034-1 |  |  | 2 | Transmission |  | Fitting |  |  | Damage by 3rd Party | Dig-In | 2003-07-10 |  |  |  | Steel/Wrought Iron |  | Sonoma
| 04-40081-1 | 1305-01 |  | 3 | Transmission |  | Valves |  |  | Material Failure | O Ring | 2004-09-08 | 2005-09-01 | Other |  | Steel/Wrought Iron |  | Santa Rosa | At valve cluster strong odor V8.63. Replaced double "O" Ring seal in valve
| 05-20004-1 |  |  | 8 | Transmission | [6 empty] | 2005-08-15 | 2005-08-29 |  |  | Steel/Wrought Iron |  | Sonoma | At reg 684 2% around HPR box. Could not find leak.
| 05-40065-1 |  |  | 2 | Transmission |  | Valves |  |  | Other | Mechanical | 2005-03-03 | 2005-03-18 | Replace Valve >= 2 inch |  | Steel/Wrought Iron |  | Healdsburg | Valve 15' W/O HPR. Replaced valve
| 05-40088-1 | 1302-02 |  | 6" | Transmission |  | Valves |  |  | Construction Defect |  | 2005-11-03 | 2006-12-02 | Replace Valve >= 2 inch |  | Steel/Wrought Iron |  | Sebastopol | Flange valve leak at reg #408-CGT to dra same-reg station to be replaced this sum. Replaced valve
| 05-40136-1 | 135-01 |  | 6" | Transmission |  | Valves |  |  | Material Failure |  | 2005-09-21 | 2005-09-23 | Welded Sleeve/Can - Weld |  | Other | Steel | Glen Ellen | In backyard near poplar tree/odor/uprate. Installed teo PCF & can
| 05-40136-1 | 135-01 |  |  |  |  | Valves |  |  | Material Failure |  | 2005-09-21 | 2005-09-23 | Welded Sleeve/Can - Weld |  |  |  | Glen Ellen | In backyard near poplar tree/odor/uprate. Cut in 20" section of 6" gas main.
| 06-40142-1 |  |  | 0.75 | Single Service |  | Body of Pipe |  |  |  |  | 2006-09-18 | 2006-09-18 | Replace Partial Service |  | Steel/Wrought Iron |  | Healdsburg | Top tap-Bussnut-28' of TR418-Air Test-CGI
| 06-40130-1 |  |  | 1 | Branch Service |  | Body of Pipe |  |  |  |  | 2006-08-25 | 2006-08-25 | Replace Partial Service |  | TR 418 |  | Cloverdale | Replace 6" of 1" PL with 1 metfit
| 06-40116-1 |  |  | 0.5 | Branch Service |  | Body of Pipe |  |  |  |  | 2006-07-26 | 2006-07-26 | Replace Partial Service |  | TR 418 |  | Santa Rosa | Installed (2) 1/2" perfection coupling & 12" of 1/2" plastic
| 07-40023-1 |  |  | 1 | Branch Service |  | Riser |  |  |  |  | 2007-03-22 | 2007-03-22 | Other | RISER ONLY | TR 418 |  | Santa Rosa | Replaced 11/4 Riser with by-pass
| 07-40028-1 |  |  | 0.5 | Single Service |  | Body of Pipe |  |  |  |  | 2007-04-04 | 2007-04-04 | Replace Partial Service |  | TR 418 |  | Healdsburgh | Install 2 perfection & 1' TR418- air test
| 07-40032-1 |  |  | 0.75 | Branch Service |  | Body of Pipe |  |  |  |  | 2007-04-12 | 2007-04-12 | Replace Entire Service |  | Steel/Wrought Iron |  | Santa Rosa | replaced service to 1428
| 07-40215-1 |  |  | 1 | Branch Service |  | Body of Pipe |  |  |  |  | 2007-11-01 | 2007-01-01 | Replace Partial Service |  | TR 418 |  | Santa Rosa | Used 1 2" repair coupling
| 08-41016-1 |  |  | 0.75 | Single Service | [6 empty] | 2008-03-05 | 2008-03-06 | Deactivated Entire Service |  | Steel/Wrought Iron |  | Santa Rosa | C/O Service at main
| 09-00247-1 | 1307-01 |  | 0.75 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 2009-04-13 | 2009-07-01 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | Santa rosa | Redoped cap and tighten
| 09-00472-1 | 021E | 68 | 0.75 | Single Service |  | Body of Pipe |  |  | External Corrosion |  | 2009-07-13 | 2009-08-20 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | Healdsburg | Installed 3/4" skinner clamp on 3/4" steel services
| 09-00467-1 | [10 empty] | 2009-07-13 | [5 empty] | Petaluma | Orchard Ln. e/s/o 101. over 12" TP between main
| 09-00465-1 | 1307-01 |  | 2 | Transmission |  | Valves |  |  | Unknown |  | 2009-07-09 | 2009-08-07 | Other | Greased | Steel/Wrought Iron |  | Windsor | At valve V-2.84 V-A&V-B. Shrloh & Corde W Windsor. Greased. No USA (Work in vault
| 09-00435-1 | 1305-01 |  | 0.75 | Transmission |  | Line Valve |  |  | Other |  | 2009-06-10 | 2011-02-08 | Greased - Other |  | Steel |  | Sonoma | Greased valve
| 09-00420-1 | DFM 1301 | 28.82 | 8 | Transmission |  | Valves |  |  | Material Failure |  | 2009-06-30 |  |  |  | Steel/Wrought Iron |  | Penngrove
| 09-00409-1 |  |  | 2" | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2009-05-15 | 2009-08-01 | Tighten Cap/Bolt - Fitting | Redoped | Steel/Wrought Iron |  | Santa Rosa | Redoped and tightened cap. New s/o should show up for alteration 1/2" PL inserted in 3/4
| 09-00320-1 | dfm 1301 | 28.82 | 8 | Transmission |  | Valves |  |  | Material Failure |  | 2009-03-25 | 2009-04-07 | Replace TP Main |  | Steel/Wrought Iron |  | Penngrove | In ETS box (HCA) 100ppm V28.82.1%
| 09-00312-1 | 21A |  | 12" | Transmission |  | Valves |  |  | Unknown |  | 2009-03-19 | 2010-09-16 | Other | GREASED | Steel/Wrought Iron |  | Sonoma | Greased valve
| 09-00684-1 | DFM 1302-2 |  | 125 | Single Service |  | Fitting |  |  | Construction Defect |  | 2009-12-01 | 2011-05-25 | Other | BY PASS FITTING & VALVE | Steel |  | Graton | Replaced all fitting on by pass
| 09-00670-1 | 1305-01 |  | 6 | Transmission |  | Fitting |  |  | Unknown |  | 2009-11-02 | 2009-11-04 | Other | 6" PCF top | Steel/Wrought Iron |  | Sonoma | Leak on PCF. Spring in cater of completion plug leaking. Replaced spring while doing valve replacement.
|  | 1305-01 |  | 6 | Transmission |  | Fitting |  |  | Unknown |  |  | 2009-11-04 | Other | 6" PCF top | Steel/Wrought Iron |  | Sonoma | Leak on PCF. Spring in cater of completion plug leaking. Replaced spring while doing valve replacement
| 09-00974-1 |  |  | 0.75 | Gathering |  | Valves | Other | riser Threads | Other | Riser Threads | 2009-04-03 | 2009-04-30 | Soap and/or Tape - Other | Tightened valve (New riser installed recently) | Steel/Wrought Iron |  | Petaluma | Tightened loose svc valve on 9 more manifold. Soap tested+;
| 08-10482- |  |  | 1.25 | Branch Service |  | Valves |  |  | Other | Threads | 2008-02-07 | 2008-02-07 | Replace Valve >= 2 inch |  | Steel/Wrought Iron |  | Cotati | Leak at riser threads. replaced service valve, regulator, and required 2nd leak at manifold elbow, soap
| 08-02657- |  |  | 2 | Transmission |  | Valves |  |  | Other | Grease | 2008-09-26 |  |  |  | Steel/Wrought Iron |  | Sonoma | Gas Leak
| 08-02611-1 |  |  | 0.75 | Single Service |  | Valves |  |  | Other | Threads | 2008-09-23 | 2008-11-19 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | Petaluma | Replaced stop cock
| 08-02569- | [5 empty] | Valves |  |  |  |  | 2008-09-30 | [5 empty] | Sonoma
| 08-02569-1 | 1306-01 |  | 3 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other |  | 2008-09-30 | 2011-02-09 | Tighten Cap/Bolt - Fitting |  | Steel |  | Sonoma | Tighten bolts
| 08-02229-1 |  |  | 0.75 | Branch Service |  | Valves |  |  | Unknown |  | 2006-07-18 | 2008-08-23 | Other | TIGHTEN VALVE | Steel/Wrought Iron |  | Petaluma | Tightened valve
| 08-02087-1 | DFM 1302-02 |  | 6 | Transmission |  | Tap Connection |  |  | Construction Defect | CAP NOT TIGHT | 2008-11-24 | 2008-12-08 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | Sebastopol | Redoped and Tighten cap
| 08-02043-1 |  |  | 8 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 2008-04-16 | 2010-07-15 | Other | 8" Plidco clamp | Steel/Wrought Iron |  | Santa Rosa | Installed 8" clamp on T-P
| 08-02037-1 |  |  | 8 | Transmission |  | Valves | Other | Above drip | Other | Various leaks on valve |  | 2009-08-27 | Welded Sleeve/Can - Weld
| 08-02036-1 | 1301-01 |  | 8 | Transmission |  | Drip |  |  | Unknown |  | 2008-04-09 | 2009-10-09 | Other | REPLACED 4' TRANS MAIN | Steel/Wrought Iron |  | Penngrove | Removed drip
| 08-02035-1 | 3851661 |  | 4 | Transmission |  | Valves |  |  | Other | Leaking valves | 2008-04-09 | 2009-09-10 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | Petaluma | cut out 4" valves and bridol connected 2 reg 484. Installed 7'can 8' / also cut of reg 484 from dist. side
| 08-02034-1 |  |  | 8" | Transmission | DFM | Body of Pipe |  |  | External Corrosion |  | 2008-04-08 |  |  |  | Steel/Wrought Iron |  | Cotati | Over main & service of given address
| 08-02025-1 |  |  | 4" | Transmission |  | Valves |  |  | Other | bolts on 4" ball valve | 2008-03-31 |  |  |  | Steel/Wrought Iron |  | Petaluma | Leaky 4' valve welded to 5x4 tee with 90'. Welded to other side of valve. Looking up leak bubbles coming out bolts and or ball valve.
| 08-02012-1 | 1119SR |  | 6 | Transmission |  | Other |  | Center plug on 6" muller leaking | Unknown |  | 2008-03-13 | 2008-03-13 | Other | Center plug on 6" muller fitting | Steel/Wrought Iron |  | Windsor | Removed, redoped, and tape then replaced center plug on 6" muller
| 08-02011-1 | [10 empty] | 2008-02-04 | [5 empty] | Fulton | HCA on 6" HP main
| 08-02011-1 | 21E | 61.06 | 0.75 | Transmission |  | Girth Weld |  |  | Unknown |  | 2008-03-06 | 2008-03-06 | Patch Weld - Weld |  | Steel/Wrought Iron |  | Windsor | Weld leak on previous weld at HPR box
| 08-02010-1 |  |  | 6" | Distribution Main |  | Unknown |  |  | Unknown |  | 2008-03-04 | 2009-10-27 | Replace Dist Main >= 100 ft |  | Steel/Wrought Iron |  | Santa rosa | Replaced 6" steel main
| 08-02008-1 | 21E | 85.92 | 0.75 | Single Service |  | Regulator |  |  | Material Failure |  | 2008-02-28 | 2008-02-29 | Other | H.P.R. | Steel/Wrought Iron |  | Cloverdale | Soap
| 08-02008-1 | 21E | 85.92 | 0.75 | Single Service |  | Regulator |  |  | Material Failure |  | 2008-02-28 | 2008-02-29 | Other | H.P.R. | Steel/Wrought Iron |  | Cloverdale | Soap
| 08-02007-1 | [10 empty] | 2008-02-07 | [5 empty] | Healdsburg | No reading along 12" T.P
| 08-02000-1 | 021E | 65.58 | [8 empty] | 2008-01-22 | [5 empty] | Healdsburg | Poss dist. leak
| 08-02001-1 | 021E | 66 | [8 empty] | 2008-01-22 | [5 empty] | Healdsburg | Poss Dist Leak
| 08-02002-1 | 021E | 65.58 | [8 empty] | 2008-01-22 | [5 empty] | Healdsburgh | Poss Dist leak
| 08-02003-1 | 021E | 64.36 | [8 empty] | 2008-01-23 | [5 empty] | Healdsburg | PGE valve yard M.P. 64.36 made grade 2 because of proximity to hywy 101
| 08-02004-1 | 021E | 68 | 0.75 | Single Service |  | Unknown |  |  | Unknown |  | 2008-02-06 |  |  |  | Steel/Wrought Iron |  |  | Soap tested ok. Could not find leak vaulted .5%
| 08-11835-1 | [10 empty] | 2008-02-15 |  |  |  |  | Fuzz leak on stem. Fuzzed no leaks suggest. recheck in 6 months. Soap tested-Found no fuzz leak. Used gas ranged, no readings. Have T&R recheck in 6 months | Santa Rosa
| 08-11781-1 | 21C |  | 12.00" | Transmission |  | Fitting |  |  | Other |  | 2008-01-21 | 2009-01-14 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | Santa Rosa | Fixed leaks on orifice meter
| 08-12391-1 | 1126 |  | 1.25 | Transmission |  | Regulator |  |  | Other | Threads | 2008-03-12 | 2008-06-02 | Tighten Cap/Bolt - Fitting | FITTINGS | Steel/Wrought Iron |  | Glen Ellen | Fizz leaks on reg. Needs M&C
| 08-12279- |  |  | 0.75 | Distribution Main |  | Valves |  |  | Other |  | 2008-03-06 | 2008-03-06 | Other | Greased | Other |  | Graton | Valve 2&7. At valve
| 08-14170-1 |  |  | 0.75 | Gathering | Single Service | Valves | Valves |  | Other | LOOSE VALVE DRY PIPE DOPE | 2008-03-19 | 2008-04-25 | Other | TIGHTENED & DOPED SHUT OFF VALVE | Steel/Wrought Iron |  | Petaluma | Re Doped, Retightened, Shut off valve
76 |  |  |  | 2 | Distribution Main |  | Valves |  |  | Material Failure |  | 1970-10-13 |  | Other |  | Steel/Wrought Iron |  | Petaluma | Replaced valve and tighten packing nuts on top of valves
44 | 71-18003- |  |  | 8 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1971-03-16 | 1971-05-20 | Other |  | Steel/Wrought Iron |  | Cotati | Found 2" blow off. Leaking-greased same. Stopped leak
44 | 71-38007- |  |  | 200 | Other |  | Tap Connection |  |  | Corrosion |  | 1971-07-21 | 1971-07-21 | Other |  | Steel/Wrought Iron |  | Penngrove | Repaired leaking plug on service tee, still leakage on service which is p. had badly. Should be renewed
44 | 71-58002- |  |  | 75 | Service |  | Fitting |  |  | Other |  | 1971-10-06 | 1971-10-06 | Other |  | Steel/Wrought Iron |  | Petaluma | Abandoned service tee (homemade) had no plug. Had to redoped cap that was leaking and replace with new cap.
44 | 71-58004- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1971-05-26 | 1971-05-26 | Other | WELDED PITS | Steel/Wrought Iron |  | Petaluma | Needed up (2) small pits and telephone pole 80115
44 | 71-58005- |  |  | 0.5 | Service |  | Other |  |  | Damage by outside Forces |  | 1971-07-22 | 1971-07-22 | Other |  | Other Plastic |  | Petaluma | Put in piece with use of compression type couplings
44 | 71-58007- |  |  | 0.5 | Service |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1971-06-06 | 1971-06-07 | Replace Pipe |  | Other Plastic |  | Cotati | Replaced plastic to steel fitting at riser with compression fitting riser.
257 | 71-58015- |  |  | 3 | Distribution Main |  | Other |  |  | Material Failure |  | 1971-04-02 | 1971-04-02 | Patch Welded |  | Steel/Wrought Iron |  | Petaluma | Both valves leaking.
76 | 71-58016- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1971-05-19 | 1971-05-19 | Patch Welded |  | Steel/Wrought Iron |  | Petaluma
44 | 71-58017- |  |  | 16 | Transmission |  | Body of Pipe |  |  | Other |  | 1971-05-21 | 1971-05-25 | Other |  | TR 418 |  | Santa Rosa | Made neccessary performance repair to condensation line on 16"
44 | 71-58017- |  |  | 2 | Other |  | Fitting |  |  | Other |  | 1971-07-01 | 1971-07-01 | Other |  | Steel/Wrought Iron |  | Petaluma | Redoped plug and cap on 2" PCF
44 | 71-58018- |  |  | 0.75 | Service |  | Other |  |  | Damage by outside Forces |  | 1971-06-02 | 1971-06-02 | Replace Pipe |  | Steel/Wrought Iron |  | Petaluma | Broken service, Jumped in piece of plastic
44 | 71-58019- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1971-05-26 | 1971-05-26 | Other |  | Other |  | Petaluma
44 | 71-98004- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-06-07 | 1971-06-07 | Clamp |  | Steel/Wrought Iron |  | Petaluma | Made temporary repair to main and permanent repairs to service cap on tee and pit on service
44 | 71-98006- |  |  | 2 | Distribution Main |  | Fitting |  |  | Other |  | 1971-06-18 | 1971-06-18 | Other |  | Steel/Wrought Iron |  | Petaluma | Redoped and tighten plug and cap on 2" P.C.F.
4 | 78-40158-1 |  |  | 1.25 | Service |  | Fitting |  |  | Damage by outside Forces |  | 1978-04-12 | 1978-04-12 | Other |  | Steel/Wrought Iron |  | Santa Rosa | 1 1/4" screwed pipe to drip. Location was pulled up. Damage by county rd. dept. Cleaning out ditches made temp. Prepare to stop leaking fittings. Will ask walt about cut-off at main. Temp repair made 4-12-1978. Cut off and seal. Completed 4/13/1978
44 | 78-40202-1 |  |  | 75 | Transmission |  | Fitting |  |  | Damage by outside Forces |  | 1978-10-25 | 1978-10-25 | Replace Pipe and/or Service |  | Steel/Wrought Iron
4 | 80-58022-1 | 21 |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1980-04-28 | 1980-04-28 | Other |  | Steel/Wrought Iron |  | On Southerly Xing | pipe not exposed, under river. River Xing valves V-2.60 & V-2.70 Closed on 4/28/1980. Main shut off across river
44 | 80-58029-1 | 21 |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1980-06-23 | 1980-06-26 | Patch Welded |  | Steel/Wrought Iron |  | Petaluma | Weld 12" half-sole, 13" long to repair leak. inst. 32 lb. Anode same location.
44 | 80-58038-1 |  |  | 0.16 | Transmission |  | Fitting |  |  | Other |  | 1980-07-17 | 1980-10-08 | Other |  | Steel/Wrought Iron |  |  | Greased valve
44 | 80-58052-1 |  |  | 16 | Transmission |  | Valves |  |  | Other |  | 1980-11-03 | 1980-11-06 | Other |  | Steel/Wrought Iron |  |  | Greased valve in H.P.R. box
44 | 80-58059-1 |  |  | 0.75 | Transmission |  | Regulator |  |  | Damage by outside Forces |  | 1980-12-31 | 1980-12-31 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Petaluma | Repaired by valving & replacing 3/4" by pass. Car broke 3/4" 450 lb. Pipe in HPR box
44 | 73-00008-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1973-02-13 | 1973-04-02 | Other |  | Steel/Wrought Iron |  | Healdsburg | Leak detection compound. Flange leaking on inlit valve to valve pit. Tightened bolts
44 | 73-00029-1 |  |  | 0.75 | Other |  | Valves |  |  | Other |  | 1973-03-15 | 1973-03-22 | Other |  | Steel/Wrought Iron |  | graton
44 | 73-00043-1 |  |  | 2 | Other |  | Valves |  |  | Other |  | 1973-04-05 | 1973-04-12 | Other |  | Steel/Wrought Iron |  | Sebastopol | All clear 6/7/93
44 | 73-00044-1 |  |  | 2 |  |  | Valves |  |  | Other |  | 1973-04-05 | 1973-04-12 | Other |  | Steel/Wrought Iron |  | Sebastopol | All clear 6/7/73
44 | 73-20067-1 |  |  | 2 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1973-07-05 | 1973-09-17 | Other |  | Steel/Wrought Iron |  | Graton | Greased valve
44 | 73-20154-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1973-07-16 | 1973-09-13 | Other |  | Steel/Wrought Iron |  | Santa Rosa | Greased valve
44 | 73-40186-1 |  |  | 8 | Distribution Feeder Main |  | Valves |  |  | Damage by outside Forces |  | 1973-09-24 | 1973-10-12 | Other |  | Steel/Wrought Iron |  | Santa Rosa | Grease stem broken off
44 | 73-40226-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-11-23 | 1973-11-23 | Clamp |  | Steel |  | Healdsburg | C.P.A. # 566-01. Leak close to same area. See LK# 40133. Leak on main 2' North of service "T" 12 204 old rd hwy
44 | 71-00001- |  |  | 12 | Transmission |  | Valves |  |  | Other |  | 1971-03-16 | 1971-03-16 | Other |  | Steel/Wrought Iron |  | Santa Rosa | 2-2" valves leaking. Greased repaired
44 | 71-20032- |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1971-05-25 | 1972-12-15 | Patch Welded |  | Steel/Wrought Iron |  | Santa Rosa
44 | 71-40063- |  |  | 8 | Transmission |  | Valves |  |  | Material Failure |  | 1971-11-27 | 1971-10-27 | Other |  | Steel/Wrought Iron |  | Santa Rosa | A 2" valve off of the 8" H.P. gs main was leaking in the ground. I greased the valve & stopped leakage. We rewrapped valve.
44 | 72-00011-1 |  |  | 6 | Distribution Feeder Main |  | Regulator |  |  | Other |  | 1972-04-03 | 1972-04-20 | Other |  | Steel/Wrought Iron |  | Windsor | We tightened union. We bar tesred main. No sign of leakage
44 | 72-40018-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-02-02 | 1972-02-10 | Clamp |  | Steel/Wrought Iron |  | Windsor | Installed 3" clamp and wrapped. 2/14/72
44 | 72-40063-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-07-21 | 1972-07-21 | Clamp |  | Steel/Wrought Iron |  | Santa Rosa
44 | 72-40123-1 |  |  | 8 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1972-12-20 | 1973-01-23 | Other |  | Steel/Wrought Iron |  | Santa Rosa | Flange was leaking
44 | 74-00006-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-01-31 | 1974-02-08 | Clamp |  | Steel/Wrought Iron |  | Windsor S.W | Installed 1-6" clamp. 4/17/74 Installed 360 Clamp 3ft S. of first clamp
44 | 74-40090-1 |  |  | 2 |  |  | Fitting |  |  | Other |  | 1974-07-29 | 1974-08-27 | Other |  | Steel/Wrought Iron |  | Healdsburg | No gas indication. Replaced cap and tightened. 11/4" SHU-H-valve was leaking at cap
44 | 71-39007- |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1971-12-15 | 1971-12-15 | Replace Pipe |  | Steel/Wrought Iron |  | Sonoma
44 | 71-59003- |  |  | 0.75 | Other |  | Fitting |  |  | Material Failure |  | 1971-01-19 | 1991-01-19 | Other |  | Steel/Wrought Iron |  | Shellville | Installed 2" save-a-valve over exist. 3/4 nipples. Exist 6" reinforcing ring. Note: *Built up weld on reinforcing ring to a 45. 450'-3/4" condensate line abandoned in place
44 | 73-59020-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-12-20 | 1973-12-24 | Replace Pipe and/or Service |  |  |  | Sonoma | Service replaced with plastic insert
16 | 79-00274-1 |  |  | 1.25 | Service |  | Fitting |  |  | DAMAGE BY OUTSIDE FORCES |  | 1979-08-01 | 1979-08-01 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Stockton
16 |  |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1979-08-07 | 1979-08-07 | CLAMP |  | Steel/Wrought Iron |  | Stockton
16 |  |  |  | 2 | Distribution Main |  | Fitting |  |  | Corrosion |  | 1979-08-07 | 1979-08-07 | CLAMP |  | Steel/Wrought Iron |  | Stockton
16 | 85-00102- |  |  | 6 | Distribution Feeder Main | [6 empty] | 1985-05-09 |  |  |  | Steel/Wrought Iron |  | Ione
| 01-02276-1 |  |  |  | Transmission |  | Valves |  |  | Other | Valve Lubed | 2001-05-03 | 2003-10-09 | Other | Lubed valve | Steel/Wrought Iron |  | Stockton
|  | 108-C |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 108C |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron
93 | 72-40517-1 | 140 |  | 6 | Transmission |  | Body of Pipe |  |  | DAMAGE BY OUTSIDE FORCES |  | 1972-09-15 | 1972-09-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Lodi
| 06-01136- |  |  | 0.75 | Service |  | Regulator |  |  | Damage by Natural Forces |  | 2006-10-17 | 2006-10-17 | Service Partially Replaced |  | Steel/Wrought Iron |  | Lodi
16 |  | 139-140.3 |  | 300 | Transmission | [6 empty] | 1983-07-12 |  |  |  | Steel/Wrought Iron |  | Acampo
| 05-01127- | 139 |  | 0.75 | Single Service |  | Other |  | HPR blow off |  |  | 2005-08-24 | 2005-08-24 | Other | REPLACED HPR BLOW OFF | Wrought Iron | Steel | Acampo
09-02015-1
| 05-01063- | [5 empty] | Fitting |  |  | Digin |  | 2005-04-19 | 2005-04-19 | Tighten Cap or Bolt |  | Steel |  | Acampo | Shut HPR down & capped svc due to pending alteration
| 05-01063- | [5 empty] | FITTING |  |  | DIGIN |  | 2005-04-19 | 2005-04-19 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Acampo | Shut HPR down and capped svc due to pending alterations
93 | 98-01077-1 |  |  | 6 |  |  | Body of Pipe |  |  | Digin |  | 1998-07-23 | 1998-07-23 | Replace Pipe |  | Steel/Wrought Iron
93 | 75-40014-1 | 140 |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-08-09 | 1975-08-11 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Acampo
|  | 140 |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
|  | 140 |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 140 |  |  | Transmission
|  | 140 |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Acampo
93 | 78-00663-1 | 140 |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-11-17 | 1978-11-17 | Patch Welded |  | Steel/Wrought Iron |  | Lodi | LEAKAGE WAS CAUSED BY INTERNAL CORROSION. TR WELDED HAY SOLE TO REPAIR.
93 | 73-02023-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-01-15 | 1973-01-30 |  |  | Steel/Wrought Iron
93 | 80-00316-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-09-11 | 1980-09-11 | WELD OVER SLEEVE OR CAN
|  |  |  | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron
|  |  |  | 3 | [11 empty] | Steel/Wrought Iron
|  |  |  | 3 | Transmission | [10 empty] | Steel/Wrought Iron
93 | 93-01004-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1993-01-30 | 1993-01-30 | Replace Pipe |  | Steel/Wrought Iron
| 89-00230-1 |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1989-04-28 | 2003-11-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Stockton
93 | 79-00298-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Other |  | 1979-08-30 | 1979-08-30 | Other |  | Steel/Wrought Iron |  | Clements
16 |  |  |  | 12 | Transmission | [6 empty] | 1985-11-07 |  |  |  | Steel/Wrought Iron
| 09-02037-1 | 196 |  | 0.75 | Single Service |  | Regulator |  |  | Other | REUGLATOR LEAKING @ THREADS | 2009-03-17 | 2009-04-09 | Other | TIGHTENED NIPPLES GOING INTO FISHER 62T | Steel/Wrought Iron |  | Lodi
93 | 72-40511-1 |  |  | 0.75 | Distribution Feeder Main |  | Fitting |  |  | Material Failure |  | 1972-06-02 | 1972-07-17 | Other | Regulator | Steel/Wrought Iron
| 00-00005-1 |  |  | 4 | Transmission |  | Valves |  |  | Other | Valve Leak | 2000-05-16 | 2000-05-22 | Other | Greased valve | Steel/Wrought Iron |  | Woodbridge
93 | 74-40013-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Material Failure |  | 1974-08-28 | 1976-05-05 | Other |  | Steel/Wrought Iron |  | Lodi
93 | 78-00717-1 |  |  | 0.75 | Service |  | Fitting |  |  | CONSTRUCTION DEFECT |  | 1978-11-29 | 1979-10-10 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron
| 09-02744-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | DOPED/TIGHTENED GAUGE TAP | 2009-11-25 | 2010-01-22 | TIGHTEN CAP OR BOLT |  | Steel/Wrought Iron |  | Woodbridge
| 09-02744-1 | 197 |  | 0.75 | Transmission |  | Valves |  |  | Other | DOPED/TIGHTENED GAUGE TAP | 2009-11-25 | 2010-01-22 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Woodbridge
| 09-02744-1 |  |  | 6 | Transmission |  | Valves |  |  | Other | Grees fitting | 2009-11-25 | 2010-01-26 | Other | Grees fitting | Steel/Wrought Iron
|  | 197 | [15 empty] | Woodbridge
16 |  |  |  | 6 | Transmission | [6 empty] | 1979-09-19 |  |  |  | Steel/Wrought Iron |  | Lodi
|  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Lodi
93 | 86-00329-1 |  |  | 2 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1986-10-08 | 1987-03-23 | Other |  | Steel/Wrought Iron |  | Lodi
16 | 86-00343-1 |  |  | 3 | Distribution Feeder Main |  | Valves |  |  | DIGIN |  | 1986-10-13 | 1986-10-15 | Other |  | Steel/Wrought Iron |  | Lodi
93 | 73-20036-1 |  |  | 0.75 | Service |  | Fitting |  |  | Material Failure |  | 1973-03-27 | 1973-12-07 | Other | INSERT NEW REG | Steel/Wrought Iron
93 | 73-20029-1 |  |  | 0.75 | Service |  | Fitting |  |  | Material Failure |  | 1973-03-27 | 1973-12-07 | Replace Pipe and/or Service | INSERT NEW REG | Steel/Wrought Iron |  | Lodi
93 | 73-20007-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Material Failure |  | 1973-03-22 | 1973-12-17 | Replace Pipe and/or Service | Regulator | Steel/Wrought Iron
| 05-01007-1 |  |  | 0.5 | Distribution Main |  | Plastic Tee Cap |  |  | Material Failure |  | 2005-01-18 | 2005-01-24 | Other | Replaced Plastic Tee Cap | Other |  | Lodi
[12 empty] | 2005-01-24 | [5 empty] | Stockton
| 05-01007-1 | [10 empty] | 2005-01-18 | [5 empty] | Lodi
|  | 108C |  | 16 | Transmission
|  | 108C | 13.39 | 16 | Transmission | [10 empty] | Steel/Wrought Iron
93 | 73-20017-1 |  |  | 0.75 | Distribution Main |  | Valves |  |  | CONSTRUCTION DEFECT |  | 1973-03-23 | 1973-09-06 | Other |  | Steel/Wrought Iron
93 | 72-20185-1 |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-03-23 | 1973-03-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron
93 | 73-20016-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Other |  | 1973-03-23 |  | Other
|  |  |  | 2 | Distribution Feeder Main |  | VALVES |  |  | Other |  | 1982-03-03 | 1982-03-03 | Other |  | Steel/Wrought Iron |  | Lodi
| 93-00126-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Material Failure |  | 1993-08-17 | 1994-07-25 | Replace Pipe |  | Steel/Wrought Iron |  | Lodi
93 | 73-20051-1 |  |  | 0.75 | Distribution Main |  | Regulator |  |  | CORROSION |  | 1973-03-23 | 1974-04-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron
16 |  |  |  | 4 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Lodi
16 |  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | Lodi
| 09-02135-1 |  |  | 4 | Transmission |  | Valves |  |  | Other | VALVE LUBE DRIED OUT RELUBED | 2009-04-28 | 2009-09-06 | Other | Greased underground main valve | Steel/Wrought Iron |  | Lodi
93 | 73-20025-1 |  |  | 0.75 | Service |  | Regulator |  |  | Material Failure |  | 1973-03-26 | 1973-08-29 | Other |  | Steel/Wrought Iron
| 09-02185-1 |  |  | 0.75 | Single Service |  | Other |  | HPR |  |  | 2009-05-07 | 2009-07-22 | Other | Replaced Hpr | Steel/Wrought Iron |  | Lodi
| 09-02185-1 |  |  | 0.75 | Single Service |  | Other |  | HPR |  |  | 2009-05-07 | 2009-07-22 | Other | Replaced Hpr | Steel/Wrought Iron |  | Lodi
|  |  |  | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron
93 | 84-00275-1 |  |  | 0.75 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1984-07-05 | 1986-10-24 | Other |  | Steel/Wrought Iron |  | Lodi
|  | 197-(060) |  | 08.00 - (old) | [11 empty] | Steel/Wrought Iron |  | Lodi
|  |  |  | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | Lodi
93 | 74-60005-1 | 197B |  | 8 | Transmission |  | Fitting |  |  | Material Failure |  | 1974-03-22 | 1975-05-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron
93 | 74-60003-1 | 197B |  | 8 | Transmission |  | Valves |  |  | Other |  | 1974-02-26 | 1974-03-21 | Other |  | Steel/Wrought Iron
93 | 73-20003-1 |  |  | 8 | Transmission |  | Girth Weld |  |  | Corrosion |  | 1973-02-05 | 1975-07-11 | Patch Welded |  | Steel/Wrought Iron |  |  | 32% AT LOCATION STATED BELOW 2-11-75; PINHOLE LEAK ON WELD THIS LOCATION - REPAIRED BY WELDING.
|  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1991-04-18 |  | Other | WRAP PIPE | Steel/Wrought Iron
93 | 74-60010-1 | 197B |  | 8 | Transmission |  | Body of Pipe |  |  | DAMAGE BY OUTSIDE FORCES |  | 1974-04-22 | 1975-07-11 | PATCH WELDED |  | Steel/Wrought Iron
| 98-01116-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Digin |  | 1998-10-02 | 1998-10-02 | Replace Pipe |  | Steel/Wrought Iron |  | Stockton
93 | 73-61001-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | CONSTRUCTION DEFECT |  | 1973-03-23 | 1973-03-23 | Replace Pipe and/or Service |  | Other Plastic |  | Stockton
16 | 77-00912-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | DAMAGE BY OUTSIDE FORCES |  | 1977-10-10 | 1977-10-10 | Replace Pipe and/or Service |  | Other Plastic |  | Stockton
93 | 73-41016-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | DAMAGE BY OUTSIDE FORCES |  | 1973-05-25 | 1973-05-25 | Replace Pipe and/or Service |  | Other Plastic |  | Stockton
93 | 77-00697-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1977-06-24 | 1977-06-24 | Patch Welded |  | Steel/Wrought Iron |  | Stockton
93 | 79-00188-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | DAMAGE BY OUTSIDE FORCES |  | 1979-05-29 | 1979-05-29 | Replace Pipe and/or Service |  | Other Plastic |  | Stockton
93 | 79-00125-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | DAMAGE BY OUTSIDE FORCES |  | 1979-04-06 | 1979-04-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Stockton
| 03-01032-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Digin |  | 2003-04-17 | 2003-04-17 | Service Partially Replaced |  | Other Plastic |  | Stockton
16 | 77-01012-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1977-12-23 | 1977-12-27 | Clamp |  | Steel/Wrought Iron
16 | 77-01012-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1977-12-23 | 1977-12-27 | Clamp |  | Steel/Wrought Iron
16 | 77-00842-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | CONSTRUCTION DEFECT |  | 1977-08-23 | 1977-08-23 | Other |  |  |  | Stockton
93 | 80-00282-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | DAMAGE BY OUTSIDE FORCES |  | 1980-07-28 | 1980-07-28 | REPLACE PIPE AND/OR SERVICE |  | Other Plastic |  | Stockton
| 96-00235-1 |  |  | 8 | Transmission |  | Valves |  |  | Other | Old valve grease dried up | 1996-09-09 | 2001-07-23 | Other | Repaired fitting/greased valve | Steel |  | Stockton
| 92-00245-1 |  |  | 4 |  |  | MECHANICAL JOINT |  |  | Material Failure |  | 1992-11-03 | 1993-03-05 | Other |  | Aldyl A (Tan or Gray) |  | Stockton
93 | 81-10282-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | DAMAGE BY OUTSIDE FORCES |  | 1981-07-30 | 1981-07-03 | Replace Pipe and/or Service |  | Other Plastic |  | Stockton
93 | 73-03003-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-01-02 | 1974-03-04 | Patch Welded |  | Steel/Wrought Iron
93 | 73-03005-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | CORROSION |  | 1973-01-02 | 1974-04-16 | Patch Welded |  | Steel/Wrought Iron |  | Stockton | 6% 1-21-74 GHW (WORKED). 15% 5-3-74 ELECT CG BOX GHW. 6% AT BAREHOLE BESIDE ELECTRIC BOX 5-31-74. CLEAR 6-20-24; 1/16" HOLE IN 8" MAIN. WELDED ON 6"X6" PATCH.
|  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Stockton
93 | 77-00573-1 |  |  | 0.5 | Distribution Main |  | Body of Pipe |  |  | DAMAGE BY OUTSIDE FORCES |  | 1977-05-31 | 1977-05-31 | Replace Pipe and/or Service |  | Other Plastic |  | Stockton
| 00-00013-1 |  |  | 0.5 | Service |  | Riser |  |  | Construction Defect |  | 2000-05-25 | 2000-05-25 | OTHER | REPLACED RISER | Other Plastic |  | Stockton
93 | 77-00930-1 |  |  | 2 | Service |  | Body of Pipe |  |  | DAMAGE BY OUTSIDE FORCES |  | 1977-10-06 | 1977-10-06 | Replace Pipe and/or Service |  | Other Plastic
93 | 74-42044-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | DAMAGE BY OUTSIDE FORCES |  | 1974-06-05 | 1974-06-05 | Replace Pipe and/or Service |  | Other Plastic
93 | 74-42068-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | DAMAGE BY OUTSIDE FORCES |  | 1974-07-31 | 1974-07-31 | Other |  | Other Plastic |  | Stockton
| 93-01139-0 |  |  | 2 |  |  | BODY OF PIPE | Body of Pipe |  | Digin |  | 1993-01-22 | 1993-01-22 | WELD OVER SLEEVE OR CAN |  | Steel/Wrought Iron
93 | 75-20097-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Other |  | 1975-10-10 | 1975-10-13 | Other
16 | 77-00513-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-10-10 | 1977-10-10 | Replace Pipe and/or Service |  | Other Plastic |  | Stockton
93 | 79-00367-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-11-06 | 1979-11-06 | Replace Pipe and/or Service |  | Other Plastic |  | Stockton
16 | 79-00273-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-07-30 | 1979-07-30 | REPLACE PIPE AND/OR SERVICE |  | Other Plastic |  | Stockton
|  |  |  | 2 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
93 | 78-00568-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Material Failure |  | 1978-09-12 | 1978-09-12 | REPLACE PIPE AND/OR SERVICE |  | Other Plastic |  | Stockton
16 | 78-00229-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1978-03-02 | 1978-03-20 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Stockton
93 | 76-62013-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | CORROSION |  | 1976-01-14 | 1976-01-14 | Clamp |  | Steel/Wrought Iron |  | Stockton
93 | 78-00038-1 |  |  | 0.5 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-10-24 | 1978-01-24 | Replace Pipe and/or Service |  | Other Plastic |  | Stockton
|  |  |  | 10 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Stockton
|  |  |  | 10 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Stockton
|  |  |  | 10 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Stockton
93 | 79-00293-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-09-26 | 1979-09-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Stockton
| 88-00453-1 |  |  | 0.04 |  | Drip | Body of Pipe |  |  | Corrosion |  | 1988-08-12 | 1989-03-06 | Other |  | Steel/Wrought Iron |  | Stockton
93 | 79-00275-1 |  |  | 2 | Other |  | Drip |  |  | Corrosion |  | 1979-08-16 | 1979-08-22 | Other |  | Steel/Wrought Iron |  | Stockton
93 | 72-40067-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-05-29 | 1972-05-30 | Patch Welded |  | Steel/Wrought Iron
93 | 72-40068-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-05-23 | 1972-05-30 |  |  | Steel/Wrought Iron
93 | 77-00474-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1977-05-17 | 1977-05-17 | Clamp |  | Steel/Wrought Iron |  | Stockton
| 96-00182-1 |  |  | 6 | Other | B | Bell Joint |  |  | Material Failure |  | 1996-07-03 | 1997-08-04 | Bell Joint Clamp |  | Cast/Ductile Iron |  | Stockton
| 96-00182-1 |  |  | 6 | Other | B | Bell Joint |  |  | Material Failure |  | 1996-07-03 | 1997-08-04 | Bell Joint Clamp |  | Cast/Ductile Iron |  | Stockton
93 | 78-00381-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-05-31 | 1978-05-31 | Clamp |  | Cast/Ductile Iron |  | Stockton
93 | 88-00429-1 |  |  | 0.04 | Other | M | Bell Joint |  |  | Material Failure |  | 1988-09-07 | 1988-12-07 | Bell Joint Seal |  | Cast/Ductile Iron |  | Stockton
93 | 85-00236-1 |  |  | 1.25 | Service |  | Body of Pipe | Body of Pipe |  | Corrosion | FUEL LINE | 1985-02-12 | 1986-06-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Stockton
93 | 74-62096-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-08-14 | 1974-11-13 | Patch Welded |  | Steel/Wrought Iron |  |  | 6" PATCH WELDED OVER LEAK.
93 | 74-62065-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-08-14 | 1974-09-26 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Stockton
16 | 79-00155-1 |  |  | 0.5 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-05-10 | 1979-05-10 | Replace Pipe and/or Service |  | Other Plastic |  | Stockton
93 | 72-00056-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-08-28 | 1973-06-08 | Clamp |  | Steel/Wrought Iron |  | Stockton
93 | 72-00058-1 |  |  | 4 | Distribution Main | Service | Body of Pipe |  |  | Corrosion |  | 1972-08-29 | 1972-09-01 | Patch Welded |  | Steel/Wrought Iron |  | Stockton
|  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1976-04-30 |  |  |  | Steel/Wrought Iron
93 |  |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-06-11 |  |  |  | Cast/Ductile Iron
93 | 73-62023-1 |  |  | 0.75 | Other |  | VALVES |  |  | Other |  | 1973-03-06 | 1973-05-30 | Other |  | Steel/Wrought Iron
93 | 10-81503-1 | [10 empty] | 2010-10-05
93 |  |  |  | 1.25 | Service | [10 empty] | Steel/Wrought Iron |  | Stockton
93 | 86-00146-1 |  |  | 4 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1986-08-04 | 1986-10-08 | Bell Joint Seal |  | Cast/Ductile Iron |  | Stockton | BELL JOINT SEAL INSTALLED 4' FROM SERVICE TEE TO 337 HARRISON. SERVICE OUT AND TESTED 9.5... SHOWED NO LEAKAGE...
93 | 75-62234-1 |  |  | 0.75 | Other |  | Drip |  |  | Corrosion |  | 1975-05-14 | 1975-05-15 | Other |  | Steel |  |  | 20% in bar hole c/main 20' w/o E/PL 6/4/75
93 | 72-40075-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-06-10 | 1972-06-13 | PATCH WELDED |  | Steel/Wrought Iron |  | Stockton
93 | 74-23042-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-02-26 | 1974-06-14 | Patch Welded |  | Steel/Wrought Iron |  | Stockton | 6/5/74 25% 258' W/O GARFIELD. YELLOW MARK AT CURB.
93 | 73-03071-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-01-10 | 1974-05-14 | Patch Welded |  | Steel/Wrought Iron
93 | 76-62104-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-03-19 | 1976-03-30 | WELD OVER SLEEVE OR CAN |  | Steel/Wrought Iron
93 | 76-62103-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-03-19 | 1976-03-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | FOUND LEAK ON 10"... 5'/NO/O MUELLER TIE-IN. 12" X12" BLK ASPHALT LAYING ON GAS MAIN. REPAIRED WITH 10"X12" HALF SOLE.
|  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
93 | 74-62055-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1974-08-27 | 1976-03-12 | Patch Welded |  | Steel/Wrought Iron
93 | 73-23128-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-10-11 | 1974-06-05 | Patch Welded |  | Steel/Wrought Iron |  | Stockton | 5% IN VALVE 5' N/O REG PIT. 2-13-74; FOUND LEAK ON BOTTOM OF PIPE. ROCKS IN WRAPPING. WELDED ON 6" X 6" HALF SOLE.
93 | 73-23128-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-10-11 | 1974-08-23 | PATCH WELDED |  | Steel/Wrought Iron |  | Stockton
93 | 72-00226-1 |  |  | 6 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-10-20 | 1974-05-05 | Patch Welded |  | Steel/Wrought Iron
93 | 72-40075-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-06-10 | 1972-06-13 | Patch Welded |  | Steel/Wrought Iron
93 | 73-23129-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-10-11 | 1973-12-11 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Stockton
93 | 79-10051-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1979-12-13 | 1980-01-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Stockton
93 | 83-00420-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-08-25 | 1987-03-03 | Patch Welded |  | Steel/Wrought Iron |  | Stockton
93 | 76-62470-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-11-04 | 1976-12-01 | Patch Welded |  | Steel/Wrought Iron |  | Stockton | .17% L.E.L. @ M.H. control of intersection of Fresno & Hazelton. 1-11-77 S. Day
93 | 87-00752-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Digin |  | 1987-12-09 | 1987-12-09 | Patch Welded |  | Steel/Wrought Iron |  | Stockton
93 | 74-22112-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-06-20 | 1974-06-21 | Patch Welded |  | Steel/Wrought Iron
93 | 74-22113-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1974-06-19 | 1974-06-19 | Other |  | Steel/Wrought Iron
93 | 73-22130-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-10-11 | 1973-11-29 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Stockton | 15% 18' w/o s/w PL 2-13-74 GHW #2; 12% 18' w/o s/w PL 4-9-74 GHW; 4% 16' w/o Madison on Scotts o/ main center of s. sidewalk; 12% 53' w/o Madison o/ main in center of driveway 8-27-74 G.P.G.
| 08-00005-1 | 1607 01 |  | 8 | Transmission |  | BODY OF PIPE |  |  | Other | GC paint crew - sand blast | 2008-05-29 | 2008-05-29 | REPLACE TP MAIN |  | Steel/Wrought Iron |  | Stockton
93 | 74-22009-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1974-02-09 | 1974-09-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Stockton | 100' w/o Van Buren .2.5 4-4-74 EM; 5' E/O W/RL o/main 15% 4-4-74 EM; 27' E/o Van Buren .1.5 4-4-74 EM; .6% and .8% [illegible] 5-7-74 GPG; 5% in manholes 7-5-74 OK; Clear in manholes + 30 e/o Van Buren on Scott [illegible] 9-4-74 DK
93 | 73-22124-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-10-11 | 1973-10-18 | Patch Welded |  | Steel/Wrought Iron
93 | 74-02044-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1974-02-15 | 1974-04-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Stockton
|  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
| 95-00147-1 |  |  | 0.08 | Transmission |  | Longitudinal Weld |  |  | Other |  | 1995-08-25 | 1996-10-31 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Stockton
93 | 97-00101-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1997-06-18 | 1997-10-31 | Patch Welded |  | Steel/Wrought Iron |  | Stockton
| 89-00146-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1989-03-17 | 1989-03-20 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Stockton
93 | 75-42018-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1975-06-25 | 1975-06-30 | Patch Welded |  | Steel/Wrought Iron |  | Stockton | Great! Clear 7-31-75 JHW. ARC WELDED 1 - 6"X8" PATCJ AND 1 - 3"X3" PATCH. ROCKS ALL AROUND MAIN, WRAP VERY BRITTLE.
93 | 87-00016-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1987-01-08 | 1988-04-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron
[5 empty] | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
93 | 76-63105-1 |  |  | 8 | Transmission |  | Valves |  |  | Corrosion |  | 1976-11-04 | 1977-07-11 | Other |  | Steel/Wrought Iron |  |  | 55% in gas valve 4-8-77 [illegible initials]; 30% @ 1st gas valve +/-300' w/o Fresno on Navy Drive; No indication of gas with J.W. Fester 8-3-77 GRD;
Stockton
93 | 80-00257-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-07-13 | 1980-07-13 | Replace Pipe and/or Service |  | Other Plastic |  | Stockton
93 | 76-41035-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-12-22 | 1976-12-22 | Other |  | Steel/Wrought Iron |  | Stockton
16 | 78-00520-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1978-07-07 | 1978-07-07 | Clamp |  | Steel/Wrought Iron |  | Stockton
93 | 74-42039-1 |  |  | 1 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-06-06 | 1974-06-06 | Replace Pipe and/or Service |  | Other Plastic |  | Stockton | Clear 6-14-74 GPG
93 | 77-00879-1 |  |  | 0.5 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-09-23 | 1977-09-23 | Replace Pipe and/or Service |  | Other Plastic |  | Stockton
93 | 71-20078- |  |  | 2.38 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-06-02 | 1971-07-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Stockton | 6/7/71 BG test holes over service & water location [illegible]; 6/8/71 CG 10% at back of sidewalk.; 9/23/71 BG Clear
93 | 86-00461-1 |  |  | 1 | Distribution Main |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1986-10-28 | 1987-08-04 | Replace Pipe and/or Service |  | TR 418 |  | Stockton
| 04-02075- | 108 |  | 6 | Transmission |  | Valves |  |  | Other |  | 2004-06-23 | 2004-06-24 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Stockton
93 | 87-00705-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Digin |  | 1987-11-04 | 1987-11-04 | Replace Pipe and/or Service |  | TR 418 |  | Stockton
| 87-00705-1 | [16 empty] | Stockton
Stockton
| 78-00359-1 |  |  | 4 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-05-15 | 1978-05-15 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Stockton
93 | 87-00683-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Material Failure |  | 1987-11-04 | 1988-04-09 | Replace Pipe and/or Service |  |  |  | Stockton
16 | 77-00619-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-06-13 | 1977-06-13 | Replace Pipe and/or Service |  | Other Plastic
[10 empty] | Corrosion |  | 1977-01-07 |  | Other |  | Steel/Wrought Iron |  | Stockton
| 00-02153-1 |  |  | 24 | Transmission |  | VALVES |  |  | Other | STEM LEAK | 2000-09-05 | 2001-04-23 | Other | LUBED VALVES | Steel/Wrought Iron |  | Stockton | Lubricated valve to stop leak.
| 01-02331-1 | 108 | 29.17 | 8 | Transmission |  | Valves |  |  | Other |  | 2001-09-19 | 2001-10-19 | Other |  | Steel/Wrought Iron |  | Stockton
| 01-02321-1 | 108 | 29.17 | 8 | Transmission |  | Valves |  |  | Other | LUBED VALVES | 2001-09-05 | 2001-10-19 | Other | GREASED/OPER | Steel/Wrought Iron |  | Stockton
93 | 74-22013-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1974-02-21 | 1974-12-06 | Other |  | Steel/Wrought Iron |  | Stockton | .7% 2' east of N/E PL of 1328 in water box - DCA 1-8-75;; 12% w/b 4-8-74 EMA; 10% water box 6-11-74 GPG; 3005-13 500/PPN [illegible]; .1% in WMB 9-4-74 DK
| 00-02157-1 |  |  |  | Transmission |  | Valves |  |  | Other | LUBED VALVES | 2000-09-13 | 2000-09-14 | Other | Lubed valve | Steel |  | Stockton
16 | 85-00825-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Digin |  | 1985-09-09 | 1985-09-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Stockton
93 | 77-00837-1 |  |  | 4 | Other |  | Drip |  |  | Corrosion |  | 1977-08-03 | 1978-01-24 | Other |  | Steel/Wrought Iron |  | Stockton | 50% @ PT&T manhole s/e [illegible] 1-16-78 G. Day
93 | 76-42012-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-06-14 | 1977-07-18 | Clamp |  | Steel/Wrought Iron |  | Stockton | 4% in PT&T manhole nothing o/ main 2-16-77 [illegible initials];; 20% in PT&T manhole 7-8-77 G. Day;; 23% of PT&T manhole 8-3-77 GPG
93 | 79-*0407-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-12-27 | 1979-12-27 | Replace Pipe and/or Service |  | Other Plastic |  | Stockton
93 | 77-00833-1 |  |  | 0.5 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-08-18 | 1977-08-18 | Other |  | Other Plastic |  | Stockton
93 | 86-00369-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1986-10-09 | 1986-10-09 | Replace Pipe and/or Service |  | TR 418 |  | Stockton
|  |  |  | 8 | Transmission |  | OTHER |  |  | Other |  | 1998-06-09 | 1998-06-09 | Other |  | Steel/Wrought Iron
16 | 79-00107-1 |  |  | 1.25 | Distribution Main |  | VALVES |  |  | Damage by outside Forces |  | 1979-02-23 | 1979-02-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Stockton
93 | 72-40099-1 |  |  | 4 | Service |  | Other |  |  | Corrosion |  | 1972-08-16 | 1972-08-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron
Stockton
93 | 72-60066- |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-11-27 | 1972-11-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Stockton
93 | 71-00154- |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-02-12 | 1971-02-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Stockton
93 | 87-00689-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1987-05-22 | 1987-05-22 | Replace Pipe and/or Service |  | Aldyl A (Tan or Gray) |  | Stockton
93 | 71-00160-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1971-02-12 | 1971-12-10 | Other |  | Other |  | Stockton
93 | 87-00629-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1987-08-20 | 1987-08-20 | Replace Pipe and/or Service |  | TR 418 |  | Stockton
93 | 84-00640-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 1984-11-06 | 1984-11-13 | Other |  | Aldyl A (Tan or Gray) |  | Stockton
93 | 81-10280-1 |  |  | 2 | Service |  | Valves |  |  | Material Failure |  | 1981-07-08 | 1981-07-08 | Other |  | Steel/Wrought Iron |  | Stockton
| 93-00147-1 |  |  | 1.75 | Other |  | Valves |  |  | Construction Defect |  | 1993-09-15 | 1994-06-16 | Other |  | Steel/Wrought Iron |  | Stockton
93 | 71-40006- |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-01-23 | 1971-01-27 | Other |  | Steel/Wrought Iron
93 | 71-20050- |  |  | 12 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-05-20 | 1971-10-29 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | 5/26/71 BS 20% IN WTS.; 11/18/71 BS CLEAR.; WELD ON 10"X10" PATCH. WELD IN EXCEPTION. 10-29-11.
|  |  |  | 12 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-05-17 | 1973-05-18 | Patch Welded |  | Steel/Wrought Iron |  | Stockton | CLEAR 9-4-73 GHW; 55% 2' S/O REPAIR ON 12" TEST HOLE. .1% O/5 6-19-73. " 7-20-73. 6" SQUARE PATCH WELDED IN PLACE.
| 98-00077-1 |  |  | 12 | Transmission |  | Unknown |  |  | Unknown |  | 1998-09-02 | 2000-03-22 | ABANDON |  | Steel |  | Stockton | Replace Main under RR tracks. see job No. 7026165
93 | 98-00077-1 | [10 empty] | 1998-09-02 | [5 empty] | Stockton
| 93-01048-1 |  |  | 0.02 | Other | X was entered for "line use" | BODY OF PIPE |  |  | Material Failure |  | 1993-05-25 |  | Replace Pipe |  | Aldyl A (Tan or Gray) |  | Stockton
| 87-00096-1 |  |  | 10 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1987-01-29 | 1987-01-30 | Other |  | Steel/Wrought Iron |  | Stockton
Stockton
93 | 72-40035-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-03-12 |  | Other |  | Steel/Wrought Iron |  |  | [Repair date illegible.]
93 | 72-40035-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-03-10 | 1972-03-13 | Other |  | Steel/Wrought Iron |  |  | 100/1000 5'/o S/P.L. 12-11-73; 100% 25' s/o s/w P> 1-25-74 JHW;; issued new leak (74-4200-3)
93 | 75-00031-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-01-07 | 1974-01-16 | PATCH WELDED |  | Steel/Wrought Iron |  | Stockton | 300-PPM o/main n/e corner of intersection at yellow mark 1-7-75 SA;; 55% 12' west of n/w corner of intersection, o/main at barehole 2-13-75 GPG
93 | 85-00861-1 |  |  |  | Other | X was entered for "line use" | Valves |  |  | Material Failure |  | 1985-09-24 | 1986-11-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Stockton
93 | 86-0021-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1986-08-08 | 1986-08-08 | Replace Pipe and/or Service |  | TR 418
93 | 94-00121-1 |  |  | 0.08 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1994-05-02 | 1994-05-02 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Stockton | INSTALLED 30" HALF SOLE; COULD NOT FIND END OF MAIN AT 5' W/O TEE.
| 93-00162-1 |  |  | 0.08 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1993-10-15 | 1994-05-02 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Stockton
93 | 93-00162-1 | [10 empty] | 1993-10-15
| 94-00121-1 |  |  | 0.08 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1994-05-02 | 1994-05-02 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Stockton
| 94-00121-1 |  |  | 0.08 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1994-05-02 | 1994-05-02 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Stockton
| 93-00162-1 |  |  | 0.08 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1993-10-15 | 1994-05-02 | WELD OVER SLEEVE OR CAN |  | Steel/Wrought Iron |  | Stockton
| 93-00162-1 | [16 empty] | Stockton
93 | 81-10373-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | OTHER |  | 1978-12-07 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Stockton
|  |  |  | 6 | Distribution Main |  | BODY OF PIPE |  |  | Corrosion |  | 1976-12-20 | 1976-12-20 | Patch Welded |  | Steel/Wrought Iron
93 | 87-00530-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1987-06-30 | 1987-06-30 | Replace Pipe and/or Service |  | TR 418 |  | Stockton
93 | 87-00529-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1987-06-18 |  | Replace Pipe and/or Service |  | TR 418 |  | Stockton
93 | 87-00631-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1987-08-25 | 1987-08-25 | Replace Pipe and/or Service |  | TR 418 |  | Stockton
93 | 85-00507-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1985-05-21 | 1986-02-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Stockton
93 | 87-00630-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1987-08-11 | 1987-08-11 | Replace Pipe and/or Service |  | TR 418 |  | Stockton
93 | 71-00159-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1971-02-12 | 1971-12-10 | Other |  | Other |  | Stockton
93 | 71-00159- | [16 empty] | Stockton
13 | 78-00660-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1978-10-30 | 1978-10-31 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Stockton
93 | 86-00449-1 |  |  | 1.25 | Service |  | Fitting |  |  | Damage by outside Forces |  | 1986-12-08 | 1986-12-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron
93 | 76-62466-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-10-22 | 1976-10-26 | Patch Welded |  | Steel/Wrought Iron |  | Stockton | .2% IN MANHOLE DROPPING TO ... NEXT TO MAIN 12-9-76. 2" MAIN TO GOG PIT ... THREE HOLES IN IT. WELDED ON 3" PATCH. SEWER LINE IN WAY WAS STRUCK WHEN THEY PUT IN SEWER LINE.
| 93-00658-1 |  |  | 0.12 | Distribution Feeder Main |  | Girth Weld |  |  | Corrosion |  | 1993-05-18 | 1994-05-17 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Stockton
93 | 82-10449-1 |  |  | 12 |  |  | Body of Pipe |  |  | Corrosion |  | 1982-07-20 | 1982-07-20 | Patch Welded |  | Steel/Wrought Iron |  | Stockton | FOUND 30% WHERE STEEL PLATE IS COVERING HOLE. 8-19-82 T.A.P; GAS MAIN PITTED AND LEAKING DIRECTLY AT TOP OF PIPE-PITTED AREA APPROC 3" IN DIA. COMPLETED INSPECTION WHILE MAKING PERMANENT REPAIRS TO 12" STL GAS MAIN - INSTALLED 1 - 10"X10" PATCH AND 1 = 6"X6" PATCH.
93 | 72-20496-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Construction Defect |  | 1972-09-11 | 1973-02-21 |  |  | Steel/Wrought Iron |  | Stockton
93 | 73-42092-1 |  |  | 0.75 | Other |  | Drip |  |  | Corrosion |  | 1973-12-05 | 1973-12-05 | Patch Welded |  | Steel/Wrought Iron
93 | 82-10477-1 | [10 empty] | 1982-08-10 | [5 empty] | Stockton
| 96-01015-1 |  |  | 0.12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1996-03-22 | 1996-03-27 | Patch Welded |  | Steel/Wrought Iron |  | Stockton
93 | 79-00217-1 |  |  | 0.75 | Other |  | Drip |  |  | Corrosion |  | 1979-06-22 | 1979-07-06 | Other |  | Steel/Wrought Iron |  | Stockton
93 | 78-00508-1 |  |  | 4 | Distribution Main |  | Bell Joint |  |  | Corrosion |  | 1979-07-05 | 1979-05-14 | Bell Joint Seal |  | Cast/Ductile Iron |  | Stockton
93 | 85-00997-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1985-10-17 | 1985-10-18 | Other |  | Steel/Wrought Iron |  | Stockton
93 | 87-00687-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1987-04-20 | 1987-04-20 | Replace Pipe and/or Service |  | Aldyl A (Tan or Gray)
98 | 80-00085-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Material Failure |  | 1980-02-12 | 1980-04-08 | Replace Pipe and/or Service |  | Cast/Ductile Iron |  | Stockton
93 | 80-00085-1 |  |  | 4 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1980-02-12 | 1980-03-17 | Other | 10% FROM BAR HOLE W/ YELLOW PAINT 3-10-80 A.C. 10,000 P.P.M. FROM REPAIR PATCH 4/7/80; LARGE HOLE IN MAIN REPLACED WITH A FULL CIRCLE CLAMP. ALSO SOAP TESTED. MAIN APPEARS TO JUST BE TOUCHING THE FACE OF THE B.J. CAN STICK A ... THIS SECTION OF PIPE IS SHOT. HAS TO BE REPLACED. | Cast/Ductile Iron
93 | 78-00593-1 |  |  | 4 | Distribution Main |  | Bell Joint |  |  | Corrosion |  | 1978-10-09 | 1980-01-08 | Bell Joint Seal |  | Cast/Ductile Iron |  | Stockton
93 | 87-00455-1 |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1987-04-08 | 1987-06-12 | Patch Welded |  | Steel/Wrought Iron |  | Stockton
Stockton
93 | 86-00362-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1986-10-22 | 1986-10-22 | Replace Pipe and/or Service |  | Other Plastic |  | Stockton
16 | 78-00543-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-08-07 | 1978-08-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Stockton
93 | 77-00840-1 |  |  | 1 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-08-25 | 1977-08-25 | Replace Pipe and/or Service |  | Other Plastic |  | Stockton
93 | 78-00346-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1978-05-11 | 1978-05-11 | Clamp |  | Steel/Wrought Iron |  | Stockton
93 | 78-00544-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-08-10 | 1978-08-10 | Replace Pipe and/or Service |  | Other Plastic |  | Stockton
93 | 93-02039-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Material Failure |  | 1993-08-18 | 1983-08-19 | Replace Pipe and/or Service |  | Aldyl A (Tan or Gray)
93 | 73-42004-1 |  |  | 0.01 | Service |  | Fitting |  |  | Construction Defect |  | 1973-01-10 | 1973-01-10 | Patch Welded |  | Copper |  | Stockton
|  | 108D |  |  | Transmission | [10 empty] | Steel/Wrought Iron |  | Stockton
93 | 80-00124-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Material Failure |  | 1980-01-11 | 1980-01-14 | Bell Joint Clamp |  | Cast/Ductile Iron
93 | 80-00125-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Material Failure |  | 1980-01-11 | 1980-01-14 | Bell Joint Clamp |  | Cast/Ductile Iron
93 | 72-20167-1 |  |  | 1.25 | Other | marked as "C" | Body of Pipe |  |  | Corrosion |  | 1972-03-07 | 1972-03-08 | Other |  | Steel/Wrought Iron |  | Stockton
16 | 86-00065-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Digin |  | 1986-04-14 | 1986-04-14 | Replace Pipe and/or Service |  | Other Plastic |  | Stockton
108B
93 | 84-00201- |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1984-04-21 | 1984-04-21 | Replace Pipe and/or Service |  | TR 418 |  | Stockton
93 | 74-42046-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-06-17 | 1974-06-17 | Replace Pipe and/or Service |  | Other Plastic
16 | 79-00146-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-05-03 | 1979-05-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Stockton
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron
| 08-02025-1 |  |  | 0.5 | Service |  | Body of Pipe |  | TAP CONNECTION | Plastic Crack Failure |  | 2008-02-28 | 2008-05-12 | Replace Partial Service |  | Aldyl A (Tan or Gray) |  | Stockton | svc cracked @ tap connection-replaced 18" of Aldyl-A using one 1/2" met-fit coupling.
| 08-02025-1 |  |  | 0.5 | Single Service |  | Body of Pipe |  | TAP CONNECTION | Plastic Crack Failure |  | 2008-02-28 | 2008-05-12 | Replace Partial Service |  | Aldyl A (Tan or Gray) |  | Stockton
| 05-01141-1 |  |  | 0.5 | Single Service |  | BODY OF PIPE |  |  |  |  | 2005-09-15 | 2005-09-15 | Replace Partial Service |  | TR 418 |  | Stockton
93 | 87-00693-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1987-04-22 | 1987-04-22 | Replace Pipe and/or Service |  | Aldyl A (Tan or Gray) |  | Stockton
93 | 85-00760-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1985-08-05 | 1985-08-05 | Replace Pipe and/or Service |  | TR 418 |  | Stockton
93 | 73-42049-1 |  |  | 75 | Service |  | Body of Pipe |  |  | CONSTRUCTION DEFECT |  | 1973-05-18 | 1973-05-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Stockton
93 | 83-00619-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1983-11-18 | 1984-04-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | French Camp
93 | 86-00155-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Digin |  | 1986-06-19 | 1986-06-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Lathrop
16 | 85-00822-1 |  |  |  | Service |  | Body of Pipe |  |  | Digin |  | 1983-09-03 | 1985-09-03 | Replace Pipe and/or Service |  | Other Plastic |  | Lathrop
16 |  |  |  |  | Service |  | Body of Pipe |  |  | Digin |  | 1984-04-16 | 1984-04-17 | Replace Pipe and/or Service |  | TR 418 |  | Manteza
93 |  |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1984-04-26 | 1984-04-26 | Replace Pipe and/or Service |  | TR 418 |  | Manteca
93 | 74-00503-1 |  |  | 1.5 | Other |  | Regulator |  |  | Other |  | 1974-03-04 | 1974-10-29 | Other |  | Steel/Wrought Iron |  | Manteca
| 00-02079-1 | 108 |  | 4 | Transmission |  | Valves |  |  | Other | BOLT NOT TIGHT BOLT BROKE WHEN TIGHTENING | 2000-09-14 | 2000-11-17 | Tighten Cap or Bolt |  | Cast/Ductile Iron |  | MANTECA | TIGHTENED BOLT
| 00-02079-1 | 108 |  |  | Transmission |  | Valves |  |  | Material Failure |  | 2000-09-14 | 2000-11-17 | Other | REPLACED BOLTS | Steel/Wrought Iron |  | MANTECA | REPLACED 8 BOLTS ON TOP VALVE HOUSING; REPLACED BOLTS ON TOP OF VALVE #4
| 00-02079-1 | 108 |  | 4 | Transmission |  | Valves |  |  | Other | BOLT NOT TIGHT BOLT BROKE WHEN TIGHTENING | 2000-09-14 | 2000-11-17 | Tighten Cap or Bolt |  | Cast/Ductile Iron |  | MANTECA | TIGHTENED BOLT
| 00-02079-1 | 108 |  |  | Transmission |  | Valves |  |  | Material Failure |  | 2000-09-14 | 2000-11-17 | Other | REPLACED BOLTS | Steel/Wrought Iron |  | MANTECA | REPLACED 8 BOLTS ON TOP VALVE HOUSING
| 09-06002-1 | 108 |  | 1 | Transmission |  | Body of Pipe |  |  |  |  | 2009-01-05 | 2009-01-05 | Replace Partial Service | REPLACE TP SERV. | Steel/Wrought Iron |  | MANTECA | G.C. INST. 1'-1" SOCKETS + 5' OF 1" STL. 1 -3/4" X 1" SOCKET; EXCAVATOR TRENCHING TO INSTALL 48" IRRIGATION LINE DUG INTO 1" TP SERVICE
|  |  |  | 0.16 | [13 empty] | MANTECA
MOVED HPR SET 20' W/O EXISTING LOCATION
| 00-02077-1 | DISTRIBUTION |  | 20 | Distribution Main |  | Other |  | METRIC FITTING | Unknown |  | 2000-09-14 | 2000-09-20 | Other | TIGHTENED FITTING | Steel/Wrought Iron |  | MANTECA | FIXED LEAK IN HPR BOX ON METRIC FITTING
| 00-02078-1 | DISTRIBUTION |  | 0.75 | Distribution Main |  | Fitting |  |  | Other | METRIC | 2000-09-14 | 2000-09-20 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | MANTECA | TIGHTENED METRIC FITTING
| 04-05014 |  |  | 0.75 | Service |  |  |  |  | Digin |  | 2004-04-19 | 2004-04-23 | Service Partially Replaced |  |  |  | MANTECA | REPLACED 17.5' OF PIPE AND 2 EA ELBOWS &COUPLING; USE PRE TESTED 3/4" SEAMLESS PIPE (REPLACED 2 EA 3/4 SOCKETWELD ELBOWS AND INSTALLED 1EA SOCKET WELD COUPLING, REPLACED 17 1/2' OF 3/4" STL)
| 01-02291-1 |  |  | 12 | Transmission |  | Valves |  |  | Other | OPERATED VALVE | 2001-08-06 | 2001-09-26 |  |  | Steel/Wrought Iron |  | RIPON | OPERATED VALVE 6.66
93 | 87-00562-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-05-08 | 1987-05-20 | Patch Welded |  | Steel/Wrought Iron |  | RIPON | LEAK IN BOTTOM OF MAIN AT 6 O'CLOCK POSITION. HAS PLANT WELDED PATCH ON.
|  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1974-09-18 |  |  |  | Steel/Wrought Iron |  | MANTECA
|  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1974-09-23 |  |  |  | Steel/Wrought Iron |  | MANTECA
93 | 74-20523-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-01-17 | 1974-03-11 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | INSTALLED NEW 1/2" PL INSERT
|  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1974-09-19 |  |  |  | Steel/Wrought Iron |  | MANTECA
16 |  |  |  | 12 | Transmission | [6 empty] | 1976-03-24 |  |  |  | Steel/Wrought Iron |  | MANTECA
| 98-00097-1 |  |  | 8 | Transmission |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1998-12-14 | 1998-12-16 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | MANTECA | WELDED CAN ON 8" DRESSER
93 | 84-00625-1 |  |  | 0.5 | Service |  | Tap Connection |  |  | Construction Defect |  | 1984-10-18 | 1984-10-19 | Replace Pipe and/or Service |  | Aldyl A (Tan or Gray) |  | MANTECA | LEAK WAS AT 1/2" PL WHERE IT WAS FUSED TO SERV "T". REFUSED NEW PL INTO "T"
93 | 97-05013 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1997-06-12 | 1997-06-12 | Replace Pipe and/or Service |  | Aldyl A (Tan or Gray) |  | MANTECA | INSP AND REPAIR DUE TO DIG-IN
| 01-02324-1 | MOD. RIPON FEEDER | 4.17 |  | Transmission |  | Valves |  |  | Other | LUBR. VALVE | 2001-09-07 | 2001-10-15 | Other | LUBED & OPER VALVE. | Steel/Wrought Iron |  | RIPON | OPERATED VALVE (MULTI TURN)
93 | 87-00753 |  |  | 8 | Distribution Feeder Main |  | Physical/Mechanical Joint |  |  | Corrosion |  | 1987-12-22 | 1987-12-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | RIPON
| 08-06166-1 | [10 empty] | 2008-08-11 | [5 empty] | RIPON
| 08-06166-1 |  |  | 0.75 | Single Service |  | Regulator |  |  | Equipment Malfunction |  | 2008-08-11 | 2008-08-13 | Other | REPLACE O RINGE | Steel/Wrought Iron |  | RIPON | REPLACED HPR O RINGS
93 | 89-00158-1 |  | 31 | 0.75 | Transmission |  | Valves |  |  | Other |  | 1989-04-07 | 1989-04-14 | Tighten Cap or Bolt |  |  |  | RIPON | GREASED & OPERATED
93 | 97-05008 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Digin |  | 1997-04-08 | 1997-04-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | RIPON
|  | 1615-01 | 5.58 | [9 empty] | 2007-07-26 | Welded Sleeve/Can - Weld |  |  |  | RIPON | TYPE B SLEEVE INSTALLED OVER GOUGE (13" LONG, 0.156" DEEP)
93 | 90-00209-1 |  |  | 8 | Transmission |  | Valves |  |  | Other |  | 1990-10-22 | 1990-12-07 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | RIPON | WELD CAN OVER 1/4" VALVE LEAKING AT STEM. (IT MUST HAVE BEEN OLD GAGED TAP CONNECTION)
93 | 90-00114-1 |  |  | 8 | Transmission |  | Tap Connection |  |  | Other |  | 1990-05-14 | 1990-05-16 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | RIPON | WELD CAN OVER LEAKING 1/4" METRIC VALVE
|  | F-01 | [15 empty] | RIPON
| 03-05011- |  |  | 0.75 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party |  | 2003-05-06 | 2003-05-06 | Service Partially Replaced |  | Steel/Wrought Iron |  | RIPON | OVER SUC 10' FROM MAIN. REPLACED 4" OF 3/4" STL SUC; DAMAGED 3/4" TRAN SUC REPAIRED WITH 4' OF PRETESTED SEAMLESS PIPE SOCKET WELDED WITH ARC MACHINE.
RIPON
| 01-04020 |  |  | 0.75 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party |  | 2001-07-10 | 2001-07-10 |  |  | Steel/Wrought Iron |  | TRACY | BLOWING GAS; THREADED PIPE. SCREWED INTO VALVE
93 | 95-00699-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other |  | 1995-11-03 | 1995-11-03 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | TRACY | REDOPED AND TIGHTENED UNION FITTING IN H.P.R. BOX
93 | 92-00094-1 | [16 empty] | TRACY
93 |  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1982-04-05 | [5 empty] | TRACY
93 |  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1982-04-01 | [5 empty] | TRACY
93 | 76-60252-1 |  |  | 0.75 | Transmission | 3/4" FEED TO DIST REG | Body of Pipe |  |  | Corrosion |  | 1976-01-23 | 1976-01-23 | Replace Pipe and/or Service | REPLACE 6 OF PIPE | Steel/Wrought Iron |  | MANTECA | 3/4" FEED TO DIST REG. REPLACE 6" OF PIPE
|  |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-06-24 | 1976-06-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | STOCKTON | REPLACED 28" OF 2" STL H.P. MAIN, BADLY PITTED AND LEAKING AT (3) LOCATIONS - INSTALLED (1) 2" M2 P.CF TO COMPLETE THIS OPERATION. (ALSO REMOVED OLD 2" STL DRESSER)
93 | 77-00799-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Damage by Outside Forces |  | 1977-07-22 | 1977-07-22 | Other |  | Other Plastic |  | STOCKTON | MADE INSPECTION OF SERVICE WHILE MAKING PERMANENT REPAIRS TO DAMAGED AREA
93 | 73-22152-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-11-15 | 1973-11-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | STOCKTON | BAR TEST FOUND GAS SERVICE TO BE LEAKING. DUG OUT OVER SERVICE AND MADE AIR TEST. WOULD NOT HOLD TEST. REPLACE WITH 1" PLASTIC PIPE.
93 | 72-40074-1 |  |  | 4 | Other |  | Other |  |  | Material Failure |  | 1972-06-07 | 1972-06-08 | Clamp |  | Cast/Ductile Iron |  | STOCKTON
93 | 78-00551-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by Outside Forces |  | 1978-09-01 | 1978-09-01 | Other |  | Other Plastic |  | STOCKTON
93 | 77-00524-1 |  |  | 2 | Service |  | Other |  |  | Construction Defect |  | 1977-05-23 | 1977-05-23 | Replace Pipe and/or Service |  | Copper |  | STOCKTON | PREFORMED INSPECTION WHILE REPAIRING POWELL RESER KIT
[18 empty] | STOCKTON | INSTALLED M2 FITTING 8" SOUTH OF MAIN ON SERVICE, TO ABANDON SAME AT PROPERTY LINE
93 | 74-22068-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-06-27 | 1974-06-13 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | STOCKTON | FOUND SERVICE LEAKING IN LAWN IN FRONT OF 6310 HERNDON. SERVICE IS FOR 6301 HERNDON STREET. SERVICE WAS LEAKING IN 3 PLACES. 6" 8" & 10" FROM TEE. 1/2" PLASTIC INSERT WAS USED TO REPAIR SERVICE.
16 | 79-00295-1 |  |  | 0.5 | Distribution Main |  | Body of Pipe |  |  | Damage by Outside Forces |  | 1979-08-27 | 1979-08-27 | Replace Pipe and/or Service |  | Other Plastic |  | STOCKTON
93 | 78-00562-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-09-13 | 1978-09-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | REPLACED 4' 5" OF PIPE
16 |  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | INSPECTION DUE TO WORK OF INSTALLING FIRE VALVE TO H.P.R. BOXES
16 |  |  |  | 0.75 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | STOCKTON | INSPECTION DUE TO INSTALLING 3/4" FIRE VALVE
93 | 87-00436-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1987-04-30 | 1987-04-30 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | TRACY | INSTALL (1) 2" SKINNER CLAMP ON MAIN RERUN SERVICE WITH 1/2" PL 3/4" SH CASING. STANDUP TEST ON SERVICE PIPE. LEAK WAS ON SERVICE 1' FROM TEE.
93 | 73-00328-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-01-29 | 1974-07-18 | Patch Welded |  | Steel/Wrought Iron |  | TRACY | 1-10-75 CLEAR.
93 | 83-00181-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1983-03-15 | 1983-04-08 | Patch Welded |  | Steel/Wrought Iron |  | TRACY
| 08-02198-1 | [16 empty] | TRACY
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1980-09-24 |  |  |  | Steel/Wrought Iron |  | TRACY;
16 | 88-00340-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1988-06-13 | 1988-10-06 | Patch Welded |  | Steel/Wrought Iron |  | TRACY | WELDED HALF SOLE ON 6" STL PIPE
|  |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1988-06-20 | 1988-10-16 | Patch Welded |  | Steel/Wrought Iron |  | TRACY
93 | 87-00727-1 | 162 | [9 empty] | 1987-12-21 | [5 empty] | TRACY | 45% 0/M BETWEEN 2 PATCHES AT LOCATION ABOVE.
93 | 85-00932-1 | 162 |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1985-10-03 | 1987-04-06 | Patch Welded |  |  |  | TRACY
93 | 85-00932-1 | 162 |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1985-10-03 | 1987-04-06 | Patch Welded |  | Steel/Wrought Iron |  | TRACY
| 86-00111-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Construction Defect |  | 1986-06-11 | [5 empty] | TRACY | CAP ON PLS TEE LEAKING
| 87-00749-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by Outside Forces |  | 1987-12-18 | 1987-10-21 | Replace Pipe and/or Service |  |  |  | TRACY
| 86-00154-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1986-07-30 | 1986-08-04 | Clamp |  | Steel/Wrought Iron |  | TRACY | CORROSION LEAK INSTALLED 2" HP SKINNER CLAMP.
93 | 82-10470-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1982-08-04 | 1982-08-17 | Other | GREASE VALVE | Steel/Wrought Iron |  | TRACY
93 | 87-00523-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1987-07-09 | 1987-07-09 | Clamp |  | Steel/Wrought Iron |  | TRACY | INSTALL 1' - 2" SKINNER CLAMP ON MAIN
| 86-00466-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1986-12-31 | 1987-01-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | TRACY | REPLACED 2' OF 3/4" STL PIPE SERVICE ONLY PITTED 1' FROM TEE. PRESSURE TESTED SERVICE AT 100 LBS FOR 10MIN. O.K.
16 | 87-00706-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1987-12-12 | 1987-12-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | TRACY | RERUN SERVICE LEAK OVER SERVICE IN STREET. INSERT 1/2" RL.
93 | 72-41511- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-03-25 | 1972-03-29 | Patch Welded |  | Steel/Wrought Iron
93 | 98-00098-1 |  |  | 2 | Service |  | Body of Pipe |  |  | Corrosion |  | 1998-10-01 |  | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | TRACY | CANNED AT WELD WORKED THIS LEAK ON SATURDAY SO COULD NOT GET CORROSION TEST ON PIPE
C/O H.P.R. SET @ MAIN
16 | 87-00421-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Construction Defect |  | 1987-03-09 | 1987-03-10 | Replace Pipe and/or Service |  | Other Plastic |  | TRACY | 1/2" PL SERVICE CRACK AT 2" FROM STL SERVICE TEE.
16 | 86-00153-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by Outside Forces |  | 1986-07-28 | 1986-07-28 | Replace Pipe and/or Service |  |  |  | TRACY | CONTRACTOR INSTALLED 8" WATER MAIN CUT 3/4" STL SERVICE REPLACED INSERTED 1/2" PLS PIPE.
93 | 86-00447-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1986-12-08 | 1986-12-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | TRACY | RERUN SERVICE INSERT 1/2" PLS
93 | 87-00095-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1987-01-26 | 1987-01-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | TRACY | INSTALLED (2) 4"M2, & 4' OF 4" STL PIPE, (2) 2" SAVE-A-VALVES. (2) 1" SAVE-A-VALVE
93 | 88-00399-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1988-08-10 | 1989-09-21 | Clamp |  | Steel/Wrought Iron |  | TRACY | REPAIRED WITH P. CLAMP
93 | 74-00259-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-02-22 | 1974-04-17 | Patch Welded |  |  |  |  | 5% OF MAINS AT REPAIR PATCH WHERE BOTH MAINS CROSS EACH OTHER AT N/W CORNER OF INTERSECTION; 20% LEAK IN MAIN IN ALLEY BETWEEN 6TH & 7TH W/S STREET.
93 | 73-00255-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-01-25 | 1973-02-02 | Patch Welded |  | Steel/Wrought Iron |  | TRACY | TESTED ALL FACILITIES CLEAR; LEAK IN M.H. ON MCARTHUR ST. & E. 10TH ST. MARKED YELLOW BY MANHOLE
93 | 74-00259-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-02-22 | 1974-04-17 | Patch Welded |  | Steel/Wrought Iron |  |  | 20% LEAK IN MAIN IN ALLEY BETWEEN 6TH & 7TH W/S STREET. INST. 4' OF HALF SOLE. 5 OTHER LEAKS HAVE BEEN REPAIRED ON THIS MAIN FROM...
93 | 75-00253-1 |  |  | 0.25 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1975-01-13 | 1975-09-16 | Other |  | Copper
93 | 72-62007-1 |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-10-26 | 1972-10-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | TRACY | REPLACE 3/4" SERVICE WITH 1/2" PL INSERT.
93 | 76-60506-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-07-29 | 1976-07-30 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | TRACY | 100% BLOWING 1' E/O REG PIT; STANDARD OIL LINE LAYING ON 4" GAS LINE LEAK BETWEEN PIPES. 100% BLOWING P E/O REG PIT.
93 |  |  |  | 4 | Distribution Feeder Main | [12 empty] | TRACY
93 | 77-00009-1 |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1977-01-10 | 1977-02-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | TRACY
93 | 72-00088-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-09-12 | 1973-12-05 | Patch Welded |  | Steel/Wrought Iron
93 | 77-00008-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1977-01-10 | 1977-02-18 | Patch Welded |  | Steel/Wrought Iron |  | TRACY | WRAP REMOVED BY BACKHOE TOO WHEN ST. OIL LINE INSTALLED.
93 | 72-00090-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-09-12 | 1974-10-07 | Patch Welded |  | Steel/Wrought Iron |  |  | 7% 68' WEST OF HPR BOX O/ MAIN BETWEEN YELLOW MARKS ON ROAD; 10% N/S ND 62' G/O DRIVE, 20% N/S ND W/S DRIVE, N/S ND SO W/O DRIVE. FOUND 4" HP STEEL MAIN IN BAD CONDITIONAT THEIR YOT. WELDED IN 4' OF HALF HOLE. 4" FILLED.
93 | 77-00007-1 | [10 empty] | 1977-01-10 | [6 empty] | RECHECK AT LATER DATE. LEAK #77-00008 FIXED. COULD BE SAME LEAK.
93 | 77-00214-1 |  |  | 0.25 | Other |  | Valves |  |  | Other |  | 1977-03-18 | 1978-01-13 | Other |  | Steel/Wrought Iron |  |  | 20% U.E.L. - @ H.P.R BOX LEAK ON 1/4 PLUG BASE OF METRIC VALVE. 100% IN H.P.R REG. BOX.
93 | 87-00660-1 |  |  | 2 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1987-10-06 | 1987-10-06 | Other |  | Steel/Wrought Iron |  | TRACY | VALVE ON REG STATION LEAKING, GREASED VALVE, PACKING LEAKING
93 | 89-00101-1 |  |  | 0.08 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1989-03-09 | 1989-08-09 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | TRACY | WELDED STL. PATCH OVER CORROSION LEAK
93 | 88-00405-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1988-08-15 | 1989-09-22 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | TRACY | T & R WELDED PATCH
93 | 79-00044-1 |  |  | 0.75 | Transmission |  | Other |  | BLOW OFF | Material Failure |  | 1979-01-06 | 1979-01-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | TRACY | REPLACE BLOW OFF ON H.P. REG. RECEIVE 3/4" IN H.P. REG. BOX
INSPECTION DUE TO EXPOSING VALVE NEAR MAIN TO LOWER 3/4" THAT FEEDS REG STATION. MAIN IN GOOD SHAPE.
| 10-09030-1 |  |  | 0.75 | Single Service |  | Regulator |  |  | Material Failure |  | 2010-05-19 | 2010-05-21 | Other | REPLACED HPR | Steel/Wrought Iron |  | ACAMPO | SOAP TESTED
| 10-09034-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | NEED GREASE | 2010-05-20 | 2010-07-14 | Other | GREASE VALVE | Steel/Wrought Iron |  | ACAMPO | GREASE VALVE IN HPR BOX
93 | 10-81202-1 | 1625-10 | 0.57 | 0.75 | Transmission >= 20% SMYS |  | Fitting | Regulator/Pilot | REGULATOR/PILOT | Construction Defect |  | 2010-09-27 | 2011-01-18 | Tighten Cap/Bolt - Fitting |  | Steel |  | COLLIERVILLE ACAMPO | TIGHTEN & REDOPED CAP & TIGHTEN REG FLANGE; LEAK IN HPR BOX - LEAK AT REG FLANGE& VALVE TEE. TIGHTEN & REDOPE CAP ON TEE - TIGHTEN FLANGE, SOAP TEST.
| 10-09011-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other | SCREWED LOOSE VALVE THREADS | 2010-05-13 | 2010-08-05 | Replace Main Valve < 2-inch |  | Steel/Wrought Iron |  | ACAMPO | MAIN LEAK; LEAK IS ON MAIN; REPLACED VALVE INSTALLED; SOAP TEST.
93 | 10-02491-1 | [5 empty] | Compression Coupling Stainless Steel | Fitting | FITTING | Other | LOOSE FITTING & REPLACED "O" RING |  | 2011-01-07 | Tighten Cap/Bolt - Fitting | GREASED |  |  | LODI | TIGHTEN FITTINGS & REPLACED "O" RINGS; ALL ABOVE GROUND PIPING TIGHTEN BOLTS & REPLACED O RINGS TO REPAIR.
| 10-02490 | 108 | 42.72 | 16 |  |  | Line Valve |  |  | Other |  | 2010-11-01 | 2011-01-04 | Tighten Cap/Bolt - Fitting | VALVE GLAND | Steel |  |  | LEAK ON MAIN; TIGHTENED GLAND ON 16" MLV 42.72
| 10-06187-1 |  |  | 0.75 | Single Service |  | Riser |  |  | Atmospheric Corrosion |  | 2010-06-07 | 2010-06-07 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | STOCKTON | SMALL LEAK ON RISER PUT 3/4" CLAMP. PUT CLAMP ON PIT; RISER HAD SMALL PITTED LEAK, REPAIRED BY INSTALLING 3/4" CLAMP. SOAP TESTED
| 10-06012-1 |  |  |  | Single Service |  | Body of Pipe |  |  |  |  | 2010-01-11 | 2010-01-11 | Other |  | Steel/Wrought Iron |  | SACRAMENTO | NO GAS FLOW. 3/4" STL SERVICE BENT AT CURB AND GUTTER, PULL RISER AND MANIFOLD 2" FROM WALL OF HOUSE.
| 10-06130-1 | 108 | 29.17 |  | Transmission |  | Valves |  |  | Other | 3/4" THREAD LEAK | 2010-04-14 | 2010-04-14 | Other | LUBED VALVE/ STAND PIPE | Steel/Wrought Iron |  | STOCKTON
| 10-06130-1 | 108 | 29.17 |  | Transmission |  | Valves |  |  | Other | 3/4" THREAD LEAK | 2010-04-14 | 2010-10-14 | Other | LUBED VALVE/ STAND PIPE | Steel/Wrought Iron |  | STOCKTON
| 10-02009-1 |  |  | 24 | Transmission |  | Valves |  |  | Other | TIGHTEN & GREASE VALVE | 2010-01-12 | 2010-01-13 | Other | TIGHTEN & GREASE VALVE | Steel/Wrought Iron |  | STOCKTON | TIGHTEN & GREASE VALVE; SOAP TESTED
| 10-02010-1 |  |  | 24 | Transmission |  | Valves |  |  | Other |  | 2010-01-13 | 2010-01-16 | Other | TIGHTEN & GREASE VALVE | Steel/Wrought Iron |  | STOCKTON | GREASED VALVE & TIGHTEN; SOAP TESTED
| 10-02010-1 | 108 |  | 24 | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2010-01-13 | 2010-01-16 | Other | TIGHTEN & GREASE VALVE | Steel/Wrought Iron |  | STOCKTON | GREASED VALVE & TIGHTEN; SOAP TESTED
| 10-91661-1 |  |  | 8 | Transmission |  | Fitting |  |  | Other | LOOSE CAP ON PCF FITTING | 2010-02-04 | 2010-09-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | STOCKTON | RE SEATED COMPLETION PLUG TIGHTENED CAP; SOAP TESTED FITTING AFTER SEATING COMPLETION PLUG AND TIGHTENING CAP
| 10-02244-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | THREADS TRANS VALVE | 2010-05-15 | 2010-08-04 | Replace Main Valve < 2-inch |  | Steel/Wrought Iron |  | TRACY | LEAK WORK ON BODY OF 3/4" VALVE. REPLACED WITH NEW 3/4" STL WELD-ON VALVE; CREW REPAIR LEAK WITH OVER 20 WELDER, SOAP TEST.
| 10-00059-1 | 384507 |  | 8 | Transmission |  | Fitting |  |  | Other | DRY PIPE DOPE | 2010-09-17 | 2010-09-20 | Other | REDOPED SAVER VALVE CAP AND RE-TIGHTENED | Steel/Wrought Iron |  | TRACY | REDOPED CAP ON SAVOR VALVE; SOAP TESTED CAP AFTER REDOPING 3/4" SAVER VALVE. TIGHTENED CAP.
| 10-06155-1 | 108 |  | 0.75 | Single Service |  | Body of Pipe |  |  |  |  | 2010-05-06 | 2010-05-06 | Replace Partial Service |  | Steel/Wrought Iron |  | MANTECA | REPLACED 11' OF 3/4 STEEL SERVICE ON HIGH SIDE OF HPR
| 10-06138-1 |  |  | 0.75 | Single Service |  | Other |  | BLOW OFF UN H.P.R. SET | Equipment Malfunction |  | 2010-04-22 | 2010-04-22 | Other | BLOW OFF VALVE | Steel/Wrought Iron |  | MANTECA | REPLACED REGULATOR & BLOW OFF VALVE; LEAK FOUND IN HPR ENCLOSED VAULT. T & R IS TO FIX. SOAP TESTED.
93 | 10-81682-1 | 1615-04 | 6.72 | 0.75 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Construction Defect |  | 2010-10-05 | 2011-01-14 | Tighten Cap/Bolt - Fitting |  | Steel |  | RIPON | TIGHTEN BOLTS ON REG; IN HPR BOX LEAK AT FLANGE OF REG. TIGHTEN TO STOP LEAK, SOAP TEST AND OK
93 | 10-00077-1 | 1615-04 |  | 0.75 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Construction Defect |  | 2010-10-15 | 2011-02-28 | Tighten Cap/Bolt - Fitting |  | Steel |  | RIPON | TIGHTEN FLANGE; LEAK ON FLANGE ON REG - TIGHTEN FLANGE - SOAP TESTED.
|  | 196 |  | 12 | [11 empty] | Steel |  | Andrus Is. | Tar Wrap on dog-leg. No water under wrap. Primer good. No crop damage
|  | 196 |  | 12 | [11 empty] | Steel |  | Andrus Is. | No crop damage.
|  |  |  | 12 | [11 empty] | Steel |  | Andrus Is. | Near irrigation ditch. No crop damage.
|  |  |  | 12 | [11 empty] | Steel |  | Andrus Island | No crop damage.
|  | 196 |  | 12 | [11 empty] | Steel |  | Andrus Is. | No crop damage
|  | 196 |  | 12 | [11 empty] | Steel |  | Andrus Is. | No crop damage
|  | 196 |  | 12 | [11 empty] | Steel |  | Andrus Is. | No crop damage
|  | 196 |  | 12 | [11 empty] | Steel |  | Andrus Is. | Wrap & primer in excellent condition. No crop damage.
|  | 196 |  | 12 | [11 empty] | Steel |  | Andrus Island | Wrap has been damaged. Area approx. 6" x 8" on top of pipe. Heavy scale limited to area damaged. Pipe exposed 10' each way from damaged area.
|  | 196 |  | 12 | [11 empty] | Steel |  | Andrus Is.
|  | 196 |  | 12 | [11 empty] | Steel |  | Andrus Is.
|  | 196 |  | 12 | [11 empty] | Steel |  | Andrus Is.
|  | 196 |  | 12 | [11 empty] | Steel |  | Andrus Is.
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Water next to main. No crop damage
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | Water next to main. No crop damge
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | WRAP good. No water. No crop damage.
|  | 195 |  | 10 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No crop damage
|  | 195 |  | 4 | [11 empty] | Steel |  | Rio Vista | No water under wrap. Rust. No crop damage
|  | 195 |  | 6.00 & 6.00 x 4.00 | [11 empty] | Steel |  | Rio Vista | No water under wrap. No crop damage
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | Heavy rust, lots of water. No pitting. no crop damage
|  | 195 |  | 6 | [11 empty] | Steel |  | Rio Vista | No water under wrap. No crop damage
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | No water under wrap. No crop damage
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Lots of water under wrap. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | No water under wrap. No crop damage
|  | 195 |  | 12 | [13 empty] | Rio Vista | Water under wrap. No pits. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No pits. No crop damage
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Water under wrap main was dug up under road that is why its so deep. No crop damage
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Water under main no crop damage
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Water under main. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No crop damage.
|  | 195 |  | 12 | [13 empty] | Rio Vista | Water under wrap. No crop damage
|  | 195 |  | 12 | [13 empty] | Rio Vista | Water under wrap. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | Water under wrap. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | No water. No crop damage.
|  | 195 |  | 8 | [11 empty] | Steel |  | Rio Vista | No water. No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | No water. No crop damage
|  | 195 |  | 8 | [11 empty] | Steel |  | Rio Vista | No crop damage
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | No water under wrap. No crop damage
|  | 195 |  | 8 | [11 empty] | Steel |  | Rio Vista | No crop damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Rio Vista | No crop damage. No water under wrap.
|  | 195 |  | 4 | [11 empty] | Steel |  | Sherman Isl. | Wrap looked good; 10'x10' corn damage
|  | 195 |  | 12 | [11 empty] | Steel |  | Sherman Isl. | Wrap looked good; 10'x10' corn damage
|  | 195 |  | 12 | [11 empty] | Steel |  | Sherman Isl. | Wrap looked good; 10'x10' corn damage.
|  | 195 |  | 4 | [11 empty] | Steel |  | Sherman Isl. | Wrap bonded to pipe good. Pipe looks good. 10'x10' corn damage.
|  | 195 |  | 12 | [11 empty] | Steel |  | Sherman Isl. | Wrap bonded to pipe good. Pipe looks good. 10'x10' corn damage
|  | 195 |  | 12 | [11 empty] | Steel |  | Sherman Isl. | Wrap bonded to main good. Pipe looks good. 10'x10' corn damage.
| 05-16901-1 | 169 | 5.1 | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2005-04-11 | 2005-04-23 | Other | Welded new pipe section; |  |  | Willows | Cut out and replaced 179'-6" of 16" L-169
|  | 169 | 5.10-5.14 | 16
|  | 167 | [13 empty] | Other | X-42
| 99-167-2 |  |  | 12 | Transmission |  | Body of Pipe | Other | Dig-in pipe servered | Damage by 3rd Party |  | 1999-11-11 | 1999-11-12 | Other | Inst. 44' pipe | Steel/Wrought Iron |  | Princeton | Inst. 44" Pipe; replaced pipe..44"
[5 empty] | Gathering | [7 empty] | 2001-08-22 |  |  |  |  | Orland
[16 empty] | Other | X-42 |  | weld on 2" sevice tee
Transmission
Transmission
52 | 82-57003-1 |  |  | 8.625 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1982-09-16 | 1982-11-04 | Clamp |  | Steel/Wrought Iron |  |  | Repaired with a 8" Plideo leak clamp. See MR459780; Internal Corrosion Leak, Hole at 5:30 on pipe
52 | 87-57003-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1987-02-08 | 1987-02-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Tyler Isl. | ACCT-3661-2040 Leak repaired with 25 3/8'' piece of pretested 6'' pipe spects - API-5LX4200 Internal corr.
52 | 87-90003-1 |  |  | 8 | Gathering |  | Other Welds |  |  | Other |  | 1987-03-10 | 1988-03-01 | Other |  | Steel/Wrought Iron |  | Sacto county uninc | Closed Pin-off tee & abandoned gage tap. Work done on maintenance activity 6088/1020
52 | 87-90004-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1987-11-09 | 1987-11-09 | Other |  | Steel/Wrought Iron |  | Rio Vista Uninc. | Repaired 2-4-88 as part of GM4611323. Replaced ruptured segment with 15' of API 5LGR B SMLS SMYS 35000 .280 WT
| 87-90006-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Other |  | 1987-08-12 | 1988-03-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | RIO VISTA UNINC | REPLACED SECTION OF 1/2 IN" SENSING LINE ON MAINT ACCT 6088/1020
|  |  |  | 2 | Other | [6 empty] | 1982-06-22 |  |  |  | Steel/Wrought Iron |  | Pindale
25 |  |  |  | 8 | Distribution Main |  | Body of Pipe |  |  | Other |  | 1973-11-29 |  |  |  | Steel/Wrought Iron |  | Fresno
25 |  |  |  | 6 | Distribution Main |  | Other |  |  | Other |  | 1973-06-11 |  | PATCH WELDED |  |  |  | Fresno
25 |  |  |  | 8 | Distribution Main |  | Other |  |  | Other |  | 1973-07-13 |  | PATCH WELDED |  | Steel/Wrought Iron |  | Fresno
25 |  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  | 1973-09-07 |  | PATCH WELDED |  | Steel/Wrought Iron |  | Fresno
| 09-30536-1 |  |  | 1.25 | Gathering |  | Valves |  | VALVE THREADS | Other | Threads | 2009-05-26 | 2009-07-24 | Other | Tighten Valve | Steel/Wrought Iron |  | Fresno | Riser; Bottom of valve; Tigthen valve; 20' N/W of Palm. 20' W/On Palm. N/W corner of Palm & Sierra.
| 09-30580-1 |  |  | 0.75 | Gathering |  | Threads |  | THREADS | Other | THREADS | 2009-06-04 | 2009-07-31 | Other | Tightened valve | Steel/Wrought Iron |  | Fresno | Riser; Bottom of valve; Threads; Tightened valve "threads leaking"; Tightend valve; 585 W/Sierra Ave. 75' S/W end of build. 33# next to elect boxes. Apartments N/W end of complex.
| 09-30581-1 |  |  | 0.75 | Gathering |  | Body of Pipe |  |  | Other | loose valve | 2009-06-04 | 2009-07-31 | Other | TIGHTEN VALVE | Steel/Wrought Iron |  | Fresno | Riser on south side; Bottome of valve; Tighten valve.
| 09-30587-1 |  |  | 0.75 | Single Service |  | Other |  | VALVE THREADS | Other | Threads | 2009-06-04 | 2009-07-31 | Other | VALVE THREADS | Steel/Wrought Iron |  | Fresno | Riser; Bottom of valve; Tighten valve to stop leak; 50/ W. Sierra Ave. N/W front of building. Bld 27" & 28"
| 09-38569- |  |  |  | Branch Service |  | Fitting |  |  | Stress Corrosion Cracking |  | 2009-06-02 | 2009-06-03 | Replace Partial Service |  | PE2406 (Yellow or Orange) |  | Fresno | Between houses at 6473 + 6461 N. Reminton Ave; Repaired by replacing branching tee; Branching ampfit 3 way tee corroded and leaking. Replaced with 1" permasert tee + coupling, 5' of 1" pc., + 1 1/4" riser.
70 | 76-30259-1 |  |  | 3 | Other |  | Valves |  |  | Material Failure |  | 1976-07-12 | 1976-07-14 | OTHER |  | Steel/Wrought Iron |  | Fresno | Repaired Leak by greasing valve made soap test found no leak. 3" - FLG'D Valve near Sta. A - 05.
25 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1973-11-16 |  | Other | OTHER | Steel/Wrought Iron |  | Fresno
25 |  |  |  | 2 |  |  | Body of Pipe |  |  | Damage by outside Forces |  | 1973-04-23 |  |  |  | Steel/Wrought Iron |  | Fresno | Repair 3/4" Gas Service. Just 9" anode at tee. Test at 100 PSI for 10min at tee.
70 |  |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1981-10-20 | 1981-10-20 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Clovis | Contractor damaged 2" steel main on W. Holland at Villa on 10-20-81 @ 9:16am. Damaged section is to be removed on 10-21-81. No leak or gas loss. 10-21-81 Repair made by installing 2 - 2" m/2's, cutting out 12" of 2" stl pipe and welding 12" of new 2" stl pipe.
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-01-15 |  |  |  | Steel/Wrought Iron |  | Fresno
25 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1973-04-25 |  | PATCH WELDED |  | Steel/Wrought Iron |  | Fresno | Killed gas service at main.
70 | [17 empty] | Clovis | Spot check TP main for bore job; Transmission main was dug-up to daylight for bore job. It was in good condition.
[5 empty] | Transmission | [10 empty] | Steel/Wrought Iron |  | Fresno | Bored and installed new leads. From the 10" T.P. main to E.T.S
|  |  |  | 10 |  |  | Body of Pipe | [8 empty] | Steel/Wrought Iron |  | Fresno | Exposed 6" of T.P. Main at this location to test thickness.
[7 empty] | Bell Joint | [8 empty] | Steel/Wrought Iron
70 | 81-30141-1 |  |  | 12 | Distribution Feeder Main |  | Physical/Mechanical Joint |  |  | Other | 1/2 NIPPLE BETWEEN VALVE & PILOT FILTER; LEAKING @ THREADS | 1981-04-01 | 1981-04-01 | Other | DOPED & TIGHTENED | Steel/Wrought Iron |  | Fresno | 1/2" nipple between valve and Pilot filter leaking @ threads. Doped & tightned.
|  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Fresno | Contractor digging with shovel for the installation of an eight inch sewer... off of 12" feeder main. Inspected main O.K. ; illegible comments due to fading.
|  |  |  | 6 | Transmission |  | Body of Pipe | [8 empty] | Steel/Wrought Iron |  | Fresno | Dug up 6" TP main to do pipe thickness test rapps pipe & backet 100% sand.
| 09-30831-1 |  |  | 0.75 | Single Service |  | Fitting |  |  | Material Failure |  | 2009-07-18 | 2009-12-17 | Deactivated Entire Service |  | Steel/Wrought Iron |  | Fresno | c/o 3/4" Stl. SVC. at main.
|  |  |  | 6 | Transmission |  | Other | [8 empty] | Steel/Wrought Iron |  | Clovis
70 | 79-50169-1 |  |  | 2 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-07-19 | 1979-07-19 | Other |  | Other Plastic |  | Fresno | contractor damaged 2" PL main with 580 case backhoe. repairs made by InSt. (2) 2" AMD fit coupling and 18" 2" pl. pipe. Photos taken.
70 | 10-81104-1 | 1202-18 | 4.07 | 0.25 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-02 | 2011-02-18 | Other | REDOPED/TIGHTENED 1/4 NIPPLE | Steel |  | Fresno | 3lks @ st all marked w/yellow zip ties; fitting leaking on metric valve; Redoped Nipple beyond metric valve; Repared leak on nipple pipe coming out of metric valve. redoped and reTightened, soap tested.
70 | 85-70021-1 |  |  |  | Transmission |  | Fitting |  |  | Other |  | 1985-03-22 | 1985-03-22 | Replace Pipe and/or Service |  | Steel |  | Clovis | Dope on line to gage box was dry. Redoped fittings. Post checked 4.3.85
70 | 85-70020-1 |  |  | 12 | Transmission |  | Other |  |  | Material Failure |  | 1985-03-22 | 1985-03-22 | Replace Pipe and/or Service |  |  |  | Clovis | Body casting on 829 grove pilot was craced. replaced with new part. Post ck .1% 4.3.85 Br. New A form made out. ; illegible comment due to fading
70 | 91-30345-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1991-10-10 | 1991-10-15 | Other |  | Steel |  | Fresno | Grease vavle (F-04)
70 | 88-30345-1 |  |  |  | Transmission |  | Other |  |  | Other |  | 1988-10-19 |  | Tighten Cap or Bolt |  | Steel |  | Fresno | Thighten all bolts on Flange
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1973-05-10 |  | PATCH WELDED |  | Other Plastic |  |  | Killed 1" plastice gas service
|  |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  |  | 1977-04-22 |  |  | Steel |  | Fresno | Test 1/2" pe. Gas se to 3922.24 white hot. Branch se - to 3934-36 white. Cut off 3/4" gas se - to 3934-36 white. Gut off 1/2" Cas. gas se - at 3922.24 white; partical illegible comment due to fading.
|  |  |  | 16 | [8 empty] | 1999-04-19 |  |  | Steel/Wrought Iron |  | Fresno | Wrapped Slot on 16" T.P. main damaged.
70 |  |  |  | 16 | [8 empty] | 1992-07-16 |  |  | Steel |  | Fresno | Connected two locating wires to TP main and installed a G-5 Box inside curb. Main is 59" deep.
70 | 77-50036-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-04-14 | 1977-04-14 | OTHER |  | Steel/Wrought Iron |  | Fresno; | contractor was ripping out old curb, cracked 3/4 wipple @ drin riser. Removed drip riser 3" N of main. Did not go to main. Contractor has since poured anro cement alley approch. No billing required.
70 | 82-50021-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  | 1982-04-06 | 1982-04-06 | Other |  | Steel/Wrought Iron |  |  | Damaged 1" dripline. contractor was excavating at a depth of 54" with a case 580-B backhoe, for installation of an 8" water main. The backhoe struct and damaged the 1" stl. dripline. Dripline was already leaking due to corrosion leaks made permannet by removing drip line from the tup of drip pot and installing 1" screwed cap at the top of the drip pot. Pot may removed at later date. At company convience.
70 | 79-50011-1 |  |  | 1.25 | Other |  | Drip |  |  | Damage by outside Forces |  | 1979-01-04 | 1979-01-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Fresno | Permanent repairs 1-17-1979 on w03-4519C
|  |  |  | 16 | Transmission | [7 empty] | 1977-06-27 |  |  | Steel |  | Fresno | installed ETS on 16" T.P. main #138 2 white wires #10
70 | 80-50113-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-06-16 | 1980-06-16 | Other |  | Steel/Wrought Iron |  | Fresno | While digging to install curb. Contractor broke valve off 1 1/4" blow-off. Made permanet repairs by abandoning 1 1/4" blow-off at main. Gas lost to atomospahere was negilible. No AR. No billing.
70 | 83-50018-1 |  |  | 1.25 | Other | Drip riser | Body of Pipe |  |  | Damage by outside Forces |  | 1983-04-08 | 1983-04-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Fresno | City of Fresno street crew hit drip riser with 580c backhoe while cleaning up by side of roadway. Drip riser and casing were way above grade level made temp repars by pinching down 1 1/4" stl. pipe and removing screwed 90 degree elbow 56" below ground level and replacing it with an 1 1/4" service valve. All leakage was then stopped made permanet repair by cutting-out drip riser. Also installed 1 1/4" P.C.F 12" s/of the 4" Gas Main. No charge, for file only.
25 | 73-70009-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-06-13 | 1973-06-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Fresno
|  | 138 |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Fresno | 626 ' N/N P.L of E. florence Ave, + 18' E/W P.L. of Maple; Browning Constr, co; Trenched alongside line #138 for about 15', to install 12" waterline for the city, about 3' horizontal seperation.
|  |  |  | 0.75 | Other | [6 empty] | 1979-01-18 |  |  |  | Steel/Wrought Iron |  | Fresno
|  | 138 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | crossing T.P. 138 645' s/s P.L. of East Dorothy Ave; Browning Constr. trenced across T. P. #138 to install a 6" sewer line.
|  |  |  | 12 | Transmission | [6 empty] | 2008-09-15 |  |  |  | Steel/Wrought Iron |  | Fresno
| - 40- |  |  | 12 | Transmission |  | Physical/Mechanical Joint |  |  | CONSTRUCTION DEFECT |  | 1985-03-12 | 1985-04-17 | Tighten Cap or Bolt |  |  |  |  | Redope & tighten 1" plug on blow off valve A; Valve A-24 6' E/E PL of Cherry & 37' S/N PL of Jensen.
70 | 81-30380-1 |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1980-10-27 | 1981-12-03 | Other |  | Steel/Wrought Iron |  | Fresno | Repair leak in 25c Pilot Reg; upgrade N W Pet to #2 9.8.81. Found readings in Reg. Vaults. Issued new leaks report. 2-2-82
70 | 81-30507-1 |  |  | 12 | Transmission |  | Other |  |  | Other |  | 1981-12-02 | 1982-11-02 | Other |  | Steel/Wrought Iron |  | Fresno | Made permannet repair by lowering line pressure on T.P. Main #138. Rethreading 1/4" nipple on body of pipe and replacing 1/4" metric of valve. downgrade to #2 5-3-82. Found #3 reading in valve casing. Issued new #3 Leaks report 12-1-1982.
70 | 81-30367-1 |  |  | 12 | Transmission |  | Valves |  |  | Other |  | 1981-09-01 | 1981-10-05 | Other |  | Steel/Wrought Iron |  | Fresno | Metric valve leaking. Tightened plug. Stafford 10-5-81. Found readins - issused new leak report 12-2-1981
70 | 81-30046-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1981-02-10 | 1981-03-02 | Other |  | Steel/Wrought Iron |  | Fresno | Tightened Bonnet on metric Ftg. Found valves #4 & 5 leaking. Leaking at down stream flanges. Replaced gaskets and insulation kits in both valves. 3-10-1981 Pihil Sotry; 1/4" metric leaking from Bonnet prossed holes 12" deep D.S. of valves #3, 4 & 5, #3 clear, #9 & #5 30% readins on J.W.
70 | 80-30302-1 |  |  | 0.5 | Other |  | Regulator |  |  | Other |  | 1980-07-09 | 1980-07-09 | Other |  | Steel/Wrought Iron |  | Fresno | Tightened bolts on 25c Pilot S/E Pit. Flamepack checked on 10-27-90. Found various readings, issued new #3 leak reports 10-27-80. LY
70 | 80-30303-1 |  |  | 1 | Other |  | Other Welds |  |  | Other |  | 1980-07-09 | 1980-07-09 | Other |  | Steel/Wrought Iron |  | Fresno | Fiybd gas leak on 1" HP Tee on 4" TP. Feeder main in station. ...pairs by arc welding our leak. No other leaks found. Flamepack checked on 10-27-82. Found various reading issued new #3 leak report 10-27-1980.
| 79-30055-1 |  |  |  | Distribution Feeder Main |  | Regulator |  |  | Other |  | 1979-04-05 |  | Other |  | Steel/Wrought Iron |  | Fresno | Ref 80-30302 80-30303; Refer to leak # 6-7-79 Repaired leack on 25C-100 pilot, (lose bolts on dia.) Peterson/Schulte; Note 10% leak was A#1 attached new number this leak # to be #3 leak
70 | 79-30139-1 |  |  |  | Distribution Main |  | Regulator |  |  | Other |  | 1979-06-07 | 1979-06-07 | Other |  | Steel/Wrought Iron |  | Fresno | 6/17/79 Repaired leak on 25c-100 pilot. Found loose bolts on diaphram tightened same. Peterson/Schulte; Found reading. Issued new leak report 7.9.79 LY
70 | 78-30409-1 |  |  |  | Distribution Main |  | Regulator |  |  | Other |  | 1978-10-23 | 1978-11-13 | Replace Pipe and/or Service |  | Other |  | Fresno | 11-13-78 repair leaks in to regulators pits only. H Mcrilin; All reading except at reg. pits are a ground level next to valve & tees. Also odor in air with prob. appr. 5' above ground got reading as high as 0.1%.
70 | 82-30029-1 |  |  | 0.5 | Other | [6 empty] | 1982-02-02 |  |  |  | Steel/Wrought Iron |  | Fresno
70 | 81-30431-1 |  |  | 6 | Distribution Feeder Main | [6 empty] | 1981-09-03 |  |  |  | Steel/Wrought Iron |  | Fresno
70 | 79-30296-1 |  |  | 0.5 | Other |  | Physical/Mechanical Joint | Regulator | REGULATOR | CONSTRUCTION DEFECT | OTHER | 1979-09-13 | 1979-09-19 | Other |  | Other |  | Fresno | Repair 1/2" 2 SC Pilot.. redop pipe fittings; reading are in Blue on attached sketch 2-5-80. Issued New grade 3 leak. Reading at valves are ground level of stems. Also at gage box. 3869-j1-8 2-5-80 LY. Issued new #3.
70 | 82-70025-1 |  |  | 0.75 | Other |  | Valves |  |  | Other |  | 1982-08-02 | 1982-08-02 | Other |  | Steel/Wrought Iron |  | Fresno | Relief on Pri. Rea blowing Rebuil Pri Rea
70 | 82-70003-1 |  |  | 0.75 | Transmission |  | Regulator |  |  | Other |  | 1982-01-12 | 1982-01-12 | Other |  | Steel/Wrought Iron |  | Fresno | Relief 1/alue blowing
70 | 95-30114-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  |  | 1996-03-01 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Fresno | welded two corrossion leaks 5' n/o tee. Soap tested OK. Stafford. 3-1-96
25 | 72-40017-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-05-15 | 1972-05-16 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Clovis | Cathodic protection for belt line job in progress
70 | 94-30121-1 |  |  | 6 | Transmission |  | Valves |  |  | Material Failure |  | 1994-02-24 | 1994-02-24 | Other |  | Steel/Wrought Iron |  | Fresno | Grease valve for permanent repairs; Contractor exuacating - for the installation of water pipe. Smell odor of gas in the air. Flame pack leak surveyer were notified and they surveyed the area, and found leak on TP main at valve casing. Crew went out and dug up around valve casing and expose complete valve 6" STL and soap tested. Flange blots were not leaking, but valve stem was. Grease vavle fitting for permanent repaires, it was an old abandon service valve. Buried valve but wrapped valve first. Soap tested no leaks.
|  |  |  | 12 | Transmission | [6 empty] | 2008-07-10 |  |  |  | Steel/Wrought Iron |  | Fresno | The contractor, Pavletich Elect., bored across Olive Ave, to install (4) 4" phone ducts. Stand-by required while crossing 12" T.P. main.
70 | 81-30273-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1981-06-16 | 1981-12-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Fresno | Found gas leak on 6" HP gas valve. Repaired by freasing gas valve. Also uncovered 4" HP gas valve which was blacktop over. No leak found on 4" gas valve.
[12 empty] | 1998-07-15 | [5 empty] | Fresno | inst 3/4 serv Tee on 6" TP Main and ran new 2" TP Serv. 3/8 tap; ran new 2" TP serv. 3/4" serv. Tee with 3/8 tap. Fire valve 1' off 6" main.
70 | 83-30219-1 |  |  | 6 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1983-11-04 | 1984-03-23 | Other |  | Steel/Wrought Iron |  | Fresno | Found leak at flanges on valve F-03. Repaired by tighting botls around flange. Painted bolts and nuts with primer and wrapped completed 3-23-83. G. Gilmore.
25 |  |  |  | 2 | Distribution Main | [10 empty] | Other Plastic |  | Fresno
70 | 79-30160-1 |  |  | 0.75 | Other |  | Other |  |  | MATERIAL FAILURE |  | 1979-06-12 | 1979-06-12 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron |  | Fresno | corrosion leaks on riser. Temp. repairs made. See permanent info below. R. Garcia. Made permantent repairs by installing a 1/2" plastic insert 6-26-79. 3/4" riser leaking at seam. Used (2) handy clamps for temp. Repair. Customer complaint of gas oder in patio area. R. Garcia
70 | 79-50010-1 |  |  | 1.25 | Other |  | Fitting |  |  | Damage by outside Forces |  | 1979-01-05 | 1979-01-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Sanger | Customer was backing out of driveway. Part of auto hooked exposed 1 1/4 blow off valve and broke off at reducing weld blow off to be abandoned. Removed blow off 1-19-79. No billing.
70 | 91-50125-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1991-09-04 | 1991-09-04 | Replace Pipe |  | Aldyl A (Tan or Gray) |  | Sanger | Repaired 1/2" Aldyl A plastic service. Replaced 2" plastic using two couplings; 1/2" adyl A service damaged by hoptoe Replaced 2' section with plastic using two coupling. Service was cut 10' from PL. on w/s of "O" str.
[5 empty] | Other | House Line | [11 empty] | Sanger | Buried house line was leaking 20 C.F.H. Piser area and 1 houseline covered with cement. Serviceman isolated leaking section of H.L. and other H.L. test OK. Got 32% gas readings got continually smaller after H.L. section was disconnected. All reading cleaing after H.L shut off.
| 09-30217- |  |  | 3 | Distribution Main |  | Mechanical Joint |  |  | Other |  | 2009-03-31 |  |  |  | Steel/Wrought Iron |  | Tranquility | Leak in reg pits vaults on N/S of Morton, marked with yellow X; Leak in regulator pits on N/S of Morton w/o Colorado.
[13 empty] | 2009-04-01 |  |  | Steel/Wrought Iron |  |  | Repaired leaks on union coupling, and doped and tightened. repaired leaks on stainless steel fittings by tightening.
70 | 09-31338-1 |  |  | 0.75 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Other | Loose bolts | 2009-09-23 | 2011-03-01 | Tighten Cap/Bolt - Fitting |  | Steel |  | Tranquility | NE conrner at Colorado; Hi Lo Set. On valve at hi 0 hi set. hi/low valve. Primary pit; Tightened bolts on regulator body; Tightened bolts on regulator in primary pit. Soap tested OK.
70 | 09-31338-1 |  |  | 0.75 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Other | Loose Bolts | 2009-09-23 | 2011-03-01 | Tighten Cap/Bolt - Fitting |  | Steel |  | Tranquility | NE corner at Colorado; Hi Lo Set. On valve at hi to hi set. hi /low valve. Primary Pit; Tightened bolts on regulator in primary pit. Soap tested OK.
70 | 96-30156-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-09-12 | 1996-09-12 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | San Joaqun | Welded sleeve;
70 | 96-30156-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | INTERNAL CORROSION |  | 1996-09-12 | 1996-09-12 | WELD OVER SLEEVE OR CAN |  | Steel/Wrought Iron |  | San Joaqun | Welded sleeve
| 09-30216- |  |  | 2 | Transmission |  | Fitting | Regulator | REGULATOR | Material Failure |  | 2009-03-31 | 2009-04-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | San Joaquin | Leak in 3 HPR pits, marked in yellow X; Repaired diapheram on regulator. Tightened bolts on other regulator. Also tightened and redoped union fittings for regulator.
|  | 111 |  | 3 | Transmission | [10 empty] | Steel/Wrought Iron |  | San Joaquin | Installed E.T.S Big Fink
|  | 111 |  | 3 | Transmission | [10 empty] | Steel/Wrought Iron |  | San Joaquin | installd ET.S. Big Fink
70 | 91-30312-1 |  |  | 3 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1991-09-12 | 1991-09-24 | Weld Over Sleeve or Can |  |  |  | San Joaqin | Welded sleeve over corrosion leak;
70 | 91-30312-1 |  |  | 3 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1991-09-12 | 1991-09-24 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | San Joaqin | Welded sleeve over corrosion leak; Welded sleeve over internal corrosion leak 9.24.91. Sleeve to be removed and pipe to be resplaced per ridding. Peraces
|  |  |  | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | San Joaquin | Contractor, Golden State, is boring acrossing Clolrado, + Trenching on the E/ side, to install phone duct. They are corssing T.P. lines. PG+E standby required.
70 |  | 111 | [13 empty] | Steel |  | San Joaquin | relocated reg. pit and installed D.B & insert; part of comment is illegible due to fading
70 | 91-50102-1 |  |  | 2 | Other | M | Body of Pipe |  |  | Digin |  | 1991-07-16 | 1991-07-16 | Replace Pipe |  | TR 418 |  | San joaquin | Replaced 2 plastic main; Contractor damaged 2 main...; illgeible comment due to fading
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | Fresno | Installed E.T.S big fink.
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | Fresno | Installed E.T.S big fink
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | Fresno | Installed E.T.S big fink
|  |  |  | 4 | [11 empty] | Steel |  | Kerman | install new 2" pl main
70 | 93-30142-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1993-08-05 | 1993-08-12 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Kerman
70 | 78-30261-1 |  |  | 4 | Transmission |  | Other |  |  |  |  | 1978-07-20 |  |  |  | Steel/Wrought Iron |  | Fresno | 1-18-79 Note: 6" steeline crossing paved road is casing and belongs to Texaco. In the 6" casing their is 42" fiberglass pipe. At location where 2" fiber glass pipe comes through casing is where we are getting 45.0% reading left trench open and notified Texaco; There is a 6" - 50 lb Texaco gas return line over the Irans line reading is at point where the 6" goes under ground for street crossing. Reading could be from the 6". 6" is hallow. Jst for road crossing.
70 | 81-30434-1 |  |  | 4 | Transmission |  | Regulator |  |  | CONSTRUCTION DEFECT |  | 1981-06-02 | 1981-06-02 | Other |  | Steel/Wrought Iron |  | Kerman | Repair 1 1/2 HPR 2nd stage. Replace diaph & botls, rusted.
70 | 79-30151-1 |  |  |  | Transmission | [6 empty] | 1979-06-06 | [5 empty] | Kerman | Issued new leak Gr#3 (2-2-82)
|  | 111 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Installed E.T.S big fink
70 | 82-30028-1 |  |  | 2 | Distribution Feeder Main | [6 empty] | 1982-02-02 |  |  |  | Steel/Wrought Iron |  | Kerman | Name changed to black valvet ptbm. 500' batch. Changed to 5 M rotory mts installed.
70 |  | 111 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | Fresno | Note rewapped 50' 12". Wrap single coat of tar found wrap 2" x 2' knocked off pipe. Light rust at this point. Also found 8" x 2" metal ring about 2" from bare spot on pipe. Found no other at this point.
| 10-30201-1 | 111 |  | 0.75 | Transmission |  | Other |  | valve tee cap | Other | REDOPED & TIGHTENED | 2010-10-03 | 2010-10-19 | Other | redoped & tightened | Steel/Wrought Iron |  | Fresno | Tightened cap; redoped, tightened cap, soap test.
70 | 71-40002- | 111 |  | 12 | Transmission | [6 empty] | 1971-01-14 |  |  |  | Steel |  | Fresno | Probed & checked with J/W indicator. Found no evidence of leak.
|  | 111 |  | 12 | Transmission |  | Body of Pipe | [8 empty] | Steel/Wrought Iron |  | Fresno | Installed E.T.S big fink
|  | 111 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | Fresno | installed ETS big fink
70 | 73-50009-1 | 111 | 17.1 | 12 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 1973-03-30 | 1973-04-04 | Other |  | Steel/Wrought Iron |  | Fresno | Welded 1" HP say-a-valve over pin pole in Girth Weld. On top of 12" Main. Note! Tope of valve is 23" below ground level owner was notified. Repaired 4-4-73 John Pate
70 | 82-50044-1 |  |  | 12.38 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1982-07-01 | 1982-07-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Fresno | illegible comments due to fading
70 | 92-70022-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Damage by outside Forces |  |  | 1992-04-30 | Replace Pipe |  | Steel/Wrought Iron |  | Selma | Repaired gas leak due to trks driving over valve; recommend service be replaced BS. Service very thin.
|  |  |  | 0.75 | Service |  | Body of Pipe |  |  | Other |  | 1973-01-08 | 1973-01-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Selma
70 | 86-30319-1 |  |  | 1.5 | Distribution Main |  | Regulator |  |  | Other |  | 1984-09-04 | 1986-09-08 | Other | ; | Cast Iron |  | Fresno | South reg. box apx 598' N/N PL of annadale on W. side of east -Upgrade #hot 2 86 BR. Rebuilt H.P.R.
20 | 94-50040-1 |  |  | 3 |  |  | Body of Pipe |  |  | Digin |  | 1994-02-22 | 1994-02-22 | Replace Pipe |  | TR 418 |  | Fresno | Reparied Damaged 3" plastic main; Reparied damaged 3" plastic coas. main. Replaced 44" TR-418. Used two 3" electro-fusion couplings. Soup tested Ok.
70 |  | 138 |  | 16 | [11 empty] | Steel |  | Frenso | Installed test leads on gas line #138TP; Installed test: Leads on gas line #138 TP at both locations. 2 wires bonded to main
| 85-70003-1 |  |  | 1.25 | Distribution Main |  | Regulator |  |  | Other |  | 1985-01-05 | 1985-01-05 | Other |  | Steel/Wrought Iron |  | Fresno | Spring chamber froze reg. in open position. Rebuilt reg (secondary reg., east run)
| 00-30092- | 138 |  | 0.75 | Service |  | Regulator |  |  | Material Failure |  | 2000-09-11 | 2000-09-12 | Other | REPLACE REG. GASKET. | Steel/Wrought Iron |  | Fresno | Repaired by M&C mechanic R. Schlepp; Found gas leak on H.P.R set in 17" x 30" box leaking at the regulator. Called M&C mechanic to replace Reg. Gasket. No other leaks found.; Replace existing reg. pit and installed 2024 Rock well fire vavle.
|  | 138 |  | 12 | Transmission | [12 empty] | Fresno | Browning construction Co. Trenched across T.P. Line 138 to install an 18" water line, requiring a P.G. & E. Stand-by.
| 10-30185-1 | [10 empty] | 2010-09-14 | [5 empty] | Fresno | (Post-it note) Need: Permit; - COF-SWP; -TP/TC ; See Terry McBlahaney
| 10-30185-1 |  |  |  | Single Service |  | Valves |  |  | Other | NEEDED GREASE. | 2010-09-14 | 2010-10-09 | Other |  | Steel/Wrought Iron |  | Fresno | Greased Valved
| 10-30185-1 |  |  | 4 | Single Service |  | Valves |  |  | Other |  | 2010-09-14 | 2010-10-09 | Other |  | Steel/Wrought Iron |  | Fresno | Tighten grease, soap test
70 | 86-30398-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1986-10-07 | 1986-10-08 | Other |  | Copper |  | Fresno | Found cracked curb valve. Greased and wrapped valve. Called Jerry Scott, valve's to be replaced 2-9-87; Replaced broken curb valve. Reset valve box. Soap tested for leaks, NO leak; 10% in W. Valve. Greased valve 10-8-86. Called for crew at 2750 S. East, 3710 crew responded
70 | 86-30416-1 |  |  | 12 | Transmission |  | Other |  |  | Other |  | 1986-10-07 | 1986-10-08 | Other |  | Steel/Wrought Iron
25 | 84-30184-1 |  |  |  | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1984-09-04 | 1984-09-04 | Other |  | Steel/Wrought Iron |  | Fresno | Tore down, 1 1/4" H.P.R. set -Rebuilt. Pipe dope dried out- Redoped fittings
25 |  |  |  | 1.25 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1984-09-04 | 1984-09-04 | Other |  | Steel/Wrought Iron |  | Fresno | Removed, repaired, replaced 11/4" H.P.R. set. Pipe dope dried out. Redoped leaking fittings.; Post check clear 1-9-85 BR.
70 | 84-50056-1 |  |  | 1.25 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1984-05-08 | 1984-05-08 | Replace Pipe and/or Service |  | TR 418 |  | Huron | Backhoe dug-in to 11/4" PL main. Repair was made by installing one 11/4" AMP fit one dressor and 12" 11/4" PL Main. Bar Test ok.
68 | 92-70015-1 |  |  | 3 | Other | M | Other |  |  | Other |  | 1992-03-25 | 1992-03-26 | Other |  | Aldyl A (Tan or Gray) |  | Huron | Customer complaint of odor in air. Ran land air mover 2-25-92. 3-26-92 rechecked, risidual to be rechecked; Customer compaint of odor in air. Leak was repaired on 3-15-92. Risidual gas used land air mover.
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | Coalinga
|  |  |  | 6 | [11 empty] | Steel/Wrought Iron |  | Coalinga
|  |  |  | 4 | Distribution Feeder Main | [10 empty] | Steel |  | Coalinga | Abandoned 4" DFM and old meter station. Install new meter station.
|  |  |  | 4 | [11 empty] | Steel |  | Coalinga | Install Trans. Tap and Service for Santa Fe Energy
|  |  |  | 4 | [11 empty] | Steel |  | Coalinga | Install 2" gas service
|  |  |  | 4 | [11 empty] | Steel |  | Coalinga | Install tap and H-11/H-12 Set
|  | 300B | 359.16 | 1.25 | [11 empty] | Steel |  | Caolinga
70 | 85-30376-1 |  |  | 2 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1985-10-16 | 1985-12-04 | Other |  | Steel/Wrought Iron |  | Three Rocks | 2 Reg. pit from north, side by side 1% off of 300A. Center Reg Pit. Redoped cap on by-pass valve P.S.
68 | 84-25017-1 |  |  | 2 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-10-03 |  | Clamp |  | Steel/Wrought Iron |  |  | Approx 2676FT N/of section line. Install 2" leak clamp on main; Install leak clamps for temporary repair.
68 | 84-25017-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1984-10-03 | 1984-10-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Three Rocks | Installed 2 2" Splite mueller fittings and 4-1" savor valve nipple and replaced 17' ot 2" grade "B" seamless pipe.; Down greaded leak to #2. Location in remote area and only 20% gas. Down graded...
25 |  |  |  | 2 | Transmission | [6 empty] | 1975-11-06 |  |  |  | Steel/Wrought Iron
|  | 111 |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Inst. E.T.S. next to line marker
|  | 111 |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Hielm
|  |  |  | 18 | Transmission | [10 empty] | Steel/Wrought Iron |  | Burrell
|  | 138 |  | 18 | Transmission | [6 empty] | 1974-06-10 |  |  |  | Steel/Wrought Iron |  | Burrell
|  | 138 |  | 18 | [11 empty] | Steel |  | Burrell | Abandoned tap ES240+21 & Reg. Sta. IT-08
70 |  | 138 |  | 16 | [11 empty] | Steel |  | Burrell | Installed two test leads and installed link marker for cathodic protection; Inst. Two test leads for cathodic protection ;
| 10-70054-1 |  |  | 0.5 | Branch Service |  | Other |  | POWELL KIT LEAKING | Unknown |  | 2010-04-19 | 2010-04-21 | Replace Partial Service |  | PE2406 (Yellow or Orange) |  | Cantua Creek | Reinserted 1/2" PL into casing used new powell kit to complete service. Also used electro-fusion 1/2" coupling.
70 | 93-30129-1 |  |  | 0.75 | Transmission |  | Tap Connection |  |  | Material Failure |  | 1993-04-29 | 1993-05-04 | Tighten Cap or Bolt |  | Steel |  | Five Points | Redoped & Tightened plug & cap on punch tee.; Tightened cap & plug on 3/4" punch TP main.
70 | 87-30014-1 | 138A |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1987-03-02 | 1987-03-03 | Other |  | Other Plastic |  | Five Points | H202 Leaking replace.; W/ Line 138A on Mt. Whitney Ave. N/W Reg. pit 10% and needs repair ASAP.
|  |  |  | 20 | [11 empty] | Steel/Wrought Iron |  | Five Points | Installed ETS on 16" & 20" TP Mains.
70 | 85-70088-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1985-11-07 | 1985-11-07 | Other |  | Cast Iron
68 | 81-25043-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1981-07-24 | 1982-07-30 | Other |  | Steel/Wrought Iron |  | Coalinga | Leak in 2nd stage Reg. pit 1% gas. Caps on Mueller valves leaking.
68 | 82-25014- |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1981-07-24 | 1982-07-30 | Other |  | Steel/Wrought Iron |  | Coalinga | Leak in 1st stage reg. pit 1% gas. 1/4" metric leaking
25 | 86-50048-1 |  |  | 6 | Transmission |  | Valves |  |  | Damage by outside Forces | ; | 1986-07-05 | 1986-07-05 | Other |  | Steel/Wrought Iron |  | Coalinga | Contractor damaged 1/4" metric valve with trailor hitch. Made permanent replairs 7-5-86 by rethreading 1/4" nipple and installing metric valve. Gas blew to atmosphere for 1hr. 25 min. Three customers involved in shut down.
|  |  |  | 2 | Other |  | Regulator |  |  | Other |  | 1981-08-26 | 1981-08-26 | Other |  | Steel/Wrought Iron |  |  | 3/4" plugs on reg. loose, redpoed. Found meter set covered w/ grain. Advised sup. of mill to get cleaned off & kept as such
70 | 91-30060-1 | 300B |  | 0.75 | Transmission |  | Fitting |  |  | Other |  | 1991-01-16 | 1991-01-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Coalinga | Tightened union on Reg. pit; Bar tested area for leak. Found Reg. pit covered. Leak inside Reg. pit @ Union. Tightened Union.; Bar tested area for leak. Found reg. pit covered. Leak inside reg. pit @ union. Tihgtened union.
70 | 97-30086-1 |  |  | 10 | Transmission |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1997-07-14 | 1997-07-25 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Caolinga | Due to lack of matsrialt pressure drop procedure unable to work. LK. unitl 7-25-97. Per gas supply-Mike Teare; Found 10" bolted flange dresser leaking. Lowered pressure to 250 PSI. Tightened fitting, brought pressure up. Soap teested O.K.
|  | 164 |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | Coalinga
70 | 84-30059-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1984-05-10 | 1984-06-05 | Other |  | Steel/Wrought Iron |  | Coalinga | Valve #52 needs repair. Blowing gas 10% #2. Greased valve. ; ; ;
70 | 96-30195-1 | 164 |  | 10 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1996-05-22 | 1996-05-24 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | 198 / I5 | Found leak on 10" dresser. Stopped leak by tightening bolts on dresser.; Found leak on 10" T.P. main by Amador station. Repaired leak by tightening bolts on dresser. Approx 2 miles N/o Hwy 198, 10' W/o Power Poles - 10" T.P. main is bare pipe with bare dressers and should be put in for replacement.
70 | 96-30194-1 | 164 |  | 10 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1996-05-22 | 1996-05-22 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | 198 / I5 | Tightened dresser on 10" T.P. Main; 10" T.P. main is bare along with dresser. Should be put in for replacement.
70 | 96-30193-1 | 164 |  | 10 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1996-05-22 | 1996-05-28 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | 198 / I5 | Repaired leak on 10" T.P. dresser by tightening bolts on dresser.; Found leak on 10" T.P. Main by Amador station. Repaired leak by tighening bolts on Dresser- 64' E/o N/E corner of Amador corner fence. 23' N/o N/E corner of Amador Station fence. T.P. main should be replaced - Pipe is bare and so are dressers.
68 | 81-25025-1 |  |  | 5 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1980-02-25 | 1981-08-11 | Other |  | Steel/Wrought Iron |  | Coalinga | Welded can on main Marker 77+80
70 | 80-30533-1 |  |  | 5 | Transmission |  | Valves |  |  | Other |  | 1980-02-25 | 1981-01-07 | Other |  | Steel/Wrought Iron |  | Coalinga | Repaired by removing metric valve and welding 2" savor valve over nipple. 1-7-81; Reading at bottom of hill just 5 of second... N/o 198...ground with ... 10-31-80. Will be checked on annual. In May.
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | Coalinga;
|  | 164 |  | 8 | Transmission |  |  | Valves | [7 empty] | Steel/Wrought Iron |  | Coalinga | Installed E.T.S. Big FInk
68 | 98-70112-1 | 164 |  | 8.625 | Transmission |  | Body of Pipe |  |  | Digin |  | 1998-08-17 | 1998-08-17 | Replace Pipe |  | Steel/Wrought Iron |  | Coalinga | Isolated 3 miles of Transmission Main to the end of line #164, using valve at Amador Station. Cut out 6' section of damaged 8" pipe, welded in pre-tested 6' section of 8" pipe for repair.
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Coalinga | Inst. E.T.S. big fink
70 | 90-30126-1 | [11 empty] | 1990-05-21 |  |  |  |  | Coalinga | Found leak on standard oil's house line. Advised customer, repairs made by customer
[12 empty] | 1986-03-05 | [5 empty] | Coalinga | Info only; Surveyed approx. 1/2 mile w/ Oil City Rd. Found Clear.
|  |  |  | 4 | [11 empty] | Steel |  | Coalinga | Installed 14' 6" STL. Installed 6" Kerotest valve. Installed 16" casing cover. Installed 4" PCF B.T. per GM4293528
68 | 89-30072-1 | [10 empty] | 1989-05-01 | [5 empty] | Coalinga | Found leak on Chevron line 5-4-89 Repaires referred to customer
68 | 89-30073-1 | [10 empty] | 1989-05-01 | [6 empty] | Found Leak on Texaco house line 5-6-89 Repairs referred to customer
70 | 80-30060-1 |  |  | 1.25 | Other |  | Valves |  |  | Construction Defect |  | 1980-02-13 | 1980-12-02 | Other |  | Steel/Wrought Iron |  | Coalinga | Close leaking 1/4" needle valve (gage connection) tighten 3/4" valve bonnet on filter
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Coalinga
25 |  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Coalinga | Install drain tube on 6" line. ...Oil line
|  |  |  | 8 | [11 empty] | Steel |  | Coalinga | Install T.P. Service
|  |  |  | 8 | [11 empty] | Steel |  | Coalinga | Removed 3" valve due to leak. Installed 3" weld cap.; Installed 1" Sava-A-Valve nipple. Cut off and remove 3" valve installed weld cap.
|  |  |  | 6 | [11 empty] | Steel |  | Coalinga
70 | 90-30214-1 |  |  |  | Transmission |  | Valves |  |  | Other |  | 1990-08-29 | 1991-03-25 | Other |  |  |  | Coalinga | Bar tested and JW area. Aerated area for temporary repairs; Located main and bar tested and J.W. area and found 6% over 3-way tee and 2% in valve casing. Released gas build-up in valve casing and readings dropped. T.P. Gas valve is in the process of being replaced because each year valve gets repaired, and the following year it starts leaking again. 3-25-91
70 | 91-30402-1 | [10 empty] | 1991-11-12 | [5 empty] | Coalinga | See Remarks other side; Bar tested over main... Los Gatos Creek, 100ft. to the north... Future stub N/o Creek -Records show was removed due to leak
70 | 90-30125-1 |  |  | 4 | Transmission |  | Valves |  |  | Material Failure |  | 1990-05-21 | 1990-05-23 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Coalinga | Found bolts under. Under valve leaking. Removed bolts and isntalled lock washer. Six bolts under valve could not be tightened.
70 | 88-30081-1 |  |  | 3 | Transmission |  | Valves |  |  | Other |  | 1988-06-15 | 1988-06-15 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Coalinga | Tightened bottom flauge on Rockwell. Hyperseal valve and greased to slow leak. Valve should be replaced ASAP. ; No welding at this location
|  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
70 | 97-30032-1 |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1997-05-06 | 1997-05-20 | Other |  | Steel/Wrought Iron |  | Coalinga | Look for gas leak; All reading are 15' apart. On 5/-19-97 we dug up 8" from power pole to the south 150' and we found no leak. Soap tested all of the pipe also. 5-7-97 Dug up area, green dirt. Let airiate. Will return w/ Backhoe to excavate other location.; Unwrapped 3 welds and soap tested Ok. Welds are marked Red. There 40' apart. First weld is 15' n/o e/s marker 581+58 Marker is over 6" pipe (T.P.)
|  |  |  | 10 | [11 empty] | Steel |  | Coalinga | Installed 1" rockwell plug valve with high head extension and extended grease fitting. Welded 11/4" socket weld elbow and 3/4" socket weld coupling for tie in.
70 | 79-30065-1 |  |  | 4 | Distribution Feeder Main |  | Girth Weld |  |  | Construction Defect |  | 1979-04-19 | 1979-04-19 | Other | WELD OVER SLEEVE | Steel/Wrought Iron |  | Coalinga | Repairs made by welding 6" full weld over sleeve on main. Installed 4/24/79
70 | 90-30127-1 |  |  | 8 | Transmission |  | Fitting |  |  | Corrosion |  | 1990-05-24 | 1990-05-24 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Coalinga | Tightened cap & plug on blow off Save-A-Valve.; Found cap & plug leaking on 8" T.P. Main, tightened to stop leak.
70 | 80-30532-1 |  |  | 0.75 | Other |  | Valves |  |  | Other |  | 1980-10-31 | 1980-12-02 | Other |  | Steel/Wrought Iron |  | Coalinga | Greas by-pass valve
70 | 80-30530-1 |  |  | 5 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1980-02-14 | 1981-01-07 | Other |  | Steel/Wrought Iron |  | Coalinga | Repaired by loosening cap, doping and putting cap back on. 1-7-81; Cap on nipple under feeder line above ground.
70 | 84-30070-1 |  |  |  | Transmission |  |  |  |  | Other |  | 1984-05-10 | [5 empty] | Coalinga | Replaced on GM1938034; Bolts on the flange are loose
70 | 89-30074-1 | [10 empty] | 1989-05-05 | 1989-05-08 |  |  |  |  | Coalinga | Wind blowing, probably picked up readings from surrounding oil field/ gas facilities
68 | 85-25009-1 |  |  | 10 | Distribution Feeder Main |  | Physical/Mechanical Joint |  |  | Other |  | 1985-05-08 | 1985-06-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Coalinga | Found leak on screw flange on 10" valve in vault. On E/side of HWY 33 on- Coalinga line. Could not repair need M&C mechanic with Right tools.; T.P. Line. new ... adult approx 126' E/E PL of HWY 33 poss. V-3-12 leak of 1% recommend repair ASAP. Tightened 2 loose bolts on flange to valve 4.00 Rest ck. clean. 7-31-85
68 | 85-25010-1 |  |  | 10 | Distribution Feeder Main | [6 empty] | 1985-05-08 |  |  |  | Steel/Wrought Iron |  | Caolinga | .5% T.P. HP- Reg Pit
68 | 98-70112-1 | 164 |  | 8.625 | Transmission |  | Body of Pipe |  |  | Digin |  | 1998-08-17 | 1998-08-17 | Replace Pipe | ; | Steel/Wrought Iron |  | Coalinga | Isolated 3 miles of Transmission main to the end of line #164, using valve at Amador Station. Cut out 6' section of damaged 8" pipe, welded in pre-tested 6' sectionof 8" pipe for repairs.
| 00-50108-1 | 164 | 5.55 | 8 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party |  | 2000-07-05 | 2000-07-06 | Other | 2" SAVER VALVE | Steel/Wrought Iron |  | Coalinga | Weld 2" save valve over hole; See attached sheet
|  | 164 |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | Coalinga | Installed E.T.S. Big fink
|  | 164 |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | Coalinga | Inst. E.T.S. big fink
|  |  |  | 2 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Installed ETS on 2" T.P. Main
68 | 94-70090-1 | 300B | 367.62 | 2 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1994-06-27 | 1994-06-28 | Replace Pipe |  | Steel/Wrought Iron |  | Huron | Repair corrosion leak by repairing pipe 1' section; Needed 1' section of pipe 2" .54 APSI SL GB SMLS tested 12-2-81 1350# at Weld saop
70 | 80-30592-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1980-09-26 | 1981-02-12 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Fresno | Repaired main by installing 3' of 2" main. Installed 1" savor valve down stream of tie-in piece, 2-12-81; Dead cotton (bare ground) 30' radius 9-26-...
70 | 80-30593-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-09-26 | 1981-02-11 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Fresno | Repaired main by installing 32" -2" Stl. Main. This leak was apparently caused by a ripper. 2-12-81; Dead cotton (bare ground) 50' Radius 9-26-80
70 | 80-30594-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1980-09-26 | 1981-02-11 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Fresno | Repaired leaks by installing 18" piece & 3' piece 2" main. Install 1" savor valve down stram on tie-in piece.; Power pole #9 consit of 3 poles in a row. Dead cotton 70' radius
70 | 80-30595-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1980-09-26 | 1981-02-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Fresno | Repaired leak by installing 18" -2" pipe. Installed 1" savor valve down stream of tie-in piece.; Dead cotton 50' radius ; ;
70 | 80-30596-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1980-09-26 | 1981-02-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Fresno | Repaired leak by installing 7' of 2" main. Installed 1" Nipple down stream of tie-in piece 2-10-81; Dead cotton 45" radius 9-26-80
68 | 82-25009-1 |  |  | 1.25 | Transmission |  | Regulator |  |  | Other |  | 1982-09-02 | 1982-09-05 | Other |  | Steel/Wrought Iron |  | Fresno County | Rebuilt reg. diaphram was leaking
| 85-70062-1 |  |  | 4 | Transmission |  | Meter |  |  | Other |  | 1985-08-12 | 1985-08-12 | Other |  | Cast Iron |  | Avenal | Both threads on Arms leaking, both inspection plates leaking. Redoped all & tightened MTR#497731-J Rd-62914
25 |  |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1984-07-16 | 1984-09-07 | Other |  | Steel/Wrought Iron |  | Kettleman City | Info See MTR Leak; *Valve leaking through grease stem. Greased valve, leak stopped! (Tough one!); Found #3 leak on valve #2 of MTR Station. Recomend repairs, as leak will get worse.
98 | 10-88220-1 | DCUS2451 |  | 2 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-22 | 2011-02-18 | Other | Turned inlet valve off. | Steel |  | Kettleman City | To be repaired when idol service is requested to be turned back on.; Above ground inlet/outlet valve at reg station shut off service to meter set is not in use at this time, leaks will be repaired when request for gas to be turned back on.
|  |  |  | 2 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1985-04-04 | 1985-04-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Kettleman City | Replaced 6' of damaged 2" pipe. Rebuilt Reg. set. (Set run over by car) Pipe rep#2959585
| 09-30214-1 |  |  | 0.75 | Distribution Main |  | Other |  | LEAK ON GUAGE TAP OUTLET | Other | LOOSE | 2009-03-30 | 2009-04-06 | Other | TIGHTENED FITTING | Steel/Wrought Iron |  | Kettleman City | Gas leak found on guage tap outlet in H.P.R. box, repaired and soap tested.
| 71-40004- |  |  | 2 | Other | M | Body of Pipe |  |  |  |  | 1971-03-11 | 1971-03-11 |  |  | Steel |  |  | Pipe is in very bad condition should be replaced
Other Plastic
98 | 10-82015-1 | 379 | 1.62 | 4 | Transmission >= 20% SMYS |  | Other |  | LEAK ON CUSTOMER SIDE OF PIPE | Inspection Only | INSPECTION ONLY, NO LEAK, NO DAMAGE | 2010-09-29 | 2011-01-26 | Soap and/or Tape - Other |  | Steel |  | Coalinga | Soap tested rewrapped main; Customer's house line leaking. PG&E crew dug up 98' of main soap test main. No leaks found. Notified Harris Ranch w/ issue and also spoke w/ Dave Woods (resident).
98 | 10-88030-1 | 300B | 365.17 | 1.25 | Single Service |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-10-26 | 2011-03-29 | Tighten Cap/Bolt - Fitting |  | Steel |  | Coalinga | Repaired leaks. Soap tested ok.; Repaired leaks. Soap tested ok.
98 | 10-88030-1 | 300B | 365.17 | 1.25 | Single Service |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-10-26 | 2011-03-29 | Tighten Cap/Bolt - Fitting |  | Steel |  | Coalinga | Repaired leaks. Soap tested ok.; Repaired leaks. Soap tested ok.
| 10-81101-1 | 1202-06 |  |  | Distribution Main | [6 empty] | 2010-10-02 | [5 empty] | Fresno | Distribution leak; Over Dist. valve (#2), at intersection of switch and mill brook
|  | 138 | V-22.04 | 6 | Transmission |  | Fitting |  |  | Other | O-Ring | 2010-09-29 | 2011-03-29 | Tighten Cap or Bolt | BLOW OFF | Steel/Wrought Iron |  | Burrell | Greased valves, cleaned, oiled, greased O-ring, made gasket, and reset blow off gasket.; Greased valves, cleaned, greased o-ring, made gasket, and reset blow off. Soap tested, no leaks.
98 | 10-88030-1 | 300B | 365.17 | 1.25 | Single Service |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-10-26 | 2011-03-29 | Tighten Cap/Bolt - Fitting |  | Steel |  | Coalinga | Repaired leaks. Soap tested OK.
10 | 10-81101-B |  |  | 2 | Distribution Main <= 60 PSIG |  | Threads |  |  | Other | DRY SEALANT | 1970-10-02 | 2011-03-01 | Other | REMOVE/RESEAL COMPLETION PLUG | Steel |  | Fresno | Over Dist. @PCF; Extract completion plug apply sealant and reseal and cap.; Remove and reseal completion plug
| 10-81101-1 | 1202-06 | [15 empty] | Fresno | Distribution leak. Over Dist. Valve (#2) at intersection of switch and millbrook.; Need crew for repaires- Distribution;
| 10-81101-1 | 1202-06 | 2.03 | 2 | Distribution Main |  | Other |  | Threads | Other | DRY THREAD SEALANT | 2010-10-02 | 2011-03-01 | Other | REMOVE/RESEAL COMPLETION PLUG | Steel/Wrought Iron |  | Fresno | Reseal completion plug
| 10-82018-1 | 1210-01 | 3.25 | 2 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-05 | 2010-10-06 | Other | SPLIT CONTROL | Steel/Wrought Iron |  | Huron | Crew excavated location. Found that a tree root had wrapped around the main pulling off the tar wrap, this causing the pipe to be exposed to the ground/soil, this causing the pipe to corrode,
| 10-82018-1 | 1210-01 | 3.25 | 2 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-05 |  |  |  | Steel/Wrought Iron |  | Huron
| 10-82076-1 | 1210-01 | 3.25 | 2 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-05 | 2010-10-06 | Other | SPLIT CONTROL | Steel/Wrought Iron |  | Huron | Crew excavated location. Found that a tree root had wrapped around the main pulling off the Tar wrap. This causing pipe to be exposed to the ground this caued pipe to corrode.
10 | 10-88124-1 | 1209-01 | 9.05 | 0.75 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-10-27 | 2011-03-10 | Tighten Cap/Bolt - Fitting |  | Steel |  | Fowler | Trans, tap for 1-2?; Remove cap apply new sealant, install cap; Remove cap re-doped & re-installed cap for repair
70 | 10-88124-1 | 1209-01 | 9.05 | [8 empty] | 2010-10-27 | [5 empty] | Fresno
70 | 10-88124-1 | 1209-01 | 9.05 | 0.75 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-10-27 | 2011-03-10 | Tighten Cap/Bolt - Fitting |  | Steel |  | Fowler | Trans tap for 1-2?; Remove cap apply new sealant, install cap; Remove cap re-doped & re-installed cap for repair
70 | 10-88124-1 | 1209-01 | 9.05 | [8 empty] | 2010-10-27 | [5 empty] | Fresno
70 | 10-88061-1 | 1211-04 | 11.34 | [8 empty] | 2010-10-25 | [5 empty] | Coalinga | No leaks found on our equipment; No leaks found on PG&E equipment. Odor coming from well#23, across street per Tony Guzman 3/9/11
70 | 10-88124-1 | 1209-01 | 9.05 | 0.75 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-10-27 | 2011-03-10 | Tighten Cap/Bolt - Fitting |  | Steel |  | Fowler | Trans. tap for 1-2?; Remove cap apply new sealant, install cap; Remove cap re-doped & re-install Cap for repair
70 | 10-81101-B |  |  | 2 | Distribution Main <= 60 PSIG |  | Threads |  |  | Other | DRY SEALANT | 2010-10-02 | 2011-03-01 | Other | REMOVE/RESEAL COMPLETION PLUG | Steel |  | Fresno | Over Dist. @PCF; (Post-it Note) GM 75350; Extract completion plug apply sealant and reseal and cap; Remove and reseal completion plug
| 10-81101-1 | 1202-06 |  |  | Distribution Main | [6 empty] | 2010-10-02 | [5 empty] | Fresno | Distribution leak. Over Dist. Valve (#2) at intersection and Millbrook.; Need crew for repairs - Distribution;
| 10-81101-1 | 1202-06 | 2.03 | 2 | Distribution Main |  | Other |  | THREADS | Other | DRY THREAD SEALANT | 2010-10-02 | 2011-03-01 | Other | REMOVE/RESEAL COMPLETION PLUG | Steel/Wrought Iron |  | Fresno | Reseal completion plug
70 | 10-88500-1 | 138B | 7.63 | 0.75 | Single Service |  | Regulator/Pilot |  |  | Unknown |  | 2010-10-26 | 2011-03-14 | Other | REBUILT REGULATOR | Steel |  | Fresno | HPR box; Rebuilt regulator; Rebuilt regulator in secondary vault; Rebuilt regulator in secondary pit. Soap tested ok.
70 | 10-88502-1 | 1209-01 | 9.46 | 0.75 | Single Service |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-28 | 2011-03-04 | Tighten Cap/Bolt - Fitting |  | Steel |  | Fresno | In Box; Redoped and tightened all fittings. Soap tested ok.; redoped and tightened fittings in vault. Soap tested ok.
70 | 10-81104-1 | 1202-18 | 4.07 | 0.25 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-02 | 2011-02-18 | Other | REDOPED/TIGHTENED 1/4" NIPPLE | Steel |  | Fresno | Fittings on Metric valve leaking; Redoped nipple beyond metric valve; Redoped nipple beyond metriv valve; Replaired leak on nipple. Pipe coming out of metric valve. Redoped and retightened. Soap test ok .
| 10-81082-B |  |  | 0.75 | Distribution Main <= 60 PSIG |  | Other |  | STEEL CAP | No/Deteriorated Pipe Dope |  | 2010-10-03 | 2011-02-22 | Tighten Cap/Bolt - Fitting |  | Steel |  | Fresno | AX from hwy marker 35 & hwy 145; Redoped and tightened 3/4" steel cap; redoped and tightened 3/4" steel cap; Re- pipe-doped and tightened steel cap
| 10-81123-1 | 1209-01 |  | 0.25 | Distribution Main |  | Valves |  |  | Other | TIGHTENED FITTING | 2010-10-04 | 2011-02-15 | Other | REDOPED/TIGHTENED METRIC VALVE | Steel/Wrought Iron |  | Fresno | In Dist. Reg pit.; Repairs made in Dist. Pit
98 | 10-88106-1 | 1221-01 | 0.04 |  |  |  | Fitting |  |  | Other | DRIED PIPE DOPE | 2010-11-03 | 2011-02-22 | Other | REDOPED | Steel |  | Avenal | Avenal primary reg; Redoped and retightened H-202 Relief valve; Redoped, retightened H-202 Relief valve
98 | 10-88220-1 | DCUS2451 |  | 2 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-22 | 2011-02-18 | Other | TURNED INLET VALVE OFF | Steel |  | Kettleman City
98 | 10-88220-1 | DCUS2451 |  | 2 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-22 | 2011-02-18 | Other | TURNED INLET VALVE OFF | Steel |  | Kettleman City | To be repaired when idol service is requested to be turned back on; Above ground inlet/outlet valve at reg. station shut off, service to meter is not in use at this time. Leaks will be repaired when request for gas to be turned back on.
70 | 10-81001-1 | 1212-01 | 2.75 | 2 | Single Service |  | Curb Valve |  |  | Other |  | 2010-10-06 | 2011-02-16 | Greased - Other |  | Steel |  | Coalinga | Greased valve; Greased valve; Leak on grease fitting of valve. Greased to stop leak.
70 | 10-88121-1 | 1209-01 | 6.68 | 0.75 | Single Service |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-10-27 | 2011-03-07 | Tighten Cap/Bolt - Fitting |  | Steel |  | Fowler | Redoped, tightened fittings; Repaired leaks in H.P.R. box. Soap tested ok.
70 | 10-88122-1 | 1209-02 | 1 | 6 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other |  | 2010-10-27 | 2011-03-04 | Greased - Other |  | Steel |  | Fowler | Greased valve; Greased & operated valve; Greased valve and valve box filled w/ water, no bubbles
70 | 10-88501-1 | 1209-01 | 9.5 | 0.75 | Single Service |  | Curb Valve |  |  | Other |  | 2010-10-28 | 2011-03-04 | Other |  | Steel |  | Fresno | Operated valve; Operated valve. Soap tested ok.
98 | 10-88106-1 | 1221-01 | 0.04 | 0.75 |  |  | Fitting |  |  | Other | DRIED PIPE DOPE | 2010-11-03 | 2011-02-22 | Other | REDOPED | Steel |  | Avenal | Avenal primary reg.; Redoped and retightened H-202 Relief valve; Redoped, retightened H-202 relief valve.
70 | 10-88001-1 | 379 | 1.6 | 2 | [7 empty] | 2010-10-26 |  |  |  | Steel |  | Coalinga | GTLS leak; O reads over PGE main- customer side; Soap tested 2" pipe at 300# no leaks found. Approx 90' trench open and soap tested.
|  |  |  | 4 | Gathering | [10 empty] | TR 418 |  | Fresno | Stand by insted posts.;
70 |  |  |  | 4 | Transmission | [6 empty] | 1976-09-24 |  |  |  | Steel/Wrought Iron |  | Kerman | Installed 4" PCF untilired exsisting PCF and removed 4" valve welded in 28" of 4" pipe; GM 490785
|  |  |  | 4 | [11 empty] | Steel |  | Kerman | Install gas service. Repair leak on single customer reg. set. H.P.R.; Existing HPR set welded leak on HPR set-Pin off serv. at main.
| 85-30377-1 |  |  | 0.75 | Distribution Main |  | Regulator |  |  | Other |  | 1985-11-14 | 1985-11-14 | Other |  | Steel/Wrought Iron |  | Kerman | Installed rebuilt reg & Relief. Greased by-pass valve. Cleaned out box, painted set.
70 | 81-30531-1 |  |  | 0.75 | Service |  | Tap Connection |  |  | Other |  | 1981-12-18 | 1982-02-12 | Other |  | Steel/Wrought Iron |  | Kerman | Repaired leaking Dist. Reg. pit. Repairs were made by pinning of tee st. t.p. main. Then installing a 3/4" 2024 fire valve and high head ext. and replacing old by-pass valve with a rockwell 2024 3/4" valve. Testing welds and putting pit back into operation.
|  |  |  | 4 | [11 empty] | Steel |  | Kerman | Repaired leak in Dist. Reg Pit. Repairs were made by pining off tee at T.P. main. Installed 3/4" 2024 fire valve and high to high. Installled new 2024 by-pass valve. Testing welds and putting service back into operation.
70 | 81-30527-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Material Failure |  | 1981-12-18 | 1981-12-29 | Other |  | Steel/Wrought Iron |  | Kerman | Found various fitting leaking due to pipe dope drying up shut set down and redoped all fitting and valves that were leaking.
70 |  |  |  | 4 | Transmission | [6 empty] | 1976-09-21 |  |  |  | Steel/Wrought Iron |  | Kerman | Installed 4" PCF at 32' and 38' N/N PL. Show removed drip riser welded in 18" of 4" pipe.
70 | 81-30113-1 |  |  | 0.75 | Distribution Main |  | Valves |  |  | Other |  | 1981-04-13 | 1981-04-15 | Other |  | Steel/Wrought Iron |  | Fresno | Upgrade to Hot#2 as it is nearing explosive mixture 4-13-81. Bypass leaking. Greased by-pass. To be done on upgrade.
70 |  |  |  | 4 | Transmission | [6 empty] | 1976-09-14 |  |  |  | Steel/Wrought Iron |  | Kerman | Installed 2-4" PCF ANSI, 1031+1037 N/N PL Gettysburg. Removed drip riser welded in 24" 4" pipe.
70 | 85-30028-1 |  |  | 0.75 | Transmission |  | Regulator |  |  | Other |  | 1985-01-28 | 1985-02-04 | Other |  | Steel/Wrought Iron |  | Kerman | 3/4" by pass valve leaking. Greased valve. OK; 10% at above address. Hot #2 post check 10% new form a made at BR. 4-3-85
70 | 84-50131-1 |  |  | 0.75 | Distribution Main |  | Regulator |  |  | Other |  | 1984-10-20 | 1984-10-20 | Other |  | Steel/Wrought Iron |  | Kerman | Greased by-pass valve, rebuilt reg. & relief. Issued new leak.
70 | 81-30423-1 |  |  | 4 | Distribution Feeder Main | [6 empty] | 1981-08-28 |  |  |  | Steel/Wrought Iron |  | Fresno | Leak surveyed main and could not find leak asumed clear. 8-13-84
70 | 81-30343-1 |  |  | 0.75 | Transmission |  | Other Welds |  |  | Other |  | 1980-03-14 | 1981-08-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Fresno | Upstream of H.P.R. leaking repaired. Replaced union and nipple; 8.0% reading on 1st ...upgraded to #2 8-18 4PPM on 4th ...8-19-81
70 | 82-70012-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Material Failure |  | 1982-02-26 | 1982-02-26 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Kerman | After uncovering T.P. main, we located two pinholes in the seam at the bottom of main 432' N/N PL of Ashland and 8' W/E PL of Madera Ave. Repairs were made by welding a full encirclement can 18" long on sleeve. We used an 8' stack out of bellhole to control gas we then puraed and soap tested can line pressure 200lbs; Seam opened up 8' from weld. On 4" stl. T.P. main two holes in a 5" area. 6" full circle can API-5L 6R. B. SMLS .250wall
70 |  |  |  | 4 | Transmission | [6 empty] | 1976-09-23 |  |  |  | Steel/Wrought Iron |  | Kerman | Installed 2-4" PCF ANSI 719' + 725' N/N PL Ashland. Removed drip riser welded in 5' of 4" pipe.
70 | 78-30219-1 |  |  |  | Transmission | [6 empty] | 1978-07-25 | [5 empty] | San Joaquin | Clear 9/15/80 Mobil/survey; There are three reg. pits and all are reading 2%
70 | 86-30324-1 |  |  | 0.75 | Distribution Feeder Main |  | Other |  |  | Other |  | 1986-08-12 | 1986-08-26 | Other |  | Steel/Wrought Iron |  | Kerman | No leak up on Reg. Replaced H.P.R. Set
70 | 82-30286-1 | [10 empty] | 1982-10-29 | [5 empty] | Kerman
70 | 82-70028-1 |  |  | 0.75 | Distribution Main |  | Regulator |  |  | Other |  | 1982-09-13 | 1982-09-14 | Other |  | Steel/Wrought Iron |  | Kerman | Rebuilt trans. set. Tightened packing glands on valves. Issued new leak form
70 |  |  |  | 4 | Transmission | [6 empty] | 1976-09-28 |  |  |  | Steel |  | Kerman | Installed 2-4" PCF 407' + 411' N/N PL Dakota. Removed blow off and replaced 18" 4" pipe
70 |  |  |  | 4 | Transmission | [6 empty] | 1976-09-29 |  |  |  | Steel/Wrought Iron |  | Kerman | Installed 2-4" PCF 1082' + 1078' N/N PL. Removed drip riser and replaced 18" 4" pipe
|  |  |  | 4 | Transmission | [7 empty] | 1973-07-02 |  |  | Steel/Wrought Iron |  | Kerman | Installed new service
|  |  |  | 0.75 | Distribution Main | Transmission Main | [9 empty] | Steel/Wrought Iron |  | Kerman
|  |  |  | 0.75 | Service | [7 empty] | 2006-04-27 |  |  | Steel/Wrought Iron |  | Kerman | 8" stub w/ dead end cap; C/O @ TP Main
70 |  |  |  | 4 | Transmission | [6 empty] | 1976-10-06 |  |  |  | Steel/Wrought Iron |  | Kerman | Installed 2-4" PCF 100' and 108' Safe clinton. Installed 4" block valve and blow off 103' safe clinton
70 | 84-30208-1 | [10 empty] | 1984-08-13 | [5 empty] | Kerman | Leak at valve# K-02 approx. 12' W/E P2 of madera and 75' S/S PL of Clinton
70 | 84-30207-1 | [10 empty] | 1984-08-13 | [5 empty] | Kerman | Leak in reg. pit at above AD
|  | 283 |  | 4 | Transmission | [6 empty] | 2002-03-14 |  |  |  | Steel/Wrought Iron |  | Kerman | Altered pit-abandon 3/4" Mueller tee installed 1" Valve tee.
| 01-30047-1 |  |  |  | Transmission |  | Regulator |  |  | Material Failure |  | 2001-10-10 |  | Other |  | Steel/Wrought Iron |  | Kerman | Meter set leaking (reg. pit) blow off leaking- replace; 10-22-01 Soap tested all fittings their was leak on H&R set. Will repair 10-23-01; 4-3-02 Found blow off leaking replaced blow off. Completed 4-3-02
|  |  |  | 4 | Distribution Feeder Main | [10 empty] | Steel |  | Kerman | Installed 2" steel cap on 2" PCF side assembly for uprate feeder main.
70 | 91-30186-1 | [10 empty] | 1991-06-04 | 1991-06-17 |  |  |  |  | Kerman | Bar tested over Sap. and Soap tested H.P.R. Sati "o" reading found S/GNS that H.P.R. set had worked on.; Bar tested over ser & main J.W. test readiing all "0%" soap test on H.P.R. set showed evidence of being worked on recently.
70 |  |  |  | 4 | Transmission | [6 empty] | 1976-10-01 |  |  |  | Steel/Wrought Iron |  | Kerman | Installed 2-4" PCF 441' + 451' N/N PL belmont removed pot drip replaced 5' 4" pipe.
70 | 81-30387-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1981-08-18 | 1981-08-18 | Other |  | Steel/Wrought Iron |  | Fresno | 8/18/81 Found leak on DS service repaired.
70 | 91-30333-1 |  |  | 1 | Service |  | Riser |  |  | Other |  | 1991-08-09 | 1991-08-09 | Replace Pipe |  | TR 418 |  | Kerman | Replace 11/4 PL Riser; Date 8-9-91 Found leak on 11/4 riser. Made perm. repair by replacing riser.
| 10-50026-1 |  |  | 0.5 | Branch Service |  | Body of Pipe |  |  |  |  | 2010-04-08 | 2010-04-08 | Replace Partial Service |  | PE2406/2708 (Yellow) |  | Kerman | (2) 1/2" PL coupling and a 2' piece of line; Fixed 1/2" dig-in, 2 couplings and 2' of pipe.; Looks like digging for his fence. Crew pilled up 4 hours later.
| 08-30036-1 |  |  | 0.75 | Branch Service |  | Valves |  |  | Other | LOOSE VALVE | 2008-06-16 | 2008-06-16 | Tighten Cap or Bolt |  | PE2406 (Yellow or Orange) |  | Kerman | At Riser; Leak found on serv. valve @ riser. Backed off valve. Redoped and tightened
| 05-50163-1 |  |  | 0.5 | Branch Service |  | Body of Pipe |  |  |  |  | 2005-10-19 | 2005-10-19 | Replace Partial Service |  | TR 418 |  | Kerman | 39' W/W R Del Norte/ 251' s/s R middleton; Contractor was excavating with a shovel to instal cable T.V. when he hit and damaged a 1/2" plastic service. Serive man pinch down and cap... Permanent repair was made by replacing 1' of 1/2" plastic. One customer affected in shutdown. U.S.A. was not call; Contractor hit a 1/2" plastic service with a shovel while excavating to install cable T.V. conduit. Service was cap by servicemant. USA was not call. Repaire wire made by replacing 1' of 1/2" plastic with two permanet couplings.
| 10-50033-1 |  |  | 0.5 | Branch Service |  | Body of Pipe |  |  |  |  | 2010-04-17 | 2010-04-17 | Replace Partial Service |  | Aldyl A (Tan or Gray) |  | Kerman | Replaced 1' of 1/2" PL Pipe and (2) 1/2" electro-fusion couplings; Gas was hit by a shovel while to install a fence post.; Hand digging for fence post, hit 1/2 gas svc.
70 |  |  |  | 4 | Transmission | [6 empty] | 1976-10-04 |  |  |  | Steel/Wrought Iron |  | Kerman | Installed 2-4" PCF at 1552' + 1558' N/N PL whites bridge. Removed pot drip and replaced 4' of 4" pipe.
| 08-50057-1 |  |  | 0.5 | Branch Service |  | Body of Pipe |  |  |  |  | 2008-06-02 | 2008-06-02 | Replace Partial Service |  | PE2406 (Yellow or Orange) |  | Kerman | 18" repaired; Telephone Co. hit into 1/2" gas svc. Marks present.; Telephone Co. Hit 1/2" Branch gas serv. While digging for Tele.
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-01-10 |  |  |  | Steel/Wrought Iron |  | Kerman
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-01-10 |  |  |  | Steel/Wrought Iron |  | Kerman
| 09-70106- |  |  | 0.5 | Branch Service |  | Mechanical Joint |  |  | Equipment Malfunction |  | 2009-05-05 | 2009-05-05 | Replace Partial Service |  | PE2406 (Yellow or Orange) |  | Kerman | Leak found on coupling by electric crew, leak called in and repaired by replacing coupling
| 10-50041-1 |  |  | 0.5 | Branch Service |  | Body of Pipe |  |  |  |  | 2010-05-04 | 2010-05-04 | Replace Partial Service |  | PE2406 (Yellow or Orange) |  | Kerman | 2-1/2" Electro-Fusion couplings; Contractor hit 1/2" Plastic SVC.; Contractor hit 1/2" plastic with bobcat back hoe. Contractor claims kids moved his marks and thats why they hit 1/2" plastic
70 | 87-30024-1 |  |  | 0.25 | Transmission |  | Regulator |  |  | Material Failure |  | 1987-02-24 | 1987-03-03 | Other |  | Steel/Wrought Iron |  | Fresno | Diph. Leaking rebuilt R.P.; N/O Shields Ave.
70 | 87-30018-1 |  |  | 0.25 | Transmission |  | Drip |  |  | Construction Defect |  | 1987-02-24 | 1987-03-03 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Fresno | Tighten line gauge nut on 3/4" H.P.R. Pit full of gray white dirt; .05% in reg. pit N/O Shields Ave
70 | 72-00029-1 | 118 |  | 12 | Transmission |  | Fitting |  |  | Material Failure |  | 1972-03-08 | 1973-05-30 | Other |  | Steel/Wrought Iron |  | Fresno | Installed 1" valve tee and new 3/4" fire valve and casing. Removed old 3/4" valve and welded steel plug in coupling.
70 |  | 118 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | Fresno | Installed 1/2" H.P. Plastic Gas Serivce. Note WO 3-4207-A
|  | 118 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | Fresno
70 | 82-30024-1 |  |  | 0.5 | Other |  | Fitting |  |  | Other |  | 1982-02-04 | 1982-02-04 | Other |  | Steel/Wrought Iron |  | Fresno | Found leak on Gyrolok fitting on control line of north run. Tightened same. ;
70 | 82-30023-1 |  |  | 0.5 | Distribution Main |  | Regulator |  |  | Other |  | 1982-02-02 | 1982-02-02 | Other |  | Steel/Wrought Iron |  |  | Open pit soap out No Leak (Temp). Found 25.0% in east reg. pit. Reported same to MYC need T.M. leak was located on steel taking and corrected new no. 1 leak ... issued
70 | 80-30378-1 |  |  | 12 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1980-09-10 | 1980-09-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Fresno | Numerous fittings leaking, removed H.P.R.-25 relief and security valve H.P.R.-20 installed H.P.R.-20 and fisher H-202 relief
70 | 80-30326-1 |  |  | 0.75 | Other |  | Valves |  |  | Other |  | 1980-08-13 | 1980-08-13 | Other |  | Steel/Wrought Iron |  | Fresno | By-pass valve grease stem leaking. Also, leaking up to relief set point. Greased valve, checked reg. for L.U. left OK
70 | 79-30269-1 | [10 empty] | 1979-08-17 | [5 empty] | Fresno | Called in #1 8/13/80
| 88-30103-1 |  |  | 0.75 | Transmission |  | Regulator |  |  | Other |  | 1988-08-18 | 1988-08-18 | Other |  | Steel/Wrought Iron |  | Fresno | Changed H.P.R. per leak at diaphram
70 | 80-30377-1 |  |  | 12 | Transmission |  | Other |  |  | Other |  | 1980-09-10 | 1980-09-15 | Other |  | Steel/Wrought Iron |  | Fresno | Threads on Relief valve leaking tightened c/ok
|  |  |  | 12 | [11 empty] | Steel |  | Fresno | Installed 1" pin off tee on 12" T.P. Main installed 29' of 3/4" STL and one external shut off valve.; 12" T.P. Main has off set in it for 2" drip. Main is 6' at reg pit and 34' dept. were new pin off tee was installed
25 |  |  |  | 8 | Transmission | [6 empty] | 1987-07-28 | 1987-07-29 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Fresno | Co. Trencher damaged 8" TP main 118 E. Replaced 26' of pretested pipe approx .140 measured at deepest mark. No leak occurred
70 | 79-30293-1 |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1979-09-11 | 1979-11-07 | Other |  | Steel/Wrought Iron |  | Fresno
|  |  |  | 0.75 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1981-09-11 |  | Other |  | Steel/Wrought Iron |  | Fresno | ... a Hot#2 as it is in yard. Needs M&C to repair Reg. Station @15-18
70 | 81-30342-1 |  |  | 2 | Distribution Main | [6 empty] | 1979-08-17 | 1981-09-04 |  |  | Steel/Wrought Iron |  | Fresno | On 5-4-81 Repair leak in threads on numerous fittings. Per log sheet 9 9522-44. 9-4-81 Soap out checked out Ok.
|  |  |  | 12 | [11 empty] | Steel |  | Fresno | Relocated gas... Inst. E.T.S. off of ...T.P. Main; c/o 2' Ueht pipe approx. 4' e/o T.P. main. Welded 90 degree 2' elbow extended approx 16' to the north. Inst. E.T.S. and wires off of casing (white) and T.P. Main (black).
|  | 111 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | Fresno | Installed E.T.S. big fink
|  | 111 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | Fresno | Installed E.T.S big fink
70 | 81-50106-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1981-11-08 | 1981-11-08 | Replace Pipe and/or Service | ; | Steel/Wrought Iron |  | Fresno | See attached sketch Isolated 5.85 miles of pipe by crossing valve 15.18 & 21.65 to stop gas flow 11-8-81-Temp. Perm. Repairs made by installing 34' 11" of 12.750" pipe 11-9-81
|  | 111 | 1687 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | Fresno | South west contractors pot holed T.P> line #111 for future tie-in.
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | Fresno | South West Contractors pot-holed this 4" T.P. line for future tie-in
|  |  |  | 12 | [11 empty] | Steel |  | Fresno | Installed 73' 3/4" T.P. and 10' 2" stl. H.P. two reg set one 3/4" shut off valve 2224 and abandoned existing reg sets and removed abandon 87' 2" stl
70 | 91-50120-1 |  |  | 2 | Other | M | Body of Pipe |  |  | Digin |  | 1991-08-26 | 1991-08-26 | Replace Pipe |  | TR 418 |  | Fresno | Repair 2" plastic main 1 fusion, 1 electro-fusion; Contractor drove stalk into 2' Main. Use one fusion and 1 electro-fusion coupling J West made.
| 05-50181-1 |  |  | 0.5 | Branch Service |  | Body of Pipe |  |  |  |  | 2005-11-10 | 2005-11-10 | Replace Partial Service |  | TR 418 |  | Fresno | Replaced/ repaired 1' of 1/2 plastic pipe; Service man installed 1/2 dead end before I showed up. I repaired w/2 perm. couplings and 1' of plastic pipe.; Repaired 1/2 serv. on 5372 W. University. Service man deadended. dig-in...to me. Repaired w2 couplins and 12" of 1/2 plastic. No USA
| 07-30008-1 |  |  | 0.5 | Branch Service |  | Fitting |  |  | Equipment Malfunction |  | 2007-01-25 | 2008-07-15 | Replace Partial Service |  | PE2406 (Yellow or Orange) |  | Fresno | Bad svc. tee, 2'' fusion tee w/ 1/2'' perma. sert. coupling, coupling was leaking. We pluged down svc. tee and dead end. New electro-fusion tee installed
| 10-70170-1 |  |  | 0.5 | Branch Service |  | Plastic Tee Cap |  |  | Other | LOOSE CAP | 2010-11-12 | 2010-11-12 | Replace Plastic Tee Cap - Plastic |  | PE2406 (Yellow or Orange) |  | Fresno | Loose service tee cap, so crew replaced the cap with a new one.
|  |  |  | 2 | Single Service | Branch Service, 1/2" Serv. Stub | [9 empty] | PE2406 (Yellow or Orange) |  | Fresno
|  |  |  | 2 | Single Service | Branch Service, 1/2" Serv. Stub | [9 empty] | PE2406 (Yellow or Orange) |  | Fresno | c/o 1/2" TR-418 Gas stub @ main
| 08-70104-1 |  |  | 0.5 | Branch Service |  | Plastic Tee Cap |  |  | Plastic Crack Failure |  | 2008-12-02 | 2008-12-02 | Replace Plastic Tee Cap - Plastic |  | PE2406/2708 (Yellow) |  | Fresno | Replaced PL tee cap to 2231 N. Milburn
| 09-70138-1 |  |  | 0.5 | Branch Service |  | Plastic Tee Cap |  |  | Plastic Crack Failure |  | 2009-08-10 | 2009-08-12 | Replace Plastic Tee Cap - Plastic |  | PE2406 (Yellow or Orange) |  | Fresno | Crew found svc. cap cracked and replaced it
| 08-70058-1 |  |  | 0.5 | Branch Service |  | Body of Pipe |  |  | Damage by 3rd Party |  | 2008-06-03 | 2008-06-05 | Replace Partial Service | 1 REPAIR COUPLING | PE2406/2708 (Yellow) |  | Fresno | A ground rod in telephone box driven through 1/2" gas svc. line
| 09-70028-1 |  |  | 0.5 | Branch Service |  | Plastic Tee Cap |  |  | Plastic Crack Failure |  | 2009-01-24 | 2009-01-24 | Replace Plastic Tee Cap - Plastic |  | PE2406 (Yellow or Orange) |  | Fresno | Svc. tee cap was cracked, cracked cap was replaced.
70 | 77-50018-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Construction Defect |  | 1977-02-24 | 1977-02-24 | Other |  | Steel/Wrought Iron |  | Fresno | Fresno county const. crew was regrading shoulder of road when motor grader truck struck valve casing forceing it into curb valve and breaking threads of 3/4" pipe at curb valve. Repairs were made by closing valve A. Trans.; Installed new valve casing & cover installed oil dirt around valve casing and along shoulder off road so that the county will not have to regrade this area. D. Britton.
|  |  |  | 8 | Transmission | [7 empty] | 1973-05-25 |  |  | Steel/Wrought Iron
70 | 72-00147-1 | 111 |  | 8 | Transmission |  | Valves |  |  | Material Failure |  | 1972-12-11 | 1973-11-27 | Other |  | Steel/Wrought Iron |  | Fresno | .3% high pressure Reg.. Box. Tested clear around pit. 5 services on shutdown. Leak was in threads on bypass valve repaired by replacing 6" of pipe and threads.
70 | 87-30140-1 | 111 |  | 8 | Transmission |  | Girth Weld |  |  | Corrosion |  | 1987-08-10 | 1987-08-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Fresno | Found corrosion leak on T/P #111E. Inst. leak clamp for temp repair. Inst. (2) 8" PCF fitting on T/P line 111E approx. 600' & 579' W/O Blythe Ave. and replaced approx. 17' of 8"Stl. Main.
70 | 88-30102-1 |  |  | 8 | Transmission |  | Girth Weld |  |  | Corrosion |  | 1988-08-18 | 1988-08-22 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Fresno | Excavated over suspected leak and aired out for temp repair. 8-18-88. Install clamp around leak for temp repair. 8/18/88; Found a pinhole leak on the 8" T.P. main. Temporary repair were made by installing a patch with a clamp on leak. 3/19/88; Repaired leak by lowering line pressure to 100PSI. Then welding an 8" welded sleeve 8/-22-88
|  |  |  | 8 | [11 empty] | Steel |  | Fresno | Abandoned exisiting 3/4" tap. Installed new 3/4" tap and #2024 valve as per WO 40436-A. Used existing #2024 valve at abandoned tap. Screwed 3/4" Stl. plug in valve and wrapped T.G.W. 1-24-84
25 |  |  |  | 8 | Transmission | [6 empty] | 1975-10-15 |  |  |  | Steel/Wrought Iron |  |  | Installed E.T.S. 10-15-75. 2" also inspected wrapp is good condition 30 in pipe.
70 | 74-70082-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-11-14 | 1974-11-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Fresno | Replaced 52" 3/4" steel seamless pipe. Made frame... pipe all tests...
70 | 79-50314-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-11-27 | 1979-11-27 | Other |  | Steel/Wrought Iron |  | Fresno
70 | 81-70062-1 |  |  | 0.5 | Other |  | Physical/Mechanical Joint |  |  | Other |  | 1981-12-23 | 1981-12-23 | Other |  | Steel/Wrought Iron |  | Fresno | Cap on Mueller no-blow valves loose; Re-doped fittings and valves repaired all leaks in pit. Re-doped caps on no blow valves.
|  |  |  | 8 | Transmission | [7 empty] | 1975-09-16 |  |  | Steel/Wrought Iron |  | Fresno | Cut out old reg pit... Reg pit installed fire valve 10' s/npl of Nialson, 1158' E/E PL of Brawley WO 3-4046-B
|  | 111 |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | The contractor, John Gorsky Construction, trenched across this 8" T.P. line to install a 2" waterline.
|  | 111 |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Stand by; The contractor, John Gorsky Construction, trenched (2) crossings on this T.P. line, to install 8" water lines with a backhoe.
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | Fresno | Pothole was requested for city of Fresno for future irrigation canal; c/o 3/4 T.P. main remove reg. pits and relocate and installed 20' 3/4" SMLS grade "8" pipe and one 3/4" fire valve.
| 09-30681-1 |  |  | 1 | Gathering |  | RISER |  |  | OTHER | LOOSE FITTING | 2009-06-25 |  |  |  | Steel/Wrought Iron |  | Fresno | Tanked meters replaced leaking parts & skinner repair clamp.
25 |  |  |  | 2 | Distribution Main |  | OTHER |  |  | OTHER |  | 1973-10-31 |  |  |  | Steel/Wrought Iron
25 |  |  |  | 1.14 | Distribution Main |  | OTHER |  |  | OTHER |  | 1973-11-14 |  |  |  | Steel/Wrought Iron
25 |  |  |  | 2 | Distribution Main |  | OTHER |  |  | OTHER |  | 08/00/1973 |  |  |  | Steel/Wrought Iron
25 |  |  |  | 2 | Distribution Main |  | OTHER |  |  | OTHER |  | 1974-04-15 |  |  |  | Steel/Wrought Iron
70 | 94-50035-1 |  |  | 2 | Distribution Main |  | BODY OF PIPE |  |  | DIGIN |  | 1990-02-14 | 1994-02-14 | REPLACE PIPE |  | TR 418 |  | Fresno | Repaired hole in 2" plastic main.
2 |  |  | 13.39 | 0.12 | Distribution Main |  | OTHER |  |  | OTHER |  | 1973-05-01 |  |  |  | Steel/Wrought Iron
25 |  |  |  | 1.14 | Distribution Main |  | OTHER |  |  | OTHER |  | 1973-11-01 |  |  |  | Other Plastic
25 |  |  |  | 14 | Distribution Main |  | OTHER |  |  | OTHER |  | 1973-07-03 |  |  |  | Other Plastic
25 |  |  | 13.39 | 2 | Distribution Main |  | OTHER |  |  | OTHER |  | 1973-11-30 |  |  |  | Steel/Wrought Iron
70 | 76-50076-1 |  |  | 0.75 | Other |  | TAP CONNECTION |  |  | CORROSION |  | 1976-06-14 | 1976-06-14 | OTHER |  | Steel/Wrought Iron
25 |  |  |  | 2 | Distribution Main |  | OTHER |  |  | OTHER |  | 1973-07-25 |  | PATCH WELDED |  | Steel/Wrought Iron
| 07-50200-1 |  |  | 00..50 | Branch Service |  | BODY OF PIPE |  |  |  |  | 2007-12-25 |  | REPLACE PARTIAL SERVICE |  | TR 418 |  | Fresno | GSR. plugged off. Repaired W/2 couplings and 1'- 1/2" Plastic.; Elec. crew hit into 1/2" pl gas svc. while digging to repair fault in elec svc. No USA due to emergency dig and holiday
| 09-31093-1 |  |  | 1 | Branch Service |  | OTHER |  | LOOKING AT 1' X 1' X 1/2 BRANCH SERVICE TEE | PLASTIC CRACK FAILURE |  | 2009-08-19 |  |  |  | Aldyl A (Tan or Gray) |  | Fresno | Dug 36" deep and 5'x41/2 bell hole. Had to cut concrete at side walk leading to the backyard. Tamped bell hole and used asphalt from the sack to finish the job
70 | 78-50060-1 |  |  | 2 | Distribution Main |  | BODY OF PIPE |  |  | DAMAGE BY OUTSIDE FORCES |  | 1978-07-11 | 1978-07-11 | REPLACE PIPE AND/OR SERVICE |  | Steel/Wrought Iron
70 | 86-30320-1 |  |  | 4 | Distribution Main |  | Valves |  |  | Other |  | 1984-09-14 | 1986-09-12 | Other |  | Steel/Wrought Iron |  | Fresno | Reg pit N/E corner of N. of unit 0 W. Dakato 10% in reg. pit. 86. Greased inlet & outlet valves in pit. (Bonnets were leaking)
|  |  |  | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Fresno
70 | 74-70079-1 |  |  | 1.25 | Other |  | Drip |  |  | Damage by outside Forces |  | 1974-10-07 | 1974-10-07 | Other |  | Steel/Wrought Iron |  |  | Installed 1/4" M2 P.C.F. 22' W.E. P/L moroa. 141' N.N. P/L Shaw. Extended drip riser 13 1/2' Installed all may...Installed drip box. 8' W.E. P/L Moroa, 141' N.N. P/L Shaw, 1 1/4" steel pipe and a standard 3/4" steel riser. Depth 33". ; ;
25 |  |  |  | 3 | Distribution Main | [6 empty] | 1973-04-17 |  |  |  | Steel/Wrought Iron |  | Fresno | Branch service installed from 923E Garland. Killed 1/2" cap gas serivce at 913E Garland. Installed 1/2" plastic gas serivce. 4-17-73
| 08-50097-1 |  |  | 0.5 | Branch Service |  | Body of Pipe |  |  |  |  | 2008-08-08 | 2008-08-08 | Replace Partial Service |  | Aldyl A (Tan or Gray) |  | Fresno | Replace 1' of 1/2" plastic; Customer hit and damaged 1/2" Aldyl A gas serv. with post hole digger.; Damage 1/2" plastic service with post hole digger to install a fence post. USA was not call. Permanent repair WC/F made by replaceing 1' of 1/2" plastic. Two customers affected in shut down.
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1973-06-22 |  |  |  | Steel/Wrought Iron |  | Fresno
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1973-06-25 |  | Patch Welded |  | Steel/Wrought Iron |  | Fresno
|  |  |  | 0.5 | Service | [6 empty] | 2003-01-23 |  |  |  | Copper |  | Fresno | Called out for a plugged copper service- Tapped pipe to unplug A.S.A.P.
5 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1973-10-26 |  |  |  | Steel/Wrought Iron |  |  | Fresno
70 | 79-70008-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-02-10 | 1979-02-10 | Other |  | Steel/Wrought Iron |  | Fresno | Unknown third party hit and damaged 5 meter manifold. Repaired by turning off gas and welding two new nipples on the 5 meter mainifold and replumbing 2 house lines.
70 | 82-70041-1 |  |  | 2 | Other |  | Valves |  |  | Other |  | 1982-12-08 | 1982-12-08 | Other | GREASED VALVE | Steel/Wrought Iron |  | Fresno | Found gas leak, at valve to blow-off riser. Leak was due to grease drying out in the valve. Made repair by greasing valve and stopping gas leak.
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | Fresno | Exposed 6" of belt main to take wall thickness readings
70 | 86-30070-1 |  |  |  | Distribution Feeder Main | [6 empty] | 1986-03-04 |  |  |  | Steel/Wrought Iron |  | Fresno | 12' N/O N/PL of W. Harvard; 18' W/O E/PL of N. Arthur
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Fresno | Tested 300LBS; 5-8-03 c/o service at T.P. main, c/o 3/4" riser at pole, soap tested no leaks.
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Fresno | Exposed 6" of belt main to take wall thickness readings.
70 | 81-30376-1 |  |  | 6 | Other |  | Fitting |  |  | Other |  | 1981-09-09 | 1981-10-26 | Other |  | Steel/Wrought Iron |  | Fresno | Tighten 4" fitter lid and 2 1/4 needle valvel; Found reading in W. Reg. pit issued new leak report 2-2-82
70 | 99-30101-1 |  |  | 4 | [7 empty] | 1999-09-10 |  |  |  | Steel |  | FRESNO | OPENED TWO BELL HOLES OVER H.P. MAIN. READS DISSAPATED. SUGGEST 90 DAY RECHECK. (IN FRONT OF 711 HARVARD)
|  |  |  | 1 | Other |  | Other |  |  | Other |  | 1976-03-19 |  |  |  | Steel
70 | 71-2001- |  |  | 2 |  |  | Fitting | Other |  | Material Failure |  |  | 1971-03-04 | Other |  |  |  | FRESNO | THREADS WERE LEAKING WHERE THE PIPE WAS SCREWED TOGETHER WITH A COUPLING, REPAIRED BY WELDING COUPLING TO THE MAIN AND OVER THE THREADS.
25 |  |  |  | 3 |  |  | Other | Other |  | Other |  | 1974-04-04 |  |  |  | Steel |  | FRESNO
70 | 91-30310-1 |  |  | 4 | Service |  | Body of Pipe |  |  | Corrosion |  | 1991-09-09 | 1991-09-13 | Replace Pipe |  | Copper |  | FRESNO | PERMANENT REPAIRS WERE MADE BY REPLACING COPPER SERVICE WITH 1/2" PL. COPPER SERVICE LEAKING; PERMANENTLY REPAIRED BY CUTTING OUT 2' COPPER AND REPLACING WITH 2' PL. PIPE. WELDED 3/4" TRANS. FITTING ON EXISTING SERVICE TEE. NEED TO REPLACE SERVICE
25 |  |  |  | 3 | [8 empty] | 1972-12-26
| 09-50055-1 |  |  | 0.5 | Branch Service |  | Body of Pipe |  |  |  |  | 2009-07-01 | 2009-07-01 | Replace Partial Service |  | PE2406/2708 (Yellow) |  | FRESNO | PERMANENT REPAIR MADE BY REPLACING 14' IF 1/2" PL, & (2) 1/2" PERMASERT COUPLINGS; CONTRACTOR'S EXCAVATION CAVED IN RIPPING OUT 14' OF NEWLY REPLACED 1/2" PL. (3/4)" SVC; CONTRACTOR DUG INTO THIS SAME SVC. THE DAY BEFORE. REPLACED 14' OF 1/2" PL., FROM MAIN TO CASING. CONTRACTOR, WHILE EXCAVATING TO INSTALL STORM DRAIN, CAUSED DITCH TO CAVE IN ON NEWLY REPLACED 1/2" PL. SVC., RIPPING IT APART. CONTRACTOR DUG INTO THIS SAME SVC. THE DAY BEFORE.
70 | 81-70074-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Corrosion |  | 1981-12-16 | 1982-03-02 | Other |  | Steel |  | FRESNO | FOUND CORROSION LEAK ON 1 1/4" BLOW OFF VALVE MADE TEMP. REPAIR BY INSTALLING 1 1/4" HANDI-BAND CLAMP CASING BODY SHOULD BE RAISED BECAUSE IRON LID RESTS ON TOP OF VALVE; REMOVED 1 1/4" STL. BLOW-RISER & INST'ED 1 1/4" PCF FITTING TO SHUT DOWN GAS FLOW CUT 12" SECTION & WELD SHUT.
70 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-01-23 | 1974-01-23 |  |  | Steel |  | FRESNO
25 |  |  |  | 3 | Other |  | Other |  |  | Other |  | 1974-01-25 |  |  |  | Steel |  | FRESNO
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-01-25 |  |  |  | Steel |  | FRESNO | REPLACE GAS SERVICE
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-01-29 |  |  |  | Steel |  | FRESNO | REPLACE GAS SERVICE
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-01-30 |  |  |  | Steel |  | FRESNO
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-02-11 |  |  |  | Steel |  | FRESNO
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-02-06 |  |  |  | Steel |  | FRESNO
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-02-11 | [5 empty] | FRESNO
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-02-12 |  |  |  | Steel |  | FRESNO
25 |  |  |  | 3 | Distribution Main |  | Other | Other |  | Other |  | 1974-02-13 |  |  |  | Steel |  | FRESNO
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-02-14 |  |  |  | Steel |  | FRESNO
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-02-15 |  |  |  | Steel | S;
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-02-25 |  |  |  | Steel |  | FRESNO
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-02-28 |  |  |  | Steel |  | FRESNO
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-03-01 |  |  |  | Steel |  | FRESNO
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-03-05 |  |  |  | Steel |  | FRESNO
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-01-31 |  |  |  | Steel |  | FRESNO
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-02-01 |  |  |  | Steel |  | FRESNO
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-02-21 |  |  |  | Steel |  | FRESNO
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-02-22 | [5 empty] | FRESNO
70 | 79-50139-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-06-25 | 1979-06-25 | Other |  | Steel |  | FRESNO | MAIN MARKED - STUB NOT MARKED DAMAGE 4" GAS MAIN CONTRACTOR STRUCK AND DAMAGED 3' STUB OFF OF 4" MAIN; INSTALLED TWO 4" M/2 FITTINGS AND 15 OF 4" PIPE LOCATED 12' N/O S.P.L. OF PERALTA AND 29' N/O S.P.L. OF PERALTA. 3' STUB 14' N/O S.P.L. OF PERALTA
|  |  |  | 2 | [7 empty] | 1996-01-11 | [5 empty] | FRESNO
| 08-30092- |  |  | 10.5 | Branch Service |  | Plastic Tee Cap |  |  | Plastic Crack Failure |  | 2008-09-16 |  |  |  | PE2406 (Yellow or Orange) |  | FRESNO
25 |  |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Material Failure |  | 1973-08-03 |  | Patch Welded |  | Steel |  | FRESNO
77 |  |  |  | 12 | Distribution Feeder Main | [6 empty] | 1977-06-02
| 91-30171-1 |  |  | 2 | Service |  | Body of Pipe |  |  | Corrosion |  | 1991-04-22 | 1991-05-15 | Replace Pipe |  | Copper |  | FRESNO | INSERT SERVICE; FOUND CORROSION LEAK ON 1/2" COPPER GAS SERVICE. MADE PERMANENT REPAIR BY INSERTING 1/2" TR-418 INTO 1/4" CASING. INSTALLED NON-CORRODIDLIE RISER
| 88-30145-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Construction Defect |  | 1988-08-16 | 1988-08-16 | Replace Pipe |  | TR 418 |  | FRESNO | PINCHED SERVICE OFF NEAR TEE & REPLACED ENTIRE 1/2" PLASTIC SERVICE TO 716 & 718 E. FLORADORA; REPLACED 1/2" PLASTIC GAS SERVICE DUE TO LEAK IN BODY OF PIPE.
70 | 78-30104-1 | [10 empty] | 1978-05-03 | [5 empty] | FRESNO | LOOKED LIKE REPAIR JOB OVER MAIN SQUARE PATCH 2% GAS
70 | 78-30089-1 |  |  |  | Transmission | [6 empty] | 1978-05-03 | [5 empty] | FRESNO
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1973-05-03 |  | Patch Welded |  | Steel |  | FRESNO | KILLED 3/4" GAS SERVICE
25 | 84-70014-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Construction Defect |  | 1984-02-29 | 1984-02-29 | Replace Pipe and/or Service |  | Steel |  | FRESNO | REPAIRED (2) LEAK ON BYPASS REMOVED PIT REWELDED SOCKET FITTINGS AND RESTORED SERVICE
70 | 81-30426-1 |  |  | 10 | [7 empty] | 1981-09-09 |  |  |  | Steel |  | FRESNO
| 08-70002-1 |  |  | 0.75 | Gathering |  | Drip |  |  | Construction Defect |  | 2008-01-07 | 2008-01-10 | Other | TIGHTEN VALVE | Steel/Wrought Iron |  | FRESNO | RETIGHTEN VALVE ON DRIP RISER; FOUND DRIP RISER WITH A FIZZER BELOW THE VALVE. LOOSEN UP VALVE REDOPE AND RETIGHTEN. DRIP SHOULD BE REMOVE ASAP SO CITY CAN FINISH POURING CURB. RISER WAS PINCH DOWN AT A PREVIOUS DATE TO CHANGE OUT SERVICE VALVE; LEAK FOUND ON 4" PLASTIC MAIN UNDER WHEEL CHAIR RAMP. REPAIRED 30', PULLED OUT OLD MAIN WHILE PULLING IN NEW MAIN TO PREVENT BREAKING OUT CONCRETE.
70 | 85-50110-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Digin |  | 1985-05-01 | 1985-05-01 |  |  | Steel |  | FRESNO | REPAIR LEAK ON 3/4" STL SERV. PERM REPAIRS - SHUT OFF @ MAIN REPLACED 25' OF 3/4 PIPE
70 | 80-30171-1 | [10 empty] | 1980-06-16 | [5 empty] | FRESNO
|  |  |  | 16 | Transmission |  | Other |  | GOUGE | Digin |  | 2002-01-01 | 2002-01-08 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | FRESNO | GOUGE NO LEAK; GC WELDED SLEEVE OVER GOUGE; CAUSED BY CONTRACTOR; HOPTOE FROM FLOYD JOHNSON STRUCK AND GOUGED 16" BOLT MAIN. GC IS TO WELD SLEEVE OVER GOUGE
77 |  |  |  | 12 | Distribution Feeder Main | [6 empty] | 1977-06-01 |  |  |  | Steel |  | FRESNO | INSTALLED RECTIFIER & ETS WITH DEEP WELL ANODE
25 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1973-04-12 |  |  |  | Steel |  | FRESNO
70 | 72-00056-1 |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1972-03-15 | 1974-12-31 | Other |  | Steel |  | FRESNO | 85.% 6' S/O NE PL OF W.FRANKLIN TESTED WITH FLAME IONIZATION ON SURFACE AS SHOWIN IN ORANGE. GOT .3% AT VALVE VAULT. PLUG ON 1 1/2" BLOW DOWN VALVE LEAKING. GREASED VALVE & DOPED PLUG. MADE FLAME IOINIZATION TESTS IN ORANGE ALL TESTS CLEAR.
70 | 87-30153-1 |  |  | 8 | Transmission |  | Fitting |  |  | Construction Defect |  | 1987-09-15 | 1987-09-17 | Tighten Cap or Bolt |  | Steel |  | FRESNO | 9-16-87 - DRILLED HOLE OVER DIS. MAIN READING 10% TO 20% USED LAMB AIR MOVER TO AREATE. REPLACED CAP ON PLASTIC SERVICE TEE TO STOP LEAK, LEAK ON DISTRIBUTION MAIN E/O TP MAIN; 10% OVER T.P. MAIN, APX. 15' W/F PL. OF FRUIT. 60' S/S PLS. OF NAPA
| 00-30042- |  |  | 0.75 | Gathering |  | Valves |  |  | External Corrosion |  | 2000-03-10 | 2000-03-14 | Other | SEE REPAIR REMARK; REMOVE BLOW-OFF VAVLE FOR REPAIR AND CAP LINE TO STOP LEAK | Steel/Wrought Iron |  | FRESNO | 7' NOT MAIN IN SIDEWALK STRONG ODOR AT TIMES; REMOVE BLOW-OFF VALVE FOR REPAIR AND CAP LINE TO STOP LEAK; FOUND 3/4" BLOWOFF VALVELEAKING. REMOVE VLAVE AND CAP FOR REPAIR. CALL JESS VARGAS ON DRIP TO BE REMOVE. HE WOULD DRAW UP JOB.
|  |  |  | 8 | Transmission | [6 empty] | 2003-09-11 |  |  |  | Steel/Wrought Iron |  | FRESNO | INSTALLED NEW H-12 7 PIN OFF TEE & 5' OF 2" PL STUB FOR FUTURE. SOAP TEST OK
70 | 85-70002-1 |  |  |  | Distribution Main |  | Regulator |  |  | Material Failure | BAD SEAT | 1985-01-15 | 1985-01-15 | Replace Pipe and/or Service |  | Other |  | FRESNO | REMOVE SET, KILL SERVICE; SHUT OFF REG SET. SET TO BE REM - SER TO BE CUT OFF
70 | 78-30060-1 |  |  | 0.75 | Distribution Feeder Main |  | Regulator |  |  | Material Failure |  | 1978-05-23 | 1978-06-06 | Patch Welded |  | Steel |  | FRESNO | FOUND RELIEF BLOWING. INSTALLED NEW REGULATOR AND ALSO REPLACED REGULATOR BOX. OLD REGULATOR BOX WAS DAMAGED WITH THE TRAFFIC DRIVING OVER IT THROUGH THE YEARS. NEW BOX INSTALLED WITH FRAFFIC COVER; FOUND RELIEF BLOWING, MADE PERMANENT REPAIRS.
|  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1977-02-24 |  |  |  | Steel |  | FRESNO
70 | 90-30018-1 |  |  | 30 | Transmission |  | Girth Weld |  |  | Other | STRESS CORROSION CRACKING | 1989-01-09 | 1990-05-16 | Replace Pipe |  | Steel/Wrought Iron |  | FRESNO | REPLACED 9FT OF 30" O PIPE THAT CONTAINED BAD WELD (WO 43046C)
|  | 111 | [15 empty] | FRESNO | ABANDONED 1 1/4 MUELLER TEE ON (LINE III) TP. PRESSURE
[18 empty] | FRESNO | ABANDONED 3/4 MUELLER TEE INSTALLED 1" TP PIN OFF TEE LOWERED PIT 36" & 180' OF 2" PLASTIC GAS MAIN
[18 empty] | FRESNO | ABANDONED 1 1/4 SERVICE TO PIT REPLACED WITH 3/4" TP 1" TEE PIN OFF MOVED PIT 1" PLASTIC FROM PIT TO RISER
70 | 79-50236-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-10-16 | 1979-10-16 | Other |  | Steel |  | FRESNO | INSTALLING NEW CURB AND GUTTER DAMAGED LP. BLOW OFF RISER MOVED RISER SOUTH OF CURB LINE. RAISED B.O. BOX TO NEW SIDEWALK GRADE; REPLACED BROKEN 3/4" SCREWED NIPPLE AND 3/4" X 1" SCREWED REDUCER - INS CONCERETE V -F&C.
70 | 76-30002-1 |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1976-01-08 | 1976-02-20 | Bell Joint Clamp |  | Cast/Ductile Iron |  | FRESNO | REMOVE CONCRETE JOINT & INSTALLED (1) 16" LEAK CALMP 2' N/S PL OF TUOLUMNE & 25' W/EPL OF "N". AE CHECKED OVER MAIN CLEAR
70 | 76-30002-1 |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1976-01-08 | 1976-02-20 |  |  | Cast/Ductile Iron |  | FRESNO | 10% GAS, POSSIBLE MAIN TEE. RESOAPED 11-16", 9-10" & 10-8" EXIST. CONCRETE LEKPRUF JOINTS IF FOUND TO BE LEAKING
70 | 72-40080-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-09-11 | 1972-09-11 | Other |  | Steel |  | FRESNO | RELOCATED DRIP RISER USING 1 1/4" M/2 EXTENDED RISER TO ONE FOOT BACK TO NEW CURB. M/2 LOCATED 29' S/O N.P.L. OF DIVISADERO, 5' E/O E.P.L. OF BLACKSTONE.
25 |  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  | 1974-03-21 |  |  |  | Cast/Ductile Iron |  | FRESNO
| 06-50154-1 |  |  | 0.5 | Branch Service |  | Body of Pipe |  |  |  |  | 2006-10-09 | 2006-10-09 | Replace Partial Service |  | TR 418 |  | FRESNO | REPAIRED WITH 2 COUPLINGS & 18" PLASTIC; CONTRACTOR HIT SERVICE WITH POST HOLE DIGGERS DIGGING FOR POST. NO U.S.A.
|  |  |  | 1.25 | Other |  | Body of Pipe |  |  | Corrosion |  | 1975-11-20 | 1975-11-26 | Other |  | Steel |  | FRESNO | LOCATED LEAK IN B.O. RISER C/O AT MAIN AND ABANDONED RISER.
|  |  |  | 0.75 | Branch Service | [10 empty] | Steel/Wrought Iron |  | FRESNO | C/O 3/4" STL BRANCH SERVICE
| 10-50043-1 |  |  | 0.5 | Branch Service |  | Body of Pipe |  |  |  |  | 2010-05-07 | 2010-05-07 | Replace Partial Service |  | Aldyl A (Tan or Gray) |  | FRESNO | 2-1/2" ELECTROFUSION COUPLING; DIG IN WITH POST-HOLE DIGGER; CONTRACTOR HIT 1/2" PLASTIC WITH POST HOLE DIGGER
| 09-50045-1 |  |  | 0.5 | Branch Service |  | Body of Pipe |  |  |  |  | 2009-05-29 | 2009-05-29 | Replace Partial Service |  | Aldyl A (Tan or Gray) |  | FRESNO | SQUEEZED AND INSTALLED 2 1/2" COUPLINGS AND 1' OF 1/2" PLASTIC PIPE; CUST. DUG-INTO 1/2" PL. SVC. WITH POST HOLE DIGGER - NO USA WAS CALLED; CUSTOMER HIT 1/2" ALDYLE WITH POST HOLE DIGGER, NO U.S.A. CALLED
25 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1973-10-24 |  | Other |  |  |  | FRESNO
| 09-50041-1 |  |  | 0.5 | Branch Service |  | Body of Pipe |  |  |  |  | 2009-05-11 | 2009-05-11 | Replace Partial Service |  | PE2406 (Yellow or Orange) |  | FRESNO | PERMANENT REPAIR MADE BY REPLACING 1' OF 1/2" PL. PIPE WITH SAME (2) PERMASERT COUPLINGS; CONTRACTOR DUG INTO 1/2" PL BRANCHING SVC. WITH TRENCHER WHILE INSTALLING STREET LIGHTS. PERMANENT REPAIR MADE; CONTRACTOR DUG INTO & SEVERED 1/2"PL. BRANCHING SVC. WHILE TRENCHING FOR STREET LIGHTS. PERMANENT REPAIR MADE BY REPLACING 1' OF 1/2" PL. WITH SAME, + (2) 1/2" PERMASERT COUPLINGS.
25 |  |  |  | 3 | Distribution Feeder Main |  | Other |  |  | Other |  | 1973-05-30 |  | Patch Welded |  | Steel |  | FRESNO
25 |  |  |  | 2 | [8 empty] | 1972-12-20 |  |  | Steel |  | FRESNO
25 |  |  |  | 2 | [8 empty] | 1972-12-20 |  |  | Steel |  | FRESNO
25 | [12 empty] | 1972-12-28 |  |  | Steel |  | FRESNO
25 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1973-04-26 |  |  |  | Steel |  | FRESNO | KILLED 3/4" GAS SERVICE AT MAIN
25 |  |  |  | 12 | Distribution Main |  |  |  |  | Other |  | 1973-01-23 |  |  |  | Other Plastic |  | FRESNO | INSTALLED 1/2" PLASTIC GAS SERVICE
| 07-50005-1 |  |  | 1 | Branch Service |  | Body of Pipe |  |  |  |  | 2007-01-16 | 2007-01-16 | Replace Partial Service |  | Aldyl A (Tan or Gray) |  | FRESNO | REPAIRED (2) 1" COUPLINGS & 1' PL. PIPE; ELECTRIC CONTRACTOR AVOIDED WARNING TO HAND DIG/ EXP. USA, AND WHILE TRENCHING WITH WALK BEHIND TRENCHER HIT BRANCH SERV. FOR APT.
20 | 90-30051-1 |  |  | 4 | Distribution Main |  | Fitting |  |  | Material Failure |  | 1990-03-28 | 1990-03-28 | Tighten Cap or Bolt |  | Steel |  | FRESNO | THE CAP WAS REMOVED AND REDOPE AND RETIGHTEN: SOAP TEST (NO LEAKS); CITY OF FRESNO REMOVED ASPHALT FROM STREET AND DISCOVERED GREEN SOIL, THRU INVESTIGATION OF BAR TESTING & JW GAS INDICATOR THE LEAK WAS FOUND ON THE 4" M/2 MCP CAPPED WAS LEAKING, FOR PERMANENT REPAIRS THE 4" M/2 CAP WAS REMOVED AND REDOPED FOR PERMANENT REPAIRS. SOAP TESTED-NO LEAKS
25 |  |  |  |  | Distribution Main |  | Other |  |  | Other |  | 1973-04-27 |  | Patch Welded |  | Steel |  | FRESNO | KILLED 1/2" CU. GAS SERVICE AT MAIN
| 08-50068- |  |  | 0.5 | Branch Service |  | Body of Pipe |  |  |  |  | 2008-06-21 | 2008-06-21 | Replace Partial Service |  | PE2406 (Yellow or Orange) |  | FRESNO | REPAIR SVC. (1/2"); HOME OWNER DIGGIN OUT SERVER LINE FOR REPAIR HIT INTO 1/2" BRANCH SVC, NO USA;
25 |  |  |  | 2 |  |  | Other |  |  | Other |  | 1973-04-25 |  |  |  | Steel |  | FRESNO | KILLED 3/4" GAS SERVICE AT MAIN
70 | 95-30113-1 |  |  | 4 | Service |  | Body of Pipe |  |  | Corrosion |  | 1995-09-11 | 1995-09-25 | Replace Pipe |  | Copper |  | FRESNO | REPAIRED CORROSION LEAK ON 1/2" C.U. SERVICE; FOUND CORROSION LEAK ON 1/2" C.U. SERVICE AT TEE. REPLACED C.U. WITH APPROX. 3' TR.418 1/2" PIPE. WELDED 3/4"X1/2" TRANS. FITT. INST. ONE C.U. TO PL. MECH. COUPLING. DUE TO LENGTH OF SERVICE (34') COULD NOT INSERT WITH 1/4" BAS PIPE.
70 | 94-50094-1 |  |  | 4 | Distribution Main |  | Tap Connection |  |  | Digin |  | 1994-06-01 | 1994-06-01 | Clamp |  | Steel/Wrought Iron |  | FRESNO | S/S CLAMP OVER DAMAGED MAIN WELDED NEW TEE INSERTED SERVICE; MADE TEMP REPAIR ON 4" STL MAIN WHERE CONTRACTOR PULLED 3/4" MUELLER TEE OFF OF MAIN. INSTALLED 4X6 STAINLESS STEEL CLAMP ON MAIN FOR TEMP. REPAIR. WELDED NEW PUNCH TEE 2' S/O REPAIR AND INSERTED SERVICE.
| 10-50113- |  |  |  | Single Service |  | Other |  | HOUSE LINE | Damage by 3rd Party |  | 2010-12-01 |  |  |  | PE2406 (Yellow or Orange) |  | FRESNO | HOUSELINE BROKEN BELOW GROUND. NO REPIAR TO PG&E FACILITIES NEEDED.
25 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1973-10-23 |  |  |  | Steel |  | FRESNO | KILLED 3/4" GAS SERVICE
|  |  |  | 2 | Distribution Main | [6 empty] | 1973-01-22 |  |  |  | Steel |  | FRESNO
25 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1973-10-23 |  | Patch Welded |  | Steel |  | FRESNO | KILLED 3/4" GAS SERVICE
|  |  |  | 2 | Distribution Main | [6 empty] | 1973-01-22 |  |  |  | Steel |  | FRESNO
[18 empty] | FRESNO | DUG UP T.P. MAIN TO DO WALL THICKNESS TEST.
| 10-70151-1 |  |  | 0.5 | Branch Service |  | Plastic Tee Cap |  |  | Other | CRACKED CAP | 2010-10-19 | 2010-10-19 | Aldyl A Overcap - Plastic |  | Aldyl A (Tan or Gray) |  | FRESNO | SERVICE TEE CAP. ALDYL A OVERCAP. ELECTROFUSED ON A ALDLY A OVER CAP
25 |  |  |  | 3 | [8 empty] | 1972-12-26 |  |  | Steel |  | FRESNO
70 | 80-30472-1 |  |  | 1.25 | Other |  | Valves |  |  | Other |  | 1980-10-06 | 1980-11-05 | Replace Pipe and/or Service |  | Steel |  | FRESNO | FOUND GAS LEAK ON 1 1/4" NORD GAS B.O. VALVE. REPAIRED BY PACKING WITH GREASE.
| 07-70112-1 | [5 empty] | Regulator |  | REGULATOR H.P. |  |  | 2007-12-14 | 2007-12-14 | Other | REPLACED H.P. REGULATOR |  |  | FRESNO | REPLACED H.P. REGULATOR INSIDE PIT; FOUND RELIEF VALVE ON A HIGH PRESSURE REGULATOR, INSIDE A PIT RELEASING GAS, CALL OUT JIM HAGAPIAN TO DO REPAIR. REPLACED REGULATOR.
[18 empty] | FRESNO | MOVED HPR SET 15' TO NORTH 5' 3/4" STL NEW HPR SET TIED INTO 1" PL EXISTING TO TWO NEW SERVICES.
70 | 86-30333-1 |  |  | 0.75 | Distribution Main |  | Regulator |  |  | Other |  | 1986-09-10 | 1986-09-12 | Other |  | Steel |  | FRESNO | LEAK IN REG PITS TO ABOVE A.D. INST. NEW REG & RELIEF, GREASED INLET VALVE.
70 | 82-70043-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1982-12-27 | 1982-12-27 | Replace Pipe and/or Service |  | Steel |  | FRESNO | 3/4" PIPE UP STREAN OF VALVE IN TRANS BOX - REPLACE WITH H-12 SET ABOVE GROUND
70 | 88-30063-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  |  | 1988-09-12 | Replace Pipe |  | Steel |  | FRESNO | CALLED FOR M&C MECHANIC TO REPLACE LEAKING STREET ELBOW ON REG SET & ALSO CHANGED ENCLOSURE TO A 17 X 30 PER M&C MECH; FOUND LEAK ON 3/4" STREET ELBOW ON HPR SET. CALLED M&C MECHANIC TO MAKE REPAIRS. REPLACED REG. BOX WITH 17X30 PER M&C MECHANIC.
70 | 75-30068-1 |  |  | 1 | Other |  | Valves |  |  | Other |  | 1975-07-11 | 1975-07-18 | Other |  | Steel |  | FRESNO | VALVE IS LEAKING TIGHTEN VALVE CORE AND GREASED VALVE STOPPED LEAK.
| 09-70017- |  |  | 0.75 | Branch Service |  | Valves |  |  | Other | LOOSE; | 2009-01-16 | 2009-01-26 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | FRESNO | SVC. VALVE LEAK; SVC VALVE LEAK VALVE NEEDED TIGHTENING
25 | 78-30225-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1978-06-22 | 1978-06-22 | Other |  | Steel/Wrought Iron |  | FRESNO | VALVE PIT CHESTNUT & CLINTON 4" BLOW DOWN VALVE LEAKING IN FLANGES GREASED VALVE LEAK STOP
70 | 82-30216-1 |  |  | 0.75 | Other |  | Valves |  |  | Other |  | 1982-09-08 | 1982-09-08 | Other |  | Steel/Wrought Iron |  | FRESNO | GREASED VALVE - STOPPED LEAK. IN VALVE CASING
70 | 82-30272-1 |  |  | 12 | Distribution Feeder Main |  | Valves |  | BLOW-OFF VALVE 4" | Material Failure |  | 1982-10-28 | 1982-10-28 | Other | GREASED VALVE | Steel/Wrought Iron |  | FRESNO | FOUND 4" BLOW-OFF VALVE LEAKING FROM THE FLANGE MADE REPAIR BY GREASING THE VALVE. GOT THE VALVE TO STOP LEAKING. VALVE MIGHT START TO LEAK AGAIN AT FUTURE TIME; FOUND 4" BLOW-OFF VALVE LEAKING FROM FLANGE. GREASED THE VALVE & GOT LEAK TO STOP, GASKET ON VALVE MIGHT HAVE TO BE CHANGED? LEAKS TO THIS VALVE PIT HAVE BEEN CALLED IN BEFORE
| 02-70141-1 |  |  | 4 | Transmission |  | Fitting |  |  |  |  | 2002-10-18 | 2002-10-18 | Other | SEE REMARKS; REPLACED 4 GASKET ON VALVE. | Steel/Wrought Iron |  | FRESNO | REPLACED 4" GASKET ON VALVE.
| 08-50066-1 |  |  | 0.5 | Branch Service |  | Body of Pipe |  |  |  |  | 2008-06-17 | 2008-06-17 | Replace Partial Service |  | PE2406 (Yellow or Orange) |  | FRESNO | SQUEEZED MAIN LINE 1" AND USED TWO PERMASSERT COUPLING ON THE 1/2" PLASTIC; HIT THE 1/2" PLASTIC WITH A SHOVEL
25 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1973-09-06 |  |  |  | Steel/Wrought Iron |  | FRESNO
| 06-50092-1 |  |  | 0.75 | Branch Service |  | Body of Pipe |  |  |  |  | 2006-07-16 | 2006-07-16 | Deactivated Partial Service |  | Steel/Wrought Iron |  | FRESNO | TREAD AND CAP 3/4" STEEL; CONTRACTOR WAS IN THE PROCESS OF EXCAVATING WITH A BACKHOE TO A DEPTH OF 2' WHEN HE HIT A SERVICE TEE TO A BRANCH. SERVICE WAS PINCH DOWN AND CAP, FOR TEMPORARY REPAIR. BRANCH SERVICE SHOULD BE RE-INSTALL A.S.AP. USA WAS NOT CALL. ONE CUSTOMER AFFECTED IN SHUTDOWN. GAS BLOW FOR 2 HRS.; DAMAGE 3/4" STEEL SERVICE TEE WITH A BACKHOE WHILE EXCAVATING TO A DEPTH OF 2'. USA WAS NOT CALL. ONE CUSTOMER AFFECTED IN SHUTDOWN. PINCH 3/4" STEEL THREAD AND CAP FOR TEMPORARY REPAIR. ONE CUSTOMER AFFECTED IN SHUTDOWN. SERVICE SHOULD BE RECONNECTED A.S.A.P.
| 02-50018-1 |  |  | 1.25 | Gathering |  | Drip |  |  | Digin |  | 2002-02-21 | 2002-02-21 | Other | RETHREAD DRIP | Steel/Wrought Iron |  | FRESNO | RE THRED 1 1/4" PIPE & CAP BELOW CURB LEVEL; CONTRACTOR WAS IN PROCESS OF REMOVING DIRT WITH HIS CLAM LOADER ON HIS BACKHOE WHEN HE HIT THE TOP OF THE BLOW-OFF VALVE ON A DRIP. GAS WAS CONTROL AT 4:45P.M. PERMANENT REPAIR WERE MADE BY CUTTING OFF BLOW-OFF LINE BELOW CURB. RE THREADED AND CAP - OFF. USA WAS CALL.
| 08-50023-1 |  |  | 0.5 | Branch Service | [6 empty] | 2008-03-16 | 2008-03-17 | Replace Partial Service |  | TR 418 |  | FRESNO | GSR SHUT GAS OFF 03.16.08 AND CREW REPAIRED 03.17.08; CUSTOMER DIGGING FENCING POST AND HIT INTO 1/2" BRANCH SVC. CUSTOMER WAS UNAWARE OF USA. NO USA CALLED. GAS SHUT OFF BY GSR. SVC. HIT WAS SVC. TO 2323 E. OLIVE;; CUSTOMER HIT 1/2" PLASTIC WHILE DIGGING HOLE FOR FENCE POST. NO US.A.
70 | 90-30038-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1990-03-10 | 1990-03-07 | Replace Pipe |  | Steel/Wrought Iron |  | FRESNO | INSERTED SERVICE WITH 1/2" PL PIPE AND POWELL KIT USED AT RISER FOR PERMANENT REPAIRS; LEAK FOUND 3/4 STL SERVICE INSERTED 3/4 STL WITH 1/2" PL PIPE ALSO INSTALLED A RISER POWELL KIT FOR PERMANENT REPAIRS. BAR TEST AND JW AREA
70 | 11-70064-A |  |  | 0.75 | Branch Service |  | Riser Valve Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-12-31 | 2011-01-20 | Replace Service Valve <2-inch |  | Steel |  | FRESNO | LEAK AT RISER THREADS CHANGED RISER VALVE; CHANGED SVC VALVE ON SERVICE RISER.
| 08-70096-1 |  |  | 0.75 | Branch Service |  | Riser |  |  |  |  | 2008-11-08 | 2008-11-09 | Other | RISER VALVE | PE2406 (Yellow or Orange) |  | FRESNO | SHUT VALVE ON SVC. VALVE; CAR HIT INTO APARTMENT AND BROKE MANIFOLD @ REG. VALVE INTACTED, SVC. VALVE WAS SHUT; CAR HIT SVC. @ MANIFOLD AND GAS BLOWING OUT OF SVC. VALVE. VALVE WAS SHUT OFF BY CREWS.
|  |  |  | 2 | Other |  | Valves |  |  | Other |  | 1981-05-20 | 1981-05-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | FRESNO | REMOVED DRIP TO CLEAR RIGHT-OF-WAY FOR NEW HIGHWAY.
25 |  |  |  | 1.25 | Other |  | Valves |  |  | Damage by outside Forces |  |  | 1972-12-19 |  |  | Steel/Wrought Iron |  | FRESNO | INSTALLED 1 1/4 M/2 FITTING 14' S/N/PL CUT & CAPPED RISER 1' N/FITTING. SHOULD BE RELOCATED WHEN NEW SIDEWALK & CURB ARE INSTALLED
70 | 90-30122-1 |  |  |  | Transmission |  | Valves |  |  | Other |  |  | 1990-06-05 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | FRESNO | TIGHTENED PLUG ON VALVE. LEAK STOPPED
70 | 81-70054-1 |  |  | 16 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1981-10-09 | 1981-10-09 | Other |  | Steel/Wrought Iron |  | FRESNO | TIGHTENED FITTINGS ON MON. CONTROL VALVE
25 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1973-04-23 |  |  |  | Steel/Wrought Iron |  | FRESNO
138
70 | 77-30411-1 |  |  | 2 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1977-12-02 | 1979-03-07 | Other |  | Steel/Wrought Iron |  | FRESNO | REMOVED VALVE CASING, INSTALLED GREASE FITTING WITH 2' RISER. GREASED VALVE LEAK STOPPED.
25 |  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | FRESNO
70 | 87-30164-1 |  |  | 6 | Transmission |  | Regulator |  |  | Other |  | 1987-09-10 | 1987-09-11 | Other |  | Steel/Wrought Iron |  | FRESNO | VERY HOT; BY PASS VALVE - LEAKING BY, SEAT CUT OUT AN DIPH BLOWING. REPAIR AS NEEDED & GREASE VALVE; ON NORTH/SI OF CENTRAL 1ST REG BOX E/5618 E CENTRAL
|  |  |  | 0.75 | [13 empty] | FRESNO | C/O 3/4" STL SERVICE AT MAIN & REMOVED REGS
70 | 82-50008-1 |  |  | 0.75 | Transmission |  | Regulator |  |  | Other |  | 1982-02-07 | 1982-02-07 | Other |  | Steel/Wrought Iron |  | FRESNO | REBUILT PRI. REGULATOR
|  |  |  | 6 | [7 empty] | 1992-01-30 | [5 empty] | FRESNO | INSTALLED 3/4" FIRE VALVE, ABANDONED EXISTING H.10 & H.12, INSTALLED NEW H.10 H.12
70 | 96-70048-1 |  |  | 6 | Transmission |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1996-03-02 | 1996-03-03 | Replace Pipe |  | Steel/Wrought Iron |  | FRESNO | REPAIR LEAK ON TRANS LINE; REPAIRED TRANS. LEAK LEAKING DRESSER COUPLING BY REMOVING DRESSER COUPLING & REPLACED WITH 17" OF 8" STL.
|  |  |  | 6 | [13 empty] | FRESNO | C/O - 3/4 STL SERVICE FROM 6" TP MAIN AND ABANDONED ABOVE GROUND REG. STATION.
70 |  |  |  | 6 | Transmission | [7 empty] | 1975-03-25 |  |  | Steel/Wrought Iron |  | FRESNO | C/O 3/4" TP STL SERVICE AND REMOVED REG. STATION. CONVERTED EXISTING SERVICE TO 2" PLASTIC MAIN.
25 |  |  |  | 0.75 |  |  | Regulator |  |  | Other |  | 1976-11-08 | 1976-11-18 | Other |  | Steel/Wrought Iron |  | FRESNO; | PRIMARY REG SET. FOUND RELIEF LEAKING REPAIRED REG.
70 |  |  |  | 6 | [13 empty] | FRESNO | C/O 3/4" SERVICE OFF OF T.P. MAIN AND RECONNECTED SERVICE TO 2" STL MAIN ON SOUTH SIDE OF ST.
70 | 88-30200-1 |  |  | 0.75 | Transmission |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1988-08-19 | 1988-09-13 | Other |  | Steel/Wrought Iron |  | FRESNO | REDOPE MULDER CAPS & TIGHTEN
70 | 80-30331-1 |  |  | 16 | Transmission | [6 empty] | 1980-08-18 |  |  |  | Steel/Wrought Iron |  | FRESNO
|  |  |  | 6 | [13 empty] | FRESNO | ABANDONED GAS SERV.; ABANDONED SERV. AT MAIN
70 | 81-30413-1 |  |  | 16 | Transmission | [6 empty] | 1981-09-01 |  |  |  | Steel/Wrought Iron |  | FRESNO
70 | -94566 |  |  | 8 | [7 empty] | 1990-08-09 | [5 empty] | FRESNO | INSTALLED 3/4" MUELLER T.P. PIN-OFF TEE BY GAS MECHANIC T.U. AND 3/4" STL PIPE T.P. SOAP TESTED AND NO LEAKS.
| 02-50085- | 138 | 35.74 |  | Transmission |  | Body of Pipe |  |  | Digin |  | 2002-06-11 | 2002-06-11 | Other | REPLACE PIPE | Steel/Wrought Iron |  | FRESNO | WELDED IN NEW PIECE OF PIPE
70 | 80-30381-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1980-09-03 | 1980-09-12 | Other |  | Steel/Wrought Iron |  | FRESNO | TIGHTEN GREASE FITTING IN BY PASS VALVE
|  | 138 | [15 empty] | FRESNO
|  | 138 |  | 16 | [13 empty] | FRESNO | WELD SLEEVE TO REPAIR GAUGE ON LINE 138
70 | 86-30334-1 |  |  | 1.25 | Transmission |  | Regulator |  |  | Other |  | 1986-09-05 | 1986-09-08 | Other |  | Cast/Ductile Iron |  | FRESNO | NORTH REG PIT 10% HOT #29 BR - ACROSS FROM 3898 EAST. REPAIR DIAPHRAM ON WEST REG.
| 03- | 138 | [15 empty] | FRESNO | EXPOSED FOR BORE ACROSS PIPE TO INSTALL 1 1/4" PLASTIC 32" DEPTH OF SERVICE 16" HP LINE 138 DEPTH 42"
70 |  | 138 |  | 16 | [7 empty] | 1992-07-15 | [5 empty] | FRESNO | INSTALLED ETS STATIONS FOR T&R DEPT ON LINE #138 TP; INSTALLED TEST LEADS ON GAS LINE #138 PER GAS STANDARD 0-10. INSTALLED 2 LEADS TO A PEDESTAL FOR PRECAUTIONS.
70 | 81-30405-1 |  |  | 16 | Transmission | [6 empty] | 1981-09-04 |  |  |  | Steel/Wrought Iron |  | FRESNO
70 | 81-30404-1 |  |  | 16 | Transmission | [6 empty] | 1981-09-04 |  |  |  | Steel/Wrought Iron |  | FRESNO
|  |  |  | 16 | Transmission | [7 empty] | 1976-07-07 |  |  |  |  | FRESNO
|  |  |  | 16 | [13 empty] | FRESNO
70 | 88-38026-1 |  |  | 0.75 | Distribution Main |  | Regulator | Regulator |  | Construction Defect |  | 1988-12-13 | 1988-12-13 | Other |  | Steel/Wrought Iron |  | EASTON | REPAIR DRI HPR
70 | 86-30301-1 |  |  | 0.75 | Other |  | Physical/Mechanical Joint |  |  | Other |  | 1980-05-30 | 1986-08-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | FRESNO | REPLACE 3/4" X 2" NIPPLE ON INLET SIDE OF REG. UPGRADE TO HOT 2, 10% 8-4-86. 10-9-86 CLEAR.
25 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1973-04-26 | [5 empty] | FRESNO | KILLED 1" GAS SERVICE AT MAIN.
70 | 86-30342-1 |  |  | 0.75 | Transmission |  | Regulator |  |  | Other |  | 1986-09-09 | 1986-09-12 | Other |  | Steel/Wrought Iron |  | FRESNO | LEAK ON FIRST STAGE REG SIDE ON THREADS. REBUILT PTI. REG, RE-DOPED ALL FITTINGS
70 | 94-70100-1 |  |  | 6 | Transmission |  | Other Welds |  |  | Construction Defect | ; | 1994-07-06 | 1994-07-06 | Other |  | Steel/Wrought Iron |  | Fresno | REPAIRED LEAK BY WELDING OVER EXISTING WELD AROUND SERVICE TEE
70 | 81-30523-1 |  |  | 4 | Other |  | Valves |  |  | Other |  | 1981-12-02 | 1981-12-14 | Other |  |  |  | FRESNO | VALVE LEAKING AROUND GREASE PLUG. STOP LEAK BY GREASING VALVE.
70 |  |  |  | 6 | Transmission | [6 empty] | 1976-08-10 |  |  |  | Steel/Wrought Iron
68 | 72-60005-1 |  |  | 1.25 | Other |  | Body of Pipe | Body of Pipe |  | Corrosion |  | 1972-09-21 | 1972-09-22 | Other |  | Steel/Wrought Iron |  | FRESNO | FOUND LEAK IN B.O. RISER REPLACED RISER; CUSTOMERS IN THIS AREA SMELL GAS ODOR. (REQUEST CHECK SERVICEMAN)
|  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | FRESNO | INSTALLED 1 1/4" T.P. TAP KILL 3/4" T.P. TAP
70 | 89-30288-1 |  |  | 2 | Other |  | Physical/Mechanical Joint |  |  | Other |  | 1989-08-25 | 1989-08-25 | Other |  | Steel/Wrought Iron |  |  | RECAP 2"X3/4" REDUCER
6
70 | 90-30028-1 |  |  | 4 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  |  | 1990-01-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SANGER | TIGHTEN BOLTS, STOPPED LEAKS
70 | 81-30048-1 |  |  | 2 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1978-03-09 | 1981-03-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | FRESNO | FLAMEPACKS CHECKED. FOUND #2 READINGS - 3-2-81. 2" SCREWED ELL D.S. OF INLET VALVE LEAKING @ THREADS. REDOPED L/ OK.
|  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | FRESNO
25 |  |  |  | 6 | Transmission | [10 empty] | Steel |  | FRESNO;
|  |  |  | 4 | [13 empty] | FRESNO | INST. 1" TR-418; INST. 175' OF 1" TR-418 SET 1 1/4" 3' MTR. MANIFOLD & WELDED 1" TRANS. FITT. AT H.P.R. BOX
70 | 92-30155-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2010-09-09 | 1992-09-10 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SANGER | LEAK ON 4" TP WELDED SOAP TESTED OK WELDED 2" WELD O LET OVER CORROSSION LEAK SOAP TESTED OK; ALSO FOUND A OLD STYLE CAN WELD ON THE 4" MAIN WITH A THREADED NIPPLE ON TOP OF THE CAN (2' EAST OF CORROSSION LEAK). WELDED A "WELD" O LET- LEAK - SOAP TESTED OK OVER CORROSSION
70 | 85-30301-1 |  |  | 0.75 | Distribution Feeder Main |  | Regulator |  |  | Other |  | 1985-09-06 |  | Other |  | Other |  | SANGER | DIPH. LEAKING; NEW FORM A- CURRENT FORM A LOST - POST CH CLEAR
70 | 81-30412-1 |  |  | 4 | Distribution Feeder Main | [6 empty] | 1981-09-03 |  |  |  | Steel/Wrought Iron |  | FRESNO
70 |  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | FRESNO
[18 empty] | DEL RAY | INST 1 1/4" TP SERVICE
| 03-70019-1 | 1209-05 |  | 0.75 | Transmission |  | Valves |  |  | Construction Defect |  | 2003-01-29 | 2003-02-03 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | FRESNO; FRESNO | OVER SERVICE; TIGHTEN CAP ON VALVE FOR REPAIRS; SURVEYED LEAK & FOUND ODOR OF GAS BY CURB VALVE. DUG UP CURB VALVE AND FOUND TP GAS VALVE LEAKING ON CAP TIGHTEN CAP & SOAP TESTED NO LEAKS.
70 | 93-30033-1 |  |  | 0.75 | Distribution Feeder Main |  | Body of Pipe |  |  | Other |  | 1993-01-25 | 1994-12-15 | Replace Pipe |  | Steel/Wrought Iron |  | FRESNO | C/O 10" 3/4" PIPE REPLACED WITH NEW PIECE THREAD INTO FIRE VALVE WELDED OTHER END TO SERVICE
70 | 87-30143-1 |  |  | 0.75 | Distribution Feeder Main |  | Physical/Mechanical Joint |  |  | Other |  | 1979-09-07 | 1987-09-11 | Other |  | Steel/Wrought Iron |  | FRESNO | LEAK AT THREADS, NIPPLE TO REG, REBUILD UNIT - BACK IN SERVICE.
70 |  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
70 | 88-30061-1 | [10 empty] | 1988-09-07 | [5 empty] | SELMA
70 | 81-30411-1 |  |  | 6 | Distribution Feeder Main | [6 empty] | 1981-09-03 |  |  |  | Steel/Wrought Iron |  | FRESNO;
|  |  |  | 6 | Transmission | [6 empty] | 1975-11-18 |  |  |  | Steel/Wrought Iron |  | FOWLER
|  |  |  | 6 | Transmission | [6 empty] | 1975-11-17 |  |  |  | Steel/Wrought Iron |  | FOWLER
|  |  |  | 6 | Distribution Feeder Main | [7 empty] | 1973-02-20 |  |  | Steel/Wrought Iron |  | FRESNO
70 | 79-30300-1 |  |  | 0.75 | Other |  | Regulator |  |  | Other |  | 1979-09-07 | 1979-09-18 | Other |  | Other |  |  | BAD SEAT REPLACED
70 | 93-50058-1 |  |  | 0.75 | Service |  | Physical/Mechanical Joint |  |  | Damage by outside Forces |  | 1993-04-13 | 1993-04-13 | Other |  | Steel/Wrought Iron |  | SANGER | CLOSED 1" MUELLER VALVE TEE ON 8" DF MAIN. REMOVED BROKEN 3/4" FIRE VALVE. INSTALLED NEW 3/4" FIRE VALVE; BROKEN 3/4" FIRE VALVE CLOSED 3/4" FIRE VALVE TO CONTROL GAS BLOWING ON BROKEN THREADS DOWNSTREAM OF VALVE. FOUND LEAKING THREADS ON THE UPSTREAM SIDE OF THE FIRE VALVE. CLOSED 1" MUELLER VALVE TEE AT THE MAIN AND REPLACED 3/4" FIRE VALVE BY RETHREADING THE UPSTREAM SIDE AND WELDING IN A NEW 3/4" X 1 1/4" REDUCER ON THE DOWNSTEAM SIDE.
|  |  |  | 8 | [7 empty] | 1993-03-08 | 1993-03-08 |  |  |  |  | SANGER | INSTALLED 103' - 1 1/4" SERV. TO CNG STATION; CNG STATION SERVICE INSTALLED 103' - 1 1/4" SERV. WELDED 1" MUELLER VALVE TEE TO 8" T.P. MAIN (5/8" TAP HOLE). INSTALLED 3/4" FIRE VALVE 18' W/E PL ACADEMY. VALVE IS INSTALLED WITH HIGH HEAD EXT. AND GREASE EXT. MAIN IS 9 1/2' DEEP. VALVE IS 4' DEEP. INSTALLED 2" STL. RISER WITH BYPASS.
70 | 71-00014- |  |  | 0.4 | Transmission | [6 empty] | 1971-07-02 |  |  |  | Steel |  | SAN JOAQUIN
70 | 71-00013- |  |  | 0.4 | Transmission | [6 empty] | 1971-07-29 | 1971-08-02 |  |  | Steel |  | SAN JOAQUIN
70 | 79-30309-1 |  |  | 3 | Transmission |  | Valves |  |  | Other |  | 1979-09-12 | 1980-02-05 | Other |  | Steel/Wrought Iron |  | FRESNO | VALVE WAS GREASED AND LEAK STOPPED.
70 | 83-50112-1 |  | 7.178 | 4 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1983-09-26 | 1983-10-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN JOAQUIN | FOUND CORROSION LEAK ON TRANSMISSION MAIN 27' E/ER OF DONNA. INST. FULL BAND. OPEN BELL HOLE AND USED LAMM AIR MOVER. SUSPECT INTERNAL CORROSION. REMOVED 24" STL. PIPE REPLACED WITH SAME; NOTES L#111 HAS WATER WITHIN THE PIPING SYSTEM.
70 | 85-30288-1 |  |  | 0.75 | Distribution Main |  | Other |  |  | Construction Defect |  | 1985-09-17 | 1985-09-18 | Other |  | Steel/Wrought Iron |  |  | TIGHTEN 3/4" UNION TO HPR SET (DRY PIPE DOPE)
SAN JOAQUIN
4
FRESNO
[18 empty] | SAN JOAQUIN | ABANDONED EXISTING 4". INSTALLED NEW 4" MAIN & ROCKWELL 21 45 1/2 VALVE PER WORK ORDER 43754-A; FOUND INHIBITOR IN MAIN.
[18 empty] | SAN JOAQUIN | INSTALLED 4" PCF & 4" ROCKWELL D2145 1/2 VALVE PER WORK ORDER 43754-A; FOUND INHIBITOR IN MAIN.
|  | 111 |  | 3
70 | 94-70046-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1994-03-23 | 1994-03-23 | Replace Pipe |  | Steel/Wrought Iron |  | HELM | CORROSION LEAK ON RISER. REPLACED 3/4" STL. RISER; FOUND CORROSION LEAK ON 3/4" STL. RISER. PERMANENT REPAIR BY WELDING IN A NEW RISER STOPPED GAS FLOW AT REG. PIT.
| 02-70142-1 | 111 | 1001.05 |  | Transmission |  | Valves |  |  |  |  | 2002-10-16 | 2002-10-16 | Other | GREASE | Steel/Wrought Iron |  | HELM | PIT FULL OF WATER VALVE LEAKING AIRED OUT OF GREASE; TEE ON TRANS MAID NOT TO STANDARD ADDITIONAL WORK NEEDED TO INSTALL TEE
[18 empty] | HELM | THE CONTRACTOR, EXCAVARE, WAS TRENCHING WITH A CABLE PLOW TO INSTALL FIBER OPTIC, & IT WAS NECESSARY TO CROSS THIS 16" T.P. GAS LINE. I STOOD BY AS REQUIRED.
70 | [17 empty] | HELM | POT HOLED THREE LOCATION ONE FOR 4" T.P. & TWO FOR 2" STL. H.P. MAIN
70 | 84-30276-1 |  |  | 0.75 | Distribution Feeder Main |  | Regulator |  |  | Material Failure |  | 1984-10-02 | 1984-10-02 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | HELM - FRESNO | TIGHTEN BOLTS ON 2ND REG AT DIPHT - LEAK TEST OK; NEW A FORM MADE OUT
25 |  | 111 |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | HELM | PROSPECTED TRANS. LINES VALLEY NITROGEN, BECAUSE RANCHER RIPPED OVER LINE, RIPPING DOWN TO A DEPTH OF 30", COVER ON LINE IS 57" BOTH LOCATIONS, LINE IN THE CLEAR.
[18 empty] | FRESNO | INSTALLED GAS SERVICE
|  | 111 | 7.43 | 12 | Transmission |  | Other |  |  | Other | OTHER COMPANY PIPE LINE | 2002-07-22 | 2002-07-22 | Other | COMPANY PIPE LINE LEAKING | Steel/Wrought Iron |  | KERMAN | MOBIL SURVEY FOUND LEAK - BARLOTE OVER TP MAIN & J.W.; SOAP TESTED MAIN NO SIGN OF LEAKS; MOBIL SURVEY VEHICLE PICK UP GAS FUMES ON MADERA 145. FLAME PACK WENT OUT & SURVEYED & LOCATED THE TP MAIN. GAS CREW WENT OUT & DRILLED HOLES AND JW ALSO AND FOUND. 50% - 20% READINGS BACKHOE UNCOVERED 123 FT OF 12" TP MAIN AND FOUGHT NO LEAK. THERE IS ODOR OF GAS, BUT NOT FROM OUR MAIN. OUR MAIN IS CLEARED OF LEAKS, OTHER COMPANIES HAVE TO CHECK THEIR MAIN FOR LEAKS.
THE CONTRACTOR, SOUTHWESTERN, IS TRENCHING TO INSTALL 30" T.P. GAS PIPE FOR P.G.& E. I STOOD BY WHILE THEY EXPOSED IT.
|  | 138 |  | 16 | [13 empty] | CARUTHERS | WELDED 3/4" TEE ON TP LINE 138 AND INST. VALVE 4' FROM LINE AND CONNECTED TO THE GAS COMPANYS 3/4" STL SERV.; INST 3/4" TP TEE ON 16" TP LINE 138. MADE 1/2" TAP AND INST. VALVE 4' TO THE SOUTH. INST 1 1/4" INSULATING FITTING 1' TO THE SOUTH OF VALVE. ATTACHED TO THE GAS COMPANY'S 3/4" STL SERVICE LINE.
|  | 138 | [15 empty] | FRESNO
|  | 111-A | [16 empty] | INSTALLED 2 LOCTA
|  | 111 | 2.99 | [14 empty] | HELM | INSTALL 2" TP SERVICE INDUSTRIAL METER 38M - FOSTER FARMS
|  | 111 |  | 12 | [14 empty] | 2" TAPPED STRAIGHT OUT OF MAIN THEN 2" VALVE * 2" SERVICE TO 2" RISER; C/O 2" AT FLANGED VALVE INSTALLED BLEND TURNED BACK ON VALVE TO SOAP TEST (OK) SHUT VALVE. LEFT 18" STUB
70 | 81-50119-1 | 111 |  | 12 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1981-12-07 | 1981-12-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | LINE #111, DAMAGED BY D-8K CAT WHILE SUB SOILING FOR FRESNO FARMS, 13526 SO. ELM, CARRUTHERS. MAIN REPAIRED BY BUTT WELDING 15' 9" OF .280 WALL, GRADE X-42 PIPE IN THE LINE.; THE REPAIRED SECTION IS 124' SOUTH OF THE PIPELINE MARKER ON THE N/SIDE OF NEBRASKA.
70 |  | 138 |  | 48 | [11 empty] | Steel |  | Fresno | Abandoned 1/2" T.P. Service from line 138 -Serv. Fed southern cal- reg pit.; Left 1/2" c/o serv and plugged end of valve re-wrapped tee and valve. per gary gilmore
|  | 138 |  | 36 | [7 empty] | 1994-07-12 | [5 empty] | Fresno | Assit. SoCal shut off fire valve.
|  | 138 | [13 empty] | Steel/Wrought Iron |  | Fresno
[16 empty] | Steel/Wrought Iron |  | fresno | Existing main marker. Inst. E.T.S
[18 empty] | Fowler | Installed 1/2" PL
70 | 81-70036-1 |  |  | 4 | Transmission |  | BODY OF PIPE |  |  | CORROSION |  | 1981-04-20 | 1981-04-20 | WELD OVER SLEEVE OR CAN | CLAMP | Steel/Wrought Iron |  | San Joaquin
[12 empty] | 2000-12-26 |  |  |  | Steel/Wrought Iron |  | Fresno | Cut off 3/4" steel service and removed H.P.R. set
68 | 84-25004-1 |  |  | 0.75 | Transmission |  | BODY OF PIPE |  |  | OTHER |  | 1984-01-25 | 1984-01-31 | OTHER |  | Steel/Wrought Iron
70 | 85-30386-1 |  |  | 6 | Transmission |  | OTHER WELDS |  |  | OTHER |  | 1985-12-05 | 1985-12-05 | OTHER |  | Steel/Wrought Iron
[18 empty] | Selma | Posted to plat NLW 4/4/05
70 |  |  |  | 8 | Transmission | [6 empty] | 1973-06-21 |  |  |  | Steel/Wrought Iron
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron
70 | [11 empty] | 1996-07-26 | [5 empty] | Fresno | Changed HPR set
25 |  |  |  | 2 | Distribution Main |  | OTHER |  |  | OTHER |  | 1974-04-03 |  |  |  | Steel/Wrought Iron
[12 empty] | 2008-08-21 | [5 empty] | Fresno | Browning Construction Co. Trenching across 12# T.P., line 118A, To install 6"pl. sewer pipe at these two points. Pipe installed under T.P.
25 |  |  |  | 0.12 | Distribution Main |  | OTHER |  |  | OTHER |  | 1980-12-04 |  |  |  | Other Plastic
03-50119-1 |  |  |  | 0.75 | Service |  | BODY OF PIPE | Fitting |  | DAMAGE BY 3RD PARTY |  | 2003-08-04 | 2003-08-04 | SERVICE ENTIRELY REPLACED |  | Steel/Wrought Iron |  | Fresno | Replaced 25' of 3/4" steel pipe
[18 empty] | Fresno | C/O+ abandoned 1" steel service off of 12" T.P. main.
|  |  |  | 12 | Transmission | [12 empty] | Fresno
|  |  |  | 12 | Transmission | [6 empty] | 2008-09-04 |  |  |  | Steel/Wrought Iron |  | Fresno | Telstar Constr. co, Trenched across this 12" T.P. to install 18" D.I. Pipe, Requiring standby.
[18 empty] | Fresno | Repaired line 118 by installing 12" band .375 wall and sava valve nipple. Tested band at 450lbs PSIG ofr 35 min; Wrap on 12" is very poor shape. Condensation between wrap and stl.
70
70 |  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron
| 10-30006-1 |  |  | 4 | Distribution Main |  | Valves |  |  | MATERIAL FAILURE |  | 2010-01-05 | 2010-01-06 | OTHER |  | Steel/Wrought Iron |  | Fresno | Grease valve and tighten to stop leak.
[18 empty] | Fresno | Installed 23" TP Stl. (1) 3/4" 2024 valve. (1) casing and cover abandoned 3' 3/4" T.P. Stl. as per wd 40468-A
[18 empty] | Fresno | Abandoned 21' 2" HP Stl. Abandone dist. reg. sta (system #662). Abandoned 2' 3/4" stl. as per wd 40463-A; No T.P. tee on main-3/4" nipple with 2004 valve. Shot valve off and installed 3/4" stl plug. no weld stamp
Fresno
|  |  |  | 4 | [11 empty] | Steel/Wrought Iron |  | Fresno | Exposed T.P. main. Stand by for contractor trenching to landscape center island.
|  |  |  | 12 | Transmission |  | FITTING | Meter | [5 empty] | OTHER | C/O SERVICE AT MAIN AND TRANSFER TO PLST MAIN | Steel/Wrought Iron |  | fresno
|  |  |  | 0.5 | Service | [6 empty] | 2002-03-07 |  |  |  | Aldyl A (Tan or Gray) |  | fresno | C/O at P/L 3/7/02 Stafford
25 |  |  |  | 2 | Distribution Main |  | OTHER |  |  | OTHER |  | 1973-10-02 |  |  |  | Steel/Wrought Iron |  | Fresno
25 |  |  |  | 2 | Distribution Main |  | OTHER |  |  | OTHER |  | 1973-10-25 | [5 empty] | Fresno
70 | 84-70009-1 |  |  | 2 | Distribution Feeder Main |  | BODY OF PIPE |  |  | Damage by outside Forces |  | 1984-02-07 | 1984-02-07 | OTHER |  | TR 418 |  | Fresno | G.C. crew hit D.E. of 2" pl. main in 4" stl. Casing repair weremade by shutting off gas floe & installing one 2" amp. fit D.E. No costumer shut down was involved
25 |  |  |  | 3 | Distribution Main |  | OTHER |  |  | OTHER |  | 1973-08-14 |  | OTHER |  | Steel/Wrought Iron |  | Fresno
[5 empty] | Transmission | [10 empty] | Steel/Wrought Iron |  | Fresno | Exposed T.P. main. Standby for Contractor trenching to landscape center island
|  |  |  | 4 | Transmission | [12 empty] | Fresno | The Contractor, C.D.S., Trenched across Ashland to install A 14" D>I., & ran iot over the top of this 4' T.P. line.
25 |  |  |  | 4 | Distribution Main |  | OTHER |  |  | OTHER |  | 1973-12-19 |  |  |  | Steel/Wrought Iron |  | Fresno
25 |  |  |  | 12 | Distribution Main |  | OTHER |  |  | OTHER |  | 1973-04-10 | [5 empty] | Fresno
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Fresno | The contractor, Jerry's trenching, bored across Ashlan to install a 4" F.O. duct, & crossed this 6" T.P. main
|  |  |  | 6 | Transmission |  | OTHER |  |  | OTHER |  |  | 1981-12-14 | WELD OVER SLEEVE OR CAN |  | Steel/Wrought Iron |  | Fresno | No leak main damaged by back hoe; Welded 6"x5' full circle can over damaged area for permanent repair; Can tested 100 PSIG with air prior to tapping 6"x5' full circle can .250 wall grade B.
25 |  |  |  | 2 | Distribution Main |  | OTHER |  |  | OTHER |  | 1973-09-10 |  | PATCH WELDED |  | Steel/Wrought Iron |  | Fresno
25 |  |  |  | 2 | Distribution Main |  | OTHER |  |  | OTHER |  | 1973-07-23 |  | PATCH WELDED |  | Steel/Wrought Iron |  | Fresno | Installed new service
25 |  |  |  | 2 | Distribution Main |  | OTHER |  |  | OTHER |  | 1973-12-12 |  |  |  | Steel/Wrought Iron |  | Fresno
25 |  |  |  | 2 | Distribution Main |  | OTHER |  |  | OTHER |  | 1973-09-10 |  | PATCH WELDED |  | Steel/Wrought Iron |  | Fresno
25 |  |  |  | 2 | Distribution Main |  | OTHER |  |  | OTHER |  | 1973-11-19 |  |  |  | Steel/Wrought Iron |  | Fresno
25 |  |  |  | 2 | Distribution Main |  | OTHER |  |  | OTHER |  | 1973-11-20 |  |  |  | Steel/Wrought Iron |  | Fresno
|  |  |  | 2 | Distribution Main |  | OTHER |  |  | OTHER |  | 1973-07-16 |  | PATCH WELDED |  | Steel/Wrought Iron |  | Fresno
98 | 84-30001-1 |  |  | 10.75 | Transmission |  | Body of Pipe |  |  | Material Failure |  | 1984-08-01 | 1984-08-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | 6 mi. north east of avenal | Crack-material failure K8 discharge lateral pipe (10.75") cracked on bottom of line 4" long. Replace 27"
98 | 84-00001-1 |  |  | 10.75 | Transmission |  | Body of Pipe |  |  | Material Failure |  | 1984-08-01 | 1984-08-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Avenal | K8 10" lateral pipe cracked. 4" long on bottom of disharge line. Replaced 27"
11 |  |  |  |  | Transmission | [6 empty] | 1984-03-22
98 | 79-30001-1 | 300-A | 401.23A | 34 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1979-06-26 | 1979-06-27 | Other |  | Steel/Wrought Iron |  |  | Pipe exposed for GM 403928 current span test leads. Leak found in cross over piping insulating flange. Repaired made by tighting flange bolts.
98 | 80-30602-1 |  |  | 8 | Distribution Feeder Main |  | Fitting |  |  | Material Failure |  | 1980-05-12 | 1980-05-15 | Replace Pipe |  | Steel/Wrought Iron |  | Morro Bay Primary | Crack runs parallel with pipe, topp side, across weld. 2" on T.T., 1" on pipe. Found during annual over-haul of regulater by T.M. Crack was visible, performed dy check.
98 | 71-00005-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Material Failure |  | 1971-04-19 | 1971-04-22 | Replace Pipe |  | Steel/Wrought Iron
98 | 71-00002-1 |  |  | 1 | Other |  | Gas Cooler |  |  | Material Failure |  | 1971-11-06 | 1971-11-07 | Other |  | Other
98 | 71-00003-1 |  |  | 24 | Transmission |  | Body of Pipe |  |  | Material Failure |  | 1971-12-03 | 1972-02-16 | Replace Pipe |  | Steel/Wrought Iron
98 | 71-00004-1 |  |  | 24 | Transmission |  | Body of Pipe |  |  | Material Failure |  | 1971-12-04 | 1972-02-17 | Replace Pipe |  | Steel/Wrought Iron
98 | 71-30001-1 | 300A | 230.09 | 34 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 1971-01-16 | 1972-04-12 | Weld Over Sleeve or Can |  | Steel/Wrought Iron
11 |  |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1985-05-28 | 1985-06-14 | Patch Welded |  | Steel/Wrought Iron
11 |  | SP-2 | 41 | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1985-05-28 | 1985-06-14 | Patch Welded |  | Steel/Wrought Iron |  |  | Leak repair with patch
11 |  | SP-2 | 41 | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1985-05-28 | 1985-06-14 | Patch Welded |  | Steel/Wrought Iron |  |  | Leak repair with patch
;
98 | 77-30001-1 |  | 355.77 | 34 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 1977-02-24 | 1977-02-28 | Weld Over Sleeve or Can |  | Steel/Wrought Iron
| 77-30001-1 |  | 355.77 | [9 empty] | 1977-02-28
98 | 76-00002-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Damage by Outside Forces |  | 1976-05-22 | 1976-05-22 | Replace Pipe |  | Steel/Wrought Iron
98 | 76-00001-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-03-21 | 1976-03-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron
98 | 75-00006-1 |  |  | 8 | Transmission |  | Compression Coupling Steel |  | COMPRESSOR COMPONENTS | Material Failure |  | 1975-11-24 | 1976-03-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  | L-300-B | 297.5 | 0.34 | Transmission |  | Girth Weld |  |  | Damage by 3rd Party |  |  | 2005-06-29 | Other | Replace section | Steel/Wrought Iron |  | Safter
|  |  | 306.61B |  | Transmission | [10 empty] | Steel/Wrought Iron |  | wasco | Exposed line to install cathode wire for new anode bed at MP - 306.61B. Map attached.
|  | 300-B | 352.55 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Install ETS station M.P. 352.55 L-300-B
|  |  | 339.50A | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  | Kettleman City | Exposed line to install new ETS @ MP 339.50A. Map attached.
|  |  | 346.56A | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  | Kett City | Completed by Don Oliveira. Install test lead @ MP 346.56A. Map attached.
|  |  | 343.31A | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  | Kettleman City | Installed new coupon @ MP 343.31A. Map attached.
|  | 300-A | 341.2 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Install ETS station M.P. 341.20 - Line 300-A
|  | 300-A | 340.58 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Install ETS station M.P. 340.58 Line 300-A
| 08-30006-1 | 300A | 344.52 | 34 | Transmission |  | Fitting | Other | GREASE FITTING |  |  | 2008-10-21 | 2008-11-18 | Other | SERVICE GREASE FITTING | Steel/Wrought Iron |  | Kettleman city | 400' East of street names - 300A MP 344.52; Service/grease tap - stop leak at fitting
|  |  | 238.5-A |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Install test leads at M.P. 238.5-A; Picture next page
|  |  | 249.03-A |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Install ETS station M.P. 249.03-A 6/12/08
|  | 300-B | 359.05 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Install test leads at M.P. 359.05 L-300-B; Picture on next page
| 07-30001-1 | 300-B | 354.2 | 34 | Transmission |  | Other |  | Drill hole | Other | Drilled wrong line | 2007-08-13 | 2007-08-16 | Other | WELD 1 SAVE-A-VALVE | Steel/Wrought Iron |  | Avenal | Kett comp. sta.; Drilled wrong line with a 15/64 drill; Drill 15/64 hole on 300-B when it should of been drilled on 300-A for a sniff hole to replace V-56 at Kett. Comp. Sta.
|  | 190 | 7.73 | 12 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 190 | 6 | 12 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 300B | 297 | 34 | Transmission | [7 empty] | 1994-01-21 | Other | BAND | Steel/Wrought Iron |  |  | Weld band - over Nick's .020 to .060 deep; Installed band
|  | 300-A | 373.8-A | 34 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  |  | 1996-12-15 | Replace Pipe |  |  |  |  | Weld 6 feet can to replace puncture (approx 6" x 8" hole) in main. Cat. Ripping 6" feet for new orchard.
|  | 306 | 15 | 20 | Transmission | [7 empty] | 1996-01-08 |  |  | Steel/Wrought Iron |  | Avenal | L-306 @ mp 15, Install test leads for deep well anode; attach 2 #10 wires and 1 #4 wire with cool weld apply handicaps and recoat with plastic #50
|  |  |  | 0.375 | Transmission |  | Physical/Mechanical Joint |  |  | Corrosion |  | 1990-04-19 | 1990-04-23 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  |  | 3/8 steel tubing leaking; at pitting reg V-14 m1 orifice to be leaking around packing gland
|  |  |  | 0.375 | Transmission |  | Physical/Mechanical Joint |  |  |  |  | 1990-04-19 |  | Tighten Cap or Bolt |  | Steel/Wrought Iron |  |  | 3/8 steel tubing leaking; at pitting reg v-14 m1 orifice tube leaking around packing gland
| 91-30001-1 | 300B | 346.3 | 34 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1991-08-28 | 1991-08-28 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Kettleman City | Excavate to locate gas leak. Found a rust spot (donut) with a 1/16" or 1/8" hole approx. 21" from the top on west side of pipe.
|  | PG&E #2 | 45 | 26 | Transmission | [8 empty] | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Weld a 26" repair sleeve over a D90 guage.
|  | PG&E #2 | 45 | 26 | Transmission | [7 empty] | 1992-01-21 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Chevron Oil company found an oil leak next to our line. Our line was saturated with oil. Need to replace 73" of our wrap.
|  | 300-B | 346 | 34 | Transmission | [7 empty] | 1991-09-24 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Weld a split sleeve over the .080 pit.
|  | 300-A | 371-A | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Contractor installed 8" plastic line under our row. We have 21" cover. Plastic water line was installed 78" deep, with 13" between pipes.
|  |  | 354-A | 34 | Transmission | [13 empty] | Pipe to soil .916 reading; Found a small amount of moisture. Inspected top and bottom of pipe and found a small amount of rust at the bottom. Wire brushed and rewrap pipe. Check O.K..; Note: see map for location (next page)
|  | 2 | 59.96 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-2 M.P 59.96 in Hole #2 Cluster of pits shown on attached picture. Deepest pit was .224 thousands of an inch. Pits were found by the smart pig data; L-2 M.P 59.96 in Hole #1 with the deepest pit at .120 thousands of inch. Pit were found by the Smart Pig Data
|  | 2 |  | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-2 - For Smart Pig
98 | 10-88236-1 | 300A | 368.91 | [8 empty] | 2010-10-28 | 2011-03-05 | Other |  |  |  | Coalinga | Reading in vault on W. Dorris Ave. Line 300A; same, no leak found PR; vegatation decomposing, no leak
98 | 10-82049-1 | 300B | 309.2 | [8 empty] | 2010-10-07 | [5 empty] | Wesco | BLOW DOWN STACK; CITY: LOST HILLS, 309.20
98 | 10-82052-1 | 300B | 32787 | [8 empty] | 2010-10-07 | [5 empty] | Kettleman City | L-300B MP327.87, blow down stack; SAME, Tighten
98 | 10-88221-1 | X6506 | 35261 | [8 empty] | 2010-10-22 | [5 empty] | Kettleman City | Kettleman intertie mtr & reg. sta, flange & plug; same, tighten
98 | 10-88216-1 | 300A | 29353 | [8 empty] | 2010-10-22 | [5 empty] | Shafter | south of V293.53A MP 293 Pole #71; same/wall map 4925 plat D02, 293.53 Tighten
98 | 10-88214-1 | 300A | 267.26 | [8 empty] | 2010-10-22 | [5 empty] | Bakersfield | n. of Rt. 223 E. of S. Union Ave. V-267A; line 300A v-267A outside of reg station, 267.26 Tighten
98 | 10-88093-1 | 300B | 24142 | [8 empty] | 2010-10-19 | [5 empty] | 3 Rocks | 100' north of valve 241: City = Tehachapi; Line 300B MP 241, WM is 5234-108, cummings valley rd, mp 241.40B
98 | 10-88029-1 | 300B | 393.76 | [8 empty] | 2010-10-25 | [5 empty] | Fresno | V393 76 - multiple valves and fitting all marked; Line 300B, WM is 3979-H06, M.P. 393 Line 300B, WM is 3979-H06
98 | 10-88033-1 | 300A | 366.57 | [8 empty] | 2010-10-29 | [5 empty] | Coalinga | Valve yard, L300A AMP 366.57; WM is 4233
98 | 10-88238-1 | 300A | [9 empty] | 2010-10-29 | [5 empty] | Coalinga | Leaks on valve tubing marked w/ yellow cable ties; Valve 366A V 366.57A, WM is 4233-D02
98 | 10-88102-1 | 300A | 270.85 | [8 empty] | 2010-10-20 | [5 empty] | Bakersfield | visual soap test on valve Line 300 mile 270-85A; same, 270.85
98 | 10-88089-1 | 300B | 261.03 | [8 empty] | 2010-10-19 | [5 empty] | Bakersfield | Inter S. Edison & Millux Rd.; MP. 261.03
98 | 10-88085-1 | 300A | 267.24 | [8 empty] | 2010-10-18 | [5 empty] | Bakersfield | east Bear Mountain Blvd. retangle valve box-inbetw; in between Sunset and Hwy 223, 267.24
98 | 10-88104-1 | BD517 | 0 | [8 empty] | 2010-10-20 | [5 empty] | 3 Rocks | Threaded end cap on pressure relief valve; BD517, WMi si 5331-H07, 266.66 BD plug
98 | 10-88084-1 | 300B | 284.62 | [8 empty] | 2010-10-16 | [5 empty] | Bakersfield | Leak on valve (marked w/ cable tie) in station; Bakersfield Tap, WM is 5024-B02, 284.62 Tighten
98 | 10-88098-1 | 300A | 287.74 | [8 empty] | 2010-10-20 | [5 empty] | Bakersfield | Visual @ swedge fitting for pressure tap valve; eacham Rd valve V287.74A, WM 4926-J0, 287.74 Tighten
98 | 10-88095-1 | 300A | 29024 | [8 empty] | 2010-10-20 | [5 empty] | Bakersfield | btwn flanges on blwdwn stck of valve, V290.33A; Sullivan & Bussell Rd, WM is 4925-G08, 290.25 Tighten
98 | 10-88083-1 | 300B | 288.41 | [8 empty] | 2010-10-16 | [5 empty] | Bakersfield | Leak on 1 1/4" vlave on header; Button willow intertie, MW is 4926-I03, 288.41
98 | 10-88080-1 | 300B | 290.25 | [8 empty] | 2010-10-16 | [5 empty] | Bakersfield | Leaks on 3/4" valve on valve; L300B V290.25B, WM is 4925-G08, 290.25
98 | 10-88231-1 | 190 | 1063 | [8 empty] | 2010-10-27 | [5 empty] | Coalinga | Plug @ end off drip; V-10 53 Line 190, WM is 4233-G06, V-10.53 L-190
98 | 10-88233-1 | 2 | 0.16 | [8 empty] | 2010-10-28 | [5 empty] | Mendota | rec valve box s side of rd (reg stat 4129); same, 417.9 R-14 valve
98 | 10-88090-1 | 300B | 256.64 | [8 empty] | 2010-10-19 | [5 empty] | Arvin | vlv @ line 300B @ point 256B; @ reg sta L 300B MP 256, WM is 5230-F0, soap d/on Tape - other
98 | 10-88020-1 | 300B | 363.89 | [8 empty] | 2010-10-23 | [5 empty] | Coalinga | Both pressure tap 1/2" valves; V363.89B, WM is 4233-G06, V363.89B, WM4233G06
98 | 10-88100-1 | 300A | 280.58 | [8 empty] | 2010-10-20 | [5 empty] | Bakersfield | Visible leek on V20; same, 280.58 V-20
98 | 10-88081-1 | 300B | 287.7 | [8 empty] | 2010-10-16 | [5 empty] | Bakersfield | Leak @ 3/4" line @ valve; V287.70B L300B, WM is 4926-I04, 287.70 Tighten
98 | 10-88217-1 | 300A | 292.44 | [8 empty] | 2010-10-22 | [5 empty] | Shafter | valve 292-44A; same, 292.44 Tighten
98 | 10-88021-1 | X6528 | 363.89 | [8 empty] | 2010-10-23 | [5 empty] | Coalinge | Reading under unibolt cap/visual on 1/2" valve; 363.89B blowdown stack, WM is 4233-G0, 1 1/2" valve power, 363.89B BDV Stack, WM 4233-G0
98 | 10-88096-1 | 300A | 256.21 | [8 empty] | 2010-10-20 | [5 empty] | Arvin | 300 north 300A @ point 256A; WM is 5230-F08, 256.21
98 | 10-88094-1 | 300B | 314.19 | [8 empty] | 2010-10-19 | [5 empty] | 3 Rocks | Blwdwn stk 75' from MLV 314.20B, City = Lost Hills; Seq 110 MLV 314.20B, WM is 4639-I02, 314.19
98 | 10-88019-1 | 300B | 362.85 | [8 empty] | 2010-10-23 | [5 empty] | Coalinge | Drip is located in grapevine bet rows 119 & 120; WM is 4233-H07, 362.85 B
98 | 10-88027-1 | 300B | 388.6 | [8 empty] | 2010-10-25 | [5 empty] | Cantua Creel | L-300B valve 388.60; Wall map is 4042-D06, 388.60 B
98 | 10-88028-1 | BD549 | 388.6 | [8 empty] | 2010-10-25 | [5 empty] | Cantua Creek | Spur SW of valve 388.60; MP 388.60 B
98 | 10-88031-1 | BD549 | 1 | [8 empty] | 2010-10-26 | [5 empty] | Mandota | Leak @ plug on 1/2" press tap valve; V396.70B, WM is 3978-E08, MP 396.70 B
98 | 10-88032-1 | BD549 | 2 | [8 empty] | 2010-10-26 | [5 empty] | Mendota | Fitting on Topick blowdown stack leeking @ threads; V396-70B, WM is 3978-E08, MP 396.70B
98 | 10-88023-1 | 300B | 1 | [8 empty] | 2010-10-25 | [5 empty] | Mendota | 1/2" pressure tap valve leaking; V405.48B, WM is 3976-C05, MP 405.48B
98 | 10-88026-1 | 300B | 40151 | [8 empty] | 2010-10-25 | [5 empty] | Mendota | Vis @ union connection on 3/4" valve on MLV; MLV 401.51B, WM is 3977-C06, MP 401.51B
98 | 10-88227-1 | 300A | 40520 | [8 empty] | 2010-10-27 | [5 empty] | Mendota | Readings and visual @ plug to 1/2" press tap valv; V 405.20A, WM is 3976-D05, MP 405.20 A
98 | 10-88107-1 | 300B | 344.52 | [8 empty] | 2010-11-03 | [5 empty] | Kettleman City | regulator station leak on metric valve ss of mlv 3; same, 344.52 B/P
98 | 10-88079-1 | BD549 | 344.52 | [8 empty] | 2010-10-15 | [5 empty] | Kettleman City | vent box 75' w. of reg. station; same, 344.52 B/O
98 | 10-88229-1 | BD464 | 396.45 | [8 empty] | 2010-10-27 | [5 empty] | Mendota | Readings under cap of unibolt on blowdown stack; V 396.45A WM is 3979-F01, Unibolt cap, MP 396.45A unibolt cap
98 | 10-88035-1 | 300B | 383.8 | [8 empty] | 2010-10-21 | [5 empty] | Kettleman City | Blwstck V-A side, Line 300B MP 383.80 in orchard; same, WM is 4043-J04
98 | 10-82054-1 | 300B | 314.19 | [8 empty] | 2010-10-07 | [5 empty] | Kettleman City | L-300 MP 314.19, Blow down stack; Same, 314.19
98 | 10-88233-1 | 2 | 16 |  |  |  | Other |  |  | Other |  | 2010-10-28 | 2011-03-14 | Tighten Cap/Bolt - Fitting | SOAP AND/OR TAPE  OTHER |  |  | Mendota | rec valve box s side of rd (reg stat 4179); same, 417.9 R-14 valve; Tighten
| 10-82025-1 | 300B | 362.88 | 0.75 | Transmission |  | Valves |  |  | Other | Grease fail | 2010-10-02 | 2010-10-03 | Tighten Cap or Bolt | SOAP AND/OR TAPE  OTHER | Steel/Wrought Iron |  | Huron | Drip Lag; SAME
95 | 10-88019-1 | 300B | 36285 | [8 empty] | 2010-10-23 | 2011-03-11 | Remove/Replace Completion Plug Fitting |  |  |  | Coalinga | Drip is located in grapevine bet rows 119 & 120; WM is 4233-H07, 362.85 B; Remove, retape, replace plug-soap test
98 | 10-88020-1 | 300B | 363.89 | 12 | Transmission >= 20% SMYS | [6 empty] | 2010-10-23 | 2011-02-25 |  |  |  |  | Coalinga | Both pressure tap 1/2" valves; V363.89B, WM is 4233-G06, V363.89B, WM 4233G06; Remove, Plug, Tape, Replace @ soap test
98 | 10-88021-1 | X6528 | 363.89 | 12 | [7 empty] | 2010-10-23 | 2011-02-25 |  |  |  |  | Coalinga | Reading under unibolt cap/visual on 1/2" valve; 363.89B blowdown stack, WM is 4233-G0, 363.89B BDV stackm WM is 4233-G0; Remove plug, tape & replace soap test
98 | 10-88035-1 | 300B | 383.8 | 12 | Transmission >= 20% SMYS |  | Other |  |  |  |  | 2010-10-21 | 2011-03-05 | Tighten Cap/Bolt - Fitting |  |  |  | Kettleman City | Blwstck V-A side, Line 300B MP 383.80 in orchard; Same, WM is 4043-J04; Cleaned & tighten1
98 | 10-88027-1 | 300B | 38860 | [8 empty] | 2010-10-25 | 2011-03-11 | Remove/Replace Completion Plug Fitting |  |  |  | Cantua Creek | L-300B valve 388.60; Wall map is 4042-D06, 388.60 B; Tighten packing - Soap test
98 | 10-88028-1 | BD549 | 38860 | [8 empty] | 2010-10-25 | 2011-03-11 | Remove/Replace Completion Plug Fitting |  |  |  | Cantua Creek | Spur SW of valve 388.60; MP 388.60 B; Tighten valve, remove, retape, replace plug - soap test
98 | 10-88029-1 | 300B | 39376 |  |  |  | Compression Coupling Stainless Steel | Compression Coupling Stainless Steel | THREADS, OTHER MECHANICAL JOINT | Material Failure | OTHER | 2010-10-25 | 2011-03-05 | Mechanical Repair Fitting - Fitting | TIGHTEN CAP/BOLT  FITTING; SOAP AND/OR TAPE  OTHER | Other |  | Fresno | V393 76 - multiple valves and fitting all marked; MP 393 Line 300B, WM is 3979-H06, M.P. 393 Line 300B, WM is 3979-H06; Tighten fitting tape + soap test
98 | 10-88032-1 | BD549 | 2 | [8 empty] | 2010-10-26 | 2011-03-11 | Remove/Replace Completion Plug Fitting |  |  |  | Mendota | Fitting on Topock blowdown stack leaking @ threads; V396-70B, WM is 3978-E08, MP 396.70B; Tightend fitting - soap test
98 | 10-88031-1 | BD549 | 1 | [8 empty] | 2010-10-26 | 2011-03-11 | Remove/Replace Completion Plug Fitting |  |  |  | Mendota | Leak @ plug on 1/2" press tap valve; V396.70B, WM is 3978-E08, MP 396.70 B; Remove, retape, replace plug - soap test
98 | 10-88026-1 | 300B | 401.51 | [8 empty] | 2010-10-25 | 2011-03-11 | Tighten Cap/Bolt - Fitting |  |  |  | Mendota | Vis @ union connection on 3/4" valve on MLV; MLV 401.51B, WM is 3977-C05, MP 401.51 B; Tighten unions - soap test
98 | 10-88023-1 | 300B | 1 | [8 empty] | 2010-10-25 | 2011-03-11 | Tighten Cap/Bolt - Fitting |  |  |  | Mendota | 1/2" pressure tap valve leaking; V 405.48B, WM is 3976-C05, MP 405.48B; Remove, retape, replace plug - soap test
| 09-30001-1 | 300 | 353.85 | 12 | Transmission |  | Other |  | UNI BOLT CAP | Material Failure | Gasket | 2010-10-04 | 2010-10-16 | Fill Weld - Weld |  | Steel/Wrought Iron |  | Avenal | Valve A Block Down Stack; SAME; This repair was done at 34453 Playmouth Ave. (Kettleman Comp. Sta.), This is a blow down stack at the Comp. Sta., We replaced the old Uni-Bolt cap with the new Flange and Blinde Flange design.
98 | 10-88033-1 | 300A | 366.57 | 0.25 | Transmission >= 20% SMYS |  | Fitting |  |  |  |  | 2010-10-29 | 2011-03-05 | Soap and/or Tape - Other |  |  |  | Coalinga | Valve yard, L300A AMP 366.57; WM is 4233; Tighten & repaired
98 | 10-88238-1 | 300A |  |  | Single Service |  | Compression Coupling Stainless Steel |  |  | Material Failure |  | 2010-10-29 | 2011-03-05 | Soap and/or Tape - Other |  | Steel |  | Coalinga | Leaks on vlave lubing marked w/ yellow cable ties; Valve 366A V 366.57A, WM is 4233-D02; Tighten & Retapeded
98 | 10-88236-1 | 300A | 368.91 | [8 empty] | 2010-10-28 | 2011-03-05 | Other |  |  |  | Coalinga | readings in vault on W. Dorris Ave. Line 300A; same; Vegatation decomposing
| 10-82028-1 | 300 | 378.65 | 12 | Transmission |  | Valves |  |  | Material Failure |  | 2010-09-28 | 2010-10-06 | Tighten Cap or Bolt | SOAP AND/OR TAPE | Steel/Wrought Iron |  | Coalinga | L-300 A M.P. 378.65 Blowdown stack
| 10-82027-1 | 138 | 0.02 | 0.5 | Distribution Main |  | Valves |  |  | Other |  | 2010-09-28 | 2010-10-06 | Tighten Cap or Bolt | SOAP AND/OR TAPE | Steel/Wrought Iron |  | Coalinga | V-0.02
98 | 10-88227-1 | 300A | 405.2 | [8 empty] | 2010-10-27 | 2011-03-11 | Tighten Cap/Bolt - Fitting |  |  |  | Mendota | Readings and visual @ plug to 1/2" press tap valv; V 405.20A, WM is 3976-D05, MP 405.20 A; Remove, retape, replace plug - soap test
| 10-82026-1 | 306 | 0 | 20 | Transmission |  | Valves |  |  | Other | Stem packing | 2010-10-04 | 2010-10-07 | Other | Stem packing |  |  | Avenal | V-56
| 10-82026- | 306 | 0 | 20 | Transmission >= 20% SMYS |  |  |  |  | Other |  |  | 2010-10-07 | Other |  | Other |  | Avenal | V-56; V-56
| 10-82030- | 306 | 4.4 | 1 | Single Service |  | Regulator/Pilot |  |  | Other |  | 2010-10-04 | 2010-10-06 | Soap and/or Tape - Other |  |  |  | Avenal | Reg set; tightened bolts on housing
98 | 10-88108-1 | 306 | 13.32 | 1 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-11-04 | 2011-02-05 | Greased - Other |  | Steel |  | Avenal | mp 13.32 line 306
98 | 10-88109-1 | 306 | 446 | 0.75 | Transmission >= 20% SMYS |  | Riser | Regulator/Pilot | REGULATOR/PILOT | Other |  | 2010-11-05 | 2011-02-05 | Tighten Cap/Bolt - Fitting | GREASED; SOAP AND/OR TAPE  OTHER | Steel |  | Avenal | Multiple leaks @ reg 30' south & 45' south of mark; MP 4.45
98 | 10-88110-1 | 306 | 40.29 | 0.75 | Single Service |  | Curb Valve |  |  | Other |  | 2010-11-02 | 2011-02-05 | Tighten Cap/Bolt - Fitting |  | Steel |  | Paso Robles | Estrella Station below grnd valve (yellow cover); same; Fully open vlv
98 | 10-88111-1 | 306 | 40.29 |  |  |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-11-02 | 2011-02-02 | Soap and/or Tape - Other |  |  |  | Paso Robles | Estrella Station blow gas at drain vlv on filter; pic 8 pad; Tighted fitting's & soap tested
98 | 10-88110-1 | 306 | 40.29 | 0.75 | Single Service |  | Curb Valve |  |  | Other |  | 2010-11-02 | 2011-02-05 | Tighten Cap/Bolt - Fitting | SOAP AND/OR TAPE  OTHER | Steel |  | Paso Robles | Estrella Station below grnd valve (yellow cover); same
98 | 10-82024-1 | 306 | 40.3 | 1 | Transmission >= 20% SMYS |  | Curb Valve |  |  | Other |  | 2010-10-03 | 2011-02-05 | Soap and/or Tape - Other |  |  |  | Paso Robles | Curb valve; Estrella river Sta, curb valve; Fully opened valve
98 | 10-88112-1 | 306 | 40.29 | 1.25 | Transmission >= 20% SMYS |  | Threads | Threads | OTHER MECHANICAL JOINT | No/Deteriorated Pipe Dope |  | 2010-11-02 | 2011-02-05 | Soap and/or Tape - Other |  |  |  | Paso Robles | multiple leaks in station at blowdown stack; same;
98 | 10-88231-1 | 190 | 10.63 | [8 empty] | 2010-10-27 | 2011-02-27 |  |  |  |  | Coalinga | Plug @ end off drip; V-10 53 Line 190, WM is 4233-G06, V-10.53 L-190; Remove, retape, replace plug-soap test
| 10-82050-1 | 300A | 345.05 | 12 | Transmission |  | Other |  | 2 IN PLUG | Material Failure |  |  | 2010-10-09 | Tighten Cap or Bolt | SOAP AND/OR TAPE | Steel/Wrought Iron |  |  | Blow down stack; same
| 10-82051-1 | 300B | 333.38 | 12 | Transmission |  | Other |  | 1/2 IN GAUGE LINE | Other | loose connection | 2010-10-07 | 2010-10-09 | Tighten Cap or Bolt | SOAP AND/OR TAPE | Steel/Wrought Iron |  | Kettleman | Blow Down Stack; SAME
98 | 10-88213-1 | 300A | 323.87 | 12 | Transmission >= 20% SMYS |  | Other Mechanical Joint |  |  | Material Failure |  | 2010-10-21 | 2011-02-22 | Tighten Cap/Bolt - Fitting |  | Steel |  | Kettleman City | Readings under cap of blow down stack; Valve V323.87A, WM is 4536-I01, Same;
| 10-82048-1 | 300B | 319.9 | 12 | Transmission |  | Other |  | 2 IN PLUG | Material Failure |  | 2010-10-07 | 2010-10-09 | Tighten Cap or Bolt | SOAP AND/OR TAPE | Steel/Wrought Iron |  | Lost Hills | Blow Down Stack; SAME
| 10-82048-1 | 300B | 319.9 | 12 | Transmission |  | Other |  | 2 IN PLUG | Material Failure |  | 2010-10-07 | 2010-10-09 | Tighten Cap or Bolt | SOAP AND/OR TAPE | Steel/Wrought Iron |  | Lost Hills | Blow Down Stack; SAME
98 | 10-88217-1 | 300A | 292.44 | [6 empty] | Other |  | 2010-10-22 | 2011-02-25 | Soap and/or Tape - Other |  | Steel |  | Shafter | valve 292-44A; same, 292.44 Tighten; Tighten soap test
98 | 10-88216-1 | 300A | 293.53 | [6 empty] | Other |  | 2010-10-22 |  | Soap and/or Tape - Other |  | Steel |  | Shafter | south of V293.53A MP 293 Pole #71; same/wall map 4925 plat D02, 293.53 Tighten; Tighten soap test
| 10-82047-1 | 300A | 290.3 | 12 | Transmission |  | Other |  | UNI-BOLT CAP | Material Failure |  | 2010-10-07 | 2010-10-15 | Fill Weld - Weld |  | Steel/Wrought Iron |  | Buttonwillow | Blow Down Stack; SAME; This repair was done at M.P. 290.33 on L-300A B/D Stack, North of Sillivan Rd. & West of Bussell Rd. Stack is near the N/W corner of intersection in Buttonwillow, We replaced the old Uni-Bolt cap with the new Flange and Blind Flange design.
98 | 10-88095-1 | 300A | 290.24 | [6 empty] | Other |  | 2010-10-20 | 2011-02-25 | Soap and/or Tape - Other |  | Steel |  |  | btwn flanges on blwdwn stck of valve, V290.33A; Sullivan & Bussell Rd, WM is 4925-G08, 290.25 Tighten; Tighten soap test
98 | 10-88098-1 | 300A | 287.74 |  | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-20 | 2011-02-25 | Soap and/or Tape - Other |  | Steel |  | Bakersfield | Visual @ swedge fitting for pressure tap valve; eacham Rd valve V287.74A, WM 4926-J0, 287.74 Tighten; Tighten soap test
98 | 10-88099-1 | BD464 | 287.74 |  |  |  | Fitting |  |  |  |  | 2010-10-20 | 2011-02-25 | Tighten Cap/Bolt - Fitting | SOAP AND/OR TAPE  OTHER | Steel |  | Bakersfield | Readings under cap of bllwdwn stk; Meacham Rd V 287.74A, WM is 4926-J04, 287.74 Tighten; Tighten Bolt
98 | 10-88100-1 | 300A | 280.58 |  | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-20 | 2011-02-25 | Soap and/or Tape - Other |  | Steel |  | Bakersfield | Visible leak on V20; same, 280.58 V-20; Tighten
98 | 10-88102-1 | 300A | 270.85 | [6 empty] | Other |  | 2010-10-20 | 2011-02-23 | Soap and/or Tape - Other |  | Steel |  | Bakersfield | visual soap test on valve Line 300 mile 270-85A; same, 270.85; Tighten
98 | 10-88214-1 | 300A | 267.26 |  |  |  | Fitting |  |  | Other |  | 2010-10-22 | 2011-02-23 |  |  | Steel |  | Bakersfield | n. of RL 223 E. Union Ave. V-267A; line 300A v-267A outside of reg station, 267.26 Tighten; Tape and tighten
98 | 10-88085-1 | 300A | 267.24 |  | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-18 | 2011-02-23 | Tighten Cap/Bolt - Fitting | SOAP AND/OR TAPE  OTHER |  |  | Bakersfield | east Bear Mountain Blvd. retangle valve box-inbetw; in between Sunset and Hwy 223, 267.24; Tighten and tape
98 | 10-88096-1 | 300A | 256.21 |  | Transmission >= 20% SMYS |  | Fitting |  |  |  |  | 2010-10-20 | 2011-03-02 | Tighten Cap/Bolt - Fitting | SOAP AND/OR TAPE  OTHER |  |  | Arvin | 300 north 300A @ point 256A; WM is 5230-F08, 256.21; Tighten Fitting
98 | 10-88091-1 | 300B | 230.26 | 1 | Transmission >= 20% SMYS |  | Other |  |  | Material Failure |  | 2010-10-19 | 2011-02-21 | Soap and/or Tape - Other | REPLACE SAFTY TAPATAIL PLUG | Steel |  | Tehachapi | 1" fitting on blwdwn stck of V230.26B; V230.26B, City=Tehachapi, WM 5336-F07, access via jameson rd, repaired Leak; Body of Blow Down Stack; Pressure Safety Tafatail Plug Replaced
98 | 10-88104-1 | BD517 | 0 |  | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-20 |  | Remove/Replace Completion Plug Fitting | TIGHTEN CAP/BOLT; SOAP AND/OR TAPE  OTHER |  |  | 3 Rocks | Threaded end cap on pressure relief valve; BD 517, WMi si 5331-H07, 226.66 BD Plug
98 | 10-88079-1 | BD549 | 344.52 | [6 empty] | Other |  | 2010-10-15 | 2011-03-05 | Tighten Cap/Bolt - Fitting | SOAP AND/OR TAPE  OTHER | Steel |  | Kettleman City | vent box 75' w. of reg .station; same, 344.52 B/D; Tighten Bolt and cap
98 | 10-88107-1 | 300B | 344.52 | [6 empty] | Other |  | 2010-11-03 | 2011-03-05 | Tighten Cap/Bolt - Fitting | SOAP AND/OR TAPE  OTHER | Steel |  | Kettleman City | regulator station leak on metric valve ss of mlv 3; Same, 344.52 B/P; Tighten Bolt and cap
98 | 10-88078-1 | BD549 | 319.97 | 12 | Transmission >= 20% SMYS |  | Other Mechanical Joint |  |  | Material Failure |  | 2010-10-15 | 2011-02-22 | Tighten Cap/Bolt - Fitting |  | Steel |  | Lost Hills | ; cap abv grnd 50' from reg station #319B to the eas; same, same; cleaned & tighted uni-bolt cap
98 | 10-82054-1 | 300B | 314.19 | 12 | Transmission |  | Other |  | UNI-BOLT CAP | Material Failure |  | 2010-10-07 | 2011-03-05 | Tighten Cap/Bolt - Fitting | SOAP AND/OR TAPE  OTHER | Steel/Wrought Iron |  | Lost Hills | Blow Down Stack; SAME, 314.19
98 | 10-88094-1 | 300B | 314.19 |  |  |  | Other |  |  | Other |  | 2010-10-19 | 2011-03-05 | Tighten Cap/Bolt - Fitting | SOAP AND/OR TAPE  OTHER |  |  | 3 Rocks | Blwdwn stk 75' from MLV 314.20B, City = Lost Hills; Seq 110 MLV 314.20B, WM is 4639-I02, 314.19; Tighten
98 | 10-82046-1 | 300B | 293.2 | 12 | Transmission |  | Other |  | UNI-BOLT CAP | Material Failure |  | 2010-10-07 | 2011-03-06 | Tighten Cap/Bolt - Fitting | SOAP AND/OR TAPE  OTHER | Steel/Wrought Iron |  | Shafter | Blow Down Stack; SAME; Tighten
98 | 10-88080-1 | 300B | 290.25 |  | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-16 | 2011-03-05 | Soap and/or Tape - Other |  |  |  | Bakersfield | Leaks on 3/4" valves on valve; L300B V290.25B, WM is 4925-G08, 290.25
98 | 10-88083-1 | 300B | 288.41 |  | Transmission >= 20% SMYS |  | Fitting | Threads | THREADS |  |  | 2010-10-16 | 2011-03-05 | Tighten Cap/Bolt - Fitting | SOAP AND/OR TAPE  OTHER |  |  | Bakersfield | Leak on 1 1/4" vlave on header; Button willow intertie, WM is 4926-I03, 288.41; Tighten
98 | 10-88082-1 | 300B | 287.7 | [6 empty] | Other |  | 2010-10-16 | 2011-02-25 | Soap and/or Tape - Other |  | Steel |  | Bakersfield | v-287.70B blow down readings btw cap on stack; same, same; Tighten tap & soap test
98 | 10-88081-1 | 300B | 28770 |  | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-16 |  | Soap and/or Tape - Other |  | Steel |  | Bakersfield | Leak @ 3/4" line @ valve; V287.70B L300B, WM is 4926-I04, 287.70 Tighten; Tighten tap & soap test
98 | 10-88084-1 | 300B | 28462 |  | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-16 | 2011-02-25 | Soap and/or Tape - Other |  | Steel |  | Bakersfield | Leak on valve (marked w/ cable tie) in station; Bakersfield Tap, WM is 5024-B02, 284.62 Tighten; Tighter
98 | 10-88089-1 | 300B | 261.03 |  | Transmission >= 20% SMYS |  | Other |  |  |  |  | 2010-10-19 | 2011-03-05 | Soap and/or Tape - Other |  |  |  | Bakersfield | Inter S. Edison & Millux Rd.; MP. 261.03; Tridant seal, soap and/or tape
| 10-82044- | 300B | 2566 | 0.5 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-08 | 2010-10-12 | Tighten Cap/Bolt - Fitting |  | Other |  | Arvin | PLS4, 1/2 in Gauge Line
| 10-82044-1 | 300B | 256.6 | 0.5 | Transmission |  | Other |  | Gauge plug | Other |  | 2010-10-08 | 2010-10-12 | Tighten Cap/Bolt - Fitting | SOAP AND/OR TAPE | Steel/Wrought Iron |  | Arvin | 1/2 in Gauge line; SAME
| 10-82044- | 300B | 2566 | 0.5 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-08 | 2010-10-12 | Tighten Cap/Bolt - Fitting |  | Other |  | Arvin | PLS4, 1/2 in Gauge Line
98 | 10-88090-1 | 300B | 256.64 |  | Transmission >= 20% SMYS |  | Other |  |  |  |  | 2010-10-19 | 2011-03-02 | Soap and/or Tape - Other |  |  |  | Arvin | vlv @ line 300B @ point 256B; @ reg sta L 300B MP 256, WM is 5230-F0, Soap &/on Tape - Other; Trident Seal
| 10-88087- | 300B | 237.5 | 0.75 | Transmission >= 20% SMYS |  | Curb Valve |  |  | Incorrect Operation |  | 2010-10-18 | 2010-11-17 | Tighten Cap/Bolt - Fitting |  | Steel |  | 3 Rocks | VB near entrce & SO vlv on B side, City = Teha; MLV237.50B Tap in vlv box, WM is 5335-B; fully open curb valve
| 10-88088- | 300B | 237.5 |  | Transmission >= 20% SMYS |  | Fitting | Other | UNI-BOLT CAP | Material Failure |  | 2010-10-18 | 2010-12-03 | Other | Welded a new flange | Steel |  | Tehachapi | blwdwn stk 15' N of MLV 237-50B reg sta; foodford Tehachapi, City = Tehachapi, WM; replaced uni-bolt cap with blind flange-set-up; This repair was done by replacing old uni-bolt cap design with a new ansi 600 series 12" flange + blind flange assembly
| 09-30605-1 | 306 | 70 | [8 empty] | 2009-08-05 | 2010-01-27 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | Morro Bay | Morro Bay primary yard - cut 8 valve along N-side fence line; V-C8
| 09-30604-1 | 306 | 70 |  | Transmission | [6 empty] | 2009-08-05 | 2010-01-28 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | Morro Bay | Morro Bay Primary yard. Cut 8 valve along N-side fence line; V-CC
| 09-30602-1 | 306 | 0 | 20 |  |  | Other |  | STAINLESS STEEL TUBING |  |  | 2009-04-02 | 2009-06-08 | Mechanical Repair Fitting - Fitting |  |  |  | Avenal | East side tubing to valve operator
| 09-30601-1 | 306 | 0 | 20 |  |  | Valves |  |  |  |  | 2009-04-02 | 2009-06-08 | Mechanical Repair Fitting - Fitting |  |  |  | Avenal | Button Head grease fitting
| 09-19001-1 | 190 | 0 | 12.75 |  |  | Other |  | GAGUE TAP |  |  | 2009-04-02 | 2009-06-08 | Mechanical Repair Fitting - Fitting |  |  |  | Avenal | 1 in grease fitting
| 09-30002-1 | 300B | 354.01 | 34 |  |  | Valves |  |  |  |  | 2009-04-02 | 2009-08-12 | Mechanical Repair Fitting - Fitting |  |  |  | Avenal | Fire valve next to V-364.01B; Installed New cap
| 09-30005-1 | 300A | 284.69 | 34 | Transmission |  | Other |  | Blow down Stack | Material Failure |  | 2009-04-28 | 2009-07-23 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | Bakersfield | Blow down stack for L-300A; Welded flange w/ blind flange; removed unibolt cap, cleaned and replace cap to blow-down stack. Still leaks. Need to replace unibolt cap with a blind flange. work reg #152313
| 09-30006-1 | 300B | 284.62 | 34 | Transmission |  | Fitting | Other | FIRE VALVE |  |  | 2009-04-28 | 2009-07-24 |  |  | Steel/Wrought Iron |  |  | Fire valve located SE of V-4; Replace curb valve cap; Attended to repair fire valve. Tighen cap, but it slill leaks. Would have to excavate to main and close service tap to replace fire valve cap. 6/17/09 Work Reg #152319
| 09-30003-1 | 300B | 256.64 | 34 | Transmission |  | Fitting |  |  | Material Failure |  | 2009-05-14 | 2009-06-26 | Tighten Cap/Bolt - Fitting | SOAP AND/OR TAPE | Steel/Wrought Iron |  | Arvin | Insertion Meter Pit; remove insertion meters and replaced it with 3" blind flange. No more leaks. See operating diagrm M.P. 256.64 - B PLS#4
| 09-30004-1 | 300A | 256.21 | 34 | Transmission |  | Fitting |  |  | Material Failure |  | 2009-05-14 | 2009-06-26 | Other | REPLACE INSERTION METER WITH A BLIND FLANGE. | Steel/Wrought Iron |  | Arvin | Insertion Meter Pit; Repaired; M.P. 256.21 - A, the insertion meter was removed and replace with a 3" blind flange. Stopped gas leak. See operating Diagram M.P. 256.21-A
| 09-30603-1 | 306 | 69.8 | 8 | Transmission |  | Valves |  |  | Atmospheric Corrosion |  | 2009-06-17 | 2009-09-23 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | Morro Bay | V-2
| 09-30605-1 | 306 | 70 |  | Transmission | [6 empty] | 2009-08-05 | 2010-01-27 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | Morro Bay | Morro Bay primary yard - cut 8 valve along N-side fence line; V-C8
|  | 300B | 270.67 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | See attached map
| 10-00202-1 | 2 | 59.5 | 26 | Transmission |  | Valves |  |  | Other | plug | 2010-04-19 | 2010-04-19 | Soap and/or Tape - Other | CLEAN AND RETAPE PLUG | Steel/Wrought Iron |  | Firebaugh | Valve Yard V-59.5
| 10-16401-1 | 164 | 0.34 | 10 | Transmission |  | Mechanical Joint |  |  | Material Failure |  | 2010-04-27 | 2010-04-09 | Replace Dist Main < 100 ft | BELL JOINT CLAMP | Steel/Wrought Iron |  | Coalinga | 100% gas with gas ranger indicator; Found a 10" dresser coupling leaking at bottom. Cut a 82" section to remove coupling and replaced it with a 82" of tested 10" pipe.
|  | 164 | 0.34 | 10 | Transmission |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2010-04-07 | 2010-04-08 | Replace Dist Main < 100 ft |  | Steel/Wrought Iron |  |  | 100% Gas with a Gas Ranger Indicator; Found a 10" Dresser Coupling leaking at bottom. Cut a 82' section to remove coupling and replaced it with a 82' of tested 10" pipe.
|  | 2 | 58 |  | Transmission | [10 empty] | Steel/Wrought Iron |  | Mendota | L-2 M.P. 58.00; 5 ft. of pipe exposed to install locating wires
|  | 306 | 41.4 |  | Transmission | [10 empty] | Steel/Wrought Iron |  | Paso Robles | L-306 M.P. 41.40; 5ft. of pipe exposed to install 1 INCH TAP
|  | 300B | 360.95 |  | Transmission | [10 empty] | Steel/Wrought Iron |  | Huron | L-300 m.p. 360.95; 3 ft. of pipe exposed to install locating wires
|  | 300B | 277.5 | 0.34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | USA Ticket # 116528 L-300B MP277.5
|  | 300B | 299.01 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-300B M.P. 299.01
|  |  |  | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Request Per ENG. Pipeline
|  |  |  | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Request Per ENG. Pipeline
[5 empty] | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Per Request Eng. Pipeline
|  |  |  | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Per Request ENG. Pipeline
|  | 300B | 277.8 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-300 B M.P. 277.80
|  | 300B | 277.1 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-300 B M.P. 277.1
|  | 300B | 285.33B | 0.34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Install ETS station. L-300-B M.P. 285.33-B
|  | 300B | 281.25 |  | Transmission | [10 empty] | Steel/Wrought Iron
|  | 300B | 268.05B |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Install ETS station M.P. 268.05 - B
|  | 300B | 260.31B | 0.34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Install ETS station M.P. 260.31-B
| 08-30001-1 | 300A | 304.34 | 12 |  |  | Fitting |  |  | Other | Fitting | 2008-09-09 | 2008-09-09 | Tighten Cap/Bolt - Fitting | SOAP AND/OR TAPE | Steel/Wrought Iron |  |  | Leak located on Blow Down Stack; Survived valve & tighten uni-bolt cap & plug on 1" vent.
|  | 300A | 292.15B | 0.34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Install ETS station L-300-A M.P. 292.15-B
|  | 300A | 281.07 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Install ETS station M.P. 281.07 L-300-A
|  | 300A | 269.86 | 0.34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Install ETS station M.P. 269.86 - Line 300-A
|  | 300A | 263.09A | 0.34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Install ETS station M.P. 263.09-A
|  | 300A | 259.94A | 0.34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Install ETS station M.P. 259.94-A 6/18/08
|  | 300A | 258.14A | 0.34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Install ETS station M.P. 258.14-A
|  | Sp-1 | 0.49 | 22 | [11 empty] | Steel |  |  | Line pressure reduced to 5 PSI
|  | SP-1 | 1.1 | 22 | [11 empty] | Steel |  |  | Line pressure reduced to 5PSI
|  | SP-1 | 1.6 | 22 | [11 empty] | Steel |  |  | Line pressure reduced to 5PSI
|  |  | 1.64 | [15 empty] | Line pressure reduced to 5 PSI
|  |  | 1.87 | [15 empty] | Line pressure reduced to 5 PSI
|  |  | 1.88 | [15 empty] | Line pressure reduced to 5 SPI
|  |  | 2.01 | [15 empty] | Line pressure reduced to 5 PSI
|  |  | 2.52 | [15 empty] | Line pressure reduced to 5 PSI
98 | 72-138 -1 |  |  | 10 | Transmission |  | Longitudinal Weld |  |  | Other |  | 2006-01-01 | 2007-01-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron
98 | 74-18001-1 |  |  | 16 | Gathering |  | Drip |  |  | Corrosion |  | 1974-01-09 | 1974-01-09 | Other |  | Steel/Wrought Iron
98 | 74-18002-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18027-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18026-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion | [5 empty] | Steel/Wrought Iron
98 | 74-18025-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18024-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18023-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18022-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18021-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18020-1 |  |  | 1600 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18019-1 |  |  | 1600 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18018-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18017-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18016-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18015-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18014-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18013-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18012-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18011-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18010-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18009-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18008-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18007-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18006-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18005-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18004-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
98 | 74-18003-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1974-02-06 |  |  |  | Steel/Wrought Iron
|  |  |  | 26 | [11 empty] | Steel/Wrought Iron |  |  | L-2 M.P. 59.96 in hole cluster of pits shown on attached picture. Deepest pit was .224 Thousands of an inc. Pits were found by the smart pig data
|  |  |  | 26 | [11 empty] | Steel/Wrought Iron |  |  | L-2 M.P. 59.96 in hole #1 with the deepest pit at .120 thousands inch. Pit were found by the smart pig data
|  |  |  | 26 | [11 empty] | Steel/Wrought Iron |  |  | L-2- for smart pig
|  |  |  | 34 | [11 empty] | Steel/Wrought Iron |  |  | Exposed for instertion meter installation
|  |  |  | 34 | [11 empty] | Steel/Wrought Iron |  |  | L-300 A MP.
|  |  |  | 34 | [11 empty] | Steel/Wrought Iron |  |  | USA ticket #116528. L-300A MP 277.84A
|  |  |  | 34 | [11 empty] | Steel/Wrought Iron |  |  | USA Ticket #116528 L-3008 MP277.5
|  |  |  | 34 | [11 empty] | Steel/Wrought Iron
| 00-40041-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 2000-05-18 | 2000-05-18 | Other | Replaced | TR 418 |  | American Canyon | Installed 1' of 1/2" Plastic & 2 perfection coulplings
|  |  |  | 12 | [7 empty] | 2003-06-17 |  |  |  | Steel/Wrought Iron |  | American Canyon | wrap was in very bad condition; In some spots pipe was bare and would flake off uncovered; Installed ETS for 7/17/03; Locating purposes
|  |  |  | 12 | Transmission |  | Body of Pipe |  |  | Digin | NO LEAK CAUSE  DIG-IN, SCRATCH ONLY | 2005-07-01 | 2005-07-05 | Other | BUFF SCRATCHES | Steel/Wrought Iron |  | American Canyon | Buffed scratches per engineer Gary Vanbrects instruction
40 |  |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1993-06-21 | 1993-07-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Novato | repair leaking valve flange
| 98-05000-1 | 21 | 49 | 0.75 | Transmission |  | Fitting |  |  | Construction Defect |  | 1999-09-15 | 1999-09-15 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Novato | Extracted and inserted pluged cap on gauge line tee
40 | 98-05001-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Construction Defect |  | 1998-06-03 | 1999-09-15 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Novato | Extracted and inserted plug & cap on gauge valve tee
|  |  |  | 12 | [7 empty] | 2005-09-22 |  |  |  | Steel/Wrought Iron |  |  | Installed ETS at main marker
|  |  |  | 16 | [7 empty] | 2005-09-22 |  |  |  | Steel/Wrought Iron |  | Novato | Installed ETS at main marker
| 05-00323-1 |  |  | 4 | Distribution Main |  | Regulator |  |  | Unknown |  | 2005-09-01 | 2005-09-22 | Replace Main Valve >= 2-inch |  | Steel/Wrought Iron |  | Novato | Replaced regulator
40 | 71-2114 |  |  | 0.5 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-05-18 | 1971-05-18 | Replace Pipe and/or Service |  | Copper |  | Novato | Install 1/2" copper flange fitting & steel to copper fitting at riser inside meter box
40 | 71-374 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Material Failure |  | 1971-08-26 | 1971-08-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Novato | Repaired leaks on "manifold" set and riser
4 | 72-00147-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-02-23 | 1972-02-23 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Novato | Note: Gas main wrap was scratched off from previous sewer main stallation. Corrosion in bare are is what cause leak.
| 76-00238-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-04-28 | 1977-07-07 | Clamp |  | Steel/Wrought Iron |  | Novato
[18 empty] | Novato | Crossed and exposed 12" main while trenching for service to #159 So. Novato Blvd, Novato
|  |  |  | 6 | [11 empty] | Steel/Wrought Iron |  | Novato | 6" D.F.M. pothold by contractor depth
|  |  |  | 6 | [11 empty] | Steel/Wrought Iron | 6" D.F.M pothold depth | Novato
|  |  |  | 6 | [7 empty] | 2001-06-26 |  |  |  | Steel/Wrought Iron |  | Novato | pothold to top of 6" D.F.M. Exposed top only
|  |  |  | 6 | [7 empty] | 2005-06-09 |  |  |  | Steel/Wrought Iron |  | Novato | On site for DFM stand by. Contractor dug pothole one day early. Knocked off wrap. Const. was to plate hole
4 | 73-00206 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-05-23 | 1973-07-23 | Clamp |  | Steel/Wrought Iron |  | Novato | Installed 4" skinner leak clamp w/9th Anode
| 76-353-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  |  | 1976-08-19 | Clamp |  | Steel/Wrought Iron |  | Novato | Installed 4" pclamp, 9# anode
| 79-00169-1 |  |  | 12 | Transmission |  | Girth Weld |  |  | Material Failure |  | 1979-04-23 | 1979-11-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Novato | 4" cover on main at the points. cut out leaking weld & replaced of 60 if 12' main
|  |  |  | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | Novato | Dug up 3/4" valve going to H.P.R so P&T could put stop on valve
40 | [11 empty] | 1989-05-09 | [5 empty] | Marin/N. Novato | Exposed top of casing on 16" Exposed top of casing on 16" main at 63" deep. Found large crushed rock over main. The casing over the 20" main 9' deep and 12' south of 16" main at crossing location on hwy 101
40 | [11 empty] | 1989-05-19 | [5 empty] | Marin/N. Novato | Exposed top of 20" main casing at 9' deep. Found rock around casing. 16" trams. main casing was 63" deep and 12' N of 20" main where they both cross hwy101.
[18 empty] | Novato | Installed E.T.S.. Wires on line worker pole. See plat for location of E.T.S.
[18 empty] | Novato | Installed E.T.S. extended wires to line marker pole. See plat for location of E.T.S.
| 02-00140-1 | 21 |  | 12 | Transmission |  | Valves |  |  | Other | No grease | 2002-03-11 | 2002-03-21 | Other | Grease valve | Steel/Wrought Iron |  | Novato | IGIS will not allow without metallic pipe. No changed to 5/0
|  |  |  | 0.2 | Other | [10 empty] | Other Plastic |  | Novato | Main inspection report only; This 2" plastic main is in good condition. Rock backfill dt. Only 18' in depth 10/23/79
4 | [11 empty] | 1995-06-09 | [5 empty] | Novato | Depth check for sewer
[13 empty] | 2000-04-05 | OTHER | WRAPPED MAIN | Steel/Wrought Iron |  | Novato | No leak/wrap damaged. Wrapped main took pipe to soil.
[16 empty] | Steel/Wrought Iron |  | Novato | Patched 5' section of line 21 S/Rowland blvd.
|  |  |  | 1600/1200 | Transmission | [10 empty] | Steel/Wrought Iron |  | Novato;
|  |  |  | 1200 | Transmission | [10 empty] | Steel/Wrought Iron |  | Novato | New street. No address yet
|  |  |  | 1600 | Transmission | [10 empty] | Steel/Wrought Iron |  | Novato | New street. No address yet
| 76-00307-1 |  |  | 0.75 | Other | Telemeter | Body of Pipe |  |  | Corrosion |  | 1976-06-04 | 1976-12-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Fairfax | Caution (2) water main and service main
| 76-00233-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-04-22 | 1976-09-27 | Clamp |  | Steel/Wrought Iron |  | Fairfax | Inst 9# zinc anode. 4" leak clamp
40 | 94-80103-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Other |  | 1994-05-19 | 1994-05-19 | Other | Vented | Steel/Wrought Iron |  | Fairfax | Tightened existing clamps on main. Main in bad shape & needs to be replaced. Still small leaks on old valve down street
| 76-02008-1 |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-01-26 | 1976-05-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | San Anselmo | Installed 24' 3/4" # Stl to #254. Inserted 30' 1/2 pl.
40 | 71-2078 | [10 empty] | 1971-05-14 | [5 empty] | San Anselmo | Checked manhole-water meter box & water valve box-no gas found. TJ 7/1/71
|  |  |  | 4 | Transmission | [6 empty] | 1968-07-09
|  | 21 |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 21 |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 21 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Depth check on 12" line 21. Installed ETS
|  | 21 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Depth check on 12" line 21
|  | 21 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | Novato | Depth check on 12" line 21. Installed E.T.S.
|  | 21 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | Novato | Depth check on 12" line 21. Installed E.T.S. at this location
|  | 21 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | Novato | Depth check on 12" line 21.
|  | 21 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | Novato | Wrap is very poor condition. Can peel of f by hand, some moisture under wrap-spot wrapped.
|  |  |  | 2 | [11 empty] | TR 418 |  | Novato
40 | 74-00548- | 21 |  | 12 | Transmission |  | Physical/Mechanical Joint |  |  | MATERIAL FAILURE |  | 1974-07-31 | 1974-08-10 | Other |  | Steel/Wrought Iron |  |  | Log'd into pipe line history book 8/27/79
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron
[18 empty] | San Rafael | Installed wires on exposed 16" and washout for E.T.S.
40 |  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Installed ETS 2 feet from curb on Notrh side of Smith Ranch Rd. has line marker beside it. Installed 2 leads in ETS box.
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | San Rafael | Dug up main at end of circled fence by main marker for depth check for state
40 | 98-05009-1 |  |  | 6 | Transmission |  | Fitting |  |  | Construction Defect |  | 1998-06-10 | 1999-05-28 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | San Rafael | Teflon tape threads & tighten cap on 21/2" HP. Save-a-valve
|  |  |  | 16 | [11 empty] | Steel/Wrought Iron |  | San Rafael | Cont. dug over/under 16" depth to install sewer lat.
4 | 00-00000-0 |  |  | 12 | Transmission |  | Other |  |  | Other |  | 1982-10-05 |  | OTHER |  | Steel/Wrought Iron |  |  | Found single wrap on PGE Transmission main scoggy and flaky. Also the SNT II separator as mad indicates its only 3' apart from 2' distribution main
40 | 78-00316-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-06-22 | 1978-06-22 | Patch Welded |  | Steel/Wrought Iron |  | San Rafael | This rock are likely to cause further. Vented patch welded on by G.C. Welder 44' N/E of HPR tightened leaking service tee cap of an abandoned service
| 00-00553-1 | LINCOLN 16 DFM |  | 16 | Transmission |  | Body of Pipe |  |  | Digin |  | 2000-08-17 | 2000-08-17 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | San Rafael | On 16" Trans, main. Pedro Rd, 23' off P/L-installed 18" long sleeve.
[16 empty] | Steel/Wrought Iron |  | San Rafael
[12 empty] | 1989-05-16 | [6 empty] | SO, Tie-in on GM4529442
[18 empty] | San Rafael | Installed 6-5 box for ETS and (2) 32# MCG Anode
| 79-03269-F |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-08-20 | 1979-09-05 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | San Rafael | 10% Percent flame out of base of utility pole at pl. No reading. Welded patch on main 76' from
4 | 80-03134-1 |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1980-03-04 | 1980-04-16 | Other |  | Steel/Wrought Iron |  |  | 1.2.% gas reasing 1.2+% out vent and lid of box odorof gas present. Checked and cleaned 4/23/80; Tightened flared fitting with special tubing wrench. Leak was in downstream 3/4" static line.
40 | 73-00069-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-02-15 | 1973-11-16 | Patch Welded |  |  |  | San Rafael | Installed 12x12" 360 clamp over corrosion pit. Installed weld patch over leaks & pits, inst anodie.
| 75-00541-1 |  |  | 0.75 | Other |  | Fitting |  |  | Material Failure |  | 1975-10-09 | 1975-11-12 | Other |  | Steel/Wrought Iron |  | San Anselmo | Plgged off tee and dope and tightened cap. Cap on abaandoned per leaking.
4 | 80-03149-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1980-03-10 | 1980-08-08 | Clamp |  | Steel/Wrought Iron |  | San Rafael | Poor condition. No sjw 8/18/80 to research for possible replace pl 08/15/80. No precious leak history this area, not feasable at this time.
| 75-00436-1 |  |  | 8 | Transmission | F-Distribution Feeder Main | Body of Pipe |  |  | Corrosion |  | 1975-07-30 | 1976-02-17 | Patch Welded |  | Steel/Wrought Iron |  | San Rafael | Weld vent patch
4 | 79-03272-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 08/21/0197 | 1980-01-25 | Clamp |  | Steel/Wrought Iron |  | San Rafael | Installed one 8x12" leak clamp. Installed #9 anode.
4 | 79-03272-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 08/21/0197 | 1980-03-12 | Patch Welded |  | Steel/Wrought Iron |  | San Rafael | Patch welded 8" transmission main. Installed #9anode and E.T.S at location below.
4 | 80-00447-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1980-12-12 | 1981-08-13 | Clamp | PERMANENT, COLUMN; CLAMP | Steel/Wrought Iron |  | San Rafael | The leak must be repaired before 11/31/81. Found 8" leak clamp leaking due to winter. 14" failure, installed 8" full circle clamp over leakinfg pit at location below. Main in poor shape; Found 8" dresser coupling in excurtion that is corrected badly
4 | 80-00445-1 |  |  | 8 | Distribution Feeder Main |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1980-12-12 | 1981-06-16 | Other |  | Steel/Wrought Iron |  | San Rafael | This leak must be repaired before 11/30/81. Found 1" plug leaking on a vented patch. Doped plug- and re-tightened at location below; Main has been patched 3 times at this location also.
4 | 81-00222-1 |  |  | 8 | Distribution Feeder Main |  | Physical/Mechanical Joint |  |  | Material Failure |  | 06/11/0198 | 1981-06-16 | Other |  | Steel/Wrought Iron |  | San Rafael | 10% flamed out in probe holes over 8" marked in yellow paint.
| 80-00446-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1980-12-12 | 1981-05-11 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | San Rafael | This leak must be Repaired before 11/30/1981; Installed 61' of 8" Steel to make repairs.
4 | 80-03256-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1980-06-17 | 1980-12-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | San Rafael | 1% reading in patch in front of 1566.% around curb and patch in front #1564 patch mark in yello paint slight over; Flame out in probes holes marked in yellow; This leak must be repaired before 05/01/1981; Found 2 leaking pits on 8" Lincoln line both pits patched just #9 anode on main.
4 |  |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1980-11-25 | 1980-12-09 | Patch Welded |  | Steel/Wrought Iron |  | San Rafael | Found 2 leaking pits on 8" Lincoln line, Both pits patched note location below. Also 9# anode was installed on main; Main in bad shape, haevy pitlink all over main in this area. Potentially more leakage can be expected here should be considered for replacement A.S.A.P.
| 84-00131-1 |  |  | 3 | Distribution Main |  | Valves |  |  | Other |  | 1984-04-05 | 1984-05-18 | Other |  | Steel/Wrought Iron |  | San Rafael | 10% In yellow marked pacth in intersection above gas valve; This leak must be repaired before 04/01/1985; Grease 3" H.P. Valve in Street area
[12 empty] | 1989-05-16 | [6 empty] | North 16"-12" tie in on GM4529442
40 | 98-05014-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1998-06-19 | 1999-04-06 | Clamp |  | Steel/Wrought Iron |  | San Rafael | At D/W TD #191 Deer Park 3' N/O mueller Inst. (1) 3" skinner clamp (1) 3" 360 SS. Clamp over Corr. Pitts; 12" apart 3' from Mueller.
40 | 99-00311 |  |  | 3 | Distribution Main |  | Fitting |  |  | Other |  | 1998-06-19 | 1999-06-08 | REPLACE PIPE |  | Steel/Wrought Iron |  | San Rafael | cut out sleeved fittings & pit on Main 5'; Cut out 5' of 3' with tope tapes & saver valves due to sleeves fitting leaking.
40 | 93-00240-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1993-09-29 | 1993-12-02 | REPLACE PIPE |  | Steel/Wrought Iron |  | San Rafael | Replaced Svc to #11 Castlewood Drive
40 | 74-00684-1 |  |  |  | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-12-23 | 00/00/1975 |  |  | Steel/Wrought Iron |  | San Rafael | Repaired by crew
| 88-2931-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1988-08-02 | 1988-08-07 | REPLACE PIPE |  | TR 418 |  | San Rafael | Install 1/2" Repair couplings; 7' from meter set #292 margarita san rafael.
[18 empty] | San Rafael | 2" TO 3' PL. TO PL. TIE IN.
|  |  |  | 200 | Distribution Main | [10 empty] | TR 418 |  | San Rafael | Tie-in 2" plastic main in park to existing 2" plastic on Rivera Dr.; TR-418 PL in excellent shape.
|  |  |  | 6 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | San Rafael | Tie-in 2" plastic main to 6" STL main.
4 |  |  |  | 200 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  |  | 1983-10-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | San Anselmo | Not a dig in per Sat. crew; Saturday crew responded to Dig-In. I only made repairs to give customer service (FL); See new S.D. #11358 for details and sketch; This inspection is only for 2" STL gas main; 2" gas main will be a future problem! Crew Inserted 46' of 1/2" Nipak PL. pipe through 3/4" STL. "3/4" Mueller weld & 1/2" buzz nut 46' out from riser.
40 | 75-00118-1 |  |  | 0.34 | Service |  | Body of Pipe | Valves |  | Corrosion |  | 1975-03-04 | 1975-03-12 | Clamp |  | Steel/Wrought Iron |  |  | Service to #82" w/w/pl.
| 76-00143-1 |  |  | 0.5 | Service |  | Other |  |  | Construction Defect |  | 1976-03-04 | 1976-06-07 | Replace Pipe and/or Service |  | Copper |  | San Anselmo | Broken solder joint inst 1'1/2" pl continental fitting 1 type-"k" amp fitting (transition)
| 82-00238-1 |  |  | 0.75 | Other | Housing | Body of Pipe |  |  | Corrosion |  | 1982-06-16 | 1982-09-16 | Other |  | Steel/Wrought Iron |  |  | 10% in water box in sidewalk marked in yellow;
San Anselmo
| 81-00297-1 |  |  | 0.5 | Service |  | Other |  |  | Construction Defect |  | 1981-07-27 | 1981-08-03 | Replace Pipe and/or Service |  | Copper |  | San Rafael | 10% gas odor very strong over serv. tee. meter
4 | 80-00146-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1980-04-02 | 1980-04-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | S.D. 6317-HH completed-4-7-80; Cut of 4' pipe and renew service #6317 HH no address.
|  |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  |  |  | Clamp |  | Steel/Wrought Iron |  | San Rafael | Area of inspection; screwed ftg pipe existing couplings; wrapped aqua seal around pipe then weaped electric tape around aqua seal.
40 | 72-00220 |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1972-04-06 | 1972-05-15 | Other |  |  |  | San Rafael | Pipe from drip
| 75-03735-1 |  |  | 3 | Distribution Main |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1975-12-19 | 1976-09-24 | Other |  |  |  | San Rafael | New leak tag made 10/06/76 DW; O bell hold clear, but still make leakage ziegler 09/27/76; S7E7 10% water box; Class2 10% at patch in front of W/B. Ziegler 07/26/1976; PT UG in area; Tightened UG n. coupling on main service #139; Tightning in coupling.
4 |  |  |  | 1 | Service | [7 empty] | 1983-11-08 | Replace Pipe and/or Service |  | Copper |  | San Rafael | SEE S.O. # 6365 N.M. FOR INFORMATION; Crew utilized existing 1" Cu. c/o at PR using one 1" x 1" white coupling & 1' mipak PL to 1"x1 1/4" amp fill coupling for service tie-in.
40 | 72-00709-1 |  |  | 0.75 | Other | 5 Unsused stub | Body of Pipe |  |  | Corrosion |  | 1972-11-17 | 1972-11-22 | Other | Cut-off at main | Steel/Wrought Iron |  | Santa Rosa | 10% gas on service or on unused stub; Found 3/7" stub leaking under driveway. Cut-off unused 3/4: stub at main.
40 | 74-00571-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | CORROSION |  | 1974-08-29 | 1974-10-07 | Patch Welded |  | Steel/Wrought Iron |  |  | Per Zegler (leak #74-418); Reading on main feeder to South Marin. Two flame outs.
| 75-03721-1 |  |  | 0.74 | Other | Meter set | Physical/Mechanical Joint |  |  | Construction Defect |  | 1977-04-01 | 1977-04-01 | Other | Tightened | Steel/Wrought Iron |  |  | Repaered amall leaks on meter set @ #29 Bungalow, S.L.
| 77-00159-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1977-04-15 | 1977-05-26 | Replace Pipe and/or Service |  | Other |  |  | Repaired static gauge line with new stl. tubing
| 78-00373-1 |  |  | 2 | Service | M-Distribution Main | Body of Pipe |  |  | MATERIAL FAILURE | CORROSION | 1978-08-23 | 1978-08-25 | Replace Pipe and/or Service |  | Copper | S-steel and/or wrought iron | San Rafael | Repaired-coupling leaking. HT tee inst. 2-2" repair clamps on main
| 78-03384-1 |  |  | 1.25 | Other |  | Tap Connection |  |  | Material Failure |  | 1978-11-27 | 1979-06-20 | Other |  | Steel/Wrought Iron |  | San Rafael | At large patch at begin of drive way.
| 80-03258-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1980-06-17 |  | Other |  | Steel/Wrought Iron |  |  | 10% flame-out INET.S box in curb. Across from #109 woodland. no leaks around reg. pit. No gas-clear 11/21/1980
| 82-00291-1 |  |  | 10 | Transmission |  | Valves |  |  | Other |  | 1982-07-13 | 1984-05-08 | Other |  | Steel/Wrought Iron |  | San Rafael | .02% valve box in front of 108 woodland ave. by reg station; 2% in area of probe hole marked yellow with arrow; No readings at this time 6/14/84;
| 84-00124-1 |  |  | 0.75 | Service |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1984-03-29 | 1984-04-13 | Other |  | Steel/Wrought Iron |  | San Rafael | .5% in splice box south edge of driveway; No reading this time; Tightened down stream connection at H.P.R. No other leaking
4 | [17 empty] | San Rafel
San Rafael
San Rafael
40 | 97-05006-1 |  |  | 10 | Distribution Feeder Main |  | Girth Weld |  |  | Construction Defect |  | 1997-06-16 | 1998-06-10 | Patch Welded |  | Steel/Wrought Iron |  | San Rafael | Weld at base of service tee leaking. Pinned svc and reweld svc. tee
40 | 76-02105-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-05-13 | 1976-07-08 | Clamp |  | Steel/Wrought Iron |  |  | 100' w/o corte comoda-on S.F.D. ; 600 PPM no bar test;
40 | 71-00061 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1971-03-22 | 1971-03-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Kentwoodland | Replace Serv; The above 3/4" steel gas service, should be reuse when ever possible. This complete service has minor leakage checked 3/22/71
40 | 71-469 |  |  |  | Distribution Main |  | Fitting |  |  | Material Failure |  | 1971-09-09 | 1971-11-17 |  |  | Steel/Wrought Iron |  | Green Brae | Turn into mecanic for repair and change of meter set at bldg.
| 77-00534-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1977-11-23 | 1977-12-13 | Clamp |  | Steel/Wrought Iron
| 77-00534-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1977-11-23 | 1977-12-13 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Larkspur
| 78-00231-1 |  |  | 16 | Distribution Feeder Main |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1978-04-20 | 1978-04-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Removed part that was leaking and replaced with new piece of pipe (64")
|  |  |  | 16 | Distribution Feeder Main |  | Other | [8 empty] | Steel/Wrought Iron |  | Larkspur | Pipe not shift or pull apart when pipe was cut.; 16" gasket was removed for inspection. Visual inspection indicate no damage to gasket.
40 | 88-00151-1 |  |  | 6 | Distribution Feeder Main |  | Fitting |  |  | Material Failure |  | 1988-04-29 | 1989-03-22 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | LK | Welded 12" over leaking kerotest insulating fitting.
| 90-00110-1 |  |  | 0.75 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1990-03-07 | 1990-03-07 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Larkspur | Welded 2" sav-a-va;ve over 1/2: tap.; Welded over leak.
4 |  |  |  | 2 | Distribution Feeder Main | [7 empty] | 1981-09-08 |  |  | Steel/Wrought Iron
40 | 74-03035-1 |  |  | 0.75 | Other |  | Fitting |  |  | Material Failure |  | 1974-04-09 | 1974-04-22 | Other |  | Steel/Wrought Iron |  |  | Meter in sidewalk; Found .7% in curb meter box. Vent to go pp no oder; Curb meter ftgs leaking in box. abandoned 1/2 pl srvc. at main as this meter is no longer in service. Cust confronted to all elect appliances 1/14/" pl main run through curb box. Removed meter.
| 75-02147-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | CORROSION |  | 1975-04-18 | 1975-07-16 | Clamp |  | Steel/Wrought Iron |  |  | 80% lel water box; Per clamp. Rechecked with flames. Found reading per cans. Its not as hot as before so maybe need to vent out.
79-00285-1 | 79-00285-1 | [10 empty] | 1979-08-14 | 1979-11-02 |  |  |  |  | Mill Valley | See LK tag #79.003371; This leak was cleaned do to repairs on LK tag
|  |  |  | 10.75 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1975-02-15 | 1975-05-08 | Patch Welded |  | Steel/Wrought Iron |  |  | No leakage. Pipe damage only; Note: Pipe is exposed across creek bullet. Dent was patched with a piece of "6"x6"x.365" wt plate
[18 empty] | Mill Valley | Debth Check
[18 empty] | Mill Valley | Debth Check
[18 empty] | Mill Valley | Debth Check
| 90-80029-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1990-06-07 | 1990-06-07 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Mill Valley | Delded 10"x12" sleeve over damaged section
| 82-00088-1 |  |  | 0.75 | Service |  | Fitting |  |  | Corrosion |  | 1982-02-16 | 1982-06-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Corde Madera | 3/4" Elbow leaking on H.P. side of H.P.R. No odor present.; Service replaced
| 00-00420-1 |  |  | 0.75 | Transmission | HPR | Regulator |  |  | Damage by Natural Forces |  | 2000-05-17 | 2000-05-17 | Other | Replaced Reg | Steel/Wrought Iron |  | Corte Madera | Installed new fisher 627 3/4" HPR reg feeding single service; Called out by service man to HPR leaking in curb box. Found broken bolt on reg. Replaced Reg with new fisher 627-3/4" reg with 3/16" orfice and set at 30PSIG and pop off (H202) at 45PSIG
4 | 79-00359-1 |  |  | 0.5 | Distribution Feeder Main |  | Girth Weld |  |  | Material Failure |  | 1979-10-08 | 1979-10-25 | Replace Pipe and/or Service |  | Copper |  | Mill Valley | 10% Flames-out in probe hole over service tee and main service to 6 oz Edgewood. 7% in probe hole by service tee to 600 marked in.; Install buzz nut on service #602 and install anode.
40 | 71-00649-1 |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-11-29 | 1971-11-29 | OTHER |  | Steel/Wrought Iron |  | Mill Valley | SEE S.O. 23704; Abandon 3/4" steel stub that was leaking; Stub can't be used due to concrete wall.
| 74-00698-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-12-26 | 1975-01-17 | Clamp |  |  |  | Mill Valley | No Gas Reading; Center punched weld; Intalled clamp & anode on 3/4" abandoned STRV.
| 76-03395-1 |  |  | 0.5 | Service |  | Fitting |  |  | Construction Defect |  | 1976-12-17 | 1984-03-06 | Other |  | Other Plastic |  | Mill Valley | .03% Service tee; .5% over serv same tee; .1% in same area; .2% between sidewalk & street D.D; Cap was leaking reopen and tighten; Pipe is in good condition.
4 | 80-00467-1 |  |  | 0.5 | Service |  | Fitting |  |  | Material Failure |  | 1980-12-23 | 1980-12-23 | Other |  | Copper |  | Mill Valley | Eliminated leaks; See New Service Order on work done; Cu Servvice is in good shape; Squeezed 1/2" service and pulled fitting apart, cleaned and doped to eliminate leak, referred to Eng. for relocating service!
40 | 71-00217 |  |  | 0.75 | Other |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1971-04-19 | 1971-04-20 | Other |  | Steel/Wrought Iron |  | Mill Valley | No leak on Service, 3/4" plug was not tight in coupling on main where old service was abandoned.
| 77-03378-1 |  |  | 0.75 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1977-09-02 | 1980-03-25 | Other |  | Steel/Wrought Iron |  | Mill Valley | 10% Stopecock leaking badly; .05 same 6-6-78; Soaped meter found it was leaking under Reg needs to be redoped; Rep'd fittings & metar; Not exposed; 4-2-80.
| 76-02187-1 |  |  | 3 | Distribution Main | [6 empty] | 1976-07-16 |  |  |  | Steel/Wrought Iron |  | Mill Valley | Clear at this time.
| 76-00345-1 |  |  | 3 | Distribution Main | [6 empty] | 1976-06-23 |  |  |  | Steel/Wrought Iron |  | Mill Valley | Clear at this time 7-23-76; PT UG NO;
| 76-02182-1 |  |  | 2 | Distribution Main | [6 empty] | 1976-07-16 |  |  |  | Steel/Wrought Iron |  | Mill Valley | Readings to mall for crew 8-26
| 76-02183-1 |  |  | 2 | Other | [6 empty] | 1976-07-16 |  |  |  | Steel/Wrought Iron |  | Mill Valley | Readings to small for crew 7-28-76; No reading over main or service.
| 76-02180-1 |  |  | 0.75 | Distribution Main | [6 empty] | 1976-07-15 | 1976-07-23 |  |  | Steel/Wrought Iron |  | Mill Valley | St. Overlay. In front of #128 Reed - 200 PPM. Liegler readings too small for leak crew: No repairs...
4 | 80-00397-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1980-11-05 | 1980-11-05 | Clamp |  | Steel/Wrought Iron |  | Mill Valley | Clear; Gas leak was at the west side of house on riser; Installed 3/4" clamp on riser, wrote up service order for replacement "see S.O.# for information."
4 | 80-00397-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1980-11-05 | 1980-11-05 | Clamp | PERMANENT, COLUMN; REPLACE PIPE AND/OR SERVICE | Steel/Wrought Iron |  | Mill Valley | Leak on riser; S.O. 6825-BO RERUN; Gas leak was at west side of house on riser; Intalled 3/4" clamp on riser, wrote up service order for replacement "see S.O.# for information."
4 | 79-03289-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-08-23 | 1980-02-26 | Patch Welded |  | Steel/Wrought Iron |  | San Rafael | Patch welded 8" main that was leaking. Installed anode on main at location below. Patch is in the same area. 4" main in same general area approx 2' north of 8 " T.P. main 22" deep, next to or inside island.
4 | 84-00220-1 |  |  | 8 | Distribution Feeder Main |  | Other Welds |  |  | CONSTRUCTION DEFECT |  | 1984-06-21 | 1985-04-16 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | San Rafael | Main dives 2' with 4h degree bend 4' east of leak 90 degrees ELL. Repaired cold lap on 90 degree bend heading toward Margarita Dr. made arc weld pass of over old arc weld cold lap to make repairs.
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | San Rafael | INSTALL E.T.S.; 48' N/N/L San Pedro Rd on Manderly; Installed ETS Box Cad welded 2 wire on 8" &2 wires on 4" mains in same box.
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | San Rafael | Intersection Manderly and Locksly San Rafael: Installed ETS box. Cleared contact with 6" C.I. water main. Installed E.T.S. Box. Cad welded 2 wires on 8" main and 2 wires on 4" main. Used same box.
40 | 97-05015-1 |  |  | 8 | Distribution Feeder Main |  | Girth Weld |  |  | Corrosion |  | 1997-06-19 | 1998-09-15 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | San Rafael | INSY 12" CAN OVER WELD
40 | 71-00010 | [10 empty] | 1971-02-12 | [5 empty] | Tiburon | No readings; Customer smelled gas once but...???
40 | 7 |  |  | 12 | Transmission | [6 empty] | 1971-12-29 |  |  |  | Steel/Wrought Iron |  |  | Pipe Exoposed
4 |  |  |  | 12 | Transmission | [12 empty] | Tiburon | Installed E.T.S. Station; 135' N/N PL via Los Altos; Sand & Rock.
4 | 79-00187-1 |  |  | 0.5 | Other |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1979-05-03 | 1979-09-25 | Other |  | Other Plastic |  | Tiburon | Found 1/2" continental D/E cupleaking. Replaced it with 1/2" PL Amp. Fit. D/E at location, 9' W/S Edge of Electrical Box, 8' W/N Edge of Electrical Box; There are 2 1/2" continue service tees in the hole. One 3/4" service tee for 3S Andrew Drive, (Branch Service) and 2" toptap, *Note locacation above.
13 |  |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1993-04-29 | 1994-02-04 | Clamp |  | Steel/Wrought Iron |  | Mill Valley | Dug bell hole over a large corrosion pitt. Installed a 2" 360 deg clamp for repairs
4 | 81-00116-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1981-03-19 | 1981-03-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Mill Valley | See attached service order; See new service for work proposed.
40 |  |  |  | 2 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Mill Valley | Main in good condition.
4 |  |  |  | 0.5 | Service | [7 empty] | 1980-12-09 | Replace Pipe and/or Service |  | Other Plastic |  | Tiburon | See New Service Record; 45' N/N/PL Linda Vista noa maintenance county incl.; Dig-up 3/4" stL pipe 15' Alum ? riser in dirt area cut ou section to ??? 1/2" PL. Performed work in riser at meter set. Bid service ??? with one 1/2" continental coupling.
|  |  |  | 2 | [7 empty] | 1967-12-26 | 1970-05-22 | Tighten Cap or Bolt |  | Steel-Other |  | TIBURON
40 | 76-00225-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  |  | 1976-07-15 | Clamp |  | Steel/Wrought Iron |  | Tiburon | Inst 360 deg. leak clamp 9' line.
| 73-00274-1 |  |  | 0.75 | Other |  | Fitting |  |  | Material Failure |  | 1973-07-02 | 1973-07-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | S.O. #32919; Repaired 2 leaks on H.P. nipple on 4 M.F.D.
40 | 78-00057-1 |  |  | 0.75 | Other |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1978-01-22 | 1978-10-27 | Other |  | Steel/Wrought Iron |  | Sausalito | No leak odor; Repaired two leaks on service meter set S.O. - 29040.
|  |  |  | 2 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Sausalito
45 |  |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1980-10-09 | 1980-10-09 | Clamp |  | Steel/Wrought Iron |  | Sausalito | Made temporary repairs on riser, service must be rerun, turned in service order for replacement.
4 | 80-00014-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1980-01-10 | 1980-02-05 | Other |  | Steel/Wrought Iron |  | Sausalito | Cut off 12' pipe at deep ens 3-28-80
| 82-00405-1 |  |  | 0.5 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1982-11-18 | 1982-11-18 | Other |  | Copper |  | Sausalito | Dig in on copper stub hit old squeeze with shavel and sipped it open. Cut off Squeeze, left 2" of copper coming out of tee and install dead end.
|  |  |  | 2 | Distribution Main |  |  |  |  | Corrosion |  | 1968-01-23 | 1968-01-25 |  |  | Steel-Other |  | SAN RAFAEL | INSTALLED BOILER PLUG INTO LEAK HOLE. INSTALLED 2" LEAK CLAMP OVER HOLE AND BOILER PLUG. SEAM ON MAIN LOOKS BAD. VERY BAD PITS ON MAIN. NO WRAP LEFT ON MAIN. I WOULD SAY THAT THIS MAIN SHOULD BE RENEWED. CLAMP WILL OUTLAST GAS MAIN. MAIN REPLACED BY GM 442846 1968.
|  |  |  | 2 | Distribution Main |  |  |  |  | Corrosion |  | 1968-01-23 | 1968-01-25 |  |  | Steel-Other |  | SAN RAFAEL | INSTALLED BOILER PLUG INTO LEAK HOLE. INSTALLED 2" LEAK CLAMP OVER HOLE AND BOILER PLUG. SEAM ON MAIN LOOKS BAD. VERY BAD PITS ON MAIN. NO WRAP LEFT ON MAIN. I WOULD SAY THAT THIS MAIN SHOULD BE RENEWED. CLAMP WILL OUTLAST GAS MAIN. MAIN REPLACED BY GM 442846 1968.;
| 04-00033-1 | 0401-13 | 0.8 | 8 | Distribution Main | Transmission | Other |  | FLANGE | Construction Defect |  | 2004-01-31 | 2004-02-03 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Corte Madera | At flange; ETS/valve/sewer flange @ ETS; Replaced bolts, tested ins. sleeves - ok.
| 07-00012-1 | 21G |  | 0.75 | Service |  | Regulator |  |  | Unknown |  | 2007-01-15 | 2007-01-19 | Other | REPLACED REGULATOR | Steel/Wrought Iron |  | Novato | In spiice box containing high pressure regulator; replaced regulator; S.O.# 45890 & 45895; T&R fIXED leak on regulator
| 09-20199-1 |  |  | 0.5 | Single Service |  | Unknown |  |  | Unknown |  | 2009-12-02 | 2009-12-02 | Replace Entire Service |  | PE2406 (Yellow or Orange) |  | Corte Madera | Base of riser & out 2'-service fed of H.P.R; Pulled out existing 1/2" PL and in teel 3' of 1/2" PL w/ non corrodible riser; See S.O.#9992
| 09-20011-1 |  |  | 0.75 | Branch Service |  | Other |  | THREADS BELOW VALVE | Unknown |  | 2009-01-14 | 2009-01-14 | Other | change valve | Steel/Wrought Iron |  | San Rafael | Base of service valve; Threads below valve; Changed valve
40 | 10-00215-B |  |  | 4 | Distribution Main |  | Other Mechanical Joint |  |  | Other | Loose bolts | 2010-12-01 | 2010-12-01 | Tighten Cap/Bolt - Fitting |  | Steel |  | San Rafael | 18% in valve box 0-21; Blew off flange; dug hole-leak on pinoff tee not on valve; no changes 1/18/11,
| 10-00118-1 | X6897 OR 0401-01 | 0 | 6 | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2010-03-03 | 2010-03-03 | Other | Replace corroded grease stem | Steel/Wrought Iron |  | Greenbrae | 0-94; new leak #10-00119; not needed as grease stem was attached to valve; replace corroded grease stem; pipe not inspected; Found corroded & leaking grease stem; Removed & replaced with 1/2" stainless tubing. Greased and operated valve; Leaking x tie valve 0-94 aka 5.17
| 10-20202-1 | 21 | 19.93 | 12 | Transmission |  | Valves |  |  | Other | Cracked Gasket | 2010-11-06 | 2010-11-07 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Terralinda | Flange at valve box T45; See 10-00392 PRR; Tightened Plug, greased vlv., change flange gasket & bolts on B/O vlv.
40 | 11-20100-B | [10 empty] | 2011-04-28 | [5 empty] | San Rafael
| 11-20039-B |  |  | 4 | Distribution Main > 60 PSIG |  | Line Valve |  |  | Construction Defect |  | 2011-02-07 | 2011-02-07 | Tighten Cap/Bolt - Fitting |  | Steel |  | San Rafael | Tightened bolts on flange valve; Reg pits; 1-66 tightened flange bolts on valve #I-66
40 | 11-20044-A |  |  | 0.75 | Distribution Main > 60 PSIG |  | THREADS |  | THREADS | CONSTRUCTION DEFECT |  |  | 2011-02-12 | REPLACE PARTIAL SERVICE
40 | 11-20100-B |  |  |  | Transmission |  | Other |  |  | No/Deteriorated Pipe Dope |  | 2011-04-28 | 2011-04-28 | Tighten Cap/Bolt - Fitting |  | Steel |  | San Rafael | Put new dope on plug and cap of pin off tee.
40 | 11-20039-B |  |  |  | Distribution Main >60 PSIG and <20% SYMS |  | Line Valve |  |  | Construction Defect |  | 2011-02-07 | 2011-02-07 | Tighten Cap/Bolt - Fitting |  | Steel |  | San Rafael | Tightened bolts on flange valve
40 | 11-20044-A |  |  | 0.75 | Distribution Main > 60 PSIG |  | THREADS | Threads | THREADS | Construction Defect |  | 2011-02-12 | 2011-02-12 | Replace Partial Service |  | Steel |  | Mill Valley | removed & Replaced corroded & Leaking piping, fitting, & reg.; Repaired HPR. multiple leaks with atmospheric corrosion. Replaced with new piping & equipment
40 | 11-20100-B |  |  | 16 | Transmission |  | Other |  |  | No/Deteriorated Pipe Dope |  | 2011-04-28 | 2011-04-28 | Tighten Cap/Bolt - Fitting |  | Steel |  | San Rafael | Put new dope on plug and cap of pin off tee
|  |  |  | 0.75 | Service |  | Body of Pipe |  |  | External Corrosion |  | 1998-12-31 | 2000-05-23 | Other | FULL CIRC CLAMP | Steel/Wrought Iron |  | St. helena | Installed full circle clamp
| 99-20018-1 |  |  | 6 | Transmission |  | Physical/Mechanical Joint |  |  | Damage by Natural Forces |  | 1999-12-12 | 2000-12-19 | Other | CAN | Steel/Wrought Iron |  | Napa | 30ft South of Creek at driesser coupling shown on the map; Weld can over leaking
| 00-40039-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Digin |  | 2000-06-12 | 2000-06-12 | Other |  | TR 418 |  | Napa | 2" stub; Replaced dead end cap
| 99-60001-1 |  |  | 1.25 | Service |  | Plastic Tee Cap |  |  | Unknown |  | 1999-09-09 | 2001-02-05 | Other | Adyl "A" repair cap | Aldyl A (Tan or Gray) |  | St. Helena | Install Adyl "A" plastic tee. Repair cap
|  |  |  | 0.5 | Service |  | Other |  | Riser kit | Unknown |  | 2001-03-21 | 2001-03-21 | Service Partially Replaced |  | TR 418 |  | Napa | Replaced riser kit & 2" of 1/2" plastic
|  |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  |  | 2011-02-27 | Mechanical Repair Fitting - Fitting |  | TR 418 |  | Napa | Installed 2-1/2" Coupling and approx. 4" to 6" 1/2" 2 pipe
01-20060-1 | 01-20050-1 | DFM | 12.1 | 6" | Distribution Main | Main | Body of Pipe |  |  | External Corrosion |  | 2001-10-27 | 2002-09-09 | Other |  | Steel/Wrought Iron |  | Napa | Installed 2,000lb repair sleeve (Bolt-On)
| 02-008-1 |  |  | 0.25 | Transmission |  | Tap Connection |  |  | Vehicle |  |  | 2002-02-20 | Other | REPLACED VENT STACK & RECORDER | Other | SS |  | Shut off valve & replaced; Car dorve into vent stack and recorder
| 02-00010-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Digin |  | 2002-03-11 | 2002-03-11 | Replace Dist Main < 100 ft |  | TR 418 |  | Napa | Installed two plastic couplings & 2' of new plastic
|  |  |  | 4 | Transmission |  | Other Welds |  |  | Other | Bad weld | 2003-05-15 | 2003-05-19 | Patch Welded |  | Steel/Wrought Iron |  | St. Helena | Steel pin svc tee, Grid out bad weld, re-welded
| 03-00025-1 |  |  | 0.75 | Service |  | Girth Weld |  |  | Construction Defect |  | 2003-02-21 | 2003-02-21 | Patch Welded |  | Steel/Wrought Iron |  | Deepark | Welded over leak
| 02-20011-1 |  |  | 2 | Transmission |  | Valves |  |  | Unknown |  | 2002-06-08 | 2003-01-03 | Other | GREASE VALVE | Steel/Wrought Iron |  | Yountville | No digging, valve only; Middle sidewal V102 give to Gamba to grease valve; Inserted valve with selant
| 02-20012-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Unknown |  | 2002-05-09 | 2003-01-03 | Other | grease valve | Steel/Wrought Iron |  | Napa | At Inlet valve to reg 88 this goes to gamba; Inserted valve with sealant; grease valvel; In Reg station
|  | 215 | 2.2 | 215 | Transmission |  | Physical/Mechanical Joint | Other | FLANGE | Other | Loose bolts | 2003-07-14 | 2003-08-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Napa | @ Valve # 2.20 and 2.21 on east side of valves; @ MLV 2.21; On blow off valve B replaced bolts on 6" flanged valve; Leak on flange, replaced all flange bolts
| 05-00033-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 2005-06-09 | 2005-06-09 | Service Partially Replaced |  | TR 418 |  | Napa | pm 40506445; GSR cisneros; Repl 365' or 1/2" PL 272' from riser
|  |  |  | 0.75 | Service |  | Other |  | cap | Construction Defect |  | 2005-06-20 | 2005-06-20 | Tighten Cap or Bolt | OTHER | Steel/Wrought Iron |  | Napa | E/S PN7 driveway 254' N/O golden gate; Over service tee to HPR; Redope & tighten service tee cap
|  | 21 |  | 0.75 | Service | Transmission | Other |  | BROKEN THREADS | Other | CAR DROVE OVER BOX | 2005-09-22 | 2005-09-22 | Other | TEMP. REPAIRS REBUILD SET WITH THREADED PIPE | Steel/Wrought Iron |  | Napa | Car drove over box; Temp repairs, rebuild set with threshold pipe; Car drove over box and broke threads off of valve, Box is sunk and needs new HPR; Al thresded fittings
| 06-00087-1 | DFM |  | 6 | Transmission |  | Fitting |  |  |  |  | 2006-10-10 | 2006-10-11 | Replace TP Main |  | Steel/Wrought Iron |  | St. Helena | Replaced 6' by 6" stl gas pipe; Contractor dug into 2' TP stub off on 6" TP main
| 06-00061-1 |  |  | 0.75 | Single Service |  | Fitting |  |  |  |  | 2006-06-20 | 2006-06-20 | Other | Replace H.P.R. | Steel/Wrought Iron |  | St. Helena | Replaced HPR box, fitting and regulator in box
| 06-00013-1 | DFM | [9 empty] | 2006-02-03 | [5 empty] | St. Helena | In HPR box
| 06-00011-1 |  |  | 0.75 | Service |  | Valves |  |  | Other | No grease | 2006-01-31 | 2006-02-28 | Other |  | Steel/Wrought Iron |  | St. Helena | Cutt-off abandoned HPR at main
| 06-00013-1 | DFM |  |  | Service |  | Valves |  |  | Other | Grease |  |  | OTHER
| 06-00061-1 |  |  | 0.75 | Single Service |  | Fitting |  |  |  |  | 2006-06-20 | 2006-06-20 | Other | REPLACE H.P.R. | Steel/Wrought Iron |  | St. Helena | Replace H.P.R.; Fittings & Regulator; Contractor drove over exposed & marked HPR box; Replace HPR box & fittings & regulator in box; Contractor drove excavator over HPR BOX, excavator crushed box & cranked fitting inside of box.
[18 empty] | San Rafael | Contractor dug into 2" TP stub off on 6" TP main; Contractor digging to have 2" PL 1-P gas main lowered dug intp 2" DFM stub off 6" DFM main.
| 08-00019-1 | 0406-01 |  | 0.75 | Transmission |  | Valves |  |  | Construction Defect |  | 2008-02-25 | 2008-02-25 | Other | REPLACED GREASE TAP INTO VALVE | Steel/Wrought Iron |  | Napa | Replaced broken grease tap into valve
| 91-00001-1 | 0405-02 | 1.93 | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1991-03-15 | 2009-06-29 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | Angwin | Welded out plidco repair clamp; welded sealed plidco fitting and soap tested; A-Found canned service tee with leaking plug. Welded save-a-valve on end of can to repair; B-Found external corrosionon bottom of pipe. Installed plidco repair clamp. Weld sealed the clamp body. Wrapped and adjacent pipe with wax tape.
| 09-00027-1 | DFM |  | 3/4" | Transmission |  | MECHANICAL JOINT | Mechanical Joint |  | Equipment Malfunction |  | 2009-04-25 | 2009-04-29 | Other | TIGHTENED GREASE FITTING | Steel/Wrought Iron |  | Yountville | Tightened grease fittings
| 09-00028-1 | DFM |  | 3/4" | Transmission |  | Mechanical Joint |  |  | Unknown |  | 2009-04-25 | 2009-04-29 | Other | TIGHTENED REG BODY | Steel/Wrought Iron |  | Napa | Tightened Reg Body
| 09-00029-1 | DFM |  | 11/4" | Transmission |  | Mechanical Joint |  |  | Unknown |  | 2009-04-25 | 2009-04-29 | Other | Tightened valve body | Steel/Wrought Iron |  | Napa | Tightened valve body
| 09-00050-1 | 6040501 |  | 2" | Transmission |  | Other |  | Mueller valve tee | Other | O Ring | 2009-06-04 | 2009-07-03 | Other | REPLACE O RING | Steel/Wrought Iron |  | St. Helena | Replaced leaks on 2" mueller valve tees on inlet of reg sta
| 09-00138-1 | 3801257 |  | 3 | Distribution Main |  | Other Welds |  |  | Construction Defect |  | 2009-11-16 | 2009-11-17 | Patch Welded |  | Steel/Wrought Iron |  | Napa | Welded leaks on 90 5 3"&4" reducer
| 09-00139-1 | 3801257 |  | 4 | Distribution Main |  | Regulator |  |  | Construction Defect |  | 2009-11-16 | 2009-11-17 | Other | SEE REPAIR REMARKS  ABANDON OLD REG #30 | Steel/Wrought Iron |  | Napa | Abandoned old reg #30
| 09-20006-1 | DFM |  | 4 | Transmission |  | Valves |  |  | Unknown |  | 2009-04-18 | 2009-04-20 | Other | Grease valve | Steel/Wrought Iron |  | Napa | Leak on valve packing grease; Operated valve to stop leakage; Sketch is on valve record fm-u-24 located in Vallejo office records gas T.R.
| 02-00071-1 | 6-0406-1 |  | 0.75 | Single Service |  | Regulator |  |  | Unknown |  | 2002-10-17 | 2010-01-27 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Napa | Notified manager on 01/12/10 @1400 ARCO GAS STATION (curb MTR - possible H/L leak); In area around HPR & Valve box; same area slight odor; Middle south side of drvwy @ 198 sosco; (DH) Reg Box; In HPR box; Tighten bolts on regulator
| 09-00022-1 |  |  | 0.75 | Single Service |  | Fitting |  |  | Other | Loose | 2009-04-08 | 2010-07-27 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Napa | (CGT) HPR leaking; HPR leaking 0% w/ CGI; No reading w/ CGI - 2% W/ flamepak; Tighten Cap; Soap rest
| 09-00153-1 | 0405-02 |  | 0.75 | Transmission |  | Other |  | CAP | Other | DOPE ON THREAD DRY | 2009-11-30 | 2010-10-26 | Other | redoped cap tightend | Steel/Wrought Iron |  | Angwin | 660' north on 701 crystal springs (permit); (CGT) O/4" main next to reg 56; (5YR) O/4 main next to reg.56; Cap on tee in reg 56 box; Dope on thread dry; Redoped cap tightend; sketch note: tee cap leak.
| 09-00178-1 |  |  | 4 | Transmission |  | Valves |  |  | Construction Defect |  | 2009-12-02 | 2010-11-30 | REPLACE TP MAIN |  | Steel/Wrought Iron |  | St. Helena | Replace Pipe
| 09-00185-1 |  |  | 0.5 | Transmission |  | Valves |  |  | Other | LOOSE FITTING & VALVE PACKING | 2009-12-07 | 2010-02-09 | Other | TIGHTENED & DOPED FITTING & TIGHTENED VALVE PACKING | Steel/Wrought Iron |  | Napa | Above ground to MTC; Loose fitting & valve packing; Tightened fitting & valve packing;
| 09-00215-1 |  |  | 0.5 | Single Service |  | Plastic Tee Cap |  |  | Construction Defect |  | 2009-12-18 | 2010-03-10 | Replace Partial Service |  | PE2406 (Yellow or Orange) |  | St. Helena | To GC over DRM between Hwy & RR; GT)0/6" TP main & 2" PL Dist Main by utility; Replaced tee with 2" PL;
| 09-20050-1 | 6-0405-06 |  | 3/4" | Service |  | Fitting |  |  | Other | GASKET  O-RING | 2009-12-17 | 2010-08-06 | Other | REPLACED GASKET  ORING | Steel/Wrought Iron |  | St. Helena | Soap test
| 10-00085-1 | 6-0405-6 |  | 0.75 | Transmission |  | Fitting |  |  | Other | Pipe dope dried out | 2010-08-11 | 2010-08-19 | Other | DOPE ON TEE DRIED OUT | Steel/Wrought Iron |  | St. Helena | Pulled cap off teflon tape doped retightened
| 10-30109-1 | 6-0406-1 |  | 0.75 | Transmission |  | Fitting |  |  | Construction Defect |  | 2010-09-10 | 2010-09-10 | Other | REPLACE BLOW-OFF IN HPR BOX | Steel/Wrought Iron |  | Napa | Relaced leaking blow-off in HPR box
43 | 09-00196-1 | 4-0405-01 |  | 0.75 | Branch Service |  | Riser Valve Threads |  |  | Construction Defect |  | 2009-12-14 | 2011-06-13 | Replace Service Valve <2-inch |  | Steel |  | St. Helena | replaced H.P.R. valve. Installed new HPR
43 | 05-00058-1 |  |  | 6 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | External Corrosion |  | 2005-08-19 | 2011-04-04 | Other | PLIDCO CAMP | Steel |  | Yountville | Installed PLIDCO Clamp
43 | 05-00055-1 |  |  | 0.75 | Distribution Main >60 PSIG and <20% SYMS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2005-08-16 | 2011-05-09 | Other |  | Steel |  |  | TOT 9; JST5; CALL BACK 5-25-11; (5YR) HPR; (DH) at HPR; Redope
43 | 09-00218-1 | 0405-01 |  | 0.75 | Distribution Main >60 PSIG and <20% SYMS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2009-12-18 | 2011-05-25 | Tighten Cap/Bolt - Fitting |  | Steel |  |  | (CGT) leak on reg 68 in vault; (5yr) leak on reg. 68 in vault; 3/4" x 1/4" bushing on sense line; Retaped & redope; No changes on latest sketch.
43 | 09-00210-1 |  |  | 1 | Distribution Main >60 PSIG and <20% SYMS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2009-12-17 | 2011-04-29 | Tighten Cap/Bolt - Fitting |  | Steel |  |  | (CGT) Leak on HPR; Leak on tee cap on HPR; High side of HPR on tee cap;Tape & dope & tighten; No change to latest sketch.
43 | 09-00200-1 |  |  | 1 | Distribution Main >60 PSIG and <20% SYMS |  | Other |  |  | Other |  | 2009-12-15 | 2011-04-30 | Other |  | Steel |  |  | Leak on HPR; Replace rubber o-ring; No change to latest sketch.
| 09-20050-1 | [10 empty] | 2009-12-17 | [5 empty] | St. Helena
| 10-81023-1 | DCST6627 | 1 | [8 empty] | 2010-10-09 | [5 empty] | St. Helena | Replaced gas fire. Abandoned reg sta. 67
43 | 10-81040-1 | 0407-01 | 12.74 | [8 empty] | 2010-10-04 | 2010-11-30 | Deactivate #TP Main |  |  |  | Napa | Deactivated main [30777996]; Deactivated 5800 ft of transmission main
43 | 10-81041-1 | 0407-01 | 12.74 | [8 empty] | 2010-10-06 | 2010-11-30 | Deactivate #TP Main |  |  |  | Yountville | Deactivated main [30777996]; Deactivated 5,800 feet pf TP main
| 08-00019-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Construction Defect |  | 2008-02-25 | 2008-02-25 | OTHER | REPLACED GREASE TAP INTO VALVE | Steel/Wrought Iron |  | Napa | Replaced broken grease tap into valve
| 10-20010-1 | 4-0408-1 |  | 00.04" | Transmission |  | Unknown |  |  | Unknown |  | 2010-04-08 | 2010-04-13 | Deactivate #TP Main |  | Steel/Wrought Iron |  | Napa | Cutt off main going to river; Cut & cap main to stop leak in river bank; We were told that 4" ML fitting was or to use because main id back fed from reg at 60 psi
42 | 09-00024-1 |  |  | 3" | Distribution Main >60 PSIG and <20% SYMS |  | Other |  |  | Other |  | 2009-03-23 | 2011-05-04 | Greased - Other |  | Steel |  | Vallejo | Greased; No change to latest sketch
| 09-00142-1 |  |  | 1/2" | Distribution Main >60 PSIG and <20% SYMS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2009-10-12 | 2011-05-04 | Tighten Cap/Bolt - Fitting |  | Steel |  | Vallejo | Dope 1/2" bushing above metric; No change to latest drawing
INSTALLED BOILER PLUG INTO LEAK HOLE. INSTALLED 2" LEAK CLAMP OVER HOLE AND BOILER PLUG. SEAM ON MAIN LOOKS BAD. VERY BAD PITS ON MAIN. NO WRAP LEFT ON MAIN. I WOULD SAY THAT THIS MAIN SHOULD BE RENEWED. CLAMP WILL OUTLAST GAS MAIN. MAIN REPLACED BY GM 442846 1968.;
|  |  |  | 6 | Distribution Main |  |  |  |  | Corrosion |  | 1968-05-11 | 1968-05-17 | Other | PERMANANT WELD AND LEAK CLAMP | Steel-Other |  | San Rafael
| 08-00025-1 | 210 | [13 empty] | Steel/Wrought Iron
| 08-00024-1 | 210 |  | 0.18 | [7 empty] | 2008-03-07 |  |  |  | Steel/Wrought Iron |  | Benicia
| 08-00021-1 | 210 |  | 0.18 | [7 empty] | 2008-03-07 |  |  |  | Steel/Wrought Iron |  | Vallejo
| 08-00020-1 | 210 |  | 0.24 | [7 empty] | 2008-03-06 |  |  |  | Steel/Wrought Iron |  | Vallejo | In reg Pit 29
| 08-00019-1 | 210 |  | 0.24 | [7 empty] | 2008-03-06 |  |  |  | Steel/Wrought Iron |  | Vallejo | In valve VT-30
| 08-00017-1 | 21 |  |  |  |  | Valves |  | UNSURE UNDER WATER | OTHER | NO GREASE | 2008-03-04 | [5 empty] | Vallejo | VT 34 valve
| 08-00016-1 | 21 |  | 0.25 |  |  | Fitting |  |  | Construction Defect |  | 2008-03-04 |  |  |  | Other | Stainless steel | Benicia | Reg Pit 3
|  |  |  | 2 | Distribution Main |  |  |  |  | Corrosion |  | 1968-01-23 | 1968-01-25 |  |  | Steel-Other |  | SAN RAFAEL | INSTALLED BOILER PLUG INTO LEAK HOLE. INSTALLED 2" LEAK CLAMP OVER HOLE AND BOILER PLUG. SEAM ON MAIN LOOKS BAD. VERY BAD PITS ON MAIN. NO WRAP LEFT ON MAIN. I WOULD SAY THAT THIS MAIN SHOULD BE RENEWED. CLAMP WILL OUTLAST GAS MAIN. MAIN REPLACED BY GM 442846 1968.;
|  |  |  | 2 | Distribution Main |  |  |  |  | Corrosion |  | 1968-01-23 | 1968-01-25 |  |  | Steel-Other |  | SAN RAFAEL | INSTALLED BOILER PLUG INTO LEAK HOLE. INSTALLED 2" LEAK CLAMP OVER HOLE AND BOILER PLUG. SEAM ON MAIN LOOKS BAD. VERY BAD PITS ON MAIN. NO WRAP LEFT ON MAIN. I WOULD SAY THAT THIS MAIN SHOULD BE RENEWED. CLAMP WILL OUTLAST GAS MAIN. MAIN REPLACED BY GM 442846 1968.;
|  |  |  | 2 | Distribution Main |  |  |  |  | Corrosion |  | 1968-01-23 | 1968-01-25 |  |  | Steel-Other |  | SAN RAFAEL | INSTALLED BOILER PLUG INTO LEAK HOLE. INSTALLED 2" LEAK CLAMP OVER HOLE AND BOILER PLUG. SEAM ON MAIN LOOKS BAD. VERY BAD PITS ON MAIN. NO WRAP LEFT ON MAIN. I WOULD SAY THAT THIS MAIN SHOULD BE RENEWED. CLAMP WILL OUTLAST GAS MAIN. MAIN REPLACED BY GM 442846 1968.;
| 08-00016-1 | 21 |  | 0.25 | Transmission |  | Fitting |  |  | Construction Defect |  | 2008-03-04 | 2008-03-05 | Tighten Cap or Bolt |  | Other | Stainless steel | Benicia | Paper work took longer than repairs; Reg #3 folder
| 08-00017-1 | 21 |  | 3 | Transmission |  | Valves |  | Unsure under water | Unknown | NO GREASE | 2008-03-04 | 2008-03-05 | Other | GREASED VALVE | Other |  | Vallejo | Paper work more time consuming than repairs; See drawing for reg sta 31 Turner Pkwy & Adm Callahan Pkwy, Vallejo
| 09-00018-1 |  |  | 2 | Distribution Main |  | Regulator | Valves | VALVE | Other |  | 2009-03-20 | 2009-03-23 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Benicia | Tighten bolt. Reg folder V45
| 09-00032-1 |  |  | 0.75 | Single Service |  | Other |  | Riser Threads | Construction Defect |  | 2009-03-31 | 2009-05-04 | Other | SEE ABOVE  TIGHTEN EXIST. INSULATED SEV COCK | Steel/Wrought Iron | Riser | Vallejo | Tightened existing svc. cock
| 09-00148-1 | 4041001 |  | 2 | Transmission |  | Other |  | FILTER | Other | BAD 2 RING | 2009-10-28 | 2009-10-29 | Other | New "O" ring | Steel/Wrought Iron |  | Vallejo | Replaced Bad "o" ring on filter cap; Sketch can be found in Vallejo office T&R records. Reg station 50 leak was on cap of 2" filter. Bad "O' ring replaced and soap tested ok
| 09-00150-1 | 6040301 |  | 0.5 | Transmission |  | Fitting |  |  | Other | Loose | 2009-10-28 | 2009-10-29 | Tighten Cap or Bolt |  | Other | SS fitting | Vallejo | Tighten up SS fitting; Sketch can be found in Vallejo T/R office. Reg folder R-13. leak was on down strem sense line on. Left run 1/2" nut was loose compression style fitting, soap ok.
| 98-40095-1 | 12-0403-01 |  | 1/2" | Distribution Main | DFM | Valves |  |  | External Corrosion | Material Failure | 1998-10-28 | 2010-03-26 | Other | ½ VALVE CLOSED, REPLUMBED SCADA TO ALTERNATIVE VALVE | Steel/Wrought Iron |  | Vallejo | Closed 1/2" valve & SCADA line to alternate valve
| 09-00027-1 |  |  | 3/4" | Single Service |  | Valves |  |  | Other | GREASE | 2009-03-24 | 2011-08-06 | Other | Greased valve | Steel/Wrought Iron |  | American Canyon | Soap test.
| 09-00161-1 | 6-0404-4 |  | 6 | Transmission |  | Other | Butt weld | BUTT WELD | Construction Defect | Weld failure | 2009-12-03 | 2010-02-18 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | Benicia | maj flux tedsted; Plidco split sleeve 3m marker installed in backfilled for future locate #1803517 10000 wp/wcc ph7 welded 100% mag flux tested and soap test.
| 10-00080-1 | 12-21-1-1 |  | 0.75 | Transmission |  | Other Welds |  | Socket weld | Construction Defect | WELD FAILURE | 2010-09-20 | 2010-10-07 | Fill Weld - Weld |  | Steel/Wrought Iron |  | Vallejo | Pin hole leak on fillet/socker weld. Ground out defect & welded 2 process on tee.
| 10-30127-1 |  |  | 2 | Service |  | Riser | Valves | VALVE | Construction Defect | Other-Dry pipe compound | 2010-06-21 | 2010-09-15 | Other | RE DOPED 2 THREADS | Steel/Wrought Iron |  |  | Bypass meter set, tighten packing on pipe on valve, removed & redopred threads on riser-soap at line.
| 10-30151-1 |  |  | 01.75 2 meter manifold | Distribution Feeder Main |  | Fitting |  |  | Construction Defect |  | 2010-09-08 | 2010-11-11 | Other | SEE ABOVE  REMOVED, RETIGHTENED, REINSTALLED MANIFOLD | Steel/Wrought Iron | Manifold | Vallejo | Removed, rebuild, reinstalled 2 meter manifold
| 98-40095-1 | [10 empty] | 2010-03-19 | [5 empty] | Vallejo
| 09-00025-1 |  |  | 0.75 | Single Service |  | Other | Fitting | FITTING | Construction Defect |  | 2009-03-24 | 2009-07-08 | Other | SEE ABOVE  CUT OFF HPR AT MAIN |  |  | American Canyon | HPR has been C/O at main.
| 09-00204-1 | 2 |  | 26 | Transmission |  | Unknown |  |  | Unknown |  | 2009-04-06 | 2009-07-03 | Other |  | Steel/Wrought Iron |  | Tracy
| 09-00201-1 | [10 empty] | 2009-03-09 | 2009-04-02 |  |  |  |  | Tracy
| 09-00202-1 | [10 empty] | 2009-03-09 | 2009-04-20 |  |  |  |  | Tracy
| 09-00203-1 | [10 empty] | 2009-03-09 | 2009-03-31 |  |  |  |  | Tracy
11 |  | 114 | 13.39 | 22 | Transmission |  | Body of Pipe |  |  | Digin |  | 1998-10-22 | 1998-10-22 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Brentwood;
| 98-11200- | 114 | 15.8 | [6 empty] | Damage by 3rd Party |  | 1998-10-22 | [5 empty] | Brentwood
|  |  |  | 3 | [11 empty] | Steel/Wrought Iron
|  |  | 4 | [12 empty] | Steel/Wrought Iron
|  |  |  | 3 | [11 empty] | Steel/Wrought Iron
|  |  |  | 4 | [11 empty] | Steel/Wrought Iron
|  | 107 | 5.89 | 22 | [11 empty] | Steel |  |  | GM4417168
|  | 107 | 5.89 | 22 | [11 empty] | Steel |  |  | GM4417168; See Sht. 1
|  | 107 | 5.89 | 22 | [11 empty] | Steel |  |  | GM4417168, see SHT 1
|  | 107 | 5.89 | 22 | [11 empty] | Steel |  |  | GM4417168; see SHT 1 of 4
|  | 107 | 6.6 | 22 | [11 empty] | Steel |  |  | Remove 3" Drip W.O. 40043A
|  | 107 | 5.3 | 22 | [11 empty] | Steel |  |  | Remove 3" drip w.o. 40043A
| 85-107-1 | 107 | 4.9 | 22 | [7 empty] | 1984-06-05 | 1985-06-14 |  |  | Steel |  |  | Removed drip on W.O.40043A 6/14/85
|  | 107 | 13 | 22 | [11 empty] | Steel |  | Livermore | Removed 3" drip- replaced drip with 3/4" pipe
|  | 107 | 8.73 | 22 | [11 empty] | Steel |  |  | Installed 1" tap
|  | 107 | 1.7 | 22 | [11 empty] | Steel
|  | 107 | 11.5 | 22 | [11 empty] | Steel
|  | 107 | 8.71 | 22 | [11 empty] | Steel
|  | 107 | 9.81 | 22 | [11 empty] | Steel
|  | 107 | 12.47 | 22 |  |  | Body of Pipe | [8 empty] | Steel |  | Tracy
11 |  | 107 |  | 16 | Transmission |  | Meter |  |  | Other |  | 1993-02-25 | 1993-03-25 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Livermore | This leak was coming from around the access bar, which is part of the meter tube. The Access bar allows removal of orifice plate.
96 | 88-10701-1 | 107 | 14.25 | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1988-02-01 | 1988-03-29 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Livermore | Leak was repaired
96 | 88-13101-1 | 131 | 24.49 | 22 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1988-05-02 | 1988-05-02 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Line hit by outside contractors, emergency repair.
96 | 89-00206-1 | 2 | 124.2 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1989-04-25 | 1989-10-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron
96 | 89-00207-1 | 2 | 127.5 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1989-04-27 | 1989-10-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron
96 | 89-00201-1 | 2 | 88.3 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1989-04-13 | 1989-11-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron
96 | 99-00201-1 | 2 | 88.5 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1989-04-13 | 1989-11-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron
96 | 89-00203-1 | 2 | 107.6 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1989-04-18 | 1989-11-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron
96 | 89-00204-1 | 2 | 123.9 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1989-04-25 | 1989-10-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron
96 | 89-00205-1 | 2 | 124.1 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1989-04-25 | 1989-10-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron
96 | 87-00202-1 | SP-2 | 98.8 | 26 | Transmission |  | Other |  |  | Other |  | 1987-02-09 | 1988-10-10 | Other |  | Steel/Wrought Iron |  |  | Facilities were tightened and serviced; Leakage around unibolts at blowoffs A,G, & H, Leakage around 3/4" Elbow below valve B
96 | 87-00201-1 | SP-2 | 105 | 26 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1987-02-10 | 1988-10-10 | Other |  | Steel/Wrought Iron |  |  | Valve was serviced and repaired; mays tap- leakage at regulator or valve.
96 | 87-00203-1 | SP-2 | 115.2 | 26 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1987-02-11 | 1988-10-10 | Other |  | Steel/Wrought Iron |  |  | Valve was serviced and repaired; metric valve at center of crossover leaking
96 | 88-00204-1 | SP-2 | 124.1 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1988-02-03 | 1988-09-15 | Patch Welded |  | Steel
96 | 88-00205-1 | SP-2 | 124.2 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1988-02-03 | 1988-09-15 | Weld Over Sleeve or Can |  | Steel
96 | 88-00202-1 | SP-2 | 84.5 | 26 | Transmission |  | Bell Joint |  |  | Corrosion |  | 1988-02-08 | 1988-03-02 |  |  | Steel/Wrought Iron
96 | 88-00201-1 | SP-2 | 124.2 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1988-01-26 | 1988-02-03 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Welded full encirclement sleeve; leak on bottom of pipe @ approx. 5 O'Clock.
96 | 87-00207-1 | SP-2 | 120.6 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-04-21 | 1988-01-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Line was replaced GM448437-4
96 | 87-00206-1 | SP-2 | 121.6 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-04-21 | 1988-01-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Line was replaced GM448437-4
96 | 87-00208-1 | SP-2 | 121.9 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-04-27 | 1988-01-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Line was replaced GM448437-4
96 |  | SP-2 | 107.8 | 26 | Transmission | [6 empty] | 1986-04-14 |  |  |  | Steel/Wrought Iron |  |  | Leak temperarally repaired with skinner clamp to allow farmer to harvest crop 7/17/86
96 |  | SP-2 | 119.3 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1985-04-16 | 1985-10-22 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | 1/4 mi. to FWY mellow field. No open in air. continue to monitor-cite w/ ; Installed full encirclement sleeve. Sleeve width 30"
96 |  | SP-2 | 119.4 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1985-04-16 | 1985-10-22 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | 100% @ 4% 1/4 mi. to fwy mellow field; Installed full encirclement sleeve, sleeve width 24"
96 |  | SP-2 | 119.8 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1985-04-16 | 1985-10-22 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | No Odor in air 8/16, Checked visual and w/ instruments,...100 yds to FWY Grain field; Installed full encirclement sleeve, sleeve width 24"
96 |  | SP-2 | 107.4 | 26 | Transmission |  | Valves |  |  | Other |  | 1986-04-14 | 1986-07-31 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  |  | Tap valve leaking around threaded plug & stem. 2" chapman valve #2-960 cast steel; tightened packing nut & plug on 2" gate valve
96 |  | SP-2 | 82.6 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1986-04-09 | 1986-08-26 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Temporarily repaired until clearance obtained; Max welding pressure is 505 PSIG
96 |  | SP-2 | 119.6 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-02-11 | 1987-03-03 | Patch Welded |  | Steel/Wrought Iron |  |  | Welded patch over Pit.
96 |  | SP-2 | 124.1 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1985-07-18 | 1985-07-26 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Welded...
96 |  | SP-2 | 107.6 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1985-04-15 | 1985-10-23 | Patch Welded |  | Steel/Wrought Iron |  |  | Almond Field- no indication of tree damage, tree shows new growth; Installed 12' Dia. Steel Patch
96 |  | SP-2 | 107.5 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1985-04-15 | 1985-10-23 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Almond field- no apparent growth or damage installed full encirclement sleeve, sleeve width 48"
96 |  | SP-2 | 70.5 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-04-09 | 1984-05-02 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Replaced pipe on W.O. SP3743
96 |  | SP-2 | 119.9 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-03-22 | 1984-09-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | replaced 18' of 26" pipe W.O. SP3754
96 |  | SP-2 | 119.9 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-03-22 | 1984-09-21 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Installed sleeve W.O. SP 3754
96 |  | SP-2 | 121.9 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-03-22 | 1984-04-21 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Repaired on W.O. SP-3754 9-21-84
96 |  | SP-2 | 119.9 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-04-03 | 1984-09-21 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Repaired on W.O. SP-3754
96 |  | SP-2 | 119.8 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-03-22 | 1984-09-21 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Installed sleeve W.O. SP3754
|  | SP-2 | 119.8 | 26 | Transmission |  | Other |  |  | Corrosion |  | 1982-03-24 | 1982-07-27 | Patch Welded |  | Steel/Wrought Iron |  | Los Banos | Welded a 15 1/2" x 18" patch over leak and heavy pitted area 7:30 position. Extensive pitting throughout exposed pipe. Sand blasted, double wrapped and installed 60# zink Anode. P/S 502Mv.
|  | SP-2 | 88.25 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-03-14 | 1983-04-20 | Patch Welded |  | Steel/Wrought Iron |  |  | welded 12" x 15" patch to corrosion leak and deep pit area, 9:00 position. Sand blasted, double wrapped and installed 30# zink Anode. P/S 685 mv.
|  | SP-2 | 107.65 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-03-29 | 1983-04-20 | Patch Welded |  | Steel/Wrought Iron |  |  | Patch 12" x 12" 9:00- P/S .395. Sand blasted , double wrapped and installed 30# zink Anode. P/S .395mv.
|  | SP-2 | 88.23 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-03-14 | 1983-04-20 | Patch Welded |  | Steel/Wrought Iron |  |  | Welded 12" x 12" patch 3:00 position. Sand blasted, double wrapped and installed 30# zink anode P.S .415mv
|  | SP-2 | 87.76 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-03-14 | 1983-04-20 | Patch Welded |  | Steel/Wrought Iron |  | Los Banos | Welded 14 1/2" x 12" patch to corrosion leak located 3:30 position. Sand blasted double wrapped and installed 30# zink anode. P/S .510mv.
|  | SP-2 | 87.42 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-03-14 | 1983-04-21 | Patch Welded |  | Steel/Wrought Iron |  | Los Banos | Welded 17" x 13" patch to corrosion leak located 9:00 position, San blasted, double wrapped and installed 30# zink anode. P/S .400mv
|  | SP-2 | 70.55 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-03-10 | 1983-04-21 | Patch Welded |  | Steel/Wrought Iron |  | Los Banos | welded 17" x 20" patch covering three leaks and heavey pit area 5:00 position. Sand blasted, and double wrapped. Installed #30 zink anode. P/S .469mv
|  | SP-2 | 107.77 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-03-29 | 1983-04-20 | Patch Welded |  | Steel/Wrought Iron |  | Los Banos | Welded a 12" x 12" patch to corrosion leak located at 9:00 position. Sand blasted, double wrapped and installed a 30# zink anode. P/S .395mv
|  | SP-2 | 88.25 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-03-14 | 1983-04-20 | Patch Welded |  | Steel/Wrought Iron |  | Los Banos | Welded 12" x 15" patch to corrosion leak located 9:00 position. Sand blasted, double wrapped and installed 30# zink anode. P/S .685mv.
| 71-00251- | SP-2 | 88.23 | 26 | Transmission |  | Valves |  |  | Corrosion |  | 1983-03-14 | 1983-04-20 | Patch Welded |  | Steel/Wrought Iron |  | Los Banos | Welded 12" x 12" patch to corrosion leak located 3:00 position. Sand blasted, double wrapped and installed #30 zink anode. P/S .415mv
|  | SP-2 | 122.54 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-03-29 | 1983-05-18 | Patch Welded |  | Steel/Wrought Iron |  |  | Welded 14" x 26" patch to corrosion leak at 6:30 position and heavey pit area. Sand blasted, double wrapped and installed 60# zink anode. P/S 300 mv
|  | SP-2 | 119.75 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-06-15 | 1983-06-21 | Patch Welded |  | Steel/Wrought Iron |  |  | 40" x 48" P/S 400mv
|  | SP-2 | 119.4 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-04-01 | 1983-05-18 | Patch Welded |  | Steel/Wrought Iron |  |  | Welded 14" x 36" patch to leak and heavy pit area. Sand blasted double wrapped and installed two 60# zink anodes P/S 400mv
|  | SP-2 | 117.22 | 26 | Transmission |  | Other Welds |  |  | Corrosion |  | 1983-04-01 | 1983-05-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Replaced 63' section pipe containing two weld patches, one with corrosion lek, double wrapped and installed two 60# zink anodes. P/S
|  | SP-2 | 122.05 | 26 | [7 empty] | 1983-04-01 |  |  |  | Steel |  |  | Excavated 40' section line soil saturated with oil. No leak found. This area will be kept under surveillance
|  |  | 87.76 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-03-14 | 1983-04-20 | Patch Welded |  | Steel/Wrought Iron |  |  | Pit 3:30 position- patch 14 1/2" x 12" P/S .510mv
|  |  | 87.42 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-03-14 | 1983-04-21 | Patch Welded |  | Steel/Wrought Iron |  |  | Pit 9:00 position patch 12" x 13" P/S .400
|  |  | 70.55 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-03-10 | 1983-04-21 | Patch Welded |  | Steel/Wrought Iron |  |  | P/S 469.mv. 17" x 20" patch covering 3 leaks and heavy pit area - 30# zink anode
|  | SP-2 | 40.55 | [8 empty] | 1982-03-09 | 1982-11-18 | [5 empty] | 3:00 position 1/16" hole 12" x 14" patch
|  | SP-2 | 42.99 | 22 | Transmission |  | Bell Joint |  |  | Corrosion |  | 1982-03-09 | 1982-11-17 | Clamp |  | Steel/Wrought Iron |  |  | Installed skinner clamp to leak on bell joint weld. 8:00 position. Wrapped with polykin and installed 60# zink anode P/S .440
|  | SP-2 | 107.25 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1982-07-07 | 1982-08-04 | Patch Welded |  | Steel/Wrought Iron |  | Los Banos | Welded 12" x 22 1/2" patch covering 3 corrosion leaks 6:00 position. Sand blasted, double wrapped and installed 60# zink anode. P/S .605 mv. damage to walnut orchard z-82-5001
|  | SP-2 | 115.87 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1980-04-04 | 1980-10-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Los Banos | Replaced 54' section pipe containing leaking patch and corrosion pits. Wrapped with polykin and installed 2 60# Zink Anodes. P/S 450 mv. Includes leak reporated at MP 115.88 on foot patrol and leak survey 4-8-80
|  | SP-2 | 41.89 | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1981-03-09 | 1981-06-17 | Patch Welded |  | Steel/Wrought Iron |  | Lost Banos | Welded 14" x 14" patch to corrosion leak at a 6:00 position. Patch covered all pitting in excavation. San blasted, double wrapped, and installed 60# zink anode. P/S 325 mv.
|  | SP-2 | 88.35 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1981-03-18 | 1981-06-16 | Patch Welded |  | Steel/Wrought Iron |  | Los Banos | Welded a 13" x 14" patch to corrosion leak 4:30 position. Heavy pitting throughout the exposed pipe within the excavation. Sand Blasted, double wrapped, and installed 60# zink anode. P/S 450mv.
|  | SP-2 | 88.55 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1981-03-18 | 1981-06-15 | Patch Welded |  | Steel/Wrought Iron |  | Los Banos | Welded 12" x 12" patch to corrosion leak 12:30 position. Heavy pitting throughout the exposed pipe within the excavation. Sand Blasted, double wrapped, and installed 60# zink anode. P/S 680mv
|  | SP-2 | 107.6 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1981-03-23 | 1981-06-11 | Patch Welded |  | Steel/Wrought Iron |  | Los Banos | Welded 15" 17 1/2" patch over leak and heavy pit area 8:00 position. Extensive pitting throughout exposed pipe. Sand blasted, double wrapped, and installed 60# zink anode. P/S 410 mv.
|  | SP-2 | 102.29 | 26 | Transmission |  | Fitting |  |  | Other | No description | 1981-03-23 | 1981-06-11 | Other |  | Steel/Wrought Iron |  | Los Banos | Leaking threads on 2 1/2" mueller fitting installed 9-5-79 for flame control stack SP 3564. Sealed by tightening plug and cap. Double wrap and install 60# zink anode. P/S 675mv.
|  | SP-2 | 107.6 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1982-03-23 | 1982-07-30 | Patch Welded |  | Steel/Wrought Iron |  | Los Banos | Welded 12" x 12" patch to corrosion leak 5:30 position. Sand Blasted, double wrapped and installed 2 60# zink anodes P/S 450mv.
|  | SP-2 | 43.08 | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1980-03-17 | 1980-09-15 | Patch Welded |  | Steel/Wrought Iron |  | Los Banos | Welded 17" by 19" patch covering three leking pits and deep pit area at 7:00 to 7:30 position. Double wrapped with polykin and installed 60# zink anode P/S 450mv.
|  | SP-2 | 43.01 | [14 empty] | Los Banos | Instrument readings did not justify excavation for leak repair. Location will be kept under surveillance with periodic probe and J-W instrument check.
|  | SP-2 | 42.88 | 22 | Transmission |  | Bell Joint |  |  | Corrosion |  | 1980-03-17 | 1980-09-11 | Clamp |  | Steel/Wrought Iron |  | Los Banos | Installed skinner seal clamp to leak on bell joint and leak on body of pipe at 3:00 position. Double wraped with polykin and isntalled 60# zink anode. P/S 430mv.
|  | SP-2 | 88.35 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1980-03-31 | 1980-09-05 | Patch Welded |  | Steel/Wrought Iron |  | Los banos | Installed 12" by 12" patch to corrosion leak at 10:30 position. Double wrapped with polykin and installed 60# zink anode P/S 480mv
|  | SP-2 | 85.86 | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1980-03-27 | 1980-09-18 | Patch Welded |  | Steel/Wrought Iron |  | Los Banos | Installed 13" by 13 1/2" patch covering a leaking pit and deep pit area at 6:00 position. Double wrapped with polykin and installed 60# zink Anode. P/S 610mv.
|  | SP-2 | 39.9 |  | Transmission |  | Body of Pipe |  |  |  |  | 1980-03-17 |  |  |  | Steel/Wrought Iron |  | Los Banos | Excavated valve 1 & valve 2 and all adjacent piping. Leak was not detectible after excavation and soap testing. Area will be kept under surveillance
96 | 72-11401-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-02-22 | 1972-03-06 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Tracy | Full sleeve welded over leak; 1/16" hole in 1 1/4" pit at 6:00 O'clock 18" long full encirclement sleeve installed over leak
96 | 74-11403-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1974-04-09 | 1974-04-22 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Tracy | Pitted areas 6' apart
96 | 74-11402-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1974-04-09 | 1974-04-18 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Tracy
96 | 74-11401-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1974-04-08 | 1974-04-19 | Weld Over Sleeve or Can |  | Steel/Wrought Iron
96 | 72-11402-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-09-01 | 1972-09-08 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Tracy | 26" long sleeve welded over leak
96 | 74-11404-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1974-05-03 | 1974-05-07 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Tracy
96 | 74-11405-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1974-09-28 | 1974-10-02 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Tracy | 1/16" hole in 1" pit on bottom of pipe
96 | 74-11406-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1974-09-28 | 1974-10-02 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Tracy | 1/16" hole in 3/4" pit on bottom of pipe
96 | 75-11403-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-04-18 | 1975-04-23 | Patch Welded |  | Steel/Wrought Iron |  |  | Leak bottom - 6 O'clock, welded on 2 12" patches
96 | 71-11401-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1971-03-17 | 1971-03-22 | Patch Welded |  | Steel/Wrought Iron |  | Tracy | Dead Vegitation; Main 114 M.P. 21.77 (FS1149471) 2-1/2" corrosion pits 2 1/2" apart. Welded 12" x 12" patch over leaks
96 | 78-11401-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-06-01 | 1978-06-12 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | 3 pits from.... .250 in depth
96 | 75-11401-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-04-18 | 1975-04-23 | Patch Welded |  | Steel/Wrought Iron |  |  | Leak 6:00 o'clock welded on 12" round patch
96 | 75-11402-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-04-18 | 1975-04-23 | Patch Welded |  | Steel/Wrought Iron |  |  | Leak 6:00 o'clock welded on 12" round patch
96 | 72-11402-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-09-01 | 1972-09-08 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Tracy | 26" long sleeve welded over leak. Leak at 6:00 o'clock
96 | 78-11401-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-06-01 | 1978-06-12 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | 3 pits from .200 to .250 in depth
96 | 78-11401-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-06-01 |  | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | 3 pits from .200 to .250 in depth
96 | 75-11402-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-04-18 | 1975-04-23 | Patch Welded |  | Steel/Wrought Iron |  |  | Leak 6:00 o'clock, Welded on 12" round patch
96 | 75-11401-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-04-18 | 1975-04-23 | Patch Welded |  | Steel/Wrought Iron |  |  | Leak 6:00 o'clock, welded on 12" round patch
|  | 114 | 27 | 22 | [8 empty] | 1988-03-15 |  |  | Steel |  | Livermore | Brass plug on 3/4" mueller service tee leaking; tightened to repair
96 | 82- | 114 | 21.7 | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1982-08-13 | 1982-10-20 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Corrosion leak was caused by a rock. Damage to the wrap on the bottom of the pipe- all pipe around tee..pit was in excellent condition
96 | 82-11402-1 | 114 | 21.97 | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1982-08-13 | 1982-10-20 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Corrosion leak was caused by a rock cutting into wrap on the bottom of the pipe- all pipe wrap and pipe areound leak pit was in excellent condition
96 | 83-10702-1 | 107 | 20.58 | 22 | Transmission |  | Other |  |  | Corrosion |  | 1983-06-22 | 1983-09-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Livermore | Pit on wrinkle 100% damage of pipe surface in very good condition- pit on wrinkle @ 9 o'clock. replaced 6' on W.O. 7066
96 | 83-10701-1 | 107 | 9.1 | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-06-03 | 1983-06-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Livermore | Tied into existing replacement pipe at 2 section W.O. 46637
96 | 85-10702-1 | 107 | 4.92 | 3.5 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-06-05 | 1985-06-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Removed drip on W.O. 40043A
96 | 85-10701-1 | 107 | 0.94 | 22 | Transmission |  | Other Welds |  |  | Construction Defect |  | 1985-02-22 | 1985-04-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Replaced 11' of 22" .312 w.t. AoSmith. Pipe with 22" .375w.t. API SLX x52 DSAW including a 3" miter to replace bell & spigot miter. Pipe used from emergency stock report T-16
96 | 82-10703-1 | 107 | 16.7 | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1982-11-16 | 1982-11-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Livermore | Leak repaired by replacing pipe on W.O. 45521
96 | 82-10702-1 | 107 | 18.5 | 22 | Transmission |  | Body of Pipe |  |  | Other |  | 1982-11-14 | 1982-11-15 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Livermore | Leak in span was caused by gun shot. Cleak penetration with no disturbance to curvature of line. Repaired with full encirclement sleeve.
96 | 80-10702-1 | 107 | 5.9 | 22 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-08-17 | 1980-08-18 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Repair leak that in span
96 | 82-10701-1 | 107 | 1.3 | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1982-04-05 | 1982-06-11 | Weld Over Sleeve or Can |  | Steel/Wrought Iron
96 | 81-10701-1 |  | 18.69 | 22 | Transmission |  | Girth Weld |  |  | Corrosion |  | 1981-07-22 | 1981-08-20 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | 8-12-81 Original to Steve Belmude; Installing a full encirclement sleeve over bell joint
96 | 77-10700-1 |  | 17 | 22 | Transmission |  | Drip |  |  | Material Failure |  | 1977-01-10 | 1977-01-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron
96 | 75-10702-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-03-28 | 1975-04-07 | Patch Welded |  | Steel/Wrought Iron |  | Tracy | Lean on bottom of pipe- 6:00 O'Clock, 6" round patch welded over leak
96 | 75-10701-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-03-28 | 1975-04-07 | Patch Welded | ; | Steel/Wrought Iron |  | Tracy | Leak on bottom of pipe- 6:00 o'clock. 6" round patch welded over leak
96 | 72-10701-1 | 107 |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-02-29 | 1972-03-06 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Tracy | Dead Vegitation; 1/8" hole in 1" pit at this location. 18" long full encirclement sleeve welded over leak
96 | 72-10702-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-05-05 | 1972-05-08 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Full sleeve welded over leak; two leaks 1/8" dig in 1" pits at 16:00 & 18:00 on pipe. Sleeve welded over leaks under line pressure
96 | 72-10703-1 |  |  | 22 | Transmission |  | Bell Joint |  |  | Corrosion |  | 1972-05-12 |  | Clamp |  | Steel/Wrought Iron |  | Tracy | Dead Vegitation
96 | 72-10704-1 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-05-12 |  | Clamp |  | Steel/Wrought Iron |  | Tracy | Leak location 1/8" hole in 2" pit. Sleeve will be welded leak
96 | 79-13102-1 |  | 26 | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-09-17 | 1979-09-27 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Near Livermore
96 | 71-13103-1 |  |  | 24 | Transmission |  | Body of Pipe |  |  |  |  | 1971-11-18 |  |  |  | Steel/Wrought Iron
96 | 80-13101-1 | 131 | 43.3 | 24 | Transmission |  | Other |  |  | Corrosion |  | 1980-07-31 | 1980-08-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Replaced 90' of pipe at leak location
96 | 79-13103-1 | 131 |  | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-09-17 | 1979-09-25 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Livermore
96 | 71-13103-1 | 131 | 35.5 | 24 | Transmission |  | Body of Pipe |  |  | Other |  | 1979-08-28 | 1979-09-25 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Tracy | Leak was due to pipe resting on large rock causing indentation and small crack in wall.
96 | 79-13102-1 |  | 26.3 | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-08-28 | 1979-09-27 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Tracy | Poor wrapping at 12 o'clock on pipe and pitted area about 2 feet long due to the poor wrap. Leak and one pit 0.250 Inch deep
96 | 79-13101-1 |  | 37.41 | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-06-04 | 1979-06-28 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Tracy | Pitting at 6 o'clock on pipe due to corrosion. Pitting will be covered by repairs. pipe wrapping in poor condition.
96 | 79-13101-1 |  | 37.41 | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-06-04 | 1979-06-28 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Tracy | wrapping in very poor condition. Pitting and leaks at 6 o'clock. Installed 24" x 18" sleeve to cover pitting and leak
96 | 78-13101-1 |  | 38.5 | 24 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 1978-09-01 | 1978-09-07 | Other |  | Steel/Wrought Iron |  | Tracy
96 | 76-13101-1 |  |  | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-03-15 | 1976-03-25 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Replaced 6' section of pipe
96 | 74-13101-1 |  |  | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1974-04-09 | 1974-04-17 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | ; ;
96 | 73-13101-1 |  | 29.37 | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-09-05 | 1973-09-06 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Livermore | 1/8" hole in 3/4" pit on bottom of pipe, 6 o'clock sleeve installed
96 | 71-13101-1 |  |  | 24 | Transmission |  | Girth Weld |  |  | Corrosion |  | 1971-02-28 | 1971-03-01 | Patch Welded |  | Steel/Wrought Iron |  | Tracy | Dead Vegitation; Dead vegitation @ M.P. 41.22 main 131 indicated leakage 1/32" hole in 2/4" dia pit in girth weld, bottom of pipe. Permanent repair, 10" dia patch welded over leak
96 | 71-13102-1 |  |  | 0.75 | Other | DRIP LINE | Body of Pipe |  |  | Corrosion |  | 1971-10-19 | 1971-10-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Tracy | While patroling pipeline found 3/4" drip line leaking Main 131 M.P. 24.45. Permament repair, replaced 3/4" drip line.
|  | 114 | 18.25 | 22 | [11 empty] | Steel
|  | 114 |  | 24 | [11 empty] | Steel |  | Brentwood | Installed 2" blow off stack on W.O. 4505G
|  | 114 | 30.73 | 36 | [11 empty] | Steel |  | Tracy | Excavated line to eliminate metallic contact between line and casing W.O. 4403G
|  | 114 | 31 | 36 | [11 empty] | Steel |  | Livermore | 12' sewer line clearance under line 114-9'
|  |  |  | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | Oakley, Contra Costa County.
|  |  |  | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | Oakley, Contra Costa County
|  |  |  | 12.37 | Transmission | [10 empty] | Steel/Wrought Iron |  | Oakley | Antioch gas terminal, Oakley Contra Costa County
|  | 114 |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | Brentwood | Brentwood gas terminal; station piping; Line 114 Brentwood, Contra Costa County
|  | 114 |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | Brentwood | Brentwood gas terminal; station piping. Line 114 Brentwood, Contra Costa County
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | Brentwood | Brentwood Gas Terminal; station piping, Brentwood Contra Costa County
|  | 316 |  | 12 | Gathering | [7 empty] | 2008-10-13 | Other | wrap pipe with stack wrap | Steel/Wrought Iron |  | Brentwood
| 08-13102-1 | 131 |  | 24 | Transmission |  | Valves |  |  | External Corrosion |  | 2008-11-05 |  |  |  | Steel/Wrought Iron |  | Livermore
[13 empty] | 1999-09-28 | [5 empty] | cut and capped 4" cap leak to retire .... as well
|  |  |  | 6.25 | [8 empty] | 1999-09-28 | [5 empty] | cut and capped 10" s/o V45; to retire portor #1 install 6" cap
|  |  |  | 6.25 | [8 empty] | 1999-09-28 | [5 empty] | cut and capped 10" s/o V45 ; to retire portor #1 install 6" cap
| 02-31801-1 |  |  | 3 | Gathering |  | Valves |  |  | Unknown |  | 2002-03-18 | 2002-03-21 | Other | Replaced |  |  |  | leak around valve body (3" V-B) at black butte station
|  | 169 | [15 empty] | Orbend
318
| 99-16900-3 | 169 | 1,779 ft S/O V-105 | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-12-07 | 1999-12-16 | Other | INST. 75' | Steel/Wrought Iron |  | Glenn | 50 ft S/O PREVIOUS LEAK 11/2t
| 95-10006-1 |  |  | 2011-03-04 | Transmission |  | Regulator |  |  | Other |  | 1995-10-16 | 1996-06-26 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Gridley | Fittings tightened in reg. box. Diaphragm replaced in regulator. Replaced entire regulator.
19 | 95-10006-1 | [10 empty] | 1995-10-16 | [5 empty] | Gridley
|  | 167 |  |  | Transmission | [6 empty] | 2002-01-25 | [5 empty] | near Gridley | *see attached sheets ; *excavation due to Ducks Unlimited Water delivery project- concrete cap also installed by Ducks Unlimited, Ok'd by George Karkazis
167
167
| 03-16901-1 | 169 |  | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion | suspect int. corrosion | 2003-12-01 | 2003-12-03 | Weld Over Sleeve or Can |  |  |  | E/O Willows | Rice Field 100 YDS S/E V-230
| 08-16901-1 | 169 | 2.08 | 12.75 | Transmission |  | Body of Pipe |  |  |  |  | 2008-03-31 | 2008-04-01 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | Glenn
13 | 93-56353-1 | [10 empty] | 1993-09-14 | [5 empty] | Oroville
13 | 93-56352-1 | [10 empty] | 1993-09-14 | [5 empty] | Oroville
13 | 93-56351-1 | [10 empty] | 1993-09-14 | [5 empty] | Oroville
|  | 131 | 38.68 | 24 | Transmission |  |  |  |  | Construction Defect | EXTERNAL CORROSION |  | 2002-09-30 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  |  | Welded Sleeve Over Dent
66 | [15 empty] | Steel
[5 empty] | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Bakersfield
|  |  |  | 4 | [11 empty] | Steel |  | Bakersfield
|  |  |  | 4 | [11 empty] | Steel/Wrought Iron |  | Bakersfield
66 | 85-20004-1 |  |  | 6 | Distribution Main |  | Valves |  |  | Other |  | 1985-01-03 | 1985-01-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Lubed valve.
25 |  |  |  | 6 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Bakersfield | Installed to cutoff 6" gas main and 6" valve 04-16-86...
25 |  |  |  | 4 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron | Bakersfield |  | I tied in with a 4' side assembly we had to move the trench because of the 8" ...
66 | 76-20043-1 |  |  | 12 | Transmission |  | Valves |  |  | Other |  | 1976-05-12 | 1977-08-02 | Other |  | Steel/Wrought Iron |  | Bakersfield | This is transmission line- flange on west side of valve is leaking 6/23/77; repaired leak in valve by greasing;; permit and repairs
66 | 77-20178-1 |  |  | 10 | Transmission |  | Valves |  |  | Other |  | 1977-06-28 | 1980-06-23 | Other |  | Steel/Wrought Iron |  | Bakersfield | Repaire dleak in valve B.by greasing; Greased valve.
| 81-20221- | [10 empty] | 1981-05-22 | [5 empty] | Bakersfield | Delete; Checked tar pressure cans leak. With leak indicator... Found no leak.
66 | 83-20019- |  |  | 12 | Transmission |  | Valves |  |  | Other |  | 1983-01-07 | 1983-01-28 | Other |  | Steel/Wrought Iron |  | ; Bakersfield
66 | 84-20011-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1984-01-17 | 1984-02-10 | Other |  | Steel/Wrought Iron |  |  | Repaired leaking valve and replaced casing; Regreased and ...valve casing
|  |  |  | 6 | [11 empty] | Steel |  | Bakersfield | Installed 6" E.V.-11-Valve
66 | 85-20003-1 | 142 |  | 6 | Distribution Main |  | Valves |  |  | Other |  | 1985-01-03 | 1985-01-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ; Bakersfield | Put new "O" rings in valve by manaf. refp.
|  |  |  | 11 | [11 empty] | Steel/Wrought Iron |  | Bakersfield
|  |  |  | 4 | [11 empty] | Steel |  |  | Inserted 1" plastic serv.; Installed 9... abandoned, permanent clamp
|  |  |  | 2 | [11 empty] | Steel-Other |  | BAKERSFIELD
|  |  |  | 4 | Distribution Main | [6 empty] | 1974-01-02 |  |  |  | Steel/Wrought Iron
|  |  |  | 6 | [11 empty] | Steel-Other |  | BAKERSFIELD
66 | 76-20214-1 |  |  | 6 | Distribution Main |  |  |  |  | Corrosion |  | 1976-04-15 |  |  |  | Steel/Wrought Iron |  | Bakersfield | Change to #3. Refer to GM 476...
66 | 76-20212-1 |  |  | 6 | Distribution Main |  |  |  |  | Corrosion |  | 1976-04-15 |  |  |  | Steel/Wrought Iron |  | Bakersfield | Change to #3 refer to GM 496159
66 | 76-20211-1 |  |  | 4 | [5 empty] | Corrosion |  | 1976-04-15 |  |  |  | Steel/Wrought Iron |  | Bakersfield | Cange to #3 refer to GM496159
66 | 76-20210-1 |  |  | 6 | Distribution Main |  |  |  |  | Corrosion |  | 1976-04-15 |  |  |  | Steel/Wrought Iron |  | Bakersfield | Change to #3 refer to GM496159
|  |  |  | 4 | [11 empty] | Steel/Wrought Iron
66 | 76-20219-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-04-15 | 1977-10-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | File for follow ups, change to #3
66 | 76-20218-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-04-15 | 1977-10-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ; Bakersfield | File for follow ups, Change to #3
66 | 76-20217-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-04-15 | 1977-10-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | File for follow ups, change to #3
66 | 76-20216-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-04-15 | 1977-10-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | File for follow ups, change to #3
66 | 74-00072-1 | [10 empty] | 1974-12-18 | [5 empty] | Bakersfield | Servie tap. Checked scr.. Background readings M.C.S. 1-25-78 (new SCR); Delete
66 | 74-00071-1 | [10 empty] | 1974-12-18 | [5 empty] | Bakersfield | Servie tap. Checked SCR background readings 1-25... MCJ
66 | 76-20215-1 |  |  | 4 | Distribution Main |  |  |  |  | Corrosion |  | 1976-04-15 | [5 empty] | Bakersfield; | Change to #3 refer to GM 496159
66 | 76-20213-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-04-15 | 1977-10-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ; Bakersfield | File for follow ups, change to #3
66 | 76-60015-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-05-12 | 1976-05-13 | Clamp |  | Steel/Wrought Iron | Bakersfield |  | Main in bad conditionn all exposed main badley pitted and small fissures leaks (unable to stop all leaks with clamps, Denis made aware of this condition.
66 | 77-20098-1 |  |  | 3.34 |  |  | Body of Pipe |  |  | Corrosion |  | 1977-03-02 | 1978-03-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Service....ASAP...; Insert service w/ plastic tested 100# 10#...3-1-78
|  |  |  | 4 | [11 empty] | Steel/Wrought Iron |  | Bakersfield
|  |  |  | 4 | [8 empty] | 1971-08-23 |  |  | Steel-Other | ; | BAKERSFIELD | 1 1/4" LP SERVICE ABANDONED AT THIS LOCATION
25 |  |  |  | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | C/O 1" plastive per service order. Smet R. Maning 9-36-85
66 | 79-20116-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-04-20 | 1980-05-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Permit to insert. Insert service.
66 | 80-20031-1 | [10 empty] | 1980-04-07 | [5 empty] | Bakersfield | Permit and Insert (...)
|  |  |  | 4 | [11 empty] | Steel |  | Bakersfield
66 |  |  |  | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Bakersfield | Inst. 1" pl. insert with dresser riser. Old riser and meter under porch. Service order called for replacement and alter.
66 | 77-20306-1 | [10 empty] | 1977-08-17 | [5 empty] | Bakersfield | Follow up 12 mos.
|  |  |  | 3 | [11 empty] | Steel/Wrought Iron |  | Bakersfield
66 | 74-00069-1 | [10 empty] | 1974-12-18 | [5 empty] | Bakersfield | Service tap.... Checked over ser. and main found 103. 12-15-76 M.C.J. Checked over serp & main found 40PPM at riser- this is a new ser. Checked around found..1/15/1979
66 | 74-00068-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-12-18 | 1978-01-10 | Clamp |  | Steel/Wrought Iron |  | Bakersfield | Service tap... Checked SCR> & Main found .03 over T. 12-15-76 M.C.J. Checked over main & Ser. found 1% over ser. M. C. Jones 1-6-78
66 | 74-00068-1 |  |  | 0.3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-12-18 | 1978-01-10 | Clamp |  | Steel/Wrought Iron |  | Bakersfield
|  |  |  | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Bakersfield
|  |  |  | 2 | [11 empty] | Steel
66 | 84-20010-1 |  |  | 0.5 | Other |  | Physical/Mechanical Joint |  |  | Other |  | 1984-01-17 | 1984-02-01 | Other |  | Steel/Wrought Iron
|  |  |  | 6 | [11 empty] | Steel |  | Bakersfield
Steel/Wrought Iron
66 | 90-20200-1 | [10 empty] | 1990-08-29 | 1990-09-21 |  |  |  |  | Bakersfield | Checked for gas leak, found nothing; Delete
66 | 88-20068-1 | [10 empty] | 1988-09-27 | 1988-09-29 |  |  |  |  | Bakersfield | Macle at Pit. (R.J.)
66 | 88-20067-1 |  |  | 0.38 | Distribution Main |  | Regulator |  |  | Other |  | 1988-09-27 | 1988-09-29 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Bakersfield | Ritightened fittings on pilot and reg.
66 | 88-20066-1 |  |  | 0.38 | Distribution Main |  | Fitting |  |  | Other |  | 1988-09-27 | 1988-09-29 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Bakersfield | Retightened fitting on pilot and Reg.
66 | 76-60041-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1976-12-18 | 1976-12-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Found leak in service 4' to 6' from main. INserted with 1/2" plastic
|  |  |  | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Bakersfield
|  |  |  | 4 | [8 empty] | 1971-09-24
|  |  |  | 4 | [5 empty] | Other | ELECTROLYSIS |  | 1968-10-21 | Patch Welded |  |  |  | BAKERSFIELD | THE CAP ON THE SERVICE TEE TO 216 T WAS LOOSE AND LEAKING. THIS COULD POSSIBLY HAVE STARTED THE ELECTROLYSIS.
|  |  |  | 4 | [11 empty] | Steel |  | Bakersfield
25 | 82-60039-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1982-07-08 | 1982-07-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | ... temp....service to re...Insert 1/2" pl. service
66 | 74-20104-1 | [10 empty] | 1974-06-03 | [5 empty] | Bakersfield | Delete; Checked location found .01% over scr. 3-9-76. Checked ser. found 30PPM over ser. M.C.J. 8/25/1977. Found no leakage 4-20-79; Delete
66 | 76-40020-1 |  |  | 0.75 | Service |  | Tap Connection |  |  | Corrosion |  | 1976-12-18 | 1976-12-18 | Patch Welded |  | Steel/Wrought Iron |  | ; ; Bakersfield | FOund leak at service tee....
|  |  |  | 2 | [11 empty] | Steel |  | Bakersfield | Cut off and abandoned 2- Blow off.
66 | 82-40038- |  |  | 2 | Other |  | Other |  |  | Damage by outside Forces |  | 1982-04-01 | 1982-04-01 | Other |  | Steel/Wrought Iron |  | Bakersfield | Repair broken 2" Blow-off by installing 1 M2PLF and abandoning below ground level (33").
66 | 72-00248-1 |  |  | 2 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-02-03 | 1972-12-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Installed 2" with by blastic. Installed 9" ... on riser.
66 | 72-00249-1 | [10 empty] | 1972-02-03 | [5 empty] | Bakersfield
66 | 84-60050- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1984-01-17 | 1984-05-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Installed temp. clamp on 3/4" ser. above ground level. _relayed service ... 1/2" P/, Service
|  |  |  | 2 | Distribution Main | [12 empty] | Bakersfield | ...and regraded 2 1/2" PL. Serviced to new curb and (t) tiers old service shallow; Regraded and reserviced due to curb and (t) tiers old service shallow
66 | 80-40046-1 |  |  | 1 | Other |  | Fitting |  |  | Damage by outside Forces |  | 1980-06-18 | 1980-06-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Installed new 3 MM. for permanent repair. Complete.
|  |  |  | 2 | Distribution Main | [6 empty] | 1973-09-04 |  |  |  | Steel/Wrought Iron
|  |  |  | 2 | Distribution Main | [6 empty] | 1975-04-28 |  |  |  | Steel/Wrought Iron |  |  | 3' of main exposed 4-28-75 J.M.V.
|  |  |  | 2 | Distribution Main | [6 empty] | 1973-10-31 |  |  |  | Steel/Wrought Iron
66 | 84-60010-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1984-06-30 | 1984-10-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Needs to be lowered, will be done on GM 4415071
66 | 87-20002-1 |  |  | 10 | Transmission |  | Fitting |  |  | Other |  | 1987-01-09 | 1987-01-28 | Other |  | Steel/Wrought Iron |  | Bakersfield | Replaced 1/2" metric valve and fittings
66 | 83-20017- |  |  |  | Transmission | [6 empty] | 1983-01-06 | [6 empty] | Delete; Leak in valve casing e/s/o V st. Approx 85' N/o Brundage; 0% reading E.L. at valve casing.
25 | 83-60001- |  |  | 0.75 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1983-01-06 | 1983-01-07 | Other |  | Steel/Wrought Iron |  | ; Bakersfield | Repaired leaking 1" caop on 1" pin off tee for 3/4 control line to Reg. Pit; Repaired leak at 1" service tee cap on 3/4 pit control line.
25 |  |  |  | 2 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Bakersfield
66 | 83-20016- |  |  | 0.5 | Transmission |  | Other |  |  | Other |  | 1983-01-06 | 1983-01-24 | Other |  | Steel/Wrought Iron |  | Bakersfield | Leak in pit L-04 E/S/O Vst. (1st pit no brundage)
66 | 83-20018- |  |  | 0.5 | Transmission |  | Other |  |  | Material Failure |  | 1983-01-06 |  | Other |  | Steel/Wrought Iron |  | Bakersfield | Leak in Pit L-03 E/S/O V St 2nd Pit N/O Brundage; tightened...
|  |  |  | 8 | Distribution Main | [6 empty] | 1975-02-26 |  |  |  | Steel/Wrought Iron
66 | 84-20004-1 |  |  | 8 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1984-01-17 | 1984-01-31 | Other |  | Steel/Wrought Iron |  | Bakersfield | Redoped & Tightened fittings. Control line tightened pilot. Dust trap...
66 | 84-20005-1 |  |  | 8 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1984-01-17 | 1984-01-31 | Other |  | Steel/Wrought Iron |  | Bakersfield | Redoped & Tightened...
66 | 84-20006-1 |  |  | 8 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1984-01-17 | 1984-01-31 | Other |  | Steel/Wrought Iron |  | Bakersfield | Re-doped & tightened fittings...
66 | 84-20007-1 |  |  | 8 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1984-01-17 | 1984-01-31 | Other |  | Steel/Wrought Iron |  | Bakersfield | Redoped & Tightened fittings. Dust trap blow-off valve.
66 | 84-20008-1 |  |  | 8 | Distribution Main |  | Physical/Mechanical Joint |  |  | Other |  | 1984-01-17 | 1984-01-31 | Other |  | Steel/Wrought Iron |  | Bakersfield | Redoped & Tightened fittings...
66 | 84-20009-1 |  |  | 8 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1984-01-17 | 1984-01-31 | Other |  | Steel/Wrought Iron |  | Bakersfield | Redoped & Tightened fittings control line....
66 | 90-20006-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Other |  | 1990-01-03 | 1990-01-31 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Bakersfield | Repaired leak
| 05-40110-1 | L-142S | 9 | 10 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2005-09-08 | 2005-09-09 | Welded Sleeve/Can - Weld | WEDDING BAND | Steel/Wrought Iron |  | Bakersfield | Welded band around leak 21" long; 18" band welded over leak
|  |  |  | 10 | [11 empty] | Steel/Wrought Iron |  | Bakersfield
|  |  |  | 3 | [11 empty] | Steel/Wrought Iron
66 | 82-20008- |  |  | 4 | Distribution Main |  | Valves |  |  | Other |  | 1982-01-08 | 1982-04-30 | Other |  | Steel/Wrought Iron |  | ; Bakersfield | Grimes greased valve 1-12-82. Repaired leak in 6" valve. Bad grease seal replaced.
|  |  |  | 6 | [11 empty] | Steel/Wrought Iron
|  |  |  | 3 | [8 empty] | 1969-04-14 |  |  | Steel-Other
66 | 83-20014- |  |  | 6 | Distribution Main | [6 empty] | 1983-01-06 |  |  |  | Steel/Wrought Iron |  | Bakersfield | Delete; Found 0% reading on L.I.L. ... indication of leakage at vavle casing.
66 | 82-20009-1 |  |  | 6 | Distribution Main |  | Valves |  |  | Other |  | 1982-01-08 | 1982-03-09 | Other |  | Steel/Wrought Iron |  | Bakersfield | Repaired leak ... 6" valve by tightening nuts on flanges
25 | 81-60032- |  |  | 0.75 | Single Service |  | Body of Pipe |  |  | Corrosion |  | 1981-05-03 | 1981-05-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Installed d1/2" PL tubing into 3/4" stl. Casing. Install new...riser. Delete
66 | 82-40051- |  |  | 6 | Distribution Main |  | Tap Connection |  |  | Damage by outside Forces |  | 1982-04-20 | 1982-04-20 | Patch Welded |  | Steel/Wrought Iron |  | Bakersfield | REinstalled 3/4" st. service tee. Torn off 6" main; Arc welded..PL in 3/4" STL. Service tap hole rewelded. Service tee damaged by contractor
|  |  |  | 6 | [11 empty] | Steel |  |  | Installed 46' of 1/2" PL pipe and riser to complete new service.
|  |  |  | 6 | [8 empty] | 1971-01-05 | Other |  | Steel-Other |  | BAKERSFIELD | TIED IN NEW 3/4 STEEL SERVICE.
66 | 82-60031-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1982-05-11 | 1982-05-11 | Patch Welded |  | Steel |  |  | Found leak on 6" gas main weld patch on main; Installed 1" PL Ser.
66 | 79-20426-1 |  |  | 6 | Service |  | Body of Pipe |  |  | Other |  | 1979-11-09 | 1981-02-18 | Replace Pipe and/or Service |  | Copper |  | Bakersfield | 1/2" copper service. Inst.- plastic service.
|  |  |  | 6 | [11 empty] | Steel |  | Bakersfield
[16 empty] | Steel-Other |  | BAKERSFIELD
[13 empty] | 1970-07-31 | Other |  | Steel-Other |  | BAKERSFIELD | INSTALL 3/4" GAS SERVICE.
|  |  |  | 06.00 AND 04.00 | [8 empty] | 1970-01-22 |  |  | Steel-Other |  | BAKERSFIELD | BROKEN GASKET... BOTH 4" AND 6" ARE IN ... ATH THIS LOCATION.
25 |  |  |  | 6 | Distribution Main | [10 empty] | Steel |  | Bakersfield | Asandon 3/4" H.P. Stl. service
[16 empty] | Steel |  | Bakersfield
66 | 84-20317-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1984-10-01 | 1988-08-16 | Patch Welded |  | Steel/Wrought Iron |  |  | Repaired leak 6" STL main with weld patch
|  |  |  | 4 | Distribution Main |  |  |  | None |  | None |  | 1977-05-16 |  | NONE | Steel/Wrought Iron |  | Bakersfield | We inspected 1 ft. of pipe water was under wrap.
|  |  |  | 4 | [11 empty] | Steel/Wrought Iron |  | Bakersfield | Installed 1" PL. ser.
|  |  |  | 4 | [11 empty] | Steel |  | Bakersfield
25 |  |  |  | 2 | Distribution Main | [10 empty] | Other Plastic |  | Bakersfield
66 | 72-00151-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Corrosion |  | 1972-01-20 | 1972-10-25 | Other |  | Steel/Wrought Iron |  | Bakersfield | Removed blow-off line at valve. Greased & plugged valve. 10/25/72. Found 2 EA holes in 1 1/4" pipe blowing gas
|  |  |  | 4 | [11 empty] | Steel |  | Bakersfield | Installed 1 1/4" Pl ser.
|  |  |  | 4 | Distribution Main | [6 empty] | 1972-10-20 |  |  |  | Steel/Wrought Iron
66 | 72-00150-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-01-20 | 1974-12-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Surveyed area found 33 ppm of...3708 wible. Surveyed area found 30-33 ppm over ser. at main...12/73. Surveyed area found 20-33 ppm over ser. 11/13/1974...
|  |  |  | 2 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Bakersfield | Cut off service 8' E//o Main
|  |  |  | 2 | [11 empty] | Steel |  | Bakersfield
66 | 76-40015-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-12-21 | 1977-05-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Installed ... 4" ...
66 |  |  |  |  | Distribution Main |  | Body of Pipe |  |  | Corrosion |  |  | 1977-05-17 |  |  | Steel/Wrought Iron |  | Bakersfield | The wrap was fait at the tie-in.
|  |  |  | 4 | [11 empty] | Steel
66 | 72-00144-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-02-14 | 1972-02-23 | Other |  | Steel/Wrought Iron |  | ; Bakersfield | Found (2) leaks and ...Installed (2) ...weld clamps over ...area
66 | 77-20119- |  |  | 0.34 | Service |  | Body of Pipe |  |  | Corrosion |  | 1977-04-08 | 1978-06-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Permit and instert. Insert- sevice/branch- tested secv. 50 CB is leak 15.LS
25 | 79-40070-1 |  |  | 0.34 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-07-03 | 1979-07-03 | Clamp |  | Steel/Wrought Iron |  | Bakersfield | Made temp. repaires with 3/4" clamp service should be relayed, due to tree stump and unable to see other damage to service.
25 |  |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-07-24 | 1979-07-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Inst. Plas...Insert
|  |  |  | 2 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Bakersfield
66 | 73-60009-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-03-28 | 1973-03-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | 2 Leaks in the but weld. Bad corrosion leaks on bottom of pipe. Replaced 14' of 2" STL. pipe with 2" plastic.
|  |  |  | 10 | [11 empty] | Steel/Wrought Iron |  | Bakersfield | a;
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | Bakersfield
|  |  |  | 3 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Bakersfield
66 | 84-20018-1 |  |  | 0.5 | Other |  | Physical/Mechanical Joint | Valves |  | Other |  | 1984-01-19 | 1984-01-31 | Other |  | Steel/Wrought Iron |  | Bakersfield | Redoped & tightened fittings centrol line fittings & Dust trap blow off valve
66 | 79-60038- |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-06-12 | 1979-06-12 | Replace Pipe and/or Service |  | Other Plastic |  | Bakersfield | Repaired 1/2" PL. service. Installed 2-1/2" AMP fittings at riser
66 | 83-60090-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1983-09-09 | 1983-09-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  |  |  | 3 | [11 empty] | Steel |  | Bakersfield
|  |  |  | 3 | Distribution Main | [6 empty] | 1973-06-04 |  |  |  | Steel/Wrought Iron
|  |  |  | 2 | Distribution Main |  |  |  | None |  | None |  |  | Other | Karo test | Steel/Wrought Iron |  | Bakersfield | Wires for crossing lights cross bell hole twice. ETS is in valve box
|  |  |  | 4 | Distribution Main | [6 empty] | 1975-12-01 |  |  |  | Steel/Wrought Iron |  | Bakersfield
|  |  |  | 2 | Distribution Main | [6 empty] | 1975-11-24 |  |  |  | Steel/Wrought Iron |  | Bakersfield
|  |  |  | 2 | Distribution Main | [6 empty] | 1973-12-18 |  |  |  | Steel/Wrought Iron
25 |  |  |  | 5 | Transmission | [8 empty] | Patch Welded |  | Steel/Wrought Iron |  | Bakersfield
|  |  |  | 2 | [8 empty] | 1988-06-10 |  |  | Steel |  | Bakersfield
|  |  |  | 2 | [11 empty] | Steel |  | Bakersfield
25 | 82-20308- |  |  | 2 | Distribution Main |  | Fitting |  |  | Other |  | 1982-09-23 | 1982-09-23 | Other |  | Steel/Wrought Iron |  | Taft | Vented area. Dug up transition, installed clamp. Replaced transition fitting.
66 | 80-60056-1 |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1980-07-17 | 1980-07-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Taft | Replaced... 7-16-80 Billy Gee. Complete.
25 |  |  |  | 0.75 | Service |  | Body of Pipe |  |  |  |  | 1980-05-01 | 1980-05-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Taft | Repaired old 3/4 stl serv. with 1/2" pls tubing.
66 | 82-20191-1 | [10 empty] | 1982-05-11 | [5 empty] | Arvin | Leaks over buried piping - Various locations
66 | 82-20192- |  |  |  | Other | [6 empty] | 1982-05-11 |  |  |  | Steel/Wrought Iron |  | Arvin | Leaks over buried piping - various Locations.
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Bakersfield
|  |  |  | 6 | Transmission | [12 empty] | RidgeCrest | Rewrapped valve, installed valve frame and cover. Then back filled around it.
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Ridgecrest | Rewrapped valve. Installed valve frame and cover then backfilled around frame and cover.
66 | 78-20134-1 |  |  |  | Other |  | Other |  |  | Other |  | 1978-06-12 |  | Other |  | Other |  | Oildale | Meter leaking...; 7-2-80 S.R. .06% gasleak at swivel on meter. 25 P.P.M. underground by riser. 100P.P.M. at telephone man hole. 6-5-80 Note: coundn't find water box, but got .05% in telephone man hole same area.; Permit and instert (Delete).
66 | 77-20102- |  |  | 0.34 | Service |  | Other Welds |  |  | Other |  | 1977-03-03 | 1978-06-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Insert and permit. Inst-plastic insert 6-6-78
66 | 72-60002- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-01-07 | 1972-01-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Installed anode 32#. Installed (2) 2" ...control fittings and replaced 4' section main.
66 | 90-20008-1 |  |  | 2 | Distribution Main | [6 empty] | 1990-01-05 | 1990-05-18 |  |  | Steel |  | Bakersfield | Bar test done and main exposed, but no leak found.
| 90-20008-1 |  |  | 2 | Distribution Main | [6 empty] | 1990-01-05 | 1990-05-18 |  |  | Steel |  |  | Bar test done and main exposed, but no leak found
66 | 90-20007-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1990-01-05 | 1990-05-10 | Clamp |  | Steel/Wrought Iron |  | Bakersfield | Repair corrosionleak with permanent clamp on 2" main
66 | 90-20098-1 | [10 empty] | 1990-04-10 | [5 empty] | Bakersfield | Delete
66 | 77-20170- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1977-06-22 | 1978-08-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Permit & Insert. Complete
66 | 72-20002-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-01-17 | 1972-02-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Note: checked out area and found... Lake St. Leaking- inserted 1/2" plastic. Area should be checked again in about 2 wks to see if this was trouble, there is a 8" transmission line in same area and valve to pin... leak at this time 2/25/72
|  |  |  | 2 | [11 empty] | Steel |  | Bakersfield
66 | 77-40032-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Other |  | 1977-06-28 | 1977-07-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron
66 | 79-60056-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1979-09-04 | 1979-09-04 | Clamp |  | Steel/Wrought Iron |  | E. Bakersfield
66 | 79-20069-1 | [10 empty] | 1979-03-22 | [5 empty] | Bakersfield | Leak over service at riser.
66 | 79-20070-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-03-22 | 1979-09-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Leak over service at fence- dead grass area.; Permit & Insert. Inst. Plastic Insert.
66 | 79-20071-1 | [10 empty] | 1979-03-22 | [5 empty] | Bakersfield | Delete; Leak over service
66 | 77-20154-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1977-06-07 | 1977-07-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Leak on service; Change to #3)
66 | 82-20157- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1982-04-05 | 1983-04-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Inserted 1/2" PL. Service. Leak by tee at main.
[18 empty] | Bakersfield | Insert old with 1/2" PL
|  |  |  | 2 | Distribution Main | [6 empty] | 1972-02-25 |  |  |  | Steel/Wrought Iron |  |  | Note: Inspection on 2" main only
|  |  |  | 2 | Distribution Main | [6 empty] | 1972-02-25 |  |  |  | Steel/Wrought Iron
66 | 73-20075-1 | [10 empty] | 1973-05-01 | [5 empty] | Bakersfield
25 |  |  |  | 2 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Bakersfield | Abandoned old ser. and replaced ser. W/ 1/2" plastic direct burial. Changed meter locations to...house.
|  |  |  | 2 | [5 empty] | Corrosion |  |  | 1971-07-16 | Other | INSTALLED PLASTIC SERVICE | Steel-Other |  | BAKERSFIELD
| 84-20098- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1984-03-23 | 1984-04-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Replaced Stl. service with 1/2" plastic insert
66 | 83-20164-1 | [10 empty] | 1983-04-11 | [6 empty] | Leak reading at Gutter approz 10'-15' w/o service
25 |  |  |  | 2 | Distribution Main |  | Other Welds |  |  | Corrosion |  | 1986-10-10 | 1986-10-10 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Bakersfield | Inserted 1/2" plt. service and repaired a leak on main at hip...
66 | 90-20013-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1990-01-08 | 1990-01-18 | Patch Welded |  | Steel/Wrought Iron |  | Bakersfield | Welded patch over leak. Wrap not bonded to main very wel;
|  |  |  | 10 | Distribution Feeder Main | [6 empty] | 1972-11-01 |  |  |  | Steel/Wrought Iron
|  |  |  | 0.75 | [11 empty] | Steel
66 | 74-00131-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-12-26 | 1974-12-27 | Other |  | Steel/Wrought Iron |  | Bakersfield | The gas leak was on the old abanden ser. Welded up the gas leak.
66 | 79-40071-1 |  |  | 0.5 | Service |  | Other |  | RISER | Damage by outside Forces |  | 1979-06-09 | 1979-06-09 | Replace Pipe and/or Service |  | Other Plastic |  | Bakersfield | Installed 2' PL. 1/2" tubing. INstalled 2-1/2" AM fittings
|  |  |  | 4 | [11 empty] | Steel |  | Bakersfield
|  |  |  | 4 | Distribution Main | [6 empty] | 1973-11-16 |  |  |  | Steel/Wrought Iron
|  |  |  | 4 | [11 empty] | Steel |  | Bakersfield
25 |  |  |  | 0.51 | Service |  | Body of Pipe |  |  | Corrosion |  |  | 1995-06-20 | Replace Pipe |  | Steel/Wrought Iron |  | Bakersfield | Inserted service with 1/2" PL. IAMPO
66 | 83-40093-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1983-10-20 | 1983-10-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ; Bakersfield | Insert 2-1/2" PL. Ser. Service main installed...and ..at 1907... St.
66 | 79-40121-1 |  |  | 0.34 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-12-27 | 1979-12-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Over service- near tree stump 1634' w/o MT. Vernon; Complete.
66 | 79-20214-1 | [10 empty] | 1979-06-21 | [5 empty] | Bakersfield | Delete
6 | 79-20231-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-06-21 | 1979-08-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Over service-Lawn is dying.; Insert service. Complete
[16 empty] | Steel |  | Bakersfield | Installed 1" Pl. Ser.
66 | 79-20211-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-06-21 | 1979-10-11 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Leak over service; ...the old 3/4" gas ser. it was...
66 | 79-20212-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-06-21 | 1979-07-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield
66 | 79-20213-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-06-21 | 1979-08-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | over service; complete
66 | 74-00142-1 | [10 empty] | 1974-12-27 | [5 empty] | Bakersfield | delete; ser. tap checked... found... checked service found 10% over main 60 PP18 over service 1/21/77 F.L ... checked ser. reading background... file for follow up
|  |  |  | 2 | [11 empty] | Steel |  | Bakersfield
|  |  |  | 2 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Bakersfield
66 | 74-00141-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-12-27 | 1977-04-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Checked ser... -0.1% over ser at main... checked service + found 1% plus over service at main 1/21/77 F.L. Stoke. Permit and insert.
25 |  |  |  | 2 | Distribution Main | [6 empty] | 1974-04-08 |  |  |  | Steel/Wrought Iron |  | Bakersfield | Insert...
|  |  |  | 2 | Distribution Main | [6 empty] | 1972-04-25 |  |  |  | Steel/Wrought Iron
66 | 79-20232-1 | [10 empty] | 1979-06-22 | [5 empty] | Bakersfield | Leak over service about 3' from riser
66 | 84-20207- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1984-05-09 | 1984-05-09 | Clamp |  | Steel/Wrought Iron |  | Bakersfield | C/O 3/4" Stl. service and made repair by inserting with 1/2" plastic service.; INstalled leak clamp
|  |  |  | 2 | [11 empty] | Steel |  | Bakersfield | Abandoned 84' of 3/4"...
66 | 87-20044-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Construction Defect |  | 1987-05-15 | 1987-12-02 | Replace Pipe and/or Service |  | Aldyl A (Tan or Gray) |  | Bakersfield | Repaired leaking 1/2 pl. service and main. Transition fitting of pnuch tee....of missing sleeve..
66 | 87-20085-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  |  |  | 1987-08-11 | 1988-02-03 | Other |  | Other |  |  | Leaking diaphram ... Reg.
|  |  |  | 0.75 | [11 empty] | Steel |  | Bakersfield | Contractor dig in. Wrap damage only.
|  |  |  | 2 | Distribution Main |  | Girth Weld |  |  | Damage by outside Forces |  |  |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Replace 2" PL main, ...Replaced 2" PL main ... To old main damage Bx contractor installing storm drain.
66 | 71-20025-1 |  |  | 0.75 | Other |  | Valves |  |  | Other |  | 1971-11-11 | 1971-12-23 | Other |  | Steel/Wrought Iron |  | Bakersfield | Curb valve was leaking needed grease
|  |  |  | 2 | [8 empty] | 1970-08-19 |  |  | Steel-Other |  | BAKERSFIELD | PLUG ON CAP AND MUELLER SERVICE TEE LOOSE. MAIN HAS BEEN RECENTLY RELAYED, BUT SOIL MAY HOLD GAS ODOR FROM OLD MAIN NEARBY.
[16 empty] | Steel |  | Bakersfield
66 | 76-60035-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1976-09-28 | 1976-10-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Service needs to be replaced.
66 | 72-00223-1 | [10 empty] | 1972-01-31 | [5 empty] | Bakersfield | Survey location founr (.02%) over main.
|  |  |  | 2.38 | Distribution Main | [10 empty] | Steel |  | Bakersfield
66 | 79-60059-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-07-31 | 1979-07-31 | Replace Pipe and/or Service |  | Steel |  | Bakersfield; | Pressure tested old steel service at 40psi. drop to 0 in 30 seconds. Replace service by insert. 7-31-79 R. John (Complete)
66 | 79-60058- |  |  | 0.75 | Service | b | Body of Pipe |  |  | Corrosion |  | 1979-06-25 | 1979-06-25 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Made temp repairs with 3/4 leak clean- should be relayed A.S.A.P. Inserted service ...Pressure tested old service at 40# Prop to zero in 10 sec. (Complete)
66 |  |  |  | 2 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Bakersfield
|  |  |  | 3 | Other | [10 empty] | Steel |  | Bakersfield | Installed ETS station as perscribed, ETS station was set in pavement as shown on drawing.; Install this ETS at least 50' from 4wat. Install one end of #10 wire on 2' other end of loop. Charge time to cathodic protection ...
25 |  |  |  | 2 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Bakersfield
66 | 78-60025-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1978-03-17 | 1978-03-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Found service leaking replaced by insert pressure tested old stl. service at 100# for 5 min. Drop to zero
66 | 78-60026-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1978-03-17 | 1978-03-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Found service leaking replaced by inserting with plastic 3-20-78
|  |  |  | 0.5 | [13 empty] | Bakersfield | Branch service to 904 Crane St. SO045708
25 | 79-40089-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-05-02 | 1979-08-02 | Replace Pipe and/or Service |  | Other Plastic |  | Bakersfield | Made permanent repairs with 2-1/2" AMP fittings and 2' OL 1/2 tubing (Complete).
Other Plastic
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron |  | Bakersfield
66 | 85-20008-1 |  |  | 8 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1984-01-05 | 1985-01-14 | Other |  | Steel/Wrought Iron |  | Bakersfield | Greased the...the..leak; Leak on Valve Cover;
|  |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1986-01-06 | 1986-01-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield
66 | 77-20148- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1977-06-03 | 1978-10-12 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Leak over patches; Permit & Insert. SVC transferred only. WO 3-4456-C main replaced
66 | 76-60004-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-01-23 | 1976-02-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Transfered (4) services over to new main. Installed (2) 2" RT. PCF and installed 50' of new 2" steel pipe.; Lot of electrolis over all exposed pipe.
66 | 76-60003-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-01-23 | 1976-01-23 | Clamp |  | Steel/Wrought Iron |  | Bakersfield; | Installed ...temp Clamps because sea...main...
66 | 90-20148-1 | [10 empty] | 1990-05-17 | [5 empty] | Bakersfield | Delete; Ran survey and could not get any readings.
66 | 89-20006-1 |  |  | 8 | Distribution Main |  | Valves |  |  | Other |  | 1989-01-04 | 1989-02-09 | Other |  | Steel/Wrought Iron |  | Bakersfield | Greased valves
25 | 82-60069- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1982-10-05 | 1982-10-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | ...Temp repairs with a... clamp- service...
66 | 82-60059-1 | [10 empty] | 1982-09-22 | [6 empty] | Leak at Riser; Checked ser. found no leakage- tightened cudb on top cock to fly leak. Delete leak
66 | 76-60000-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-01-23 | 1976-02-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | This area consentrated...area pipe loods good on ....
66 | 73-20014-1 | [10 empty] | 1973-04-10 | [5 empty] | Bakersfield | Surveyed area found .04% over ser. as said at brich wall 70/1000... at meter...
|  |  |  | 2 | Distribution Main | [6 empty] | 1973-08-27 |  |  |  | Steel/Wrought Iron |  | Bakersfield
|  |  |  | 2 | [13 empty] | Bakersfield | Replace 100' of 2" main WO 3-4456-C
|  |  |  | 2 | Distribution Main | [6 empty] | 1973-09-18 |  |  |  | Steel/Wrought Iron
66 | 73-00084-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-10-29 | 1974-01-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Surveyed location found 7% (no #1 leak) over ser. at main.
66 | 73-00085-1 | [10 empty] | 1973-10-29 | [5 empty] | Bakersfield | Surveyed area found 1% over control...the N/E ...
66 | 74-20000-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-01-07 | 1974-01-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Service was inserted already.
|  |  |  | 2 | Distribution Main | [6 empty] | 1974-01-09 |  |  |  | Steel/Wrought Iron
66 | 82-20228- |  |  | 0.5 | Distribution Main |  | Fitting |  |  | Other |  | 1982-06-08 | 1982-06-10 | Other |  | Steel/Wrought Iron |  | Bakersfield | Greased valve to stop leakage.
|  |  |  | 3 | [11 empty] | Steel-Other |  | BAKERSFIELD
|  |  |  | 3 | [8 empty] | 1970-09-01 |  |  | Steel-Other |  | BAKERSFIELD
|  |  |  | 0.75 | [11 empty] | Steel |  | Bakersfield | Rewrapped service line due to granite cont. hitting service. No damage to pipe. No leak.
|  |  |  | 3 | [8 empty] | 1990-08-27 |  |  | Steel-Other |  | BAKERSFIELD
|  |  |  | 3 | [8 empty] | 1970-08-31 |  |  | Steel-Other |  | BAKERSFIELD
66 | 79-40024-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-04-18 | 1979-04-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Service inserted due to contractor damaging service while digging trench to install drain pipe.
| 79-40024-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-04-18 | 1979-04-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Install 3 temp 3/4 clamps. Service will have to be inserted A.S.A.P.
25 | 79-60078-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-10-26 | 1979-10-26 |  |  | Steel/Wrought Iron |  | Bakersfield | Made temp repair on riser, with 3/4" clamp. Inst- plastic inseert.
66 | 78-20139-1 |  |  | 2 | Single Service |  | Body of Pipe |  |  | Corrosion |  | 1978-06-15 | 1978-06-27 | Patch Welded |  | Steel/Wrought Iron |  | Bakersfield | Inst. weld patch 7" long 4" wide on 2" m.P. Main. Between 901 & 907 over main. Leak at edge of curb. Lawn and trees dying. Pipe in exellent condition except for a 6" portion of 2" main running over a sewer line at 907 blossom. 282' S/O rosewood...Leak caused by isntallation of sewer lateral. Gas depth 49"
|  |  |  | 2 | [11 empty] | Steel |  | Bakersfield | ... Gas service.
|  |  |  | 2 | [11 empty] | Steel
|  |  |  | 2 | [11 empty] | Steel/Wrought Iron |  | Bakersfield | Inserted both services per same bell hole
|  |  |  | 2 | [11 empty] | Steel |  | Bakersfield | Inserted gas services
|  |  |  | 2 | [11 empty] | Steel |  | Bakersfield | Inserted gas services
|  |  |  | 2 | [11 empty] | Steel |  | Bakersfield
25 | [12 empty] | 1990-10-04 |  |  |  |  | Bakersfield | c/o 3/4" stl. service at main/
|  |  |  | 2 | Distribution Main | [6 empty] | 1975-03-06 |  |  |  | Steel/Wrought Iron |  | Bakersfield
|  |  |  | 2 | [11 empty] | Steel |  | Bakersfield | Instal gas service
|  |  |  | 2 | [8 empty] | 1970-06-25 |  |  | Steel-Other |  | BAKERSFIELD
[16 empty] | Steel-Other |  | BAKERSFIELD
25 | 79-40078-1 |  |  | 0.34 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-07-06 | 1979-07-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Over service along house.; Insterted old stl. service with 1/2" PL. Tubing.
|  |  |  | 3 | [11 empty] | Steel |  | Bakerfield | Installed 1/2" PL. Ser. S.O> 20772
66 | 74-20115-1 | [10 empty] | 1974-06-11 | [5 empty] | Bakersfield | ... Checked ser. found 10PPM ....01% at riser 4/17/78. .01% at riser 4/5/79. Checked ser. found back ground reading.; Follow up 12 mos.
66 |  |  |  | 3 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Bakersfield | Abandoned 3/4" H.P. stl. service at main and riser.
66 | 74-20108-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-06-11 | 1977-06-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Foreman: Furnish sketch....MLH 3-26-75 Checked location found...over. Checked over ser. found .02 at riser M.C.J. 3/25/77. Service insert .0% ...; Complete
|  |  |  | 4 | [11 empty] | Steel |  | Bakersfield | Cut off and abandoned and gas service at main. Demolishing bldgs.
66 | 74-20109-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Other |  | 1974-06-11 | 1977-06-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Forman: furnish sketch.... Checked location found...Checked service and found 100PPM...
66 | 74-20111-1 |  |  | 0.75 | Service |  | Body of Pipe | Clamp |  | Corrosion |  | 1974-06-11 | 1974-07-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield
66 | 74-20114-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-06-11 | 1974-06-29 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Found leak on ... 12" ... main reading serv....
66 | 72-00201-1 | [10 empty] | 1972-01-27 | [5 empty] | Bakersfield
66 | 79-20283-1 | [10 empty] | 1979-08-02 | [5 empty] | Bakersfield
66 | 77-60005-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Corrosion |  | 1977-06-23 | 1977-06-25 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield
66 | 90-20207-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1990-09-24 | 1991-03-14 | Clamp |  | Steel/Wrought Iron |  |  | Ist. 3" skinner clamp
66 | 79-60047-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-06-13 | 1979-06-13 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Service to be relay A.S.A.P. isnt-plastic insert 3/4" clamp on riser. Complete
66 | 83-20196- | [10 empty] | 1983-05-04 | [5 empty] | Bakersfield
|  |  |  | 8 | Transmission |  |  |  | NONE |  | None | 1979-05-22 | 1979-10-08 | Patch Welded |  |  |  | Bakersfield | No leakage; Arc welded patch over. Groove in top of 8" H.P. main ....; Arc welded patch over Groove in top of 8" H.P. main. No leaks included small gauge in 8" pipe repaired.
66 | 78-40005-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-05-09 | 1978-05-09 | Patch Welded |  | Steel/Wrought Iron |  | Bakersfield | 12" x 174" patch welded over damaged pipe at this location 5-9-78.
25 | 81-40014- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1981-02-25 | 1981-02-25 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Made temp repaires by installing 5' of 2" PL tubing and ... tee -crew to relay- ...Need service order to replace permit.
| 81-40014- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  |  | 1981-03-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield | Insert 1/2" PL ser. The riser was leaking...
66 | 78-60069-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1978-08-28 | 1978-08-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | E. Bakersfield | Inst. Plastic insert. Tested service leak hole in... Found leak in ser. while retesting meter and inserting.
25 |  |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1978-08-28 | 1978-08-28 | Patch Welded |  | Steel/Wrought Iron |  | E. Bakersfield | Tested service leak 20L..in 10 min. Service order turned in to mapping.
|  | 134 |  | 8 | Transmission | [6 empty] | 1974-10-24 |  |  |  | Steel/Wrought Iron |  |  | Inspection on 8" main TP 134
| 81-20242- |  |  | 0.75 | Other |  | Other |  |  | Material Failure |  | 1981-08-27 | 1981-11-20 | Replace Pipe and/or Service |  | Other |  | Greenfield | Changed diaphram only.
25 |  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel |  | Bksfld
66 | 85-20125-1 |  |  | 4 | Distribution |  | Body of Pipe |  |  | Corrosion |  | 1985-05-20 | 1985-08-19 | Clamp |  | Steel |  | Oildale | Leak number on second page of A-Form does not correspond to leak number listed on first page; 4" L.P. Steel Main Badly Deteriorated Should Be Relayed
66 | 85-20124-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1985-05-20 | 1985-08-19 | Clamp |  | Steel |  | Oildale | 4" L.P. Steel Main Badly Deteriorated Should Be Relayed
66 | 85-20123-1 | [10 empty] | 1985-05-20 | 1986-07-24 |  |  |  |  | Oildale | In For Repair House Line Is Pitted At Ground Level (6-17-86); Found Leak in Cust. House Line 7-23-86
66 | 75-00011-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-05-20 | 1975-10-09 | Replace Pipe and/or Service |  | Steel |  | Oildale | Fol.Up. Sept-76; Found Gas Leak Tee At 325 Lincoln Ave Relayed; Completed 10/29/75; Unable to read portion of comments due to fading
66 | 72-00523-1 | [10 empty] | 1972-02-04 | [5 empty] | Oildale | No Leak Found; "B" Issued
66 | 82-40085 |  |  | 0.75 | Other |  | Other |  |  | Other |  | 1982-08-17 | 1982-08-17 | Other |  | Steel/Wrought Iron |  | Oildale | Checked out pit did not find odor. Sent flame park in AM J L D 8-17-82; Additional notes appear below these, unable to read due to fading.
|  |  |  | 2" | [11 empty] | Steel |  | Oildale | Abandon 1/2" PL. service at main-Left approx. 6" stub for possible future use.
|  |  |  | 3" | [11 empty] | Steel |  | Oildale
25 |  |  |  | 3 | Distribution Main | [10 empty] | Steel |  | BKSFLD | Active white powder under wrap.
|  |  |  | 3 | Distribution Main | [6 empty] | 1975-03-14 |  |  |  | Steel/Wrought Iron
|  |  |  | 3" | [11 empty] | Steel |  | Oildale
66 | 82-40009- |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1982-01-08 | 1982-01-08 | Clamp |  | Steel |  | Oildale | Inserted Plastic Ser Due to Leakage in Old 1 1/4" Stl., Riser; Unable to read some of the notes included in the comment section
|  |  |  | 4 | Distribution Main | [10 empty] | Steel |  | Oildale
|  |  |  | 3 | Distribution Main | [10 empty] | Steel |  | Oildale
|  |  |  | 4 | Distribution Main |  | Body of Pipe |  |  |  |  | 1986-08-19 | 1986-08-19 | Clamp |  | Steel
66 | 83-20024- |  |  |  | Transmission | [6 empty] | 1983-01-10 |  |  |  | Steel |  | BAK | Found Leak To Be in Souther Calif, Fas 2" H.P. Dist Main Notified on Leakage
25 |  |  |  | 12.75 | Transmission | [7 empty] | 1981-09-03 | Weld Over Sleeve or Can |  | Steel |  | Bakersfield | Contractor struck main with ditch digging equip. Nicks are .025 to .050 Installed 12x18" Sleeve - Tapped to equalize
66 |  |  |  | 12 | Transmission | [10 empty] | Steel |  | Bksfld. | Contractor nicked 12" line while digging to install conduit with ditch whitch. Repaired line by installing full weld sleeve.
66 | 83-20023- | 142 |  | 12 | Transmission | [6 empty] | 1983-01-01 |  |  |  | Steel |  | BAK | Found no leakage ser 12" T.P. main - No reading on P.G. line call oil co's to respond
66 | 82-60070- |  |  | 3 | Transmission |  | Valves |  |  | Material Failure |  | 1982-10-07 | 1982-10-07 | Replace Pipe and/or Service |  | Steel |  | Bksfld. | Unable to read notes included in comments section due to fading.
66 | 87-20011-1 | 142 | [9 empty] | 1987-01-19 | 1987-01-21 |  |  |  |  | BKSD | Delete; Checked valve no reading LEL; Alson no soap bubbles anywhere RPN
66 | 87-20012-1 |  |  | 3" |  |  | Other |  | SEE OVER |  |  | 1987-01-19 | 1987-02-03 | Other |  | Steel |  | BKSD | Delete; Opened up PG&E facilities found no indication of leakage, Also I feel that any leak is originating from various petroleum lines west of PG&E gas mains. The various companies have been notified.
| 25-40050-1 |  |  | 0.75 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1990-10-19 | 1990-10-19 | Tighten Cap or Bolt |  | Steel |  |  | Cap off Nipple
66 | 89-20003-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1989-01-04 | 1989-02-10 | Other |  | Steel
66 | 87-20010-1 | 142 |  | 4 | Transmission |  | Valves |  |  | Other |  | 1987-01-15 | 1987-01-16 | Other |  | Steel |  | BKSD | Lubed Valve; Repair date on back of A-Form differs from repair date on front of form. Repair date on rear of form listed as 1-16-86
66 | 90-20003-1 | 142 |  |  | Transmission |  | Valves |  |  | Other |  | 1990-01-04 | 1990-01-17 | Other |  | Steel/Wrought Iron |  | BAK | Greased valve & operated; Re checked
|  |  |  | 16 | [8 empty] | 2007-10-10 | Other | DIGIN |  |  | BKSFLD | Feather and re-wrap main (Dig in)
|  | L-142N |  | 16 | Transmission | [6 empty] | 2005-08-10 |  |  |  | Steel/Wrought Iron |  | Bakersfield | Stand-by; Pipe data section and repair data sections are both crossed out
|  | L142N 16 |  | 10 | Transmission | [6 empty] | 2003-12-15 | 2003-12-15 | Other | Grind smooth | Steel/Wrought Iron |  | Bakersfield | Inspection is circled at the top of the A-Form, next to which is written "Only"; Repair remarks section reads as follows: Ground down scratch smooth
|  | L142N |  | 12" | Transmission | [12 empty] | BKSFLD | Standby only; Repair remarks section reads as follows: Standby for third part
|  | L142N |  |  | Transmission | [12 empty] | BKSFLD | Standby Only; Repair remarks section reads as follows: Standby for third party
|  | L142N |  | 12" | [13 empty] | BKSFLD | Standby Only; Repair remarks section reads as follows: Standby for third party
|  | L142N |  | 12" | [13 empty] | BKSFLD | Standby Only; Pipe and Repair Data sections are crossed out
|  | 375 | [15 empty] | Bakersfield | At the top of the A-Form, Inspection has been circled.
[12 empty] | 2000-03-11 | [6 empty] | Inspection, has been circled at the top of the form; We re-wrapped about 8 ft. of 2" pipe at new 18" PVC water crossing.
66 | 82-20016-1 | [10 empty] | 1982-01-19 | [5 empty] | BAK | Delete has been written and underlined on the front of the form.
66 | 82-20015-1 | [10 empty] | 1982-01-19 | [6 empty] | Delete has been written and underlined over the front of the form; Leak is at valve packing on "Standard Oil" line
66 | 75-20144- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-11-04 | 1976-05-10 | Replace Pipe and/or Service |  | Steel |  | BAK | Ser. should be inserted; Inserted ser.; Corrosion spots on pipe; Complete
|  |  |  | 3" | [11 empty] | Steel |  | Bakersfield | Relocated ser and insert 1/2" Plse.
|  |  |  | 3/4" | [11 empty] | Steel |  | Bakersfld | relocated ser and insert 1/2" plse.
|  |  |  | 3" | Distribution Main | [10 empty] | Steel |  | Bakersfield | Inspection has been circled on the front of the form; Inserted ser - Leaking; Corrosion on main
25 | 80-60092- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1980-10-17 | 1980-10-17 | Replace Pipe and/or Service |  | Steel |  | Bksfld. | Two dates written for repair, second repair date listed as 12-30-80; Installed 3/4" leak clamp on riser service will have to be relayed. Permit & service order ASAP
66 | 83-20022- | L-19 |  | 0.5 | Distribution Main |  | Other |  |  | Other |  | 1983-01-10 | 1983-01-10 | Other |  | Steel |  |  | Notes included in comments section are badly faded and illegible at this point.
25 |  |  |  | 0.75 | [7 empty] | 1994-01-31 |  |  |  | Steel |  | BKRSLFD
|  |  |  | 3" | [11 empty] | Steel |  | Bakersfield | Inspection has been circled on the rear side of A-Form; Install 2" PL Gas Main
|  |  |  | 3" | [11 empty] | Steel |  | Bakersfield | Inspection has been circled on the front of A-Form
|  |  |  | 12 | Transmission | [10 empty] | Steel |  | BKSFLD. | Inspection has been circled on the front of the form; Installed Line Marker; Unable to read final word in comments section
|  |  |  | 3 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Bakersfield | Inspection has been circled on the front of the form;
66 | 82-20264- |  |  | 3" | [7 empty] | 1982-07-19 |  |  |  | Steel |  | BAK
66 | 88-60037-1 |  |  | 8 | Distribution Feeder Main |  | Physical/Mechanical Joint |  |  | Other |  | 1988-12-09 | 1988-12-15 | Tighten Cap or Bolt |  | Steel |  | Bakersfield | There was slight pitting on 8" to 12" reducer
|  |  |  | 3" | [11 empty] | Steel |  | BKSFLD | Inspection has been circled at the top of the form; Inserted and Branched 1/2" Plastic Ser Due to Cond 1/2" Copper Gas Ser at 315 30th St.
|  |  |  | 8" | [11 empty] | Steel |  | BKSFLD | On the back of the form the word "Inspection" has been circled.
25 |  |  |  | 12 | Transmission | [10 empty] | Steel |  |  | Installed line marker sign
|  |  |  | 3/4" | [11 empty] | Steel |  | BKSFLD. | Abandoned service at main
|  |  |  | 6 | Distribution Main | [10 empty] | Steel |  | BKSFLD. | The word "Inspection" has been circled at the top of the form;
|  |  |  | 4" | [11 empty] | Steel |  | BKSFLD. | Installed 1/2" Pl. services
|  |  |  | 6 | [11 empty] | Steel |  | Bakersfield | Abandoned 18' of 3/4" Stl. Servc
|  |  |  | 6" | [11 empty] | Steel |  | BKSFLD. | Installed 1/2" Pl. Service
|  |  |  | 6" | [11 empty] | Steel |  | Bksfld. | The word "Inspection" has been circled at the top of the form; Installed 1/2" Pl ser S.O. 348622
66 | 82-20012-1 | [10 empty] | 1982-01-08 | [6 empty] | Delete has been written and underlined across the front of the form
25 |  |  |  | 2 | [11 empty] | Steel |  | Bakers.
66 | 78-60028-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1978-03-22 | 1978-03-23 | Replace Pipe and/or Service |  | Steel |  | Bksfld.
|  |  |  | 0.75 | Gathering |  | Other |  |  | Other |  | 1979-12-03 |  | Other |  | Steel |  | Bakersfield | This was a customer houseline leaking.; Additional notes written beneath, though the writing is badly faded and illegible at this point
66 | 78-20035-1 | [10 empty] | 1978-02-23 | [5 empty] | BAK | Delete has been written across the front of the form; Delete
|  |  |  | 2 | Distribution Main | [10 empty] | Steel |  | BKSFLD.
25 |  |  |  | 2.38 | Distribution Main | [10 empty] | Steel |  | Bakersfield
|  |  |  | 2" | [11 empty] | Other Plastic |  | BKRSFLD.
25 |  |  |  | 4 | [11 empty] | TR 418 |  | Bakersfield
25 | 79-60050-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-04-16 | 1979-05-31 | Replace Pipe and/or Service |  | Steel |  | B.K. | Need survey over main & service at 1001 30th St on Espee St Gas leak; Follow up; Repair date on rear side of form differs from date listed on the front of the form, repair date on rear of form listed as 5/29/1979.
25 | 79-60048-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1979-04-30 | 1979-04-30 | Clamp | REPLACE PIPE AND/OR SERVICE | Steel |  | Bakersfield | Install 5 lk clamps on main 4-30-79 J. Vie; Replaced main with 4" plastic insert see w/o 3-4666-e RHD; Beneath Repair Code reads the following: PR 5-31-79; Repair date listed on rear of form differs from date listed on the front of the form, date listed as 5/29/79
66 | 75-00083- | [10 empty] | 1975-05-29 | [5 empty] | BKSFLD. | Delete has been written across the front of the form and is included in the comments section.
25 |  |  |  | 2 | Distribution Main | [10 empty] | Steel |  | BKSFLD | Water under wrap
66 | 79-20131-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-04-27 | 1979-05-31 | Replace Pipe and/or Service |  | Steel |  | BAK. | No leak per const. 4-27-79; Press tested serv. 50 lb no leaks - Press tested 100 lb no leaks - Inserted serv.
66 | 77-23393-1 | [10 empty] | 1977-09-19 | [5 empty] | Bakersfield | Delete has been written across the front of the form; File & follow up
|  |  |  | 12 | Transmission | [10 empty] | Steel |  | BKSFLD. | Installed Link Marker Sign
|  |  |  | 4" | [11 empty] | Steel |  | BKSFD | Abandoned 1 1/4" L.P. service at tee.
|  |  |  | 12 | Transmission | [10 empty] | Steel |  | BKSFD. | Installed line marker sign
|  | 142 |  | 4.12 | [11 empty] | Steel
|  | 142 |  | 12 | Transmission | [10 empty] | Steel |  | BKSFD | Installed line marker.
66 | 87-20013-1 | 142 |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1987-01-19 | 1987-01-22 | Clamp |  | Steel |  | BKSD | Notes in comments section badly faded, illegiible
66 | 85-20228-1 | [10 empty] | 1985-07-10 | [5 empty] | BKSD
25 | 79-40025-1 |  |  | 0.34 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-04-11 | 1979-04-11 | Replace Pipe and/or Service |  | Steel |  | E.B.K.
66 | 75-00036-1 | [10 empty] | 1975-05-22 | [5 empty] | BKSFLD. | Delete written across the front of the form; Follow-up; DELETE
|  |  |  | 3 | Distribution Main | [10 empty] | Steel |  | BKSFLD. | ;
66 | 75-00035-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1975-05-22 | 1976-09-21 | Clamp |  | Steel |  | BKSFLD. | Insert service (unable to read rest of note, ink badly faded); Found rock imbedded in wrap on top of main causing leak; Completed 9/22/76 KED
|  |  |  | 3 | [11 empty] | Steel |  | E.B.K.
|  |  |  | 3 | [11 empty] | Steel |  | BKSFLD.
|  |  |  | 3 | Distribution Main | [6 empty] | 1973-01-12 |  |  |  | Steel
66 | 84-60025-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1984-02-24 | 1984-04-30 | Replace Pipe and/or Service |  | Steel |  | Bakersfield | Re Run Service
66 | 85-20229-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1985-01-10 |  | Replace Pipe and/or Service |  | Steel |  | BKSD | Notes in comments section badly faded and unable to read; unable to read repair date as well
25 | 82-60043-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by Electrical Defect |  | 1982-07-20 | 1982-07-20 | Replace Pipe and/or Service |  | Other Plastic |  | Bksfld | ...1/2" PL service by...2, 1/2" PL. couplings; partial comment illegible due to fading.
66 | 82-40005-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1982-01-15 | 1982-01-15 | Replace Pipe and/or Service |  | Other Plastic |  | Baksfld | Repaired 1/2" Pl. service - Installed 2 - 1/2" amp fit coupleings & 18" place 1/2" Pl tubing.
| 82-40127 | 142 |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1982-12-02 | 1982-12-02 | Clamp |  | Steel/Wrought Iron |  | Bksfld | Repaired corrosion leak in 16" Trans Main 142 mo. Apprent hloe and 2" area affected. Repaired ... by install 1-16 Skinner repair clamp; Repaired 16" Trans Main temp by installed 1-16" skinner clamp. Ins 18" x 16" Full circle sleeve (taped main) API 5Lx42 ASTM A441 .500" wt 50,000 SMYS
66 | 82-20018 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1982-01-19 | 1982-12-14 | Other | Permanent | Steel/Wrought Iron |  | Bak | Temp clamp installed 16" x 12" Full sleeve. Taped main. API 5L x 42 ASTM A441 .500" w.t. 50,000 SMYS
66 | 82-20017-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1982-01-09 | 1982-12-08 | Clamp |  | Steel/Wrought Iron |  | BAK | installed temp repaire clam. Perm repair made 12.15.82 installed 18" complete circle weld patch P.L.O; Made temp repairs by installing 16" temp clamp. Permanent repairs were made by welding complete circle weld patch over leak area 12-15-82.
66 | 83-20026 |  |  | 12 | Transmission | [6 empty] | 1983-01-12 |  |  |  | Steel/Wrought Iron |  | Rosedale | ...gas...in ground from previous leak. Repaired...; partial comment illegible.
66 | 82-20188 |  |  | 3 | Other |  | Physical/Mechanical Joint |  |  | Other |  | 1982-05-06 | 1982-05-10 | Other | Permanent | Steel/Wrought Iron |  | BAK | Loose flange. Tightened. 5-10-82
66 | 83-60004 |  |  | 10 | Transmission |  | Regulator |  |  | Other |  | 1984-03-21 | 1984-04-20 | Other | Permanent | Steel/Wrought Iron |  | BAK | Repaired leaking relief on secondary set.
66 | 83-20000 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other |  | 1983-01-03 | 1983-01-10 | Other | Permanent | Steel/Wrought Iron |  |  | Tighten valve.
66 | 84-20019-1 |  |  | 0.5 | Other |  | Other |  |  | Other |  | 1984-01-19 | 1984-02-02 | Other | Permanent | Steel/Wrought Iron |  | Bakersfield | Tightend loose flanges and redoped
66 | 85-20001-1 |  |  | 10 | Transmission |  | Other Welds |  |  | Construction Defect |  | 1985-01-02 | 1985-01-07 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Bksd | the 2" weld gas on top of main was leaking over the leak pits. The...on the weld; to find leak on Gsford Rd, look for sewer 1/400/... Between 400/11 and leak will be appx 105 ft east of pole #1/400/1V; partial comment illegible due to fading.
66 | 83-20262-1 |  |  | 0.75 |  |  | Regulator |  |  | Other |  | 1983-07-26 | 1983-07-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | line use illegible due to fading; comment illegible due to fading.
|  |  |  | 4 | [7 empty] | 2007-08-23 |  |  |  | Steel/Wrought Iron |  | Bakers | installed 3 watering ETS over anodes
66 | 82-20181 | [10 empty] | 1982-04-26 | 1982-05-10 |  |  |  |  | BAK. | * check pit "ok" no ... open area refer to crew. (5-7-82) Ran BAR test around pit found nothing. Found 10% reading inside second pits. 5-10-82 Found leak on CAP of TEE inside pit
66 | 78-40061-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-08-15 | 1978-08-15 | Other | Permanent | Other Plastic |  | Bakersfield | Made permanent repairs with 2" couple & 2" elbow. Plastic.
66 | 85-20136-1 |  |  | 12 | Transmission |  | Valves |  |  | Other |  | 1985-05-31 | 1985-06-19 | Other | Permanent | Steel/Wrought Iron |  | Greenacres
66 | 85-20011-1 |  |  | 6 | Transmission |  | Fitting |  |  | Other |  | 1985-01-08 | 1985-02-21 | Other |  | Steel/Wrought Iron |  |  | redped & tightned fittings.
|  |  |  | 10 | Transmission | [12 empty] | BAK | Installed cathodic protection wire on 142-5
[16 empty] | Steel/Wrought Iron |  | Bakersfield
66 | 76-60023-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1976-07-23 | 1976-07-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bakersfield
Bakersfield
|  |  |  | 4 | [8 empty] | 1988-11-14
66 | 74-00088-1 | [10 empty] | 1971-12-20 | [5 empty] | Bksfld. | Line use illegible; Service tap checked ser... checked- nothing 15ppm m.c.s. 10-3-77. Checked - Background reading m.c.s. 10-19-78
66 | 85-20138-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1985-05-31 | 1985-06-20 | Other |  |  |  | Bakersfield
66 | 84-20012-1 |  |  | 0.5 | Other |  | Other |  |  | Other |  | 1984-01-17 |  | Other | Permanent | Steel/Wrought Iron |  | Bakersfield | repair date illegible; comment illegible due to fading.
66 | 83-20158 | [10 empty] | 1983-04-08 | [5 empty] | Bak
66 | 82-20193 |  |  | 2 | Other |  | Other |  |  | Other |  | 1982-05-12 | 1982-05-17 | Other | Permanent | Steel/Wrought Iron |  | Bak | Repaired leaking diaphram in pilot
|  |  |  | 12 | [11 empty] | Steel |  | Bakersfield
25 |  |  |  | 12 | Transmission | [9 empty] | Permanent | Steel/Wrought Iron |  | Bakersfield | took petential @ interface of L-142-s, 2' w/o control - 950; Pits found were covered by 12" P.C.F. Pits approx 3/16" deep.
Bakersfield
|  |  |  | 12 | [11 empty] | Steel |  | Bakersfield | Found bad pit on exist. 12" main. Installed 12" P.C.F. over pit when tie-in was made.
66 |  |  |  |  | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Bakersfield
|  | 142 |  | 8.58 | Distribution Main | [10 empty] | Steel/Wrought Iron
|  |  |  | 8 | Distribution Main | [6 empty] | 1976-01-20 |  |  |  | Steel/Wrought Iron
|  | 142 |  | 12.34 | Transmission | [10 empty] | Steel/Wrought Iron |  | Bakersfield
66 | 79-20259-1 |  |  | 2 | Other |  | Body of Pipe |  | CUST. HOUSE LINE | Damage by outside Forces | CUST. HOUSE LINE | 1979-07-12 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Bak | repair date illegible due to fading; Note! conducted Bar leak test on...Leakage found leaking house line where it goes into blds. Leak was...; leakage was in customer house line and repaired; partial comment illegible.
|  |  |  | 4 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Bkrfld
66 | 90-20086-1 |  |  | 4 | Distribution Main |  | Other |  |  | Construction Defect |  | 1990-03-29 | 1990-05-30 | Replace Pipe |  | TR 418 |  | BAK | Replaced sections of main. removing 4" TR 418 Tee.
66 | 79-20259-1 |  |  | 2 | Other |  | Body of Pipe |  | CUST. HOUSE LINE | Damage by outside Forces | CUST. HOUSE LINE | 1979-07-12 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | BAK | repair date illegible due to fading; Note! Conducted BAR test on...leakage found leaking house line where it goes into blds. leak was...; leakage was in customer house line and repaired; partial comment illegible
| 09-81138-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2009-08-03 | 2009-09-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Bakersfield | BG D-335 s/o south & n/o V Z-155, X/ST White Ln; removed, redoped, replaced fittings; soap tested OK.
| 09-81139-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2009-08-03 | 2009-09-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Bakersfield | BG D-335 at middle pit, X/ST Whtie Ln; Soap tested OK
| 09-81140-1 |  |  | 2 | Transmission |  | Other |  | No gas found | Unknown |  | 2009-08-03 | 2009-09-23 | Other | No Leak | Steel/Wrought Iron |  | Bakersfield | BD D-335 3' N/o mid pit, X/ST White Ln; No Gas found; Leak test completed no gas found.
| 09-81141-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2009-08-03 |  | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Bakersfield | BG D-335 at North pit, X/ST White Ln; removed, redoped, replaced fittings; soap tested ok.
66 | 11-20180-1 | 142N | [9 empty] | 2011-05-03 | [5 empty] | Bakersfield | L-142-N E/o Henry Ln on N/S of Downing
66 | 11-20180-B | 142N |  | 10 | Transmission |  | Body of Pipe |  |  |  |  | 2011-05-03 | 2011-05-03 |  |  | Steel |  |  | Leak located on L142 N. Just east of Henry Ln on Downing; Determined So. Cal line across street at 80%; Upon arival star drilled 15 holes over L-142N. Found gas. Called superviseor upon finding gas - continude survey every hour with airiating at 1700 time - with supervisor standing by - later found so. cal gas line across the street leak serveyed and found 80% Gas. It was dettermind there gas line was leaking when they have completed work we will resurvey.
66 | 10-20044-1 | 566 |  | 2 | Transmission >= 20% SMYS |  | Line Valve |  |  | No/Deteriorated Pipe Dope |  | 2010-03-09 | 2010-12-03 | Remove/Replace Completion Plug Fitting |  | Steel |  | Shandon | line # illegible; Valve box; bottom of valve; shut valve off and repaired leak; excaveted around 2" transmission main and valve, found leak at bleed line at bottom of valve. - shut valve and repaired leak.
| 10-20506-1 |  |  | 3 | Transmission |  | Valves |  |  | Construction Defect |  | 2010-01-25 | 2010-04-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Edwards | 3" valve in casing JPL Feeder EAFB; tightened nuts on top of vavle collar; soap tested
| 10-20528-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2010-03-18 | 2010-03-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Red Mtn. | Red MTN Reg Sta box w/o tap valve 26.59 various leaks; removed, doped replaced fittings; soap tested ok
| 10-20527-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2010-03-18 | 2010-03-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Red MTN. | tap valve box line 311 26.59. Various leaks; Removed, redoped, replaced fittings; soap tested.
| 10-40067-1 | [10 empty] | 2010-04-24 | [5 empty] | Bakersfield | Gosford Reg sta D-401; Found no leak;
| 10-40067-1 | [5 empty] | Fitting |  | GREASE FITTING | Other | Needs Grease | 2010-04-24 |  |  |  | Steel/Wrought Iron |  | Bakersfield | Gosford N/O Panama Ln; Small bubbling on grease fitting;
| 10-81000 | [10 empty] | 2010-10-08 | [6 empty] | North east corner of montery and Miller;
| 10-81020 | 142N. | [9 empty] | 2010-10-08 | [6 empty] | leak on underground valve at Arro & Gilmore;
| 10-81021 | [10 empty] | 2010-10-09 | [5 empty] | Bakersfield | Leak at reg station on NW corner of Union Ave & Monterey st;
| 10-81040 | [10 empty] | 2010-10-08 | [6 empty] | West side of Wible Rd in front of PG&E yard;
| 10-81060 | [10 empty] | 2010-10-08 | [5 empty] | Tehachapi | Reg station, underground on San Juan, Between Martingale & Plantation
| 10-81140 | [10 empty] | 2010-10-10 | [5 empty] | Bakersfield | E. of rail road trax next to barn;
| 10-81141 | [10 empty] | 2010-10-10 | [5 empty] | Bakersfield | California Dairys 1/2 mile south of 223
| 10-81180 | [10 empty] | 2010-10-09 | [5 empty] | Taft | Taft meter station D-200 & D-205, corner of Lincoln & Ash
| 10-81300 | [10 empty] | 2010-10-07 | [5 empty] | Mojave | Cal port cement Pri reg sta is 500 ft south of Oak Creek Rd;
| 10-81301 | [10 empty] | 2010-10-07 | [6 empty] | station inside cement plant. go through main gate & take a right;
| 10-88020-1 | [16 empty] | Backersfield | 18% in valve box. 18' North of GPS Mile Point # 300, 50A;
| 10-88021 | [10 empty] | 2010-10-16 | [5 empty] | Bakersfield | Bakersfield tap reg. station
66 | 10-88120-1 | [10 empty] | 2011-10-16 | [5 empty] | Bakersfield | Leak is 50' south of well #35 surrounded by yellow pole barrier and marked on ground with paint.
| 10-88121 | [10 empty] | 2010-10-16 | [5 empty] | Oildale | 1/4 mi from Reed cny & 33 North rd intercscton
66 | 10-88240-1 | [10 empty] | 2010-10-19 | 2008-11-20 | Other | REPACK STEM PACKING TURN VALVE TO OPERATE TO ELIMINATE LEAK |  |  | North Edwards | vale box on north end marked w zip tie; Repack stem packing to repair leaks.
| 96-20515-1 | 311-12 | 26.17 | 10 | Transmission |  | Valves |  |  | Other | Packing leaking | 1996-06-25 | 2008-11-19 | Other | REPACK STEM PACKING TURN VALVE TO OPERATE TO ELIMINATE LEAK |  |  | Red Mountain | On Line-311 Sheet-12, Redmountain; around valve 26.17 E/ of HWY-395; over valve; downgrade to #3; base of V-26.17: Line-311;
| 96-20514-1 | 311-4 | 17.39 |  | Transmission |  | Valves |  |  | Other | Packing leaking | 00/25/1996 | [5 empty] | Atolia | Line-311 Sheet-8, Atolia; Arount valve at M.P. 17.39; Change grade #3; leak was change per john B. 2- #3 befor; Base of V-17.39: Line-311
| 96-20516-1 | 311-12 | 26.17 | 10 | Transmission |  | Valves |  |  | Other | Packing Leaking | 1996-06-25 | 2008-11-20 | Other | REPACK STEM PACKING TURN VALVE TO OPERATE TO ELIMINATE LEAK | Steel/Wrought Iron |  | Red Mountain | On line-311 Sheet-12, Redmountain; around valve 26.17 E/of hwy-395. Over valve. downgrade to #3. Base of V-26.17: Line-311. Same as above; Repack stem packing to repair leaks.
| 97-20508-1 | 311-4 | 8.7 | 10 | Transmission |  | Valves |  |  | Other | Packing leaking | 2008-11-20 | 2008-11-20 | Other | REPACK STEM PACKING TURN VALVE TO OPERATE TO ELIMINATE LEAK |  |  | Kramer | On line-311 sheet-4; vavle-8.70 (valve A). valve-8.70 (valve A). Over valve. Base of V-8.70: Line-311. Same as above; Repack stem packing to repair leaks
| 05-40132-1 | 311 | 34 | [8 empty] | 2005-10-11 | [5 empty] | Kramer | Duplicate leak, deleted from IGIS. On 10/15/2010; Line 311 Hwy 58 crossing at vent; at vent line 311 hwy 58 crossing. At vent on S/S of Hwy 58
| 08-20506-1 | 311 | [9 empty] | 2008-03-04 | [5 empty] | Kramer | vent: hwy-58 at ETS on N/S of Hway-58. E?O Kramer .2; At vent: S/S of Hwy-58. ETS on N/S Hwy. Vent: S/S Hwy-58. EST on N/S Hwy-58. TS N/S of HWY 58. No read S/S of Hwy. At vent on S/S off of Hwy 58.
| 08-20004-1 | [10 empty] | 2008-01-15 | [5 empty] | Bakersfield | Duplicate leak#, Leak deleted. RTK6 - 1/14/09; East Reg. Pit; see leak #06-20002-1;
| 09-20570-1 |  |  | 4 | Transmission |  | Fitting |  |  | Construction Defect |  | 2009-06-26 | 2009-09-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Kramer | Plug on top of primary filter; Plug on top of Primary filter; Tightened Plug; Soap tested all ok.
09-20570-1 | 09-20570-1 |  |  | 4 | Transmission |  | Fitting |  |  | Construction Defect |  | 2009-06-26 | 2009-09-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Kramer | Plug on top of primary filter; plug on top of Primary filter; plug on top of primary filter; soap tested ok
| 09-40049-1 |  |  | 8 | Transmission |  | Girth Weld |  |  | Weld Failure |  | 2009-03-13 | 2009-03-15 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | Ridgecrest | .02% main; Trans. main; Welds were inspected by Valley Industrial x-ray; Installed welded 8" sleeve over leaking weld sleeve is 12" long.
| 09-40180-1 |  |  | 0.5 | Gathering |  | Riser |  |  | Material Failure |  | 2009-10-26 | 2009-10-26 | Replace Partial Service |  | PE2406 (Yellow or Orange) |  | Taft | On riser below stopcock; replaced riser; replaces riser with short permasat riser and 1' of new plastic with 1-1/2" coupling
| 09-20578-1 |  |  | 2 | Transmission |  | Fitting |  |  | Construction Defect |  | 2009-08-20 | 2009-09-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Daggett | X/ST Solar One - Segs Primary R-621; Segs Primary R-621 at various above grou; Segs Primary R-621 various; removed, redoped, replaced various fittings; soap tested all ok
| 09-20578-1 |  |  | 2 | Transmission |  | Fitting |  |  | Construction Defect |  | 2009-08-20 | 2009-09-09 |  |  | Steel/Wrought Iron |  | Daggett | X/ST Solar One - Segs Primary R-621; Segs Primary R-621 at various above grou; segs Primary R-621 various leaks; Soap tested all ok
| 09-20571-1 |  |  | 0.25 | Transmission |  | Fitting |  |  | Construction Defect |  | 2009-06-26 | 2009-09-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Kramer | West most Reg. Sta. box on T-181.79A; Leak auto oiler; removed, redoped, replaced; different line size on second page, 06.00;
| 09-20571-1 |  |  | 0.25 | Transmission |  | Fitting |  |  | Construction Defect |  | 2009-06-26 | 2009-09-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Kramer | West most Reg. Sta. Box on T181.79A; reoved, redoped, replaced; Different line size on second page, 06.00; soap tested, OK
| 04-20162-1 |  |  | 1 | Service |  | Fusion Joint |  |  | Construction Defect |  | 2004-04-06 | 2004-04-06 | Service Partially Replaced |  | Aldyl A (Tan or Gray) |  | Bakersfield | 10% over Bellhole in Alley & on ser in back yard; bellhole in ally 10% coek ser in yard; Location remards illegible due to fading; Repair remarks illegible due to fading; Comments illegible due to fading
| 04-20000-1 | 142 | [9 empty] | 2004-01-06 | [5 empty] | Bakersfield | over line 142 in pit w/o pcf; end of Fairhaven Dr. W/o pcf on 1-142. Zero redings over main/pcf;
| 04-20000-1 | 142 | [9 empty] | 2004-01-06 | [5 empty] | Bakersfield | over line 142 in pit w/o pcf; end of Fairhaven Dr. W/o pcf on 1-142. Zero reading on main
| 03-20000-1 | 376 | [9 empty] | 2003-01-29 | [5 empty] | Oildale | L-376 on N.33 & Reed Canyon at well 544/in yellow; at well 544 on main/N.33 & reed Canyon r. Gas extracted from ground found to be of different origin than gas from P.G.E line. Tested done by Zalco Labs. 3-6-03 *see lab results;
| 03-20005-1 |  |  | 4 | Distribution Main |  | Fitting |  |  | Material Failure |  | 2003-11-05 | 2003-11-06 | Other | REPLACED 4" PLASTIC ELL | TR 418 |  | Bksfld | over vale in st; Over main. over 4" main at ell woso street; replaced leaking 4" plastic ell; installed 4"x1" pl tee for by-pass. Installed new 4" butt-fusion ell and (2) electro-fusion couplings to make repair. installed 4"x1" for by-pass
| 97-20508-1 | 311-4 | 8.7 | [8 empty] | 1997-11-13 | [5 empty] | Kramer | On line-311 Sheet-4; valve-8.70 (Valve A);
| 97-20508-1 | 311-4 | 8.7 | [8 empty] | 1997-11-13 | [5 empty] | Kramer | On line-311 sheet-4; valve-8.70 (valve A); down grade to #3
| 03-20023-1 | 311 | 31.97 | [8 empty] | 2003-09-23 | [5 empty] | Atolia | over main line valve; over main line valve 31.97;
| 03-20019-1 | 311 | 6.71 | [8 empty] | 2003-09-23 | [5 empty] | Atolia | at Boron Prison tap; at tap 6.71;
| 97-20509-1 | 311-4 | 8.7 | [8 empty] | 1997-11-13 | [5 empty] | Kramer | On line-311 sheet-4; valve-9.70 (valve B);
| 98-20502-1 | [10 empty] | 1998-03-03 | [5 empty] | Ridgecrest | Line 311 - valve 43.82; valve 43.82 (372 tap); around valve stem.
| 03-20019-1 | 311 | 6.71 | 0.75 |  |  | Valves |  |  | Equipment Malfunction |  | 2009-05-28 | 2009-06-25 | Other | Grease Valve | Steel/Wrought Iron |  | Atolia | C Boron Prison tap: t-6.71, Line 311
| 03-20019-1 | 311 | 6.71 | 0.75 | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2003-09-23 | 2009-06-25 | Other | GREASE VALVE | Steel/Wrought Iron |  | Atolia | At Boron Prison tap: t-6.71, Line-311; replace grease fitting, greased; soap tested
| 02-20006-1 | 376 | [9 empty] | 2002-01-08 | [5 empty] | Bakersfield | Myers Dam Rd & Getty Frwy; leak out of E.T.S. Found no leak
| 02-20007-1 | 142S | [9 empty] | 2002-01-08 | [5 empty] | Bakersfield | Gosford Reg. Sta. at fire valve; leak at fire-valve;
| 02-20008-1 |  |  | 2 |  |  | Fitting |  |  | Other | Loose | 2002-01-08 | 2002-11-25 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Bakersfield | White Ln. & gosford Rd. at reg sta.; tightened fittings;
| 02-20030-1 | 142N. | 11.3 | 12 | Transmission |  | Valves |  |  | Other | Needed grease | 2002-01-16 | 2002-01-24 | Other | GREASED VALVE | Steel/Wrought Iron |  | Bakersfield | N/W corner of Gilmore & Standard St.; over trans line/dist. valve # 11.29-2 leaking. Valve greased - delete leak; Changed out grease fitting and filled with grease; changed out grease fitting on valve and filled with grease to stop gas leak;
| 01-20001 |  |  | 0.75 | Distribution Main |  | Fitting | Regulator | REGULATOR | Other |  | 2001-01-22 | 2001-01-25 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Wasco | 5% at reg pits in st; at reg pits; Removed, redoped, replaced cap on pin-off tee.;
| 00-20000-1 |  |  | 0.75 | Distribution Main |  | Fitting | Regulator | REGULATOR | Other |  | 2000-01-03 | 2000-06-20 | Tighten Cap or Bolt | DIAPHRAM | Steel/Wrought Iron |  | Bakersfield | out of reg pits at school; out reg pits at school; replaced leaking, diaphram, removed, redoped, fittings, rechecked ok;
| 00-20006 | [16 empty] | BKFD | .04 percent; Reed Cyn side of road flat ground. leak surveyed and opened bell hole - will send samples to lab for natural gas verification
| 00-20006-1 | 376 | [9 empty] | 2000-01-20 | [5 empty] | Bakersfield | Reed Canyon rd. 1/5 mi from North rd.; Reed Canyon rd 1/5 mi. from north rd. DG#2 soil sample sent to lab. Bar test over L376 Reed Cyn 1100' s/o North Rd. Delete;
| 00-20007-1 | [16 empty] | Bakersfield | Badger Cr. CO-GEN on service line; 1 mi e/o Oilfield Rd to Badger Cr. readings over Destec line 6". Readings are much higher over Destect line. Delete leak, delete line, leak is on S. Adams 7-3-00;
| 00-20007- | 375 | [9 empty] | 2000-02-20 | 2000-01-20 |  |  |  |  | Bksfld | 10% + o/serv line to co. gen.; o/serv line. aprox 50' from tap reading over 10" destec line; Readings over destec line; Hot location - #B
| 00-20008-1 | 375 |  | 8 | Transmission |  | Other |  | None Leaking | Other | NOT LEAKING | 2000-01-20 | 2000-06-20 | Other | Not leaking | Steel/Wrought Iron |  | Bksfld | 10%+ out of valve valts (2) at road; valve valts (2); soap tested and found no leaks;
| 00-20009-1 | 375 |  | 0.75 | Distribution Main |  | Regulator |  |  | Material Failure |  | 2000-01-20 |  | Other | NEW DIAPHRAM | Steel/Wrought Iron |  | Bksfld | 10%+ out of reg pits (3); reg pits; removed regulator, replaced diaphram, reinstalled, recheck no leaks;
| 00-20010 |  |  | 0.75 | Distribution Main |  | Other |  | Relief | Unknown |  | 2000-01-21 | 2000-03-30 | Other | reset pressure. | Steel/Wrought Iron |  | Bksfld | 10% at reg pit; at reg pit; Reset pressure, rechecked no leaks;
| 00-20011 | 142S |  | 4 | Distribution Main |  | Fitting |  |  | Unknown |  | 2000-01-24 | 2000-05-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Bksfld | North reg pit leaking 1%; n/ reg pit; removed, doped, replaced, rechecked ok;
| 00-20012 | 142S |  |  | Distribution Main |  | Fitting | Regulator | REGULATOR | Other |  | 2000-01-24 | 2000-02-24 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Bksfld | Reg pits leaking 1%; Reg pits (2); redoped & tightened fittings;
| 00-20026-1 | 142S |  | 3 | Transmission |  | Unknown |  | CUSTOMER HOUSE LINE | Unknown |  | 2000-02-01 | 2000-03-17 |  |  | Steel/Wrought Iron |  | Bksfld | 10%+ over line in field both sides of st; over line. Over L-142/HP. Over Trico lines. 4" Pl. checked OK. Found no leaks 3/17/00; Trico Oil Co. has made repairs.; soaped 3" T.P. Line
| 00-20026-1 | [5 empty] | Unknown |  |  | Unknown |  | 2000-02-01 | 2000-02-08 | Other |  |  |  | Bakersfield | 200' e/o 325 Belle Terrance xst. Union; over main at gas well; over 3" T.P at 90 degree. Over 4" HP Pl. Found no leaks 3/17/00; leak may be from Trico; soaped PG&E lines - no leak;
| 08-20004-1 | [10 empty] | 2008-01-15 | [5 empty] | Bakerfield
| 08-20012-1 | 312 |  | 0.75 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2008-01-29 | 2009-01-29 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Bakersfield | Dup leak-info from leeak #09-20025-1; Duplicate leak - info from leak #09-20025-1
| 08-20013-1 |  |  |  | Transmission |  | Regulator |  |  | Other |  | 2008-01-30 | 2008-02-20 | Tighten Cap or Bolt | Other | Steel/Wrought Iron |  | Bakersfield | Tightened fittings and replaced diaphram on regulator
| 08-20015-1 | 300B |  | 6 | Distribution Main |  | Other |  |  | Other |  | 2008-01-30 | 2008-02-20 | Other | Greased valve | Steel/Wrought Iron |  | Bakersfield | Greased valve and rechecked, ok.;
| 08-20034-1 | 306 |  | 0.75 | Distribution Main |  | Valves |  |  | Equipment Malfunction |  | 2008-03-06 | 2009-06-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Shandon | Removed, redoped, replaced cap on pin-off tee rechecked, OK
| 08-20163-1 | 300 |  | 0.75 | Single Service |  | Fitting |  |  | Other | LOOSE FITTING | 2008-07-28 | 2008-07-28 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Shafter | Tightened union fittings in 2 pits. Rechecked ok.
| 08-20506-1 | [16 empty] | Kenner
| 08-00001-1 | L-313 | [15 empty] | Lucerne Valley | IN El Vaquerro hotel tap box and to the east of box, Could be the pipe running from L-313 tap to reg. box
| 08-20520-1 | 372 |  | 2 | Transmission |  | Valves |  |  | Construction Defect |  | 2008-07-31 | 2009-09-23 | Other | Grease valve | Steel/Wrought Iron |  | Ridgecrest | Greased valve; Soap tested all ok
| 06-20058-1 |  |  | 0.25 | Distribution Main |  | Fitting |  |  | Other |  | 2006-07-27 | 2006-08-02 | Tighten Cap or Bolt |  | Other |  |  | Gun Club & hwy 46 middle pit; middle pit close to school 5'+~; Leak repaired; minor leak 1/4" fitting;
| 06-20059-1 |  |  | 2 | Distribution Main |  | Other |  | 1/4" fittings | Other | Treads on 1/4" fitting | 2006-07-28 | 2006-08-08 | Other | Fitting | Steel/Wrought Iron |  | Bakerfield | Gosford & White Ln W. Pit; W. pit;
| 06-60077-1 | 312 | 2.14 | 8 | Transmission |  | Body of Pipe |  |  |  |  | 2006-07-18 | 2006-07-18 | Welded Sav-A-Valve - Weld |  | Steel/Wrought Iron |  | Bakersfield | 1/2 mile s/o Bear Mt. 1 mile w/o Old River; welded 2" Sav-a-valve over damaged area; Carlos Mendoa was excavation to bury a deal cow at 12139 Bear Mt Blv. (Palla Rosa Dairie) When he hit L312, a *' transmissioini main operating at 540 PSI. causing gas to exlope. Did not call USA, but know line was tehre. We repaired by lowing line PSI and welding a 2" Sav-A-valve over damaged area.
| 05-20**0-1 | 142S | 9 | 10 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2005-09-08 | 2005-09-09 | Welded Sleeve/Can - Weld | WEDDING BAND | Steel/Wrought Iron |  | BAkers. | Leak # faded, illegible; Welded band around leak - 21" long; 18" band welded over leak;
|  | 142 |  | 16 | Transmission | [7 empty] | 2001-08-30 |  |  | Steel/Wrought Iron |  |  | installed ETS off of L142; installed new E.T.S on 142 N for locating purposes.
|  |  |  | 8 | Transmission | [7 empty] | 2001-09-17 | Other | INSTALLED ETS | Steel/Wrought Iron |  |  | installed (2) wire E.T.S off of E. B Feeder.; Install new ETS
|  |  |  | 4 | Transmission | [7 empty] | 2001-09-06 | Other | INSTALLED ETS | Steel/Wrought Iron |  |  | installed G-S E.T.S. off of E. B feeder in pit.
|  |  |  | 8 | Transmission | [7 empty] | 2001-09-07 | Other | INSTALLED E.T.S. | Steel/Wrought Iron |  |  | installed (2) E.T.S. wires with G-5 box off of E.B. Feeder;
|  |  |  | 4 | Transmission | [7 empty] | 2001-09-24 |  |  | Steel/Wrought Iron |  | BKS | 81' n/o White Ln on So "H" St; inspection only; installed locating wiresto Dist & Trans;
[5 empty] | Transmission | [7 empty] | 2001-09-25 | Other | Installed locating wires | Steel/Wrought Iron |  | BKs | 100' N/O White Ln on So. Union; Inspection only; Installed (2) locating wire off of L142 in to G-5 box
|  | 142 |  | 10 | Transmission | [7 empty] | 2001-10-03 | Other |  | Steel/Wrought Iron |  | Bakersfield | 2' e/o w/o of Ashe on White Ln; inspection only; Installed new E.T.S...; Repair remarks faded; installed (2) locating wires off of L-142. Installed above garound Fink station;
|  |  |  | 8 | Gathering | [7 empty] | 2001-11-13 | Other |  | Steel/Wrought Iron |  |  | installed fink with (2)...8"...feeder.; repair remarks faded.; Comment illegible due to fading.
|  |  |  | 12 | Transmission | [6 empty] | 2001-11-01 |  |  |  | Steel/Wrought Iron |  |  | 130' w/o Union Ave. (Frontage Rd); 2" vent makes 33' offset to East crew extended 2" vent and ETS:
|  |  |  | 12 | Transmission | [6 empty] | 2001-10-24 | [6 empty] | We found old 2" casing 10'-12' from tracks. Old map said 114' of 16" casing;
|  | 142 |  | 16 | Transmission | [7 empty] | 2001-08-30 | Other |  | Steel/Wrought Iron |  |  | installed ETS. off of L-142; Installed new E.T.S on 142 N for locating purposes;
|  | 142 |  | 20 | Transmission | [7 empty] | 2001-08-31 | Other |  | Steel/Wrought Iron |  |  | Installed E.T.S off of L142; installed new E.T.S on 142 N for locating;
|  | 142 |  | 142 | [8 empty] | 2001-09-04 | Other | *** WELD WIRES ON T.P. MAIN |  |  |  | Installed ETS off of L-142; installed new E.T.S on 142 N for locating.
[12 empty] | 2001-03-29 |  |  |  | Steel/Wrought Iron |  | Bakers. | X-St. W. Sumner St. ; installed 2" vent; #10 Loops inside 1" TR418;
|  |  |  | 12 | [7 empty] | 2001-04-04 | [5 empty] | Bakers | Golden state Ave. / "v" st.; ETS wires inside 1" TR418;
|  |  |  | 10 | [11 empty] | Steel/Wrought Iron
|  | L-142 SO. |  | 10 | Transmission | [6 empty] | 2001-09-18 | 2001-09-18 |  |  | Steel/Wrought Iron |  | Bakersfield | Approx 875' w/o El Potrero Dr.;
|  | 21 | [13 empty] | Steel |  | Vallejo
42 | 81-20161-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Material Failure |  | 1981-12-15 | 1982-06-15 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Napa | Leak is located 187' N/O 1st main. Marker n/o r/r tracks.; Welded on 5' 12" sleeve over leak to correct leakage. Leak appeared to be a flaw in the manufacturing of the pipe.
42 | 93-40065-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  |  | 1993-11-04 | Replace Pipe |  | TR 418 |  | Vallejo | H.P.R. Service to toll plaza carquinez bridge 120' North of H.P.R. on service; Replaced 1 ft TRA 10 and 2 1" couplings
42 | 93-40064-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Digin |  | 1993-10-13 | 1993-10-13 | Replace Pipe |  | Steel/Wrought Iron |  | Vallejo | Replace 1' of 3/4' STL pipe H.P.R leaking on FT9 weeds replacing
4 |  |  |  | 12 | [7 empty] | 1990-04-05 |  |  |  | Steel |  | Vallejo
4 |  |  |  | 12 | [7 empty] | 1990-04-05 |  |  |  | Steel |  | Vallejo
4 |  | 210 |  | 4 | [11 empty] | Steel |  | Vallejo
|  |  |  | 0.75 | [13 empty] | Vallejo
42 | 72-0_039-1 |  |  | 4 | Distribution |  | Body of Pipe |  |  | Corrosion |  | 1972-03-10 | 1972-04-04 | Patch Welded |  | Steel/Wrought Iron |  | Vallejo
| 99-40098-1 |  |  | 2 | Distribution Main |  | Valves |  |  | Construction Defect |  | 1999-10-16 | 1999-10-16 | Other | Grease | Steel/Wrought Iron |  | Vallejo | Reg station; Greased valve
| 99-40102-1 |  |  | 6 | Distribution Main |  | Valves |  |  | Construction Defect |  | 1999-10-16 | 1999-12-03 | Other | Greased valve | Steel/Wrought Iron |  | Vallejo | Valve in st.; Valve VT23 in street; Greased & operated valve 'O' Reading with Jw
42 | 91-40032-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Digin |  | 1991-04-17 | 1991-04-17 | Replace Pipe |  | Aldyl A (Tan or Gray) |  | Vallejo | Replace 2' of 1 1/4 PL
42 | 76-00017-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1976-02-11 | 1976-02-25 | Other |  | Steel/Wrought Iron |  |  | Greased valves and soap tested, 2-25-76
4 |  | 210 |  | 2 | [11 empty] | Steel |  | Vallejo
42 | 79-20290-1 |  |  | 3 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1979-10-17 | 1979-10-29 | Other |  | Steel/Wrought Iron |  | Vallejo | Glen Core Animal Center near freeway sign in patch .5%; Valve is leaking on 3" main, refer to M&C mech to grease
42 | 95-20066-1 |  |  | 4 | Transmission |  | Fitting |  |  | Other |  | 1995-05-20 | 1996-10-22 | Other |  | Steel/Wrought Iron |  | Vallejo | Soap fittings & regulators could not find leak
|  |  |  | 8 | [11 empty] | Steel
|  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1987-07-29 |  |  |  | Steel/Wrought Iron |  | Benicia | Install HPR set
42 | 89-60051-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1989-09-07 | 1989-10-11 | Replace Pipe |  | Steel/Wrought Iron |  | Vallejo | Shut HPR off and installed new all welded HPR.
47 | 75-20014-1 |  |  | 24 | Transmission |  | Fitting |  |  | Other |  | 1975-01-07 | 1975-01-29 | Other |  | Steel/Wrought Iron |  |  | Herrmann sta. 10% Small leak on fittings 1/9/75; shut off valve #4 from top & ground filters in cage; Tightened several fittings in station
42 | 76-40042-1 |  |  | 8 | Other | M | Body of Pipe |  |  | Corrosion |  | 1976-06-22 | 1976-06-23 | Clamp |  | Steel/Wrought Iron |  | Vallejo | Replugged main 3/29/79 with 2" main plastic by GC; Installed 6" of main for perm repair
42 | 73-00078-1 |  |  | 8 | Transmission |  | Valves |  |  | Other |  | 1973-12-10 | 1974-02-27 | Other | TIGHTEN BOLTS | Steel/Wrought Iron |  | Vallejo | Butte St. & Mare Island Rd. Causeway; Intersection marked with yellow paint, leakage at flange on 8" line - retightened all bolts & stopped leakage - 2-27-74
42 | 79-20029-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1979-01-22 | 1979-04-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Vallejo | Replace leaking 3/4" STL pipe 10 drip and install meuller box over drip inline with main. 4-10-79
42 | 75-60026-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1975-05-28 | 1975-06-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Benicia | WR & W 13th ST Benicia SE corner west side of 1298 readings .03 & .1; No reading 2-2-76; Found a 3' section of 4" pipe that had raked over by a backhoe. The pipe was leaking in 3 locations. I installed perminent leak clamps a one nine pound anode.
42 | 72-00093-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-11-08 | 1973-05-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | ATTN. Joe, This section of main was replaced, Leon; "over"; In front of #1298 West K St; 5' Temp leak clamp installed
42 | 98-40041-1 |  |  | 0.75 | Service |  | Tap Connection |  |  | Other |  | 1998-06-11 | 1998-06-11 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Benicia | Over main at H.P.R. Tee; Repair leak on cap.
42 | 74-00042-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-01-17 | 1974-03-27 | Clamp |  | Steel/Wrought Iron |  | Benicia | Gucker LN. 50% (weldor on this repair); No elect V.G.; W/S Gucker LN 500' S/O freeway; Installed temporary stainless leak clamp at this location - clamp is south end of bell-hole, 30 degs "Caution" 8" Transite Water main crosses directly under our gas main, also another water main runs parralell with our main
42 | 74-00041-1 |  |  | 4 | Distribution Feeder Main | [5 empty] | NONE | 1974-01-17 | [5 empty] | Benicia | Gucker Ln. 100%; No elect J.G.; W/S Gucker LN 300' S/O Freeway; Bar tested main 3-20-74, returned this date 3-22-74 and found all holes aired out at this particular location 3-22-74
42 | 82-60122-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1982-06-01 | 1982-06-09 | Clamp |  | Steel/Wrought Iron |  | Vallejo | 06-01-82 Leak over main between property line and three ft. behind sidewalk, manked 1 in yellow, installed 2" perm clamp on main 3' N/S/PL of 122 Round St.
42 | 81-20162-1 |  |  |  | Transmission | [6 empty] | 1981-12-21 |  |  |  | Steel/Wrought Iron |  | Vallejo | 531 Taper St. Vallejo Inc., No elect. U.G.; Bar tested area of 12" HP transmission main on 100% same with negative results 10-22-81 D. Dean
42 | 98-40046-1 |  |  | 12 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1998-06-23 | 1998-06-24 | Other |  | Steel/Wrought Iron |  | Vallejo | Pulled completion plug with EHS machine teflon taped & doped plug made back up w/no leak on plug.
42 | 89-20017-1 | [10 empty] | 1989-05-10 | [5 empty] | Val
42 | 85-60200-1 |  |  | 0.5 | Other | A | Fitting |  |  | Other |  | 1985-01-21 | 1985-07-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Vallejo | Bar tested main & cross tie in - recneck in future - 6-27-85 ( O.Dean) service tee cap leaking tightened to correct
42 | 82-20066-1 |  |  | 0.75 | Other |  | Tap Connection |  |  | Construction Defect | LOOSE CAP | 1982-03-12 | 1984-03-01 | Other |  | Steel/Wrought Iron |  | Vallejo | Elect. U.G.; tightened loose 3/4" serv. tee cap on abandoned serv. stub to correct leakage
|  |  |  | 0.75 | Service |  | Other Welds |  |  | Damage by outside Forces |  |  | 1983-07-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Vallejo | Broke tee off of 4" main repaired tee & inserted service to #424
42 | 85-40046-1 |  |  | 2 | Distribution Feeder Main |  | Fitting |  |  | Corrosion |  | 1985-06-20 | 1985-06-20 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Vallejo Inc. | Mare Island Causeway @ gate - Vallejo Inc.,; Blow off valve leak below threads - corroded & a hole was present - cut off 12' foot, D.E. Pipe to correct. Blow off is now 19' from main - T.I.
42 | 81-20115-1 | [10 empty] | 1981-06-19 | [6 empty] | No Elect. U.G.; Bar-tested main & services 11-2-81 best reading obtained was 15% on 100% scale. Unable to determine origin of leakage at this time, D. Burnett, Opened 4'X10' hole found no trace of leak 5-12-83 RLP; Picking up leak on crosswalk N/E corner of Indiana + Sacramento St. 10+%, 4-11-85 Water valve box flamens out J.M.Q. See leak 85-60010, Upgrade this leak to A #2
42 | 95-20060-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1995-05-20 | 1996-11-14 | Other |  | Steel/Wrought Iron |  | Benicia | Greased & soap valve
42 | 75-20008-1 |  |  | 12 | Transmission |  | Fitting |  |  | Other |  | 1975-01-03 | 1975-01-09 | Other |  | Steel/Wrought Iron |  | Benicia | Humble oil MTR. station 3%; Gas in air & meter hardware; tightened several fittings 1-29-75
42 | 95-40041-_ |  |  | 0.75 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 1995-09-11 | 1995-09-11 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Benicia | On a static line; R&R cap to a pin off tee
42 | 79-20289-1 |  |  | 1.5 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1979-10-09 | 1979-10-19 | Other |  | Steel/Wrought Iron |  | Benicia | Found small leak on relief valve repaired same 10-19-79
|  |  |  | 2 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  |  | M-TAG 9658E
42 | 82-20107-1 |  |  | 1.25 | Other | Houseline | Other |  |  | Other |  | 1982-04-20 | 1982-04-23 | Other | DISCONNECTED HOUSE LINE | Steel/Wrought Iron |  | Vallejo | Elect U.G.; leaking was found on houseline that goes to emergency generator. House line was disconnected by crew and serv. dept to correct leakage dt request of Mr. Don Rollins general foreman and Al Stewart field foreman
42 | 73-60008-1 |  |  | 2 | Distribution |  | Body of Pipe |  |  | Corrosion |  | 1973-01-22 | 1973-01-23 | Clamp |  | Steel/Wrought Iron |  | Vallejo | Due to past history of main I installed temo-crary 2" leak clamp and recomend replacement of the main; Should be renewed
42 | 74-60063-1 |  |  | 4 | Other |  | Fitting |  |  | Other |  | 1974-11-07 | 1974-11-12 | Other |  | Steel/Wrought Iron |  | Vallejo | Sears meter
42 |  |  |  | 2 | [7 empty] | 1987-10-10 | 1987-10-12 |  |  | Steel/Wrought Iron |  | VJO | extended main, added 1" service
42 | 72-20009-1 |  |  | 0.5 | Service |  | Other Welds |  |  | Material Failure |  | 1972-04-18 | 1972-04-18 | Weld Over Sleeve or Can |  | Copper |  | Vallejo | Solder connection came apart
42 | 81-40019-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1981-03-16 | 1981-03-17 | Clamp |  | Steel/Wrought Iron |  | Vallejo | 1033 & 1037 York St in alley; Installed 4" leak clamp 292' E/E/PL Monterey; Replace main do to very poor condition
42 | 81-20091-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1981-06-10 | 1985-03-13 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Vallejo | Alley over black patch marked in yellow
42 | 73-00073-1 |  |  |  | Distribution Feeder Main |  |  |  | NONE |  |  | 1973-12-04 |  |  |  | Steel/Wrought Iron |  | Vallejo | S.W. corner of intersection 395 woodrow; S.W corner of intersection near fire plug marked with yellow paint; No indication of any leakage of gas in area
42 | 73-00058-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-02-23 | 1973-03-22 | Clamp |  | Steel/Wrought Iron |  | Vallejo | 292 Woodrow Ave 20%; No elect U.G.; In paving 4' from curb 8' N/W of fence gate yellow paint. Inst. 2-4" temp. leak clamps on 4" main. Because of bad corrosion and pitts a section of main should be replaced as was recommended by crew who worked same leak previously A.S.A.P.
42 | 75-20013-1 |  |  | 8 | Transmission |  | Fitting |  |  | Other |  | 1975-01-07 | 1975-01-08 | Other |  | Steel/Wrought Iron |  | Vallejo | Vallejo terminal 10%+ leak on valve referred to; shut off valves above ground main shut off valves below ground; greased valve
42 | 74-00034-1 |  |  | 4 | Transmission |  |  |  | NONE |  |  | 1974-01-15 |  |  |  | Steel/Wrought Iron |  | Vallejo | Maple St W/S 30% 20' N/O Idora Ave.; W/S maple 20' N/O Idora; No indication or reading of any leakage of gas at this location
28 | 85-40072-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1985-11-26 | 1985-11-26 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Vallejo | Over; Repair made by just 1-12" x 24" welded can on 8" steel main and stuwert
42 | 73-40027-1 |  |  | 24 | Transmission |  | Fitting |  |  | Construction Defect |  | 1973-02-26 | 1973-02-27 | Other |  | Steel/Wrought Iron |  | Vallejo | 409 Rolling wood
42 | 93-40010-1 |  |  | 2 | Other | M | Body of Pipe |  |  | Corrosion |  | 1993-03-31 | 1993-04-02 | Clamp |  | Steel/Wrought Iron |  | Benicia | Installed a 2XG" stainless steel clamp, over a pit.
42 | 73-40510-1 |  |  | 2 | Distribution |  | Body of Pipe |  |  | Damage by outside Forces | N73-4624-D23 | 1973-02-22 | 1973-02-22 | Other |  | Steel/Wrought Iron |  | Calistoga | D+C 23558-H Lang Bro broke our 2" main repaired by installing 2 2" top tap fitting and cutting out broken piece and installing new one (12")
42 | 72-40520-_ |  |  | 2 | Distribution |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-12-06 | 1972-12-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron
42 | 73-40528-1 |  |  | 2 | Distribution |  | Body of Pipe |  |  | Damage by outside Forces | N73-4680-D23 | 1972-06-04 | 1972-06-04 | Other |  | Plastic |  |  | Rapp const hit & leaked our 2" main installed two couplings & 2' of 2" upper plastic
|  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Calistoga | C/O SER
|  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Calistoga | Replace valve trime & cover
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | St. Helena | C-O 3/4" STL SERV at main
42 | 78-20588-1 |  |  | 4 | Distribution Feeder Main |  | Tap Connection |  |  | Other |  | 1978-03-03 | 1978-04-20 | Other |  | Steel/Wrought Iron |  | St. Helena
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Napa county
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Napa county
| 75-40521-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1975-02-28 | 1975-02-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | St. helena | Service broken by county repaired by install 1/2" instrt from main to river tested at 100# for ten min.
42 | 72-40521-_ |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces | Memo III | 1972-12-25 | 1972-12-25 |  |  | Plastic |  | Angwin
42 | 84-20502-_ |  |  | 4 |  |  | Valves |  |  | Other |  | 1984-03-06 | 1984-04-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | St. Helena | Replaced pit & associated piping wo 49050 to be repaired 4/84 on W.C.
42 | 72-00536-1 |  |  | 6 | Distribution Feeder Main |  | Girth Weld |  |  | Construction Defect |  | 1972-11-21 | 1972-12-05 |  |  | Steel/Wrought Iron |  | St. Helena | Punched Holes at this location; found leak where service has been aband. Leak on can which has been welded over service tee. Used center punch to stop leak
42 | 79-00504-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-01-31 | 1979-02-09 | Patch Welded |  | Steel/Wrought Iron |  | St. Helena
42 | 73-40509-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Other | meme 12 | 1973-01-29 | 1973-01-29 |  |  | Steel/Wrought Iron |  | St. Helena | Our gas lone was broken by a retaning wall at ... fell down due to heavy ... plastic & a new riser
42 | 72-40518-1 |  |  | 2 | Distribution |  | Body of Pipe |  |  | Damage by outside Forces | N-72-4170-D23 | 1972-11-27 | 1972-11-27 | Other |  | Plastic |  |  | Install two transiation fitting
| 80-20509-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1980-03-28 | 1980-03-29 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Duplicated leak; Replaced 3/'4" stl service with 1/2" ... Plastic do to corrossion leak.
42 | 73-40533-1 |  |  | 2 | Distribution |  | Body of Pipe |  |  | Corrosion |  | 1978-06-08 | 1973-06-08 | Clamp |  | Steel/Wrought Iron
|  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | St. Helena
42 | 74-40533-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-11-11 | 1974-11-11 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | On 11-11-74 check out leak on riser 4" below cock found pits due to corrosion Put 2 temp clamp on it untill - 12-12-74 which we install a new insert service. The corrosion was due to pit's ground being tied on to our riser OLD ser. Order #6874 A.B.
42 | 74-40525-1 |  |  | 6 | Distribution |  | Tap Connection |  |  | Damage by outside Forces | N74-3962-D23 | 1974-10-10 | 1974-10-10 | Other |  | Steel/Wrought Iron
42 | 78-00500-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Other |  | 1978-03-14 | 1978-04-04 | Other |  | Steel/Wrought Iron |  | St. Helena | Found leak in weld on 6" Repaired some, found leak in weld on 2" Repaired some, comp. 4-4-78
| 81-40505-1 |  |  | 6 | Distribution Feeder Main |  | Fitting |  |  | Construction Defect |  | 1981-02-17 | 1981-02-18 | Other |  | Steel/Wrought Iron |  | St. Helena | Working on W.O. 4432-6 found leak on 1 1/4 tee cap leaking
42 | 88-20539-1 |  |  | 10 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1988-09-29 | 1988-10-13 | Other |  | Steel/Wrought Iron |  | St. helena | Relief part on grove ball valve leaking - repaired ok
42 | 88-20538-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1988-09-29 | 1988-10-14 | Other |  | Steel/Wrought Iron |  | St. Helena | Rebuilt HPR & repaired leaks
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | St. Helena | Exposed service tee to trailer park
42 | 88-00504-1 |  |  | 0.06 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1988-03-16 | 1989-06-14 | Clamp |  | Steel/Wrought Iron |  | Rutherford | Installed 6" temp repair clamp
42 | 74-40506-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces | N74-5823-D23 | 1974-02-21 | 1974-02-21 |  |  | Steel/Wrought Iron
42 | 86-00513-1 |  |  | 6 | Distribution Feeder Main |  | Other Welds |  |  | Construction Defect |  | 1986-03-24 | 1987-08-26 | Patch Welded |  | Steel/Wrought Iron |  | Rutherford | Leak near H.P.R. near transition fitting (rechecked 2-11-87 change) 2/12/87 downgrade to #3, replaces 80-20585, need G&S machic to weld. leak 3-27-87
42 | 74-00513-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-01-07 | 1974-09-20 |  |  | Steel/Wrought Iron |  |  | 8490 HWY 29 E/S 100' S/O meter @ driveway; Duplicate Form; Inst. 4" can over 3/4" service tee that was leaking in weld
42 | 74-00515-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-01-07 | 1974-09-20 |  |  | Steel/Wrought Iron |  |  | 8490 HWY 29 150' N/S of driveway; 773-04 Duplicate Form; inst. 4" can over 3" abandon service tee that was leaking at weld
42 | 75-00516-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1975-01-13 | 1976-06-25 | Patch Welded |  | Steel/Wrought Iron |  | Oakville | Found a 20% reading at driveway 8282 hwy 29 oakville; n/o Mondavi Winery. Between dirt rd. & group of mail boxes on E/S of HWY 29. Rechecked leak 6-17-76. Leak in blacktop area of driveway by box 8282 156' N/O P.M. 23 54
42 | 88-40544-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1988-10-27 | 1989-10-03 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Oakville | Installed 6" can over 1 1/2" valve brazed to side of 6" main installed 5# anode
42 | 87-40500-1 |  |  | 6 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 1987-01-08 |  | Patch Welded |  | Steel/Wrought Iron
42 | 74-00_06-1 |  |  | 10 | Distribution Feeder Main |  | Longitudinal Weld |  |  | Material Failure |  | 1974-01-05 | 1974-01-21 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | Original leak form is kept in pipe line history file.
43 | 96-40040-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1996-12-20 | 1997-02-06 | Other |  | Steel/Wrought Iron |  | Napa | Cleaned and replaced H.P.R.
4 |  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Napa, Inc. | See Attached Sketch Fill out inspection report below & return to gas mapping when complete. Hower 2" Eas Main Dec. 317494
|  |  |  | 0.1 | Distribution Feeder Main | [6 empty] | 1999-06-10 |  |  |  | Steel/Wrought Iron |  | Napa | Main & pipe wrap is in excellent shape
42 | 75-00524-1 |  |  | 6 | Distribution Feeder Main |  | Girth Weld |  |  | Construction Defect | WELD & LEAKING | 1975-01-15 | 1975-05-21 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Napa | HWY 29 & Solano, between E. & W. Salvador 70% gas over line 3' W/O vent between W. Salvador & E Salvador (marked with wooden stake)
42 | 75-00526-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Material Failure |  | 1975-01-15 | 1975-05-17 | Patch Welded |  | Steel/Wrought Iron |  |  | See original leak from in pipe line history folders 8" & 10" feeder main - stanley ln. to Dwyer Ln.
42 | 81-40525-1 |  |  | 0.5 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1981-07-30 | 1981-07-30 | Replace Pipe and/or Service |  | Plastic |  | Napa | Fixed with dead end cap
| 76-40518-1 |  |  | 2 | Other | M | Body of Pipe |  |  | Corrosion |  | 1976-04-20 | 1976-04-26 | Clamp |  | Steel/Wrought Iron |  | Napa | Installed a leak clamp on a small corrosion pit.
42 | 75-40514-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1975-01-28 | 1975-01-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Napa
42 | 75-40512-1 |  |  | 0.5 | Service |  | Physical/Mechanical Joint |  |  | Damage by outside Forces |  | 1975-01-30 | 1975-01-30 | Replace Pipe and/or Service |  | Plastic |  |  | Service was broke by dig in, repaired by crew with ... pipe 1/30/75
42 | 75-00528-1 |  |  | 8 | Distribution Feeder Main |  | Longitudinal Weld |  |  | Construction Defect |  | 1975-01-15 | 1975-09-19 | Other |  | Steel/Wrought Iron |  | Napa | See original form - pipe line history file 8" & 10" feeder; 30% gas at old patch with bored test holes on ETS of Solano about 50' N/O HPR. Station on Solano (N/O Redwood)
|  |  |  | 4 | Distribution Feeder Main | [12 empty] | Napa | Extended H.P.R. Set
| 80-00501-1 |  |  | 2 | Distribution Feeder Main |  | Tap Connection |  |  | Corrosion |  | 1980-03-18 | 1980-04-09 | Other |  | Steel/Wrought Iron |  | Napa | Leakover bellhole patch on N/W corner of west F St & Solano; Fixed by welding around tee
42 | 78-20552-1 |  |  | 2 | Distribution |  | Body of Pipe |  |  | Corrosion |  | 1978-02-14 | 1980-05-29 | Clamp |  | Steel/Wrought Iron |  | Napa | Small leak on main less then 1% dead spot in lawn marked with yellow paint; Found & fixed leak at sewer crossing with 2" leak clamp 5-29-80
|  |  |  | 16 | [11 empty] | Steel |  | Napa Rural | Inst. new HPR & 1/2" svc.
43 | 98-40058-1 | 200 |  | 16 | Transmission |  | Body of Pipe |  |  | Digin |  | 1998-11-05 | 1998-11-05 | Replace Pipe |  | Steel/Wrought Iron |  | Napa | Replaced 22' of 16" stl transmission main
[18 empty] | Napa | Inspect only!
[16 empty] | Steel/Wrought Iron |  | Napa | Inspect only
[16 empty] | Steel/Wrought Iron |  | Napa | Inspect only; loose wrap on main
42 | 73-40515-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-03-25 | 1973-04-02 | Clamp |  | Steel/Wrought Iron |  |  | Inst. new 1/2" PL service 4-2-73; SO #22018, CO #22019
42 | 90-40540-1 |  |  | 0.75 | Service |  | Girth Weld |  |  | Corrosion |  | 1990-11-16 | 1991-01-11 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Napa | Ran new bead on weld
42 | 72-40515-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-09-18 | 1972-09-18 | Replace Pipe and/or Service |  | Plastic |  | Napa | Break in Plastic pipe repaired comp coupling; Installed ...
42 | 81-00500-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1981-02-20 | 1981-03-13 | Patch Welded |  | Steel/Wrought Iron |  | Napa | Changed to #2 E.R. 2-20-81
43 | 98-40016-1 |  |  | 3 | Distribution Feeder Main |  | Other Welds |  |  | Construction Defect |  | 1998-05-12 | 1998-05-12 | Patch Welded |  | Steel/Wrought Iron |  | Napa | Weld leak to arc weld by Ed Gomba
|  |  |  | 0.75 | [11 empty] | Steel |  | Napa
42 | 86-20343-1 |  |  | 8 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1986-05-02 | 1987-07-23 | Other |  | Steel/Wrought Iron |  | Napa | Greased valve 2.10
43 | 98-40039-1 | [10 empty] | 1998-09-25 | 1998-09-25 |  |  |  |  | Napa | None - leak was on customer house line - had customer turn of valve on his own house line + MTR. Stop turning; Customer said leak was at H.P.R. I found no indication of gas @ H.P.R. I did pick up gas about 70' foot away I ask customer if he had another house line & he said yes. I check gas mtr and found 1/2 foot hand spinning very fast. I ask customer if he a valve on his own house line, he said yes. I had customer turn his own house line off. I then check gas mtr + 1/2 foot hand had completely stop. I informed customer it was his responsibility.
43 |  |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1995-08-07 | 1995-09-17 | Other |  | Steel/Wrought Iron |  | Napa | Greased 3/4" valve
| 01-20015-1 | [10 empty] | 2001-04-02 | [5 empty] | Napa | pver service tee; over service tee to 1010, Wyatt
43 | 95-20025-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1995-07-22 | 1995-08-17 | Other |  |  |  | Napa | Greased leaking valve
42 | 81-40536-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1981-12-16 | 1981-12-17 | Patch Welded |  | Steel/Wrought Iron |  | Napa | Installed two leak patches, pits confined to area of culvert crossing
| 75-20634-1 |  |  | 0.75 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1975-03-05 | 1975-06-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Napa | Leak over main approx 5' South of service to 2181 Patton, .1% over service & "T", Found serv. leaking replaced with 1/2" plastic. S.O. #24179
43 | 95-40030-1 |  |  |  | Transmission | [6 empty] | 1995-07-21 | [5 empty] | Napa
| 99-200_8-1 |  |  | 6 | Transmission |  | Physical/Mechanical Joint |  |  | Unknown |  | 1999-12-21 | 2000-12-19 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | Napa
42 | 85-00500-1 |  |  | 6 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1985-03-11 | 1986-04-10 |  |  | Steel/Wrought Iron |  | Napa | Note: This line to be abandoned prior to 9/1/85 should be clear on next check, 9/6/85 - not abandoned yet (G.C. Job) Downgrade to #3, 4/10/86 Rwd take off compuiter, C/O 2" svc from 6" DFM
[5 empty] | Transmission | [6 empty] | 2002-06-12 |  |  |  | Steel/Wrought Iron |  |  | main insepction 88 Thao 108' S/of valve 279 main dept at s/fogging 25' air port road; Top of main is in poor condition - rewrapped 20'
|  |  |  | 6 | [11 empty] | Steel |  |  | 150# main
| 10-00023-1 | L21E | 111.94 | [8 empty] | 2010-04-15 | [5 empty] | Ukiah
| 08-00053-1 | 021-E | 121.8 | [8 empty] | 2008-04-29 | [5 empty] | Redwood Valley | Found no leaks at valve
| 08-00021-1 | L21E | 111.94 | 4 | Transmission |  | Valves |  | NULL | Other | Needs Grease | 2008-03-19 | 2008-03-25 | Other | GREASED VALVE | Steel/Wrought Iron |  | Ukiah
| 08-00025-1 | L021E | 119.41 | 2 | Transmission |  | Valves |  | NULL | Other | Needed Grease | 2008-04-04 | 2008-04-24 | Other | Serviced Valve | Steel/Wrought Iron |  | Calpella | Page 3 Comment 1: Serviced Valve and Replaced Grease Stem
| 08-00028-1 | L021E | 111.94 | 4 | Transmission |  | Valves |  | NULL | Other |  | 2008-04-24 |  |  | NULL | Steel/Wrought Iron |  | Ukiah | Comment 1 Page : No Leak Detected
| 08-00030-1 | 021-E | 137.21 | [8 empty] | 2008-04-28 | [5 empty] | Wllltis
| 08-00032-1 | 021-E | 136.04 | 0.75 | Distribution Main |  | Other | Other | CAP | Unknown |  | 2008-04-28 | 2009-08-29 | Other | tighten | Steel/Wrought Iron |  | Wllltis
| 08-00033-1 | 021-E | 135.91 | 0.75 |  |  | Mechanical Joint |  | NULL | Unknown |  | 2008-04-28 | 2009-04-11 | Other | clean tighten | Steel/Wrought Iron |  | Willits | REPAIR TO SECONDARY UNION.
| 08-00034-1 | 021-E | 135.79 | 0.75 | Transmission |  | Mechanical Joint |  | NULL | Unknown |  | 2008-04-28 | 2009-04-11 | Other | Clean Tighten | Steel/Wrought Iron |  | Willits | REPAIR TO PRIMARY UNION.
| 08-00035-1 | 021-E | 135.04 | 0.25 | Transmission |  | Valves |  | NULL | Unknown |  |  | 2009-04-11 | Other | Reseal Valve | Steel/Wrought Iron
| 08-00036-1 | 021-E | 134.72 | 0.75 |  |  | Mechanical Joint |  | NULL | Unknown |  | 2008-04-28 | 2009-04-11 | Other | CLEAN & TIGHTEN | Steel/Wrought Iron |  | Willits | REPAIR TO SECONDARY BYPASS CAP.
| 08-00037-1 | 021-E | 133.68 | 0.75 |  |  | Mechanical Joint |  | NULL | Unknown |  | 2008-04-28 | 2009-04-11 | Other | Clean Tighten | Steel/Wrought Iron |  | Willits | REPAIRED LEAK ON PRIMARY CAP.
| 08-00038-1 | 021-E | 133.53 | 0.75 | Transmission |  | Mechanical Joint |  | NULL | Unknown |  | 2009-04-28 | 2009-04-11 | Other | Clean tighten | Steel/Wrought Iron |  | Willits | REPAIRED LEAK ON SECONDARY UNION.
| 08-00039-1 | 021-E | 133.31 | 0.75 |  |  | Mechanical Joint |  | NULL | Unknown |  | 2008-04-28 | 2009-04-11 | Other | CLEAN & TIGHTEN | Steel/Wrought Iron |  | Willits | REPAIR TO UNION IN PRIMARY BOX.
| 08-00040-1 | 021-E | 133.04 | 0.75 | Transmission |  |  |  |  | Unknown |  | 2008-04-28 | 2009-04-11 | Other | CLEAN & TIGHTEN | Steel/Wrought Iron |  | Willits
| 08-00041-1 | 021-E | 124.19 | 0.75 | Transmission |  | Fitting |  | NULL | Unknown |  | 2008-04-29 | 2009-04-28 | Tighten Cap or Bolt | NULL | Steel/Wrought Iron |  | Redwood Valley
| 08-00043-1 | 021-E | 123.95 | 0.75 | Transmission |  | Fitting | Fitting | NULL | Unknown |  | 2008-04-29 | 2009-04-28 | Tighten Cap or Bolt | NULL | Steel/Wrought Iron |  | Redwood Valley
| 08-00044-1 | 021-E | 123.95 | 0.75 | Transmission |  | Fitting |  | NULL | Unknown |  | 2008-04-29 | 2009-04-28 | Tighten Cap or Bolt | NULL | Steel/Wrought Iron |  | Redwood Valley
| 08-00045-1 | 021-E | 123.7 | 0.75 | Transmission |  | Regulator |  | NULL | Other | SCREWS LOOSE | 2208-04-29 | 2009-10-16 | Other | Replaced Regulator | Steel/Wrought Iron |  | Redwood Valley
| 08-00046-1 | 021-E | 123.27 | 0.25 | Distribution Main |  | Valves |  | NULL | Other |  | 2008-04-29 | 2008-09-03 | Tighten Cap/Bolt - Fitting | NULL | Steel/Wrought Iron |  | Redwood Valley
| 08-00047-1 | 021-E | 122.86 | 0.75 | Distribution Main |  | Other |  | REG DIAPH | Other | Old |  | 2008-08-21 | Other | REPAIR REG | Steel/Wrought Iron |  | Redwood Valley
| 08-00048-1 | 021-E | 122.86 | 0.75 | Distribution Main |  | Other |  | REG DIAPH. | Other | Old | 2008-04-29 | 2008-08-21 | Other | REPAIR REG | Steel/Wrought Iron |  | Redwood Valley
| 08-00049-1 | 021-E | 122.6 | 0.75 | Distribution Main |  | Other |  | NULL | Unknown |  | 2008-04-29 | 2008-07-17 | Tighten Cap or Bolt | NULL | Steel/Wrought Iron |  | Redwood Valley
| 08-00051-1 | 021-E | 122.14 | 0.75 | Distribution Main |  | Valves |  | NULL | Unknown |  | 2008-04-29 | 2009-10-16 | Other | Tighten | Steel/Wrought Iron |  | Redwood Valley
| 08-00052-1 | 021-E | 122.14 | 8 | Transmission |  | Valves |  | NULL | Unknown |  | 2008-04-29 | 2008-07-17 | Other | Greased Valve | Other | Valve | Redwood Valley | Comment 1 page 3: Greased valve to fix leak.
| 08-00053-1 | 021-E | 121.8 | 0.25 | Transmission |  | Fitting |  | NULL | Other |  | 2008-04-29 | 2008-07-24 | Other | REDOPE & TIGHTEN | Steel/Wrought Iron |  | Redwood Valley
| 08-00054-1 | 021-E | 121.49 | 0.75 | Transmission |  | Fitting |  | NULL | Unknown |  | 2008-04-29 | 2009-08-26 | Other | Tighten | Steel/Wrought Iron |  | Redwood Valley
| 08-00055-1 | 021-E | 120.46 | 0.75 | Service |  | Other |  | Bolt | Unknown |  | 2008-04-29 | 2009-08-26 | Tighten Cap or Bolt | NULL | Steel/Wrought Iron |  | Redwood Valley | Tighten bolt
| 08-00056-1 | 021-E | 120.46 | 0.75 | Transmission |  | Fitting |  | NULL | Unknown |  | 2008-04-29 | 2008-07-17 | Tighten Cap or Bolt | NULL | Steel/Wrought Iron |  | Redwood Valley | Comment 1 page 3: Tighten metric.
| 08-00058-1 | 021-E |  | 0.75 | Distribution Main |  | Valves |  |  | Unknown |  | 2008-04-30 | 2009-10-20 | Other | Tightened | Steel/Wrought Iron |  | Ukiah
| 08-00059-1 | 021-E | NULL | 1 | Distribution Main |  | Other |  | T-cap | Other | Not tight | 2008-04-30 | 2009-12-02 | Other | Tighten Cap | Steel/Wrought Iron |  | Ukiah
| 08-00060-1 | 021-E |  | 0.75 | Transmission |  | Other |  | Cap | Unknown |  | 2008-04-30 | 2009-06-06 | Other | tighten | Steel/Wrought Iron |  | Ukiah
| 08-00061-1 | 021-E | 115.74 | 2 | Transmission |  | Valves |  | NULL | Other |  | 2008-04-30 | 2008-07-11 | Other | Greased | Steel/Wrought Iron |  | Ukiah
| 08-00063-1 | 021-E | 114.62 | 0.75 | Single Service |  | Fitting |  | NULL | Unknown |  | 2008-04-30 | 2009-08-18 | Deactivated Entire Service | NULL | Steel/Wrought Iron |  | Ukiah
| 08-00064-1 | 021-E | 112.6 | 4 | Transmission |  | Valves |  | NULL | Other | Packed | 2008-07-28 | 2008-07-28 | Other | NULL | Steel/Wrought Iron |  | Ukiah
| 08-00065-1 | 021-E | 122.6 | 4 | Transmission |  | Valves |  | NULL | Other | Packed | 2008-05-01 | 2008-07-28 | Other | NULL | Steel/Wrought Iron |  | Ukiah
| 08-00066-1 | 021-E | 112.6 | 4 | Transmission |  | Valves |  | NULL | Unknown |  | 2008-05-01 | 2008-07-21 | Other | Greased | Steel/Wrought Iron |  | Ukiah | Comment 1 page 3: Grease valve to stop leak.
| 08-00068-1 | 021-E | 99.31 | 0.75 | Transmission |  | Fitting |  | NULL | Unknown |  | 2008-05-01 | 2009-04-29 | Tighten Cap or Bolt | NULL | Steel/Wrought Iron |  | Hopland
| 09-00035-1 | L021E | 127.58 | 0.75 | Service |  | Valves |  | NULL | Unknown |  | 2009-05-08 | 2009-11-04 | Other | Greased | Steel/Wrought Iron |  | Redwood Valley | Comment 1 page 2: Greased valve to stop leak; Comment 1 page 3: soaped.
| 09-00031-1 | L021E | 123.95 | 0.75 | Transmission |  | Other |  | Cap | Unknown |  | 2009-05-08 | 2009-06-06 | Other | Tighten | Steel/Wrought Iron |  | Redwood Valley
| 09-00032-1 | L021E | 123.54 | 0.75 | Distribution Main |  | Other |  | H202 RELIEF | Other | REG NOT LOCKING UP | 2009-05-08 | 2009-08-10 | Other | REPLACED B/O REGULATOR | Steel/Wrought Iron |  | Redwood Valley | Comment 1 page 3: Soap test all connections.
| 09-00034-1 | L021E | 127.58 | 0.75 | Distribution Main |  | Fitting |  | NULL | Unknown |  | 2009-05-08 | 2009-10-16 | Other | Tighten nipples | Steel/Wrought Iron |  | Redwood Valley | Comment 1 page 2: tighten nipples
| 09-00036-1 | L021E | 132.47 | 0.75 | Distribution Main |  | Valves |  | NULL | Unknown |  | 2009-05-09 | 2009-08-29 | Other | Tighten | Steel/Wrought Iron |  | Willits
| 09-00085-1 | 21E | 95.91 | 12 | Transmission |  | Body of Pipe |  | NULL | External Corrosion |  | 2009-06-18 | 2009-06-18 | Welded Sav-A-Valve - Weld | NULL | Steel/Wrought Iron |  | Hopland | Comment 1 page 3: pig dig # 22 pitting found on pipe when pit guage was used leak occured.
| 09-90163-1 | NULL | NULL | 0.75 | Transmission |  | Other |  | Cap | Unknown |  | 2009-09-21 | 2009-12-20 | Tighten Cap or Bolt | NULL | Steel/Wrought Iron |  | Ukiah | Comment 1 page 2: Removed + Reinstall pinoff tee cap.
| 10-00132- | L-021E | NULL | 0.76 |  |  | Fitting |  | NULL | Unknown |  | 2010-10-08 |  |  | NULL | Steel/Wrought Iron |  | Ukiah
46 | 11-00002-B | 021-E | 89.72 | [8 empty] | 2011-01-10 | [5 empty] | Hopland
46 | 11-00002-1 | 021E | 89.72 | 12 | Transmission >= 20% SMYS |  | Body of Pipe |  | NULL | External Corrosion |  | 2011-01-10 | 2011-01-12 | Type B Sleeve - Weld |  | Steel |  | Hopland | Comment 1 page 2: Weld sleeve over pit; Comment 1 page 4: Weld on sleeve. Sleeve data (P.O. 25000/53426, WT. 375, 18" long, X52) Save-a-valve on sleeve was used for stack was not tapped due to pitt leaking.
46 | 75-40006-1 |  |  | 0.5 | Service |  | Fitting |  |  | Other |  | 1975-10-21 | 1975-10-22 | Replace Pipe and/or Service |  | Other Plastic |  | Willits
46 | 75-40005-1 |  |  | 1 | Service |  | Fitting |  |  | Construction Defect |  | 1975-10-21 | 1975-10-22 | Other |  | Other Plastic |  | Willits
| 88-20009-1 |  |  | 0.75 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1988-09-13 | 1989-02-06 | Other |  | Steel/Wrought Iron |  | Willits | Comment 1 page 1: M& C grease valve 137.38 & valve 13-9-14-88 & 9/29/88, 1/2" valve relief line leaking at threaded elbow.
| 88-40006-1 | NULL | NULL | 0.75 | Service |  | Valves |  | NULL | Material Failure |  |  | 1988-05-19 | Other | NULL |  |  | Willits | Comment 1 page 2: leak repaired by greasing #1 valve.
46 | 84-40013-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1984-03-28 | 1984-04-11 | Other |  | Steel/Wrought Iron |  | Redwood Valley | Comment 1 page 2: Found blowoff leaking due to faulty HPR, changed HPR + Blowoff.
46 | 75-40007-1 | NULL | NULL | 2 | Distribution Main |  | Fitting |  | NULL | Construction Defect |  | 1975-12-22 | 1975-12-23 | Replace Pipe and/or Service | NULL | Other Plastic
46 | 78-40006-1 |  |  | 2 | Distribution Main > 60 PSIG |  | Tap Connection |  |  | Construction Defect |  | 1978-10-10 | 1978-10-10 | Replace Pipe and/or Service |  | Other Plastic |  | Ukiah
46 | 78-40002-1 |  |  | 2 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | Corrosion |  | 1978-02-17 | 1978-02-17 | Clamp |  | Steel/Wrought Iron |  | Ukiah | Comment 1 page 2: No leakage at this time.
46 | 93-20005-1 | NULL | NULL | 0.2 |  |  | Body of Pipe |  | NULL | Corrosion |  | 1993-09-07 |  | Replace Pipe | NULL | TR 418 |  | Ukiah | Comment 1 page 1: Replaced/Repaired on 42429F 193.
46 | 93-20004-1 | NULL | NULL | 0.2 |  |  | Body of Pipe |  | NULL | Other |  |  |  | Replace Pipe | NULL | TR 418 |  | Ukiah | Comment 1 page 1: Repaired/replaced on wp 42429F 193
| 93-20002-1 | NULL | NULL | 0.2 |  |  | Body of Pipe |  | NULL | Other |  | 1993-09-07 | 1993-09-30 | Replace Pipe | NULL | TR 418 |  | Ukiah | Comment 1 page 1: Bar tested area + found more in area st should be tested + possibley renewed R Costa 9-7-93.
46 | 78-40003-1 | NULL | NULL | 2 | Service |  | Fitting |  | NULL | Material Failure |  | 1978-02-21 | 1978-02-21 | Other | NULL | Other Plastic |  | Ukiah | Comment 1 page 2: Getting read on L.E.L of 40%, but bleed off to 0%.. Will need main work done on service tee if still leaking.
46 | 78-40005-1 |  |  | 1.25 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | Corrosion |  | 1978-09-28 | 1978-09-28 | Other |  | Steel/Wrought Iron |  |  | Comment 1 page 2: Main Replaced.
46 | 81-40008-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1981-08-17 | 1981-08-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Ukiah
46 | 80-20014-1 |  |  | 2 | Service |  | Fitting |  |  | Corrosion |  | 1980-10-08 | 1980-10-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Ukiah | Comment 1 page 2: Grade 1 50 gas over service and next to building. Sewer lateral in immediatel vicinity.
46 | 74-00012-1 |  |  | 4 | Distribution Main > 60 PSIG |  | Valves |  |  | Other |  | 1974-01-29 | 1974-01-29 | Other |  | Steel/Wrought Iron |  |  | Comment 1 page 2: Greased valve and no indication of leakage.
46 | 86-40014-1 |  |  | 0.25 | Transmission |  | Body of Pipe |  |  | Damage by Electrical Defect |  | 1986-10-23 | 1986-10-23 | Replace Pipe and/or Service |  | Copper |  | Ukiah | Comment 1 page 2: 10/23/86 Capped off 1/4" copper tubing, 10/24/86 replaced piping for other damage - found none.
46 | 78-40001-1 |  | NULL | 6 | Distribution Main |  | Body of Pipe |  | NULL | Corrosion |  | 1978-02-08 | 1978-02-08 | Clamp | NULL | Steel/Wrought Iron |  | Ukiah | Comment 1 page 2: No leakage at this time.
46 | 80-40001-1 |  |  |  | Service |  | Physical/Mechanical Joint |  |  | Damage by outside Forces |  | 1980-01-03 | 1980-01-03 | Replace Pipe and/or Service |  | Other Plastic |  | Ukiah
46 | 78-40001-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1978-02-08 | 1978-02-08 | Clamp |  | Steel/Wrought Iron |  | Ukiah
| 00-00005-1 | NULL | NULL | 4 | Transmission |  | Valves |  | NULL | Other | Need grease | 2000-04-20 | 2000-04-26 | Other | VALVE MAINT. | Steel/Wrought Iron |  | Ukiah | Comment 1 page 1: Dig up valve to repair grease piping & regrease valve.
| 04-00008-1 | 21E |  | 4 | Transmission |  | Valves |  |  | Unknown |  | 2004-03-22 | 2005-07-29 | Other | Greased valve | Steel/Wrought Iron |  | Ukiah | Comment 1 page 1: Greased valve.
|  | 21 |  | 8 | [13 empty] | Willits | Comment 1 page 2: Sand around pipe tie-in L-24. Install new valve box and excavate soil away from HPR boxes.
Ukiah
| 99-00035- |  |  | 12 | Transmission |  |  |  |  | Damage by 3rd Party |  | 1999-11-29 | 1999-12-01 | Patch Weld - Weld |  | Steel/Wrought Iron |  | Ukiah | Comment 1 page 1: Damage area to be patch weld.
Ukiah
Ukiah
|  | 21 | [13 empty] | Steel/Wrought Iron |  | Ukiah | Comment 1 page 2: Inspection loc. at tie in point of HPRS to L. 21.
Hopland
|  | 021E |  | 12 | [14 empty] | Comment 1 page 3: Installed launcher.
|  | 300A | 160 | 34 | Service | TRANSMISSION | [9 empty] | Steel |  | HINKLEY | ABANDONED TAP 160.00A TO SOUTH WEST GAS CORP.
|  | 300B | 149.49B | 34 | Transmission | [10 empty] | Steel |  | BARSTOW
| 02-31402-1 | 314 | 28.12 | 10 | Transmission |  |  |  |  | Construction Defect | EXTERNAL CORROSION | 2002-12-04 | 2003-01-08 | Weld Over Sleeve or Can |  |  |  | VICTORVILLE | HOLIDAY IN WRAP CAUSED BY MOVEMENT WHILE ON SKIDS DURING INSTALLATION; LEAK REPAIRED
| 02-2- | 314 | 28.12 | 10 | Transmission |  |  |  |  | Construction Defect | EXTERNAL CORROSION | 2002-12-04 | 2003-01-08 | Welded Sleeve/Can - Weld |  |  |  | VICTORVILLE | HOLIDAY IN WRAP CAUSED BY MOVEMENT WHILE ON SKIDS DURING INSTALLATION
| 09-30025-1 | 300A | 147.91 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-09 | 2010-10-12 | Other | RESEAL FITTINGS |  |  | BARSTOW | REMOVED FITTING AND APPLIED THREAP TAP & SEALENT
| 09-30026-1 | 300A | 154.74 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-09 | 2010-10-12 | Other | RESEAL FITTINGS |  |  | BARSTOW | REMOVED THREADED FITTINGS AND INSTALLED PIPE TAPE & THREAD SEALENT.
| 09-30027-1 | 300A | 149.64 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-09 | 2010-10-10 | Mechanical Repair Fitting - Fitting | REPLACE GAUGE |  |  | BARSTOW | FITTING ON MAINLINE VALVE REPLACE GAUGE
| 09-31301-1 | 313 | 28.26 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-23 | [5 empty] | LUCERNE VALLEY
| 09-31302-1 | 313 | 27.26 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-23 | [5 empty] | LUCERNE VALLEY
| 09-31402-1 | 314 | 38.57 |  | Transmission |  | Valves |  | LEAK IS FROM VALVE PIT. THERE IS A VALVE AND CHECK VALVE IN THE PIT. | Material Failure |  | 2009-09-21 | 2010-10-14 | Other | REPLACED. STEM O-RINGS AND BUSHING | Steel/Wrought Iron |  | APPLY VALLEY | I BACK SEATED GATE VALVE AND REMOVED FAILED BUSHINGS AND O-RINGS. REPLACED WITH NEW BUSHINGS AND O-RINGS.
| 09-31403-1 | 314 | 24.72 |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-10-02 | 2010-10-09 | Other | GREASE VALVE | Steel/Wrought Iron |  | ORE GRANDE | GREASED VALVE WITH 1033 AND SEALED LEAK.
| 09-31405-1 |  | 8.76 |  | Transmission |  | Valves |  |  | Other | LOW ON STEM PACKING | 2009-10-07 | 2010-06-22 | Other | INSTALL STEM PACKING ON PLUG VALVE. (BYPASS VALVE) | Steel/Wrought Iron |  | HELENDALE
| 09-31407-1 | 314 | 30.5 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-10-28 |  |  |  | Steel/Wrought Iron |  | ORO GRANDE
| 09-31408-1 | 314 | 27.46 |  | Transmission |  | Other |  | FITTING | Equipment Malfunction |  | 2009-10-28 | 2010-10-09 | Other | RE-SEAL PIPE FITTING | Steel/Wrought Iron |  | VICTORVILLE
| 10-82057-1 |  | 159.33A |  | Transmission |  | Mechanical Joint |  |  | Equipment Malfunction |  | 2010-10-09 | 2010-10-15 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | HINKLEY | REMOVED WRAP ON D/S FLANGE TIGHTENED FALANDE TO REPAIR LEAK.
| 09-30032-1 | 300B | 180.11 |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-11-16 | [5 empty] | HINKLEY
| 09-30032-2 | 300B | 180.11 |  | Transmission |  | Fitting |  |  | Other | THREAD | 2010-11-16 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 09-30032-3 | 300B | 180.11 |  | Transmission |  | Fitting |  |  | Other | THREADS | 2010-11-16 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 09-30032-4 | 300B | 180.11 |  | Transmission |  | Fitting |  |  | Other | THREAD | 2010-11-16 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 09-30032-5 | 300B | 180.11 |  | Transmission |  | Fitting |  |  | Unknown |  | 2010-11-16 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 09-30032-6 | 300B | 180.11 |  | Transmission |  | Other |  | BOLT/SPACER | Unknown |  | 2010-11-16 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 09-30032-7 | 300B | 180.11 |  |  |  | Other |  | BOLT/SPACER | Unknown |  | 2010-11-16 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 09-30032-8 | 300B | 180.11 |  | Transmission |  | Other |  | INSPECTION PLATE | Unknown |  | 2010-11-16 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 09-30021-1 | [10 empty] | 2009-10-28 | [5 empty] | CALIFORNIA CITY
| 09-31101-1 | 300A | 180.64 | 12 | Transmission |  | Fitting | Valves | VALVES | Equipment Malfunction |  | 2009-11-16 | 2010-10-11 | Mechanical Repair Fitting - Fitting | RESEAL THREADED FITTINGS |  |  | HINKLEY | VALVES & FITTINGS VARIOUS 1/4" 3/8" PILOT LINES; SEE ATTACHED O.D # DRAWING 082131 1/4", 3/8", PILOT LINE'S BALL VALVES
| 09-30029-1 | 300A | 218.69 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-16 | [5 empty] | MOJAVE
| 09-30030-1 | 300A | 218.73 | 4 | Transmission |  | Fitting |  | VALVES | Equipment Malfunction |  | 2009-11-16 | 2010-10-11 | Mechanical Repair Fitting - Fitting | RESEAL THREADED FITTING | Steel/Wrought Iron |  | MOJAVE | FITTINGS & MECHANICAL (THREADED FITTINGS)
| 10-30024-1 | 300A | 170.62 |  | Transmission |  | Valves |  |  | Material Failure |  | 2010-11-09 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-30023-1 | 300A | 170.61 |  | Transmission |  | Clamp | Fitting | FITTING, UNI-BOLT | Material Failure | GASKET | 2010-11-09 |  |  |  | Steel/Wrought Iron |  | BARSTOW
| 10-30022-1 | 300A | 169.04 |  | Transmission |  | Unknown |  |  | Unknown |  | 2010-11-09 |  |  |  | Steel/Wrought Iron |  | BARSTOW
| 10-30025-1 | 300A | 175.711 |  | Transmission |  | Other |  | TOP VALVE | Other | METRIC VALVE | 2010-11-11 |  |  |  | Steel/Wrought Iron |  | BARSTOW
| 10-30026-1 | 300A | 175 |  | Transmission |  | Other |  | UNI CAP SEAL | Other | UNICAP GASKET | 2010-11-11 |  |  |  | Steel/Wrought Iron |  | BARSTOW
| 10-30027-1 | 300A | 174.75 | 34 | Transmission |  | Unknown |  |  | Unknown |  | 2010-11-09 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-30028-1 | 300A | 186.09 |  | Transmission |  | Other |  | UNI CAP SEAL | Other | UNICAP GASKET | 2010-11-11 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-30029-1 | 300A | 192.36 |  | Transmission |  | Other |  | STEM PACKING | Other | TAP VALVE | 2010-11-12 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-30030-1 | 300A | 197.13 |  | Transmission |  | Other |  | UNIBOLT CAP | Other | UNIBOLT GASKET | 2010-11-12 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-30031-1 | 300B | 209.07 | 12 | Transmission |  | Mechanical Joint |  |  | Unknown |  | 2010-11-17 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-30031-2 | 300B | 209.07 |  | Transmission |  | Fitting |  |  | Unknown |  | 2010-11-17 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-30032-1 | 300B | 226.74 | 34 | Transmission |  | Unknown |  |  | Unknown |  | 2010-11-16 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-30033-1 | 300A | 193.3 | 34 | Transmission |  | Unknown |  |  | Unknown |  | 2010-11-12 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-30034-1 | 300A | 218.73 |  | Transmission |  | Valves |  |  | Other | TAP VALVE | 2010-11-15 |  |  |  | Steel/Wrought Iron |  | MOJAVE
| 10-30035-1 | 300A | 180.64 |  | Transmission |  | Unknown |  |  | Unknown |  | 2010-11-11 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-88366-1 | 300A | 108.39 | 12 | Transmission |  | Other |  | UNI-BOLT | Other | GASKET | 2010-11-01 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-88367-1 | 300A | 112.97 |  | Transmission |  | Other |  | UNI-BOLT | Other | GASKET | 2010-11-01 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-88368-1 | 300A | 114.2 | 34 | Transmission |  | Other Welds |  | UNDER GROUND ON PIPELINE 300A | Weld Failure |  | 2010-11-01 |  |  |  | Steel/Wrought Iron |  | Hinkley
| 10-88369-1 | 300A | 116.15 | 34 | Transmission |  | Other Welds |  | UNDER GROUND ON PIPELINE | Weld Failure | [5 empty] | Steel/Wrought Iron |  | Hinkley
| 10-88370-1 | 300A | 116.92 | 12 | Transmission |  | Other |  | UNI BOLT CAP | Other | GASKET | 2010-11-01 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-88371-1 | 300A | 125.39 | 12 | Transmission |  | Other |  | UNI BOLT CAP | Other | LOOSE CAP | 2010-11-03 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-88372-1 | 300A | 129.92 |  | Transmission |  | Fitting |  |  | Other | STEM PACKING | 2010-11-03 | [5 empty] | HINKLEY
| 10-88373-1 | 300A | 130.37 | 34 | Transmission |  | Other |  | INSERTION METER | Other | STEM PACKING | 2010-11-03 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-88373-2 | 300A | 130.37 | 0.75 | Transmission >= 20% SMYS |  | Valves |  |  | Other | STEM PACKING | 2010-11-03 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-88373-3 | 300A | 130.37 | 0.75 | Transmission |  | Valves |  |  | Unknown |  | 2010-11-03 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-88373-4 | 300A | 130.37 | 0.75 | Transmission |  | Valves |  |  | Unknown |  | 2010-11-03 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-88374-1 | 300A | 131.35 |  | Transmission |  | Unknown |  |  | Unknown |  | 2010-11-03 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-88375-1 | 300A | 134 |  | Transmission |  | Fitting |  |  | Unknown |  | 2010-11-03 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-88377-1 | 300A | [15 empty] | DAGGETT
| 10-88386-1 | 300B | 121.45 | 12 | Transmission |  | Other |  | UNIBOLT CAP | Other | LOOSE BOLT | 2011-11-01 |  |  |  | Steel/Wrought Iron
98 | 10-88387-1 | 300A | 125.24 | 12 |  |  | Other |  |  | Other |  | 2010-11-01 | 2011-04-27 | Tighten Cap/Bolt - Fitting |  | Steel |  | HINKLEY | TIGHTENED UNI-BOLT CAP
| 10-88389-1 | 300B | 112.74 | 12 | Transmission |  | Other |  | UNI-CAP | Other | GASKET | 2010-10-31 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-88390-1 | 300B | 135.65 | 12 | Transmission |  | Other |  | BLOW OFF FLANGE | Other | GASKET | 2010-11-03 |  |  |  | Steel/Wrought Iron |  | HINKELY
| 10-88391-1 | 300B | 226.75B | [14 empty] | MOJAVE
| 10-82056-1 | 300B | 226.75 | 2 | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2010-10-08 |  |  |  | Steel/Wrought Iron |  | MOJAVE
| 10-82057-1 |  |  | 3 | Transmission |  | Mechanical Joint |  |  | Equipment Malfunction |  | 2010-10-09 | 2010-10-15 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | HINKLEY | DISCHAGE VALVE NEST. REMOVED WRAP ON D/S FLANGE. TIGHTENED FLANGE TO REPAIR LEAK.
| 10-82059-1 | 300B | 169.97 |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2010-10-11 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 10-82060-1 | 300A | 116.26 | 34 | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2010-10-10 |  |  |  | Steel/Wrought Iron |  | NEWBERRY SPRINGS
| 10-82061-1 | 300B | 116.72B | 34 | Transmission |  | Other |  | UNI-CAP SEAL | Equipment Malfunction |  | 2010-10-10 | 2010-10-15 | Other | RE-SEAL GASKET | Steel/Wrought Iron |  | NEWBERRY SPRING | REMOVED UNI-CAP. CLEANED GASKET SUFRACE AND APPLIED TYFLON TO SEAL. GREASED B.D. VALVES WITH 1033
| 10-82073-1 | 300A | 117 | 34 | Transmission |  | Other |  | UNI-CAP | Material Failure |  | 2010-10-09 | 2010-10-15 | Other | RESEAL GASKET | Steel/Wrought Iron |  | BARSTOW | REMOVED UNI-CAP AND CLEAND AND APPLIED TYFLON TO GASKET AND GREASED B.D. VALVE WITH 1033
| 10-82074-1 | 300A | 125.39 | 24 | Transmission |  | Other |  | UNI-CAP | Material Failure |  | 2010-10-09 | 2010-10-15 | Other | RE-SEAL GASKET | Steel/Wrought Iron |  | BARSTOW | REMOVED UNI-CAP FROM BLOW DOWN AND CLEANED AND APPLIED TYFLON TO GASKET AND GREASED BID. VALVE WITH 1033
| 09-31101-1 | 300A | 180.64 | 12 | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-16 | 2010-10-11 | Other | RESEAL THREADED FITTINGS |  |  | HINKLEY | SEE ATTACHED O.D # DRAWING 082131 1/4", 3/8", PILOT LINE'S BALL VALVES
| 09-31101-1 | 300A | 180.64 | 12 | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-16 | [5 empty] | HINKLEY
| 09-31303-1 | 313 | 34.34 |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-11-23 |  |  |  | Steel/Wrought Iron |  | LUCERNE VALLEY
| 09-31404-1 | 314 | 24.19 | 10 | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-10-03 | 2010-10-10 | Mechanical Repair Fitting - Fitting | RESEAL THREADED FITTINGS | Steel/Wrought Iron |  | ORO GRANDE | SEE ATTACHED DRAWING #087427
| 09-31404-1 |  |  | 10 | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-10-03 |  |  |  | Steel/Wrought Iron |  | ORO GRANDE
| 09-30018-1 | 300B | 152.46 |  | Transmission |  | Fitting | Mechanical Joint | MECHANICAL JOINT | Equipment Malfunction |  | 2009-10-28 |  |  |  | Steel/Wrought Iron |  | BARSTOW
| 09-30022-1 | 300B | 148.19 |  | Transmission |  | Fitting |  | VALVE, SENSING LINES | Equipment Malfunction |  | 2009-10-28 |  |  |  | Steel/Wrought Iron |  | BARSTOW
| 09-30023-1 | 300B | 140.51 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-10-28 | 2010-10-14 | Mechanical Repair Fitting - Fitting | RESEAL FITTINGS | Steel/Wrought Iron |  | DAGGET | SEE DRW. 089663 ATTACHED
| 09-30024-1 | 300 | 151.06 |  | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2009-11-09 | 2010-10-10 | Other | RESEAL FITTINGS | Steel/Wrought Iron |  | HINKLEY | EE REPAIRED LEAKING FITTINGS BY REMOVING AND APPLY PIPE DOPE AND SEALENT TAPE.
| 09-30028-1 | 300B | 168.39 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-16 | [5 empty] | HINKLEY
| 09-30027-1 | 300 | 149.64 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-09 | 2010-10-10 | Other | REPLACE GAUGE |  |  | BARSTOW | SEE ATTACHED DRW. #0800212
| 09-30030-1 | 300A | 218.73 | 4 | Transmission |  | Fitting |  | VALVE | Equipment Malfunction |  | 2009-11-16 | 2010-10-11 | Other | RESEAL THREADED FITTINGS | Steel/Wrought Iron |  | MOJAVE | SEE ATTACHED DRW. #082403
| 09-30031-1 | 300A | 203.02 |  |  |  | Fitting |  |  | Other | STEM PACKING | 2009-11-16 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 09-30031-1 | 300A | 203.02 |  | Transmission |  | Fitting |  |  | Unknown |  | 2009-11-16 | [5 empty] | HINKLEY
| 09-30033- | 300A | 141.03 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-23 |  |  |  | Steel/Wrought Iron |  | LUCERNE
| 09-30030-1 | 300A | 218.73 |  | Transmission |  | Fitting | Valves |  | Equipment Malfunction |  | 2009-11-16 | [5 empty] | MOJAVE
| 09-31302-1 | 313 | 27.26 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-23 | [5 empty] | LUCERNE VALLEY
| 08-20506-1 | [10 empty] | 2008-03-04 | [5 empty] | KRAMER JUNCTION
98 | 71-00001-1 |  |  | 8 | Transmission |  | Girth Weld |  |  | Material Failure |  | 1971-06-12 | 1971-06-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Hinkley
98 | 72-00009-1 |  |  | 8 | Other |  | Girth Weld |  |  | Construction Defect |  | 1972-12-12 | 1972-12-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Hinkley
98 | 72-00008-1 |  |  | 8 | Other |  | Fitting |  |  | Material Failure |  | 1972-11-27 | 1972-12-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | HINKLEY
98 | 72-00007-1 |  |  | 2 | Other |  | Girth Weld |  |  | Construction Defect |  | 1972-10-03 | 1972-10-03 | Patch Welded |  | Steel/Wrought Iron |  | Hinkley
98 | 72-00006-1 |  |  | 8 | Other |  | Girth Weld |  |  | Construction Defect |  | 1972-09-13 | 1972-09-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Hinkley
98 | 72-00005-1 |  |  | 1 | Other |  | Gas Cooler |  | GAS COOLER | Corrosion |  | 1972-08-15 | 1972-10-06 | Other |  | Other
98 | 72-00004-1 |  |  | 8 | Other |  | Fitting |  |  | Material Failure |  | 1972-08-03 | 1972-08-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron
98 | 72-00003-1 |  |  | 8 | Other |  | Girth Weld |  |  | Construction Defect |  | 1972-04-23 | 1972-04-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Hinkley
98 | 72-00002-1 |  |  | 8 | Other |  | Girth Weld |  |  | Construction Defect |  | 1972-04-02 | 1972-04-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Hinkley
98 | 72-00001-1 |  |  | 8 | Other |  | Girth Weld |  |  | Construction Defect |  | 1972-03-23 | 1972-03-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Hinkley
98 | 72-30001-1 | 300B | 161.02 | 0.75 | Other |  | Tap Connection |  |  | Construction Defect |  | 1972-02-23 | 1972-02-28 | Patch Welded |  | Steel/Wrought Iron
98 | 73-00001-1 |  |  | 1 | Other |  | Gas Cooler |  |  | Material Failure |  | 1973-06-18 | 1973-06-18 | Other |  | Other
98 | 73-00003-1 |  |  | 1 | Other |  | Gas Cooler |  | GAS COOLER | Material Failure |  | 1973-09-24 | 1973-09-24 | Other |  | Other
98 | 78-00001-1 |  | 205.5 A | 34 | Transmission |  | Girth Weld |  |  | Other |  | 1978-12-21 | 1979-02-08 | Weld Over Sleeve or Can |  | Steel/Wrought Iron
98 | 78-00002-1 |  | 192.36 A | 34 | Transmission |  | Valves |  |  | Material Failure |  | 1978-12-26 | 1979-01-10 | Other |  | Steel/Wrought Iron |  |  | WRAP ON PIPE WAS IN GOOD CONDITION, COATING ON VALVES AND GAUGE LINES WAS IN POOR CONDITION, VALVE WAS TESTED. MLV WAS LEAKING & WAS REMOVED & REPLACED
11 | 80-0000-1 |  | 159.33 A | 24 | Transmission | COMPRESS STATION | Other |  | CHANGE GASKET | Material Failure |  | 1980-01-14 | 1980-01-15 | Other | REPLACE GASKET | Steel/Wrought Iron |  | BARSTOW
98 | 78-00001-1 |  |  | 1 | Other |  | Gas Cooler |  | GAS COOLER | Material Failure |  | 1978-05-09 | 1978-05-09 | Other |  | Copper |  | HINKLEY
98 | 78-30003-1 | 300A | 131.37 | 34 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 1978-12-18 | 1979-02-20 | Weld Over Sleeve or Can |  | Steel/Wrought Iron
| 10-30002-1 | 300A | 131.35 | 34 | Transmission |  | Valves |  |  | Unknown |  | 2010-04-29 | [5 empty] | NEWBERRY SPRINGS
| 10-31401-1 | 314 | 8.76 | 12 | Transmission |  | Valves |  |  | Unknown |  | 2010-04-23 | [5 empty] | HINKLEY
|  |  |  | 10 | Transmission | [6 empty] | 2008-11-12 |  |  |  | Steel/Wrought Iron |  | Ceres
|  |  |  | 10 | Transmission | [6 empty] | 2008-11-24 |  |  |  | Steel/Wrought Iron |  | Ceres
|  |  |  | 10 | Transmission | [6 empty] | 2008-11-04 |  |  |  | Steel/Wrought Iron |  | Ceres
91 | 89-30005-1 | [10 empty] | 1989-01-06 | [5 empty] | Ceres | Delete see LK# 97 50101
91 | 90-70150-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1990-08-08 | 1990-08-15 | Other |  | Steel/Wrought Iron |  | Ceres | Dug up HLP found relief leaking metal shavings on seat of HPR rebuilt SRT
91 | 90-70149-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1990-08-08 | 1990-08-15 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Ceres | Found 301 on union made repairs
91 | 89-30004-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1989-01-06 | 1989-06-22 | Other |  | Steel/Wrought Iron |  |  | Threads under relief valve leaking; Tightened threads & redoped.
|  |  |  | 0.5 | [8 empty] | 2009-02-06 | Replace Partial Service |  | Aldyl A (Tan or Gray) |  | Ceres | No leak car hit meter (replace Riser); Replace Rise; Replaced riser only placed 4 barrier posts
|  |  |  | 3 | Distribution Feeder Main | [6 empty] | 1972-06-22 |  |  |  | Steel/Wrought Iron |  | Ceres | Note 3" gas main exposed by back hoe installing water mains for city of Ceres, Damaged pipe coating wrapped with polyken wrap.
|  |  |  | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | Ceres | Roots caused some bad spots on wrap, made repairs
91 | 92-50107-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1992-07-08 | 1992-07-08 | Other |  | Steel/Wrought Iron |  | Ceres | Abandoned at spot of cut service to be redone who
91 | 80-10022-1 |  |  | 6 | Transmission |  | Drip |  |  | Corrosion |  | 1980-02-07 | 1981-07-13 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Hughson | On Santa Fe. APRR. 300 S/O Service Rd. Hughson, OK, W.O.41472; Removed drip - replaced using 5' 6" STL. pipe
91 | 74-30014-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-03-04 | 1974-03-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Keyes | Replaced 3/4" steel service with 1/2 plastic insert installed 1# anode on riser & 9# anode on main at service tee.
91 | 74-30114-1 |  |  | 12 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1974-04-24 | 1978-05-19 |  |  | Steel/Wrought Iron |  | Ceres | Kaiser Rd & Faith home Rd. Keyes valve pit Hamilton 3236-7; E. Regulate pit next to rail road; Greased 10" section valve and redoped 1/4" plug
|  |  |  | 0.75 | Service | [10 empty] | Steel/Wrought Iron |  | Keyes
|  |  |  | 10 | Transmission | [6 empty] | 2007-04-26 |  | Other | GRINDING OUT GAUGES | Steel/Wrought Iron |  | Ceres | Ground out 2 small gouges & wraped;
|  |  |  | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | Keyes | Dan wood 652-7987, Standbym Wed Sept 17, 2003 10:00 am
|  |  |  | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | Keyes | Dan Wood 652-7929, Standby, Thurs 9-11-03 at noon (12 pm)
|  |  |  | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | Keyes
| 02-30082- | [10 empty] | 2002-08-15 | [5 empty] | Hughson | MO HP 81; Delete - move to multipurpose tag
91 | 83-30110- |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1983-08-24 | 1984-01-06 | Other |  | Steel/Wrought Iron |  | Ceres | Replaced HPC Reg with HPR Reg rebuilt set
91 | 74-10013-1 |  |  | 6 | Distribution Main |  | Valves |  |  | Other |  | 1974-01-10 | 1974-04-02 | Other | Greased Valve | Steel/Wrought Iron |  |  | Leak in PG&E valve 76%; Greased 2" valve on drip
| 02-30081- | [10 empty] | 2002-08-15 | [5 empty] | Hughson | Valve F+C in intersection; no leak found - delete
| 99-70051- |  |  | 2 | Distribution Main |  | Regulator |  |  | Unknown |  |  | 1999-12-08 | Other | REPLACED | Steel/Wrought Iron |  | Hughson | leak eliminated by abandonment of MOHP47 D...; Removed reg on PM 30090786
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Hughson
91 | 97-70044-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1997-09-08 | 1998-06-04 | Other |  | Steel/Wrought Iron |  | Hughson | Due to box found reg leaking old style replaced with 621 reg & relief soap test O.K.
91 | 97-70045-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1997-09-08 | 1998-06-26 | Other |  | Steel/Wrought Iron |  |  | Made repairs to valve
91 | 97-70046-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1997-09-08 | 1997-10-19 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Hughson | Dope & tighten fittings
91 | 95-70005-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1995-08-04 | 1995-12-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Hughson | Repair fitting on valve and soap test OK
91 | 90-30244-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1990-08-08 | 1990-08-08 | Other |  | Steel/Wrought Iron |  | Hughson | Rebuilt HPR set
91 | 89-30021-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1989-02-21 | 1989-09-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Hughson | Repaired 301 on HPR set
91 | 88-30161-1 |  |  | 2 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1988-11-18 | 1989-06-28 | Other |  | Steel/Wrought Iron |  | Ceres | Greased Valve
91 | 88-30095-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1988-10-31 | 1988-11-01 | Other |  | Steel/Wrought Iron |  | Hughson | Greased 3/4" Nord valve on H.P.R. Set
91 | 90-30299-1 |  |  | 4 | Distribution Feeder Main |  | Other |  |  | Other |  | 1990-02-20 | 1990-02-21 | Other |  | Steel/Wrought Iron |  | Hughson | Repaired 301 on 1/4" gauge line
91 | 88-30161-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1986-08-29 | 1986-09-08 | Other |  | Steel/Wrought Iron |  | Hughson | 2507 Tully Rd, Hughson; Rebuilt HPR set to repair 30l's
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Hughson
| 00-30081- |  |  | 4 | Distribution Main |  | Valves |  |  | Other |  | 2000-08-16 | 2001-12-27 | Other | Greased valve | Steel/Wrought Iron |  | Hughson
| 00-30081- |  |  | 4 | Distribution Main |  | Valves |  |  |  |  | 2000-08-16 | 2001-12-27 | Other | Greased Valve | Steel/Wrought Iron |  | Hughson
| 00-30081- | [10 empty] | 2000-08-16 | [5 empty] | Hughson
91 | 89-30025-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1989-02-23 | 1989-09-05 | Other |  | Steel/Wrought Iron |  | Hughson | Made repairs to HPR
91 | 97-70047-1 |  |  | 4 | Distribution Main |  | Fitting |  |  | Other |  | 1997-09-08 | 1998-12-07 | Replace Pipe |  | Steel/Wrought Iron |  | Hughson | Replaced 3/8" steel tubing with 316 SS Tubing
91 | 97-70043-1 |  |  | 0.25 | Service |  | Physical/Mechanical Joint |  |  | Other |  | 1997-09-08 | 1997-09-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Hughson | Tighten fittings
|  |  |  | 0.06 | Transmission | [10 empty] | Steel/Wrought Iron |  | Hughson | Wrap a little thin on main
| 02-30080- | [10 empty] | 2002-08-15 | [5 empty] | Hughson | Delete - moved to multi-purpose tag
| 00-30080- |  |  | 1.25 | Distribution Main |  | Fitting |  |  | Other |  | 2000-08-16 | 2001-12-27 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | Hughson
| 00-30080- | [10 empty] | 2000-08-16 | [5 empty] | Hughson
91 | 90-70152-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1990-08-08 | 1990-08-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Hughson | 301 on fitting @ valve & HPR bypass made repairs soap test O.K.
91 | 90-30272-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1990-02-20 | 1990-02-22 | Other |  | Steel/Wrought Iron |  | Hughson | Made repairs to HPR set
91 | 90-30273-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1990-02-20 | 1990-02-22 | Other |  | Steel/Wrought Iron |  | Hughson | Made repairs to HPR set
91 | 90-30298-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1990-02-20 | 1990-02-22 | Other |  | Steel/Wrought Iron |  | Hughson | Made repair to HPR set
91 | 73-50235-1 |  |  | 6 | Transmission |  | Fitting |  |  | Other |  | 1973-09-21 | 1974-03-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Hughson | Leak in union in HP Box permanent repair
91 | 89-30030-1 | [10 empty] | 1989-02-27 | [5 empty] | Hughson | Deleted; Believe leak has been repaired
| 02-30079- | [10 empty] | 2002-08-15 | [5 empty] | Hughson | Deteled
91 | 02-30079- |  |  | 6 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1989-02-27 | 1990-01-29 | Other |  | Steel/Wrought Iron |  | Hughson | Abnd. dresser fittings & installed 17' of 6" STL main
| 00-50066- |  |  | 6 | Distribution Main |  | Physical/Mechanical Joint |  |  | Damage by 3rd Party | DIGIN | 2000-04-13 | 2000-04-14 | Other | Abandon | Steel/Wrought Iron |  | Hughson | OK for night of 4/13/00 work 4/14/00, cracked threads between 2" pipe and 2" valve; Abandoned 2" drip valve
| 99-50106- |  |  | 0.75 | Service |  | Regulator |  |  | Other | Fire | 1999-05-30 | 1995-05-30 | Other | Abandon | Steel/Wrought Iron |  | Hughson | Removed Reg & Parts at HPR set
91 | 90-50213-1 |  |  | 0.5 | Service |  | Physical/Mechanical Joint |  |  | Other |  | 1990-11-24 | 1990-11-21 | Replace Pipe |  | TR 418 |  | Hughson | Repaired 1/2" PL. Ser. Installed perp. riser
91 | 89-30031-1 | [10 empty] | 1989-03-01 | [5 empty] | Hughson | Deleted
| 09-30540-1 |  |  | 6 | Transmission |  | Mechanical Joint |  |  | Other | Dresser coupling | 2009-08-10 | 2009-10-23 | Replace TP Main |  | Steel/Wrought Iron |  | Turlock | 150' s/o add; No read - post; Remove drip & dresser couplings; for test data see attached
91 | 90-30450-1 |  |  | 0.75 | Service |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1990-11-27 | 1990-11-27 | Other |  | Steel/Wrought Iron |  | Turlock | Tighten union.
91 | 87-30085- |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1987-07-06 | 1987-09-04 | Other |  | Steel/Wrought Iron |  | Hughson
91 | 87-30086- |  |  | 6 | Distribution Feeder Main |  | Drip |  |  | Other |  | 1987-07-06 | 1987-08-27 | Other |  | Steel/Wrought Iron |  | Hughson | Across from 4825 geer rd., Hughson
91 | 87-30086- |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1987-07-06 | 1987-08-27 | Other |  | Steel/Wrought Iron |  | Hughson
91 | 87-30086- |  |  | 6 | Distribution Feeder Main |  | Drip |  |  | Other |  | 1987-07-06 | 1987-08-27 | Other |  | Steel/Wrought Iron |  |  | Across from 4825 Geer rd., Hughson
|  |  |  | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | Hughson | Soap tested
| 00-30082- |  |  | 4 | Distribution Main |  | Other |  | Tubing | Other |  | 2000-08-16 | 2002-01-08 | Other |  | Other |  | Turlock
| 02-30083- | [10 empty] | 2002-08-15 | [5 empty] | Turlock | delete - moved to multipurpose tag
91 | 10-50245-B |  |  | 0.5 | Single Service |  | Body of Pipe |  |  | External Corrosion |  | 2010-12-21 | 2010-12-21 | Replace Riser |  | Copper |  | Hughson | On service by river; @ riser next to hono; replaced riser; copper service needs to be replaced, replaced riser, could not find ptpr
91 | 94-30020-1 | [10 empty] | 1994-02-03 | [5 empty] | Turlock | Deleted
| 98-30266- |  |  | 0.75 | Service |  | Fitting |  |  | Construction Defect |  | 1998-11-25 | 2004-10-26 | Other | Tighten fittings | Steel/Wrought Iron |  | Turlock | Possible HPR leak, HPR box leak, Repair lks on HPR; tighten fittings to repair leakage
91 | 98-30095-1 | [10 empty] | 1998-05-19 | [5 empty] | Turlock | Deleted, copper svc upgraded to 2 - 98-30266
| 98-30266- |  |  | 0.75 | Service |  | Fitting |  |  | Construction Defect |  | 1998-11-25 | 2004-10-26 | Other | TIGHTEN FITTINGS | Steel/Wrought Iron |  | Turlock | Old 98-30095
91 | 98-30095-1 | [10 empty] | 1998-05-19 | [5 empty] | Turlock | Deleted, copper svc upgraded to 2 - 98-30266
[5 empty] | Gathering | [10 empty] | TR 418 |  | Waterford
91 | 82-50144-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1982-12-13 | 1982-12-13 | Replace Pipe and/or Service |  | Plastic
91 | 82-50143-1 |  |  |  | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1982-12-13 | 1982-12-13 | Replace Pipe and/or Service |  | Plastic
|  |  |  | 3 | Gathering | [10 empty] | Steel/Wrought Iron |  | Turlock
|  |  |  | 3 | Gathering | [10 empty] | Steel/Wrought Iron |  | Turlock
|  |  |  | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | Turlock | Per Dave Willson; OKd clearance of 1" for 6" plastic sewerline over top of 10" D.F.M
|  |  |  | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | Turlock | Clyde wheeler standby 6-22-04 0830; Installed 4" & 6" water lines over 10" D.F.M. gas
91 | 83-30154- |  |  | 0.75 | Other |  | Fitting |  |  | Material Failure |  | 1983-09-02 | 1984-07-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Turlock | Cap on abandoned service tee leakings - re-doped & wrapped
| 99-30022- |  |  | 6 | Distribution Main |  | Valves |  |  | Other |  | 1999-01-28 | 1999-01-29 | Other |  |  |  | Turlock | In fenced area (station); Greased soap test OK
| 99-30023- |  |  | 6 | Distribution Main |  | Valves |  |  | Other |  | 1999-01-29 | 1999-01-29 | Other |  |  |  | Turlock | Greased soap tested OK
91 | 90-70155-1 | [10 empty] | 1990-08-10 | [5 empty] | Turlock | Delete
91 | 90-70154-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1990-08-10 | 1990-08-17 | Other |  | Steel/Wrought Iron |  | Turlock | Repaired 501 on 4" valve
91 | 89-30154-1 |  |  | 4 | Distribution Main |  | Valves |  |  | Other |  | 1989-04-26 | 1989-05-16 | Other |  | Steel/Wrought Iron |  | Turlock | Greased valve
91 | 73-30008-1 |  |  | 2 | Transmission |  | Valves |  |  | Other |  | 1973-01-10 | 1973-09-26 | Other | Greased Valve | Steel/Wrought Iron |  | Turlock
|  |  |  | 6 | Transmission | [12 empty] | Turlock | Carl - 916 275-1424, Standby, Thursday Jan 8, 2004 @ 8:00 am; T.P gas not exposed dig was 2' from it
|  |  |  | 6 | Gathering | [10 empty] | Steel/Wrought Iron |  | Turlock | Eric - Layman Electric 652-6828, Standby
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Turlock | Wrap no removed. Bore was 64" below main
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Turlock
91 |  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Turlock
91 |  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Turlock
91 | 90-70156-1 | [10 empty] | 1990-08-10 | [5 empty] | Turlock | Delete
91 | 90-30245-1 | [10 empty] | 1990-08-09 | [5 empty] | Turlock | Delete
91 | 73-50032-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-02-20 | 1973-02-20 | Patch Welded |  | Steel/Wrought Iron |  | Turlock
91 | 89-30249- |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1989-12-11 | 1990-03-08 | Patch Welded |  | Steel/Wrought Iron |  | Turlock | Welded on a 20" piece of half sole on 10" STL. pipe
91 | 88-30132-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Other |  | 1986-12-23 | 1988-10-06 | Other |  | Steel/Wrought Iron |  | Turlock | old 86-30183; Rebuilt HPR set to replace 301
|  |  |  | 10 | Transmission | [12 empty] | Turlock | City of Turlock Randy LaCrosse 614-4975, standby, Tuesday, May 4 at 8:00 am; 10" DFM not exposed
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | Turlock | City of Turlock Dana Chilcott - 481-8781, Standby, Wednesday 4/21/04 at 8:00 am
91 |  |  |  | 10 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Turlock
|  |  |  | 10 | Transmission | [10 empty] | Steel/Wrought Iron
| 80-50357-1 |  |  | 2 | Other |  | Drip |  |  | Damage by outside Forces |  | 1980-10-10 | 1980-10-10 | Other |  | Steel/Wrought Iron |  | Turlock | 240 S. First St.; C/O & Plug 1" stand pipe on 2" steel drip on 6" LP gas main
91 | 76-10029-1 | 215 |  | 12 | Transmission |  | Fitting |  |  | Other |  | 1976-11-12 | 1978-03-20 | Other |  | Steel/Wrought Iron |  | Turlock | S/E C/O south ave. & west ave. Turlock, 12" Feder main (line 215)
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | Turlock | City of Turlock potholed 12" TP Line with vac truck to place a new H20 service to House
|  |  |  | 12 | Transmission | [12 empty] | Turlock | Randy LaCroose 614-4975, Standby, Tuesday Jan 27, 2004 @ 8:00 am
91 | 93-50103-1 |  |  | 0.5 | Transmission |  | Riser |  |  | Other |  | 1993-08-17 | 1993-08-17 | Other |  | Aldyl A (Tan or Gray) |  | Turlock | Tighten Powell key and redoped
91 | 90-70153-1 | [10 empty] | 1990-08-09 | [5 empty] | Turlock | Deleted
[5 empty] | Transmission | [10 empty] | Steel/Wrought Iron |  | Turlock | Standy By City of Turlock; Standyby for City of Turlock
91 | 89-30118-1 |  |  | 0.5 | Transmission |  | Regulator |  |  | Other |  | 1989-04-27 | 1992-08-12 | Replace Pipe |  | Steel/Wrought Iron |  | Turlock | Aban. HP serv & HPR transferred serv, to new 3rd plastic distribution main
91 | 90-70157-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1990-08-10 | 1990-08-14 | Other |  | Steel |  | Turlock | Found crack in HPR CHG, Out with new one
91 |  |  |  |  | Distribution Main > 60 PSIG | [10 empty] | Steel/Wrought Iron |  | Turlock; Turlock
91 | 90-30046-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1990-01-15 | 1990-01-22 | Tighten Cap or Bolt |  | Steel |  |  | Made repairs to H.P.R. set
91 |  |  |  | 4 | Other | DF | [5 empty] | 1972-05-04 |  |  |  | Steel/Wrought Iron |  |  | Note...
91 |  |  |  | 2 | Other | DF | [5 empty] | 1972-07-07 |  |  |  | TR 418 |  | Turlock
91 | 86-30103- |  |  | 0.75 | [5 empty] | Other |  | 1986-09-03 | 1986-09-12 | Other |  | Steel/Wrought Iron |  | Hilmar
91 | 73-10091-1 |  |  | 6 | Transmission |  | Fitting |  |  | Corrosion |  | 1973-09-26 | 1974-03-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Turlock | August Rd Det - 19456 & 19585 -, 3369 - El, Turlock, Hilmar, Line #118, C.P.S. # 33-69-1; 6", Line 118; C. Copy 6/5/79 00; Clear J.K., T-118; Found 6" ... not dope...
91 | 81-30147-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1981-11-24 |  | Patch Welded |  | Steel/Wrought Iron |  | Delhi | 19019 August Rd.; DELHI; Should be 3368 E8 ...; Line # 118; Tighten 3/4" union
91 | 90-70044-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1990-08-17 | 1991-01-07 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Hilmar | Dugud buried HPR box found cap on inlet side; Leaking made repairs turn HPRoff house abandon MTR gone
91 | 91--1 | [16 empty] | Turlock
91 | 86-30100- |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1986-09-03 | 1986-09-17 | Other |  | Steel/Wrought Iron |  | Hilmar | 18196 August Rd. Hilmar; Rebuilt HPR set to repair 301
91 | 86-30099- |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1986-09-03 | 1986-09-23 | Other |  | Steel/Wrought Iron |  | Hilmar | Dairy Brown trailer, 18937 August Rd., N/S of August RD, Hilmar; Greased valve to repair 301 on HPR Set
| 99-30112- |  |  | 0.75 | Service | Transmission | Regulator | Other | RELIEF VALVE | Material Failure |  | 1999-05-26 | 1999-06-01 | Other |  | Steel/Wrought Iron |  | Delhi | Neighbor has smelled gas odor; Found relief blowing; Dug up HPR set found relief blowing bypass rebuilty reg set; Needs HPR Box Located; Lid Broken, Full of Dirt Possible leak in H.P.R. need Lid & Top Box, coned off Box, Repairs to HPR set made 6-1-99
91 | 90-300-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1990-01-23 | 1990-01-27 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Delhi | Made repairs to HPR set
91 | 89--1 | [16 empty] | Delhi
91 | 78-30013-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1978-02-16 | 1978-10-24 | Other |  | Steel/Wrought Iron |  | Delhi | Delhi, 16823 August Rd.; Delhi; (H.P.R.)
91 | 72-10200-1 |  |  |  | Transmission | [6 empty] | 1972-12-05 |  |  |  | Steel/Wrought Iron |  | Merced
91 | 72-10199-1 |  |  |  | Transmission | [6 empty] | 1972-12-05 | [5 empty] | Merced | Leaking in H.P.R. Box at 15938 August, No reading D.H...
91 | 72-10205-1 |  |  |  | Transmission | [6 empty] | 1972-12-06 |  |  |  | Steel/Wrought Iron |  | Merced | Leak at gas valve at N/E corner of August & Corner Ave., No reading 2-13-73 D.H...
91 | 97-70130-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1997-08-27 | 1998-03-26 | Tighten Cap or Bolt |  | Steel |  | Delhi | Tighten 3/4" union on HPR set soak test O.K.
91 | 97-50204-1 |  |  | 0.75 | Service |  | Physical/Mechanical Joint |  |  | Digin |  | 1997-11-25 | 1997-11-25 | Replace Pipe |  | Steel/Wrought Iron |  | Delhi | Dig in - Replaced HPR set and 19' with 1/2' pl. Service to be cut off in the near future.
91 | 90-30006-1 | [10 empty] | 1990-01-03 | [5 empty] | Delhi | Deleted; same, same, same, same
| 09-30170-1 |  |  | 0.75 | Single Service |  | Fitting |  |  | Unknown |  | 2009-04-04 | 2009-05-11 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Delhi | Leak repaired
09-30171-1 | 09-30171-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 2009-04-04 | 2009-05-11 | Other | GREASED | Steel/Wrought Iron |  | Delhi | Greased valve; Greased valve
91 | 86-314- |  |  | 0.25 | Distribution |  | Valves |  |  | Other |  | 1986-09-04 | 1989-09-27 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  |  | Repaired leak in conjunction with W.O. 41047-C (Replaced 4" bridle valve @ sta. inlet.
91 | 89-30191-1 |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  | 1989-05-14 | 1989-05-12 | Other |  | Steel/Wrought Iron |  | Delhi | Greased valves
91 | 97-70129-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1997-09-29 | 1998-03-26 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Dilhi | Doped and retightened cap spot paint soap test O.K.; HPR Box
[18 empty] | Delhi | Altered...set
91 |  |  |  | 6 | Distribution Main > 60 PSIG | [10 empty] | Steel/Wrought Iron |  | Delhi
| 09-30181-1 |  |  | 0.75 | Single Service |  | Fitting |  |  | Unknown |  | 2009-04-07 | 2009-05-11 | Other | RIDF | Steel/Wrought Iron |  | Delhi | Repaired leak; re doped Threadg and tighten
91 | 97-70133-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1997-09-30 | 1998-03-26 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Delhi | Made repairs to relief dug up pistalled new box old one broken; HPR Box
91 | 97-70132-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1997-09-30 | 1997-10-19 | Tighten Cap or Bolt |  |  |  | Delhi; Delhi | Tighten fitting
91 | 97-70131-1 |  |  | 0.75 | Service |  | Physical/Mechanical Joint |  |  | Other |  | 1997-09-30 | 1997-10-19 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Delhi | Dope + tighten fittings
91 | 89-30164-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1989-05-04 | 1989-06-02 | Other |  | Steel/Wrought Iron |  | Delhi | A... HPR Serv
91 | 89-30165-1 |  |  | 0.75 | Service |  | Threads |  |  | Other |  | 1989-05-04 | 1989-05-08 | Other |  | Steel/Wrought Iron | other; | Delhi | Made repairs HPR set
91 | 85-30124-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 08/00/1985 | 1985-09-10 | Other |  | Steel/Wrought Iron |  | Delhi | Repair 301 on HPR set 3/4" union, rebuilt HPR replaced relief valve;
91 | 90-70045-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  |  | 1992-10-31 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Delhi | 3/4" st tee leaking made repairs rerope + tighten; same, Gas venting
91 |  |  |  | 4 | Transmission |  | Other |  |  | Other |  |  | 1994-11-18 | Other |  | Steel/Wrought Iron |  | Delhi | Re-wraped trans. main
91 | 97-70134-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Other |  | 1997-09-30 | 1998-03-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Delhi | Found leak on 3/4" nipple to reg. redoped and tighten soap test OK
91 | 90-30031-1 |  |  | 8 | Transmission |  | Valves |  |  | Other |  | 1990-01-23 | 1990-01-27 | Other |  | Steel/Wrought Iron |  | Delhi | Greased + operated valve
| 09-30664-1 |  |  |  | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2009-09-23 | 2010-08-16 | Tighten Cap or Bolt |  | Steel | Sensing; Sensing | Newman | Static line; tighten fittings; tighten bolts on static line. soap tested; eliminated 8/20/10 Mtr hardware leak should not have been a graded leak
| 00-30089- |  |  | 0.75 | Distribution Main |  | Valves |  |  | Other |  | 2000-08-30 | 2002-08-29 | Other | GREASED VALVE | Steel/Wrought Iron |  | Newman | Greased valve
Newman
91 | 11-50083-B |  |  | 0.75 | Single Service | RLDF | Threads |  |  | No/Deteriorated Pipe Dope |  | 2011-03-18 | 2011-03-21 | Replace Entire Service |  | Steel |  | Newman | Gas oderant pot on cap D stream of HPR; Replaced entire service inserted 3/4 5th with 1/2" pL.; Replaced entire service from HPR to house, 135' 1/2" pL Priscoplex 072609; Replaced entire service inserted 3/4"5th with 1/2" PL 135' riser
| 10-81153-1 |  | 3.91 | [8 empty] | 2010-10-07 | [5 empty] | Newman | Original sent to Concord; farm tap; no leak found; No leak found. Soap tested HPR no leak found
| 09-30176-1 | [10 empty] | 2009-04-07 | 2009-05-12 |  |  |  |  | Newman | Lit hpr, no leak found; no leak found after visual soap test
91 | 97-50093-1 |  |  | 0.75 | Service |  | Other |  |  | Digin |  | 1997-06-30 | 1997-07-01 | Replace Pipe |  | Steel/Wrought Iron |  | Newman | Replaced HPR Box 7-1-97, + Fittings -temp. shut-off, 6-30-97Gy
| 01-30060- |  |  | 0.75 | Transmission |  | Fitting | Regulator | REGULATOR VALVES. | Other |  | 2001-08-24 | 2002-11-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Newman; Newman | Repared Leak; Rebuilt set
91 | 90-70171-1 | [17 empty] | Original misplaced; Delete
91 | 91-70038-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1991-08-20 | 1991-10-04 | Replace Pipe |  | Steel/Wrought Iron |  | Newman | Found body on HPR leaking Replaced HPR + Relief soap test O.K.
91 | 91-30032-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1991-08-20 | 1991-10-03 | Other |  | Steel/Wrought Iron |  | Newman | Found leak on valve Greased operated soaptest O.K.;
91 | 91-30031-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1991-08-20 | 1991-10-03 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Newman | Found leak on relief redope + tighten soaptest O.K.
91 | 91-30030-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1991-08-20 | 1991-09-05 | Other |  | Steel/Wrought Iron |  | Newman | Greased valve + operated
91 | 90-30167-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1990-02-03 | 1990-02-15 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Newman | Made repairs to HPR
91 | 85-30184- |  |  | 0.75 | Service |  | Valves |  |  | Material Failure |  | 1985-11-07 | 1986-06-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Newman | Leak below cock, care on cock and Insled. union, Replaced all with Insled. cock
91 | 90-30063-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1990-01-31 | 1990-02-02 | Other |  | Steel/Wrought Iron |  | Newman | Rebuilt HPR Set to Repair 301
91 | 89-30179-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1989-07-26 | 1989-08-16 | Other |  | Steel/Wrought Iron |  | Newman | Made repairs to HPR
91 | 81-90029-1 |  |  | 0.75 | Service |  | Fitting |  |  | Corrosion |  | 1981-12-11 | 1982-05-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Newman | Odorizer leaking, Removed, Replaced 4' 3/45th, Hard Digging (See Remarks Below), H.P.R. Leaking repaired. Fixed 5-21-82 D.Houx; Dug Out H.P.R. - Rebuilt Reg. & Relief. - Found no leaks - Suggest you send leak surveyor to Pin Point look - or crew -; 4-7-82 Bob, This leak is outside the HPR Box where Ron Hamiltons Group couldn't make the repair, Dave;
91 | 86-30109- | [10 empty] | 1986-09-09 | [5 empty] | Newman | Delete main removed
91 | 80-30044-1 |  |  | 4 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | Corrosion |  | 1980-01-22 | 1980-11-03 | Patch Welded |  | Steel/Wrought Iron |  | Newman | 4" half sole 6" long welded on main 1 ft so/leak coocred scrape in main
91 | 78-30072-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1978-06-26 | 1978-11-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Newman | Replaced 3/4" valve in HPR Box + Fixed Leaks on Nipple Overhaul HPR
91 | 73-30182-1 |  |  | 8 | Distribution Main > 60 PSIG |  | Valves |  |  | Corrosion |  | 1973-02-23 | 1977-06-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Newman | ... Repaired ok W.O. 4149B 6-3-77 B. Owens
|  |  |  | 6 | [13 empty] | Newman
91 |  |  |  | 8 | Other | DF | [5 empty] | 1972-08-15 |  |  |  | Steel/Wrought Iron |  | Newman | 8" main; Not 8" gas main exposed by back hoe installing irrigation line. Light damage to pipe coating. wrapped with PoL yKE. Wrap & protec to wrap
91 | 89-30206-1 |  |  | 0.75 | Service |  | Physical/Mechanical Joint |  |  | Other |  | 1989-07-26 | 1989-11-14 | Other |  | Steel/Wrought Iron |  | Newman | Removed odorizer raised box
91 | 89-30205-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1989-11-13 | 1989-11-13 | Replace Pipe |  | Steel/Wrought Iron |  | Newman | Removed at HPR Box, Removed odorizer
91 | 86-30110- |  |  | 8 | Transmission |  | Other Welds |  |  | Material Failure |  | 1986-09-09 | 1987-07-08 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Newman
91 | 89-30206-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1989-07-26 | 1989-08-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Newman | Made repairs to HPR
91 | 82-30335- | [10 empty] | 1982-09-16 | [5 empty] | Newman | looked for leak in HPR set. Found no leak.
91 | 72-30066-1 |  |  | 8 | Transmission |  | Fitting |  |  | Other |  | 1972-10-20 | 1973-09-25 | Other |  | Steel/Wrought Iron |  | Newman | Repaired leak on outlet union
91 | 72-30067-1 |  |  |  | Transmission |  | Fitting |  |  | Other |  | 1972-10-20 | 1973-09-25 | Other |  | Steel/Wrought Iron |  | Newman | Repair small leak on inlet union
|  |  |  | 6 | [13 empty] | Newman
|  |  |  | 2000-06-01 | [13 empty] | Newman
91 | 81-30108-1 |  |  | 2 | Distribution Main > 60 PSIG |  | Girth Weld |  |  | Construction Defect |  | 1981-06-05 | 1981-10-22 | Patch Welded |  | Steel/Wrought Iron |  | Newman | Rock pushed into wrap and weld ontee cut service and tested rewelded Tee
91 | 73-50246-1 |  |  | 0.5 | Service | ` | Fitting |  |  | Construction Defect |  | 1973-10-25 | 1973-10-25 | Replace Pipe and/or Service |  | Other | Plastic | Newman | Stiffmer cut thru plastic tubing. Replaced section to make repairs.
91 |  |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Other |  |  | 1990-03-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Newman | Pipe replaced by G.C. on GM. 4793667-90
|  |  |  | 6 | [11 empty] | Steel/Wrought Iron |  | Newman
| 02-30089- | [10 empty] | 2001-08-28 | [5 empty] | Newman | Deleted; HPR Box, Deleted & Moved to a multipurpose tag.
| 99-30130- |  |  | 0.75 | Service |  | Other |  | RELIEF | Other | REG | 1999-06-10 | 1999-06-10 | Other |  | Steel/Wrought Iron |  | Newman | Odor in air, Found blow off looking call. M&C - Relief valve leaking; Found relief blowing rebuilt Reg & Relief
91 | 90-30086-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1990-01-31 | 1991-05-23 | Replace Pipe |  | Steel/Wrought Iron |  | Newman | Main abandoned from Merced St to HWY 33; same
|  |  |  | 6 | [11 empty] | Steel/Wrought Iron |  | Newman
|  |  |  | 6 | [11 empty] | Steel/Wrought Iron |  | Newman | 6" gas main is 8" directly below old main
91 | 78-10016-1 |  |  | 4 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | Corrosion |  | 1978-03-10 | 1982-08-13 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Newman | 4" main settin in water from irrigation to Field.
91 | 90-30178-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1990-02-06 | 1990-02-15 | Other |  | Steel/Wrought Iron |  | Newman | Made repairs to HPR
| 99-70013- |  |  | 0.75 | Distribution Main |  | Other | Valves | RELIEF VALVE | Unknown |  | 1999-06-10 | 2000-10-30 | Other |  | Steel/Wrought Iron |  | Newman | Check press change out relief 30th; N/A
91 | 90-30179-1 |  |  | 0.75 | Distribution Main |  | Other |  |  | Other |  | 1990-02-07 | 1990-02-15 | Other |  | Other |  |  | Made repair to HPR
91 | 90-30177-1 |  |  | 3 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1990-02-06 | 1990-02-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Gustine | Made repair to HPR
| 99-70012- |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1999-06-10 | 2002-08-29 | Other | PIPE DOPE | Steel/Wrought Iron |  | Newman-Gustine | Doped threads and re-tightened
| 01-30057- | [10 empty] | 2001-08-24 | [5 empty] | Newman | entered .01 reading. Delete
| 99-70011-1 |  |  |  | Branch Service |  | Valves |  |  | Other | DRIED OUT GREASE | 1999-06-10 | 2000-10-30 | Other | GREASED VALVE | Steel/Wrought Iron |  | Newman-Gustine | Greased tighten soap test O.K.
91 | 90-30175-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1990-02-06 | 1991-06-03 | Other |  | Steel/Wrought Iron |  | Gustine | Repaired on GM 4924262-.91; Deleted; Removed on GM 4924262-9; ... 3-11-92; same, same
91 | 90-30173-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1990-02-06 | 1990-02-14 | Other |  | Steel/Wrought Iron |  | Gustine | Made repairs to HPR
91 | 90-30174-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1990-02-06 | 1990-02-14 | Other |  | Other |  |  | Made repairs
91 | 90-30176-1 |  |  | 4 | Distribution Feeder Main |  | Other |  |  | Other |  | 1990-02-06 | 1990-02-14 | Other |  | Steel/Wrought Iron |  | Gustine | Made repairs to valve
91 | 84-30136- |  |  | 2 | Distribution |  | Other |  |  | Other |  | 1984-06-07 | 1984-06-19 | Other |  | Steel/Wrought Iron |  | Gustine | Greased & operated valve
91 | 84-30135- |  |  | 4 | Other | D g... | Valves |  |  | Other |  | 1984-06-07 | 1984-06-19 | Other |  | Steel |  | Gustine | 2" valve leaking from 2" plug greasked & operated valved, redoped plug.
| 01-30058- |  |  | 0.75 | Transmission |  | Fitting | Regulator | REGULATOR | Other |  | 2001-08-29 | 2002-11-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Gustine | Rp, Repaired Leak; Rebuilt Reg Set
| 99-70015- |  |  | 0.75 | Distribution Main |  | Fitting | Other |  | Unknown |  | 2000-06-15 | 2000-10-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Gustine | Soap tested; dopped retighten soak test O.K.
91 | 90-30169-1 |  |  | 4 | Distribution Main |  | Other |  |  | Other |  | 1990-02-05 | 1990-02-15 | Other |  | Steel/Wrought Iron |  | Gustine | Made repairs to HPR station
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | Gustine
| 99-70018- |  |  | 0.75 | Transmission |  | Valves |  |  | Unknown |  |  | 2001-08-27 | Other | GREASED |  |  | Gustine | Grade 3...; Greased valve; Not uncovered
| 02-10042- | [10 empty] | 2002-08-26 | [5 empty] | Gustine | Deleted; delete - moved to multipurpose tag
91 | 90-30170-1 |  |  | 0.75 | Distribution Main |  | Other |  |  | Other |  | 1990-02-05 | 1990-02-15 | Other |  | Steel/Wrought Iron |  | Gustine | Made repairs to HPR
91 | 89--1 | [16 empty] | Gustine | Installed 1/2" Pl service & HPR set
|  |  |  | 4 | [11 empty] | Steel/Wrought Iron |  | Gustine
91 | 11-50133-B |  |  | 0.75 | Single Service |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2011-05-19 | 2011-05-19 | Other | REPLACED HPR | Steel |  | Gustine | Inlet of HPR; Replaced HPR; Soap tested
91 | 11-50081-B |  |  | 0.75 | Single Service |  | Regulator/Pilot |  |  | Other | NO PIPE DOPE | 2011-03-18 | 2011-04-13 | Tighten Cap/Bolt - Fitting |  | Steel |  | Gustine | HPR Box; Tightened cap and replaced Reg.; Replaced Reg and tightened cap soap Tested all Fittings Good
91 | 88-30024-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1988-05-10 | 1988-10-14 | Other |  | Steel/Wrought Iron |  | Gustine | Rebuilt HPR set; HPR for Canal Center
91 | 88-30024-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1988-05-10 | 1989-03-27 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Gustine | Repaired 301 on HPR (see attached note);
91 | 84-30138- | [10 empty] | 1984-06-07 | [6 empty] | Not on HPr= UG 301, Possible ... - No ... ; Delete upgrade; Deleted; found 0% with J.W., found no leakage w/ leak soap
91 | 86-30167- |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1986-09-10 | 1986-09-23 | Other |  | Steel/Wrought Iron |  | Gustine | Greased valves to repair 301
91 | 75-50130-1 |  |  | 4 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | Damage by outside Forces |  | 1975-07-29 | 1975-07-29 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Gustine | Large hole torn in pipe; Welded in 3' of 4" pipe; the...
| 10-81149- |  |  | 4 | Distribution Main >60 PSIG and <20% SYMS |  | Pressure Control Fittings |  |  | No/Deteriorated Pipe Dope |  | 2010-10-03 | 2010-12-16 | Other | REDOPED CAP | Steel |  | Gustine | Redoped Cap; M2 is 6' from face of curb. Deadened 1' past M2
| 99-70014- |  |  | 4 | Distribution Main |  | Valves |  |  | Other |  | 1999-06-15 | 2000-02-10 | Other | Greased valve | Steel/Wrought Iron |  | Gustine | Installed new grease. efusion installed; 5-1-00 Note: Unable to save instection data into IGIS because of lack of data.
97 | 89-30209-1 |  |  | 4 | Distribution Feeder Main |  | Fitting |  |  | Corrosion |  | 1989-08-03 | 1989-09-21 | Weld Over Sleeve or Can |  | Steel |  | Gustine | Replaced 3-1/4 inch coupling on Dist. Reg. Sta.
91 | 89-30210-1 |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1989-08-05 | 1989-08-16 | Other |  | Steel/Wrought Iron |  | Gustine | Valve ok
97 | 78-10019-1 |  |  | 4 | Distribution Main |  | Fitting |  |  | Material Failure |  | 1978-03-13 | 1979-03-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Gustine | Competion plug on 4" mueller was leaking
97 | 72-30072-1 |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1972-10-24 | 1972-12-18 | Other |  | Steel/Wrought Iron |  | Gustine
| 99-70017- | [16 empty] | Gustine | Delete; Grade 3; Moved to Mult. Purpose tab - HPR Set -;
91 | 78-10020-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-03-14 | 1980-05-06 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Gustine | ...Leak on seamless pipe between serv. tee and H.P.R. box only 4% reading; Possible leak on seamless pipe between H.P.R and serv. tee. Welded sleeve over corrosion leak.
| 99-70016- |  |  | 0.75 | Service |  | Fitting | Physical/Mechanical Joint | Physical/Mechanical Joint | Other |  | 1999-06-15 | 2000-02-08 | Other | Tightened Union | Steel/Wrought Iron |  | Gustine | Tightened union on H.P. side of regulator. Cleaned box
91 | 94-30086-1 | [10 empty] | 1994-10-27 | [5 empty] | Gustine | Delete
91 | 90-30172-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  |  | 1990-02-15 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Gustine | Repai to H.P.R. set. Changed broken box.
91 | 90-30171-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1990-02-05 | 1990-02-15 | Other |  | Steel/Wrought Iron |  | Gustine | Made repair to H.P.R.
| 01-30059- | [10 empty] | 2001-08-24 | [5 empty] | Gustine | Delete; Marked at valve. Moved to mult-purpose tag
91 | 89-30211-1 |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1989-08-03 | 1989-08-14 | Other |  | Steel/Wrought Iron |  | Gustine | Repaires to Reg. Pit
91 | 80-30291-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1980-10-30 | 1981-04-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Gustine | Installed...Riser insert Serv.; Instal service with 1/2" PL to H.P.R. box
|  |  |  | 0.5 | [11 empty] | Other Plastic |  |  | Service exposed to install.. Branch Service
91 | 74-30164-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Other |  | 1974-05-08 | 1978-05-19 | Other |  | Steel/Wrought Iron |  | Gustine | Repaired 2 fitting leaks; .03% H.P. Reg. Station.
91 |  |  |  | 2 | Distribution Feeder Main | [6 empty] | 1972-05-26 |  |  |  | Steel/Wrought Iron |  | Gustine | Note: 2" gas main exposed by back hoe installing sewer line. Light damaged to pipe coating. Wrapped with PL-Ken wrap.
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | New 6" stl. T.P. service (Foster Farms)
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | Livingston
|  |  |  | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Livingston | Pot hole 4" main; Pot holed 4" main (steel) depth 154"
|  |  |  | 04.00 & 06.00 | Transmission | [8 empty] | Other | DEACTIVATED DIST. MAIN > OR = 100FT. | Steel |  | Livingston | c/o 4" & 6" w/o valve #11; C/O 4" stl. At valve #11. Inst. 4" build Flange. C/o 8" stl. Abandoned and removed 6" stl. Bottom tap tie-in at 4" flange valve.
| 06-35000-1 | 118 | 23.26 | 4 | Transmission |  | Valves |  |  | Unknown |  | 2006-08-03 | 2006-06-07 | Other | Greased valves | Steel/Wrought Iron |  | Livingston | Greased valves and leaks stopped
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | Madera
72 | 81-35210-1 |  |  | 3 | Transmission |  | Valves |  |  | Damage by outside Forces |  | 1981-11-24 |  |  |  | Steel/Wrought Iron
|  |  |  | 0.25 | Transmission | [6 empty] | 2004-10-13 |  |  |  | Steel/Wrought Iron |  | Livingston | Installed: (1) new H.P.R. set 21' of 11/4" steel pipe, 23' of 2" steel pipe. (1) 11/4" split cont. fitting. (1) 11/4" Series #3M valve, F. Malcria 10/13/04. (1) valve from a cover. (1) H.P.R. box. See test data sheet for detail.
72 | 92-75012-1 | [10 empty] | 1992-11-06 | [5 empty] | Livingston | Less than 100PPM. This poper work can be eliminated. T & R department replaced lid on this valve box last year. They probably serviced this valve at that time, explaining low read.
|  |  |  | 1.25 | Transmission | [10 empty] | Steel/Wrought Iron |  | Livingston
| 03-75007-1 | 118 | 72.31 | 0.75 | Service |  | Valves |  |  | Unknown |  | 2003-02-18 | 2003-02-18 | Other |  | Steel |  | Livingston | Replace broken 3/4 valve at H.P.R. (packing bushing); Tee off tran. old style need EH. machine to shutdown
[5 empty] | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Livingston | Exposed 4" DFM per mid request tree stump removed
72 | 73-15082-1 |  |  | 4 | Transmission |  | Other |  |  | Other |  | 1973-07-17 | 1974-05-15 | Other |  | Steel/Wrought Iron |  |  | Tightened flanges on both sides of 4" fire valve
25 |  | 118 |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | At Water
[13 empty] | 2005-02-28 |  |  |  |  | Livingstonn | Raised valve cover approx. 5"
| 07-55015- |  |  | 0.75 | Single Service |  | Body of Pipe |  |  |  |  | 2007-03-19 | 2007-03-20 | Replace Partial Service |  | Steel/Wrought Iron |  | Livingston | Installed 20' of new pipe and two H.P. caplines; See attached test data presure report. Tal-working forman (559) 647-6615, Bob Superinendent (559) 994-9277; Contractor was trenching with an excavator to remove old drain line when he struch the 2" steel caseing instered with a .75" steel service. Yellow marks were visible and accurate at the time the dig-in occured.; Marks were visible and accurate. Contractor failed to notify PG&E to request a stand by.
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | New E.T.S. on transmission main 6"
|  | 118 |  | 2 | Distribution Main | [10 empty] | Steel |  |  | Abandoned Reg Pit c/o 3/4" T.P. to Pitt. Welded 2"/ -2 c/o 2"M.P. ... Box; Inst. one 2" M-2, c/o 2" stl. and 3/4" T.P. insto Reg.Pit. Abandoned and back filled box. Weld to return A.S.A.P. c/o fire valve at line 118
[5 empty] | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Exposed area 48" cover
|  | 118 |  | 8 | Transmission | [10 empty] | Steel |  | Merced | C/O 3/4" Stl. -3/4" fire valve off of L#118; c/o and abandoned 3/4" fire valve off of L-#118.
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Pot hole only 4 location. 16" to be installed job #30609011. 39" at 16" casing under 8". Under mission over pass Map 3498.A3
| 99-55050- | 118 |  | 0.75 | Transmission |  | Drip |  |  | Damage by 3rd Party |  | 1999-10-01 | 1999-10-01 | Other |  | Steel/Wrought Iron |  | Merced | Cut end caped old blow off.; No record of old blow off. Cut and welded closed
72 | 97-75019-1 |  |  | 1.25 | Transmission |  | Valves |  |  | Other |  | 1997-09-10 | 1997-09-10 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Merced | Found 11/4" valve leaking rebuilt valve.; valve leaking
Transmission
72 | 90-35046-1 | 118 |  | 0.75 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1990-06-06 | 1995-07-12 | Replace Pipe |  | Steel/Wrought Iron |  | Chowchilla | Corrosion leak on 3/4" T.P. Line to H.P.R. set off 8" T.P. Line 118.; Wled 3/4" pipe. Inst. About 2'ft.
72 | 83-35226-1 | 118 | [9 empty] | 1983-06-22 | [5 empty] | Merced | Tap off 118 for H.P.R. set 1/4mi. N/o Athlone Rd.
72 | 93-35037-1 | 118 | [9 empty] | 1993-06-10 | [5 empty] | Athlone | This 8" line has been cut off. No leak here LDS 6-19-96
72 | 80-75008-1 | 118 | 47.65 | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1980-07-28 | 1980-07-29 | Patch Welded |  | Steel/Wrought Iron
72 | 08-75042-1 | [10 empty] | 2008-08-13 | [5 empty] | Volta | No Leak;
72 | 79-35041-1 | 118 |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-06-19 | 1980-06-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron
72 | 92-35021-1 | 118 | [9 empty] | 1992-06-10 | [5 empty] | Chowchilla | 8" T.P. main has been cut off in this area- No leak here 6-19-96 LDS
72 | 86-35131-1 | 118 | [9 empty] | 1986-06-30 | [6 empty] | Leak over main by main...; 6-10-94 leakage bedining to effect crop. small area ... This 8" line has been cut off. No leak here LDS 6-19-96
|  | 331A |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | New 8" set
72 | 82-75039-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1982-10-12 | 1982-10-13 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Replaced 8' of 12" pipe
72 | 82-75038-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1982-10-12 | 1982-10-13 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | ...12" sp..sleeve
| 10-81706- | DREG4472 | 0.07 | 0.75 | Distribution Main >60 PSIG and <20% SYMS |  | Other |  | Station valve | Other | DETERIORATED GREASE | 2010-10-12 | 2011-01-21 | Greased - Other |  | Steel |  | Merced | Box s/e crnr intsctn; Greased valve- Soaped valve leak fixed
72 | 84-35015-1 | 1908 | [9 empty] | 1984-02-29 | [5 empty] | Chowchilla | Main. Main xing trucks;
72 | 84-35015-1 | [10 empty] | 1984-03-29 | [6 empty] | Leak over main 15'-30- W/o ...; readings are on both sides of ...
[12 empty] | 1998-02-23 | 1998-02-23 | [5 empty] | Replaced broken H.P.R. Box
|  | 118 | [13 empty] | Steel/Wrought Iron |  | Chowchilla | 5" Stl. casing with three 1 5/8 Ris docts inside. Depth of TP118 8" stl is 62". Quest const. bored approx. 54" below TP118-8" (pot holed prior to sore) To inst. 5" stl. casing with three 1 5/8" pls. conduits...
| 02-55001-1 | L118 | 30.24 | 12 | Transmission |  | Body of Pipe | Valves |  | Digin |  | 2002-01-24 | 2002-01-24 | Replace TP Main |  | Steel/Wrought Iron |  | Chowchilla | Replaced 15' of 12" Steel pipe; see attached sheet
| 09-35020-1 |  |  | 1.25 | Single Service |  | Plastic Tee Cap |  |  | Plastic Crack Failure |  | 2009-03-12 | 2010-07-19 | Replace Plastic Tee Cap - Plastic |  | PE2406 (Yellow or Orange) |  | Chowchilla | Replaced tee cap, soap test, OK; Replaced plstic tee cap
72 | 91-35008-1 | 118 |  | 3 | Transmission |  | Valves |  |  | Other |  | 1991-03-25 | 1991-05-15 | Other |  | Steel/Wrought Iron |  | Chowchilla | Greased valve, stopped leak.
72 | 82-75037-1 | 118 |  | 8 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1982-10-11 | 1982-10-11 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Chowchilla | Replace...H. ...main
|  |  |  | 08.00 & 12.00 | [11 empty] | Steel/Wrought Iron |  | Chowchilla | Daylighted 8" & 12" T.P. Mains
72 | 84-35036-1 | 331 |  | 0.5 | Service |  |  |  |  | Damage by outside Forces |  | 1984-08-07 |  |  |  | Aldyl A (Tan or Gray) |  | Santa Nella | Leak over service 6"...;...
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Santa Nella
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Santa Nella
|  |  |  | 600 | Transmission | [10 empty] | Steel/Wrought Iron |  | Santa Nella
|  |  |  | 06.00 & 12.00 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 331 |  | 06.00 & 12.00 | Transmission | [10 empty] | Steel/Wrought Iron
| 08-10251-1 | 2 | 82.41 | 0.75 | Transmission |  | Fitting |  |  | Other | THREAD SEAL | 2008-04-16 | 2008-04-16 | Other | THREAD SEALANT | Steel/Wrought Iron |  | Los Banos | In Box about 25ft. S.E. of Meter; I redoped nipple on Inlet side of primary H.P.R. set and replaced diaphram on Reg.
| 05-75021-1 | LBFEEDER |  |  |  |  | Fitting |  |  | Material Failure |  |  | 2005-10-06 | Tighten Cap or Bolt
72 | 76-35152-1 |  |  | 8 | Distribution Main |  | Fitting |  |  | Other |  | 1976-05-20 | 1976-05-20 | Other |  | Steel/Wrought Iron |  | Los Banos
|  |  |  | 4 | Transmission | [6 empty] | 1978-04-04 |  |  |  | Steel/Wrought Iron
72 | 94-35004-1 | 186 |  | 4 | Transmission |  | Tap Connection |  |  | Material Failure |  | 1994-02-24 | 1995-03-17 | Other |  | Steel/Wrought Iron |  | Red Top | Repaired broken 1/4". Lube tap to valve
72 | 93-35000-1 | 186 | [9 empty] | 1993-02-24 | [5 empty] | Red Top
72 | 09-35058-1 | 7208-01 | 0 | [8 empty] | 2009-05-04 | [5 empty] | Chowchilla
| 09-35058-1 | 7208-01 | 0 | [8 empty] | 2009-05-04 | [5 empty] | Chowchilla
| 09-35038-1 | 118 | 37.58 | [8 empty] | 2009-04-06 | [5 empty] | Fairmead
75 |  |  |  |  | Transmission
|  | 118 | 36.03 | 8 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | Fairmead
|  | 118 |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | Fairmead
72 | 84-55021-1 |  |  | 2 | Transmission |  | Body of Pipe |  |  | Digin |  | 1984-10-01 | 1984-10-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | ...No trace of any leak 2/6/85
|  | 118 | 20.58 | 12 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | Chowchilla | Pot hole Elect. Duct 3' Gas 47" at ...
72 | 98-55027-1 | 118A | 31.26 | 8 | Transmission |  | Body of Pipe |  |  | Digin |  | 1998-04-24 | 1998-04-24 | Replace Pipe |  | Steel/Wrought Iron |  | Permeada | Replace 6' of 8" T.P. Main
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Los Banos
|  | TP118A |  | 8.625 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party | [5 empty] | Steel/Wrought Iron |  | Madera
|  | TP118A |  | 8.25 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party | [7 empty] | Madera;
|  | TP118A |  | 8.625 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party | [7 empty] | Madera
|  | TP118B |  | 12 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party | [5 empty] | Steel/Wrought Iron |  | Madera
|  | TP118B |  | 12 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party | [7 empty] | Madera
|  | TP118B |  | 12 | Transmission | [12 empty] | Madera
|  | TP118B |  | 12 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party | [5 empty] | Steel/Wrought Iron |  | Madera
|  |  |  | 12 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party | [7 empty] | Madera
| 03-55044-1 | 118A | 30.41 | 8.625 | Transmission |  | Body of Pipe |  |  | Digin |  | 2003-08-22 | 2003-08-23 | Replace TP Main |  | Steel/Wrought Iron |  | Madera | Replaced 51ft. L-118; See CGT Job# 7048411-03 for detailed repair.
|  | 134 |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Valve 6.66 Line 134
72 | 10-35217-1 | 1907 | 772.26 | 0.75 | Single Service |  | Fitting |  |  | Other |  | 2010-10-16 | 2010-10-16 | Tighten Cap/Bolt - Fitting |  |  |  | Los Banos | This leak created to record repairs ... 10-81121. Paperwork was delayed and a 0 repair recheck was reordered on 10-81121. Before the repair paperwork was revised, making it impossible to enter the repair data. Per conversation w/ Dave... And G. Palmer I agree m... made..create 10-35217 for repair. ; Tightened plug
| 10-81121-1 | 2 | 72.25 | 0.75 | Single Service |  | Fitting |  |  | Other |  | 2010-10-09 |  |  |  | Steel/Wrought Iron |  | Los Banos | Per Dave. Issue Dist. Leak #10-35217 PM41416272
| 07-75047- | 186 | 5.81 | 4 | Transmission |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2007-11-21 |  |  |  | Steel/Wrought Iron |  | Dos Palos
| 07-95047- | 186 | 5.81 | 4 | Transmission |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2007-11-21 | 2007-12-06 | Deactivate #TP Main |  | Steel/Wrought Iron |  | Dos Palos | 275' of new 4" stl. Bored in under farmers water ditch
72 | 79-55008-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-05-03 | 1979-05-03 | Replace Pipe and/or Service |  | Copper |  | Dos Palos
|  |  |  | 2 | Gathering | [10 empty] | Steel/Wrought Iron |  | Dos Palos | See sketch on service order completed 7-2-09
| 77-55058-1 |  |  | 4 |  |  | Girth Weld |  |  | Construction Defect |  | 1977-11-07 | 1977-11-07 | Replace Pipe and/or Service |  | Steel |  | Dos Palos | Replaced- 17'-10' -4" T.P. main w/ X-42, SLPI, ERW pipe. Pipe tested for 1 hour and 10 minutes. Test pressure 1125 PSI. Testing and replacement supervised by B. Frankewich, Div. General foreman. Work completed by G.C. Crews and supervised by Bob Frankewich.
72 | 10-35035-1 | 118 | 14.99 | [8 empty] | 2010-04-23 | [5 empty] | Madera | No leak found
| 10-35035-1 | 118 | 14.99 | [8 empty] | 2010-04-23 | [5 empty] | Madera
|  |  |  | 6 | Transmission | [8 empty] | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Inspection only; Repair 6" line.
72 | 78-35076-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-03-09 | 1978-08-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Replaced 52' of 6" with .280 wall seamless. WO3-4289-C
72 | 78-35076-1 |  |  | 6 | Transmission | [6 empty] | 1978-03-09 |  |  |  | Steel/Wrought Iron
| 07-55064-1 | 186 | 21.07 | 6 | Transmission |  | Body of Pipe |  |  |  |  | 2007-03-29 | 2007-08-31 | Replace TP Main |  | Steel/Wrought Iron |  | Chowchilla | While grading dirt road, Corky Ofletree struck and punctured A. Exposed 6" T.P. line.; Excavator claimed to be working off another ticket by other pary. Invalid ticket was expired and for work other than what excavator was performing. That invalid tick was #204327
| 10-55032-B | 186 |  | 6 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | Damage by 3rd Party | DIG IN/EXCAVATION | 2010-11-29 | 2010-11-30 | Replace #TP Main < 50 ft |  | Steel |  | Chowchilla | Installed 41" 6.00 pre-tested pipe by G.C. Newman
|  |  |  | 6 | [11 empty] | Steel |  |  | 42" can of 6" pre-tested by G.C. Newman 456' s/w of reg. pit. RA50 Triangle "T" ranch
10-55032-
72 | 10-55232-B | 186 |  | 6 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | Digin/Excavation |  | 2010-11-29 |  | Replace #TP Main < 50 ft |  | Steel |  | Chowchilla | Installed 42" of 6" steel pipe. Installed 6" ANST 300 Control fitting
| 01-55054-1 | 186 | 18.8 | 0.75 | Transmission |  | Riser |  |  | Damage by 3rd Party |  | 2001-07-27 | 2001-07-27 | Other | C/o Riser at main | Steel/Wrought Iron |  | Dos Palos | C/O 3/4" stl. Blow off at main.; C/O 3/4" Stl. 2' 5/8 Main below ground. Installed barricade tape at c/o
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | Cut out old drip. Installed 2 18" pup
72 | 10-35096-1 | 186 | [9 empty] | 2010-07-07 | [5 empty] | Dos Palos
| 04-75024-1 | 186 | 19.31 | 6 | Transmission |  | Physical/Mechanical Joint |  | Physical/Mechanical Joint Flange Gaskets | Other | Grass Fire | 2004-09-06 | 2004-09-06 | Replace TP Main |  | Steel/Wrought Iron |  | Dos Palos | Replaced ML Vave 19.31 and blow offs with 6" steel pipe.; Remove V19.31, instal 16' .280WT 6" stl Pipe.
72 | 95-75018-1 |  |  | 8 | Transmission |  | Valves |  |  | Material Failure |  | 1995-08-02 | 1995-08-02 | Replace Pipe |  | Steel/Wrought Iron |  | Madera | C/O valve and abandoned tap. Welded new pipe and installed
72 | 85-35002-1 |  |  | 0.75 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1985-03-20 | 1986-05-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Madera | Leak over main between RR tracks and HWY.; 8-12-86...
| 08-10355-1 | 118 | 28.47 | 8 | Transmission | [13 empty] | ...PLS. Delete;
| 08-10355-1 | 118 | 28.47 | [8 empty] | 2008-04-14 | [5 empty] | Madera | Main
| 08-10354-1 | 118 | 28.58 |  | Transmission | [6 empty] | 2008-04-14 | [5 empty] | Madera
| 08-10354-1 | 118 | 28.58 | [8 empty] | 2008-04-14 | [5 empty] | Madera | Main
| 08-10356-1 |  | 16.64 | 12 | Transmission | [6 empty] | 2008-04-14 | [5 empty] | Madera | Southern cross. PLS. Delete. Above fround filling leaking. Dilled out multi-purpose tag GI403
| 08-10356-1 |  | 16.64 | [8 empty] | 2008-04-14 | [5 empty] | Madera | Main
72 | 89-35008-1 | 118 |  | 8 | [7 empty] | 1989-03-14 | [5 empty] | Madera
| 08-10352-1 | 118 | 27.67 |  | Transmission | [6 empty] | 2008-04-11 | [5 empty] | Madera | Southern Cross, PLS. Delete
| 08-10352-1 | 118 | 27.67 | [8 empty] | 2008-04-11 | [5 empty] | Madera | Main
| 08-10351-1 | 118 | 27.72 |  | Transmission | [6 empty] | 2008-04-11 | [5 empty] | Madera | PCF, PCF, Southern cross, PLS. Delete
| 08-10351-1 | 118 | 27.72 |  | Transmission | [6 empty] | 2008-04-11 | [5 empty] | Madera | PCF, PCF
| 98-55041-1 | 118 | 15.1 | 12 | Transmission |  | Body of Pipe |  |  | Digin |  | 1998-10-30 | 1998-10-30 |  |  | Steel/Wrought Iron |  | Madera | C/O and replaced 8' of 12" Stl Pipe
| 08-10353-1 |  |  | 0.75 |  |  | Fitting |  |  | Other | Dried Dope | 2008-04-11 | 2008-04-19 | Other | REDOPED 3/4" PLUG & TIGHTENED | Steel/Wrought Iron |  | Madera | Leak inside H.P.R.-Redoped 3/4" steel pluf
72 | 85-35004-1 | [10 empty] | 1985-04-04 | [5 empty] | Madera | leak over transmission main N/E/O Reg. Pit
| 95-35007-1 |  |  | 12 | Transmission |  | Fitting |  |  | Construction Defect |  | 2007-05-10 | 2007-06-05 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Madera | Found 2' sav-a-valve cp leaking, removed cleaned,a nd reinstalled cap
72 | 95-35007-1 | [10 empty] | 1995-04-24 | [5 empty] | Madera
|  | 118 |  | 12 | Transmission |  | Body of Pipe |  |  | Digin |  |  | 1994-08-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Madera | Weld on Sleeve
10 | 35229-A | 118 |  | 0.75 | Distribution Main > 60 PSIG |  | Fitting |  |  | Other |  | 2010-11-24 | 2010-11-24 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | Madera | High pressure valve in street; Tighten nut on 3/4" valve; Soap tested repairs- No leaks
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | In parking lot inline w/ pump inside fence 5/5 housed
|  | 118 |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | Madera | Day lighted three feet at 8" H.P. -50" at cover 3 +/- ....
70 |  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | Madera
|  | 118 |  | 8 | Transmission | [10 empty] | Steel |  | Madera | Locate wire was inst. on TP gas main 150' east of Nebraska ave. on N. Side of Cleveland Ave.
|  | 118 |  | 2 | Transmission | s | [9 empty] | Steel/Wrought Iron |  | Madera
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | Madera
70 |  |  |  | 3 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Madera
|  |  |  | 8 | Transmission | [10 empty] | Steel |  | Madera
| 08-55030- | 118 | 24.4 | 8 | Transmission |  | Fitting |  |  |  |  | 2008-08-04 | 2008-08-04 | Welded Sav-A-Valve - Weld |  | Steel/Wrought Iron |  | Madera | Instal. 2" save-a-valve....Damaged 3/4" soc tee. ; FML3 says gouge depth is not appropriate for this leak is but IGIS would ot let me process without an entry...; No stand-by requested by Foster and Son's. Foster and Sons did have a valid USA request on file. They did not request a stand by for grading on the day the incident occured. Dave Scott was on the jobsite. Three days prior to the incident Line #118 was clearly marked with yellow paint and offset marks.; Richard Matthews working for Luck Pase... of Fosters and Sons, using road grader ht and damaged gas system (c/o 3/4" Tap) both where aware of transmission line.
|  | 118 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | E.T.S. instalation only line 118 ING-5; New E.T.S.-ing- 5 27' off F-O-C w/side Ray Thomas alond pipeline
|  |  |  | 8 | Transmission | [10 empty] | Steel |  | Madera
|  |  |  | 2 | Service | [10 empty] | Steel/Wrought Iron
| 08-10202-1 | 118 | 23.39 | 2 | Distribution Main |  | Valves |  |  | Other | Needed grease | 2008-04-14 | 2008-04-14 | Other | Greased valve | Steel/Wrought Iron |  | Madera | At valve fitting and cover dry. N/e corner of intersection of Rd. and Ave. ...Anna Blakey greased valve. Leak repaired. Soap Tested Ok.
72 | 09-35113-1 | 118A | [9 empty] | 2009-07-22 | [5 empty] | Madera | Read found...repair in leak of CO-35011. This leak repaired again... GTLS...Instructed to delete 09-35113...;
72 | 00-35011-1 |  |  | 2 | Distribution Main <= 60 PSIG |  |  |  |  | Other |  | 2000-10-09 | 2009-02-11 | Other |  |  |  | Madera | Read post repair;
72 | 10-81156-1 | 118A | 23.37 | [8 empty] | 2010-10-04 | [5 empty] | Madera | ...09-35113 was replaced with this leak (GTLS) and capital order
72 | 09-35113-1 | 118A |  | 2 | Distribution Main <= 60 PSIG |  |  |  |  | Other |  | 2009-07-22 | [5 empty] | Madera | This leak deleted- multi-purpose copies... of 10-81156 creaed from post repair recheck 00-35011
| 09-35113-1 | 118A |  | 2 | Distribution Main |  | Valves |  |  | Other |  | 2009-07-22 |  |  |  | Steel/Wrought Iron |  | Madera | Old leak repair, original/Dist. (5yr) 2"...section) New T.P. survey...; Created from post repair recheck 00-35011; Trans or Dist? 2" on TP? was dist on original
66 | 81-20171-1 |  |  | 2 | Other |  | Fitting |  |  | Material Failure |  | 1981-05-07 | 1981-11-03 | Other |  | Steel/Wrought Iron |  | N. EDW's | Comment 1 page 2: Tightened fittings + pipe L.H 11-3-1981.
66 | 81-20211- |  |  | 2 | Distribution Feeder Main |  | Other |  | CC - Compressor Components | Construction Defect |  | 1981-05-20 | 1984-06-29 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | EDW's A.F.B | Comment 1 page 2: In reg pit.
66 | 92-20508-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1992-06-10 | 1992-09-12 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Kramer Junction | Comment 1 page 1: Welded 6" x 12" split sleeve over corrosion pit.
| 81-20169- | 300 |  | 2 | Other |  | Fitting |  |  | Material Failure |  | 1981-05-08 | 1981-11-03 | Other |  | Steel/Wrought Iron |  | Boyon | Comment 1 page 2: Tighten fittings & tubing
66 | 83-60000- |  |  | 0.25 | Other |  | Body of Pipe |  |  | Corrosion |  | 1983-01-04 | 1983-01-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Boron | Comment 1 page 2: Replaced 1/4" tubing from metric to recording gauge Jan 14 1983.
| 81-20212- |  |  | 6 | Other |  | Fitting |  |  | Material Failure |  | 1981-05-21 | 1981-11-03 | Other |  | Steel/Wrought Iron |  | Boron | Comment 1page 2: Leak all over set 9-17-81. Tightened fittings at rotary meter.
66 | 89-20202-1 |  |  | 6 | Transmission |  | Drip |  |  | Other |  | 1989-08-29 | 1989-09-08 | Other |  | Steel/Wrought Iron |  | Desert Lake | Comment 1page1: Grease valve.
66 | 89-20203-1 |  |  | 2 | Distribution Main |  | Valves |  |  | Other |  | 1989-08-29 | 1989-09-08 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Desert Lake | Comment 1 page 1: Grease valves tighten metrics.
Boren
| 76-20185- |  |  | 3 | Distribution Feeder Main | [6 empty] | 1976-04-27 | [5 empty] | Boron
|  |  |  | 6 | [14 empty] | Comment 1 page 2: Depth check on DFM - for proposed storm drain.
66 | 90-20381-1 |  |  | 1 | Transmission |  | Fitting |  |  | Other |  | 1990-08-22 | 1991-03-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Boron | Comment 1 page 1: Repaired leaks on caps on tap tee's.
[16 empty] | Steel/Wrought Iron |  | Trona | Comment 1 page 2: Cadwell leads for ETS station - install paddles pipe wrap chipped from main clean + repair.
66 | 91-20526-1 | 311 |  | 4 | Distribution Main |  | Valves |  |  | Other |  | 1991-06-21 | 1991-06-28 | Other |  | Steel/Wrought Iron |  | Trona | Comment 1 page 1: Greased valve.
Trona
| 76-20119- | [10 empty] | 1976-04-14 | 1976-04-14 |  |  |  |  | Trona | Comment 1 page 2: Found leak in HSE line cust. in process of replacing same. .1% at HSE line (2 capt)
| 76-20120- |  |  | 0.75 | [7 empty] | 1976-04-14 |  |  |  | Steel/Wrought Iron |  | Trona
| 76-20121- | [10 empty] | 1976-04-14 | 1976-04-14 |  |  |  |  | Trona | Comment 1 page 2: Found 3 cu ft per hour leak in cust house line - sealed metric & left hazard notice.
Comment 1 page 1: Note: this was not the original "A" form sent to R.C.
66 | 91-20502-1 |  |  | 3 | Distribution Feeder Main |  | Girth Weld |  |  | Construction Defect |  | 1991-01-22 | 1992-08-04 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | China Lake | Comment 1 page 1: Welded 6" can on main over bad weld.
[16 empty] | Steel/Wrought Iron |  |  | Comment 1 page 2: We made repairs while IMC backfilled & added an ETS station on North End 19' from Pipeline Marker.
66 | 76-20105- |  |  | 10 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1976-04-12 | 1976-04-21 | Other |  | Steel/Wrought Iron |  | Trona Road- Argus | Comment 1 page 2: Found tap valve leaking - greased valve stoped leak- left valve off -
66 | 82-20209- |  |  | 2 | Other |  | Fitting |  |  | Other |  | 1982-05-11 | 1982-05-11 | Other |  | Steel/Wrought Iron |  | Trona
|  |  |  | 6 | [8 empty] | 2002-07-11 |  |  | Steel/Wrought Iron |  |  | Comment 1 page 1: Rewrap damaged section of 6" pipe; Comment 1 page 2: Rewrap damaged section of wrap.
66 | 92-20502-1 |  |  | 2 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1992-01-07 | 1992-01-08 | Other |  | Steel/Wrought Iron |  | China Lake N.W.C. | Comment 1 page 1: Tap valve needed grease
66 | 71-00012- |  |  | 6 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | Comment 1 page 2: Exposed 80' of main and found no indication of a gas leak. No indication of leak in street however at time of survey a leak existed in adjacent building on appliane line. Found by P.G.&E at time of inspection by PG&E crews.
|  |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  | 1976-10-20 | 1976-10-20 | Other |  | Steel/Wrought Iron |  | China Lake
|  |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  | 1976-10-20 | 1976-10-20 | Other |  |  |  | China Lake | Comment 1 page 2: Exposed main at this location found gas leak on China Lak Gas line.. "not PG&E facilities"
|  |  |  | 6 | Distribution Feeder Main |  |  | Other |  | Other |  | 1976-10-20 | 1976-10-20 | Other |  | Steel/Wrought Iron |  | China Lake | Comment 1 page 2: Dug up main-no leaks found- ground saturated with fuel oil.
71-00013-
| 76-20103- |  |  | 0.75 | Other | [6 empty] | 1976-04-09 | [5 empty] | China Lake
|  |  |  | 6 | Distribution Feeder Main | [12 empty] | Ridgecrest
66 | 91-20501-1 |  |  | 8 | Distribution Feeder Main |  | Girth Weld |  |  | Construction Defect |  | 1991-01-21 | 1992-08-06 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | RC | Comment 1 page 1: Inst. 3/4" sava-valve over bad spot in weld as per standard practice A-65.
|  |  |  | 0.5 | [7 empty] | 2006-12-12 | 2006-12-15 | Replace Partial Service |  | TR 418 |  |  | Comment 1 page 1: We replaced bent riser and added 1 ft. of 1/2" plastic gas pipe. Not leaking; Comment 1 page 2: Riser was damaged by auto-replaced riser/meter set.
66 | [17 empty] | Ridgecrest | Comment 1 page 2: Pothole main for depth & find ETS, also caldweld 2 - 2" wires on 1 on each side of kero test, and 2-10 on w/side kerotest ran over to ETS. Wrapped main backfilled. M. Storment 02/12/1996.
|  |  |  | 6 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | Ridgecrest
|  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Ridgecrest
|  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Ridgecrest
R/C
Ridgecrest
66 | 88-20029-1 | [10 empty] | 1988-03-17
66 | 88-20029-1 | [10 empty] | 1988-03-17
66 | 91-20503-1 |  |  | 0.75 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1991-01-25 | 1991-02-04 | Other |  | Steel/Wrought Iron |  | Ridgecrest | Comment 1 page 1: Greased valve.
[7 empty] | Body of Pipe |  |  | Material Failure |  |  | 1991-01-10 | Replace Pipe
52 | 85-57004-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1985-11-06 | 1985-11-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Install 14'4'' of 6'' pipe w.t. .280
98 | 11-55001-1 | 300A | 0.64 | 0.75 | Transmission >= 20% SMYS |  | Curb Valve |  |  | Other |  | 2011-02-04 | 2011-02-07 | Other |  | Steel |  | Needles | Closed Curb Valve, vented downstream;
98 | 11-55001-1 | 300A | 0.64 | 0.75 | Transmission >= 20% SMYS |  | Curb Valve |  |  | Other |  | 2011-02-04 | 2011-02-07 | Other | Installed new stew cap & O-Rings on curb stop valve | Steel |  | Needles | Approx 15Ft. North of A-6 Scrubber outlet valve; Closed curb stop valve, vented dowstream pressure. Removed and installed new stem cap and O-Rings for curb stop valve; Sketch shows aerial view of leak location and side of valve position. Valve box and cover was about 6" below ground level.
98 | 11-55001-1 | 300A | 0.64 | 0.75 | Transmission >= 20% SMYS |  | Curb Valve |  |  | Other |  | 2011-02-04 | 2011-02-07 | Other | Installed new stem cap and O-rings on curb stop valve. | Steel |  | Needles; | Approx 15Ft. North of A-6 Scrubber outlet valve; Closed curb stop valve, vented downstream pressure. Removed and installed new stem cap and o-rings for curb stop valve.; Sketch shows aerial view of leak location and side view of valve position. Valve box and cover was about 6" below ground level.
| 10-81386-1 | 300A | 0.38 | 12 | Transmission |  | Valves |  |  | Unknown |  | 2010-10-11 | 2010-10-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Needles | Removal stack extension and installed unibolt cap. Greased valve with 50/50 and tested cap. No leak.
| 10-30017-1 | 300A | 0.64 | 16 | Transmission |  | Mechanical Joint |  |  | Other | Misaligned Flange | 2010-09-20 | 2010-10-09 | Other | Installed new gasket. | Steel/Wrought Iron |  | Needles | Installed new gasket for flange and reassigned.
98 | 09-30007-1 | 300A | 3.25 | 0.75 | Transmission >= 20% SMYS |  | Curb Valve |  |  | No/Deteriorated Pipe Dope |  | 2009-08-31 | 2011-04-28 | Mechanical Repair Fitting - Fitting |  | Steel |  | Needles | Fire valve marked with yesllow paint.; IRE valve marked w/ yellow paint; Replaced O-Rings in cap.
| 09-30007-1 | 300A | 3.25 | [8 empty] | 2009-08-31 | [5 empty] | Topock District | Fire valve marked with yellow paint.
| 10-81002-1 | 300A | 4.53 | 0.25 | Transmission |  | Fitting |  |  | Other | Loose fitting | 2010-08-31 | 2010-10-12 | Soap and/or Tape - Other |  | Steel/Wrought Iron |  | Needles
98 | 10-88778-1 | 300A | 6.93 | 12 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-29 | 2011-04-28 | Tighten Cap/Bolt - Fitting |  | Steel |  | Needles | MP 6.93A blow off; Tighten unibolt cap.
| 10-88778-1 | 300A | 6.93 | 12 |  |  | Other |  | Unibolt | Other | Loose cap | 2010-10-29 |  |  |  | Steel/Wrought Iron |  | Needles
98 | 10-81003-1 | 300A | 6.93 | 0.75 | Transmission >= 20% SMYS |  | Curb Valve |  |  | Unknown |  | 2010-08-31 | 2011-02-25 | Other | Replaced Stem O-rings | Steel |  | Needles | Replaced Stem Cap O-rings; Closed valve, vented downstream pressure, removed stem cap, replaced o-rings, reinstalled cap, pressurized and soap tested for leaks, No leaks.
| 10-81003-1 | 300A | 6.93 | [8 empty] | 2011-08-31 | [5 empty] | Needles
| 10-81003-1 | 300A | 6.93 | 34 | Transmission |  | Valves |  |  | Unknown |  | 2010-08-31 |  |  |  | Steel/Wrought Iron |  | Topock District
| 10-81005-2 | 300A | 10.85 | 0.5 | Transmission |  | Valves |  |  | Other | Loose fitting | 2010-09-01 | 2010-10-14 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | Needles | Tightened valve and packing, soap test, no leaks.
| 10-81005-1 | 300A | 10.85 | 0.5 | Transmission |  | Valves |  |  | Other | Loose Fitting | 2010-09-01 | 2010-10-14 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | Topock District Pipeline | Tightened valve and packing, soap test, No leaks.
| 10-81004-1 | 300A | 10.85 | 0.75 | Transmission |  | Drip |  |  | Other | Loose Fitting | 2010-09-01 | 2010-10-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Needles | Blew down, taped both ends on nipple, and soap tested. No leaks.
| 10-82067-1 | 300A | 16.33 | 12 | Transmission |  | Other |  | Unibolt Cap | Other | Gasket | 2010-10-10 | 2010-10-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Needles | Blow down, removed lid, installed with tight seal, soap test, Ok.
| 10-82069-2 | 300A | 20.84 | 12 | Transmission |  | Other |  | Unibolt Cap | Other | Gasket | 2010-10-09 | 2010-10-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Needles | Removed cap, installed with tight-seal, checked, no leaks.
| 10-82069-1 | 300A | 20.84 | 12 | Transmission |  | Other |  | Unibolt Cap | Other | Gasket | 2010-10-09 | 2010-10-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Needles | Removed cap, installed with tight-seal, checked no leaks.
| 07-30006-1 | 300A | 21.23 | 12 | Transmission |  | Other |  | Unibolt Cap | Other | Gasket | 2007-09-27 | 2010-10-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Needles | Removed lid, installed with tight-seal, no leaks.
| 07-30007-1 | 300A | 21.23 | 12 | Transmission |  | Valves |  |  | Other | Loose Cap | 2007-09-27 | 2010-10-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Needles | Removed cap, installed with tight-seal, checked, no leaks.
98 | 10-88777-1 | 300A | 25.71 | 12 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-29 | 2011-04-17 | Tighten Cap/Bolt - Fitting |  | Steel |  | Needles | Tightened unibolt cap.
| 10-88777-1 | 300A | 25.71 | 12 | Transmission |  | Other |  | Unibolt Cap | Other | Loose Cap | 2010-10-29 |  |  |  | Steel/Wrought Iron |  | Topock DIstrict
| 08-30009-1 | 300A | 31 | 34 | Transmission |  | Longitudinal Weld |  |  | Weld Failure |  | 2008-10-28 | 2010-10-15 | Welded Sav-A-Valve - Weld |  | Steel/Wrought Iron |  | Needles-Topock District | Made repair follwoing WO Standard 34134. As per Mike Teare Instruction.
| 07-30008-1 | 300A | 30.79 | 12 | Transmission |  | Other |  | Unibolt Cap | Other | Loose Cap | 2007-09-27 | 2010-09-02 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Needles | Checked cap during annual leak survey and no leak.
| 09-30009-1 | 300A | 31.69 | 34 | Transmission |  | Longitudinal Weld |  |  | Weld Failure |  | 2009-09-02 | 2010-10-15 | Welded Sav-A-Valve - Weld |  | Steel/Wrought Iron |  | Needles-Topock District Pipeline | Repaire made by following gas standard A-53. Using 2" Sav-A-Valve as per Mike Teare instructions. Also followed WO Standard 34134
98 | 10-88776-3 | 300A | 40.87 | 0.5 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-28 | 2011-05-04 | Soap and/or Tape - Other |  | Steel |  | Needles | Replaced Teflon Tap
| 10-88776-3 | 300A | 40.87 | 0.5 |  |  | Fitting |  |  | Unknown |  | 2010-10-28 |  |  |  | Steel/Wrought Iron |  | Needles
| 10-88776-2 | 300A | 40.87 | 0.25 |  |  | Fitting |  |  | Unknown |  | 2010-10-28 |  |  |  | Steel/Wrought Iron |  | Needles
98 | 10-88776-1 | 300A | 40.87 | 0.5 | Transmission >= 20% SMYS |  | Fitting |  |  | Unknown |  | 2010-10-28 | 2011-05-04 | Soap and/or Tape - Other |  | Steel |  | Needles | Replaced Teflon Tap
| 10-88776-1 | 300A | 40.87 | 0.5 |  |  | Fitting |  |  | Unknown |  | 2010-10-28 |  |  |  | Steel/Wrought Iron |  | Needles
| 10-88776-6 | 300A | 40.87 | 0.5 |  |  | Fitting |  |  | Unknown |  | 2010-10-28 |  |  |  | Steel/Wrought Iron |  | Needles
| 10-88776-5 | 300A | 40.87 | 0.75 |  |  | Fitting |  |  | Unknown |  | 2010-10-28 |  |  |  | Steel/Wrought Iron |  | Needles
| 10-30019-7 | 300A | 40.87 | 1 | Transmission |  | Valves |  |  | Other | Loose Fitting | 2010-09-02 | 2010-10-07 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | Needles | Removed line, taped both ends with teflon tape, reinstalled, open valve, and soap tested, no leaks.
98 | 10-88775-1 | 300A | 51 | 12 | Transmission >= 20% SMYS |  | Other |  |  | Unknown |  | 2010-10-28 | 2011-04-16 | Tighten Cap/Bolt - Fitting | Tightened unibolt cap | Steel |  | Needles
| 10-88775-1 | 300A | 51 | 12 |  |  | Other |  | Unibolt cap | Unknown |  | 2010-10-28 |  |  |  | Steel/Wrought Iron |  | Needles
| 09-30010-1 | 300A | 51.5 | 34 | Transmission |  | Unknown |  |  | Unknown |  | 2009-09-02 | 2010-09-03 |  |  | Steel/Wrought Iron |  | Needles | Surveyed line during annual survey with an HFI unit. Unable to fing leak. Had KBS8 re-survey area to verify, there was no leak.
| 07-30010-1 | 300A | 55.89 | 12 | Transmission |  | Other |  | Unibolt cap | Other | Loose cap | 2007-09-28 | 2010-10-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Needles | Removed lid, installed with tight-seal, no leaks.
| 07-30002-1 | 300A | 60.92 | 12 | Transmission |  | Other |  | Unibolt cap | Other | Loose Cap | 2007-09-25 | 2010-09-14 |  |  | Steel/Wrought Iron |  | Needles | During annual survey stack was checked and was not leaking.
| 07-30011-1 | 300A | 60.92 | 12 | Transmission |  | Other |  | Unibolt Cap | Other | Loose Cap | 2007-09-28 | 2010-09-14 |  |  | Steel/Wrought Iron |  | Needles | During annual leak survey, checked stack and no leak.
| 07-30011-1 | 300A | 60.92 | 34 | Transmission |  | Valves |  |  |  |  | 2007-09-28 | [6 empty] | Unibolt fitting to blow down stack;
| 09-30014-1 | 300a | 68.36 | [8 empty] | 2009-09-03 | [5 empty] | Topock District | Closed by Ridgrest Crew; gdd4 found 3/4" line going to reg. #4, leaking at tee. Found nipple between 2 elbows going to unmarked reg. leaking at both ends. All repairs will have to be done after unit is taken out of service. Repaired leak at bushing going to unmarked reg. may not be needed; as it is not hooked to anything.
| 10-81387-1 | 300a | 66.26 | 12 | Transmission |  | Other |  | Unibolt cap | Other | Loose Cap | 2010-10-10 | 2010-10-11 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Needles | Removed unibolt cap, cleaned gasket surface and cap. Used tight-seal on gasket, re-installed unibolt cap and tested at 100PSI, no leak
| 07-30009-1 | 300A | 66.25 | 12 | Transmission |  | Other |  | Unibolt Cap | Other | Loose Cap | 2007-09-27 | 2010-10-11 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Needles | Removed unibolt cap, cleaned gasket surface and cap. Used tight-seal on gasket. Re-installed unibolt cap and tested at 100 PSI no leak
| 07-30009-1 | 300A | 66.25 | 34 | Transmission |  | Valves |  |  |  |  | 2007-09-27 | [5 empty] | Needles | Uninolt fitting to blow down stack;
| 07-30004-1 | 300A | 71.98 | 0.75 | Transmission |  | Fitting |  |  | Other | LOSE FITTING | 2007-09-26 | 2010-09-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | NEEDLES-TOPOCK DISTRICT PIPELINE | DURING ANNUAL LEAK SURVEY SOUP TESTED ALL FITTING. NO LEAKS
98 | 10-81010-1 | 300A | 74.36 | 0.375 | Transmission >= 20% SMYS |  | Fitting |  |  | Unknown |  | 2010-09-15 | 2011-02-16 | Soap and/or Tape - Other |  | Steel |  | Needles | Small bubbles on reg #6 filter and sening line; MP 74.36; Tighten fitting on sensing line
| 10-81010-1 | 300A | 74.36 | 1 |  |  | Fitting |  |  | Other | Loose Fitting | 2010-09-15 |  |  |  | Steel/Wrought Iron |  | Needles | Small bubbles on filter for reg #6
98 | 10-81007-1 | 300A | 60.92 | 0.75 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-09-14 | 2011-02-16 | Tighten Cap/Bolt - Fitting |  | Steel |  | Needles | MLV 60.90A, U/S Gge line vlv packing; Soap tested small bubbles; Scanned to Wendy Geroge 2-21-11 DLLD; Shut valve and tighten packing
| 10-81007-1 | 300A | 60.9 | 34 | [7 empty] | 2010-09-14 | [6 empty] | U/S Guage line valve packing - soap tested small bubbles; MLV 60.9A
| 10-81007-1 | 300A | 60.92 | 34 | Transmission |  | Fitting |  |  | Other |  | 2010-09-14 |  |  |  | Steel/Wrought Iron |  |  | up stream gauge line valve packing - soap tested fitting - small bubbles*; mlv
98 | 10-81010-2 | 300A | 74.36 | 0.375 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | No/Deteriorated Pipe Dope |  | 2010-09-15 | 2011-02-16 | Soap and/or Tape - Other |  | Steel |  | Needles | Amboy reg M.P. 74.36A connected to Reg 5; Bubbles on unmrked vlv, conne; scanned to Wendy George 2-21-11 DLLD; Replaced Teflon tape & tighten fitting
| 10-81010-2 | 300A | 74.36 | 1 |  |  | Fitting |  |  | Other | Loose fitting | 2010-09-15 |  |  |  | Steel/Wrought Iron |  | Needles | Small bubbles on unmarked valve, connected to reg #6
| 10-82062-1 | 300A | 76.32 | 12 | Transmission |  | Other |  | Unibolt cap | Other | Loose cap | 2010-10-10 | 2010-10-20 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | Needles | Leak at Unibolt cap on BDV 76.32A; Repair was on a unibolt enclousure. Had to service the enclosure
98 | 10-81008-1 | 300A | 81.29 | 34 | Transmission >= 20% SMYS |  | Fitting |  |  | Unknown |  | 2010-09-15 | 2011-04-28 | Tighten Cap/Bolt - Fitting |  | Steel |  | Mojave | Sent to Wendy 5/20/11 DLLD; MLV 81.29 D/S gauge tap vlv lking as packing n...; MLV 81.29 Soap tested
| 10-81008-1 | 300A | 81.29 | 34 | [7 empty] | 2010-09-15 | [6 empty] | MLV 81.29 D/S Gauge Tap Valve leaking at packing nut - Soap tested
| 07-30005-1 | 300A | 87.1 | 12 | Transmission |  | Other |  | Unibolt Cap | Other | Lose cap | 2007-09-26 | 2010-10-11 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | Needles | Scan Wendy 10/25/10 DLLD; Unibolt Cap; Remove unibolt cap and cleaned gasket surface. Aplied tight seal to gasket and reinstalled. Checked for leaks at 100 PSI
| 10-81009-1 | 300A | 92.27 | 12 | Transmission |  | Other |  | Unibolt Cap | Other | Loose Cap | 2010-09-16 | 2010-10-21 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | Needles | Scan GT mapping 10/20/10 DLLD; Blow off stack leaking at unibolt cap; Removed Cap, cleaned gasket surface and gasket. Applied tight seal to gasket and re-installed cap. Tested no leaks
| 07-30003-1 | 300A | 92.27 | 12 | Transmission |  | Valves |  |  | Other | Lose Cap | 2007-09-25 | 2010-09-16 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | Topock District - Pipeline | Scan Wendy Lu 10/25/10 DLLD; Unibolt Cap; Removed cap and cleaned gasket and gasket surface. Applied tight seal to gasket and re-installed cap. Tested and no leaks
| 07-30003-1 | 300A | 92.27 | [8 empty] | 2007-09-25 | [5 empty] | Needles | unibolt fitting to blow down stack; unibolt fitting to blow down stack
| 10-81011-1 | 300A | 102.15 | 0.75 | Transmission |  | Fitting |  |  | Other | Loose fitting | 2010-09-17 | 2010-10-11 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | Needles | Scan GT mapping 10/20/10 DLLD; Save a valve on span leaks from cap soap tested; Reserved save a valve completion plug & cap with teflon tape. Soap tested to verfity repair
| 09-30016-1 | 300A | 106.39 | 34 | Transmission |  | Fitting |  |  | Other | Loose cap | 2009-09-01 | 2010-10-11 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | Needles | 200 yrds East of R.R. tracks - West side of wash
| 09-30016-1 | 300A | 106.39 | 34 |  |  | Unknown |  |  | Unknown |  | 2009-09-01 |  |  |  | Steel/Wrought Iron |  | Topock District | 200 yrds east of RR tracks, west of wash; leak is approximately 200 yards south of railroad tracks on westside of wash bed. Resealed completion plug and cap with teflon tape. Soap tested to verify repair
98 | 10-81385-1 | 300B | 0.24 | 0.75 | Transmission >= 20% SMYS |  | Curb Valve |  |  | Other | O-Rings | 2010-10-10 | 2010-10-16 | Deactivated Partial Service |  | Steel |  | Needles | At valve in pit 0.24B; Closed Valve; Closed valve supplying gas to rack. Vented off pressure at rack, soap tested stem to verify leak has stopped.
| 10-81385-1 | 300A | 0.21 | 34 | Transmission |  | Valves |  |  | Unknown | [5 empty] | Steel/Wrought Iron |  | Topock district pipeline | Leak at valve pit
| 10-81382-1 | 300B | 0.24 | 0.75 | Single Service |  | Valves |  |  | Other | Stem seals leak | 2010-10-10 | 2010-10-16 | Deactivated Partial Service |  |  |  | Needles | .24B outside PG&E/Socal intertie fence line, east side; Closed fire valve going to a rack, vented pressure at rack. Soap tested stem to verify leak has stopped
| 10-81383-2 | 300B | 0.24 | 16 | Transmission |  | Other |  | Bolted flange | Other | Loose Bolts | 2010-10-10 | 2010-10-16 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | Needles | MP 0.24B L300B North East flange; Tightened north east flange bolts to stop leak. Soap tested to verify repair
98 | 10-81383-1 | 300B | 0.24 | 24 | Transmission >= 20% SMYS |  | Fitting |  |  | Unknown |  | 2010-10-10 | 2010-10-16 | Tighten Cap/Bolt - Fitting |  | Steel |  | Needles | at flange; Scanned to Gendy George 2-21-11 DLLD; Tightened flange; Tightened flange bolts soap tested. Leak stopped.
| 10-81383-1 | 300B | 0.24 | 34 |  |  | Fitting |  |  | Unknown |  | 2010-10-10 | [5 empty] | Topock District Pipeline
| 10-81381-1 | 300B | 0.45 | 16 | Transmission |  | Other |  | Fittings | Other | Loose Fittings | 2010-10-10 | 2010-10-20 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | Needles | Topock Compressor station Line 300B B-3 scrubber orifice meter; Tighten all fittings on orifice meter. Checked and no leaks.
| 10-81384-1 | 300B | 0.75 | 34 | Transmission |  | Valves |  |  | Other | Stem packing | 2010-10-10 | 2010-11-01 | Other | Tightened packing gland | Steel/Wrought Iron |  | Needles | 0-75B L-300 West Gauge line valve
| 10-81384-1 | 300B | 0.75 | 34 | Transmission |  | Valves |  |  |  |  | 2010-10-10 |  |  |  | Steel/Wrought Iron |  | Topock District Pipeline | Leak @ gauge line valve; Tighten packing glan - no leak.
98 | 10-82066-1 | 300B | 10.5 | 12 | Transmission >= 20% SMYS |  | Other |  | Unibolt Cap | Other |  | 2010-10-09 | 2011-04-27 | Tighten Cap/Bolt - Fitting |  | Steel |  | Needles | L-300B @ 10.50, Unibolt Cap; Tighten Unibolt Cap
| 10-82066-1 | 300B | 10.5 | 12 | Transmission |  | Other |  | Unibolt Cap | Other | Gasket | 2010-10-09 |  |  |  | Steel/Wrought Iron |  | Needles | Unibolt Cap; 10.50
98 | 10-81404-1 | 300B | 6.98 | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Unknown |  | 2010-10-25 | 2011-04-27 | Mechanical Repair Fitting - Fitting |  | Steel |  | Needles | Sent to Wendy 4-28-11 DLLD; MP 6.98B small bubbles on nipple @ TEG; L300B MP 6.98; Tighten fitting; Tighten fitting at nipple
| 10-81404-1 | 300B | 6.98 | 0.75 | Transmission |  | Fitting |  |  | Unknown |  | 2010-10-25 |  |  |  | Cast/Ductile Iron |  | Needles | Sent GT mapping 11-1-10 DLLD WR# 174426; M.A 6.98B Small bubbles, on nipple, at TEG
98 | 10-30001-3 | 300B | 10.47 | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Other | Tighten cap | 2010-10-25 | 2011-04-27 | Tighten Cap/Bolt - Fitting |  | Steel |  | Needles | Sent to Wendy 4-28-11; MP 10.47 South Gauge Line for Valve A leaks; Tighten valve
98 | 10-88795-2 | 300B | 10.5 | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Other | Loose Fitting | 2010-10-25 | 2011-04-27 | Tighten Cap/Bolt - Fitting |  | Steel |  | Needles | Sent to Wendy 4-28-11; MP 10.50B dwn stream guage line valve leaks; Tighten Valve
| 10-88795-2 | 300B | 10.5 | 0.75 | Transmission |  | Fitting |  |  | Other | Loose Fitting | 2010-10-25 |  |  |  | Steel/Wrought Iron |  | Needles | Sent Wendy Liu 11-1-10 DLLD WR#174431; MP 10.50B down stream guage line valve leaks
98 | 10-30001-2 | 300B | 10.5 | 0.75 | Transmission >= 20% SMYS |  | Curb Valve |  |  | Other |  | 2010-10-25 | 2011-04-27 | Tighten Cap/Bolt - Fitting |  | Steel |  | Needles | Sent to Wendy 4-28-11; MP 10.50B Down stream guage lien valve leaks; U/S gauge tap valve tighten fitting; Tighten
98 | 10-81403-1 | 300B | 15.93 | 12 | Transmission >= 20% SMYS |  | Other |  | Unibolt Cap | Other |  | 2010-10-25 | 2011-04-27 | Tighten Cap/Bolt - Fitting |  | Steel |  | Needles | Sent to Wendy 4-28-11 DLLD; L300B @ MP15.93 Unibolt cap @ blwdwn stack; Tighten unibolt cap
| 10-81403-1 | 300A | 15.93 | 12 | Transmission |  | Other |  | Unibolt Cap | Other | Loose cap | 2010-10-25 |  |  |  | Steel/Wrought Iron |  | Needles | Sent GT mapping 11-1-10 DLLD; Unibolt cap at blowdown stack
98 | 10-81405-1 | 300B | 20.82 | 34 | Transmission >= 20% SMYS |  | Other Mechanical Joint |  |  | Other |  | 2010-10-26 | 2011-04-28 | Tighten Cap/Bolt - Fitting |  | Steel |  | Needles | Sent to Wendy 4-28-11 DLLD; MP 20.82B; Line 300B MP 20.82, repairing undr way; Flange on upstream cross over
| 10-81405-1 | 300B | 20.82 | 34 | [7 empty] | 2010-10-26 | [5 empty] | Needles | Sent GT mapping 11-1-10 DLLD; MP 20.82B
98 | 10-81405-1 | 300B | 20.82 | 34 | Transmission >= 20% SMYS |  | Other Mechanical Joint |  |  | Other |  | 2010-10-26 | 2011-01-21 | Tighten Cap/Bolt - Fitting |  | Steel |  | Needles | MP 20.82B; Flange on upstream crossover loose bolts, retorque all bolts
98 | 10-88794-2 | 300B | 40.49 | 1 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-27 | 2011-05-04 | Soap and/or Tape - Other |  | Steel |  | Needles | Sent to Wendy 5-20-11 DLLD; Replaced pipe tape on fitting
| 10-88794-2 | 300B | 40.49 | 1 | Transmission |  | Fitting |  |  | Other | Loose Fitting | 2010-10-27 |  |  |  | Steel/Wrought Iron |  | Needles | Sent GT mapping 11-1-10 DLLD WR# 145679; Nipple on power gas line
98 | 10-81406-1 | 300B | 50.61 | 0.75 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-26 | 2011-04-28 | Greased - Other |  |  |  | Needles | Sent to Wendy 4-29-11 DLLD; 1/2" plug valve on guage line leaks from valve A; MP 50.61; Greased valve
| 10-81406-1 | 300B | 50.61 | 0.75 | Transmission |  | Other |  | Greased button | Other | Lack of grease | 2010-10-26 |  |  |  | Steel/Wrought Iron |  | Needles | MP 50.61B 1/2" plug valve on guage line leaks from grease button on valve A
| 10-82065-1 | 300B | 60.95 | 12 | Transmission |  | Other |  | Unibolt Cap | Other | Loose cap | 2010-10-04 | 2010-10-20 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | Needles | Scanned to GT mapping 10/25/2010 DLLD; Unibolt Cap on blowdown stack; Removed unibolt cap, cleaned gasket surface, and tight seal on gasket and reinstalled unibolt cap, tested no leak
| 10-81394-1 | 300B | 76.3 | 0.5 | Transmission |  | Fitting |  |  | Weld Failure |  | 2010-10-01 | 2010-10-20 | Fill Weld - Weld |  | Steel/Wrought Iron |  | Needles-Topock District Pipeline | Cracked weld on gauge tap; repair was made at the bottom weld of the 1/2 90 degree elbow gauge line for the blow off valve
98 | 10-81398-1 | 300B | 81.84 | 12 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-10-01 | 2011-04-28 | Tighten Cap/Bolt - Fitting |  | Steel |  | Needles | Sent to Wendy 4-29-11 DLLD; Line 300B @ 81.84 MLV 81.84B; Gauge, BD; Tighten unibolt cap
| 10-81398-1 | 300B | 81.84 | [8 empty] | 2010-10-01 | [5 empty] | Mohave
| 10-81393-1 | 300B | 86.79 | 12 | Transmission |  | Other |  | Unibolt Cap | Other | Lose cap | 2010-09-30 | 2010-10-20 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | Needles | Unibolt cap; Removed unibolt cap, cleaned gasket surface, used tight seal on gasket and re-installed unibolt cap. Tested no leaks
| 10-81392-1 | 300B | 92.28 | 12 | Transmission |  | Other |  | Unibolt Cap | Other | Lose Cap | 2010-09-30 | 2010-10-21 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | Needles | Unibolt Cap; Removed unibolt cap. Cleaned gasket surface and applied tight seal to gasket. Reinstalled cap and tested no leaks
98 | 10-81391-1 | 300B | 97.85 | 12 | Transmission >= 20% SMYS |  | Fitting |  |  | Other | Gasket | 2010-09-30 | 2011-04-28 | Tighten Cap/Bolt - Fitting |  | Steel |  | Needles | Sent to Wendy 4-28-11 DLLD; Leak @ BD stack gauge line & unibolt cap leaking; guage, cap; Tighten unibolt cap
| 10-81391-1 | 300B | 97.85 | [8 empty] | 2010-09-30 | [6 empty] | MP 97.85B BD Valve; Guage line, unibolt cap
|  | 302 |  | 4.5 | [11 empty] | Steel |  | GRIMES | INSTALLED PROBES AND TIE-INS 4" STL. MAIN GRIMES ARCUCHLE RD.
|  | 302 |  | 4.5 | [11 empty] | Steel |  |  | REMOVE 3" VALVE & TIE IN L-302 TO POUND STEM 18-2
|  | 302 |  | 4.5 | [11 empty] | Steel |  |  | TIE-IN L-302 TO S SYCAMORE 11-T
|  | 302 |  | 4.5 | [11 empty] | Steel |  |  | TIE-IN 4" L-302 TO POUND STONE 13-1
|  | 302 |  | 3.5 | [11 empty] | Steel |  |  | TIE-IN 4" L-302 TO S. SYCAMORE #22
|  | 302 |  | 4.5 | [11 empty] | Steel |  |  | TIE-IN LINE 4" 302 TO S. SYCAMORE #14
|  | 302 |  | 6.625 | [11 empty] | Steel |  |  | TIE-IN 4" STL. MAIN TO S. SYCAMORE #19
|  |  |  | 4.5 | [11 empty] | Steel |  |  | TIE-IN 4" MAIN TO SYCAMORE #9-3
|  |  |  | 6.625 | [11 empty] | Steel |  | GRIMES | TIE-IN 4" STEEL MAIN TO 6" STEEL MAIN.
|  |  |  | 4 | [11 empty] | Steel |  |  | GM 1192392 SEE ATTACHED DRAWING
3
|  |  |  | 4.5 | [11 empty] | Other | ERW
|  |  |  | 6 | [11 empty] | Steel
|  | 220 |  | 10 | [11 empty] | Steel |  | DAVIS
|  | 220 |  | 10 | [11 empty] | Steel |  | DAVIS
|  | 150 |  | 6 | [11 empty] | Steel |  | DAVIS
|  | 150 |  | 6 | [11 empty] | Steel |  | DAVIS; | INSPECTION
|  | 150 |  | 6 | [11 empty] | Steel |  | DAVIS;
|  | 150 |  | 6 | [11 empty] | Steel |  | DAVIS
|  |  |  | 4 | [11 empty] | Steel |  | MARYSVILLE | NORTH TIE-IN
|  |  |  | 4 | [11 empty] | Steel |  | MARYSVILLE | SOUTH TIE-IN
|  |  |  | 3 | [11 empty] | Steel |  |  | TIE-IN ON MORRIS RD. GM 119266-5
|  |  |  | 6.25 | [11 empty] | Steel
|  |  |  | 4.5 | [8 empty] | 1995-08-02 |  |  | Steel |  |  | GRIMES/ARBUCKLE RD. NORTH OF LODI RED...200'. CUT AND CAPPED VALVE #474 FOR POUNDSTONE 13-1 ABANDONMENT
|  |  |  | 4 | [11 empty] | Steel |  |  | REMOVE 2 4" RISERS. ABANDON POUNDSTONE 18-1 GAS WELL
|  |  |  | 4 | [11 empty] | Steel |  |  | RE-ACTIVATED 4" STL. GAS LINE
|  |  |  | 6.625 | [11 empty] | Steel |  |  | STONY CR. 6" D.F.M. S. SIDE
|  |  |  | 6.625 | [11 empty] | Steel | ; |  | STONY CR. 6" D.F.M. N-SIDE
|  | 193 |  | 3.5 | [8 empty] | 1995-12-07 |  |  | Steel |  |  | CHRISTIAN RD. & MEYHEW RICE CREEK. DIG 3" LINE L-193. RECONNECT LINE.
|  |  |  | 3.5 | [8 empty] | 1995-11-07 |  |  | Steel |  |  | PAYNE RD. E/O S. DREYLER MOBIL 32-32-4 GAS WELL. CUT AND CAPPED TAP....GAS WELL.
|  |  |  | 3.5 | [8 empty] | 1995-11-15 |  |  | Steel |  |  | BUTTES CARROL GAS WELL #33-3. N/O PASS RD. iNSTALL INSULATING FITTING ON PRODUCERS SIDE.
|  | 302 |  | 3.5 | [8 empty] | 1995-11-15 |  |  | Steel |  |  | BUTTE CARROL GAS WELL #33-3. N/O PASS ROAD. TIE IN GAS WELL INTO L-302 217' E.O V-330
|  |  |  | 3.5 | [8 empty] | 1995-11-15 |  |  | Steel-Other |  |  | INSTALL INSULATING FITTING ON FRACTURED PIPE.
|  |  |  | 3.5 | [8 empty] | 1995-11-15 |  |  | Steel-Other |  |  | TIE-IN GAS WELL INTO L302
|  |  |  | 3.5 | [8 empty] | 1996-03-07 |  |  | Steel-Other |  |  | ABANDONED 585 GAS WELL CAPPED 3" TEE WITH CAP & SAV-A-VALVE.
|  |  |  | 4.5 | [8 empty] | 1996-03-22 |  |  | Steel-Other |  |  | CUT/CAP V-462 TO ABAN. SYCAMORE 13-1C GAS WELL.
|  |  |  | 35 | [8 empty] | 1996-12-03 |  |  | Steel-Other |  |  | ABAN. EAST WILLIAMS # 1 CLOSED VALVE #453 CUT OFF WELL REFLANGED VALVE.
|  |  |  | 6.625 | [11 empty] | Steel-Other |  |  | GM 1289040
|  |  |  | 4.5 | [8 empty] | 1996-02-22 |  |  | Steel-Other |  |  | ABANDON STONY ER #1 GAS WELL CUT AND CAP AT VALVE #16.
|  |  |  | 6.625 | [8 empty] | 1996-02-08 |  |  | Steel-Other |  |  | ABANDON BUTTE'S #62 GAS WELL.
|  |  |  | 3 | [11 empty] | Steel/Wrought Iron
|  |  |  | 3 | [11 empty] | Steel-Other
|  |  |  | 4 | [8 empty] | 1997-06-18 |  |  | Steel-Other |  |  | INSTALL 4" BLIND FLANGE ON V-179 TO ABAN. ARBUCKLE # 2 & #22 GAS WELLS.
|  | 302 |  | 4.5 | [8 empty] | 1996-05-23 |  |  | Steel-Other |  |  | TIE-IN NEW 4" TO EXISTING 4" L302.
|  | 302 |  | 6.25 | [8 empty] | 1996-05-23 | [5 empty] | TIE IN NEW 4" TO EXISTING 6" L-302.
|  | 302 |  | 4.5 | [8 empty] | 1996-05-23 |  |  | Steel-Other |  |  | TIE-IN NEW 4" TO EXISTING 4" L-302.
|  | 302 |  | 6.25 | [8 empty] | 1996-05-23 |  |  | Steel-Other |  |  | TIE-IN NEW 4" TO EXISTING 6" L-302.
|  |  |  | 3.5 | [11 empty] | Steel-Other
|  | 167 |  | 4.5 | [8 empty] | 1996-05-02 |  |  | Steel-Other |  |  | TIE-IN PRODUCERS LINE WITH INSULATING FLANGES.
|  |  |  | 6.25 | [8 empty] | 1996-05-02 |  |  | Steel-Other |  |  | TIE-IN PRODUCERS LINE WITH INSULATING FLANGES. uP STREAM FROM.
|  | 167 |  | 4.5 | [8 empty] | 1996-05-02 |  |  | Steel-Other |  |  | TIE-IN PRODUCERS LINE WITH INSULATING FLANGES.
[13 empty] | 1996-05-02 |  |  | Steel-Other |  |  | TIE-IN PRODUCERS LINE WITH INSULATING FLANGES UP STREAM FROM
|  |  |  | 4.5 | [11 empty] | Steel-Other
|  |  |  | 6 | [11 empty] | Steel-Other
|  |  |  | 16 | [8 empty] | 1996-08-22 |  |  | Steel-Other |  |  | CUT-CAP 16" TEE. ISOLATED FLANGE. a 129449
|  |  |  | 16 | [8 empty] | 1996-08-22 |  |  | Steel-Other |  |  | REMOVE CHECK VALVE FROM METER TUBE. INSTALL 11' OF 16" ABOVE GROUND. A129449.
|  |  |  | 10.75 | [8 empty] | 1996-06-13 |  |  | Steel-Other |  |  | REMOVE SEPARATOR CAP
|  |  |  | 6 | [11 empty] | Steel-Other |  |  | GM 4045126 DETAIL-2 STA 51+53
|  |  |  | 6 | [11 empty] | Steel-Other |  |  | GM 4045126 DETAIL-2 STA 51+53
|  | 302 |  | 8.625 | [11 empty] | Steel-Other |  |  | GM 4045126 DETAIL-1 STA 51+53
|  |  |  | 12 | [11 empty] | Steel-Other |  |  | GM 4045126 DETAIL-1 STA 51+53
|  |  |  | 4.5 | [11 empty] | Steel-Other |  |  | GM 4045126 DETAIL-3 STA P/L 0+00
|  |  |  | 4.5 | [11 empty] | Steel-Other |  |  | GM 4045126 DETAIL-3 STA 180+80
|  |  |  | 12 | [11 empty] | Steel-Other |  |  | GM 4045126 DETAIL-3- P/L 5+39
|  |  |  | 3.5 | [8 empty] | 1996-06-20 |  |  | Steel-Other |  |  | ABANDON DAVIS 1-13 CUT AND CAPPED 3" TAP VALVE.
|  |  |  | 4.5 | [11 empty] | Steel-Other
|  |  |  | 4.5 | [8 empty] | 1995-11-30 |  |  | Steel-Other |  |  | INSTALL CORROSOMETER.
|  |  |  | 4.5 | [11 empty] | Steel-Other
|  |  |  | 4.5 | [8 empty] | 1995-11-30 |  |  | Steel-Other |  |  | INSTALL CORROSOMETER.
|  |  |  | 3 | [11 empty] | Steel-Other
|  |  |  | 6.625 | [11 empty] | Steel-Other |  |  | INSTALLED 4" VALVE.
|  |  |  | 3 | [11 empty] | Steel-Other |  |  | GM 1369222
|  |  |  | 6.625 | [11 empty] | Steel-Other |  | YUBA CITY | P/L 50+43. GM 1369255 - RAILROAD AVE. W/S RAILROAD AVE 349', N/O RICKY DR. YUBA CITY.
|  |  |  | 6.625 | [11 empty] | Steel-Other | X-42 | YUBA CITY | P/L 0+00. GM 1369255 - RAILROAD AVE. W/S RAILROAD AVE 349', N/O RICKY DR. YUBA CITY.;
|  |  |  | 6.625 | [11 empty] | Steel-Other |  | YUBA CITY | P/L 50+43. GM 1369255 - RAILROAD AVE. W/S RAILROAD AVE 349', N/O RICKY DR. YUBA CITY.;
|  |  |  | 6.625 | [11 empty] | Steel-Other | X-42 |  | P/L 0+00. GM 1369255 - RAILROAD AVE. W/S RAILROAD AVE 349', N/O RICKY DR. YUBA CITY.;
|  |  |  | 3.5 | [11 empty] | Steel-Other |  |  | GM 1369230
|  |  |  | 4.5 | [11 empty] | Steel-Other |  |  | RECONNECT ARBUCKLE RD 67 GW. GM 1369370
|  |  |  | 4.5 | [11 empty] | Steel-Other |  |  | ABANDON ARBUCKLE RO#12
|  | 302 |  | 6.675 | [8 empty] | 1995-08-11 |  |  | Steel-Other |  |  | TIE-IN
|  |  |  | 4.5 | [8 empty] | 00/00/1995 |  |  | Steel-Other |  |  | TIE-IN VALVE 422. NEW L 302 4" .188
|  | 302 |  | 6.25 | [8 empty] | 1998-09-27 |  |  | Steel-Other |  |  | TIE-IN TUTTLE MASTER METER 4" L 302 V-481.
|  | 302 |  | 6.625 | [8 empty] | 1995-08-11 |  |  | Steel-Other |  |  | TIE-IN NORTH END OF NEW 4" L-302.
|  | 302 |  | 4.5 | [8 empty] | 1995-08-11 |  |  | Steel-Other |  |  | TIE-IN VALVE 422 NEW L 302 4" .188
|  | 302 |  | 6.25 | [8 empty] | 1998-09-27 |  |  | Steel-Other |  |  | TIE-IN TUTTLE MASTER METER 4" L-302 AT V-481.
|  |  |  | 3.5 | [11 empty] | Steel-Other |  |  | GM 1369404 " NORTH-TIE IN.
|  |  |  | 4 | [11 empty] | Steel-Other |  |  | GM 1370287 TIE-IN REID #4.
|  |  |  | 6.625 | [11 empty] | Steel-Other |  |  | GM 1370287. VICTOR RANCH 4&5 TIE-IN.
|  |  |  | 6.625 | [8 empty] | 1995-08-10 |  |  | Steel-Other |  |  | INSTALL 20' OFFSET FOR RETRACTING PROBE.
|  | 302 |  | 6 | [8 empty] | 1995-08-09 |  |  | Steel-Other
|  |  |  | 4.5 | [8 empty] | 1995-08-10 |  |  | Steel-Other |  |  | TIE-IN 20' OFFSET FOR RETRACTABLE PROBE.
|  |  |  | 3.5 | [11 empty] | Steel-Other |  |  | REPLACE 3" DFM STONY CREEK NORTH END
|  |  |  | 3.5 | [11 empty] | Steel-Other |  |  | REPLACE 3" DFM STONY CREEK SOUTH END
11 | 95-30220-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-06-27 | 1995-07-11 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | APPROX. 1/3 MILE WEST OF DRY SLOUGH ROAD & ON GRIMES - ARBUCKLE ROAD; INSERTED ROAD X-ING WITH 4" .237WT TEST PIPE 57'6" LONG
|  |  |  | 6.25 | [8 empty] | 1996-03-19 |  |  | Steel |  |  | OSWALD RD. E/O PROGRESS @ VALVE 299. ABAN TOSDALE 1-1 GAS WELL; CUT AND REMOVED 6 x 6 TEE. INSTALLED 30" OF TESTED .219 GM 4045100
|  |  |  | 3.5 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 3.5 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 3.5 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 2 | [11 empty] | Steel |  |  | 19' N/O LEPP# 1 GAS WELL
|  |  |  | 4 | [11 empty] | Steel |  | ORLAND; | 4' S/O TIE IN FOW POWTEW 27-1GAS WELL
4.5
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
11 | 94-30221-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-06-10 |  | Replace Pipe |  | Steel |  | SUTTER | BELOW RISER VALVE AT 14-1 WELL; INSTALLING NEW RISER AND 11' OF PRE TESTED 4" PIPE
|  |  |  | 20 | [11 empty] | Other | X-52 | GRIMES
|  |  |  | 20 | [11 empty] | Other | GR B DSA... | MERIDIAN
|  |  |  | 20 | [11 empty] | Other | X-52 | GRIMES
|  |  |  | 20 | [11 empty] | Other | GR B DSA... | MERIDIAN
| 94-30223-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-06-29 | 1994-07-01 | Replace Pipe |  | Steel |  |  | REPLACED 185' OF 6" .188 W/185' OF 6" .219 WALL PRETESTED PIPE (TESTED ON GM4045100 5-2-94)
11 | 94-30224-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-06-30 | 1994-07-12 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | .4 MILES EAST OF V-190 MORRIS ROAD; INSTALLED 2' OF 4" .188 WALL PRETESTED PIPE
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel |  |  | TIE-IN @ HANKINS #17-1
|  |  |  | 18 | [11 empty] | Steel
|  | 193 |  | 4 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
11 | 94-30225- | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-07-18 | 1994-07-20 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | FRANKLIN ROAD APPROX 100FT. E/O ATLANTIE #1MM. (IN REC. DIST. DITCH).; REPLACED 52' OF 6" WITH 51' OR 3" .279 WALL AND 1' OF 6" .219 WALL TO REPAIR LEAK
|  |  |  | 6.625 | [11 empty] | Steel
|  |  |  | 18 | [11 empty] | Steel
| 98-30217-0 |  |  | 12 | Gathering |  |  | Body of Pipe |  | Internal Corrosion |  | 1998-10-15 | 1999-03-23 | Welded Sleeve/Can - Weld | ABANDON | Steel |  | GRIMES | PIPE TO BE REPLACED DUE TO INTERNAL CORROSION (12" WILL BE REPLACED W/NEW 4"); REPLACED 540 FT OF 12" L-302 WITH 4" PIPE. S.O. # 6020523. NEW PIPE SECTION RETURNED TO SERVICE ON 04/15/99. C. BISH (CALIF. PROVIDERS PAID FOR REPLACEMENT)
11 | 93-302-2 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-01-10 | 1993-01-10 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | INSTALLED 34" OF 8" .188" WALL PRETESTED PIPE TO REPLACE LEAK.
11 | 93-30203- |  |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-01-21 | 1993-01-22 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPLACE 2' OF 4" PIPE. PRETESTED GM404458-2.
11 | 76-30215-1 | 302 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-10-05 | 1996-10-22 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPAIR 12" W/ 75" .312 WT TESTED ON GM 1287325
11 | 76-30215-1 | 302 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-10-05 | 1996-10-22 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPAIR 12" W/ 75" .312 WT TESTED ON GM 1287325
11 | 93-30219-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-09-09 |  | Replace Pipe |  | Steel/Wrought Iron |  | COLUSA | REPLACED 35" OF 8" TO REPAIR LEAK. REPLACED WITH 8" .219 PRE TESTED PIPE. API SL X 42 ERW,
11 | 93-302-9 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-02-25 | 1993-02-25 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | INSTALLED 47" OF 6" .188
11 | 97-30201-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-02-19 | 1997-03-11 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | EXPOSED PIPE ON 3/11/97, CUT 6 FT SECTION OUT AND DETERMINED THAT PIPE IS UNREPAIRABLE DUE TO PITTING. DISCUSSIONS STARTED WITH PRODUCER TO PURCHASE & REPLACE 1,730 FT.
11 | 97-30202-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-02-24 | 1997-03-20 | Replace Pipe |  | Steel/Wrought Iron |  | S/O MERIDIAN | CUT 6X6X4 FROM LINE TO ABANDON 1-1 REPLACED WITH 40" PRETESTED 6"/.188 WT. GM 1450279.
11 | 97-30203-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-03-26 | 1997-03-27 | Replace Pipe |  | Steel/Wrought Iron |  | COLUSA | REPLACED WITH 26" .219 WT PRETESTED PIPE.
| 97-30204-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-04-15 | 1997-10-03 | Other |  | Steel/Wrought Iron |  | S/O SUTTER | CLOSED V-224 & SCHEDULED FOR RETIRMENT. C. BISH. RETIRED THIS SECTION OF PIPE ON S.O. # 7005071.
| 97-30205-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-04-23 | 1997-04-23 | Replace Pipe |  | Steel/Wrought Iron |  | S/O MERIDIAN | REPAIRS REQUIRE 40 + FT OF DITCH CROSSING WITH SINGLE TRANSPORT WELL. PG&e WIL NOT REPAIR AND DISCUSSIONS STARTED WITH PRODUCER OF NF12-1.
| 97-30206-1 | 302 |  | 8.625 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-06-21 | 1997-06-21 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | GRIMES | CUT OFF MAIN, INSTALL 8" CAP AT VALVES
| 97-30207-1 | 302 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-07-23 | 1997-07-31 | Other |  | Steel/Wrought Iron |  | GRIMES | DID NOT REPAIR DUE TO RE-ROUTE PROJECT IN PROGRESS. THIS SECTION OF PIPE WAS REMOVED FROM SERVICE ON 7-31-97 #7003683.
| 97-30208-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 1997-07-29 | 1997-08-07 | Patch Welded |  | Steel/Wrought Iron |  | GRIMES | REPAIRED PIN HOLE IN 3/4" SOCKET WELL SOAP TEST @100 BACK FELL.
| 97-30210-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-07-29 | 1997-08-11 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPAIR LEAK WITH 22" 6" .219WT PRETESTED PIPE #7001015
| 97-30211-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-09-23 | 1997-10-07 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | INSTALL 2' OF 219 WT PIPE PRETESTED
| 97-30212-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-09-23 | 1997-10-07 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | INSTALLED 2' .219 WT PIPE PRETESTED
| 97-30213-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-09-23 | 1997-10-08 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | INSTALLED 3" PLUG VALVE & BLIND FLANGE. INSTALLED 4" CAP ON 4" LINE TO ISOLATE LEAK. PRETESTED.
| 98-16701-1 | 167 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-01-06 | 1998-01-21 | Replace Pipe |  | Steel/Wrought Iron |  | WATSON | REPAIRED LEAK WITH 36" .... PRETESTED PIPE
| 98-30201-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-01-05 | 1998-06-10 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | PIPE UNREPAIRABLE - WILL RETIRE SEVERE TROUGHING! CUT OUT LEAK. REPLACED WITH 30" PRETESTED PIPE. DUE TO HEAVY TROUGHING LINE WAS ABANDON; NEW PIPE 4" = 5100 FT 1/22/99; INSTALLED 5,100FT OF 4" PIPE AT PRODUCERS EXPENSE. SO. #7018725
| 98-30202-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-01-05 | 1998-06-10 | Other |  | Steel/Wrought Iron |  | GRIMES | PIPE UNREPAIRABLE - WILL RETIRE SEVERE TROUGHING! NOTHING DONE AT THIS LOCATION DUE TO LINE ABANDON. NEW 4" PIPE = 5,100FT; INSTALLED 5,100FT. OF 4" PIPE AT PRODUCERS EXPENSE. S.O. #7018725
| 98-30203-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-01-05 | 1998-06-10 | Other |  | Steel/Wrought Iron |  | GRIMES | PIPE UNREPAIRABLE - WILL RETIRE. SEVERE TROUGHING! LEAK WAS DETECTED 50' S/O LINE 6-302 GOING TO ___ GAS WELL. DID NOT REPAIR DUE TO ABANDON; NEW 4" PIPE = 5100FT
| 98-30204-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-02-03 | 1998-03-04 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPAIR LEAK E/OV173 WITH 32" .188 4" PRETESTED PIPE SO#7007086
| 98-30205-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-02-23 | 1998-04-16 | Replace Pipe |  | Steel/Wrought Iron |  | S/E MERIDIAN | REPAIR LEAK W/ 30" PRETESTED .188 X42 6" PIPE
| 98-30206-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-02-24 | 1998-06-03 | Replace Pipe |  |  |  | GRIMES | REPLACED TWO 30" PIECES ON THE NORTH END OF PIPE ISOLATED. FOUND 150 FEET OF UNREPAIRABLE PIPE ON SOUTH END. THIS SECTION OF PIPE WILL BE RETIRED. REMAINS O/S. PENDING RETIREMENT
| 98-30207-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-03-19 | 1998-03-19 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPLACED WITH 32" PIECE OF .219 TESTED PIPE.
| 98-30210-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-04-16 | 1998-04-16 | Replace Pipe |  | Steel/Wrought Iron |  | S/E OF MERIDIAN | REPAIR LEAK WITH 42' .188 WT PRETESTED PIPE
| 98-30209- | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-04-16 | 1998-04-16 | Replace Pipe |  | Steel/Wrought Iron |  | S/E OF MERIDIAN | REPAIR LEAK WITH 42" .188 WT PRETESTED PIPE
| 98-30208-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-04-16 | 1998-04-16 | Replace Pipe |  | Steel/Wrought Iron |  | S/E OF MERIDIAN | REPAIR LEAK WITH 42" .188 WT PRETESTED PIPE
| 98-30208-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-03-19 | 1998-03-20 | Replace Pipe | ; ; | Steel/Wrought Iron |  | MERIDIAN | REPLACED WITH 24" PIECE OF .219 TESTED PIPE
| 98-30209-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-03-19 | 1998-03-20 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPLACED WITH 50" PIECE OF .219 TESTED.
| 98-30216-1 | 302 |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-03-19 |  |  |  | Steel/Wrought Iron |  | GRIMES | REMAINS O/S 12/31/98. REMAINS O/S 44/1/99
| 98-1691-1 | 169 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-05-07 | 1998-06-04 | Replace Pipe |  | Steel/Wrought Iron |  | WILLOWS | PRODUCER DECIDED TO RUN THEIR OWN PIPE AROUND THIS LEAK SECTION. THEREFORE, THIS WAS NOT REPAIRED. REQUESTED RETIREMENT JOB FOR THIS PIPE. REMAINS O/S 12/31/98. REMAINS O/S 4/1/99
| 98-30211-1 | 302 |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-05-05 |  | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REMAINS O/S 12/31/98. REMAINS O/S 4/4/99
| 98-2091-1 | 209 |  | 4 | Transmission |  | Valves |  |  | Other |  | 1998-05-11 | 1998-05-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | WILLOWS | FOUND A SLIGHT LEAK ON THE MUELLER TEE CAP. TIGHTENED BRASS PLUG/VALVE, DOPED CAP AND TIGHTENED. (SENSING TAP FOR LAST GAUGE PRESSURE)
| 98-16902-1 | 169 |  | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-06-07 | 1998-06-18 | Replace Pipe |  | Steel/Wrought Iron |  | WILLOWS | REPAIRED LEAK 163" TESTED PIPE X65 .312 WT
| 98-169-3-1 | 169 |  | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-11-06 | 1998-11-06 | Replace Pipe |  | Steel/Wrought Iron |  | WILLOWS | INSTALL 4' PIECE TO REPAIR LEAK
| 98-30213-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-06-25 | 1998-09-23 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPLACED 28" OF PIPE WITH PRETESTED PIPE GM 10277620
| 98-30212-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-06-25 | 1998-09-23 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPLACED 5'3" OF PIPE WITH PRETESTED PIPE GM 10277620
| 98-30215-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-11-03 | 1998-11-10 | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER | REPAIR LEAK WITH 3'6" PIPE
| 98-1673-1 | 167/302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-10-27 | 1998-11-12 | Other |  | Steel/Wrought Iron |  | COMPTON LANDING | CUT AND CAPPED AT TAP LOCATION TO CARTER #4 AND RETIRED LEAK SECTION.
| 98-30214-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-06-25 | 1998-11-17 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPAIR 8" LEAK WITH 30" PIECE OF TESTED PIPE
| 98-30214-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-09-18 | 1998-12-14 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPAIR LEAK ON 4" MAIN. REPLACE 2" SECTION WITH TESTED .237 4"
| 98-30217-0 | 302 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-10-05 | 1999-03-23 | Welded Sleeve/Can - Weld | ABANDON | Steel/Wrought Iron |  | GRIMES | APPROX. 50FT W/O DRY SLOUGH RD. OUT IN DIRT FIELD. (BETWEEN #1793 & 1449 ADDRESS); PIPE TO BE REPLACED DUE TO INTERNAL CORROSION (12" WILL BE REPLACED W/ NEW 4"); REPLACED 540 FT. OF 12" L-302 WITH 4" PIPE. S.O.#6020523. NEW PIPE SECTION RETURNED TO SERVICE ON 4/15/99 (CALIF. PRODUCERS PAID FOR REPLACEMENT); REPLACED LEAKY PIECE FOR PIGGING ONLY! USE 36" X-42 PRETESTED PIPE. 12" L-302 NOT REPAIRED.
| 99-30200-7 | 302 |  | 8 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-08-19 | 1999-08-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | S/E OF MERIDIAN | FOUND WHILE MAKING ONE FINAL CHECK BEFORE SHUTDOWN ON 8/22/99; REPAIRED WITH 23 7/8 .188 WT X42 PRETESTED PIPE ON GM #496497-9
| 99-30200-4 | 302 |  | 8 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-05-11 | 1999-08-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | S/O MERIDIAN | 1/16' PIN HOLE AT 6 O'CLOCK BATH; REPAIRED WITH 32" PRETESTED PIPE .188X42 GM#496497-9
| 99-30200-6 |  |  | 4 | Gathering |  | Fitting |  |  | Other | SAV-A-VALVE | 1999-07-26 | 1999-10-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | GRIMES | 3FT. EAST OF V-337 ON GRIMES0ARBUCKLE RD.; 2" SAV-A-VALVE LEAKING. REDOPED AND TIGHTEN; TIGHTENED SAV-A-VALVE STEM & CAP.
| 99-167-2 | 167 |  | 12 | Transmission |  | Body of Pipe | Other | DIG-IN PIPE SEVERED | Damage by 3rd Party | DIG-IN | 1999-11-11 | 1999-11-12 | Other | INST. 44' PIPE | Steel/Wrought Iron |  | S/E PRINCETON | REPLACED BAD PIPE. 44' .281WT X 42 12" PIPE
| 99-30200-9 | 302 |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Internal Corrosion |  | 1999-11-13 | 1999-11-18 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | COLLEGE CITY | SITE IN FIELD; RE[AORED WOTJ 94 7/8" PRETESTED 160 -.375WT PIPE; HYP STINGER/HOT PASS - LOW HI FILLER - CAP
| 99-169- |  |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-11-26 | 1999-11-27 | Other | 6' 8 1/4" TESTED PIPE | Steel/Wrought Iron |  | GLENN | FIRE IN FIELD; REPLACE 6' 8 1/4" .250 W/T PIPE; INTERMITENT PITTING OBSERVED IN PIECE REMOVED AT 6O'CLOCK BOTTOM
| 99-16900-3 | 169 | 1,770 FT S/O V-105 | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-12-07 | 1999-12-16 | Other | INST. 75' | Steel/Wrought Iron |  | GLENN | 50FT S/O PREVIOUSLEAK; INSTALLED 75' NEW .281 WT FROM PREVIOUS; RETURNED TO 100 PSIG (MAX) SERVICE WHILE WAITING FOR RETIREMENT. (PRODUCTION WILL HAVE A NEW CONNECTION POINT)
| 99-30201-0 | 302 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-12-08 | 2000-04-20 | Other | CUT & CAP | Steel/Wrought Iron |  | GRIMES | EDGE OF RICE FIELD AND IRRIGATION DITCH; CUT & CAPPED 20'X12' TEE WITH 12" CAP & SAV-A-VALVE; ENTERED 12" WITH NITROGEN TO BE RETIRES
| 99-16700-3 | 167 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-12-23 | 2000-05-31 | ABANDON | RETIRED | Steel/Wrought Iron |  | N/O PRINCETON | BUBBLES IN FLOODED RICE FIELD; RETIRED ALL PIPING AND PRODUCER RAN PIPE OVER TO A DIFFERENT TAP VALVE.
| 99-30200-3 | 302 |  | 8 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-05-11 | 1999-08-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | S/O MERIDIAN | REPAIRED WITH 25" .188WT X42 PRETESTED PIPE ON GM #496497-9
| 99-30202-0 |  |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Internal Corrosion |  | 1999-04-26 | 1999-04-30 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | GRIMES | BUBBLES IN FLOODED RICE FIELD; REPAIRED WITH 6' OF 20" .375WT STPR #A-1321
| 99-16900-1 | 169 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-05-10 | 1999-06-23 | Other | 9' OF PIPE | Steel/Wrought Iron |  | GLENN | BUBBLES IN FLOODED RICE FIELD. BUBBLES SAME IN FLOODED FIELD.; REPLACE 9' IF .250WT PRETESTED PIPE SER# A-0020-01 FOUND PIN HOLE AT BOTTOM; FOUND PIN HOLE AT 6 O'CLOCK BOTTOM
| 99-30200-5 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-06-07 | 1999-07-20 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | GRIMES | BUBBLES IN FLOODED RICE FIELD. ISOLATED AND BLOWN DOWN.; REPLACE LEAK WITH 40" OF PRETESTED PIPE; SUCTION LINE ONLY COULD GET 80# FROM WELL.
| 99-19301-1 | 177 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-01-05 | 1999-09-30 |  |  | Steel/Wrought Iron |  | KIRKWOOD | 6" L-193 PARALLEL TO 10" L-177 GATHERING LINE IN RICE CREEK FIELD BETWEEN VALVES #13 & #15.; ISOLATED AND BLOWN DOWN. AWAITING SEASONAL STREAM TO BECOME DRY AND AWAITING PRODUCER PAYMENT FOR REPAIRS. TO BE RETIRED. RETIRED AND SOLD THIS PIPELINE TO PIONEER EXPLORATION COMPANY. THIS WAS NEVER RETURNED TO SERVICE. WELDED 5' OF TESTED PIPE TO REPAIR LEAK. PIPELINE NOT TO BE ACTIVE. NO X-RAY - NO NOT COMP TEST LINE TO BE RETEST LATER. PIPELINE WILL BE RETIRED. ENGINEERING PREPARING A FORMAL JOB FOR RETIREMENT.
| 99-30201-2 |  |  | 20 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-12-08 | 2000-09-13 |  |  | Steel/Wrought Iron |  | S/O GRIMES | PIPELINE TAKEN O/S AND BLOWN DOWN ON 6-15-00 FOR PIGGING PROJECT. REPAIR MADE DURING OUTAGE. REPLACED 56 1/4" CAN WITH PRE-TESTED PIPE; 100PSI SOAP TEST
Steel-Other
| 99-30200-8 | 302E |  | 6 | Gathering | [6 empty] | 1999-11-05 | 2000-10-27 | Other | REPLACED CROSSING | Steel/Wrought Iron |  | SE/O MERIDIAN | SUTTER BYPASS-EAST SLOUGH 20 LINEAR FEET OF BUBBLES UNDER WATER. REDUCED TO 50 PSIG UNTIL PERMITS AND REPLACEMENT JOB IS SCHEDULED.; NEW BORE E/S SUTTER BYPASS & SLURRY POUR RETIREMEMNT OF ORIGINAL PIPE. SO #7030786
| 00-30201-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2000-01-18 | 2000-03-03 | Other | 2' PIPE | Steel/Wrought Iron |  | S/O SUTTER | SMALL BUBBLES IN FLOODED RICE FIELD; REPLACED WITH 2' OF .188 WT PRETESTED PIPE JOB #7029948
| 00-30202-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | External Corrosion | INTERNAL CORROSION | 2000-02-29 | 2000-05-18 | Other | 7' PIPE |  |  | COLUSA | BUBBLES IN FLOODED FILED. REPAIR LEAK WITH 7' .188WT PRETESTED PIPE #7007086
| 00-30203-1 | 302 |  | 4 | Other |  | Body of Pipe |  |  | Digin |  | 2000-05-24 | 2000-05-25 | Other |  |  |  | SUTTER | EXCAVATOR HIT PIPE WHILE REPLACING CULVERT. DOCUMENTED FOR 2000 EMERG. RESPONSE.; INSTALL 63' NEW DOGLEG WITH 6' EACH OVER BENDS.
| 00-17401-1 | 174 |  | 10 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2000-06-30 | 2000-08-01 |  | WELD CAP |  |  | ARBUCKLE | SUSPECT INTERNAL CORROSION IN ORCHARD AREA; WELD CAP WITH SAV-A-VALVE TO ACA.. 4' STUB WITH OLD TAP VALVE
| 00-16701-1 | 169 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2000-02-25 | 2000-08-03 | Weld Over Sleeve or Can |  |  |  | PRINCETON | BUBBLES IN FLOODED WALNUT ORCHARD AT THREE LOCATIONS AFTER REPAIRS TO THIS REPORT; INSTALLED 36" PRETESTED 12" .281 PIPE WITH SAV-A-VALVE; REDUCED AND KEPT PIPELINE PRESSURE AT 100 PSIG STARTING ON 2/28/00.
| 00-30205-1 |  |  | 20 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2000-08-16 | 2000-08-17 | Weld Over Sleeve or Can |  |  |  | S/O GRIMES | FOUND DURING POST SMART PIG DATA. (PRESSURE PIPE AND LEAK CHECK DURING L-302E OUTAGE); REPLACED WITH 88 3/4' PRETESTED PIPE (1/8" PIN HOLE)
| 00-30207-1 | 302E |  | 20 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2000-09-21 | 2000-10-05 | Weld Over Sleeve or Can |  |  |  | GRIMES | FOUND DURING POST SMART PIG DATA. (PRESSURE PIPE AND LEAK CHECK DURING L-302E OUTAGE); INSTALLED A 40' PIECE OF PRETESTED PIPE WITH SLEEVE.
| 00-30204-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2000-05-26 | 2000-12-07 | Weld Over Sleeve or Can |  |  |  | GRIMES | BUBBLES NEXT TO CORN FIELD**; REPLACED 4FT OF TESTED PIPE THIS WAS O/S UNTIL 12/26/00 WHEN 20" L-302E WAS RETURNED TO SERVICE.; **PIPELINE ISOLATED AND BLOWN DOWN SAME DAY - AWAITING REPAIRS - GAS PRODUCER TO PAY FOR REPAIR
| 00-16901-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2000-05-04 | 2001-02-01 | Other | RETIRED |  |  | WILLOWS | BUBBLES IN FLOODED RICE FIELD** ISOLATED AND BLOWN DOWN 5/4/00; RETIRED THIS SECTION OF PIPING SO#6047783 ON 2/1/01; PIPELINE TO BE RETIRED ON SO 6047783, CLEARANCE ME -00-32 - PIPELINE ISOLATED AND BLOWN DOWN
| 00-16703-1 | 167 |  | 12 | Gathering | CONV. TO DISTRIBUTION | Body of Pipe |  |  | Internal Corrosion |  | 2000-08-08 | 2001-02-28 | Other | REPLACE |  |  | PRINCETON | SECTION OF LINE AT 100 PSIG. AWAITING PERMANENT REG. INSTALLATION & REPAIRS. (ALL GATHERING REMOVED) COULD NOT DETECT LEAK AT REDUCED PRESSURE.; NONE REPLACED WITH TESTED PIPE ON 12-15-99; THIS SECTION OF LINE CONVERTED TO DISTRIBUTION. SO #6033943 5/9/01
| 01-30214-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-10-22 | 2001-11-28 | Other | REPLACED PIPE AROUND WELL PAD |  |  | GRIMES | LEAK FOUND BY FARMER BURNING FIELD. * ISOLATED LINE - V/SO CLOSED - BLOCK VALVE CLOSED * TURNED IW BY GAS PRODUCER; REPLACED PIPE AROUND PRODUCERS WELL PAD.
| 01-16701-1 | 167 |  | 4 | Gathering |  | Body of Pipe | Tap Connection |  | Digin |  | 2001-10-25 | 2001-10-25 | Mechanical Repair Fitting - Fitting |  |  |  | COLUSA | GC GAS STUCK A SERVICE TEE WHILE EXCAVATING LINE: HAS BEEN DOWN GRADED TO DISTRIBUTION ON 10-16-2001 *(58PSI) 4"X1"; THREADED PIPE AND INSTALLED NEW VALVE.; INCIDENT REPORT 20001 #0116600 10/25/01
| 01-30212-1 |  |  | 3 | Gathering |  | Other Welds |  |  |  |  | 2001-10-09 | 2001-10-09 | Other |  |  |  | S/O MERIDIAN | CREW FOUND 6X6X3 TEE LEAKING AT 3" WELD (BOTTOM) * REPAIRS TO BE DONE ON 10-12-01; * STEVE WATERS TO CONFIRM AS BUILT DRAWINGS FOR THICKNESS + GRADE GROUND OUT BOTTOM AND REWELDED; LEAK ON WELD, GROUND OUT BOTTOM AND REWELDED X-RAY & MAG TEST
| 01-30204-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-03 | 2001-08-27 | Mechanical Repair Fitting - Fitting |  |  |  | S/E MERIDIAN | INSTALL LEAK CLAMP (PLEDICO CLAMP); INSTALL LEAK CLAMP SOAP @ 200PSI * X-RAY SHOWS LIGHT TO MED. PITTING *
| 01-30205-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-03 | 2001-08-27 | Mechanical Repair Fitting - Fitting |  |  |  | S/E MERIDIAN | INSTALL LEAK CLAMP (PLEDICO CLAMP); INSTALL LEAK CLAMP SOAP @ 200 PSI * X-RAY SHOWED HEAVY PITTING*
| 01-30206-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-03 | 2001-08-28 | Mechanical Repair Fitting - Fitting |  |  |  | S/E MERIDIAN | INSTALL LEAK CLAMP (PLEDICO CLAMP); 1/16' PIN HOLE AT 6 O'CLOCK BATCH; INSTALL LEAK CLAMP SOAP @ 200 PSI *X-RAY SHOWS LIGHT PITTING*
| 01-30202-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-03-12 | 2001-08-30 | Other | NEW BORE |  |  | S/O SUTTER | LARGE BUBBLES IN WATER AND MUD ON DITCH BANK. (ISOLATED & BLOWN DOWN); REPLACED LIVE OAK CANAL CROSSING WITH A NEW BORE.; INSTALL NEW BORE PIPE
| 01-30210-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-06-06 | 2001-08-27 | Weld Over Sleeve or Can |  |  |  | 8 MI. S/E/ OF MERIDIAN | BUBBLES IN IRRIGATED CORN FIELD. ISOLATED AND BLOWN DOWN. AWAITING PAYMENT FOR REPAIRS.; CUT OUT AND REPLACED WITH TESTED PIPE. SO #8047916; LEAK REPAIR
| 00-30206-1 | 302 | 12.03 | 24 | Gathering |  | Drip |  |  | Internal Corrosion |  | 2000-08-25 | 2001-07-24 | ABANDON | RETIRED |  |  | S/O MERIDIAN | BYPASSED DRIP BY WELDING 16"X6" REDUCTION TO SCRUBBER INLET.; S.O. #8040859
| 01-30203-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-07 | 2001-06-15 | Weld Over Sleeve or Can |  |  |  | S/O GRIMES | BUBBLES IN FLOODED RICE FIELD. PRODUCER SHUT-IN PRODUCTION TO ISOLATE LEAK AREA. 20 PSIG SUCTION SYSTEM U.S. OF ANDREOTTI #11 M.M.; INSTALLED 9' CAN
| 01-30201-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-03-09 | 2001-03-21 | Other | REPLACED |  |  | GRIMES | * BUBBLES IN FIELD CLOSED VALVES TO ISOLATE - PIPING BLOWN DOWN; INSTALLED NEW 3" PIPE FROM TAP VALVE TO RISER BLOCK VALVE. (PROCUREMENT) SO# 6077243
| 01-30207-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-08-20 | [5 empty] | S/E MERIDIAN | ISOLATED & BLOWN DOWN. AWAITING TRI-UNION TO COMMIT FOR PAYMENT BEFORE SCHEDULING REPAIRS.; 12/31/01 NO PAYMENT FROM PRODUCER. PIPING STILL BLOWN DOWN. 4/18/02 STILL WAITING FOR PRODUCER PAYMENT.
| 01-30211-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion | [7 empty] | S/O GRIMES | BUBBLES IN FLOODED FIELD 3-6 FT W/O V-399; WILL PLACE ON RETIREMENT LIST.; 12/31/01 AWAITING TO BE RETIRED. PIPING BLOWN DOWN. 4/18/02 STILL WAITING FOR RETIREMENT.
|  |  |  | 8 | [11 empty] | Steel
|  |  |  | 8 | [11 empty] | Steel |  |  | GM4044616
|  |  |  | 6.625 | [11 empty] | Steel |  |  | GM4044632
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel |  |  | TIE IN POINT 20' N/O N. EDGE CANAL JOB# 60013780- TESTED
|  |  |  | 6.625 | [11 empty] | Steel |  |  | GM4045092-DETAIL A P/L0+00
|  |  |  | 12.75 | [11 empty] | Steel |  |  | GM 4045092- DETAIL B-P/L 29+89
|  |  |  | 6.625 | [11 empty] | Steel |  |  | GM4045092- DETAIL E-SHT. 2 OF 2
|  |  |  | 6.625 | [11 empty] | Steel |  |  | GM4045092 DETAIL F-SHEET 2 OF 2
|  |  |  | 6.625 | [11 empty] | Steel |  |  | GM 4045092- DETAIL A P/L 0+00
|  |  |  | 12.7 | [11 empty] | Steel |  |  | GM 4045092- DETAIL B-P/L 29+89
|  |  |  | 6.625 | [11 empty] | Steel |  |  | GM 4045092 DETAIL E SHT 2 OF 2
|  |  |  | 6.625 | [11 empty] | Steel |  |  | GM 4045092 DETAIL F-SHEET 2 OF 2
|  |  |  | 4.5 | [11 empty] | Steel |  | GRIMES | TIE ON NORTH SIDE OF GRIMES ARBUCKLE RD.
|  |  |  | 6.625 | [11 empty] | Steel |  |  | TIE AT DETAIL A (6")
|  |  |  | 3.5 | [11 empty] | Steel |  |  | TIE @ DETAIL B (3")
|  |  |  | 6.625 | [11 empty] | Steel |  |  | CUT OFF @DETAIL C (6")
|  |  |  | 4 | [11 empty] | Steel |  |  | GM 4045191 DETAIL A
|  | 174 |  | 3 | [11 empty] | Steel |  |  | STRAIN RANCH
|  |  |  | 6 | [11 empty] | Steel |  |  | FM 404524 SHT. 2 OF 3 DETAIL "A"
|  |  |  | 3 | [11 empty] | Steel |  |  | GM 404524 SHT 2 OF 3 DETAIL B
|  |  |  | 3 | [11 empty] | Steel |  |  | GM404524 SHT 2 OF 3 DETAIL C
|  |  |  | 3 | [11 empty] | Steel |  |  | GM 404524 SHT 3 OF 3 DETAIL "E"
|  |  |  | 3 | [11 empty] | Steel |  |  | GM 404524 SHT 3OF 3 DETAIL "D"
|  |  |  | 8 | [11 empty] | Steel |  |  | GM 404524 SHT 3 OF 3 LOC "E"
|  |  |  | 4 | [11 empty] | Steel |  |  | TIE IN POINT EAST OF HWY 99
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel |  |  | GM 4131033 DETAIL A
|  |  |  | 4 | [11 empty] | Steel |  |  | GM 4131033 DETAIL B
|  |  |  | 4 | [11 empty] | Steel |  |  | GM 4131033 DETAIL C
|  |  |  | 4 | [11 empty] | Steel |  |  | GM 4131033 F.S. 67 & 70
|  |  |  | 6.625 | [11 empty] | Steel |  |  | GM 4131058
|  |  |  | 4.5 | [11 empty] | Steel |  |  | GM 4131066-SEE TIE IN DETAIL
|  |  |  | 4 | [11 empty] | Steel |  |  | GM 4131074- CONNECT NOSECO #1 GAS WELL
|  |  |  | 3 | [11 empty] | Steel |  |  | VICTOR RANCH #12 GM 416871-2
|  |  |  | 4.5 | [11 empty] | Steel |  |  | GM 4168829 (NORTH TIE-IN)
|  |  |  | 4.5 | [11 empty] | Steel |  |  | GM 4168829 (SOUTH TIE-IN)
|  |  |  | 4.5 | [11 empty] | Steel |  |  | GM 4168829 (COLUSA 3-1 & 3-2 TIE)
|  |  |  | 4.5 | [11 empty] | Steel |  |  | GM 4168837 NORTH TIE-IN
|  |  |  | 4.5 | [11 empty] | Steel |  |  | GM 4168837 SOUTH TIE-IN
|  | 302 |  | 4.5 | [11 empty] | Steel |  |  | SOUTH TIE IN 4" L-302
|  | 302 |  | 4 | [11 empty] | Steel |  |  | CUT ODD 4" L-302 S/O HUTTON 2
|  | 302 |  | 8 | [11 empty] | Steel |  |  | 8" LINE 302 CUT OFF
|  |  |  | 8.625 | [11 empty] | Steel |  |  | GM 4168977 TIE-IN VALVE #46 EAST END
|  |  |  | 10 | [10 empty] | ; | Steel |  |  | GM 4168977 WEST TIE IN
|  |  |  | 8.625 | [11 empty] | Steel |  |  | GM 4168977 TIE-IN VALVE #46 EAST END
|  |  |  | 10 | [11 empty] | Steel |  |  | GM 4168977 WEST TIE-IN
|  |  |  | 4.5 | [11 empty] | Steel |  | ORLAND | GM 4169267 CO. RD. H + 15 ORLAND DETAIL "A"
|  |  |  | 4.5 | [11 empty] | Steel |  |  | GM 4169264 DETAIL B. CO. RD. 12 & CO RD. E.
|  |  |  | 8 | [11 empty] | Steel-Other |  |  | GM 4908141
|  |  |  | 4 | [11 empty] | Steel-Other |  |  | GM 4854907
|  |  |  | 8 | [11 empty] | Steel-Other |  | COLUSA
|  |  |  | 8 | [11 empty] | Steel-Other |  | COLUSA
|  |  |  | 8 | [11 empty] | Steel-Other |  | COLUSA
|  |  |  | 8 | [11 empty] | Steel-Other
|  |  |  | 8 | [11 empty] | Steel-Other |  | COLUSA
|  |  |  | 8 | [11 empty] | Steel-Other |  | COLUSA
|  |  |  | 8 | [11 empty] | Steel-Other |  |  | GM 4854923
|  |  |  | 8 | [11 empty] | Steel-Other |  |  | GM 4854931. FS24445
|  |  |  | 8 | [11 empty] | Steel-Other |  |  | GM 485493-1. FS 5+18
|  |  |  | 8 | [11 empty] | Steel-Other |  |  | GM 485493-1. FS 5+72
|  |  |  | 8 | [11 empty] | Steel-Other |  |  | GM 4854931. HOLE AT 5TH 0+13
|  |  |  | 8 | [11 empty] | Steel-Other |  |  | GM 4854931. HOLE AT STA 33+27
|  |  |  | 8 | [11 empty] | Steel-Other |  |  | GM 4854964. SOUTH END F.S. 0+88
|  |  |  | 8 | [11 empty] | Steel-Other |  |  | GM 4854964. NORTH END F.S. 10+26
|  |  |  | 8 | [11 empty] | Steel-Other |  |  | GM 4854964. NORTH END F.S. 0+13
|  |  |  | 8 | [11 empty] | Steel-Other |  |  | P/L 63+92 / F.S. 37+49 - SOTUH TIE-14
|  |  |  | 6.625 | [11 empty] | Steel-Other | X-42 ERW |  | GM 4876736. P/L 0+00 / F.S. 22+20 - NORTH TIE-121
|  |  |  | 6 | [11 empty] | Steel-Other | X-42 ERW |  | GM 4908028 - CON RAMOS 3-1 GAS WELL.
|  |  |  | 6 | [11 empty] | Steel-Other |  |  | GM 4908042
|  |  |  | 6 | [11 empty] | Steel-Other |  | WOODLAND
|  |  |  | 8 | [11 empty] | Steel-Other |  |  | TIE-IN AT VALVE PIT.
|  |  |  | 8 | [11 empty] | Steel-Other |  |  | TIE-IN W/O AIRPORT STRIP S/O HWY 162
|  |  |  | 4.5 | [11 empty] | Steel-Other |  |  | GM 4876645
|  |  |  | 8.625 | [11 empty] | Steel-Other |  |  | GM 4876645
|  | 302 |  | 8 | [11 empty] | Steel-Other |  |  | TIE-IN LOCATION - 12' S/O VALVE 145. GM 4876652
|  |  |  | 4 | [11 empty] | Steel |  |  | 612' W/O RISON LOCATION DAHISLTROM 19-1 GAS WELL GM4876694
|  | 302 |  | 10 | [11 empty] | Steel |  |  | TIE-IN AT 10" LINE 302 GM4876694
|  |  |  | 4.5 | [11 empty] | Steel |  |  | G.O.U. 32-33-6 GAS WELL HAGEMAN RD. GM 4876702
|  |  |  | 6 | [11 empty] | Steel |  |  | GM 4876728 ARMSTRONG 1-12-9 GAS WELL
|  |  |  | 6 | [11 empty] | Other | X-42 |  | GRIMES 14-7 GM490806-7
|  |  |  | 8 | [11 empty] | Steel |  |  | GM 4908083
|  |  |  | 12 | [11 empty] | Steel |  |  | TIE-IN TO 12.00 OUT IN FIELD. MORONI RD. GM490817
|  |  |  | 16 | [11 empty] | Steel |  |  | GM 4908117. MORONI RD. TIE-IN AT VALVE 14.63
|  |  |  | 6 | [11 empty] | Steel |  |  | GM 4908133 CONENCT ARBUCKLE RD. 35 GAS WELL; MAIN AT ARBUCKLE #35
|  |  |  | 8.625 | [11 empty] | Steel |  |  | N/S SACRAMENTO RIVER 5' N/O 8" POINT.
|  |  |  | 8.625 | [11 empty] | Steel |  |  | S/S SACRAMENT RIVER BETWEEN F.S. 2+60 & F.S. 3+17
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel |  |  | #6001088
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 8 | [11 empty] | Steel |  |  | GM4964508
|  |  |  | 8 | [11 empty] | Steel |  |  | GM4964508
|  |  |  | 6 | [11 empty] | Steel |  |  | PIPE UNDER CANAL HAS INTERNAL COATING. LOOKS GOOD!
|  |  |  | 8 | [11 empty] | Steel |  |  | RD= AT VALVE 2D
|  | 169 |  | 12.75 | [11 empty] | Steel-Other |  |  | TIE-IN EAST WILLOW #1 TO L-169
|  | 302 |  | 20 | [11 empty] | Steel-Other |  |  | GM 4964573-R1. INST'D 4' OF 20" ODX 0.406 WT API 5LXGR X-52 DSAW TO REPLACE 20" CHECK VALVE.
|  | 302 |  | 16 | [11 empty] | Steel-Other |  |  | GM 4964573-R1. INST'D 6'-6" OF 16" 00 X 0.375" WT API SLX GRX42 ERW TO REPAIR 16" L-302.
|  |  |  | 3 | [11 empty] | Steel-Other |  |  | TEE REMOVAL FOR WFL #8 GAS WELL ABANDONMENT
|  |  |  | 2 | [11 empty] | Steel-Other |  |  | 2" ABANDONMENT WFL #1-31 GAS WELL
|  |  |  | 3 | [11 empty] | Steel-Other |  |  | TEE REMOVAL FOR WFL #17 GAS WELL ABANDONMENT
|  | 167 |  | 4 | [11 empty] | Steel-Other |  |  | GM 4964615
|  |  |  | 4.5 | [11 empty] | Steel-Other |  |  | GM 4965615
|  |  |  | 4.5 | [11 empty] | Steel-Other |  |  | GM 4964615
|  |  |  | 4 | [11 empty] | Steel-Other |  |  | TIE IN FRY 5 & 7 & 3 GAS WELLS
|  |  |  | 4 | [11 empty] | Steel-Other
|  |  |  | 6 | [11 empty] | Steel-Other
|  |  |  | 8 | [11 empty] | Steel-Other
|  | 302 |  | 8.625 | [11 empty] | Steel-Other |  |  | TIE'D NEW 4" L-302 TO EXISTING 8" L-302.
|  | 302 |  | 8.625 | [11 empty] | Steel-Other |  |  | TIE'D NEW 4" L-302 TO EXISTING 8" L-302.
|  |  |  | 3 | [11 empty] | Steel-Other |  |  | GM 496525-7
|  |  |  | 8 | [11 empty] | Steel-Other |  |  | GM 4965315 - P/L 0+00. SOUTH TIE - 1X1.
|  |  |  | 10 | [11 empty] | Steel-Other |  |  | TIE-IN FRANKLIN RD- 10". GM 4965315 P/L 80+17.5
|  |  |  | 8 | [11 empty] | Steel-Other |  |  | TIE-IN FRANKLIN RD - 8". GM 4965315 - P/L "A" 0+00
|  |  |  | 16 | [11 empty] | Steel-Other |  |  | VALVE 19.16. GM 4965315 P/L "A" 41+89
|  |  |  | 16 | [11 empty] | Steel-Other |  |  | VALVE 19.16. GM 4965315 P/L "B" 41+89
|  |  |  | 16 | [11 empty] | Steel-Other |  |  | TIE-IN NORTH END. GM 4965315 P/L "B" 9+07.
|  |  |  | 3.5 | [11 empty] | Steel-Other
|  |  |  | 4 | [8 empty] | 1996-11-21 |  |  | Steel-Other |  |  | Cut & capped to aband. Wiggins 2-11 GW and remove creek x-ings.
|  |  |  | 3 | [11 empty] | Steel-Other |  |  | CUT & CAPPED @ FIRESTONE GAS WELL. TO ABAN. ARBUCKLE UNIT'S GW.
|  |  |  | 6 | [8 empty] | 1997-03-06 | [5 empty] | CUT 6" TIE 2" PL CONVERT TO DISTRIBUTION PRESSURE.
|  |  |  | 2 | [8 empty] | 1997-03-06 |  |  | Steel-Other |  |  | CUT OFF FOSTER #1 GAS WELL TIE BACK TO 2" HP.
|  |  |  | 3.5 | [8 empty] | 1997-09-04 |  |  | Steel-Other |  |  | CUT OFF ABOVE VALVES @ POUNASTON 19-1 TIBE BACK BELOW GROUND.
[13 empty] | 1998-05-07 | [5 empty] | CUT & CAPPED 6" L-207.
[13 empty] | 1998-05-05 | [5 empty] | CUT - CAP 8' @ F/S 0400 DETALL 1.
|  |  |  | 4.5 | [8 empty] | 1997-04-17 |  |  | Steel-Other |  |  | CUT & REMOVE RISER & TEE INSTALLED 90 DEGREE ELBOW WITH CANS + SAV-A-VALVE.
|  |  |  | 4.5 | [8 empty] | 1997-04-17 |  |  | Steel-Other |  |  | REMOVE TEE TO ABANDON. WITH TESTED PIPE.
|  |  |  | 2.375 | [11 empty] | Steel-Other
|  |  |  | 3.5 | [8 empty] | 1997-07-31 |  |  | Steel-Other |  |  | HWY 45 @ BENTON DRIVER 12.1 GAS WELL; TIE IN NEW 3" LINE; INSTALL TAP VALVE
|  |  |  | 2 | [8 empty] | 1997-07-31 |  |  | Steel-Other |  |  | MORRIS ROPE e/o HWY 45 @ GOV 7-4 GAS WELL; TIE IN NEW 3" LINE WITH TAP VALVE
|  | 302 |  | 12 | [8 empty] | 1997-07-31 |  |  | Steel-Other |  |  | HWY 45 N/O GRIMES @ J-68; CUT AND CAP AT CENTER-DRIVER 12-1 GAS WALL
|  |  |  | 8.62 | [8 empty] | 1997-03-18 |  |  | Steel-Other |  |  | WHITE RD @ J112 WILKINS B-1 GAS WELL; CUT AND CAPPED @ J-112
|  |  |  | 3.5 | [8 empty] | 1997-10-21 |  |  | Steel-Other |  |  | STARKE RD @ J09 S/O MAY 20; RETIRE MM#1 GAS WELL CUT-CAPPED @ J-69
|  |  |  | 4.5 | [8 empty] | 1997-03-26 |  |  | Steel-Other |  |  | .3 MILE S/O SCHRETTERD RD ON DRY SLOUGH; REMOVE TEE TO RETIRE; MOORE 3-1 WITH 30" .232 PRETESTED PIPE 6000494
|  |  |  | 8 | [11 empty] | Steel-Other |  |  | 1/4 MI EAST OF SOUTH DREXLER; ABANDON GW WELL 9-4 CAO 8" FLANGE ON VALVE 328 ON GIRDNER
|  |  |  | 4.5 | [8 empty] | 1997-10-03 |  |  | Steel |  |  | FRYE #3 S/O FRANKLIN RD; CUT & CAP @ FRYE #5 TO ABANDON FRYE 3 GAS WELL
;
| 97-30205-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-04-23 | 1997-04-23 | Replace Pipe |  | Steel/Wrought Iron |  | S/O MERIDIAN | REPAIRS REQUIRE 40+FT OF DITCH CROSSING WITH SINGLE TRANSPORT WELL. PG&E WILL NOT REPAIR AND DISCUSSIONS STARTED WITH PRODUCER OF NF 12-1
|  | 302 |  | 9
|  |  |  | 3.5 | [8 empty] | 1997-11-06 |  |  | Steel |  |  | S/O SACHREITER RD @ STODDARD #2 GAS WELL; INSTALL 3" LINE STOPPER CUT AND CAPPED
|  | 302 |  | 4 | [11 empty] | Steel |  |  | DRY SLOUGH + GRIMES ARUCHE RD. AT VALVE 459; TIE IN 5100' 4" LINE 302
|  | 302 |  | 4 | [8 empty] | 1999-01-21 |  |  | Steel |  |  | RALSDON RANCH RD +GRIMES ARBUCLE RD AT VALVE 337; TIE IN 5100' LINE 302
|  | 172 |  | 4
|  |  |  | 4 | [14 empty] | INSPECTION ON 4" REACTIVATED S VALVE
Steel/Wrought Iron
|  | 193 |  | 4 | [11 empty] | Steel/Wrought Iron
|  | 193 |  | 4 | [11 empty] | Steel/Wrought Iron
|  | 171 | [13 empty] | Steel/Wrought Iron
|  | 172 | [13 empty] | Steel |  |  | TIED IN TO V-97 FOR TERMO RP 3" RISER. 3X2 REDUCER TO 2" 600 ANSI FLANGE
|  | 172 | [16 empty] | VALVE 133 LINE 172
| 05-16901-1 | 169 | 5.1 | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2005-04-11 | 2005-04-23 | Other | WELDED NEW PIPE SECTION |  |  | E/O WILLOWS | CUT OUT & REPLACED 179'-6" OF 16" L-169
|  |  |  | 4.5 | [8 empty] | 1997-10-27 |  |  | Steel-Other |  |  | HWY 45 N/O CO RD 59 @ FRIESEN #1 G. WELL; CUT AND CAPPED 6' N/O OF FIRE VALVE TO RETIRE GAS WELL
|  | 302 |  | 3.5 | [11 empty] | Steel-Other |  |  | RET. W. GRIMES 14-4 G.W.
|  |  |  | 4 | [11 empty] | Steel-Other |  |  | HWY 162 AFTON AREA ANDREDTTE 18-26 TAP
|  |  |  | 4 | [11 empty] | Steel |  |  | AFTON ST V122
|  | 302 |  | 2 | [8 empty] | 1998-11-24 |  |  | Steel-Other |  |  | 1/4 MI S. SULLFINGER RD IN WALNUT ORCHARD; RETIRE GOV 8-4 WELL BLIND FLANGE TAP VALVE 361
|  |  |  | 2.37 | [8 empty] | 1997-09-10 |  |  | Steel-Other |  |  | EPPERSON #1 FRANKLIN RD.; CLOSED PRODUCER 2" VALE; CUT/CAPPED PIG 4" LINE TO ABITURION GAS WELL
|  |  |  | 3.5 | [8 empty] | 1997-10-22 |  |  | Steel-Other |  |  | GRIMES/ARBUCKLE RD @ BOLSON #9 GAS WELL
|  |  |  | 2.5 | [8 empty] | 1997-10-22 |  |  | Steel-Other |  |  | GRIMES/ARBUCKLE RD @ BOLSDON #3; CUT & CAPPED ALONG GRIMES/ARBUCKLE RD @ TEE WITH 2" CAN TO RETIRE WELL
|  |  |  | 4.5 | [8 empty] | 1997-11-04 |  |  | Steel-Other |  |  | DREXLER RD 500 S/O HWY 20 @ DHAULAGARI GAS WELL; TIE IN 4X4X3 TEE AND TAP VALVE TO CONNECT DHAULAGARI GAS WELL.
|  |  |  | 4.5 | [8 empty] | 1999-09-23 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  |  | CLARK RD @ V-26; CUT OFF @ V26 TO RETIRE ???? ?????
|  |  |  | 4.5 | [8 empty] | 1999-09-28 |  |  | Steel-Other |  |  | N/O CHRUSTIAN @ LEPP #1; CUT & CAPPED 4" CAP/CAN TO RETIRE ???? GAS WELL
|  |  |  | 6.25 | [8 empty] | 1999-09-28 |  |  | Steel-Other |  |  | N/O CHRISTIAN RD ON WALTON ????? RD @ PORTER GAS WELL; CUT-CAPPED 10' S/O/ V45 TO RETIRE PORTER #1 INSTALL 6" CAP AND CAN
|  |  |  | 4.5 | [8 empty] | 1999-09-23 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  |  | CLARK RD @ V-26; CUT-CAP @ V26 TO RETIRE W???? GAS WELL
|  |  |  | 4 | Gathering | TRANSMISSION | [9 empty] | Steel/Wrought Iron |  |  | 7045885 C/O @ VESTNER #1
|  |  |  | 3.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | #7058846
|  |  |  | 3.5 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 169 |  |  | Transmission | [10 empty] | Steel/Wrought Iron
|  | 302 |  | 6 | Transmission | [10 empty] | Other | X42 |  | GRIMES ARBUCKLE RD W/O ROUNDSTONE ROAD; WELD 2" SERVICE TEE TO CONNECT TRINITY WELL; SOAP @ 100 PSI BEFORE TAPPING OUT
| 07-31801-1 | 318 |  | 4 | Transmission | GATHERING |  |  |  | Internal Corrosion |  | 2007-01-30 | [5 empty] | ORLAND
[5 empty] | Transmission | [10 empty] | Steel/Wrought Iron |  | GRIMES
| 98-30204-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-02-03 | 1998-03-04 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPAIR LEAK E/O V.173 WITH 32" .188 4" PRETESTED PIPE SO 7007086
| 98-30212-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-06-25 | 1998-09-23 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPLACED 5'3" OF PIPE WITH PRETESTED PIPE GM 10277620
| 99-167 -2 | 167 |  | 12 | Transmission |  | Body of Pipe | Other | DIG-IN PIPE SEVERED | Damage by 3rd Party | DIG-IN | 1999-11-11 | 1999-11-12 | Other | INST. NEW PIPE | Steel/Wrought Iron |  | S/E PRINCETON | REPLACED BAD PIPE 44' ???? 2" PIPE
| 99-30200-9 | 302 |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Internal Corrosion |  | 1999-11-13 | 1999-11-18 | Welded Sleeve/Can - Weld |  | Other | X52 ERW | COLLEGE CITY | REPAIRED WITH 94 7/8" PRETESTED ... PIPE
| 99-169- |  |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-11-26 | 1999-11-27 | Other | 6' 8 1/4" TESTED PIPE | Steel/Wrought Iron |  | GLENN | REPLACE 6' 8 1/4", 250 W/T PIPE
| 01-30203-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-07 | 2001-06-15 | Welded Sleeve/Can - Weld |  |  |  | S/O GRIMES | INSTALLED 9' CAN
| 01-30204-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-03 | 2001-08-27 | Mechanical Repair Fitting - Fitting |  |  |  | S/E MERIDIAN | INSTALL LEAK CLAMP; SOAP AT 200 PSI. X-RAY SHOWS LIGHT TO MEDIUM PITTING.
| 01-30205-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-03 | 2001-08-27 | Mechanical Repair Fitting - Fitting |  |  |  | S/E MERIDIAN | INSTALL LEAK CLAMP; SOAP AT 200 PSI. X-RAY SHOWED HEAVY PITTING.
| 01-30206-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-03 | 2001-08-28 | Mechanical Repair Fitting - Fitting |  |  |  | S/E MERIDIAN | INSTALL LEAK CLAMP; SOAP AT 200 PSI. X-RAY SHOWS LIGHT PITTING.
| 02-30203-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-04-18 | 2002-05-10 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | S/E MERIDIAN | INST'D PLEDICO 8" LEAK CLAMP
| 02-30204-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-04-18 | 2002-05-10 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | MERIDIAN
|  | 302 |  | 4 | Gathering | TRANSMISSION | [9 empty] | Steel/Wrought Iron |  |  | CONNECT GAS WELL HARLAN 1-24
|  | 302 |  | 4 | Gathering
|  |  |  | 3 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | SOAP TESTED 3" CAP WELD
|  |  |  | 2 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | TIE IN WELD.
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | INSTALLED 4" BLIND FLANGE ON V-133
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 12" PIPE @ ALFALFA FIELD
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | JOB #'S 30610676 & 30693862. REMOVED SECTION OF PIPE W/ TEE. INST'D 73" CAN OF 12" - 0.281" X 52 ERW.
|  |  |  | 6 | Distribution Main | [10 empty] | Steel/Wrought Iron
|  | 302 |  | 3 | Gathering | [7 empty] | 2008-05-30 | Deactivate #TP Main | CUT AND CAP 3" | Steel/Wrought Iron |  | GRIMES | CAP WITH SAV A VALVE AT 20" AND CUT OFF RISER 24" BELOW GROUND. CUT OFF AND ABANDONED APROX. 2,420' OF 3" T.P. STL MAIN.
| 08-30201-1 | 302 | 22.5 | 6.625 | Transmission |  | Body of Pipe |  | DIG-IN 3RD PARTY |  |  | 2008-02-29 | 2008-03-01 | Replace TP Main |  | Steel/Wrought Iron |  | SUTTER | CONTRACTOR DUG INTO PIPE. AREA NOT LOCATED BY LOCATOR; CONTRACTOR UNAWARE OF PIPELINE. NOT MARKED.
| 08-16901-1 | 169 | 2.08 | 12.75 | Transmission |  | Body of Pipe |  |  |  |  | 2008-03-31 | 2008-04-01 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | GLENN | INSTALLED SLEEVE OVER PUNCTURED HOLE IN PIPE; FARMER WAS DIGGING OUT BOTTOM OF DITCH WITH A V-DITCHER PLOW WHEN HE STRUCK STEEL MAIN CAUSING LEAK.
| 08-30204-1 |  |  | 6.25 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-06-03 | 2008-06-11 | Other | CUT & CAP | Steel/Wrought Iron |  | MERIDIAN | CUT & CAP 6" CU.55 TO ABANDON 5.2 GAS WELL DUE TO LEAK.
|  |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  |  | 2008-06-19 | Deactivated Partial Service |  | Steel/Wrought Iron |  |  | CUT OUT EXISTING 6" TEE INSTALLED 34" PRETEST 6" 156 CUT X 42 SOAP C100PSI.
|  | 318 |  | 3.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | INFO ON 10" CAN INSTALLED 6-19-08 A-0110-01
|  | 302 |  | 3 | Gathering | TRANSMISSION | [9 empty] | Steel/Wrought Iron
| 08-31801-1 | 318 | 2.044 | 6.5 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-02-08 |  |  |  | Steel/Wrought Iron |  |  | FOUND PIN HOLE IN BOTTOM OF PIPE. REPAIRED BY INSTALLING 24" CAN OF PRETESTED EMERGENCY STOCK.
|  | 400 | 193.82 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  | GLEN COUNTY | WELDED PIPING & TEE TO LINE 400 PREVIOUSLY TESTED BY M. SHACTTEL PUMPED 3" LINE UP TO 100LBS AND SOAP TESTED TEE WELD.
|  | 193 |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  |  | 3 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 302 |  | 4 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | BLIND FLANGED V-290 OFF L-302 AND REFIRED APROX. 1953' OF 4" STL FROM V-290 TO BILLIEJEAN 18-1 GAS WELL RISER.
|  | 302 |  | 12 | Transmission
|  |  |  | 10.75 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | JOB #'S 30610676 & 30693862. REMOVED SECTION OF PIPE W/ TEE: INST'D 73" CAN OF 12" - 0.281" X 52 ERW.
|  | 302 |  | 2 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | SOAP TESTED AT LINE PRESSURE. JOB # 30696947 RETIRED 2" STL. MAIN FROM V-478 TO SNR # 1 RISER.
|  |  |  | 4.5 | [8 empty] | 1996-06-12 |  |  | Steel-Other |  |  | TIE IN NEW 4" ROAD X-ING
|  |  |  | 4.5 | [8 empty] | 1996-06-12 |  |  | Steel-Other |  |  | TIE IN NEW 4" ROAD XING
|  |  |  | 4.5 | [8 empty] | 1996-06-12 |  |  | Steel-Other |  |  | TIE IN NEW 4" ROAD XING ORDER # 6000494
|  |  |  | 4.5 | [8 empty] | 1996-06-12 |  |  | Steel-Other |  |  | TIE IN NEW 4" ROAD XING. ORDER # 6000494.
|  | 302 |  | 4 | [8 empty] | 1999-01-22 |  |  | Steel-Other |  |  | CUT + CAP 4" STUB OFF LINE 302 TO ABANDON STRAIN RANCH 17-1 WELL.
|  | 162 |  | 4 | [8 empty] | 1998-11-12 |  |  | Steel-Other |  |  | CUT + CAP LINE 162 TO ABANDON CARTER 19-1.
|  |  |  | 4 | [8 empty] | 1998-11-12 |  |  | Steel-Other |  |  | CUT + CAP AT CARTER # 4 WELL TAP.
|  |  |  | 3.5 | [8 empty] | 1999-02-28 |  |  | Steel-Other |  |  | CUT & CAP U 428 TO RETIRE DOMENIGHINI SEA HAWK GAS WELLS. # 6016564.
|  |  |  | 3.5 | [8 empty] | 1999-04-05 |  |  | Steel-Other |  |  | CUT OFF + RETIRE GOBLE AND O'SULLIVAN GAS WELLS. PIG LINE OF ALL FLUIDS AND WOODEN PLUG- INSTALL 3" BLIND FLANGE ON U-36.
|  | 174 |  | 10 | [8 empty] | 1999-03-15 |  |  | Steel-Other |  |  | CONNECT BRADY 1-12 GAS WELL BOUCHO RD E/O ALMOND WELD 3" HOT TAP ON 10" MAIN.
|  | 167 | [13 empty] | Steel/Wrought Iron
|  | 167 | [13 empty] | Steel/Wrought Iron
Steel/Wrought Iron
|  | 169 | [13 empty] | Steel/Wrought Iron | X-42 | ORDBEND
|  |  |  | 4.5 | [8 empty] | 1999-04-15 |  |  | Steel-Other |  |  | CUT AND CAP TO RETIRE JOHNSTON #1 GAS WELL.
Steel/Wrought Iron
|  |  |  | 3.5 | [8 empty] | 1999-11-04 |  |  | Steel-Other |  |  | CUT AND CAPPED 3" @ V-173
|  |  |  | 3.5 | [8 empty] | 1999-11-04 |  |  | Steel-Other |  |  | CUT AND CAPPED 3" @ V-1
|  |  |  | 4.5 | [8 empty] | 1999-04-15 |  |  | Steel-Other |  |  | TIE NEW 4" TO EXISTING V-442
|  |  |  | 4.5 | [8 empty] | 1999-04-15 |  |  | Steel-Other |  |  | TIE NEW 4" TO ROAD XING
|  |  |  | 4.5 | [8 empty] | 1999-10-12 |  |  | Steel-Other |  |  | CUT - CAP @ V25 INSIDE BUTTE STATION. REMOVE FRAME EXTENSION COVER - BLOW OFF VALVE.
|  | 167 | [13 empty] | Steel/Wrought Iron
Aldyl A (Tan or Gray)
Steel/Wrought Iron
[13 empty] | 1999-09-15 |  |  | Steel/Wrought Iron |  |  | CONNECT GENING 1-36 TI V-1.
|  | 318 | [13 empty] | Steel/Wrought Iron |  |  | L-318 TIE IN MANTIS #1
[13 empty] | 1999-10-28 |  |  | Steel/Wrought Iron |  |  | CUT & CAPPED 8" .332 12' RISER 1-1 OUTSIDE FENCE.
|  |  |  | 18 | [8 empty] | 2000-03-23 |  |  | Steel-Other |  |  | INSTALL 3" HOT TAP TO CONNECT MAYFAIR 1-2 GAS WELL.
| 99-16900-3 | 169 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-12-07 | 1999-12-16 | Other |  | Steel/Wrought Iron |  | GLENN
[16 empty] | Steel/Wrought Iron |  |  | ONLY INSIDE PIPE.
|  |  |  | 4 | [11 empty] | Other | GRB SMLS
|  | 302 |  | 20 | [11 empty] | Steel-Other
Steel/Wrought Iron
Steel
|  | 400/401 | [13 empty] | Steel/Wrought Iron
|  |  |  | 4.25 | [8 empty] | 2001-01-05 |  |  | Steel/Wrought Iron |  |  | Relocate meter 10C 16 L-201- INSTALL NEW PIPE RISER.
PIPE HAD GROVE FROM MANDRILL.
[16 empty] | Steel/Wrought Iron |  |  | RETIRE SOUTH SYCAMORE 14-1C
[16 empty] | Steel/Wrought Iron |  |  | RETIRE SOUTH SYCAMORE 3.
[16 empty] | Steel/Wrought Iron |  |  | RETIRE SOUTH SYCAMORE 22.
RETIRE SOUTH SYCAMORE 117
[16 empty] | Steel/Wrought Iron |  |  | RETIRE SOUTH SYCAMORE 16
[16 empty] | Steel/Wrought Iron |  |  | RETIRE POWDSTONE 18-2.
[16 empty] | Steel/Wrought Iron |  |  | RETIRE SOUTH SYCAMORE 9-2.
PIPE HAD LIGHT OIL FIRM
[16 empty] | Steel/Wrought Iron |  |  | PURGED SOAP TESTED @ 95PSI
|  | 167 | [13 empty] | Steel/Wrought Iron |  |  | PURGED - SOAP TESTED WELDS @ 95PSI.
Steel-Other
Steel/Wrought Iron
Steel/Wrought Iron
Steel/Wrought Iron
|  | 167 | [13 empty] | Steel/Wrought Iron
[16 empty] | Steel/Wrought Iron |  |  | ABANDON 12" MAIN 167 FROM V115-104
[16 empty] | Steel/Wrought Iron |  |  | ABANDON MAIN FROM V105-104.
[16 empty] | Steel/Wrought Iron |  |  | NO LEAKS DETECTED.
TWO LEAKS CUT IN 25'8".
|  |  |  | 12 | Distribution Main |  | Other |  | PIT | Internal Corrosion | [5 empty] | Steel/Wrought Iron |  |  | 2 LEAKS CUT IN 25'8"
|  | 167 | [13 empty] | Steel/Wrought Iron |  |  | NO LEAKS DETECTED.
[16 empty] | Steel/Wrought Iron |  |  | ABANDON MAIN FROM V105-104
[16 empty] | Steel/Wrought Iron |  |  | ABANDON 12" MAIN 169 FROM V105-104
|  | 167 | [13 empty] | Steel/Wrought Iron
Steel/Wrought Iron
|  | 167 | [13 empty] | Steel/Wrought Iron
Steel/Wrought Iron
|  | 169 | [13 empty] | Steel/Wrought Iron
|  | 167 | [13 empty] | Steel/Wrought Iron
|  | 167 | [13 empty] | Steel/Wrought Iron |  |  | PURGED. SOAP TESTED WELDS & TEES.
|  | 167 | [13 empty] | Steel/Wrought Iron |  |  | PURGED. SOAP TESTED @ 95PSI
|  |  |  | 4.5 | [8 empty] | 2000-08-29 |  |  | Steel/Wrought Iron | X-42 |  | INSTALL 4X3 TEE WITH TAP VALVE TO CONNECT NEW GRIMES GASWELL
|  |  |  | 4.5 | [8 empty] | 2000-10-10 |  |  | Steel-Other |  |  | TIE-IN LOCAL GAS WELL INSTALL 4" TEE & RISER.
| 00-30203-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Digin |  | 2000-05-24 | 2000-05-25 | Other |  |  |  | SUTTER | INSTALL 63' NEW DOG LEG WITH 6' EACH OVER
|  |  |  | 4 | [11 empty] | Steel-Other
| 10-82036- | 302-186 | 0.43 | 3.5 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-15 | 2010-10-05 | Other |  | Steel-Other |  | SUTTER | TIGHTENED 3/4" METER TUBE TAP VALVE PLUG. SOAP TESTED, OK
| 10-82036-1 | [5 empty] | Other |  | VALVE |  |  | 2010-10-05 | 2010-10-05 |  |  |  |  | SUTTER | REPAIR LEAK ON METER TUBE; TITE PLUGE OK
| 10-82039- | 302-116 | 0.05 | 0.75 |  |  | Other |  |  | Other |  | 2010-10-06 | 2010-10-06 | Other |  | Other |  | MERIDIAN | REPAIR LEAK ON RELIEF VALVE; REMOVE NIPPLE INSTALL NEW; INSTALLED NEW 3/4" NIPPLE ON PRESSURE SIDE OF RELIEF VALVE.
| 10-82039-1 |  |  | 0.6 | [7 empty] | 2010-10-06 | 2010-10-06 |  |  |  |  | MERIDIAN | REPAIR LEAK ON RELIEF; REMOVE NIPPLES INSTALL NEW
| 10-82043- | 339-1-1 | 0.87 |  | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-09 | 2010-10-09 | Other |  | Other |  | ORLAND | TIGHTENED 3/4" METER TUBE VALVE PLUG.; TIGHTENED 3/4" METER TUBE VALVE TAP PLUG. SOAP TESTED OK.
| 10-82043-1 | 339 | 2.87 | 0.5 |  |  | Other |  | PLUG | Other | TAPE | 2010-10-09 | 2010-10-09 |  |  | Other | STEEL |  | ON METER TUBE
| 10-82042- | 169-109 | 0 |  | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Other |  | 2010-10-08 | 2010-10-08 | Mechanical Repair Fitting - Fitting |  | Other |  | WILLOWS | TIGHTENED REG. DIAPHRAGM SEAL. & SOAP TESTED. BTU GAS SAMP. AT METER TUBE.
| 10-82042-1 | 169 |  |  |  |  | Regulator |  |  |  |  | 2010-10-08 | 2010-10-08 | Mechanical Repair Fitting - Fitting |  |  |  | WILLOWS | DOGS AT LARGE GAS WELL. WELKER GAS SAMPLER.; REPAIRED LEAKING NORGEN REG. DIAPHRAGM SEAL.
| 10-82037- | 302W | 5.76 |  | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-05 | 2010-10-05 | Other |  | Steel-Other |  | DUNNIGAN | TIGHTENED ORIFICE FITTING GASKET SEAL. & SOAP TESTED.
| 10-82037-1 | 302 |  | 20 |  |  |  |  | ORIFICE METER |  | GASKET | 2010-10-05 | 2010-10-05 |  |  | Steel/Wrought Iron |  | DUNNIGAN | M-4 ORIFICE METER LEAK; TIGHTENED ORIFICE METER GASKET SEAL.;
| 10-82040- | 302-096 | 0.82 | 6 | Gathering |  | Other |  |  | Other |  | 2010-10-06 | 2010-10-06 | Other |  | Other |  | GRIMES | REPLACED REGULATOR; REPLACED 1/4" FISHER SUPPLY REG. TO INHIBITOR PUMP STATION. TO REPAIR LEAK.
| 10-82040-1 |  |  | 6 |  |  | Other |  | REG. | Other | REG. | 2010-10-06 | 2010-10-06 |  |  |  |  | GRIMES | FOUND LEAK ON REG.; REPLACE REG.
| 10-82041- | 174-4-9 | 0.01 |  | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-07 | 2010-10-07 | Other |  | Other |  | ARBUCKLE | TIGHTENED ORIFICE FITTING BLOWN DOWN.
| 10-82041-1 | 174 |  |  |  | VALVE |  |  | ORIFICE FITTING | Other | BLOWDOWN VALVE | 2010-10-07 | 2010-10-07 |  |  |  |  | ARBUCKLE | TIGHTENED BLOW DOWN FITTING ON ORIFICE METER
| 10-82038- | 302-286 | 0.4 | 3.5 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-06 | 2010-10-06 | Other |  | Other |  | GRIMES | REPLACED ORIFICE METER GASKET & SOAP TESTED OK.
| 10-82038-1 | 302 |  | 3 |  |  | Other |  | ORIFICE METER | Other | GASKET | 2010-10-06 | 2010-10-06 |  |  | Steel/Wrought Iron |  | GRIMES | 3" ORIFICE METER TUBE.; DANIEL ORIFICE FITTING; TIGHTENED ORIFICE FITTING GASKET SEAL
| 10-82095- | 169 |  | 2 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-08 | 2010-10-15 | Other |  |  |  | ORD BEND | V-15/ GREASED LEAKING BATTON HEAD FITTING; REPAIRED V-15 GREASE FITTING BY LUBING V; RJWG GREASED VALVE - FOUND NO LEAK.
| 10-82095-1 |  | 169 | 2 |  |  | Valves |  |  | Other | GREASE HEAD FITTING | 2010-10-08 | 2010-10-15 | Other | GREASE FITTING | Steel/Wrought Iron |  | ORD BEND | V-15/ GREASED LEAKING BATTON HEAD FITTING.; REPAIRED V-15 GREASE FITTING BY LUBING VALVE.
| 10-82096-1 | 193 |  | 0.5 | Gathering |  | Other |  | REG'S | Unknown |  | 2010-10-09 | 2010-10-09 | Other | REPLACE FAIRCHILD REG'S. | Other | STEEL | ORLAND | ON FAIRCHILD REG'S VENTS; RICE CREEK DEHYDRATOR STATION - ODORIZER; REPLACED REGULATORS (FAIRCHILD); REPLACED 2 FAIRCHILD REGS. TO CORRECT LEAKS. SOAP TEST - NO LEAKS.
| 10-82020- |  |  | 4 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2010-10-05 | 2010-10-07 |  |  | Steel/Wrought Iron |  | GRIMES | 4" L-302 TAP V-286; OPERATING MAP 484001 TAP VALVE #286
[7 empty] | Other |  | REG'S |  |  | 2010-10-09 | 2010-10-09 | Other | REPLACE FAIRCHILD REG'S. |  | STEEL |  | ON FAIRCHILD REG'S VENTS
| 10-82020-1 | 302-131 | 0 | 4 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2010-10-05 | 2010-10-07 | Other |  | Steel/Wrought Iron |  | GRIMES | 4" L-302 TAP V-286; TAP VALVE #286
| 10-82020-1 | 302 | 1 | 4 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2010-10-05 | 2010-10-07 | Other | PLIDCO CLAMP | Steel/Wrought Iron |  | GRIMES | 4" L-302 TA[ V-286; GTLS PHASE I LEAK FOUND BY HELICOPTER SURVEY; OPERATING MAP 484001 TAP VALVE #286; CLAMP INSTALLED; LEAK FOUND BY HELICOPTER PATROL. REPAIRED BY INSTALLING PLIDCO CLAMP. CLEARANCE # ME 10-05 ON 10-7-10
| 10-88538- | 302-141 | 0.65 |  | Gathering |  | Other |  |  | Internal Corrosion | SUSPECT | 2010-10-19 |  | Deactivate #TP Main |  | Steel-Other |  | SUTTER | SHUT IN GAS PROD.; L-302 STRANDED PIPE; PIPELINE TO BE RETIRED ON JOB #30818707; L-302 PIPE IS STRANED AND USED BY GAS PRODUCER. IT WILL BE RETIRED IN PLACE ON JOB# 30818707. PIPELINE WAS NOT EXCAVATED. PRODUCER WAS NOTIFIED TO SHUT IN THIS SECTION OF PIPE. PENDING RETIREMENT AND SALE.
| 10-88544-1 | 302-061 | 1.21 | 0.25 | Gathering |  | Fitting | Other | QUICK CONNECT | Other | DAMAGED, RING 11-17-10 | 2010-10-20 | 2010-11-01 | Other | QUICK CONNECT | Steel/Wrought Iron |  | GRIMES | SO. SYCAMORE #9-3 ORIFICE METER TUBE.; REPLACE LEAKING QUICK CONNECT FITTING.; REPLACED QUICK CONNECT ON ORIFICE METER.; SOAP TESTED NEW QUICK - CONNECT FITTING AND NO LEAKS.
| 10-88576- | 1004-03 | 0.6 | 3 | Transmission >= 20% SMYS |  | Other |  | GREASE FITTING | Other |  | 2010-10-28 | 2010-11-12 | Greased - Other |  | Steel-Other |  | ORLAND | @ ROAD P. ON VALVE NORTH OF BRAGE & GREASE VALVE; GREZ VALVZ; DFA2 REPAIRED LEAK ON GREASE FITTING BY PUTTING GREASE INTO THE FITTING - SOAP TEST - NO LEAK
| 10-88552-1 | 302-780 |  | 6 | Gathering |  | Other |  | GREASE FITTING | Other | GREASE FITTING | 2010-10-21 | 2010-11-06 | Other | GREASE FITTING | Steel/Wrought Iron |  | COLUSA | LEAK ON GREASE FITTING SOAP TEST; GREASE FITTING; GREASED VALVE - NO LEAK. (V-84)
| 10-88552-1 | 302-780 |  | 6 | Gathering |  | Other |  | GREASE FITTING | Other | GREASE FITTING | 2010-10-21 | 2010-11-06 | Other | GREASE FITTING | Steel/Wrought Iron |  | COLUSA | LEAK ON GREASE FITTING SOAP TEST; GREASE FITTING; GREASED VALVE - NO LEAK. (V-84)
| 10-88577-1 | 177 |  | 0.5 | Transmission |  | Fitting |  |  | Other | GREASE FITTING | 2010-10-28 | 2010-11-06 | Other | INJECTED GREASE | Steel/Wrought Iron |  | ORLAND | SOAP TEST; STONEY CREEK MASTER METER, 30' EAST OF METER; INJECTED GREASE INTO GREASE FITTING; GREASED VALVE - NO LEAK
| 10-88554-1 | 302 |  | 0.5 | Transmission |  | Fitting |  |  | Other | GREASE FITTING | 2010-10-21 | 2010-11-06 | Other | INJECTED GREASE | Steel/Wrought Iron |  | COLUSA | SOAP TEST; 150' EAST OF SAC. RIVER APPROX 1000' SOUTH OF KILGORE RD; INJECTED GREASE INTO GREASE FITTING; GREASED BUTTON HEAD - NO LEAKS
| 10-88554-1 | 302 |  | 0.5 | Transmission |  | Fitting |  |  | Other | GREASE FITTING | 2010-10-21 | 2010-11-06 | Other | INJECTED GREASE | Steel/Wrought Iron |  | COLUSA | SOAP TEST; 150' EAST OF SAC. RIVER APPROX 1000' SOUTH OF KILGORE RD; INJECTED GREASE INTO GREASE FITTING; GREASED BUTTON LEAK - NO LEAKS
| 10-88539-1 | 302E | 4.23 | 0.25 | Transmission |  | Valves |  |  |  | 1/4" PLUG | 2010-10-19 | 2010-11-06 | Other | VALVE PLUG | Steel/Wrought Iron |  | COLUSA | 1/4 BLOW OFF PLUG; OSWALD RD VALVE PIT MLV 299; TIGHTENED 1/4 PLUG ON BLOW DOWN STACK; REPAIRED 7% LEL LEAK ON BLOW DOWN STACK; 1/4" PLUG ON METRIC VALVE REPAIRED NO LEAK.
| 10-88539-1 | 302E | 4.23 | 0.25 | Transmission |  | Valves |  |  |  | 1/4" PLUG | 2010-10-19 | 2010-11-06 | Other | VALVE PLUG | Steel/Wrought Iron |  | COLUSA | 1/4 BLOW OFF PLUG; OSWALD RD. VALVE PIT MLV 299; TIGHTENED 1/4 PLUG ON BLOW DOWN STACK.; REPAIRED 7% LEL LEAK ON BLOW DOWN STACK; 1/4" PLUG ON METRIC VALVE REPAIRED NO LEAK.
| 10-88557-1 | DRG10274 |  |  | Distribution Main |  | Other |  | NONE | Other | NONE | 2010-10-21 | 2010-11-06 | Other | NONE | Other | NONE | COLUSA | NO LEAKS FOUND
| 10-88582-1 | 169B | 12.93 | 0.75 | Transmission | SERVICE | Valves |  |  | Other | PLUG LOOSE | 2010-11-01 | 2010-11-12 | Other | TIGHTEN PLUG | Steel/Wrought Iron |  | CHICO | REG SET BEHIND HOUSE - LOOSE PLUG; TIGHTENED PLUG; TIGHTENED PLUG ON REG SET VALVE - NO LEAKS
| 10-88618- | 167 | 18.98 | 16 |  |  | Unknown | Other | NO LEAK FOUND | Other | UNKNOWN | 2010-11-18 |  | Other | NO LEAK FOUND | Steel-Other |  | GRIDELY | NO LEAK FOUND
| 10-88605-1 | 128 |  | 0.25 | Gathering |  | Other |  | PLUG | Other | LOOSE PLUG | 2010-11-02 | 2010-11-15 | Other | TIGHTENED PLUG | Steel/Wrought Iron |  | WILLOWS | TIGHTENED 1/4" PLUG; TIGHTENED 1/4" PLUG ON METRIC VALVE - OK NO LEAK
| 10-88603-1 | 169 | V-235 | 0.25 | Gathering |  | Valves |  |  | Other | PLUG | 2010-11-02 | 2010-11-15 | Other | VALVE PLUG | Steel/Wrought Iron |  | WILLOWS | 1/4" VALVE PLUG; TIGHTENED GAUGE TAP AT MLV 235 PLUG.; TIGHTENED 1/4 PLUG; REPAIRED LEAK ON 1/4" GAUGE TAP PLUG.; REPAIRED LEAK ON 1/4" GAUGE TAP PLUG OK
| 10-88609-1 | 128 | 15.23 | 2 | Gathering | TRANSMISSION | Other |  | GREASE FITTING | Other | NEEDS GREASE | 2010-11-02 | 2010-11-12 | Other | GREASED FITTING | Steel/Wrought Iron |  | WILLOWS | GREASE FITTING & PUT GREASE IN FITTING; PUT GREASE IN FITTING; GREASED FITTING TO BLOW OFF STACK. NO LEAKS
| 10-88578-1 | 177 |  | 2 | Service |  | Valves |  |  | Other | GREASE FITTING | 2010-10-28 | 2010-11-10 | Other | VALVE | Steel/Wrought Iron |  | CHICO | M&T?RANCH MTR STA; VLV BELOW PADDLE; M&T RCH. FIRE VALVE FOR DIST. REG; GREASED VALVE TO STOP LEAK.; REPAIRED LEAK BY GREASING VALVE. (SOAP TEST OK)
| 10-88597-1 | 1030-01 | 51 | 4 | Single Service |  | Other |  | GREASE FITTING | Other | GREASE FITTING | 2010-11-02 | 2010-11-12 | Other | GREASED VALVE | Steel/Wrought Iron |  | WILLOWS | VLV@PIPE MASKE 1500A S/RD 30; 1200' E/RD U; FIRE VALVE; 1500 FT. SOUTH OF RD 3D. AT FIRE VALVE; PUT GREASE IN FIRE VALVE; GREASED FIRE VALVE - NO LEAKS
| 10-88615- | 172A | 70.07 | 0.25 |  | SUPPLY | Other |  | UNION FITTING | Other | TIGHTEN FITTING | 2010-11-04 | 2010-11-18 | Other |  | Steel-Other |  | DUNNIGAN | MRKD W/PAINT OR ZIPTIES; SEE ATTACHED SHEET; IN VALVE COVER BOX; HERSHEY SET. - REPAIRED LEAK AT SUPPLY RACK (UNION & PLUG); REPAIRED LEAK @ UNION AND PLUG ON SUPPLY RACK
| 10-88550-1 | 302E | 12.02 | 6 | Transmission |  | Valves |  |  | Other | LOOSE PLUG | 2010-10-20 | 2010-11-01 | Other | TIGHTENED VALVE PLUG | Steel/Wrought Iron |  | SUTTER | V12.02 LOCATION; HWY. 45 TOWN OF GRIMES MLV 1202 BLOW OFF STACK.; TIGHTENED VALVE BODY BLEED PLUG.; 6" CAMERON BALL VALVE @ V12.02 BODY BLEED PLUG
| 10-88545-1 | 302-040 | 0.55 | 0.75 | Gathering |  | Valves | Other | GAUGE TAP | Other | PLUG LEAK | 2010-10-20 | 2010-11-01 | Other | VALVE | Steel/Wrought Iron |  | GRIMES | POUNDSTONE REGSTA; LK ABV GRND ON VLV V-2; V-66 GAUGE TAP; REPAIRED GAUGE TAP LOOSE PLUG.; TIGHTENED VALVE BODY BLEED PLUG.
| 10-88546-1 | 302-006 | 0 | 0.75 | Gathering |  | Valves |  |  | Other | PACKING | 2010-10-20 | 2010-11-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | GRIMES | ARBUCKLE #13 METER TUBE.; TIGHTENED VALVE PACKING; TIGHTENED VALVE PACKING
| 10-88549-1 | DREG5430 | 0.08 | 0.75 | Branch Service |  | Fitting |  |  | Other | UNION LEAK | 2010-10-20 | 2010-11-01 | Other | TIGHTENED UNION | Steel/Wrought Iron |  | GRIMES | DRY SLOUGH RD. REG. STATION; TIGHTENED 3/4" UNION ON DOMESTIC ODORIZER. TIGHTENED 3/4" UNION ON ODORIZER.
| 10-88551-1 | 302-233 |  | 0.5 | Gathering |  | Other |  | PLUG | Other | LOSE PLUG | 2010-10-21 | 2010-10-25 | Tighten Cap or Bolt | PLUG | Steel/Wrought Iron |  | MERIDIAN | FEDORA RP GAS WELLL; ON METER TUBE; LOSE PLUG - TIGHTEN PLUG; TIGHTEN PLUG ON METER TUBE
| 10-88544-1 | 302-061 | 1.21 | 0.25 | Gathering |  | Fitting | Other | QUICK CONNECT | Other | DAMAGED | 2010-10-20 | 2010-11-01 | Other | QUICK CONNECT | Steel/Wrought Iron |  | GRIMES | SO. SYCAMORE #9-3 ORIFICE METER TUBE.; REPLACED LEAKING QUICK CONNECT FITTING.; REPLACED QUICK CONNECT ON ORIFICE METER.; SOAP TESTED NEW QUICK - CONNECT FITTIN AND NO LEAKS.
| 10-88543-1 | 302-185 | 0.01 | 0.5 | Gathering |  | Other |  | PLUG | Other | LOOSE PLUG | 2010-10-19 | 2010-11-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SUTTER | NONE; AT VALVE ON TAP MLV - 46 ON 302E; TIGHTEN PLUG; TIGHTENED PLUG
| 10-88599- | 169W | [9 empty] | 2010-11-02 | [5 empty] | WILLOWS | TAN K S48, BLEED BOX BLOWING; NOT PG&E LEAK - VENOCO INK.
| 10-88601- | 193-008 |  | 2 | Gathering |  | Valves |  |  | Other | VALVE OPEN | 2010-11-02 | 2010-11-02 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ORLAND | PLUG AT TOP OF TEE VALVE ON LEFT HAND SIDE OF ENTRY; ALL OK; TAYLOR GLOVER 28-1 (GAS WELL ORIFICE METER); FOUND 1/2" VALVE ABOVE BLOCK VALVE ON METER TUBE PARCIALLY OPEN WIHT NO SEAL TAP ON PLUG CLOSED VALVE & APPLIED SEAL TAPE TO PLUG. RETESTED OK.; 1/2" VALVE LEAK - REPAIRED CLOSED VALVE AND RETAPED PLUG
| 10-88565-1 | 167-63 |  | 2 | Gathering |  | Fitting |  |  | Other | NUT; | 2010-10-26 | 2010-10-26 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | WILLOWS | LEAK ON FITTIN AT REG STATION; ON METER TUBE; TIGHTEN CARRIER BOLT; STLP LEAK TIGHTENED CARRIER BOLT SOPE TEST OK
| 10-88569-1 | 174 |  | 3 | Gathering |  | Fitting |  |  | Other | OPEN VALVE | 2010-10-26 | 2010-10-26 | Tighten Cap or Bolt | INSTALLED NEW PIPE PLUG | Steel/Wrought Iron |  | ARBUCKLE | LEAK FOUND ON FITTING; ON METER TUBE AT 1/2" METRIC VALVE; CLOSED VALVE - INSTALLED NEW PLUG; REPAIRS MADE BY CLOSING VALVE COMPLETELY AND INSTALLING NEW PLUG WITH TEFLOW TAPE. SOAP TEST - NO LEAK.
| 10-88566-1 | 121/302 |  | 6 | Transmission |  | Other |  | ORIFICE FITTING | Other | PACKING NUT | 2010-10-26 | 2010-10-27 | Tighten Cap or Bolt | PACKING NUT | Steel/Wrought Iron |  | SUTTER | OPHEDS METER PACKING ON VALVE; REPAIRED ORIFICE CARRIER FITTING LEAK; SOAP TEST OK; SOAP TEST NO LEAK; TIGHTENED ORIFICE FITTING CARRIER SLIDE PACKING NUT.
| 10-88540-1 | 302W | 4.67 | [8 empty] | 2010-10-19 | [6 empty] | MARYSVILLE DIVISION - NOT GT
| 10-88541-1 | 302W | 4.67 | [8 empty] | 2010-10-19 | [5 empty] | DUNNIGAN | LK ON FARM TAP; MARYSVILLE DIVISION - NOT GT
| 10-88542-1 | 302W | 4.66 | [8 empty] | 2010-10-19 | [5 empty] | DUNNIGAN | LK ON FARMTAP; MARYSVILLE DIV - NOT GT
| 10-88547-1 | 302-077 | 0.24 | [8 empty] | 2010-10-20 | [5 empty] | GRIMES | 1500'S/O RD; LK @ REGSTA - 1.25MI W/O DRY CREEK SLO; GAS PRODUCER - NOT GT WELL EQUIP; FOOT HILL ENERGY 530-228-4292 NOTIFIED
| 10-88548-1 | 302-072 | 0.47 | [8 empty] | 2010-10-20 | [5 empty] | GRIMES | 800' N/O 1531; MARYSVILLE DIV - NOT GT
| 10-88553-1 | 302-280 | [9 empty] | 2010-10-21 | [5 empty] | SUTTER | LEAK AT FARM TAP; MARYSVILLE DIV - NOT GT
| 10-88555-1 | 302-780 | [9 empty] | 2010-10-21 | [5 empty] | SUTTER | GASKET ON REG MARKED W/YELLOW TIE. L-302780; MARYSVILLE DIV - NOT GT
| 10-88556-1 | 302-780 | 59 | [8 empty] | 2010-10-21 | [5 empty] | SUTTER | REG HE ON UNION MARKED W/YELLOW TIE; AX FRM D/WY; MARYSVILLE DIV - NOT GT
| 10-88558-1 | DREG7086 | 0.01 | [8 empty] | 2010-10-22 | [5 empty] | MERIDIAN | MARYSVILLE DIV - NOT GT
| 10-88559-1 | 302E | 16.4 | [8 empty] | 2010-10-22 | [5 empty] | MERIDIAN | FARM TAP DUCST U988 MARKED YELLOW; MARYSVILLE DIV - NOT GT
| 10-88561-1 | 302E | 5.08 | [8 empty] | 2010-10-22 | [5 empty] | YUBA CITY | 700' W. OF GREENLEAF II ODOR STAT. 30' NO. OF STREE; GAS PRODUCER - NOT GT; DOS RIOS 530-674-0751 DFAZ NOTIFIED 11-6-10
| 10-88560-1 | 302-255 | 0.26 | [8 empty] | 2010-10-22 | [5 empty] | SUTTER | LEAK A FARM TAP ON REGULATOR; MARYSVILLE DIV - NOT GT
| 10-88562-1 | 3.02 | 0.99 | [8 empty] | 2010-10-22 | [5 empty] | MERIDIAN | 250' WEST OF ADDRESS; MARYSVILLE DIV - NOT GT
| 10-88563-1 | 30.2 | 0.99 | [8 empty] | 2010-10-22 | [5 empty] | MERIDIAN | 250' WEST OF ADDRESS; MARYSVILLE DIV - NOT GT
| 10-88564-1 | 3.02 | 0.99 | [8 empty] | 2010-10-22 | [5 empty] | MERIDIAN | 250' WEST OF ADDRESS; MARYSVILLE DIV - NOT GT
| 10-88595-1 | 401 | 241.34 | [8 empty] | 2010-11-01 | [5 empty] | SACRAMENTO | MRKR 241-35; VLV BELOW MRKR; WILLOWS
| 10-88596-1 | 169A | 4 |  | Transmission | [6 empty] | 2010-11-02 | [5 empty] | WILLOWS | WELL 49-5, BUBLE RISING THROUGH WATER; GAS PRODUCER - NOT GT (NOTIFIED)
| 10-88580-1 | 1 | [9 empty] | 2010-10-28 | [5 empty] | CHICO | W/O MUD CREEK; TEST PLUG MRKD W/Y-TIE TIE; CHICO DIV - NOT GT
| 10-88581-1 | 1 | [9 empty] | 2010-10-28 | [5 empty] | CHICO | 4X8 BX MRKD W/Y-FLAG; BLDG W/I 50'; CHICO DIV NOT GT
| 10-88610-1 | 1 | [9 empty] | 2010-11-02 | [5 empty] | WILLOWS | WILLOWS REGSTA VLV MRKD IN YELLOW; CHICO DIV - NOT GT
| 10-88611-1 | 1 | [9 empty] | 2010-11-02 | [5 empty] | WILLOWS | WILLOWS REGSTA; VLV MRKD Y-PAINT; CHICO DIV - NOT GT
| 10-88612-1 | 1 | [9 empty] | 2010-11-02 | [5 empty] | WILLOWS | VLV MRK Y-PAINT; WILLOWS REGSTA; CHICO DIV - NOT GT
| 10-88613-1 | 1 | [9 empty] | 2010-11-02 | [5 empty] | WILLOWS | VLV MRKD IN YELLOW; CHICO DIV - NOT GT
| 10-88614-1 | 1 | [9 empty] | 2010-11-02 | [5 empty] | WILLOWS | WILLWS REGSTA FITTNG B/H VLTS MRKD YELLOW; CHICO DIV - NOT GT
| 10-88616-1 | 169 | [9 empty] | 2010-11-04 | [5 empty] | WIILOWS | JACINTO REGSTA; 2 ABVGRND MRKD W/ZIPTIES; CHICO DIV - NOT GT
| 10-88579-1 | 1004-01 | 3.19 | [8 empty] | 2010-10-28 | [5 empty] | ORLAND | FRM TAP N/S OF ST. 10' W/O ROAD MM; CHICO DIV - NOT GT
| 10-88598-1 | 1030-02 | 0.07 | [8 empty] | 2010-11-02 | [5 empty] | CHICO | CHICO DIV NOT GT
| 10-88600-1 | 1030-02 | 18 | [8 empty] | 2010-11-02 | [5 empty] | CHICO | CHICO DIV. NOT GT.
| 10-88602-1 | 1030-02 | 1.16 | [8 empty] | 2010-11-02 | [5 empty] | CHICO | CHICO DIV NOT GT
| 10-88607-1 | 128 | 141.14 | [8 empty] | 2010-11-02 | [5 empty] | CHICO | CHICO DIV NO GT
| 10-88608-1 | 193-016 | 1.28 |  | Transmission | [6 empty] | 2010-11-02 | [5 empty] | ORLAND | CHICO DIV NOT GT
| 10-88583-1 | 119A | 3.82 | [8 empty] | 2010-11-01 | [5 empty] | SACRAMENTO | SAC DIV NOT GT
| 10-88584-1 | 119A | 3.84 | [8 empty] | 2010-11-01 | [5 empty] | SACRAMENTO | SAC DIV
| 10-88585-1 | 119A | 3.83 | [8 empty] | 2010-11-01 | [5 empty] | SACRAMENTO | SAC DIV NOT GT
| 10-88586-1 | 201-3-2 | 0 | [8 empty] | 2010-11-01 | [5 empty] | SACRAMENTO | SAC DIV NOT GT
| 10-88587-1 | 116 | 3.86 | [8 empty] | 2010-11-01 | [5 empty] | SACRAMENTO | SAC DIV NOT GT
| 10-88588-1 | 172A | 69.81 | [8 empty] | 2010-11-01 | [5 empty] | SACRAMENTO | SAC DIV NOT GT
| 10-88589-1 | 116 | 3.86 | [8 empty] | 2010-11-01 | [5 empty] | SACRAMENTO | SAC DIV NOT GT
| 10-88590-1 | 119A | 3.85 | [8 empty] | 2010-11-01 | [5 empty] | SACRAMENTO | SAC DIV NOT GT
| 10-88591-1 | 172A | 69.81 | [8 empty] | 2010-11-01 | [5 empty] | SACRAMENTO | SAC DIV NOT GT
| 10-88592-1 | 172A | 69.81 | [8 empty] | 2010-11-01 | [5 empty] | SACRAMENTO | SAC DIV NOT GT
| 10-88593-1 | 172A | 69.81 | [8 empty] | 2010-11-01 | [5 empty] | SACRAMENTO | NOE; NONE; SAC DIV NOT GT.
| 10-88594-1 | 172A | 69.81 | [8 empty] | 2010-11-01 | [5 empty] | SACRAMENTO | NONE; NONE; SAC DIV NOT GT
| 10-88567-1 | DCUS7910 | 0.06 | [8 empty] | 2010-10-26 | [5 empty] | WILLIAMS | MSVL DIV-NOT GT
| 10-88568-1 | 120-1 | 97 | [8 empty] | 2010-10-26 | [5 empty] | SUTTER | MSVL DIV NOT GT
| 10-88570-1 | DREG6981 | 0 | [8 empty] | 2010-10-26 | [5 empty] | ARBUCKLE | MSVL DIV NOT GT
| 10-88571-1 | 172A | 5.21 | [8 empty] | 2010-10-26 | [5 empty] | BUTTE CITY | MSVL DIV NOT GT
| 10-88572-1 | GGDR5975 | 0 | [8 empty] | 2010-10-27 | [5 empty] | BUTTE CITY | MSVL DIV NOT GT
| 10-88573-1 | 0635-01 | 69 | [8 empty] | 2010-10-27 | [5 empty] | BUTTE CITY | MSVL DIV NOT GT
| 10-88574-1 | 0630-01 | 2 | [8 empty] | 2010-10-27 | [5 empty] | MERIDIAN | MSVL DIV NOT GT
| 10-88575-1 | 172A | 25 | [8 empty] | 2010-10-27 | [5 empty] | BUTTE CITY | MSVL DIV NOT GT
|  | 302 |  | 4 | [8 empty] | 2010-05-26 | Other | RETIRED |  |  |  | NEAR V-290 LINE RETIRED (BILLIE JEAN 18-1); LEAK AAREA BLIND FLANGE INSTALLED 4" L302 RETIRED
| 08-17201-1 | 172 | [9 empty] | 2008-05-20
| 08-17202-1 | 172 | [9 empty] | 2008-05-20 | [5 empty] | DUNNIGAN
| 04-30202-1 |  |  | 6 | Gathering |  |  |  |  | Internal Corrosion |  | 2004-10-21 | [5 empty] | SUTTER; | EMPLOYEE FOUND LEAK DURING FLAME PACK BEFORE EVACUATING LINE FOR PREVIOUS LEAK
| 04-30202-1 |  |  | 6 | [5 empty] | Internal Corrosion | SUSPECT | 2004-10-21 | [5 empty] | SUTTER
| 07-12001-1 | 120/121 |  | 6 | Transmission |  | Unknown |  |  | Unknown |  | 2007-08-01 | 2007-08-01 | Deactivate #TP Main |  | Steel/Wrought Iron |  | SUTTER | DEACTIVATED APPROX 105' OF 6", 4", 2" STL OF LINE 120 FROM T-2.03. SEE ATTACHED SHEET
| 07-31801-1 | 318 |  | 4 | Transmission | GATHERING |  |  |  | Internal Corrosion |  | 2007-01-30 | 2007-02-07 | Other | REPLACED PIPE |  |  | ORLAND | ISOLATED AND BLEW DOWN PIPELINE DOWN FOR SAFETY 280FT OR PIPELINE TO BE REPLACED ON 2-7-07
| 06-30202-1 |  |  | 6.25 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2006-05-30 | 2006-09-27 | Weld Over Sleeve or Can |  |  |  | GRIMES | INSTALLED 28" OF .280WT PIPE
| 06-17401-1 |  |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2006-05-08 | 2006-05-23 | Other | CUT & CAP | Other | X-42 | ARBUCKLE | CUT AND CAPPED 3" STUB
| 05-30202-1 |  |  | 6 | Gathering | SERVICE |  |  |  | Internal Corrosion |  | 2005-11-28 | 2005-12-08 | Other | NEW PIPE |  |  | MERIDIAN
| 05-30201-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Damage by 3rd Party |  | 2005-04-17 | 2005-04-26 | Other | SAVE-A-VALVE |  |  | SUTTER | BULLET HOLE IN PIPE BETWEEN WELL BU#56 AND BU#60. ISOLATED AND BLOWN DOWN UNTIL REPAIRS ARE MADE. WELDED SAVE-A-VALVE OVER BULLET HOLE.
| 05-16901-1 | 169 | 5.1 | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2005-04-11 | 2005-04-23 | Other | WELDED NEW PIPE SECTION |  |  | WILLOWS | CUT OUT AND REPLACED 179'-6" OF 16" L-169
| 04-30201-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2004-10-21 | 2004-10-28 | Mechanical Repair Fitting - Fitting |  |  |  | SUTTER | CALPINE EE SUSPECT PG+E L-302 OF LEAK NEAR CANAL - PG+E EE VERIFIED WITH FLAME PACK UNIT. INSTALLED 8" LEAK CLAMP
| 04-12801-1 | 128 |  | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2004-10-14 | 2004-10-18 | Other | CAN |  |  | WILLOWS | EMPLOYEE FOUND LEAK WHEN LOCATING GAS LINE FOR FARMER - DEAD VEGETATION. REPLACED WITH 5FT OF PRESTESTED PIPE
[10 empty] | Internal Corrosion |  |  | 2004-10-18 | Replace TP Main |  |  |  |  | REPLACED WITH 5' OF TESTED 4.5" 00X .237WT...SMLS
| 04-19302-1 | 193 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2004-10-05 | 2004-10-13 | Other | CAN |  |  | ORLAND | REPAIRED WITH 45" OF .280...; NOTE PIPE BACK GROUND TO MATCH EXISISTING .156 PIPE
| 04-19301-1 |  |  | 6.625 | Gathering |  | Unknown |  |  | Unknown |  | 2004-02-24 | 2004-03-23 | ABANDON | LEAK SECTION |  |  | ORLAND | LEAK SEXTION RETIRED C/O 6" AT READ 7 TO RETIRE #12-1 LEAK; (SEE ATTACHED FAXED COPY) LEAK SECTION = CUT, CAPPED, PIGGED OUT, INSERTED AND RETIRED. DID NOT EXCAVATE FLOODED FIELD TO PERFORM LEAK INSTPECTION C.B. IDLE PIPELINE RETIRED AND NOT NEEDED.
| 04-19301-1 |  |  | 6.625 | Gathering |  | Unknown |  |  | Unknown |  | 2004-02-24 | 2004-03-24 | ABANDON | LEAK SECTION |  |  | ORLAND | C/O 6" AT RD 7 TO RETIRE 12-1 AND LEAK; C/O AT ROAD 7 TO RETIRE 12-1 AND LEAK. UPRATED 6" TO TP PRESSURE TO FEED HIGH TO HIGH SET.
| 09-16901-1 | 169 |  | 0.5 | Transmission |  | Fitting |  |  | Construction Defect |  | 2009-06-22 | 2009-11-06 | Other | INSTALLED NEW SEALANT TAPE ON BUSHING SOAP TEST "NO LEAKS" | Steel/Wrought Iron |  | CHICO | LEAK WAS ON BUSHING (1/2) ON CONTROLLER (V-20); INSTALLED NEW SEALANT TAPE ON BUSHING- SOAP TEST NO LEAKS
| 09-13601-1 | 136 |  | 0.5 | Transmission |  | Fitting |  |  | Unknown |  | 2009-06-22 | 2009-11-06 | Other | TIGHTENED FITTING SOAP TEST - OK "NO LEAKS" | Steel/Wrought Iron |  | CHICO | TIGHTENED FITTINGS SOAP TEST NO LEAKS
| 09-17701-1 | 177 |  | 1 | Transmission |  | Valves |  |  | Unknown |  | 2009-06-22 | 2009-09-16 | Other | OPERATED VALVE - STEM LEAK STOPPED | Steel/Wrought Iron |  | CHICO | EXERCISED TWO MOST NORTH VALVES IN FRAME AND COVERS ON THE NORTH EAST CORNER OF FELL STATION LEAKS STOPPED. 9-16-09
| 09-17702-1 | 177 |  | 0.25 | Transmission |  | Fitting | Valves |  | Other |  | 2009-06-22 | 2009-09-16 | Other | TIGHTENED FITTING - EXERCISED VALVE | Steel/Wrought Iron |  | CHICO | EXERCISED VALVE AND TIHGTENED 1/4" TUBE FITTING. SOAP TEST. NO LEAKS
| 09-30201-1 | 302 |  | 6 | Gathering | PRODUCER LINE |  |  |  | Internal Corrosion |  | 2009-03-08 | 2009-03-27 | Other | PLIDCO CLAMP | Steel/Wrought Iron |  | MERIDIAN | THIS PIECE OF PIPE IS STRANDED AND IS USED BY ATLANTIC OIL AS A SUCTION LINE (20PSI). THIS WAS A GRADE 1 LEAK IN THE MIDDLE OF A BEAN FIELD. PRODUCER ISOLATED PIPE TO MAKE SAFE. REPAIR DATE IS 3-27-09 TO INSTALL PLIDCO CLAMP. PIPELINE IS ON GATHERING LIST FOR SALE TO ATLANTIC OIL.; LEAK IS LOCATED 90 YARDS EAST OF TARKE RD. AND 69 YARDS N/E OF WELL PAD.
| 09-30202-1 | 302 |  | 8 | Gathering |  | Valves |  |  | Other | O-RINGS | 2009-03-31 | 2009-04-03 | Other | REPLACE SHAFT O-RINGS (STEM); | Steel/Wrought Iron |  | GRIMES | SEE PAGE 3 COMMENTS FOR REPAIRS; V-82 LEAK REPAIRED BY INSTALLING NEW O-RINGS ON GLAND PLATE AT THE STEM. REPAIRED AND CUBED STEM- ALL OK AT THIS TIME. REPAIRED BY DFA2/RJWG 4-3-09 FIELD CHECKED.
| 09-30203-1 | 302 |  | 20 | Gathering |  | Body of Pipe | Other | INTERNAL CORROSION | Internal Corrosion |  | 2009-04-20 | 2009-05-29 | Replace TP Main | INSTALL NEW DRIP | Steel/Wrought Iron |  | GRIMES | REPLACED 20" DRIP PIPE; REPLACED ENTIRE DOWNSTONE DRIP STATION ON PM# 30709311. SEE AS BUILT FOR DETAILS.
| 08-30205-1 | 302 |  | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-12-03 | 2008-12-10 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | DUNNIGAN
| 08-31804-1 |  |  | 6.25 |  |  | Unknown |  |  | Internal Corrosion | UNKNOWN | 2008-06-09 |  |  |  | Steel/Wrought Iron |  | ORLAND | SEE GAS OPERATIONAL CHANGE NOTICE; SEE GAS OPERATION CHANGE NOTICE ATTACHED,
| 08-16902-1 | 169 |  | 1 | Transmission |  | Valves |  |  | Other | VALVE; | 2008-06-05 | 2009-09-23 | Other | SEALED CONDUITS IN SPLICE BOX FOR V-20 | Steel/Wrought Iron |  | CHICO | SEALED CONDUITS FOR V-20 SPLICE BOX.
| 08-17701-1 | 177 |  | 0.25 | Transmission |  | Fitting | Valves |  | Other |  | 2008-06-05 | 2009-09-16 | Other | TIGHTENED FITTING - EXERCISED VALVE | Steel/Wrought Iron |  | CHICO | EXERCISED VALVE AND TIGHTENED 1/4" TUBE FITTING, SOAP TEST- NO LEAKS.
| 08-31803-1 | 318 |  | 6.25 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-04-30 | 2008-06-03 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | ORLAND | INSTALLED 6" PLIDCO SPLITT SLEEVE OVER PIN HOLE. ; 6" STEEL L-318 36'6" E/O V-6 SOAP & 100 PSI
| 08-31802-1 | 318 |  | 6.25 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-04-30 | 2008-06-04 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | ORLAND | INSTALLED 6" PHIDCO SPLIT SLEEVE OVER PIN HOLE ; 6" STEEL L-318 SOAP @ 100 PSI
| 08-30203-1 | 302 |  | 12 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-07-02 | 2008-07-16 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | GRIMES | INSTALL 70" CAN WITH SAV-A-VALVE
| 08-30203-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-07-02 | 2008-07-16 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | GRIMES | INSTALLED 70" CAN WITH SAV-A-VALVE
| 08-31803-1 | 318 |  | 4 | Gathering |  | Unknown |  |  | Unknown |  | 2008-04-30 | [5 empty] | ORLAND | SEE GAS OPERATIONAL CHANGE NOTICE; SEE GAS OPERATIONAL CHANGE NOTICE ATTACHED
| 08-31804-1 | 318 |  | 6 |  |  | Unknown |  |  | Internal Corrosion | UNKNOWN | 2008-06-09 |  |  |  | Steel/Wrought Iron |  | ORLAND | SEE GAS OPERATIONAL CHANGE NOTICE; SEE OPERATIONAL CHANGE NOTICE ATTACHED
| 08-30204-1 | 302 |  | 6.25 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-06-03 | 2008-06-11 | Other | CUT & CAP | Steel/Wrought Iron |  | MERIDIAN | CUT-CAP 6" @ V.55 TO ABANDON 5-2 ; GAS WELL DUE TO LEAK
| 08-30202-1 | 302 |  | 3 | Gathering |  | Body of Pipe |  |  |  |  | 2008-05-27 | 2008-05-30 | Deactivate #TP Main | CUT AND CAP 3" | Steel/Wrought Iron |  | GRIMES | CAP WITH SAV-A-VALVE AT 20" AND CUT OFF RISER 24" BELOW GROUND. ; CUT OFF AND ABANDONED APPROX. 2,420' OF 3" T.P. STL MAIN
| 08-30201-1 | 302 | 22.5 | 6.625 | Transmission |  | Body of Pipe | Other | DIG-IN 3RD PARTY |  |  | 2008-02-29 | 2008-03-01 | Replace TP Main |  | Steel/Wrought Iron |  | SUTTER | SEE ATTACHED; CONTRACTOR DUG INTO PIPE AREA NOT LOCATED BY LOCATOR; LOCATOR DID NOT MARK OR LOCATE PIPELINE.
| 08-16901-1 | 169 | 2.08 | 12.75 | Transmission |  | Body of Pipe | Valves |  |  |  | 2008-03-31 | 2008-04-01 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | GLENN | FARMER WAS DIGGING OUT BOTTOM OF DITCH WITH A V-DITCHER PLOW WHEN HE STRUCK STEEL MAIN CAUSING THE LEAK; FARMER DID NOT CALL IN USA FOR AREA HE WAS WORKING
| 08-31801-1 | 318 |  | 6.5 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-02-08 | 2008-02-09 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | ORLAND; | FOUND PIN HOLE IN BOTTOM OF PIPE; REPAIRED BY INSTALLING 24" CAN OF PRETESTED EMERCOENEY STOCK
|  | 177 |  | 10 | Transmission | [6 empty] | 1984-09-20 | 1984-10-08 | Other |  | Steel |  | CORNING
|  |  |  | 8.62 | Gathering |  | Other |  |  | Other |  | 2004-11-26
|  |  |  | 2.38 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | ABOVE GROUND TIE-IN TO PRODUCERS SCRUBBERS AT SHUEU #1 PAD. TIED-IN TO 2" VALVE
|  |  |  | 3 | [11 empty] | Steel |  | WEST OF ORLAND
|  |  |  | 4 | [11 empty] | Steel |  | GRIMES
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
Steel
|  |  |  | 20 | [11 empty] | Steel
10 |  |  |  | 16 | Transmission | [8 empty] | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CHICO | INLET RUN TO DEHYDRATION TOWER.
10 |  |  |  | 12.75 | Transmission | [8 empty] | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CHICO | INLET RUN TO DEHYDRATOR TOWER.
10 |  |  |  | 12.75 | Transmission | [8 empty] | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CHICO | INLET RUN TO DEHYDRATOR TOWER.
|  | 169 |  | 3.5 | [11 empty] | Steel |  | WILLOWS
|  | 169 |  | 12.75 | [11 empty] | Steel |  | GLENN COUNTY
|  |  |  | 3 | [11 empty] | Steel |  |  | TIE IN 4" MAIN.
|  |  |  | 4 | [11 empty] | Steel |  | ORLAND | PIPE EXPOSED FOR 4" TIE IN GM4504262-1124-04
|  |  |  | 3 | [11 empty] | Steel |  | WILLOWS
|  | 193 |  | 4 | [11 empty] | Steel |  |  | TIE-IN LOCATIONF FOR HARDIN 1-17
|  | 193 |  | 4 | [11 empty] | Steel |  |  | TIE IN 4' L193 EAST OF MALTON 14-1
|  |  |  | 3 | [11 empty] | Steel |  | WILLOWS; | CONNECT KNIGHT #2. TIE IN- BECHIVE FIELD; GM 4504353
|  |  |  | 8 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel |  | GRIMES
|  |  |  | 2 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  | 169 |  | 4 | [11 empty] | Steel
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 3 | [11 empty] | Steel |  |  | NEW 6 LINE GN4556766
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 3 | [11 empty] | Steel
|  | 400 |  | 3
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel |  | WILLOWS
|  |  |  | 3.5 | [11 empty] | Steel |  | GLENN CO.
|  |  |  | 4.5 | [11 empty] | Other | GRB
|  |  |  | 4 | [14 empty] | TIE CUT OFF
|  |  |  | 3.5 | [11 empty] | Steel
|  |  |  | 20 | [11 empty] | Steel |  |  | DURING PUBLING OPERATION OF NEW INSTALLATION A LARGE AMOUNT OF WATER WAS DRAWN FROM 20"
|  |  |  | 20 | [11 empty] | Steel |  |  | DURIG PUBLING OPERATIONS OF NEW INSTALLATIONS A LARGE AMOUNT OF WATER WAS DRAWN FROM 20."
| 97-30206-1 | 302 |  | 8.625 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-06-21 | 1997-06-21 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | GRIMES | CUT OFF MAIN, INSTALL 8" CAP AT VALVE
|  |  |  | 8 | [11 empty] | Steel
|  |  |  | 12 | [11 empty] | Steel |  |  | 12" S/SIDE DOGLEG TIE IN
|  |  |  | 12 | [11 empty] | Steel |  |  | TIE IN 12" N/SIDE DOG LEG
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel |  |  | TIE IN TO GOMES #1 GAS WELL.
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 12 | [11 empty] | Steel
|  |  |  | 12 | [11 empty] | Steel
|  | 302 |  | 8.625 | [11 empty] | Steel |  |  | TIE IN GRMSTRONG 17-1 TO 8" LINE 302 S/SIDE WHITE RD.
|  |  |  | 4 | [11 empty] | Steel |  | GRIMES | ISNTALL 3" BALL VALVE.
|  |  |  | 3 | [11 empty] | Steel |  |  | 3" BAS VALVE INST.
[16 empty] | Steel |  |  | AT. 6" TIE FOW ARBCKLE RD. #34 GAS WELL.
|  |  |  | 4.5 | [11 empty] | Steel |  | GRIMES | 3' BAS VALVE ISNT.L EXPOSED AT ARBUCKLE #20 TIE ON 6"
|  |  |  | 4.5 | [11 empty] | Steel |  |  | ARBUCKLE RD. #14 AT 4 TO 6" TIE
|  |  |  | 6 | [11 empty] | Steel |  |  | AT VALVE 267 ROUND STONE RD.
|  |  |  | 6 | [11 empty] | Steel |  |  | LOCATION EXPOSED: AT TEST #2 - ARBUCKLE RD #13 GAS WELL AT BURIED VALVE.
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel |  |  | LOCATION: -ARBUCKLE RD. #18 GAS WELL AT RISON
|  |  |  | 6 | [11 empty] | Steel |  |  | AT 6" TIE W/O ARBUCKLE RD. #13
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 3 | [11 empty] | Steel
Steel
|  |  |  | 3.5 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel |  |  | ;
|  |  |  | 2 | [11 empty] | Steel
|  |  |  | 3.5 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel |  |  | 6" MAIN VALVE 110 GO BACK PIECE 10' E/O VALVE 110
|  |  |  | 6 | [11 empty] | Steel |  |  | V-311 TO AR-6 GAS WELL. INSPECTION
|  | 302 |  | 6 | [11 empty] | Steel |  |  | INSPECTION 6" L-302 VALVE 243
|  |  |  | 4 | [11 empty] | Steel |  |  | BROWNING WELL #2 TIE AT 6" MAIN
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 3 | [11 empty] | Steel |  |  | INSPECTION RISON, LOCATION AT BROWNING GAS WELL #4
|  |  |  | 6 | [11 empty] | Steel |  |  | INSPECTION, ABANDONED V-224 AT ABANDONED AN-1 GAS WELL S/O V-243
|  | 302 |  | 6 | [11 empty] | Steel |  |  | INSPECTION, 6" L-302 TO AN-3 GAS WELL AND 4" L-302 SOUTH TO AN-8 GAS WELL SHEET 3 OF 4
|  |  |  | 6 | [11 empty] | Steel |  |  | INSPECTION, INSTALLED AND REMOVED 6" TEST HD FOR TEST #5 S/P V-245
|  | 302 |  | 4 | [11 empty] | Steel |  |  | INSPECTION, INST'D AND REMOVED 4" TEST HD FOR TEST 8 4" l-302 TO AN-6 GAS WELL
|  |  |  | 4.5 | [11 empty] | Steel |  |  | INSPECTION, INST'D AND REMOVED 4" TEST HD FOR TEST 9 TO ANDREOTTI 10-A GAS WELL
|  | 302 |  | 6 | [11 empty] | Steel |  |  | INSPECTION 6" L-302 AT VALVE 270
|  |  |  | 4 | [11 empty] | Steel |  |  | HOLE AT CARTER RANCH ON RIVER RD.
|  |  |  | 3 | [11 empty] | Steel |  |  | HOLE ON RIVER WHERE CARTER #2 OF 3 GAS WELLS TIE IN
|  |  |  | 4 | [11 empty] | Steel |  |  | HOLE S/ EAST OF ...GAS WELL
|  |  |  | 4 | [11 empty] | Steel |  |  | HOLE OUT IN FIELD WEST OF COMPTON LANDING STATION
|  |  |  | 6 | [11 empty] | Steel |  |  | HOLE AT COMPTON LANDING STATION
|  |  |  | 6 | [11 empty] | Steel |  |  | HOLE ON S/END COMPTON LANDING...
|  |  |  | 6 | [11 empty] | Steel |  |  | HOLE AT N/END OF COMPTON LANDING...
|  |  |  | 4 | [11 empty] | Steel |  |  | HOLE ACROSS ST. FROM MARIN PRINDLE
|  | 172 |  | 4 | [11 empty] | Steel |  |  | HOLE AT INTERSECTION CORD W.W. & CORP GE
|  |  |  | 2 | [11 empty] | Steel |  |  | HOLE AT RISON MARIN PRINGLE #2
|  |  |  | 4 | [11 empty] | Steel |  |  | CO. RD. AT VALVE #112
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel |  |  | GM 4811493- CONNECT SILLER 1-20 GAS WELL
RISER C/O...CAPPED
REMOVED 3' SECTION
|  |  |  | 4 | [11 empty] | Steel |  | WOODLAND
|  |  |  | 4 | [11 empty] | Steel |  | WOODLAND
|  |  |  | 4 | [11 empty] | Steel |  | WOODLAND
|  |  |  | 6 | [11 empty] | Steel |  |  | CONNECT HEIKEN #1 GAS WELL GM 468874-3
|  |  |  | 10 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 6.5 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 2 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel-Other
|  |  |  | 2 | [11 empty] | Steel
|  |  |  | 2 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 2 | [11 empty] | Steel
|  |  |  | 2 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 2 | [11 empty] | Steel
|  |  |  | 2.375 | [11 empty] | Steel
|  |  |  | 8 | [11 empty] | Steel
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 3 | [11 empty] | Steel
|  | 302 |  | 8 | [11 empty] | Steel
|  |  |  | 8 | [11 empty] | Steel
|  | 302 |  | 4 | [11 empty] | Steel
|  | 302 |  | 8 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel |  |  | HOLE ON NORTH SIDE VALVE #131
|  |  |  | 4 | [11 empty] | Steel |  |  | HOLE ON 4" E/O VALVE 132 HWY 45.
|  |  |  | 6 | [11 empty] | Steel |  |  | HOLE AT END OF TEST #7.
|  | 302 |  | 8 | [11 empty] | Steel |  |  | HOLE ON 8" LINE 302 W/E TEST #2
|  |  |  | 8 | [11 empty] | Steel
|  |  |  | 8 | [11 empty] | Steel
|  | 302 |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 8 | [11 empty] | Steel |  |  | REPLACE 8" MAIN W/ 4" PIPE
|  |  |  | 8 | [11 empty] | Steel |  |  | REPLACE 8"MAIN W/ 4" PIPE
|  |  |  | 6 | [11 empty] | Steel |  |  | GM 4688883/BALSDON #9
|  |  |  | 3 | [11 empty] | Steel |  |  | GM4688966
11 | 95-30225-1 | 302 |  | 6 | Service |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-09-07 | 1995-09-14 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | UNABLE TO FIND ANY LEAKS. DID SMELL SOME UNUSUAL ODORS THAT COULDN'T BE EXPLAINED. NO REPAIRS MADE.
11 | 95-30226-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-12-18 |  | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES
11 | 96-30206-1 | 302 | [9 empty] | 1996-03-15 | [5 empty] | S/O GRIMES
11 | 96-30207-1 | 302 | [9 empty] | 1996-03-19 | [5 empty] | GRIMES
11 | 96-30208-1 | 302 |  | 6.62 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-03-21 | 1996-03-26 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPAIRED WITH 21" - .219 PCE TESTED PIPE
11 | 96-30209-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-04-29 | 1996-04-30 | Replace Pipe |  | Steel/Wrought Iron |  | S/E OF MERIDIAN | REPAIRED WITH 24" .219 PRETESTED PIPE GM - 1289834
11 | 96-30210-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-04-30 | 1996-04-30 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPAIRED WITH 26" .188 WT PRETESTED PIPE GUN 119398-6
11 | 96-30211-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-04-30 | 1996-04-30 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPAIRED WITH 30" .188 WT PRETESTED PIPE GUN 119398-6
11 | 96-30213-1 | 302 |  | 12.75 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-06-26 |  | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES
11 | 96-30215-1 | 302 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-10-05 | 1996-10-22 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPAIR 12" W/ 75" .312 WT TESTED ON GM 1287325
11 | 96-30216-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-10-09 | 1996-10-10 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPAIR LEAK W/ 25" .219 WT PRETESTED PIPE #119398-6
11 | 96-30217-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-10-09 | 1996-10-10 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPAIR LEAK W/ 56" OF PRETESTED PIPE #119398-6
11 | 97-30201-1 | 302 |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-02-19 |  | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN
11 | 97-30202-1 | 302E |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-02-24 |  | Replace Pipe |  | Steel/Wrought Iron |  | S/O MERIDIAN
11 | 97-30203-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-03-26 |  |  |  | Steel/Wrought Iron |  | COLUSA
| 97-30204-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-04-15 | 1997-10-03 | Other |  | Steel/Wrought Iron |  | S/O SUTTER | CLOSED V-224 & SCHEDULED FOR RETIREMENT - C. BISH; RETIRED THIS SECTION OF PIPE ON S.O. #700507
| 97-30204-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-04-15 |  | Other |  | Steel/Wrought Iron |  | S/O SUTTER | CLOSED V-224 & SCHEDULED FOR RETIREMENT - C. BISH
11 | 97-30204-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-04-15 |  | Other |  | Steel/Wrought Iron |  | SUTTER | CLOSED V-224 & SCHEDULED FOR RETIREMENT - C. BISH
| 97-30205-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-04-23 | 1997-04-23 | Replace Pipe |  | Steel/Wrought Iron |  | S/O MERIDIAN | REPAIRS REQUIRE 40+ FEET OF DITCH CROSSING WITH SINGLE TRANSPORT WELL. PG&E WILL NOT REPAIR AND DISCUSSIONS STARTED WITH PRODUCER OF NF12-1
| 97-30206-1 | 302 |  | 8.62 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-06-21 | 1997-06-21 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | GRIMES | CUT OFF MAIN, INSTALL 8" CAP AT VALVE
| 97-30211-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-09-23 |  | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES
| 97-30212-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-09-23 |  | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES
| 97-30213-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-09-23 |  | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES
| 98-30204-1 | 302 |  | 4 | [7 empty] | 1998-02-03 | [5 empty] | GRIMES
| 98-30208-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-03-19 |  | Replace Pipe |  | Steel/Wrought Iron |  | S/E OF MERIDIAN
| 98-30209-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-03-19 |  | Replace Pipe |  | Steel/Wrought Iron |  | S/E OF MERIDIAN
| 98-30211-1 | 302 |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-05-05 | 1999-11-04 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | RETIRED ON 11/4/99; SO#6019944; ; CLEAR ME-98-17 REV#1
| 98-30212-1 | 302 |  | 6 | Gathering | [6 empty] | 1998-06-25 |  |  |  | Steel/Wrought Iron |  | MERIDIAN
| 98-30213-1 | 302 |  | 6 | Gathering | [6 empty] | 1998-06-25 |  |  |  | Steel/Wrought Iron |  | MERIDIAN | ;
| 98-30214-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-09-15 | 1998-12-14 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPAIR LEAK ON 4" MAIN - REPLACE 2" SECTION WITH TESTED .237 4"
| 98-30216-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-03-19 |  |  |  | Steel/Wrought Iron |  | GRIMES
| 99-30201-0 | [5 empty] | Body of Pipe |  |  | Internal Corrosion |  | 1999-04-21 | [5 empty] | MERIDIAN
| 99-30201-0 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-04-21 |  |  |  | Steel/Wrought Iron |  | MERIDIAN
| 99-30202-0 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-04-26 | 1999-04-30 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | GRIMES | BUBBLES IN FLOODED RICE FIELD. REPAIRED WITH 6' OF 20" .375 WT STPR #A-1324
| 99-30200-3 | 302 |  | 8 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-05-11 | 1999-08-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | S/O MERIDIAN | REPAIRED WITH 25" .188 WT X 42 PRETESTED PIPE ON GM #496497-9
| 99-302 -3 |  |  | 8 | [7 empty] | 1999-05-11 |  |  |  | Steel-Other |  | S/O MERIDIAN
| 99-30200-4 | 302 |  | 8 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-05-11 | 1999-08-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | S/O/ MERIDIAN | REPAIRED WITH 32" PRETESTED PIPE .188 X 42 GM#496497-9
| 99-302 -4 |  |  | 8 | [7 empty] | 1999-05-11 | [5 empty] | S/O MERIDIAN
| 99-30200-6 | [10 empty] | 1999-07-26
| 99-30200-6 |  |  | 4 | [7 empty] | 1999-07-26 | [5 empty] | GRIMES
| 99-30200-7 | 302 |  | 8 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-08-19 | 1999-08-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | S/E OF MERIDIAN | REPAIRED WITH 23 7/8 .188 WT X 42 PRETESTED PIPE ON GM#496497-9
| 00-30202-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2000-02-29 | 2000-05-18 | Other | 7' PIPE |  |  | COLUSA | BUBBLES IN FLOODED FIELD. REPAIR LEAK WITH 7' .188 WT PRETESTED PIPE #7007086
| 99-302 -5 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-06-07 |  |  |  | Steel/Wrought Iron |  | ; GRIMES | BUBBLES IN FLOODED RICE FIELD. ISOLATED AND BLOWN DOWN.
| 99-302 -5 |  |  | 4 |  |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-06-07 |  |  |  | Steel/Wrought Iron |  | GRIMES | BUBBLES IN FLOODED RICE FIELD. ISOLATED AND BLOWN DOWN.
| 99-302 -5 |  |  | 4 |  |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-06-07 |  |  |  | Steel/Wrought Iron |  | GRIMES
| 00-30205-1 |  |  | 20 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2000-08-16 | 2000-08-17 | Welded Sleeve/Can - Weld |  |  |  | S/O GRIMES | REPLACED WITH 88 3/4" PRETESTED PIPE ; (1/8" PIN HOLE)
| 01-30201-1 | 302 |  | 4 | Gathering | . | Body of Pipe |  |  | Internal Corrosion |  | 2001-03-09 | 2001-03-21 | Other | REPLACED |  |  | GRIMES | BUBBLES IN FIELD CLOSED VALVES TO ISOLATE - PIPING BLOWN DOWN. INSTALLED NEW 3" POP FROM TAP VALVE TO RISER BLOCK VALVE (PROCUREMENT) SO#6077243
| 01-30208-1 |  |  | 3 | Gathering |  | Other Welds |  |  |  |  | 2001-10-09 | 2001-10-09 | Other |  |  |  | S/O MERIDIAN | LEAK ON WELD, GROUND OUT BOTTOM AND REWELDED. XRAY & MAG TEST.
| 01-30213-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-10-16 | [5 empty] | S/O SUTTER | DELETE ; LEAK DISAPPEARED
| 01-30214-1 | 302 |  | 4 | Gathering |  | Body of Pipe | Other |  | Internal Corrosion |  | 2001-10-22 | 2001-11-28 | Other | REPLACED PIPE AROUND WELL PAD |  |  | GRIMES | LEAK FOUND BY FARMER BURNING FIELD * ISOLATED LINE - VISO CLOSED - BLOCK VALVE CLOSED * TURNED IN BY GAS PRODUCER. REPLACED PIPE AROUND PRODUCERS WELL PAD.
|  |  |  | 4 | Gathering |  | Other |  |  | Internal Corrosion |  | 2001-10-22 | [5 empty] | ; GRIMES | LEAK FOUND BY FARMER BURNING FIELDS * ISOLATED LINE - VISO CLOSED - BLOCK VALVE CLOSED * TURNED IN BY GAS PRODUCER.
| 01-30215-1 |  |  | 8 | Gathering |  |  |  |  | Internal Corrosion |  | 2001-10-31 | [5 empty] | SE/O MERIDIAN/SUTTER CO. | DELETE, LEAK DISAPPEARED
| 01-30212-1 |  |  | 3 | Gathering |  | Other Welds |  |  |  |  | 2001-10-09 | [5 empty] | S/O MERIDIAN | CREW FOUND 6X6X3 TEE LEAKING AT 3" WELD (BOTTOM) * REPAIRS TO BE DONE ON 10-21-01
| 02-30201-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-01-10 | [5 empty] | S/O SUTTER | BUBBLES IN FLOODED RICE FIELD.
| 02-30201-1 | 302E |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-01-10 |  | Welded Sleeve/Can - Weld |  |  |  | S/O SUTTER | BUBBLES IN FLOODED RICE FIELD.
| 02-30202-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-03-28 | 2002-04-16 | Other | 56 3/4 OF NEW PIPE | Steel/Wrought Iron |  | GRIMES | PITS IN SECTION, REMOVED, P TIE-IN SECTIONS .090 DEEP
| 02-30205-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-05-08 | 2002-05-30 | Other | CAPPED & RETIRED LEAK SECTION | Steel/Wrought Iron |  | S/E MERIDIAN | DID NOT REPAIR LEAK. RETIRED LEAK PIPING TO MOBIL-WOOD #4-1 S.O.# 7043786
| 03-30201-1 | 302 |  | 6 | [5 empty] | Internal Corrosion | SUSPECT INTERNAL CORROSION | [6 empty] | SUTTER COUNTY
| 03-30202-1 | 302 |  | 6 | [5 empty] | Internal Corrosion | SUSPECT INTERNAL CORROSION | 2003-02-14 | [5 empty] | SUTTER COUNTY
| 03-30203-1 | 302 |  | 6 | [5 empty] | Internal Corrosion | SUSPECT INTERNAL CORROSION | 2003-02-14 | [5 empty] | SUTTER COUNTY
| 03-30204-1 | 302 |  | 6 | Gathering |  |  |  |  | Internal Corrosion | SUSPECT INTERNAL CORROSION | 2003-02-14 | [5 empty] | SUTTER COUNTY
| 03-30205-1 | 302 |  | 6 | Gathering |  |  |  |  | Internal Corrosion | SUSPECT INTERNAL CORROSION | 2003-02-14 | [5 empty] | SUTTER COUNTY
| 03-30206-1 | 302 |  | 8 | [5 empty] | External Corrosion |  | 2003-02-14 | 2003-03-26 | Other | WELD VALVE |  |  | SUTTER COUNTY | WELDED 2" MUELLER SAVA VALVE OVER PIT -- X-RAYED PIT; 3.4" EXTERNAL PIT INSULATED TO ONE SPOT.
| 03-30206-1 | 302 |  | 8 | [5 empty] | External Corrosion |  | 2003-02-14 | [5 empty] | SUTTER COUNTY
| 03-30207-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2003-05-17 | 2003-11-04 | Other | RETIRED |  |  | SW/O GRIMES | ISOLATED AND BLOWN DOWN. PIPE WILL BE RETIRED AT A LATER DATE. V-400 CLOSED PERMANENTLY.; 2 MILES S/W OF GRIMES
| 03-30207-1 |  |  | 6 | Gathering |  | Body of Pipe |  | SUSPECT | Internal Corrosion |  | 2003-05-17 |  | Other | RETIRED |  |  | SW O/ GRIMES | ISOLATED AND BLOWN DOWN PIPE WILL BE RETIRED AT A LATER DATE; 2 MILES S/W OF GRIMES
| 04-30201-1 | 302 |  | 8 | Transmission |  |  |  |  | Internal Corrosion | SUSPECT | 2004-10-21 | [5 empty] | SUTTER/YUBA CITY
| 04-30202-1 |  |  | 6 | Transmission |  |  |  |  | Internal Corrosion | SUSPECT | [6 empty] | SUTTER/ YUBA CITY | EMPLOYER FOUND LEAK DURING FLAME PACK BEFORE EVACUATING LINE FOR PREVIOUS LEAK.
| 05-30202-1 |  |  | 6 | Gathering | SERVICE |  |  |  | Internal Corrosion | SUSPECT | 2005-11-28 | 2005-12-08 | Other | NEW PIPE |  |  | MERIDIAN | BUBBLE NEAR GAS WELL
| 05-30201-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Damage by 3rd Party |  | 2005-04-17 | 2005-04-26 | Other | SAVE-A-VALVE |  |  | SUTTER | WELDED SAVE-A-VALVE OVER BULLET HOLE CASE#1-05-001198 SUTTER CO SHERIFF.
| 05-30201-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Damage by 3rd Party |  | 2005-04-17 | 2005-04-26 | Other | SAVE-A-VALVE |  |  | SUTTER | BULLET HOLE IN PIPE BETWEEN WELL BU#56 AND BU#60. ISOLATED AND BLOWN DOWN UNTIL REPAIRS ARE MADE. WELDED SAVE-A-VALVE OVER BULLET HOLE.
| 06-30201-1 |  |  |  | Gathering | [6 empty] | 2006-01-09 | 2006-01-13 | Tighten Cap or Bolt |  |  |  | GRIMES | AREA FLOODED - BUBBLES NEAR V-402 AND ALCOHOL POT BOX. 2-LEAK REPAIRED - CAP ON GAUGE LINE - PLUG ON ALCOHOL POT.
| 06-30202-1 |  |  | 6.25 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2006-05-30 | 2006-09-27 | Weld Over Sleeve or Can |  |  |  | GRIMES
| 08-30201-1 | 302 | 22.5 | 6.625 | Transmission |  | Body of Pipe | Other | DIG-IN 3RD PARTY |  |  | 2008-02-29 | 2008-03-01 | Replace TP Main |  | Steel/Wrought Iron |  | SUTTER
| 08-30202-1 | 302 |  | 3 | Gathering |  | Body of Pipe |  |  |  |  | 2008-05-27 | 2008-05-30 | Deactivate #TP Main | CUT AND CAP 3" | Steel/Wrought Iron |  | GRIMES | CAP WITH SAVE-A-VALVE AT 20" AND CUT OFF RISER 24" BELOW GROUND. CUT OFF AND ABANDONED APPROX. 2420' OF 2" T.P. STL MAIN.
|  | 302 |  | 3 | Gathering | [7 empty] | 2008-05-30 | Deactivate #TP Main | CUT AND CAP 3" | Steel/Wrought Iron |  | GRIMES | ... CAP WITH SAVA VALVE AT 20" AND CUT OFF RISER 24" BELOW GROUND. CUT OFF AND ABANDONED APPROX. 2420' OF 3" T.P. STL MAIN.
| 08-30203-1 | 302 |  | 12 |  |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-07-02 | 2008-07-16 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | GRIMES | INSTALL 70" CAN WITH SAVA-VALVE.
| 08-30204-1 | 302 |  | 6.25 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-06-03 | 2008-06-11 | Other | CUT & CAP | Steel/Wrought Iron |  | MERIDIAN | CUT & CAP EVSS TO A RAILON E-3 GAS WELL DUE TO LEAK.
| 08-30205-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-12-03 | 2008-12-10 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | DUNNIGAN
| 09-30201-1 | 302 |  | 6 | Gathering | PRODUCER LINE |  |  |  | Internal Corrosion |  | 2009-03-08 |  |  |  | Steel/Wrought Iron |  | MERIDIAN
| 09-30201-1 | 302 |  | 6 | Gathering | PRODUCER LINE |  |  |  | Internal Corrosion |  | 2009-03-08 | 2009-03-27 | Other | PLIDCO CLAMP | Steel/Wrought Iron |  | MERIDIAN | THIS PIECE OF PIPE IS STRANDED AND IS USED BY ATLANTIC OIL AS A SUCTION LINE (20PSIG). THIS WAS A GRADE 1 LEAK IN THE MIDDLE OF A BEAN FIELD. PRODUCER ISOLATED PIPE TO MAKE SAFE. REPAIR DATE IS 3-27-09 TO INSTALL PLIDCO CLAMP. PIPELINE IS ON GATHERING LIST FOR SAIL TO ATLANTIC OIL. LEAK IS LOCATED 89 YARDS EAST OF TARKE RD. AND 69 YARDS N/E OF WELL PAD FRYE 26-1.
| 09-30201-1 | 302 |  | 6 | Gathering | PRODUCER LINE |  |  |  | Internal Corrosion |  | 2009-03-08 | 2009-03-27 | Other | PLIDCO CLAMP | Steel/Wrought Iron |  | MERIDIAN | THIS PIECE OF PIPE IS STRANDED AND IS USED BY ATLANTIC OIL AS A SUCTION LINE (20PSIG). THIS WAS A GRADE 1 LEAK IN THE MIDDLE OF A BEAN FIELD. PRODUCER ISOLATED PIPE TO MAKE SAFE. REPAIR DATE IS 3-27-09 TO INSTALL PLIDCO CLAMP. PIPELINE IS ON GATHERING LIST FOR SAIL TO ATLANTIC OIL. LEAK IS LOCATED 89 YARDS EAST OF TARKE RD. AND 69 YARDS N/E OF WELL PAD FRYE 26-1.;
| 09-30202-1 | 302 |  | 8 | Gathering |  | Valves |  |  | Other | O-RINGS | 2009-03-31 |  |  |  | Steel/Wrought Iron |  | GRIMES
| 09-30202-1 | 302 |  | 8 | Gathering |  | Valves |  |  | Other | O-RINGS | 2009-03-31 | 2009-04-03 | Other | REPLACE SHAFT O-RING (STEM) | Steel/Wrought Iron |  | GRIMES | V-82 LEAK REPAIRED BY INSTALLING NEW O-RINGS ON GLAND PLATE AT THE STEM. REPAIRED AND LUBED STEM. ALL OK AT THIS TIME. REPAIRED BY DFA2/RJWG. 4-3-09. THIS WAS A USED VALVE, INSTALLED ON 4-21-2007. (7065166)
| 09-30203-1 | 302 |  | 20 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2009-04-20 | 2009-05-29 | Replace TP Main |  | Steel/Wrought Iron |  | GRIMES | REPLACED 20" DRIP PIPE; REPLACED ENTIRE PUNDSTONE DRIP STATION ON PM # 3070934. SEE AS-BUILT FOR DETAILS.
| 09-30203-1 | 302 |  | 20 | Gathering |  | Body of Pipe | Other | INTERNAL CORROSION | Internal Corrosion |  | 2009-04-20 | 2009-05-29 | Replace TP Main | INSTALL NEW DRIP | Steel/Wrought Iron |  | GRIMES | REPLACED 20" DRIP PIPE; REPLACED ENTIRE PUNDSTONE DRIP STATION ON PM # 3070934. SEE AS-BUILT FOR DETAILS.;
| 10-30201-1 | 302 | 2.37 | 4 | Gathering |  | Unknown | Other | SUSPECT INTERNAL CORROSION | Internal Corrosion |  | 2010-05-13 | 2010-05-26 | Other | RETIRED | Steel/Wrought Iron |  | GRIMES | 3" BLIND FLANGE INSTALLED.
| 10-30201-1 | 302 | 2.37 | [14 empty] | GRIMES | ISOLATED AND PIPELINE BLOWN FLAT. PIPELINE TO BE RETIRED ON MAY 26, 2010.
| 10-82020- | 302 | 1 | 4 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2010-10-05 | 2010-10-07 | Other | PLIDCO CLAMP | Steel/Wrought Iron |  | GRIMES | GTLS - PHASE 1. LEAK FOUND BY HELICOPTER SURVEY; LEAK FOUND BY HELICOPTER PATROL. REPAIRED BY INSTALLING PLIDCO CLAMP. CLEARANCE # ME-10-05 ON 10-7-10. CLAMP INSTALLED.
96 | 11-22002-B | 302 |  | 0.75 | Gathering |  | Body of Pipe |  |  | Internal Corrosion | ON 3/4" | 2011-04-06 | 2011-04-15 | Deactivated Partial Service |  | Steel-Other |  | MERIDIAN | CUT OFF 3/4 PIPE 24" LONG WITH LEAK AND CAPED; SOAP TEST AT LINE PRESSER WHEN CAP ON 3/4 COOLS - CUT OFF 23" OF 3/4 OLD SERVICE LEAK WAS ON BODY OF 3/4" PIPE. DIDN'T REMOVE WRAP ON 4" MAIN INSTALL 3/4" SOCKET WELD CAP 300 LB PRESSER RATING
11 | 93-3021- | 302 | [9 empty] | 1993-01-08 | [5 empty] | GRIMES | LEAK NOT REPAIRED. PIPELINE WAS ABANDONED ON WO436638. PIPELINE DID NOT OPERATE AFTER LEAK WAS FOUND.
|  |  |  | 3.5 | [11 empty] | Steel |  | GRIMES
11 | 93-3022- | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-01-10 | 1993-01-10 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | WEST OF ARMSTRONG 17-1 ON THE SOUTH SIDE OF WHITE ROAD APPROX. 1/2 MILE E/OF...; INSTALLED 4" OF 8" .188 WALL PRETSTED PIPE TO REPAIR LEAK
11 | 93-30203- | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-01-21 | 1993-01-22 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN; | S/S OF S. BUTE RD. 1584' E/O HAGMAN RD. MERIDIAN.; REPLACED 6' OF 4" PIPE PRETESTED DM 4044582
11 | 93-3024- | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-01-22 | 1993-04-22 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | E/OF BUTTE SLOUGH RD. N/OF SCIORTINO 1-33 GAS WELL; REPLACED 42" OF 8" .219 PRETESTED PIPE TO REPAIR LEAK; FIELD SHUT-IN FOR EXTENDED TIME DUE TO HIGH WATER FROM SAC. RIVER
11 | 93-3025- | 302 |  | 6.25 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-01-27 | 1993-01-28 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | E/S WELL RD 1050' N/O ANDROETTI #8 GAS WELL; INSTALLED 2 F OF 6" .219"WT 60011056-TESTED
11 | 93-3026- | 302 |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-02-02 | 1993-02-02 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | 3" L-302 1500' S/OF WOOD 1-2 GAS WELL; INSTALLED 26" OF 3" .156 WALL PRETESTED PIPE
11 | 93-3027- | 302 |  | 6.62 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-02-01 | 1993-02-01 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | SAME AS ABOVE; REPLACED WITH 2FT OF PRETESTED 6" ON GM 496531-5
11 | 93-3028- | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-02-12 | 1993-02-12 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | SOUTH SIDE OF WHITE ROAD WEST OF ARM 17-1 GAS WELL; INSTALLED 40" OF 8" .188 WALL TO REPAIR LEAK
11 | 93-3029- | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-02-25 | 1993-02-25 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | 600' NORTH OF STEIDLMATER 6-2a GAS WELL; INSTALLED 47" OF 6" .188 WALL PIPE TO REPAIR LEAK GM4045183
11 | 93-30210- | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-03-10 | 1993-03-10 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | S/OF V-243 ON E/SIDE FARM ROADL ISNTALLED 34" OF 6" .188 WALL TO REPAIR LEAK
11 | 93-30211- | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-03-13 | 1993-03-13 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | 6" L-302 3/8MILE E/OF VALVE 3.64; INSTALL 38" OF 6" .188WALL ...TO REPAIR LEAK
11 | 93-30212- | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-03-17 | 1993-03-17 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | 800' N/OF MARONI RD NEAR 33-34-2 GAS WELL; ISNTALLED 29" OF 4" .188 WALL TO REPAIR LEAK
11 | 93-30213-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1993-05-12 | 1993-05-19 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | 6" L-302 235' S/O VALVE #371 GRIMES GAS FIELD; INSTALLED 2'-7" OF PRETESTED 6.625 OD X 0.219" WT API SLX GR X - 42 ERW TO REPAIR LEAK
11 | 93-30214-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-07-21 | 1993-07-22 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | SOUTH SIDE OF S. BUTTE ROAD 4400FT E/OF HAGMAN RD.; REPLACED ONE FOOT WITH PRETESTED PIPE (4" .188) SMALL PIN HOLE ON BOTTOM
11 | 93-30215-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-07-26 | 1993-07-28 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | 4" LINE 1737 FT. W/O HWY 45 ON MORRIS ROAD 567 FT W/O RISER ON MOBILE G007-4; REPLACE LEAKING PIPE WITH 35" OF 4" OD X 0.188 PRETESTED PIPE
11 | 93-30216-1 | 302 |  | 10 | Gathering |  | Body of Pipe |  |  | Other | C | 1993-07-27 | 1993-07-27 | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER | 10" L-302 3500' W/O VALVE 46; REPLACE LEAKING PIPE WITH 34" OF 10.750" OD X 0.219" WT API SLX X-52 ERW PRETESTED PIPE; GRIMES AREA COLLECTION SYSTEM FRANKLIN RD. 2 MILES W/O ACACIA AVE. 4 MILES S/W OF SUTTER- SUTTER COUNTY.; REPLACED LEAKING PIPE WITH 34" OF PRETESTED 10.750" OD X 0.219" X-52 ERW PRETESTED STEEL PIPE. PIPE FROM PRETESTED EMERGENCY PIPE MERIDIAN S.C.
11 | 93-30217-1 | 302 |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-07-28 | 1993-08-04 | Other |  | Steel/Wrought Iron |  | MERIDIAN | 3" LINE 302 1/2 MI. SO./OF WOOD #1-3 GAS WELL; ABANDONED PIPE ON WO 442348;
11 | 93-30218-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-08-24 | 1993-08-24 | Replace Pipe |  | Steel/Wrought Iron |  | COLUSA CO. | 1000 FT. NORTH OF ANDROTTI #8 WELL ON DIRT ROAD AND SOUTH OF CONCRETE IRRIGATION DITCH; REPLACED 24" OF MAIN W/ 6" .219 PRETESTED PIPE
11 | 93-30219-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-09-09 | 1993-09-13 | Replace Pipe |  | Steel/Wrought Iron |  | COLUSA CO. | 300' SOUTH OF REG. BOARD #1 GAS WELL ON b LINE 302; REPLACED 35" OF 3" TO REPAIR LEAK. REPLACED WITH 8" .219 PRETESTED PIPE. API SL X 42 ERW
11 | 93-30220-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-10-25 | 1993-10-26 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | E/SIDE OF HWY 45____________' NORTH OF WHITE RD. 3160' S/O ROAD XING HWY45; REPLACED LEAK WITH 30" OF 6" .219... PRETESTED PIPE
11 | 93-30221-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-11-15 | 1993-11-16 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | 1262' E/O FARMLAND ROAD ... N/O...HWY 20; REPLACED 24" OF 6" PIPE W/ 24" OF PRETESTED PIPE..X-RAY WELDS
11 | 93-30222-1 | 302 |  | 3.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-11-26 |  | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER | 112 MILE WEST OF...HWY20; REPLACED LEAK WITH 24" OF 3 1/2" PRETESTED PIPE.
11 | 93-30223- | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-12-16 | 1993-12-17 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | SOUTH SIDE OF WHITE ROAD 1/2M WEST OF HWY 45 IN RICE FIELD.; REPLACED 36" WITH .219 PRETESTED PIPE
11 | 94-16701-1 | 167 |  | 6.625 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-02-03 | 1994-02-08 | Replace Pipe |  | Steel/Wrought Iron |  | PRINCETON | 6" LINE 167 APPROX 400FT. S/O BOUNDE CREEK 1-8; INSTALLED 44" OF 6.625 X 0.219 TO REPAIR LEAK
11 | 94-3021- | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-02-04 | 1994-02-09 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | 500FT. NORTH OF TISDALE RANCH #1- WELL S/O OSWALD ROAD AND W/O PROGRESS RD.; INSTALLED 40" OF 6.625" 0.219 TO REPAIR LEAK.
11 | 94-30203-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-03 | 1994-04-05 | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER | 8" LINE 302 1/2 MILE WEST OF V-46 ON FRANKLIN RD.; WILL MOUNITOR AND PREPARE JOB FOR PIPELINE REPLACEMENT. REPAIRS WITH NEW PIPE GM4168977-B 8" 8.625 API SLX X46
11 | 94-30203-1 | 302 |  | 10 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-03 | 1994-04-05 | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER | 10" LINE 302 1/2 MILE WEST OF V-46 ON FRANKLIN ROAD; WILL MONITOR AND PREPARE JOB FOR PIPELINE REPLACEMENT. rEPLACE WITH NEW PIPE GM 4168977-8 10" .219 WALL API SL X52
11 | 94-30204-1 | 302 |  | 10 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-03 | 1994-04-05 |  |  | Steel/Wrought Iron |  | SUTTER | 10" LINE 302 1/2 MILE WEST OF V-46 ON FRANKLIN RD.; WILL MONITOR AND PREPARE JOB FOR PIPELINE REPLACEMENT. REPLACE WITH NEW PIPE GM 4168977-8 10.750" .219 WALL API SL X52
11 | 94-30205-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-07 | 1994-03-08 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | SOUTH SIDE OF S. BUTTE RD. 107 FEET EAST OF HAGMAN RD.; INSTALLED 2' OF 4" PRETESTED PIPE .188 WALL
11 | 94-30206-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-07 | 1994-03-08 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | 4" L-302. SOUTH SIDE OF S. BUTTE ROAD NEXT TO DRAINAGE DITCH. LOCATED ON WEST SIDE OF FIRTST HOUSE TRAVELING RD. 1310 FEET EAST OF HAGMAN RD.; INSTALLED 2' OF PRETESTED 4" .188 WALL
11 | 94-30207-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-07 | 1994-03-08 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | 4" L-302. SOUTH SIDE OF S. BUTTE RD. APPROX 360FT WEST OF MERIDIAN 2-1 GAS WELL 4282 FEET EAST OF HAGMAN RD.; ISNTALLED 2' OF PRETESTED 4" .188 WALL
11 | 94-30208-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-07 | 1994-03-09 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | 4" L-302. 100 YEARDS SOUTH OF HAWKINS #17-1 WELL; INSTALLED 2' OF 4" PRETESTED .188 WALL PIPE.
11 | 94-30209-1 | 302 |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-11 | 1994-03-15 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | 4" L-302 ON MORRIS RD. 1287 FEET FROM RISM RISER VALVE AT GOV. 7-4; INSTALLED 48" OF 4" .188WALL PRETESTED PIPE
11 | 94-30210-1 | 302 |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-11 | 1994-03-15 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | 4" L-302 ON MORRIS ROAD 1040 FEET FROM RISER VALVE AT GOV. 7-4; INSTALLED 24" OF 4" .188 WALL PREATESTED PIPE
11 | 94-30211-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-15 | 1994-03-16 | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER | 6" L-302 ON PASS ROAD... 845 FEET WEST OF V-345; INSTALLED 3' OF 6" .188 PRETESTED PIPE
11 | 94-30212-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-22 | 1994-04-13 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | SAME AS ABOVE, WHITE RD.; CUT OUT AND REPLACED 36" OF 8" PIPE WITH PRETESTED PIPE.
11 | 94-30213-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-04-07 | 1994-04-11 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPLACED 3' OF PINS W/ PRETESTED PIPE TO REPAIR LEAK.
11 | 94-30214-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-04-29 | 1994-04-11 | Replace Pipe |  | Steel/Wrought Iron |  | COLUSA | 142 FEET E/O V-403 NEAR HENSHAW #1 WELL LOCATED 1 MILE N/O HWY 20; ISOLATED AND BLOW DOWN ON 4/29/1994; INSTALLED 12' 3" OF PRETESTED 6" .188 WALL PIPE (REPLACED W/#94-30215-1 4/11/94)
11 | 94-30215-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-05-02 | 1994-05-02 | Replace Pipe |  | Steel/Wrought Iron |  | COLUSA | 138 FEET E/O V-403 NEAR HENSHAW #1 WELL LOCATED 1 MILE N/O HWT20 (FOUND WHEN PRESSURING UP FOR SOAP TEST); INSTALLED 12'3" OF PRETESTED 6" .188 WALL PIPE (REPAIRED W/ 94-302-16/94-302-14)
11 | 94-30216-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-05-02 | 1994-05-02 | Replace Pipe |  | Steel/Wrought Iron |  | COLUSA | 147 FEET E/O V-403 NEAR HENSHAW #1 WELL LOCATED 1 MILE N/O HWY 20 (FOUND WHEN PRESSURIZING UP FOR SOAP TEST).; INSTALLED 12'3" OF PRETESTED 6" .188 WALL LINE (REPLACED W/ #94-302-15/94-302-14)
11 | 94-30217-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-05-04 | 1994-05-17 | Replace Pipe |  | Steel/Wrought Iron |  | COLUSA | 700 YDS NORTH OF SCIORINTINO 33-1 MOON BEND (S/O JUNGLE AREA). CLOSED VALVES 148 & 145 FOR ISOLATION GM 4168837 INSTALLED 3914 FEET OF NEW 4" L-302 AND ABANDONED 3842 FEET OF 8" L-302. THE NEW PIPE REPLACED THE LEAK SECTION.
11 | 94-30218-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-05-04 | 1994-05-10 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | CLOSED V-72 TO ISOLATE AND BLOW DOWN,; INSTALLED 26" X 4" NEW PRETESTED PIPE .188" API 5LX 42 ERW
11 | 94-30219-1 | 302 |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-05-05 | 1994-05-10 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | 4" L-302 APPROX 50 YDS N/O V-407 ON HADEMAN BOARD S/O HWY 20. CLOSED V-150 ISOLATE & BLOWDOWN. INSTALLED 38" X 4" NEW PRETESTED PIPE .188" API SLX 47 ERW
11 | 94-16702-1 | 167 |  | 6.625 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-05-19 | 1994-05-19 | Replace Pipe |  | Steel/Wrought Iron |  | PRINCETON | 6" L-167 APPROX 50 FEET N/O WELL PAD OF BOUNDE CREEK MM #1-8. REPLACED 3' OF 6" MAIN TO REPAIR LEAK W/3' OF PRETESTED 6" .188WALL PIPE.
11 | 94-16901-1 | 169 |  | 6.625 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-05-20 |  | Replace Pipe |  | Steel/Wrought Iron |  | WILLOWS | 200FT. N/O MC BURNEY #57-1 BETWEEN ROAD #45 AND HWY 162. EXCAVATED AND CLOSED V-329 6" L-169. NO LEAK AT SAID LOCATION ABOVE. 36' COVER AT VALVE #329
11 | 94-30220-1 | 302 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-06-10 | 1994-06-22 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | 12" L-302 AS ABOVE. REPLACED 9' 2" OF 12" W/ 9'2" OF PRETESTED .250 WALL.
11 | 94-30221-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-06-10 | 1994-06-23 | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER | BELOW RISER VALVE AT 14-1 WELL. INSTALLED NEW RISER AND 11' OF PRETESTED 4" PIPE.
11 | 94-30222-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-06-22 | 1994-06-23 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | MORROW RD. W/O DREXLER RD (277") CLOSED V-54 & 439 AT WOOD RD. USA #197115. iNSTALLED 2" OF 4" PRETESTED PIPE.
11 | 94-30223-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-06-29 | 1994-07-01 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | 287 FEET NORTH OF V-443 E/S OF GRIMES ARBUCKLE RD. THIS JOB GM 1998343. REPLACED 185' OF 6" .188 W/ 185' OF 6" .219 WALL PRETESTED PIPE (TESTED ON GM 4045100 5-2-94)
11 | 94-30224-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-06-30 | 1994-07-12 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | .4 MILE EAST OF V-190 MORRIS ROAD. INSTALLED 2' OF 4" .188" WALL PRETESTED PIPE.
11 | 94-30225-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-07-18 | 1994-07-20 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | FRANKLIN ROAD APPROX 100 FT. E/O ATLANTIC #1 MM (IN REG. DIST. DITCH). REPLACED 52' OF 6" WITH 52' OF 3" .219 WALL AND 1' OF 6" .219 WALL TO REPAIR LEAK GM 1998426
11 | 94-30226-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-07-21 | 1994-07-27 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | .2 MILE WEST OF HWY 45 ON MORRIS ROAD (WELL GOV. 7-4). INSTALLED 70" OF PRETESTED 4" .188 WALL PIPE TO ELIMINATE LEAK.
11 | 94-30228-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-08-30 | 1994-08-31 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | DREXLER 88 FEET WEST OF HWY 20 -N/S OF HWY 20. REPLACED 5' W/ .88" WALL 6" PRETESTED PIPE TO REPAIR LEAK
11 | 94-30227-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-08-30 | 1994-08-30 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | DREXLER ROAD 273 FEET S/O HWY 20 W/S OF ROAD. INSTALLED 48" OF 6" .188 PRETESTED PIPE TO REPAIR LEAK.
11 | 94-30229-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-08-30 | 1994-09-01 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | DREXLER ROAD 231 FEET WEST OF HWY 20 N/S OF HWY 20. TIE-IN 120' OF NEW 4". BORED UNDER 1...DITCH IN ORDER TO REPAIR LEAK IN 6" MAIN.
11 | 94-30230-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-09-01 | 1994-09-08 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | DREXLER ROAD 9 FEET S/P V-439 W/S OF ROAD. REMOVE 6' OF 6" AND REPLACED WITH 4" .188 DUE TO HEAVY PITTING. THIS EXSTING TO THE LEAK #94-30231
11 | 94-30231-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-09-01 | 1994-09-08 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | DREXLER ROAD 65 FEET S/O V-439 W/S OF ROAD. REPLACED 61' OF 4" .188 FROM LEAK 394-30230 TO THIS LEAK REPORT.
11 | 94-30232-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-09-01 | 1994-09-08 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | DREXLER ROAD 1196 FEET SOUTH OF V-439 W/S OF ROAD. REPAIRED 6' LEAK WITH 24" OF .188 PIPE WITH SAV-A-VALVE.
11 | 94-30233-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-09-01 | 1994-09-09 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | DREXLER ROAD 2286 FEET SOUTH OF V-439 E/S OF ROAD. REPAIR LEAK WITH 38" OF .188 WALL WITH SAV-A-VALVE
11 | 94-1692-1 | 169 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-09-27 | 1994-09-27 | Replace Pipe |  | Steel/Wrought Iron |  | WILLOWS | 301 FT. N/O MCBURNEY 57-1 BETWEEN ROAD #45 & HWY # 162. EXCAVATED AND CLOSED V-329. 6" L-169 - ISOLATED 57-1 & 57-2 FROM 12" LINE 169 WILL WAIT TILL LINE BLOWS ITSELF DOWN AND FARMER CUT RICE FROM AROUND LEAK. WILL TRY AND WORK REPAIRS 9-22-94, INSTALLED 36" OF 6" .188 PRETESTED TO REPAIR LEAK.
11 | 94-30235-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-09-22 | 1994-09-22 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | HWY 20 582 FEET WEST OF DREXLER RD. N/S OF HWY 20. REPLACED 40" OF 6" W/ PRETESTED 6" .188 WALL PIPE
11 | 94-30236-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-09-22 | 1994-09-22 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | MORONI RD. 487 FEET WEST OF VALVE 14.61 N/S OF ROAD. EXCAVATED AND NO LEAK FOUND. CBISH/J. WATERS
11 | 94-1673-1 | 167 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-10-05 | 1994-10-05 | Replace Pipe |  | Steel/Wrought Iron |  | PRINCETON | BOUNDE CREEK FIELD 100 YRDS N/O #1-10. INSTALL 36" OF 6" .188 PRETESTED PIPE
11 | 94-30237-1 | 302 |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-10-11 | 1994-10-11 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | L-302 SOUTH OF HWY 20, EAST OF WEST BUTTE RD. & SOUTH OF CENTER LINE HWY 20. INST. 3" CAP TO 219 PIPE.
11 | 94-1693-1 | 169 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-12-07 | 1994-12-13 | Replace Pipe |  | Steel/Wrought Iron |  | WILLOWS | APPROX 321 FT. N/O MCBURNEY #57-1 BETWEEN HWY 45 & HWY 162. EXCAVATED AND CLOSED V-329. ISOLATED L-169 FROM 57-1852-2. INSTALLED 24" OF 6" .188 PRETESTED PIPE TO REPAIR LEAK.
11 | 95-30201-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-01-10 | 1995-05-03 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | SOUTH BUTTE ROAD. INSTALLED 5384' OF 2" MAIN. GM1368877
11 | 95-30202-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-01-10 | 1995-01-25 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | 100 YRDS N/O WILKENS #G-1 WELL. INSTALLED 4' OF PRETESTED PIPE FROM GM 435966-7
11 | 95-30203-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-01-18 | 1995-01-18 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | N/S HWY 20 APPROX 100 YRDS W/O DREXLER ROAD. REPLACED WITH NEW 4" PIPING PROJECT
11 | 95-30204-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-01-11 | 1995-01-18 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | WEST SIDE OF DREXLER RD. APPROX 70 FEET S/O HWY 20. REPLACED WITH NEW 4" PIPING PROJECT. GM 1998350
11 | 95-30205-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-01-11 | 1995-01-12 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | EAST SIDE OF DREXLER ROAD. .3 MILES NORTH OF SUNNY ROAD. REPLACE 38" OF PRETESTED PIPE GM 1998350
11 | 95-30206-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-01-17 | 1995-01-19 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | HWY 45 AND WILSON BEND ROAD. ABANDONED SECTION OF PIPE WITH LEAK
11 | 95-30207-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-01-24 | 1995-02-23 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | 6" L-302 NEAR OSWALD AND BROWN ROAD. ...4" OF PIPE PRETESTED GM 1998350
11 | 95-30208-1 | 302 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-01-30 | 1995-02-03 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | 12" L-302 APPROX. 75 YRDS SE/O SOUTH SYCAMORE #20 WELL. INSTALLED 4' OF 12" & 23' 8" PRETESTED PIPE GM 119398-6
11 | 95-30209-1 | 302 |  | 8.625 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-02-03 | 1995-08-11 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | APPROX 100 YRDS N/O EARP ROAD, EAST HWY 45 & N/O GRIMES. DID NOT REPAIR LEAK. INSTALLED 13,000 FT. OF 4" PIPE FOR RE-ROUTE AROUND LEAK AREA. LEAK AREA ABANDONED IN PLACE. GM 1369396
11 | 95-30210-1 | 302 |  | 3.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-02-03 | 1995-02-08 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | 3" L-302 NEAR WILKINS B-1 AND WHITE ROAD. FOUND PRODUCERS 2 1/2" PLASTIC PIPE OVER THE P.G. & E. LINE TO BE LEAKING. PRODUCER CORRECTED PROBLEM.
11 | 95-30211-1 | 302 |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-02-08 | 1995-04-05 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | BROWNING FIELD. INSTALLED 26" PRETESTED 4.50" .188WT GM 199835-0
11 | 95-16701-1 | 167 |  | 6.62 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-02-09 | 1995-03-07 | Replace Pipe |  | Steel/Wrought Iron |  | PRINCETON | 6" LINE APPROX 200 YRDS S/O BOUNDE CREEK #1-8. INSTALLED 157" PRETESTED PIPE GM 1998350
11 | 95-30212-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-02-17 | 1995-02-23 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | APPROX 175 FEET E/O V-173 SOUTH OF GRIMES ON PAXON ROAD. REPLACED 5' 7" OF PIPE PRETESTED GM 1998350
11 | 95-30213-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-02-26 | 1995-04-19 |  |  | Steel/Wrought Iron |  | COLUSA | MOON BEND FIELD- APPROX 200 YRDS. EAST OF PECK #1 WELL IN WALNUT ORCHARD. INSTALLED 2' PRETESTED PIPE GM 9854969
11 | 95-16901-1 | 169 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-03-17 | 1995-04-26 | Replace Pipe |  | Steel/Wrought Iron |  | WILLOWS | SAME AS ABOVE. INSTALLED 2' OF PRETESTED PIPE GM 1998350
11 | 95-30214-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-05-03 | 1995-05-04 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | 6" L-302 ON DREXLER RD. 50 YRDS S/O WOOD RD. ON W/S OF DREXLER. INSTALLED 24" OF PRETESTED PIPE GM 1998350
11 | 95-30215-1 | 302 |  | 12.75 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-05-05 | 1995-05-08 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | 12" L-302 APPROX. 75 YRDS N/O STODAND #2. ISNTALLED 38' OF PRETESTED PIPE. PRETESTED PIPE GM 4965406 0.312"X42
11 | 95-30216-1 | 302 |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-05-10 | 1995-05-11 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | SAME AS ABOVE. ISNTALLED 2' OF PRETESTED PIPE GM 1998350
11 | 95-19301-1 | 193 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-05-23 | 1995-05-25 | Other |  | Steel/Wrought Iron |  | KIRKWOOD | 6" L-193 RICE CREEK FIELD. CUT & CAP TO FIX LEAK.
11 | 95-16902-1 | 169 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-05-30 | 1996-04-12 | Replace Pipe |  | Steel/Wrought Iron |  | WILLOWS | 200FT. N/O MCBURNERY 57-1 WELL CLOSED V-329. REPLACED 32" OF 6" PRETESTED PIPE SOAPED AT 100 PSI.
11 | 95-30217-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-06-21 | 1995-06-22 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | ON GRAMIRE ROAD APPROX 450 FT. N/O OSWALD ROAD. REPAIR LEAK WITH 35' OF .188 WALL 8" TESTED PIPE. GM 1193866
11 | 95-30218-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-06-21 | 1995-06-22 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | OSWALD ROAD APPROX 2 MILES E/P PROGRASS ROAD. REPAIRED LEAK WITH 24" .188 TESTED PIPE GM 1193866
11 | 95-30219-1 | 302 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-06-23 | 1995-06-28 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | 12" L-302 APPROX 200 YRDS W/O HWY 45 AND N/W OF GRIMES AIR STRIP AND N/O MORRIS RD. REPAIR LEAK WITH 5' OF 12" .312WT. TESTED PIPE GM 4965406
11 | 95-30220-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-06-27 | 1995-07-11 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | APPROX 1/3 MILE WEST OF DRY SLOUGH ROAD & ON GRIME ARBUCKLE ROAD. INSERTED ROAD X-ING WITH 4" .237 WT TEST PIPE...LONG. GM ....
11 | 95-30221-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-06-27 | 1995-06-29 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | APPROX 1/2 MILE S/O GRIMES-ARB. RD. NEAR BALSDON #3-1 WELL. REPAIRED LEAK W/ 36' .188WT 6" TESTED. GM 4045100
11 | 95-30222-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-07-12 | 1995-07-13 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | APPROX 50 YRDS. S/O MOBILE OFFICE ON DREXLER ROAD. REPLACED 60" PRETESTED 6" .219 WT. FOR REPAIR. GM 4045100
11 | 95-1673-1 | 167 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-07-18 | 1995-07-18 | Replace Pipe |  | Steel/Wrought Iron |  | PRINCETON | 6" L-167 50 FEET E/O WELL PAD BC #1-8 BOUNDE CREEK FIELD. REPLACED 36" PRETESTED 6" .219 WT FOR REPAIR. GM 4045100
11 | 95-30223-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-07-20 | 1995-07-21 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | BROWN RD. 2 1/2 TENTHS MILE N/O OSWALD ROAD. REPLACED LEAK WITH 36" OF .219WT PRETESTED PIPE. GM4045100
11 | 95-30224-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-08-23 | 1995-09-21 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | 205' N/O FRYE #26-1 GAS WELL 225' E/O SOUTH TARKE ROAD. REPAIRED LEAK WITH 32" 6" .188 PRETESTED PIPE. GM 145027-9
11 | 95-30225-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-09-07 | 1995-09-14 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | EAST SIDE OF DREXLER NEAR HOUSE AT 434 DREXLER ROAD. UNABLE TO DIND ANY LEAKS. DID...SOME UNEXPLAINED...THAT COULDN'T BE EXPLAINED. NO REPAIRS MADE (POSSIBLE SEPTIC....)
11 | 95-30226-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-12-18 | 1995-12-18 |  |  | Steel/Wrought Iron |  | GRIMES | APPROX 300 YRDS. E/O MOBILE #7-1...PRODUCERS WELL O/S DUE TO REWORKING TOOL STUCH DOWN HOLE. REPAIRS WAITING FOR WELL DETERMINATION. OTHERWISE THIS LINE WILL BE ABANDONED FROM SERVICE.
11 | 96-30202-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-02-15 | 1996-05-25 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | NEW PIPE INSTALLED GM 1293836. REPLACED FROM WOOD ROAD SOUTH TO SUNNY EAST 1300 +/- W/ 4" .188 DUE TO LEAK ORDER #7001015; SEE COMPLETED JOB #7001015...ALL TEST...
11 | 96-30203-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-02-15 | 1996-05-23 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | NEW PIPE INSTALLED GM 1293836. REPLACED FROM WOOD RD. SOUTH TO SUNNY RD. EAST 1300+/- W/ 4" .188 DUE TO LEAK. ORDER #7001015; SEE COMPLETE JOB # 7001015...
11 | 96-30204-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-02-15 | 1996-05-23 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | NEW PIPE INSTALLED GM 1293836. REPLACED FROM WOOD...SOUTH TO SUNNY RD 1300+/- ...DUE TO LEAKS #7001015 4"; SEE JOB ORDER #7001015 FOR COMPLETE...ALL TEST ...
11 | 96-30205-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-02-29 | 1996-06-17 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | INSTALLED NEW HIGHWAY CROSSING. INSTALL 500; .237WT 4" TO REPAIR LEAK. SO TARKE ACROSS HWY 20 ORDER #6000494; SEE JOB ORDER 600494 FOR COMPLETE...
11 | 96-30205-A | 302 |  | 6 | Gathering | [6 empty] | 1996-02-29 |  |  |  | Steel/Wrought Iron |  | COLUSA | 325FT. E/O V-403 NEAR HENSHAW #2MM. MONITOR PERIODICALLY
11 | 96-17401-1 | 174 |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-03-09 | 1996-03-09 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | W/S REDDINGTON RD. 185' S/O HILLGATE AVE ON WESTSIDE. REPLACED 30" .219. 3.50 OF TESTED PIPE (EMERGENCY STOCK)
11 | 96-30206-1 | 302 |  | 8.625 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-03-15 | 1996-03-27 |  |  | Steel/Wrought Iron |  | GRIMES | ... 1/2MILE WEST OF BROWNING ROAD. THIS SECTION OF LINE IS SCHEDULED FOR ABANDONMENT IN 1997 (LINE ...); ALL LINE IS SECTIONED AND DIGGED OF FLUIDS. SEE DRAWING 1 OF 1 OF JOB#7003917
11 | 96-30207-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-03-19 | 1996-03-27 |  |  | Steel/Wrought Iron |  | GRIMES | BROWNING #7. LINE O/S, BLOWING DOWN AND...FOR ABANDONMENT IN 1997. ABANDONED 4" FROM V-414 TO BROWNING #7 & #8; SEE DRAWING ON JOB NUMBER 7003911
11 | 96-30208-1 | 302 |  | 6.625 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-03-20 | 1996-03-26 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | MAWSON RD. 280' s/O PASS ROAD. REPAIRED WITH 21" .219 PRETESTED PIPE. GM128983-4
11 | 97-30203-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-03-26 | 1997-03-27 |  |  | Steel/Wrought Iron |  | COLUSA | 325 FT. E/O V-403 GRADE #3 UPGRADED TO DRADE #1 ORIGINAL 96-302-05A. REPAIRED WITH 26" .219WT PRETESTED PIPE. #7001015
11 | 96-30209-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-04-29 | 1996-04-30 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | BROWN ROAD .7 MILES N/P OSWALD ROAD. REPAIRED WITH 24' .219 PRETESTED PIPE GM 1289834
11 | 96-30210-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-04-30 | 1996-04-30 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | S/S OSWALD RD. 222' FT. E/O V-214 E/O BROWN RD. REPAIRED WITH 26" .188 WT. REPTESTED PIPE GM 119398-6
11 | 96-30211-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-04-30 | 1996-04-30 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | S/S OSWALD RD. 365FT E/O V-214 E/O BROWN RD. REPAIRED WITH 30" .188WT PRETESTED PIPE GM 1193986
11 | 96-30212-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-06-19 | 1996-06-25 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | 200 YRDS S/O V-453 ON E/S OF WELL ROAD TO POUNDSTONE #13-1. REPLACE LINE TIE-IN 9-12-96 UP FOR REPLACEMENT DUE TO INTERNAL CORROSION ST#1003962
11 | 96-30213-1 | 302 |  | 12.75 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-06-26 | 1996-06-26 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | 12" L-302 APPROX. 300 YRDS E/O V-66. REPLACED LEAK WITH 24" OF PRETESTED 12" .312WT FROM EMERGENCY STOCK
11 | 96-30214-1 | 302 |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-07-25 | 1996-10-07 | Other |  | Steel/Wrought Iron |  | GRIMES | 4" DOWNSTREAM OF TAP VALVE #396 TP ABANDONED WELL -WEST GRIMES #14-7. REOVED 2" FLANGE TO FLANGE FROM ...14-7 GAS WELL. INSTALLED 2" ... TO ABAND. 14-7 GAS WELL.; FOR DRAWING SEE... #095ZN93428
11 | 96-30215-1 | 302 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-10-05 | 1996-10-22 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | 12" L-302 APPROX. 100 YRDS W/O HWY 45 AND N/W OF GRIMES AIR STRIP N/O MORRIS RD.
11 | 96-30216-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-10-09 | 1996-10-10 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | 202' E/O V-214 OSWALD RD. REPAIR LEAK W/ 25" .219WT PRETESTED PIPE. #119398-6
11 | 96-30217-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-10-09 | 1996-10-10 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | 3985' E/O V-214 OSWALD RD. REPAIR LEAK W/ 56" OF PRETESTED PIPT.
11 | 96-16903-1 | 169 |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-10-26 | 1996-10-27 | Other |  | Steel/Wrought Iron |  | WILLOWS | HWY 162 AND CO. RD. T. (NORTH). CUT/CAPPED 2" L-169 4270' N/O VALVE .216
11 | 96-16904-1 | 169 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-11-25 | 1996-11-26 | Replace Pipe |  | Steel/Wrought Iron |  | WILLOWS | SAME AS ABOVE. REPAIRED WITH 30" PRETESTED PIPE GM 1998350
11 | 96-1695-1 | 169 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-12-19 | 1996-12-26 | Replace Pipe |  | Steel/Wrought Iron |  | WILLOWS | SAME AS ABOVE. REPLACED LEAK WITH NEW LOG-LEG
|  |  |  | 6 | [13 empty] | DAYTON
|  | 156 |  | 6.625 | [11 empty] | Steel |  |  | NOTE: PIPE 1/4 FULL OF WATER
|  | 156 |  | 6.625 | [11 empty] | Steel |  |  | NOTE: PIPE 1/4 FULL OF WATER
|  | 156 |  | 6 | [11 empty] | Steel |  | CHICO | WO 4907-5 LINE 156 PROBE INSTALLATION M&T RANCH; PROBE INSTALLED AT BOTTOM OF A 6 FT CANEL. DIV TAPPED OUT & INSTALLED PROBE
19 | 75-00001-1 | 155 |  | 4 | Gathering |  | Longitudinal Weld |  |  | Corrosion |  | 1975-04-29 | 1975-05-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | 155-166 FOREMAN - PLEASE COMPLETE & RETURN TO GAS ENG. - CHICO
| 90-10012-1 | 169 | 0.5 | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1990-08-14 | 1990-08-14 | Other |  | Steel/Wrought Iron |  | GLENY CO. | ABANDONED LINE
19 | 90-10012-1 | 169 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1990-08-14 | 1990-08-15 | Other |  | Steel/Wrought Iron
19 | 90-10007-1 |  |  | 4 | Transmission |  | Other |  |  | Other |  | 1990-01-23 | 1990-02-07 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | CHICO
19 | 87-10004-1 | 169 | [9 empty] | 1987-01-27 | [5 empty] | GLENN CO. | DELETED FILE
19 | 87-10004-1 | [10 empty] | 1987-01-27 | [6 empty] | CHECK BY 1-90
19 | 89-10005-1 | 169 | [9 empty] | 1989-01-27 | [5 empty] | GLENN | DELETED FILE
|  |  |  | 6 | [11 empty] | Steel |  | WILLOWS
|  |  |  | 6" & 12" | [11 empty] | Steel |  | WILLOWS | IBNSTALLED 2" VALVE FOR BLOW-OFF.
|  | 169 |  | 12 | [11 empty] | Steel |  | GLENN CO. | EXPOSED MAIN TO INSTALL 2" HOT TAP TEE.
|  |  |  | 8 | [11 empty] | Steel |  | GLENN | RECIFIER WIRE BADWELD TO 8" APPROX 8' N/O VALVE 105 ENCLOSE. ALSO TEST WIRE NEAR SAME LOCATION
|  |  |  | 16 | [11 empty] | Steel |  | GLENN
|  |  |  | 12 | [11 empty] | Steel |  | GLENN
|  |  |  | 6 | [11 empty] | Steel |  | WILLOWS
|  | 169 |  | 4 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | REMOVED 6' OF 4" LINE 169 FOR INTERNAL CORROSION ANALYSIS - PIPE WAS IN EXCELLENT CONDITION
|  |  |  | 4 | Transmission | [6 empty] | 1976-03-31 |  |  |  | Steel/Wrought Iron |  | WILLOWS | DUG UP TO SHUT VALVE #303
|  | 169 |  | 4 | [11 empty] | Steel |  | WILLOWS
|  | 169 |  | 8 | [11 empty] | Steel |  | WILLOWS
[18 empty] | Willows | INSTALLED 3216 ANODE AS PER B. STERNS. C.
|  | 169 | [16 empty] | MAIN APPROX 8' DEEP FROM EXISTING FIELD
CHICO
|  | 169 | [15 empty] | GLENN
10 |  | 169 |  | 3 | Transmission | [6 empty] | 1976-03-31 |  |  |  | Steel/Wrought Iron
10 |  |  |  | 3 | Transmission | [6 empty] | 1976-03-31 |  |  |  | Steel/Wrought Iron |  | WILLOWS
|  | 169 | [9 empty] | 1983-02-02 | [5 empty] | WILLOWS
|  |  |  | 4.12 | Gathering | [10 empty] | Steel/Wrought Iron
|  | 169 |  |  | Transmission | [10 empty] | Steel/Wrought Iron
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PIPE LOCATED ABOVE GROUND AT WELL-
|  |  |  | 6" & 3" | Transmission | [10 empty] | Steel/Wrought Iron
|  |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  |  |  | Replace Pipe and/or Service |  |  |  |  | NEW 26" SECTION CUT INTO LINE
|  | 169 | [16 empty] | CUT OFF MOBILE 81-3 AT THIS LOCATION
10 |  |  |  | 6 | Transmission | [6 empty] | 1976-03-30 |  |  |  | Steel/Wrought Iron |  | WILLOWS
CUT OFF THIS MAIN AT THIS LOCATION
169
169
19 | 90-10005-1 | [10 empty] | 1990-01-29
19 | 89-10006-1 | 169 |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1989-09-29 | 1989-09-28 | Replace Pipe |  | Steel/Wrought Iron |  | GLENN | REPLACED 22" OF 4.5" X.1566R
19 | 83-00003-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1983-08-08 | 1983-10-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron
19 | 78-00002-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1978-03-21 | 1978-03-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | WILLOWS
19 | 81-00002-1 | [10 empty] | 1981-03-16
19 | 85-00001-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1985-03-15 | 1985-03-21 | Other |  | Steel/Wrought Iron |  |  | WELD A 1" SAV-A-VALVE NIPPLE OVER CORROSION PIN HOLE.
19 | 79-00001-1 |  |  | 12 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1979-03-21 | 1979-04-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron
19 | 72-00002-1 | 169 |  | 12 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1972-04-15 | 1972-04-15 | Other |  | Steel/Wrought Iron
19 | 86-00002-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1986-01-22 | 1986-08-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron
19 | 80-00003-1 | [10 empty] | 1980-04-09
19 | 85-00004-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1985-09-26 | 1985-09-26 | Weld Over Sleeve or Can |  | Steel/Wrought Iron
19 | 71-00003-1 | 169 |  | 12 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1971-12-05 | 1971-12-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Chico | REMOVED 2' SECTION AND CAPPED. CLOSED V-301 & V-302. CLOSED V-230, V-231, V-234.
19 | 80-00002-1 | 169 |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-04-09 | 1981-03-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron
14 | 85-00001-1 | [10 empty] | 1985-03-14
19 | 83-00001-1 |  |  | 8 | Gathering |  | Longitudinal Weld |  |  | Corrosion |  | 1983-03-04 | 1983-03-04 | Replace Pipe and/or Service | INST. CAP | Steel/Wrought Iron
19 | 72-00003-1 | 169 |  | 12 | Gathering |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-05-16 | 1972-05-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron
19 | 72-00004-1 | 169 |  | 16 | Gathering |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-12-06 | 1972-12-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Oraville | ... REPAIR POINT 1000 FT N/O T-8.6. REPLACED 12' OF .231 WITH 16" ... 12' OF .312 W.T. 16' 2-BUTT WELDS.
19 | 82-00003-1 | 169 | [9 empty] | 1982-04-09
19 | 76-00004-1 | 169 |  |  | Transmission |  | Other |  |  | Other |  | 1976-06-02 | 1976-06-11 |  |  | Steel/Wrought Iron
19 | 87-00010-1 | 169 |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  |  | 1987-11-05 | Replace Pipe and/or Service
19 | 81-00001-1 | [10 empty] | 1981-03-03
19 | 82-00002-1 | 169 |  | 4 | Gathering |  | Valves |  |  | Other |  | 1982-04-08 | 1983-03-11 | Other | GREASE VALVE | Steel/Wrought Iron
Orland
193
|  | 193 | [15 empty] | Orland
Orland
193
|  | 193 | [16 empty] | CASING AND PIPE APPROX 10' DEEP.
193
|  | 193 | [16 empty] | PIPE WRAP TOUCHING CASING. CREW PLACED PLASTIC CABLE PROTECTION AT CASING END. 8' DEEP TO CASING AND PIPE FROM TOP OF CANAL.
|  | 193 | [16 empty] | CASING 4 1/2' DEEP FROM TOP OF CANAL OUT 6' FROM SOUTH EDGE.
193
193
193
193
|  | 193 | [15 empty] | ORLAND | TIE IN TO EXT. 4" LINE.
|  | 193 | [16 empty] | INSTAQLLED 4' 4" MAIN.
|  | 193 | [16 empty] | INSTALLED 6X4 REDUCER.
|  | 193 | [16 empty] | INSTALLED 6X6X4 TEE.
193
193
|  | 193 | [16 empty] | PROBE INSTALLED 1000' E/O 6TH AT BRIDGE.
19 | 87-10011-1 | 193 |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1987-12-15 | 1987-12-30 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | INSTALLED 6' - 4.5" D.D. PIPE. HPI 51 GR. "B" SMLS. 156" W.T. (12/30/87). REPLACED 6' OF 4" PIPE. WAY THREW REST ONE VERY DEEP. DIV HAS PIECE OF PIPE WE TOOK OUT.
19 | 75-00005-1 | 193 |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-01-15 | 1975-01-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron
85 | 80-00026-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-11-25 | 1980-11-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | 3/8" HOLE IN PIPE. REPLACED 53 1/4" OF 6" GATHERING LINE. (6.625" DIA. .188 W.T. 5L.GR.) B 35,000). CLASS 1 LOCATION UNODORIZED GAS.
| 07-31801-1 | 318 |  | 4 | Transmission | GATHERING |  |  |  | Internal Corrosion |  | 2007-07-30 | 2007-02-07 | Other | REPLACED PIPE |  |  | ORLAND | ISOLATED AND BLEW PIPLINE DOWN FOR SAFETY-280 FT OF PIPELINE TO BE REPLACED ON 2-7-07; SEE ATTACHED SHEET
| 08-31801-1 | 318 |  | 6.5 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-02-08 | 2008-02-09 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | ORLAND | FOUND PIN HOLE IN BOTTOM OF PIPE. REPLACED BY INSTALLING 24" CAN OF PRETESTED EMERGENCY STOCK.
| 08-31802-1 |  |  | 6.25 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-04-30 | 2008-06-04 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | ORLAND | INSTALL 6" PHIDCO SPLIT SLEEVE OVER PINHOLE 6" STEEL L-318 SOAP @ 100PSI.
| 08-31803-1 |  |  | 6.25 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-04-30 | 2008-06-03 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | ORLAND | INSTALLED 6" PLIDCO SPLIT SLEEVE OVER PINHOLE 6" STEEL L-318 E/O V-6 SOAP @ 100PSI.
| 08-31804-1 | 318 |  | 6.25 |  |  | Unknown |  |  | Internal Corrosion | UNKNOWN | 2008-06-09 |  |  |  | Steel/Wrought Iron |  | ORLAND | SEE GAS OPERATIONAL CHANGE NOTICE ATTACHED.
|  |  |  | 4 | [13 empty] | ORLAND
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | ORLAND | LOCATION INSIDE STATION YARD
[18 empty] | ORLAND | TIE IN FS. 13+42.
[18 empty] | ORLAND | TIE IN APPROX 1 MILE W.O RD DD. F.S. 24+81.
|  | 318 | [15 empty] | ORLAND
|  |  |  | 3 | [13 empty] | ORLAND
|  | 318 | [15 empty] | ORLAND
339
|  | 339 | [16 empty] | INSTALL 32# ANODE. CUT RISER OFF BELOW GROUND. INVERT PIPE WELD PLATE ON ENDS.
| 02-17201-1 |  |  | 18 | Transmission |  | Body of Pipe | Other | CRACK | Unknown |  | 2002-05-29 | 2002-06-05 | Other |  |  |  | ARBUCKLE | FOUND CRACK @ 3 O'CLOCK LOOKING SOUTH REPAIR # 8053217 INSTALLED 59 1/2" CAN
| 00- | 302E |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Internal Corrosion |  | 2000-11-30 | 2000-11-30 | Welded Sleeve/Can - Weld |  |  |  | GRIMES | INSTALL 18" SLEEVE SAV-A-VALVE AT LOCATION #2 15.8' N/O GM#1190; SOAP TEST @100PSI; SEE AS...
| 00- | 302E |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Internal Corrosion |  | 2000-12-13 | 2000-12-13 | Other |  |  |  | GRIMES | INSTALL 192.6' .312X60 NEW STATION 442339' TO 4616.5'; SOAP TEST... WELDS @ 100PSI
| 00- | 302E |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Internal Corrosion |  | 2000-12-09 | 2000-12-09 | Weld Over Sleeve or Can |  |  |  | GRIMES | INSTALL 18" SLEEVE SAV-A-VALVE AT LOCATION #2A 19.8' N/O GW# 1820; SOAP TEST @100 PSI
| 00- | 302E |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Internal Corrosion |  | 2000-11-28 | 2000-11-28 | Weld Over Sleeve or Can |  |  |  | GRIMES | INSTALL 18" SLEEVE AND SAV-A-VALVE AT LOCATION #4 ..4' N/O GW#2930; SOAP TEST @ 100PSI
| 00- | 302E |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Other | THIN WALL PIPE | 2000-12-11 | 2000-12-11 | Other |  |  |  | GRIMES | REMOVED 40' OF .280WT REPLACE 46' 312WT X60 ST. 13072.4-13118.4; SOAP TEST TIE-IN WELDS @100 PSI
| 00- | 302E |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Internal Corrosion |  | 2000-11-18 | 2000-11-18 | Welded Sleeve/Can - Weld |  |  |  | GRIMES | INSTALL 18" SLEEVE AND SAV-A-VALVE AT LOCATION #6 .6" N/O GW#4180; SOAP TEST 100PSI;
| 00- | 302E |  |  | Transmission | GATHERING | Body of Pipe |  |  | Internal Corrosion |  | 2000-12-12 | 2000-12-12 | Other |  |  |  | GRIMES | INSTALLED 732.5' .312 -X60 STATIONS 17386.2 TO 18118.7'; SOAP TEST TIE-IN WELDS @100 PSI
| 00- | 302E |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Internal Corrosion |  | 2000-12-13 | 2000-12-13 |  |  |  |  | GRIMES | INSTALL 132' X60 .312WT STATIONS #22196.4 TO 22329.0; SOAP TEST TIE-IN WELDS @100 PSI
| 00- | 302E |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Internal Corrosion |  | 2000-11-18 | 2000-11-18 | Welded Sleeve/Can - Weld |  |  |  | GRIMES | INSTALL 18" SLEEVE WITH SAV-A-VALVE AT LOCATION #8 11.1' S/O GW#5520; SOAP TEST @ 100 PSI
| 00- | 302E |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Internal Corrosion |  | 2000-11-28 | 2000-11-28 | Welded Sleeve/Can - Weld |  |  |  | GRIMES | INSTALL 36" SLEEVE AND SAV-A-VALVE AT LOCATION #9 2.4' TO 4.2' S/O GW# 6160; SOAP TEST @ 100PSI
| 00- | 302E |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Other |  | 2000-12-14 | 2000-12-14 | Other |  |  |  | GRIMES | BORE SLOUGH 50; S/0 RAW PRE/AR OFF SETS; SOAP TESTED TIE-IN WELDS @ 100 PSI; CONTRACTOR HAS AS BUILT HAD SURVERS SHOOT NEW ROW.
| 00- | 302E |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Internal Corrosion |  | 2000-12-09 | 2000-12-09 | Other | 27' REPLACEMENT |  |  | GRIMES | INSTALL 27' WITH OFFSET SOUTH/SIDE OF C-5.36; SOAP REST TIE-IN WELDS 100 PSI
| 00- | 302E |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Internal Corrosion |  | 2000-12-15 | 2000-12-15 | Other | 200 |  |  | GRIMES | INSTALL 200' WITH OFFSETS N/O V-5.36; SOAP TEST TIE-IN WELDS @100PSI
| 00- | 302E |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Internal Corrosion |  | 2000-12-11 | 2000-12-11 | Other | INSTALL 600' |  |  | GRIMES | INSTALL 630'E/O 2047 CANAL; SOAP TEST TIE-IN WELDS @100 PSI
| 00- | 302E |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Internal Corrosion |  | 2000-11-28 | 2000-11-28 | Welded Sleeve/Can - Weld |  |  |  | ARBUCKLE | INSTALL 18" SLEEVE WITH SAV-A-VALVA AT LOCATION 40828.3 .2# N/O GW#12540; SOAP TEST @100 PSI
| 00- | 302E |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Internal Corrosion |  | 2000-11-17 | 2000-11-17 | Welded Sleeve/Can - Weld |  |  |  | ARBUCKLE | ISNTALL 18" SLEEVE WITH SAV-A-VALAVE AT LOC. 41361.3 17.3' S/O GW 12670; SOAP TEST 100 PSI
| 00- | 302E |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Internal Corrosion |  | 2000-11-16 | 2000-11-16 | Welded Sleeve/Can - Weld |  |  |  | ARBUCKLE | INSTALL 18" SLEEVE WITH SAV-A-VALVE AT LOCATION 44067.1 30.8' S/O GW 13350; AIR TEST @ 100PSI WITH SOAP
| 00- | 302E |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Damage by 3rd Party |  | 2000-12-07 | 2000-12-07 | Other | 143 |  |  | ARBUCKLE | INSTALL 140' 20" DOG LEG TO REMOVE EXTERNAL DENTS; SOAP TEST TIE-IN WELDS @ 100 PSI
| 00- | 302E |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Internal Corrosion |  | 2000-11-16 | 2000-11-16 | Welded Sleeve/Can - Weld |  |  |  | DUNNIGON | INSTALL 18" SLEEVE AT LOCATION #19 .2" S/O G-WLEDS #15400; AIR TEST @100PSI WITH SOAP
|  |  |  | 4.5 | [8 empty] | 1998-01-27 |  |  | Steel |  |  | INSTALL 4" VALVE IN LINE.
Steel/Wrought Iron
| 92-302-4-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-02-01 | 1992-02-03 | Replace Pipe |  | Steel/Wrought Iron |  |  | REPAIRED LEAKS WITH 5.5" PRETESTED ...
| 92-30202-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-02-04 | 1992-02-05 | Replace Pipe |  | Steel/Wrought Iron |  |  | REPLACED 96" 6" PIPE 0.188 WITH PRETESTED 0.250 6" FROM KELLER ROAD JOB. GM 4811188 TESTED AT 2195 PSI.
| 92-302-1 |  |  | 4.5 | Gathering |  | Body of Pipe |  |  | Other |  | 1992-02-18 | 1992-02-18 | Replace Pipe |  | Steel/Wrought Iron |  |  | REPLACED 3' OF 4" PIPE WITH NEW 4" PIPE PRE TESTED 0.188 OFF FRANKLIN RD JOB.
| 92-30204-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1992-02-20 | 1992-02-21 | Replace Pipe |  | Steel/Wrought Iron |  |  | REPLACE 32" 6" PIPE WITH NEW 6" PIPE PRE TESTED ON GM4876652
| 92-12001-1 |  |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-03-03 | 1992-03-03 | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER | REPLACED WITH 6' OF 4" PRETESTED 0.156 W.T. PIPE TEST ON
| 92-30206-1 |  |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-03-03 | 1992-03-03 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPLACED 3 FT OF 4" WITH PRETESTED PIPE FROM GM 487664-5.
| 92-30307-1 | 302 |  | 6.62 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-03-17 | 1992-03-18 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPLACED 60" OF 6" WITH 6" X .188 WITH PRETESTED PIPE
| 92-30209-1 |  |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-04-30 | 1992-04-30 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REMOVED 36" OF 4" AND REPLACED WITH 4" PRETESTED ON GM 487665-2.
| 92-1612-1 | 167 |  | 6.62 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-05-20 | 1992-05-26 | Replace Pipe |  | Steel/Wrought Iron |  | COLUSA | INSTALLED 3'-4" OF 6" X 0.156" WT PRETESTED PIPE TO REPLACE LEAK.
| 92-30210-1 |  |  | 6.62 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-05-29 | 1992-05-29 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPLACED 60" OF 6" WITH 6" X .183 PRETESTED PIPE.
| 92-30211-1 |  |  | 8.62 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-06-24 |  | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPLACED WITH 90" OF 8" X .219 X-42 ECW STL PIPE TO REPLACE LEAKING PIPE.
| 92-30212-1 | 302 |  | 6.25 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-06-24 | 1992-06-24 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPLACED 5 FT OF 8" WITH 8" X X-42 ECW STL PIPE ON GM 4811105
| 92-30214-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1992-07-06 | 1992-07-27 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES
| 92-302-1 | 302 |  | 4.5 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1992-10-06 | 1992-10-07 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPLACED 2' OF PIPE.
| 92-30217-1 |  |  | 6.62 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-10-20 | 1992-10-20 | Replace Pipe |  | Steel/Wrought Iron |  |  | REPLACED PIPE WITH 3' OF PRETESTED PIPE.
| 92-30218-1 |  |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-12-07 | 1992-12-07 | Replace Pipe |  | Steel/Wrought Iron |  | COLUSA | REPLACED 4' OF 4" WITH 4" X .156" GE B ECW PIPE TESTED ON GM 480809-3.
11 | 93-302-1 | [10 empty] | 1993-01-08 | [5 empty] | GRIMES | PIPELINE DID NOT OPERATE AFTER LEAK WAS FOUND.
|  |  |  | 3.5 | [14 empty] | WO 43663-B (ABANDON PIPELINE).
11 | 93-302-2 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-01-10 | 1993-01-11 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | INSTALLED 4" OF 5" .188" WAL PRETESTED PIPE TO REPAIR LEAK.
11 | 93-30203-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-01-21 | 1993-01-22 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN
11 | 93-302-4 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-01-22 | 01/00/1993 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | FIELD SHUT IN FOR EXTENDED TIME DUE TO HIGH WATER FROM SC. RIVER. REPLACED 42" OF 8" .217 PRETESTED PIPE TO REPLACE LEAK.
11 | 93-302-5 |  |  | 6.25 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-01-27 | 1993-01-28 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | INSTALLED 2F 6" .219 W.T. 60011856 - TESTED
11 | 93-302-6 | 302 |  | 3.9 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-02-02 | 1993-02-02 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | INSTALLED 26" OF 3" .156 WALL PRETESTED PIPE.
11 | 93-302-7 |  |  | 6.62 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-02-01 | 1993-02-01 | Replace Pipe |  | Steel/Wrought Iron |  |  | REPLACED WITH 2 FT OF PRETESTED 6" ON GM 496531-5.
11 | 93-302-8 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-02-12 | 1993-02-12 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | INSTALLED 40" OF 8" .188 WALL TO REPAIR LEAK.
11 | 93-302-9 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-02-25 | 1993-02-25 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | INSTALLED 47" OF 6" .188 WALL PIPE TO REPAIR LEAK. THIS LEAK IS ON STEIDLMAYERS PROP. (THE MUD HOLE REPAIR!) GM 4045183.
11 | 93-302-10 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-03-10 | 1993-03-10 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | . INSTALLED 2' - 7" OF PRETESTED 6.625" OD X 0.214"WT API 5LX6LX.42 ERW STEEL PIPE TO REPLACE LEAKING SECTION OF PIPE. INSTALL 34" OF 6" .188 TO REPAIR LEAKING SECTION OF PIPE.
11 | 93-302-11 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-03-13 | 1993-03-13 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | INSTALL 3 FT OF 6" .188 WALL PIPE TO REPAIR LEAK.
11 | 93-302-12 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-03-17 | 1993-03-17 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | INSTALLED 29" OF 4" .188 WALL TO REPAIR LEAK.
11 | 93-30213-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1993-05-12 | 1993-05-19 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | INSTALLED 2'-7" OF PRE TESTED 6.675" X 0.219" INT API SLX GRX-42 ERW WO REPLACE LEAK.
| 93-30314-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-07-21 | 1993-07-22 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPLACED ONE FOOT WITH PRE TESTED PIPE. (4" .188) SMALL PIN HOLE ON BOTTOM.
11 | 93-30215-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-07-26 | 1993-07-28 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPLACE LEAKING PIPE WITH 35" OF 4 1/2" X 0.188 PRETESTED PIPE.
| 93-30216-1 | 302 |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1993-07-27 | 1993-07-27 | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER | REPLACE LEAKING PIPE WITH 34" OF 10.750" OD X 0.219 WT API 5LXX-52 ERW PRETESTED PIPE. 7-27-93 REPLACED LEAKING PIPE WITH 34' OF PRETESTED 10.750" DD X 0.219" X-52 ERW PRETESTED STEEL PIPE. PIPE FROM PRETESTED EMERGENCY PIPE MERIDIAN S.C.
11 | 93-30217-1 | 302 |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-07-28 | 1993-08-04 | Other |  | Steel/Wrought Iron |  | MERIDIAN | ABANDONED PIPE ON WP 44234B.
11 | 93-30218-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-08-24 | 1993-08-24 | Replace Pipe |  | Steel/Wrought Iron |  | COLUSA | REPLACED 24" OF MAIN W/6" .219 PRETESTED PIPE.
11 | 93-30219-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-09-09 |  | Replace Pipe |  | Steel/Wrought Iron |  | COLUSA | REPLACED 35" OF 8" TO REPAIR LEAK. REPLACED WITH 8" .219 PRE TESTED PIPE. API 5L X 42 ERW.
11 | 93-302-20 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-10-25 | 1993-10-26 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPAIRED LEAK WITH 38" OF 6" .219 PRETESTED PIPE.
11 | 93-30221-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-11-15 | 1993-11-16 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPLACED 24" OF 6" .219 PIPE W/24" OF PRE TESTED PIPE.
11 | 93-30222-1 |  |  | 3.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-11-26 |  | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER | REPLACED LEAK WITH 24" OF 3 1/2" PRETESTED PIPE.
11 | 93-302-23 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-12-16 | 1993-12-17 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPLACED 36" WITH .219 PRETESTED PIPE.
|  |  |  | 0.5 |  |  | Body of Pipe |  |  | Corrosion |  | 1990-05-25 | 1990-06-13 | Replace Pipe |  | Steel/Wrought Iron |  | ARBUCKLE | REPLACED 1/2" PIPE WITH 3/4" PIPE.
| 07-00129-1 | 121 |  | 6 | Transmission |  | Unknown |  |  | Unknown |  | 2007-08-01 | 2007-08-01 | Deactivate #TP Main |  | Steel/Wrought Iron |  | SUTTER
| 07-12001-1 | 120 |  | 6 | Transmission |  | Unknown |  |  | Unknown |  | 2007-08-01 | 2007-08-01 | Deactivate #TP Main |  | Steel/Wrought Iron |  | W/O SUTTER, SUTTER CO | DEACTIVATED APPROX. 105' OF 6".4".2" STL OF LINE 120 FROM T-2.03.
| 92-12001-1 |  |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-03-03 | 1992-03-03 | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER | REPLACED WITH 6' OF 4; REPLACED WITH 6' OF 4" PRETESTED 0.156 W.T. PIPE TESTED ON
|  |  |  | 4 | [11 empty] | Steel |  |  | REPAIRED LEAK IN 4" LINE HAGEMAN ROAD.
| 91-1201-1 |  |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1991-10-09 | 1991-11-12 | Replace Pipe |  | Steel/Wrought Iron |  |  | REMOVED 4' OF 4" PIPE. REPLACED WITH 4' OR 4.5" OP X 0.156 WT API 5L 6RB EPW TESTED ON WHO 48615-A 7-18-91
| 04-12801-1 | 128 |  | 4 | Transmission |  |  |  |  | External Corrosion |  | 2004-10-14 | [5 empty] | WILLOWS | EMPLOYEE FOUND LEAK WHEN LOCATING GAS LINE FOR FORMER DEAD VEGETATION
|  |  |  | 0.04 | Transmission | [7 empty] | 2004-10-18 | Replace TP Main |  |  |  |  | REPLACED WITH 5' OF TESTED 4.5"00X .237 GRB SMLS
| 09-13601-1 | 136 |  | 0.5 | Transmission |  | Fitting |  |  | Unknown |  | 2009-06-22 | 2009-11-06 | Other | TIGHTENED FITTING SOAP TEST OF "NO LEAKS" | Steel/Wrought Iron |  | NEAR CHICO | TIGHTENED FITTINGS. SOAP TEST-NO LEAKS. REPAIRED LEAKS ON THE SUPPLY RACKS AND FILTERS. LEAKS REPAIRED V-20 CONTROLLER FITTING, V-20 BUSHING.
|  | 167 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1990-03-16 | 1990-03-16 | Other |  | Steel |  | PRINCETON
|  |  |  | 4 | Gathering |  | Girth Weld |  |  | Internal Corrosion |  |  | 1990-11-05 | Replace Pipe |  | Steel/Wrought Iron |  |  | REMOVED 3' PIPE & REPLACED WITH 3' NEW PIPE
|  |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1991-05-15 |  | Replace Pipe |  | Steel |  | PRINCETON | REPLACED 2 1/2 FT SECTION OF 4" PIPE
|  |  |  | 6 |  |  | Body of Pipe |  |  | Internal Corrosion |  |  | 1991-08-21 | Replace Pipe |  | Steel |  |  | REPLACED 23 7/16" OF 6" .188W X42 GAS MAIN iNTERNAL CORROSION EXTREEM. MANY PITS
| 92-167-1 | 167 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-04-18 |  | Replace Pipe |  | Steel |  |  | REPL. SECTION OF PIPE; BLOWDOWN INFO - CLOSED V-128.
| 92-16701-1 | 167 |  | 4 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 1992-04-08 |  | Replace Pipe |  | Steel |  |  | REPL. SECTION OF PIPE
| 92-1672-1 | 167 |  | 6.62 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-05-20 | 1992-05-26 | Replace Pipe |  | Steel |  | COLUSA | INSTALLED 3'-4" OF 6" X O.156" WT PRETESTED PIPE TO REPLACE LEAK
11 | 94-167-01- | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-02-03 | 1994-02-08 | Replace Pipe |  | Steel |  | PRINCETON | INSTALLED 44" OF 6.625 X 0.219 TO REPAIR LEAK
11 | 94-16702-1 | 167 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-05-19 | 1994-05-19 | Replace Pipe |  | Steel |  | PRINCETON | REPLACE 2' OF 6" MAIN TO REPAIR LEAK W/ 3' OF PROGRESSED 6" .188 WALL PINE
450 | 94-1673-1 | 167 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-10-05 | 1994-10-05 | Replace Pipe |  | Steel |  | PRINCETON | INSTALL 36" OF 6" .188 TEST PIPE
450 | 94-167-3-1 | 167 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-10-05 |  | Replace Pipe |  | Steel |  | PRINCETON
11 | 95- | 167 |  | 6.62 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-02-09 |  | Replace Pipe |  | Steel |  | PRINCETON
11 | 95-16702-1 | 167 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-04-19 | 1995-04-19 | Replace Pipe |  | Steel |  | PRINCETON | INSTALLED 4' OF PRESTED PIPE GM 496540-6
11 | 95-16702-1 | 167 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-04-19 |  | Replace Pipe |  | Steel |  | PRINCETON
| 98-16701-1 | 167 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-01-06 | 1998-01-21 | Replace Pipe |  | Steel |  | AFTON | REPAIRED LEAK WITH 36", .188 WT PRETESTED PIPE
| 98-1672-1 | 167 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-01-28 |  |  |  | Steel |  | PRINCETON | DID NOT REPAIR - A&A CUT OFF FOR TERMD
| 98-1673-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-10-27 |  | Replace Pipe |  | Steel |  | COMPTON LANDING | SCHEDULED TO CAP AND CAP (NOT REPAIR) WITH RETIREMENT OF CARTER #1-14 M 98-34.
| 00-16701-1 |  |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2000-02-25 | 2000-08-03 | Welded Sleeve/Can - Weld |  |  |  | PRINCETON | BUBBLES IN FLOODED WALNUT ORCHARD: INSTALLED 36" PRETESTED 12" .28I PIPE WITH SON-A-VALVE. REDUCED AND KEPT PIPELINE PRESSURE AT 100 PSIG STARTING ON 2/28/00...
| 00-16702-1 |  |  | 12 | [7 empty] | 2000-08-08 | [5 empty] | PRINCETON
| 01-16701-1 | 167 |  | 4 | Gathering | SERVICE | Body of Pipe | Tap Connection |  | Digin |  | 2001-10-25 | 2001-10-25 | Mechanical Repair Fitting - Fitting |  |  |  | COLUSA | GC GAS STRUCK A SERVICE TEE WHILE EXCAVATING LINE: HAS BEEN DOWN GRADED TO DISTRIBUTION ON 10-16-2001*(58 PSI) 4"X1" R: THREADED PIPE AND INSTALLED MEMBER
| 01-16701-1 | 167 |  | 4 | Gathering | SERVICE | Tap Connection |  |  | Digin |  | 2001-10-25 | [5 empty] | COLUSA | GC GAS STRUCK A SERVICE TEE WHILE EXCAVATING LINE: HAS BEEN DOWN GRADED TO DISTRIBUTION ON 10-16-2001 *(58 PSI) 4X1" R.
| 03-16901-1 | 169 |  | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion | SUSPECT INT.CORROSION | 2003-12-01 | 2003-12-03 | Welded Sleeve/Can - Weld |  |  |  | E/O WILLOWS | RICE FIELDS 100 YDS S/E V-230
|  | 169 |  | 4.5 | [8 empty] | 1993-04-06 |  |  | Steel |  |  | REPLACED LEAKING PIPE WITH 3' OF 4.5" ODX 0.188" WT API 5LX 6RX-42 ERW STEEL PIPE (PRETESTED)
|  |  |  | 6 | [8 empty] | 1993-04-08 |  |  | Steel |  |  | INSTALLED 2'-4" OF 6.625" OD X 0.219" WT API 5LX6RX-42 ERW PRETESTED PIPE TO REPLACE LEAKING PIPE. PIPE TESTED ON 6M 4964664
|  | 167 |  | 6 | [8 empty] | 1993-04-12 |  |  | Steel |  |  | REPAIRED WITH 24" OF .219 6" TESTED ON JOB# 60007196
|  |  |  | 4.5 | Transmission |  | Physical/Mechanical Joint |  |  | Internal Corrosion |  |  | 1992-12-07 | Replace Pipe |  | Steel |  |  | INSTALLED 3' 4.50 PIPE PRETESTED
|  |  |  | 4.5 | [8 empty] | 1991-11-12 |  |  | Steel |  |  | LINE TO BE ABANDONED
11 | 94-16901-1 | 169 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-05-20 |  | Replace Pipe |  | Steel |  | WILLOWS | NO LEAK AT SAID LOCATION ABOVE. 36" COVER AT VALVE# 329
|  |  |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  |  | 1993-01-13 | Replace Pipe |  | Steel |  | WILLOWS | REPLACED 2FT OF 4' WITH 4" PIPE PRETESTED ON GM 4D4458-2
|  |  |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  |  | 1993-01-15 | Replace Pipe |  | Steel |  | WILLOWS | REPLACED 2FT 4" WITH 4" PRETESTED ON GM 404458-2
11 | 94-16901-1 | 169 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-05-20 |  | Replace Pipe |  | Steel |  | WILLOWS
11 | 94-1692-1 | 169 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-09-19 | 1994-09-27 | Replace Pipe |  | Steel |  | WILLOWS | WILL WAIT TILL LINE BLOWS ITSELF DOWN AND FARMER CUT RICE FROM AROUND LEAK. WILL TRY AND MAKE REPAIRS 9-22-94 INSTALLED 36" OF 6" .188 PRETESTED PIPE TO REPAIR LEAK
11 | 94-169-3-1 | 169 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-12-07 | 1994-12-13 | Replace Pipe |  | Steel |  | WILLOWS | INSTALLED 24" OF 6" .188" PRETESTED PIPE TO REPAIR LEAK
11 | 94-169-3-1 | 169 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-12-07 |  | Replace Pipe |  | Steel |  | WILLOWS
11 | 95-16901-1 | 169 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-03-17 |  | Replace Pipe |  | Steel |  | WILLOWS
11 | 95-16902-1 | 169 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-05-30 | 1996-04-12 | Replace Pipe |  | Steel |  | WILLOWS | REPLACED 32" OF 6" PRETESTED PIPE. SOAPED AT 100 PSI
11 | 96-16903-1 | 169 |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-10-26 | 1996-10-27 | Other |  | Steel |  | WILLOWS | CUT/CAPPED 2" L-169
11 | 96-16904-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-11-25 | 1996-11-26 | Replace Pipe |  | Steel |  | WILLOWS | REPAIRED WITH 30' PRETESTED PIPE GM- 1998350
11 | 96-169-5-1 | 169 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-12-19 | 1996-12-27 | Replace Pipe |  | Steel |  | WILLOWS | REPAIRED 12/27/1996
| 98-169-1-1 | 169 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-05-07 |  | Replace Pipe |  | Steel |  | WILLOWS
| 98-16902-1 | 169 |  | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-06-07 | 1998-06-18 | Replace Pipe |  | Steel |  | WILLOWS | REPAIRED LEAK 163" TESTED PIPE X65 .312 WK
| 98-169-3-1 | 169 |  | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-07-01 |  | Replace Pipe |  | Steel |  | WILLOWS
| 97-16901-1 | 169 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1997-09-20 | 1997-09-22 | Replace Pipe |  | Steel |  | PRINCETON | REPLACED 2 FEET WITH PRETESTED .3/2" WALL API 5LX, X42 ERW (TESTED 2/8/96)
| 99-169 - |  |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-11-26 | 1999-11-27 | Other | 6' 8 1/4" TESTED FINE | Steel |  | GLENN | INTERMITENT PITTING OBSERVED IN PIECE REMOVED AT 6 O'CLOCK BOTTOM
| 97-16901-1 | 169 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  |  | 1997-09-22 | Replace Pipe |  | Steel |  | PRINCETON | REPLACED 2 FEET WITH PRETESTED .3/2" WALL API 5LX, X42 ERW (TESTED 2/8/96) (SINGLE PIT)
| 03-16901-1 | 169 |  | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion | SUSPECT INT. CORROSION | 2003-12-01 | [5 empty] | E/O WILLOWS | RICE FIELD 100YDS S/E V-230
| 98-169-3-1 | 169 |  | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-07-01 | 1998-11-06 | Replace Pipe |  | Steel |  | WILLOWS | INSTALL 4' PIECES TO REPAIR LEAK
| 98-16902-1 | 169 |  | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-06-07 | 1998-06-18 | Replace Pipe |  | Steel |  | WILLOWS | REPAIRED LEAK 163" TESTED PIPE X65 .312 WT. SCHEDULE REPAIRS W/GC.
| 05-16901-1 | 169 | 5.1 | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2005-04-11 | 2005-04-23 | Other | WELDED NEW PIPE SECTION |  |  | E/O WILLOWS | RICE FIELD 99 YDS S/E V-230. (SMALL MUD BUBBLES): CUT OUT & REPLACED 179' - 6" OF 16" L-169
| 03-16901-1 | 169 |  | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion | SUSPECT INT. CORROSION | 2003-12-01 | 2003-12-03 | Welded Sleeve/Can - Weld |  |  |  | E/O WILLOWS | RICE FIELD 100 YDS S/E V-230: CUT OUT AND REPLACED WITH 81'/4" OF EMERGENCY PIPE (.1" W.T.)
| 05-16901-1 | 169 |  | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2005-04-11 | 2005-04-23 | Other | WELDED NEW PIPE SECTION |  |  | E/O WILLOWS | RICE FIELD 99 YDS S/E V-230. (SMALL MUD BUBBLES): CUT OUT & REPLACED 179' - 6" OF 16" L-169
| 08-16901-1 | 169 | 2.08 | 12.75 | Transmission |  | Body of Pipe |  |  |  |  | 2008-03-31 | 2008-04-01 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | GLENN | INSTALLED SLEEVE OVER PUNCTURED HOLE IN PIPE: FARMER WAS DIGGING OUT BOTTOM OF DIBCER WITH A V-DITCHER PLOW WHEN HE STRUCK STEEL MAIN CAUSING THE LEAK. LINE MARKERS PRESENT 6 FEET EITHER SIDE OF DAMAGED PIPELINE.
| 08-16901-1 | 169 | 2.08 | 12.75 | Transmission |  | Body of Pipe |  |  |  |  | 2008-03-31 | 2008-04-01 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | GLENN | INSTALLED SLEEVE OVER PUNCTURED HOLE ON PIPE: FARMER WAS DIGGING OUT BOTTOM OF DIBCER WITH A V-DITCH PLOW WHEN HE STRUCK STEEL MAIN CAUSING THE LEAK
| 08-16902-1 | 169 |  | 0 | Transmission |  | Valves |  |  | Other | VALVE | 2008-06-05 | 2009-09-23 | Other | SEALED CONDUITS IN SPLICE BOX FOR V-20 | Steel/Wrought Iron |  | CHICO | SEALED CONDUITS FOR V-20 SPLICE BOX
| 09-16091-1 | 169 |  | 0.5 | Transmission |  | Fitting |  |  | Construction Defect |  |  | 2009-11-06 | Other | INSTALLED NEW SEALANT TAPE ON BUSHING SOAP TEST "NO LEAKS" | Steel/Wrought Iron |  | NEAR CHICO | INSTALLED NEW SEALANT TAPE ON BUSING- SOAP TEST "NO LEAKS"
| 02-17201-1 |  |  | 18 | Transmission |  | Unknown |  |  | Unknown |  | 2002-05-29 | [5 empty] | ARBUCKLE | LEAK LOCATED IN TOMATOE FIELD- AREA WAS BARRICADED OFF.: PIPE APPEARS TO BE ERW PIPE NOT DSAW
| 02-17201-1 |  |  | 18 | Transmission |  | Unknown |  |  | Unknown |  | 2002-05-29 | [5 empty] | ARBUCKLE | LEAK LOCATED IN TOMATOE FIELD- AREA WAS BARRICADED OFF.
| 02-17201-1 |  |  | 18 | Transmission |  | Unknown |  |  | Unknown |  | 2002-05-29 | 2002-05-29 |  |  |  |  | ARBUCKLE | LEAK LOCATED IN TOMATOE FIELD- AREA WAS BARRICADED OFF.
|  |  |  | 0.06 | Gathering |  | Other |  | PP | Other | C | 1990-07-30 | 1990-07-31 | Replace Pipe |  | Steel |  | ARBUCKLE | REPLACED 3' OF 6" PIPE 0188
| 92-174-1 | [10 empty] | 1992-01-28 | [5 empty] | ARBUCKLE
| 92-174-2 | [10 empty] | 1992-01-28 | [5 empty] | ARBUCKLE
| 92-174-3 | [10 empty] | 1992-01-28
| 92-174-3 | [10 empty] | 1992-01-28 | [6 empty] | REPL. 3' OF PIPE
| 92-17403-1 |  |  | 6.62 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-01-28 | 1992-01-23 | Replace Pipe |  | Steel |  |  | REPL. 3' OF PIPE TESTED ON GM 481110-5
| 96-17401-1 |  |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1996-03-09 | 1996-03-09 | Replace Pipe |  | Steel |  | MERIDIAN | REPLACED 30" .219 3.5 OF TESTED PIPE (EMERGENCY STOCK)
| 00-17401-1 | 174 |  | 10 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 06/60/2000 | 2000-08-01 | Other | WELD CAP |  |  | ARBUCKLE | SUSPECT INTERNAL CORROSION IN ORCHARD AREA: WELD CAP WITH SOV-A-IN. TO ACA 4' STUR WITH OLD PIPE
|  |  |  | 10 | Gathering |  |  |  |  | Unknown |  | 2003-05-16 | [5 empty] | ARBUCKLE | LEAK FOUND DURING YEARLY SURVEY- DRAWING # 082647 REV. 19 LEAK AREA BETWEEN V-16 & V-13, INCLUDING 16" OFFSET DRIP. LEAK ISOLATED AND BLOWN DOWN TO 100 PSIG, AWAITING REPAIR
| 06-17401-1 | 174 |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2006-05-08 | 2006-05-23 | Other | CUT & CAP | Other | V42 | ARBUCKLE | SUSPECT INTERNAL CORROSION
| 06-17401-1 | 174 |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2006-05-08 | 2006-05-23 | Other | CUT & CAP | Other | X42 | ARBUCKLE | SUSPECT INTERNAL CORROSION
| 08-17701-1 | 177 |  | 0.25 | Transmission |  | Fitting | Valves |  | Other |  |  | 2009-09-16 | Other | TIGHTENED FITTING - EXERCISED VALVE | Steel/Wrought Iron |  | CHICO | EXERCISED VALVE AND TIGHTENED 1/4" TUBE FITTING, SOAP TEST- NO LEAKS
| 09-17701-1 | 177 |  | 1 | Transmission |  | Valves |  |  | Unknown |  | 2009-06-22 | 2009-09-16 | Other | OPERATED VALVE - STEM LEAK STOPPED | Steel/Wrought Iron |  | NEAR CHICO | EXERCISED TWO MOST NORTH VALVES IN FRAME AND COVERS ON THE NORTH EAST CORNER OF FELL STATION LEAKS STOPPED. 9-16-09 MWR4
| 09-17702-1 | 177 |  | 0.25 | Transmission |  | Fitting | Valves |  | Other |  | 2009-06-22 | 2009-09-16 | Other | TIGHTENED FITTING - EXERCISED VALVE | Steel/Wrought Iron |  | NEAR CHICO | EXERCISED VALVE AND TIGHTENED 1/4" TUBE FITTING SAOP TEST- NO LEAKS
| 99-19301-1 | 193 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-01-05 |  |  |  | Steel/Wrought Iron |  | KIRKWOOD | ISOLATED AND BLOWN DOWN. AWAITING SASONAL STREAM TO BECOME DRY AND AWAITING PRODUCER PAYMENT FOR REPAIRS. C BUSH: 6" l-193 PARALLEL TO 10" L-177 GATHERING LINE IN RIE CREEK FIELD BETWEEN VALVES # 13 & #15:
| 99-19300-1 | 193 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-01-05 |  |  |  | Steel/Wrought Iron |  | KIRKWOOD | ISOLATED AND BLOWN DOWN. AWAITING SEASON STREAM TO BECOME DRY AND AWAITING PRODUCER PAYMENT FOR REPAIRS. C BUSH
| 95-19301-1 | 193 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-05-23 | 1995-05-25 | Other |  | Steel |  | KIRKWOOD
| 02-19301-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-01-03 | [5 empty] | W/O ORLAND | BUBBLES IN CREAK
| 98-2091-1 | 209 |  | 4 | Transmission |  | Valves |  |  | Other |  | 1998-05-11 | 1998-05-12 | Tighten Cap or Bolt |  | Steel |  | WILLOWS | FOUND A SLIGHT LEAK ON THE MUELLER TEE CAP. TIGHTENED BRASS PLUG/VALVE, DOPED CAP AND TIGHTENED. (SENSING TAP FOR EAST GAUGE PRESSURE). ISOLATED AND BLEW DOWN. REPAIRED NEXT DAY.
| 04-19301-1 |  |  | 6.625 | Gathering |  | Unknown |  |  | Unknown |  | 2004-02-24 | 2004-03-23 | Other | LEAK SECTION |  |  | ORLAND | FLOODED RANGE LAND (SMALL BUBBLES): LEAK SECTION RETURED C/O 6" AT ROAD 7 TO RETIRE # 12-1 LEAK; LEAK SECTION = CUT, CAPPED, PIGGED OUT, INERTED AND RETIRED. DID NOT EXCAVATE FLOODED FIELD TO PERFORM LEAK INSPECTION. CB.
| 04-19301-1 | 193 |  | 6.625 | Gathering |  | Unknown |  |  | Unknown |  | 2004-02-24 | 2004-03-24 | ABANDON | LEAK SECTION |  |  | ORLAND | SMALL BUBBLES IN FIELD (FLOODED) OVER R/W; G/O AT ROAD 7 TO RETIRE 12-1 & LEAK. UPRATED 6" TO TP PRESSIRE TO FEED HIGH-HIGH SET. INSTALLED 1" VALVE TEE.
| 04-19302-1 |  |  | 4 | Gathering | [6 empty] | 2004-10-05 | 2004-10-13 |  |  |  |  | N/W ORLAND | REPAIRED WITH 45" OF .280 SANDS BACKGROUND TO .156; NOTE: PIPE BACKGROUND TO MATCH EXISTING .150 PIPE.
| 04-19302-1 |  |  | 4 | Gathering | [6 empty] | 2004-10-05 | 2004-10-13 |  |  |  |  | N/W ORLAND | REPAIRED WTIH 45" OF .280 SANDS BACKGROUND TO .156
|  |  |  | 6.62 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  |  |  | Replace Pipe |  | Steel |  |  | EXCAVATE, REPAIRED AND BACKFILLED IN STD 2' OF 6.625"00X.188 42EW PIPE FROM TEST PIPE SGM4808010
|  |  |  | 6.62 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  |  |  | Replace Pipe |  | Steel |  |  | EXCAVATE, REPLACED, BEVELLED, 2' OF 6.625' PIPE WITH 6.625" ON X.188 W.T. FROM TESTED PIPE ON GM 4808010
11 | 93-302-2 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  |  | 1993-01-11 | Replace Pipe |  | Steel |  | GRIMES | INSTALLED 34" OF 8" .188" WALL PRESTESTED PIPE TO REPLACE LEAK
|  | 302 |  |  | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1990-12-15 | 1990-02-15 | Replace Pipe |  | Steel |  | GRIMES | REPLACED WITH 102" OF 12,750 OD X.330 WT GX 42EW PRESTEST PIPE FROM STORE 280
|  | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 1990-04-09 | 1990-04-10 | Replace Pipe |  | Steel |  | GRIMES | REMOVED & REPLACED 42" 6.625 PIPE W.T. 0.188 PPI 5LX X42 ERW. PIPE PRETESTED ON ARBUCKLE HYDRO TEST JOB
11 | 93-302-4 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-01-22 | 1993-01-22 | Replace Pipe |  | Steel |  | MERIDIAN | REPLACED 42" OF 8" .219 PRETESTED PIPE TO REPLACE LEAK
|  | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1990-05-09 | 1990-05-10 | Replace Pipe |  | Steel |  |  | REPLACED 51' - 2" 8" PIPE WITH NEW PIPE
| 93-302-6 |  |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-02-02 | 1993-02-02 | Replace Pipe |  | Steel |  | MERIDIAN | INSTALLED 26" OF 3" .156 WALL PRETESTED PIPE
11 | 93-302-8 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-02-12 | 1993-02-12 | Replace Pipe |  | Steel |  | GRIMES | INSTALLED 40" OF 8" .188 WALL TO REPLACE LEAK
11 | 93-302-9 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-02-25 | 1993-02-25 | Replace Pipe |  | Steel |  | GRIMES | INSTALLED 47" OF 6" .188 WALL PIPE TO REPLACE LEAK
11 | 93-302-10 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-03-10 | 1993-03-10 | Replace Pipe |  | Steel |  | GRIMES | INSTALL 34" OF6" .188 WALL TO REPLACE LEAK
|  | 302 |  | 16 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1990-10-17 |  | Other |  | Steel |  |  | REPLACED 4 FT SECTION OR 16" L-302 TESTED 8-1-90 AT W80 PSIG API 5LX GR X-42 ERW .375 W.T.
|  |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  |  | 1990-09-26 | Replace Pipe |  | Steel |  |  | CUT OFF 6" STUB 8' LONG & WELD 6" CAP ON TEC
11 | 93-302-11 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-03-13 | 1993-03-13 | Replace Pipe |  | Steel |  | GRIMES | INSTALL 38" OF 6" .188 WALL PIPE TO REPLACE LEAK
|  | 302 |  | 16 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1990-10-17 |  | Other |  | Steel |  |  | REPLACED 3 FT. SECTION OF 16" L-302 REPLACED WITH 3FT. PIECE OF API SLX GRX42ERW.375 W.T. T
11 | 93-302-12 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-03-17 | 1993-03-17 | Replace Pipe |  | Steel |  | MERIDIAN | INSTALLED 29" OF 4" .188 WALL TO REPLACE LEAK
|  |  |  | 16 | [8 empty] | 1990-11-02 | [5 empty] | REPLACED PIPE WITH NEW SECTION 78 1/2" LONG 375 WILL 16" PIPE
11 | 93-30213-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1993-05-12 | 1993-05-19 | Replace Pipe |  | Steel |  | GRIMES | INSTALLED 2'-7" OF PRETESTED 6.625" 00 X 0.219" /NT API SLX 6RX-42 ERIN TO REPLACE LEAK
| 90-30214-1 |  |  | 6.62 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1991-02-12 | 1991-02-13 | Replace Pipe |  | Steel |  | MERIDIAN | REPAIRED LEAK - REPLACED LEAK WITH 3' SECTION OF 6.625" OD 0.188 WT API SLX-X42 PRETESTED PIPE
| 91-30214-1 | [10 empty] | 1991-02-12 | 1991-02-14 |  |  |  |  | COLUSA CO. | REPAIRED LEAK - REPLACED LEAK WITH 3' SECTION OF 6.625" ODX 0.188 WT API SLX-X42 PRETESTED PIPE-
| 91-30215-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1991-03-27 | 1991-05-06 | Patch Welded |  | Steel |  | MERIDIAN | START DATE 3-28-91 COMPLETE 5-6-91
| 91-30216-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1991-05-05 | 1991-11-12 | Replace Pipe |  | Steel |  | SUTTER CO | REPLACED LEAK WITH 2' SECTION OF PRETESTED 4.5" ODX 0.188 WT AP 15L6RBERW
| 94-30217-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-05-04 | 1994-05-17 | Replace Pipe |  | Steel |  | COLUSA | GM 4168837 INSTALLED 3914 FEET OF NEW 4" L-302. THE NEW PIPE REPLACED THE LEAK SECTION
| 93-30218-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-08-24 | 1993-08-24 | Replace Pipe |  | Steel |  | COLUSA CO. | REPLACED 24" OF MAIN W/ 6" .219 PRETESTED PIPE
|  |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1991-06-24 |  | Replace Pipe |  | Steel |  |  | REPLACED LEAKING PIPE WITH 2'-11" OR PRETESTED 6" X 0.188 WT API5LX 6RX-42 ERW STL PIPE
| 91-30219-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1991-10-07 | 1991-11-12 | Replace Pipe |  | Steel |  | SUTTER CO. | REPLACED WITH 2' SECTION OF PRETEST 4.5" OD X 0.188" WT AP15l6R BERW
| 91-30220-1 | 302 |  | 8.625 | [7 empty] | 1991-10-08 | 1991-11-12 |  |  |  |  | SUTTER CO | WELL ABANDONED LINE CUTE & CAPPED - AREA OF LEAK ABANDONED. PIPE ABANDONED ON WO 49357A.
| 91-30221-1 | 302 |  | 8 | [7 empty] | 1991-10-22 | 1991-11-12 |  |  |  |  | COLUSA CO | ABANDONED LINE REPLACED ON GM4964730. PIPELINE REPLACED ON GM 4964730.
| 91-30222-1 | 302 |  | 12.75 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  |  | 1991-11-12 | Replace Pipe |  | Steel |  | COLUSA CO | REPLACED LEAKING PIPE WITH PRETEST 12" (2')
|  | 302 |  | 4.5 | [8 empty] | 1991-11-21 |  |  | Steel-Other |  |  | REPLACED LEAKING PIPE WITH 2' - 4" PRE TESTED 4.5" ODK 0.188 WT API SLK GRY .42
|  |  |  | 4.5 | Gathering |  | Body of Pipe |  |  | Other | C | 1992-02-18 | 1992-02-18 | Replace Pipe |  | Steel/Wrought Iron |  |  | REPLACED 3' OF 4" PIPE WITH NEW 4" PIPE PRETESTED O.188 OFF FRANKLIN RL JOB.
| 92-302-1 |  |  | 4.5 | Gathering |  | Body of Pipe |  |  | Other | C | 1992-02-18 | 1992-02-18 | Replace Pipe |  | Steel/Wrought Iron |  |  | REPLACED 3' OF 4" PIPE WITH NEW 4" PIPE PRETESTED O.188 OFF FRANKLIN RL JOB.
| 95-30204-1 |  |  | 6 |  |  | Body of Pipe |  |  | Other | C | 1992-02-20 | 1992-02-21 | Replace Pipe |  | Steel/Wrought Iron |  |  | REPLACE 32" 6" PIPE WITH NEW 6" 0.188 PIPE PRETESTED ON GM 4876652
| 92-30204-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Other | C | 1992-02-20 | 1992-02-21 | Replace Pipe |  | Steel/Wrought Iron
92-3024-1 |  |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-02-01 | 1992-02-03 | Replace Pipe |  | Steel/Wrought Iron |  |  | REPAIRED LEAK WITH 5.5" PRETESTED 8.625" ODX 0.219 WT APT SLGF LPW.
|  |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  |  | 1992-02-05 | Replace Pipe |  | Steel/Wrought Iron |  |  | REPLACED 96" 6" PIPE 0.188 WITH PRETESTED 0.250 6" FROM KELLER RANCH JOB. GM4811188 TESTED AT 2195 PSI
| 92-30202-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-02-04 | 1992-02-05 | Replace Pipe |  | Steel/Wrought Iron |  |  | REPLACED 96" 6" PIPE 0.188 WITH PRETESTED 0.250 6" FROM KELLER RANCH JOB. GM4811188 TESTED AT 2195 PSI;
| 92-30206-1 |  |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-03-03 | 1992-03-03 | Replace Pipe |  | Steel/Wrought Iron |  |  | REPLACED 3 FT OF 4" WITH PRETESTED PIPE FROM GM 4876645.
| 92-30307-1 | 302 |  | 6.62 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-03-17 | 1992-03-18 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPLACED 60" OF 6" X .188 WITH PRETESTED PIPE.
| 92-30209-1 |  |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-04-28 | 1992-04-30 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REMOVED 36" OF 4" AND REPLACED WITH 4" PRETESTED ON GM 487665-2
| 92-30210-1 |  |  | 6.62 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-05-28 | 1992-05-29 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN
| 92-30212-1 |  |  | 6.25 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-06-24 | 1992-06-24 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPLACED 5 FT OF 8" WITH 8" X X-42 ECW STL PIPE ON GM 4811105.
| 92-30211-1 |  |  | 8.62 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-06-23 |  | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPLACED 90" OF 8" X .219" X-42 ECW STL PIPE TO REPLACE LEAKING PIPE.
| 92-30214-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1992-07-26 | 1992-07-27 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES
| 92-302 -1 |  |  | 4.5 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1992-10-06 | 1992-10-07 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES
| 92-30217- |  |  | 6.62 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1992-10-20 | 1992-10-20 | Replace Pipe |  | Steel/Wrought Iron |  |  | REPLACED WITH 3' OF PRETESTED PIPE.
| 92-30218-1 |  |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-12-07 | 1992-12-07 | Replace Pipe |  | Steel/Wrought Iron |  | COLUSA CO | REPLACED 4' OF 4" WITH 4" X .156" GR B ECW PIPE TESTED ON GM 480809-3.
| 93-3011-1 | 302 | [9 empty] | 1993-01-08 | [6 empty] | PIPE ABANDONED ON WO 43663B
| 93-30203- |  |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-01-21 | 1993-01-22 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPLACE 2' OF 4" PIPE PRETESTED GM 404458-2
| 93-302-5- | 302 |  | 6.25 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-01-27 | 1993-01-28 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | INSTALLED 2F 6" .219" WT. 60011056 - TESTED.
| 93-302-7 | 302 |  | 6.62 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-02-01 | 1993-02-01 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPLACED WITH 2 FT OF PRETESTED 6" ON GM 496531-5
| 93-30214-1 |  |  |  | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-07-21 | 1993-07-22 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPLACED ONE FOOT WITH PRETESTED PIPE. (4" .188) SMALL PIN HOLE ON BOTTOM.
| 93-30215-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-07-26 | 1993-07-28 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPLACE LEAKING PIPE WITH 35" OF 4 1/2" OD X 0.188 PRETESTED PIPE.
| 93-30216-1 | 302 |  | 10 | Gathering |  | Body of Pipe |  |  | Other | C |  | 1993-07-27 | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER | REPLACE LEAKING PIPE WITH 34" OF 10.750" OD X 0.219" WT API SLX X-52 ERW PRETESTED PIPE.
| 93-30217-1 | 302 |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-07-28 | 1993-08-04 | Other |  | Steel/Wrought Iron |  | MERIDIAN | ABANDONED PIPE ON WO 44234B
| 93-30219-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-09-09 |  | Replace Pipe |  | Steel/Wrought Iron |  | COLUSA | REPLACED 35" OF 8" TO REPAIR LEAK. REPLACED WITH 8" .219 PRETESTED PIPE. API SL X42 ERW.
11 | 93-30220-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-10-25 | 1993-10-26 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPLACED LEAK WITH 30" OF 6" .219" WALL PRETESTED PIPE
11 | 93-30222-1 | 302 |  | 3.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-11-26 |  | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER | REPLACED LEAK WITH 24" OF 3 1/2" PRETESTED PIPE
11 | 93-30223-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1993-12-16 | 1993-12-17 | Replace Pipe |  | Steel/Wrought Iron |  | S/O GRIMES | REPLACED 36" WITH .219 PRETESTED PIPE
| 94-302-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-02-04 | 1994-02-09 | Replace Pipe |  | Steel/Wrought Iron |  | E/O GRIMES | INSTALLEED 40" OF 6.625"X0.219 TO REPAIR LEAK
| 94-30202-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-03 |  | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER | WILL MONITOR AND PREPARE JOB FOR PIPELINE REPLACEMENT; 8" 8.625 API 5LX X46
| 94-30203-1 | 302 |  | 10 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-03 |  | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER | WILL MONITOR AND PREPAREM JOB FOR PIPELINE REPLACEMENT; 10" .219 WALL API 5L X52
| 94-30204-1 | 302 |  | 10 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-03 |  |  |  | Steel/Wrought Iron |  | SUTTER | WILL MONITOR AND PREPARE JOB FOR PIPELINE REPLACEMENT.; 10.750" .219 WALL API 5L X52
| 94-30205-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-07 | 1994-02-08 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | INSTALLED 2' OF 4" PRETESTED PIPE .188" WALL
| 94-30206-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-07 | 1994-03-08 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | INSTALLED 2' OF PRETESTED 4" .188 WALL
| 94-30207-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-07 | 1994-03-08 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | INSTALLED 2' OF PRETESTED 4" .188 WALL
| 94-30208-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-07 | 1994-03-09 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | INSTALLED 2' OF 4" PRETESTED .188" WALL PIPE
| 94-30209-1 | 302 |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-11 | 1994-03-15 | Replace Pipe |  | Steel/Wrought Iron |  |  | INSTALLED 48" OF 4" .188" WALL PRETESTED PIPE; 4" L-302 ON MORRIS ROAD 1287 FEET FROM RISER VALVE AT GOV 7-4
| 94-30210-1 | 302 |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-11 | 1994-03-15 | Replace Pipe |  | Steel/Wrought Iron |  |  | INSTALLED 24" OF 4" .188 WALL PRETESTED PIPE; 4" L-302 ON MORRIS ROAD 1040 FEET FROM RISER VALVE AT GOV 7-4
| 94-30211-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-15 | 1994-03-16 | Replace Pipe |  | Steel/Wrought Iron |  |  | INSTALLED 3' OF 6" .188 PRETESTED PIPE; 6" L-302 ON PASS ROAD (SOUTHSIDE) 845 FEET WEST OF V-345
| 94-30212-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-03-22 | 1994-04-13 | Replace Pipe |  | Steel/Wrought Iron |  |  | CUT OUT AND REPLACED 36" OF 8" PIPE WITH PRETESTED PIPE; 8" L-302 WHITE ROAD 1/2 MILE WEST OF V-227; 160' EAST OF CORROSOMETER PROBE
| 94-30213-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-04-07 | 1994-04-11 | Replace Pipe |  | Steel/Wrought Iron |  |  | REPLACED 3' OF POPE W/ PRETESTED PIPE TO REPAIR LEAK; 4" l-302, 2088FT WEST OF BROWNING #7
| 94-30214-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-04-29 | 1994-04-11 | Replace Pipe |  | Steel/Wrought Iron |  | COLUSA | INSTALLED 12'3" OF PRETESTED 6" .188 WALL PIPE (REPAIRED W/ #94-302-15)
| 94-30215-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-05-02 | 1994-05-02 | Replace Pipe |  | Steel/Wrought Iron |  | COLUSA | INSTALLED 12'3" OF PRETESTED 6" .188 WALL PIPE; (REPAIRED W/ #94-302-16, #94-302-14)
| 94-30216-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-05-02 | 1994-05-02 | Replace Pipe |  | Steel/Wrought Iron |  | COLUSA | INSTALLED 12'3" OF PRETESTED 6" .188 WALL PIPE (REPAIRED W/#94-302-15, 94-302-14)
| 91-30217-1 | [10 empty] | 1991-06-13 | [6 empty] | 300' S/O SCIORTINO I-33; LEAK REPAIRED BY PIPE LINE REPLACEMENT JOB GM 4964508
| 94-30218-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-05-04 | 1994-05-10 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | INSTALLED 26" X 4" NEW PRETESTED PIPE .188" API 5LX42 ERW
| 94-30218-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-05-04 | 1994-05-10 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | INSTALL 26" X 4" NEW PIPE FOR LEAK REPAIR .188 API 5L X 42 EEW
| 94-30219-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-05-05 | 1994-05-10 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | INSTALLED 38" X 4" NEW PRETESTED PIPE .188" API 5LX42ERW
| 94-30219-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-05-05 | 1994-05-10 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | INSTALL 38" X 4" NEW PIPE FOR LEAK REPAIR .188 API 5LX42ERW
11 | 94-30220-1 | 302 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-06-10 | 1994-06-22 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPLACED 9'2" OF 12" W/9'2" OF PRETESTED .250 WALL
11 | 94-30221-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-06-10 |  | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER | INSTALLED NEW RISER AND 11' OF PRETESTED 4" PIPE
11 | 94-30222-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-06-22 |  | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | INSTALL 2' OF 4" PRETESTED PIPE
11 | 94-30223-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-06-29 | 1994-07-01 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPLACED 185' OF 6" .219 WALL PRETESTED PIPE (TESTED ON ??? 4045100 5-2-94)
11 | 94-30223-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-06-29 |  | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES
11 | 94-30223-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-06-26 | 1994-07-01 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | REPLACED 185' OF 6" .188 W/ 185' OF 6" .219 WALL PRETESTED PIPE (TESTED ON GRM 4045100 5-2-94)
11 | 94-30224-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-06-30 | 1994-07-12 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | INSTALLED 2' OF 4" .188" WALL PRETESTED PIPE
11 | 94-302-25 | 302 |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-07-18 |  | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN
11 | 94-30227-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-08-30 | 1994-08-30 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | INSTALLED 48" OF 6" .188 PRETESTED PIPE TO REPAIR LEAK
11 | 94-30228-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-08-30 | 1994-08-31 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPLACED 5' W/.188" WALL 6" PRETESTED PIPE TO REPAIR LEAK
11 | 94-30229-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-08-30 | 1994-09-01 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | TIE-IN 120' OF NEW 4" BORED UNDER TAR DITCH IN ORDER TO REPAIR LEAK IN 6" MAIN
11 | 94-30230-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-09-01 | 1994-09-08 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REMOVE 61' PF 6" AMD REPLACED WITH 9" .188 DO TO HEAVY PITTING. THIS EXISTING TO THE LEAK; 1-94-302-31
11 | 94-30230-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-09-01 |  | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN
11 | 94-30231-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-09-01 | 1994-09-08 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPLACED 61' OF 4" .188 FROM LEAK # 94302-30 TO THIS LEAK REPORT
11 | 94-30231-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-09-01 |  | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN
11 | 94-30232-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-09-01 | 1994-09-08 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPAIRED 6" LEAK WITH 24" OF .188 PIPE WITH SAV-A-VALVE
11 | 94-30232-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-09-01 |  | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN
11 | 94-30233-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-09-01 | 1994-09-09 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPAIR LEAK WITH 38" OF .188 WALL WITH SAV-A-VALVE
11 | 94-30233-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-09-01 |  | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN
11 | 94-30234-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-09-01 |  | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN
11 | 94-30235-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-09-22 | 1994-09-22 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPLACED 40" OF 6" W/ PRETESTED 6" .188 WALL PIPE
11 | 94-30236-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-09-22 | 1994-09-22 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | EXCAVATED AND NO LEAK FOUND. C. BISH / J. WATERS
11 | 94-30237-1 | 302 |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1994-10-11 | 1994-10-11 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | INST 3" CAP TO 219 PIPE
11 | 95-30201-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-01-10 |  | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN
11 | 95-30202-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-01-10 | 1995-01-25 | Replace Pipe |  | Steel/Wrought Iron |  | S/O GRIMES | INSTALLED 4' OF PRETESTED PIPE FROM GM 435966-7
11 | 95-30203-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-01-11 |  | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN
11 | 95-30204-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-01-11 |  | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN
11 | 95-30205-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-01-11 | 1995-01-12 | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN | REPLACE 38" OF PRETESTED PIPE
19 | 91-10006-1 | 169 |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1991-01-19 | 1992-04-27 | Replace Pipe |  | Steel/Wrought Iron |  | GLENN CO. | WO49348-A REPLACED 54" OF 4" LINE 169 AT LEAK
19 | 91-10006-1 | 162 |  |  | Gathering | [6 empty] | 1991-01-19 |  | Replace Pipe |  | Steel/Wrought Iron |  | GLENN CO.
|  | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1992-03-24 | 1992-03-25 | Other |  | Steel/Wrought Iron |  | SUTTER | REPLACED PIPE
|  | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1994-03-23 | 1992-03-26 | Other |  | Steel/Wrought Iron |  | SUTTER | CUT UP 5' STUB
|  | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1992-03-24 | 1992-03-25 | Other |  | Steel/Wrought Iron |  | SUTTER | REPLACED PIPE
|  | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1989-12-28 |  |  |  | Steel/Wrought Iron |  | S/O COLUSA | 400' SOUTH OF COLUSA UNITS 2-2 AND 2-4
|  | 302 |  |  | Gathering |  |  |  |  | Corrosion |  | 1988-06-17 |  |  |  | Steel/Wrought Iron |  |  | N/S FRANKLIN RD. LINE TO BROWN #1 GAS WELL; IN RICE FIELD N/OF FRANKLIN RD
|  | 302 |  | 3 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1987-12-07 | 1987-12-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron
| 88-90065-1 | 302 |  |  | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1988-09-16 |  |  |  | Steel/Wrought Iron |  | MERIDIAN | ISOLATE LEAKING LINE.
|  | 302 |  | 3 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1987-12-07 | 1987-12-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  | 302 |  | 10 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1988-11-12 | 1988-11-03 | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER CO | REPLACE BAD SECTION OF PIPE WITH NEW 10" PIECE. 2 FEET OF NEW PIPE INSTALLED.
11 | 96-30205-A | 302 |  | 6 | Gathering | [6 empty] | 1996-02-29 |  |  |  | Steel/Wrought Iron |  | COLUSA | MONITOR PERIODICALLY
11 | 95-30206-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-01-17 |  | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES
11 | 95-30207-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-01-24 |  | Replace Pipe |  | Steel/Wrought Iron |  |  | 200 YDS S/O NL&F #1-8 MASTE4R METER NEAR OSWALD & BROWN ROADS
11 | 95-30208-1 | 302 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-01-30 | 1995-02-08 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | FOUND PRODUCERS 2 1/2" PLASTIC THAT CROSSES OVER THE TOP OF THE Pg&e LINE TO BE LEAKING. PRODUCER REPAIRED PLASTIC.
11 | 95-30209-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-02-03 |  | Replace Pipe |  | Steel/Wrought Iron |  | N/O GRIMES
11 | 95-30210-1 | 302 |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-02-03 |  | Replace Pipe |  | Steel/Wrought Iron |  | S/O GRIMES
11 | 95-30211-1 | 302 |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-02-08 | 1995-04-05 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | INSTALLED 26" PRETESTED 4.50 .188 WT GM 199835-0
11 | 95-30212-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-02-17 |  | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES
11 | 95-30213-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-02-26 |  |  |  | Steel/Wrought Iron |  | COLUSA
11 | 95-30213-1 | 167 |  | 6.625 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-02-09 |  | Replace Pipe |  | Steel/Wrought Iron |  | PRINCETON
11 | 95-30214-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-05-03 |  | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN
11 | 95-30216-1 | 302 |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-05-10 |  | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN
11 | 95-30217-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-06-21 |  | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN
11 | 95-30218-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-06-21 |  | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN
11 | 95-30208-1 | 302 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-01-30 | 1995-02-03 | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | INTALLED 4' 12" & 23' 8" PRETE4STED PIPE GM 119398-6
11 | 95-30220-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-06-27 |  | Replace Pipe | ; | Steel/Wrought Iron |  | GRIMES
11 | 95-30221-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-06-27 |  | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES
11 | 95-30222-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-07-12 |  | Replace Pipe |  | Steel/Wrought Iron |  | MERIDIAN
11 | 95-30223-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1995-07-20 |  | Replace Pipe |  | Steel/Wrought Iron |  | S/E OF MERIDIAN
|  |  |  | 3 | Gathering |  |  |  |  | Corrosion |  | 1988-06-17 |  |  |  | Steel/Wrought Iron |  |  | N/S FRANKLIN RD. LINE TO BROWN #1 GAS WELL; IN RICE FIELD N/OF FRANKLIN RD; 253' FROM CENTER LINE OF RD
|  | 302 |  | 3 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1987-12-07 | 1987-12-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1988-06-17 | 1988-06-17 | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER CO | REPLACED 8 FT OF 6" L-302; ISOLATE SECTION L-302.
|  | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1988-12-12 |  | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER | LEAK APPROX 30 YDS S/W OF BUTTES 81-83.
|  |  |  | 6 | [11 empty] | Other |  | AUBURN | NORTH TIE-IN LOC.
|  | 173 |  | 6 | [13 empty] | AUBURN | SOUTH TIE-IN LOC.
|  |  |  | 4.5 | [8 empty] | 1997-02-21 |  |  | Steel |  |  | CUT DWN CAP @ L414 TO ABAN. BROWNING 7-8 GAS WELLS
|  |  |  | 4 | [8 empty] | 1996-09-17 |  |  | Steel |  |  | ABANDON ABOVE 33-1 GAS WELL. CUT/CAPPED @ VALVE
|  | 120 |  | 3.5 | [8 empty] | 1997-06-11 |  |  | Steel |  |  | CUT & CAPPED VALVE. #46 TO ABANDONED A-9-10-11 GAS WELL
|  |  |  | 3.5 | [8 empty] | 1997-06-11 |  |  | Steel |  |  | INSTALL REG TIES INTO BYSITTING 3" @ V #4 AND BACK INTO L-2" CONVERT TO DISTRIBUTION
|  |  |  | 0.75 | [8 empty] | 1997-06-11 |  |  | Steel |  |  | REMOVED OLD REG SET. THE BACK WITH 3/4" STEEL
|  |  |  | 3.5 | [8 empty] | 1996-09-12 |  |  | Steel |  |  | TIEIN POUNDSTONE 13-1 GAS WELL
|  |  |  | 4.5 | [8 empty] | 1997-04-14 |  |  | Steel |  |  | CUT & CAP @ VALVE 2. REMOVE EXSTENTION - FRICTION / COVER
|  | 302 |  | 4.5 | [8 empty] | 1997-10-14 |  |  | Steel |  |  | CUT & CAPPED VALVE
|  |  |  | 3.5 | [8 empty] | 1997-04-14 |  |  | Steel |  |  | CUT & CAPPED TAP VALVE TO ... R&B #1 GAS WELL
|  |  |  | 3.5 | [8 empty] | 1997-10-20 |  |  | Steel |  |  | CUT & CAPPED TO ABANDON ARBUCKLE 34 @ V435 - REMOVED RISER
|  |  |  | 2 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB #30669267; SOAP TEST AT LINE PRESSURE; PIG AND ABANDON 2" STL. CUT OFF RISER.
| 08-30203-1 | 302-040 | 0.54 | 12 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-07-02 | 2006-07-16 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | MERIDIAN | POUNDSTONE DRIP STATION ENTRANCE; ENTRANCE TO POUNDSTONE STATION - BUBBLES; INSTALL 70" CAN WITH SAV A VALVE; X-RAY, INSTALL 70" CAN WITH SAV-A-VALVE. PRE-TESTED EMERGENCY PIPE
|  |  |  | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  |  | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron
[5 empty] | Transmission | [13 empty] | ORIGINAL; DIDN'T EXPOSE MAIN
| 04-12801-1 | 128 |  | 4 | Transmission |  |  |  |  | External Corrosion |  | 2004-10-14 | [5 empty] | WILLOWS | EMPLOYEE FOUND LEAK WHEN LOCATING GAS LINE FOR FARMER DEAD VEGETATION.
|  |  |  | 0.04 | Transmission |  |  |  |  | Internal Corrosion |  |  | 2004-10-18 | Replace TP Main |  | Steel/Wrought Iron |  |  | REPLACED WITH 5' OF TESTED 4.5" OOX-237 GR B SAKS
| 04-30201-1 | 302 |  | 8 | Transmission |  |  |  |  | Internal Corrosion |  | 2004-10-21 | 2004-10-28 | Mechanical Repair Fitting - Fitting |  |  |  | SUTTER/ YUBA CITY | CALPINE EE SUSPECT PGE&E L-302 OF LEAK NEAR CANAL - LP&G EE VERIFIED WITH FLAME PACK UNIT. INSTALL 5" LEAK CLAMP.
[16 empty] | Steel/Wrought Iron |  |  | #7046013 S/S E. GIBSON AD 426" W/O RD102 WOODLAND
[16 empty] | Steel/Wrought Iron |  |  | #7046013 FARMHAN AVE & HUSTON CIR.
Steel/Wrought Iron
[16 empty] | Steel/Wrought Iron |  |  | INSTALLED NEW VALVES - YOLO TAP
[16 empty] | Steel/Wrought Iron |  |  | ZAMORA VALVE REPLACEMENT INSTALLED NEW VALVES
|  | 172A | [10 empty] | 2004-06-03 |  |  | Steel/Wrought Iron |  | DUNNINGUN | INSTALL 101" OF 20" W/ 8" BALL VALVE FOR KICK #2 GAS L-172A; HERSHEY KICKER GAS JOB 7046013
|  | 172 |  | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE 172 RECEIVER TIE-IN 7046013
|  | 172 |  | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L172 - REMOVE VALVE - RD. 27 7046013
|  | 172 |  | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L172 REPLACE VALVES - RD. 5 - DUNNIGAN 7046013
|  | 172 |  | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L172 - HERSHEY LAUNCHER TIE-IN 7046013
| 01-30201-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-03-09 | 2001-03-21 | Other | REPLACED |  |  | GRIMES | BUBBLES IN FIELD CLOSED VALVES TO ISOLATE - PIPING BLOWN DOWN; INSTALLED NEW 3" PIPE FROM TAP VALVE TO RISER BLOCK VALVE (PROCUREMENT) SO#6077243
| 03-17401-1 | [10 empty] | 2003-05-16 | 2003-06-04 | Other | REPLACED NEW | Steel/Wrought Iron |  |  | PIPE CAN AT V-1L GOOD - V13 CUT TO VALVE FACE - REPLACE 90 DEGREE
|  | 172 | [13 empty] | Steel/Wrought Iron |  |  | EXISTING 6" STL. LINE 172 .188 WT
[16 empty] | Steel/Wrought Iron |  |  | EXISTING 12" STL LINE 201 W.T. 280 USED DEPTH GAUGE METER
| 03-17401-1 | [10 empty] | 2003-05-16 | 2003-06-04 | Other | REPLACED NEW |  |  |  | PIPE CAN AT V-1L GOOD - V13 CUT TO VALVE FACE - REPLACE 90 DEGREES
167
| 03-16901-1 | 169 |  | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion | SUSPECT INT. CORROSION | 2003-12-01 | 2003-12-03 | Welded Sleeve/Can - Weld |  |  |  | E/O WILLOWS | RICE FIELD 100 YDS S/E V-230
|  | 169 |  | 4 | Gathering | [7 empty] | 2002-04-29 |  |  | Other | GRB SLMS |  | CUT & CAP L-169; SOAP CAP SAVE VALVE @ 100 PSI
|  |  |  | 4.5 | [8 empty] | 2002-04-26 |  |  | Other | GRB SLMS |  | REMOVE OLD VALVE 16 TIE-IN WITH NEW LINE; SOAP @ 100 PSI
|  |  |  | 3.5 | Transmission | [7 empty] | 2002-04-26 |  |  | Other | SMLS |  | REMOVE OLD VALVES - PIPING INSTALL NEW STUFF; SOAP TEST @ 100 PSI
|  |  |  | 0.4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | JOB # 40755124
|  |  |  | 12 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | BUTTE CITY | REMOVED 2" BALL VALVE FROM 2" SAVE-A-VALVE REMOVED DRIP LINE, DID NOT REMOVE WRAP FROM 12" NO WELDING
|  |  |  | 12 | Distribution | [10 empty] | Steel/Wrought Iron
|  |  |  | 12 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | PRINCETON
|  |  |  | 0.4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | JOB # 40755124
|  |  |  | 12 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | BUTTE CITY | REMOVED 2" BALL VALVE FROM 2" SAVE-A-VALVE. REMOVED DRIP LINE. DID NOT REMOVE WRAP FROM 12". NO WELDING.
|  |  |  | 12 | Distribution | [10 empty] | Steel/Wrought Iron
|  |  |  | 12 | Distribution Main | [10 empty] | Steel/Wrought Iron
|  |  |  | 4 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | INSTALLED 3" BLIND FLANGE.
[16 empty] | Steel/Wrought Iron |  |  | SEE AS-BUILT FOR C/O INFORMATION
|  | 172 |  | 0.18 | [7 empty] | 2002-11-07 | [5 empty] | COLLEGE CITY | INSTALLED WIRES FOR ETS USING SOFT DIG METHOD
|  | 172 |  | 0.18 | [7 empty] | 2002-11-07 | [5 empty] | COLLEGE CITY | INSTALLED WIRES FOR ETS USING SOFT DIG METHOD
|  |  |  | 0.18 | [7 empty] | 2002-11-06 | [5 empty] | COLLEGE CITY | INSTALLED WIRES FOR ETS USING SOFT DIG METHOD
|  | 172 |  | 0.18 | [13 empty] | ARBUCKLE | INSTALLED WIRES ON PIPE FOR ETS USING SOFT DIG METHOD
|  | 172 |  | 0.18 | [7 empty] | 2002-11-06 | [5 empty] | ARBUCKLE | INSTALLED WIRES FOR ETS USING SOFT DIG METOD
|  | 172 |  | 0.18 | [7 empty] | 2002-11-05 | [5 empty] | WILLIAMS | INSTALLED WIRES ON PIPE FOR ETS USING SOFT DIG METHOD
|  | 172 |  | 0.18 | [7 empty] | 2002-11-05 | [5 empty] | COLUSA | INSTALL WIRES ON PIPE FOR ETS USING SOFT DIG METHOD
|  | 172 |  | 0.18 | [7 empty] | 2002-11-04 | [5 empty] | COLUSA | INSTALLED WIRES ON PIPE FOR ETS USING SOFT DIG METHOD
|  | 172 |  | 0.18 | [7 empty] | 2002-11-03 | [5 empty] | COLUSA | INSTALLED WIRES ON PIPE FOR ETS USING SOFT DIG METHOD
|  | 172 |  | 0.18 | [7 empty] | 2002-11-02 | [5 empty] | COLUSA | INSTALLED WIRES FOR ETS USING SOFT DIG METHOD
|  | 172 |  | 0.18 | [7 empty] | 2002-11-01 | [5 empty] | COLUSA | INSTALLED WIRES ON PIPE BY SOFT DIG METHOD; INSTALLED WIRES FOR ETS
|  | 172 |  | 0.18 | [7 empty] | 2002-11-01 | [5 empty] | WILLOWS | INSTALLED WIRES ON PIPE FOR ETS BY SOFT DIG METHOD; INSTALLED ETS
|  | 169A |  | 0.18 | [7 empty] | 2002-10-31 | [5 empty] | WILLOWS | PUT WIRES ON PIPE FOR ETS ONLY EXCAVATED TOP OF PIPE BY SOFT DIG; INSTALLED WIRES FOR ETS
|  | 169A |  | 0.18 | [7 empty] | 2002-10-31 | [5 empty] | WILLOWS | SOFT DIG EXCAVATION OF TOP OF PIPE FORE ETS WIRES; APPLIED TWO WIRES FOR ETS; PUT ON WIRES FOR ETS
WILLIAMS
|  | 172 |  | 0.18 | [14 empty] | PLACED WIRES ON PIPE FOR ETS USING SOFT DIG METHOD; INSTALLED WIRES FOR ETS USING SOFT DIG
WILLIAMS
WILLIAMS
|  | 117A | 43.4 | [14 empty] | ARBUCKLE
|  | 172A | 45.77 | 0.18 | [14 empty] | INSTALLED WIRES FOR ETS USING SOFT DIG METHOD; INSTALLED WIRES FOR ETS
|  | 172A | 47.07 | 0.18 | [14 empty] | INSTALLED WIRES ON PIPE FOR ETS USING SOFT DIG METHOD; INSTALLED WIRES FOR ETS
|  | 172A | 52.17 | [14 empty] | WILLIAMS
|  | 172A | 68.62 | 0.18 | [13 empty] | DAVIS | INSTALLED WIRES ON PIPE FOR ETS USING SOFT DIG; INSTALLED WIRES FOR ETS
Steel/Wrought Iron
Steel/Wrought Iron
| 02-17201-1 | 172 |  | 18 | Transmission |  | Body of Pipe | Other | CRACK | Unknown |  | 2002-05-29 | 2002-06-05 | Other |  |  |  | ARBUCKLE | LEAK LOCATED IN TOMATOE FIELD - AREA WAS BARRICADED OFF; FOUND CRACK @ 3 O'CLOCK LEAKING SOUTH REPAIR #8053217 INSTALLED 59 1/2" CAP; PIPE APPEARS TO BE ERW PIPE NOT DSAW
| 02-30201-1 | 302E |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-01-10 | [5 empty] | S/O SUTTER | BUBBLES IN FLOODED RICE FIELD; NO PITTING OR COROSION ON 8" HOLE WAS IN 6" STUB SEGMENT. 3 DEGREE SEGMENT 105" TOTAL REPLACED.
|  | 167 |  |  | Transmission | [12 empty] | NEAR GRIDLEY | PIPE AND WRAP INSPECTION ONLY; SEE ATTACHED SHEETS - EXCAVATION DUE TO DUCKS UNLIMITED WATER DELIVERY PROJECT - CONCRETE CAP ALSO INSTALLED BY DUCKS UNLIMITED, OK'D BY GEORGE KARKAYES
| 01-30203-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-07 | 2001-06-15 | Welded Sleeve/Can - Weld |  |  |  | S/O GRIMES | BUBBLES IN FLOODED RICE FIELD PRODUCER SHUT-IN PRODUCTION TO ISOLATE LEAK AREA. 20 PSIG SUCTION SYSTEM U.S. OF ANDREOTTI #11 M.M.
Steel/Wrought Iron
| 99-169- |  |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-11-26 | 1999-11-27 | Other | 6' 8 1/4" TESTED PIPE | Steel/Wrought Iron |  | GLENN | FIRE IN FIELD, FIRE IN FIELD, NORTH VALLEY DIV MERIDIAN DIST. W.W. 12/27/99; REPLACE 6' 8 1/4" .250 W/T PIPE
| 99-30202-0 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-04-26 | 1999-04-30 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | GRIMES | BUBBLES IN FLOODED RICE FIELD; REPARED WITH 6' OF 20" .375 WT
| 02-30205-1 | 302 |  | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-05-08 | 2002-05-30 | Other | CAPPED & RETIRED LEAK SECTION | Steel/Wrought Iron |  | S/E MERIDIAN | BUBBLES IN FLOODED FIELD. ISOLATED AND BLEW DOWN; DID NOT REPAIR LEAK. RETIRED LEAK PIPING TO MOBIL-WOOD #4-1 S.O. #7043786; REPAIR 5-30-02
| 01-30202-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-03-12 | 2001-03-30 | Other | NEW BORE |  |  | S/O SUTTER | REPLACED LIVE DAX CANAL CROSSING WITH A NEW BORE; INSTALL NEW BORE PIPE
[16 empty] | Steel/Wrought Iron |  |  | INSTALL 3/4 SAMPLE PRORE 12" PIPE - 6" PRORE
|  | 116 |  | 16 | [11 empty] | Steel
|  | 119 |  | 12 | [11 empty] | Steel
|  | 172 |  | 16 | [11 empty] | Steel
[16 empty] | Steel/Wrought Iron |  |  | SEE ATTACHED JOB 7003659. LURLINE RD. COLUSA COLUSA COUNTY
| 02-31801-1 | 318 |  | 3 | Gathering |  | Valves |  |  | Unknown |  | 2002-03-18 | 2002-03-21 | Other | REPLACED |  |  |  | LEAK AROUD VALVE BODY (3" V-B) AT BLACK BUTTE STATION; REPLACED VALVE S.O.# 1004563; SKETCH ON ATTACHED SHEET
|  |  |  | 2 | [11 empty] | Steel
|  | 302 |  | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | CAP BOTH ENDS OF ABANDON PIPE; REFER TO W/O 4475
|  |  |  | 4.5 | Transmission |  | Other |  |  | Other |  | 1974-10-24 |  | Other |  | Steel/Wrought Iron |  |  | REFER TO W/O 4521
|  |  |  | 3.6 | Gathering |  | Other |  |  | Other |  | 1974-09-17 |  | Other |  | Steel/Wrought Iron |  | GRIMES GAS FIELD | CUT OFF AND ABANDON 3" MAIN; REFER TO W/O 4616
9 | 80-40009-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1980-04-27 | 1980-04-27 | Other |  | Steel/Wrought Iron |  |  | SEE W.O. 4489-A; LEAK @ F.S. 50+36 SHEET 302-13. 8" LINE TO 1-4 WELL.; INSPECTION @ POINT CAP WAS INSTALLED.
|  | 302 |  | 4.5 | [7 empty] | 1993-12-17 |  |  |  | Steel |  | ; ;
|  |  |  | 6.625 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel |  | GRIMES
|  |  |  | 6.625 | [11 empty] | Steel |  | GRIMES
6
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  | 302 |  | 6.625 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  | 302 |  | 6 | [11 empty] | Steel
|  | 302 |  | 6 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 3.5 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 6.625 | [11 empty] | Steel |  |  | SEE DRAWING ON BACK.
|  |  |  | 2 | [11 empty] | Steel
|  |  |  | 3.5 | [11 empty] | Steel |  | PRINCETON
|  |  |  | 4.5 | [11 empty] | Steel |  | PRINCETON
|  |  |  | 3.5 | [11 empty] | Steel |  | PRINCETON
|  |  |  | 4.5 | [11 empty] | Steel |  | GRIMES
|  |  |  | 2 | [11 empty] | Steel
Steel
|  |  |  | 2 | [11 empty] | Steel
Steel
|  |  |  | 2 | [11 empty] | Steel
Steel
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 3.5 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6.625 | [11 empty] | Steel
|  |  |  | 6.625 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 3.5 | Transmission | [8 empty] | Other |  | Steel/Wrought Iron
|  |  |  | 4 | [11 empty] | Steel |  | CAPAY
|  |  |  | 10 | [11 empty] | Steel |  | CAPAY;
|  |  |  | 3.5 | [11 empty] | Steel |  | ORLAND
|  |  |  | 4 | [9 empty] | Replace Pipe |  | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  | 302 |  | 6 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel |  |  | CUT ABOVE GROUND FON RISON VALVE. MCBURNEY 40-1 GAS WELL. COW/RD 41&W
|  |  |  | 4.5 | [11 empty] | Steel |  |  | 6' N/O RISON, MICHAEL WAYLON #1 6W
|  |  |  | 4.5 | [11 empty] | Steel |  |  | .78" N/O 3" METER TUBE RISON
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 3.5 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 3.5 | [11 empty] | Steel
|  |  |  | 3.5 | [11 empty] | Steel |  |  | CUT OFF MAIN AT TIE IN VALVE #422 AND AT SILLEW 2-21 GAS WELL (RISON)
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 2 | [11 empty] | Steel
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6.625 | [11 empty] | Steel
|  |  |  | 6.625 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel |  |  | WO 44742-B - WELL ABANDONMENT.
|  |  |  | 6 | [11 empty] | Steel |  |  | WO 44742-B 4" VALVE INSTALLATION
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
6
4
4
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 12 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 3.5 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 8 | [11 empty] | Steel
|  |  |  | 4 | [8 empty] | 1999-09-09 |  |  | Steel |  |  | REMOVE EXISTING TOP. REPLACED WITH 6' AND 4" .188 WALL TESTED PIPE
|  |  |  | 4 | [11 empty] | Steel
|  | 302 |  | 3
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel |  | DAVIS | SEEN WHEN WE ASAND WELL AND CUT RISER OUT.
|  |  |  | 8.625 | [11 empty] | Steel |  |  | GM 4811105. REPLACE 4" WITH 8" MAIN S/SIDE WHITE RD. E/S CANAL
|  |  |  | 8.625 | [11 empty] | Steel |  |  | GM 4811105. REPLACE 4" WITH 8" S/SIDE WHITE RD. WEST/S. CANAL
|  |  |  | 8.625 | [11 empty] | Steel |  |  | GM 4811105. REPLACE 4" WITH 8" S/SIDE WHITE RD. WEST/S CANAL
|  |  |  | 8.625 | [11 empty] | Steel |  |  | GM 4811105. REPLACE 4" WITH 8" MAIN S/SIDE WHITE RD. E/S CANAL
|  |  |  | 2 | [11 empty] | Steel |  | DIXON
|  |  |  | 3 | [11 empty] | Steel |  | DIXON
|  |  |  | 3 | [11 empty] | Steel
|  |  |  | 2 | [11 empty] | Steel |  |  | 2" TIE
|  |  |  | 4 | [11 empty] | Steel |  |  | 4" TIE
|  |  |  | 4 | [11 empty] | Steel |  |  | 4" TIES
|  |  |  | 4 | [11 empty] | Steel |  |  | 4" TIE
|  |  |  | 6 | [11 empty] | Steel |  |  | 6" TIE
|  |  |  | 4 | [11 empty] | Steel |  |  | BCOU 1-6 AT 6" TIE
|  |  |  | 4 | [11 empty] | Steel |  |  | BCOU 1-7 LS 4" TIE
|  |  |  | 4 | [11 empty] | Steel |  |  | BCOU 1-7 W/S 4" TIE
|  |  |  | 4 | [11 empty] | Steel |  |  | BCOU 1-6 N/S 4" TIE
|  |  |  | 4 | [11 empty] | Steel |  |  | BCOU 1-6 S/S 4"TIE
|  |  |  | 4 | [11 empty] | Steel |  | GRIMES | ARBUCKLE RD. #20 AT 6" X 4" TIE. INSTALL 3" BALL VALVE.
|  |  |  | 3 | [11 empty] | Steel |  |  | ... AT 6" X 3" TIE. 3" BAB VALVE INST.
[16 empty] | Steel |  |  | ...GAS WELL. 3" B&b VALVE INST.
|  |  |  | 4.5 | [11 empty] | Steel |  |  | EXPOSED ...ARBUCKLE #20 TIE ON 6". 3" B&B VALVA INST.
|  |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1990-05-09 | 1990-05-10 | Replace Pipe |  | Steel/Wrought Iron |  |  | 8" LINE 302 35' N/O HELSEY 1-3 GAS WELL. REPLACED 51' - 2" 8" PIPE WITH NEW PIPE
|  | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1990-05-09 | 1990-05-10 | Replace Pipe |  | Steel/Wrought Iron |  |  | 8" L-302 86' W/O HELSEY 1-3 GAS WELL RISER. REPLACED PIPE WITH NEW PIPE.
|  |  |  | 6.625 | [11 empty] | Steel |  | SUTTER
|  |  |  | 4.5 | [11 empty] | Steel |  | SUTTER
8
|  |  |  | 8 | [11 empty] | Steel |  |  | WO 47402-A, FS 85+09
|  |  |  | 8 | [11 empty] | Steel |  |  | WO 47402-A. FS 83+09
|  |  |  | 2 | [11 empty] | Steel |  |  | WO 47509-A
|  |  |  | 4 | [11 empty] | Steel |  |  | SOUTH SYCAMORE GAS WELL #5
|  |  |  | 6 | [11 empty] | Steel |  |  | WO 42581-A
|  |  |  | 4 | [11 empty] | Steel |  |  | SOUTH SYCAMORE 9-2 GAS WELL
|  | 167 |  | 4 | [11 empty] | Steel |  |  | BOUNDE CREEK LINE 167 TIE N/S
|  | 167 |  | 4 | [11 empty] | Steel |  |  | BOUNDE CREEK 1-7 LINE 167 TIE N/S
|  |  |  | 3 | [11 empty] | Steel |  |  | CUT OFF AT 12" MAIN
|  |  |  | 3 | [11 empty] | Steel |  |  | CUT OFF AT RISER
|  |  |  | 4 | [11 empty] | Steel |  |  | WO 47983-A
|  |  |  | 4 | [11 empty] | Steel |  | WOODLAND | ABANDON V-2 VALVE
|  | 172 |  | 3 | [11 empty] | Steel |  | WOODLAND | ABANDON LINE 172
|  | 172 |  | 3 | [11 empty] | Steel |  | WOODLAND | ABANDON LINE 172
|  | 172 |  | 4 | [11 empty] | Steel |  | WOODLAND
|  |  |  | 3 | [11 empty] | Steel |  | WOODLAND
|  |  |  | 4 | [11 empty] | Steel |  |  | WO 48036-A
|  |  |  | 4 | [11 empty] | Steel |  |  | WO 48036-A
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 8 | [11 empty] | Steel |  |  | SYCAMORE SLOUGH RD. NEW MAIN LINE VALVE WO 48107-A
|  |  |  | 8 | [11 empty] | Steel |  |  | SYCAMORE SLOUGH RD. NEW MAIN LINE VALVE WO48107-A
|  |  |  | 4.5 | [11 empty] | Steel |  |  | WO48116-A
|  |  |  | 4 | [11 empty] | Steel |  | GRIMES
|  |  |  | 4 | [14 empty] | WO48143-A
|  | 302 |  | 20 | [11 empty] | Steel |  |  | WO48170-A 20" L-302 V-191
|  |  |  | 6 | [11 empty] | Steel |  |  | WO48198-A
|  |  |  | 4 | [11 empty] | Steel
|  | 302 |  | 4
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 10 | [11 empty] | Steel |  |  | WO 48606-A
|  |  |  | 4 | [11 empty] | Steel |  |  | WO48615-A
|  |  |  | 12 | [11 empty] | Steel
|  |  |  | 3 | [11 empty] | Steel |  | WOODLAND
|  |  |  | 2 | [11 empty] | Steel |  |  | WO 48679-A ABANDON MOBIL 23-26-3 GAS WELL
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 6.625 | [11 empty] | Steel |  |  | WO 48731-A
|  |  |  | 4.5 | [11 empty] | Steel-Other
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 4 | [11 empty] | Steel |  |  | WO 49083-A...
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 2 | [11 empty] | Steel |  |  | 6007131 WO 49115-A KELLOGG #2 MASTER METER
|  |  |  | 3 | [11 empty] | Steel |  |  | ...MASTER METER
|  |  |  | 4.5 | [11 empty] | Steel |  |  | DETAIL C
|  |  |  | 3.5 | [11 empty] | Steel |  |  | WO 49133-A 3" L-302 @V-215 (REMOVED)
|  |  |  | 4.5 | [11 empty] | Steel |  |  | WO 49133-A DETAIL B
|  | 302 |  | 3 | [11 empty] | Steel
|  |  |  | 1 | [11 empty] | Steel |  |  | WO49231-A
|  |  |  | 6.625 | [11 empty] | Steel |  |  | WEST TIE-IN
|  | 302 |  | 6.625 | [11 empty] | Steel |  |  | F.S. 8+64 L-302 EAST TIE-IN
|  | 207 |  | 6 | [11 empty] | Steel |  | WOODLAND
|  | 207 |  | 4 | [11 empty] | Steel |  | WOODLAND
|  | 207 |  | 6 | [11 empty] | Steel |  | WOODLAND
|  | 207 |  | 6 | [11 empty] | Steel |  | WOODLAND
|  | 207 |  | 4 | [11 empty] | Steel |  | WODDLAND
|  | 207 |  | 6 | [11 empty] | Steel |  | WOODLAND
|  | 207 |  | 4 | [11 empty] | Steel |  | DAVIS
|  | 207 |  | 4 | [11 empty] | Steel |  | DAVIS
|  | 207 |  | 6 | [11 empty] | Steel |  | DAVIS
|  | 207 |  | 8 | [11 empty] | Steel |  | DAVIS
|  | 207 |  | 6 | [11 empty] | Steel |  | DAVIS
|  | 207 |  | 8 | [11 empty] | Steel |  | DAVIS
|  |  |  | 6 | [11 empty] | Steel |  |  | WO49482-A
|  |  |  | 4 | [11 empty] | Steel |  |  | WO 49384/MOCKTON #2-5
|  |  |  | 12 | [11 empty] | Steel
|  |  |  | 3.5 | [11 empty] | Steel
|  |  |  | 3 | [11 empty] | Steel |  |  | ABANDON COUNTRY CLLUB #13-1 GAS WELL...BUTTE...WO 43382....
|  |  |  | 4 | [11 empty] | Steel
|  |  |  | 6 | [11 empty] | Steel
|  |  |  | 2 | [11 empty] | Steel
|  |  |  | 4.5 | [11 empty] | Steel
|  |  |  | 3.5 | [11 empty] | Steel
10 |  |  |  | 3 | Gathering |  | Other |  |  | Other |  | 1975-09-17 | 1975-09-18 | Other |  | Steel/Wrought Iron |  |  | PRODUCERS 3" MAIN HAS LIGHT PITTING AND RUST
10 |  |  |  | 3 | Gathering |  | Other |  |  | Other |  | 1975-09-17 |  | Other |  | Steel/Wrought Iron |  | WILLOWS
10 |  |  |  | 3 | Gathering |  | Other |  |  | Other |  | 1975-09-17 | 1975-09-18 | Other |  | Steel/Wrought Iron |  | WILLOWS
|  | 318 |  | 4 | [11 empty] | Steel-Other |  | ORLAND
|  | 318 | [13 empty] | Steel-Other |  | ORLAND
|  | 169 | [13 empty] | Steel-Other |  | WILLOWS
|  |  |  | 3 | [11 empty] | Steel-Other |  | ORLAND | W.O. 4379E; CUT OFF AND ABANDON LOWE #1 GAS WELL. LEFT 2 FT. ____ ON MAIN (SEE SKETCH)
|  | 193 |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-12-15 | 1987-12-16 | Clamp |  | Steel/Wrought Iron |  |  | INSTALLED A 4" PLIDCO SMITH CLAMP. 2,000 WORKING PRESSURE WITH TEMP ___- -20 TO +225 F.
|  |  |  | 4 | [11 empty] | Steel-Other |  |  | INSTALLED 4" VALVE EXT FRAME & COVER ACCOUNT 3661 ACT 2040
|  |  |  | 3 | [11 empty] | Steel-Other
|  |  |  | 4.5 | [11 empty] | Steel-Other
|  |  |  | 2 | [11 empty] | Steel-Other |  |  | MAIN CONTAINED KARGE AMOUTNS OF FLUIDS.
|  | 169 |  | 4.5 | [11 empty] | Steel-Other |  |  | PIPE IN GOOD CONDITION
|  | 169 |  | 4.5 | [11 empty] | Steel-Other |  |  | PIPE IN GOOD CONDITION
|  |  |  | 4.5 | [11 empty] | Steel-Other |  |  | OPEN & INSP AT CUT-OFF POINTS.
28 | 92-00083-1 | [10 empty] | 1992-02-12 | 1991-02-13 |  |  |  |  | RICH. | Delete this leak, propane tank next store; No gas leak-Odor from propane tank
| 87--1 | [16 empty] | Richmond | Alter service 5021 seaport
| 80-60229- |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1980-10-29 |  | Other | C/O | Steel/Wrought Iron |  | Richmond | C/O 3' 2 " T.P. main to repair corrosion leak on main. Main now dead-in's 1' from new service to post transportation Co.
28 | 80-30179-1 |  |  | 6 | Transmission |  | Fitting |  |  | Construction Defect |  | 1980-11-17 | 1981-09-01 | Other |  | Steel/Wrought Iron |  | Richmond | Yes, UG elect and replaced leaking cap on sav-a-nipple. See leak #80-30178 as it repaired this leak.
28 | 80-30178-1 |  |  | 6 | Transmission |  | Fitting |  |  | Construction Defect |  | 1980-11-17 | 1981-09-01 | Other |  | Steel/Wrought Iron |  | Richmond | Replaced leaking cap on sav-a-nipple. Also repaired leak #80-30179
28 | 98-25168-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1998-07-16 | 1998-07-16 | Replace Pipe |  | Steel/Wrought Iron |  | Richmond | Replace 3' of 3/4" steel
28 | 88-80457-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1988-10-26 | 1988-10-26 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Richmond | Corrosion leakage due to wrap damage one location (rock) welded canned to repair for UC Berkeley Richmond Field Station
28 | 97-50077-1 | [10 empty] | 1997-10-01 | 1997-10-31 |  |  |  |  | Richmond | From service pumping station just 30' east of main
28 | 75-20426-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-07-07 | 1975-10-01 | Patch Welded |  | Steel/Wrought Iron |  | Richmond | Installed weld patches on T.P. main 105A on W/S Carlson Blvd. 273'; 275' quad 280' s/o hastmett; House os pitted on top main almost every foot a pit. Most pitt are the size betweeen a half dollar and dollar and "4" deep a/c.
28 | 75-20425-1 |  |  | 20 | Transmission | 105-A | Body of Pipe |  |  | Corrosion |  | 1975-07-07 | 1975-08-28 | Patch Welded |  | Steel/Wrought Iron |  | Richmond | 1 large pitt on top of rest of main
28 | 95-80154-1 |  |  | 24 | Transmission |  | Valves |  |  | Other |  | 1995-06-03 | 1995-06-03 | Other |  | Steel/Wrought Iron |  | Richmond | Greased Valve
| 99-21082-1 | [11 empty] | 2000-12-11 | Tighten Cap or Bolt |  |  |  | Richmond | Tightened plug
| 04-80320-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 2004-11-17 | 2004-11-17 | Other |  | Steel/Wrought Iron |  | Richmond | Tightened union on T.P. zone valve x-23
[13 empty] | 2001-09-25 |  |  | Steel/Wrought Iron |  |  | Installled 4" bottom
28 | [11 empty] | 1995-01-18 | [5 empty] | Richmond | Welded new 3/4 tee on 2" T.P.
28 | 96-21301-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1996-10-16 | 1996-10-17 | Other |  | Steel/Wrought Iron |  | Richmond | Greased Valve
28 | 96-21300-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1996-10-16 | 1996-10-16 | Other |  | Steel/Wrought Iron |  | Richmond | Rblt set
|  | 105-A | 46.51 | [8 empty] | 2000-06-21 |  |  |  | Steel/Wrought Iron |  | Richmond | 3" DFM 21' T.D. Williamson M-stopp
| 96-40356-F |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-12-15 | 1976-12-23 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Richmond | Install 30" can on 6" TP main; This main is pittier bad.
28 | 75-20427-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-07-07 | 1975-08-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Richmond | Work within 1wk, from date found; Circle U.G. in area; Elect PT&T
395 | 71-40227- |  |  | 6 | Distribution Main | [6 empty] | 1971-03-24 | 1971-03-26 | Patch Welded |  | Steel/Wrought Iron |  | Richmond | Arc welded 2-6" patend to/w and 3 other leep
|  |  |  | 6 | Transmission | [7 empty] | 1973-03-07 |  |  | Steel/Wrought Iron |  | Richmond | Inspection Hole
28 | 81-40473- |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1981-07-28 | 1981-07-28 | Patch Welded |  | Steel/Wrought Iron |  | Richmond | Installed 1-6" skinner clamp to main. Patch welded to make perm repairs and also welded 2-pits on main
28 | 81-20180-1 |  |  | 2 | Service |  | Fitting |  |  | Construction Defect |  | 1981-02-25 | 1982-03-19 | Other |  | Steel/Wrought Iron |  | Richmond | Found a 2" cap leaking on a 2" T.P. service tee.
28 | 81-20181-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 1981-02-25 | 1982-03-22 | Other |  | Steel/Wrought Iron |  | Richmond | Found a cap on a 2" P.C.F B.T. leaking
28 | 84-20338-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1984-02-16 | 1984-02-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Richmond | Replaced 19' of stl. serv. due to leakage
28 | 87-20607-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1987-05-28 | 1987-05-28 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Richmond | Welded patch over pit
28 | 88-20424-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1988-05-02 | 1988-05-02 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Richmond | Patched over bad spots welded half sole 3' long
|  |  |  | 4 | Transmission | [7 empty] | 1973-03-07 |  |  |  |  | Richmond | Inspection hole
28 | 97-50078-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1997-10-01 | 1997-10-16 | Patch Welded |  | Steel/Wrought Iron |  | Richmond | Welded half sole patch on main
28 |  |  |  | 2 | [13 empty] | Richmond
| 79-20117-2 |  |  | 0.75 | Other | 3/4" stl. serv. stub on 4" t.p. main | Body of Pipe |  |  | Corrosion |  | 1976-02-02 | 1979-12-10 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Richmond | Weld can (corrosion leak); Pole with fire box; Weld can (old c/o 3/4" serv. stub. that was leaking)
| 79-20119-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-02-02 | 1979-12-05 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Richmond | Concrete and steel fence post was installed on top of 4" main
| 79-20118-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-02-02 | 1979-12-05 | Patch Welded |  | Steel/Wrought Iron |  | Richmond | Fence line welded patch over leak.
28 | 85-60077-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1985-04-05 | 1985-04-05 | Clamp |  | Steel/Wrought Iron |  | Richmond | Clamp and Wrap for temp repair. Fence post on top of main at these 2 location and probably broke half the way the street. Refer to engineering.
| 79-20117-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-02-02 | 1979-12-06 | Other | Two weld cans | Steel/Wrought Iron |  | Richmond | Concrete and steel fence post installed on top of main.
28 | 88-00095-1 |  |  | 4 | Distribution Feeder Main |  | Other Welds |  |  | Material Failure |  | 1988-02-08 |  | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Richmond | Welded over leaking 4" weld patch
28 | 87-00224-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1987-02-26 | 1987-02-26 | Patch Welded |  | Steel/Wrought Iron |  | Richmond
| 76-20789-1 |  |  | 0.75 | Other |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1976-01-19 | 1976-11-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Richmond | Repaired leaking on meter
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1978-03-13 |  | Other |  | Steel/Wrought Iron |  | Richmond | Installed 2" on bottom run to clear prap 5x4' rcb; Contractor had pipe exposed, we just moved over two feet by putting on 2' piece on bottom run to clear RCB
28 | 72-40113-1 |  |  | 0.5 | Service |  | Girth Weld |  |  | Construction Defect |  | 1972-01-24 | 1972-01-27 | Replace Pipe and/or Service |  | Copper |  | Richmond | Failure point: Weld connecting steel riser to 1/2" cu.; Repaired by installing new riser with copper to steel eclips fitting
28 | 90-20190-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1990-02-28 | 1990-03-12 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Richmond | Installed 10" anoid can over weld
1 | 78-20263-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1978-03-17 | 1978-05-12 | Other |  | Steel/Wrought Iron |  | Richmond | Tightened core on 3/4" service valve a/c leakage
28 | 73-00141-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-05-30 | 1973-11-06 | Patch Welded |  | Steel/Wrought Iron |  | Richmond | Welded on one patch for perm repairs
28 |  |  |  | 24 | [11 empty] | Steel/Wrought Iron |  | RICH. | INSTALL GAS STATION AT THAT LOCATION
[18 empty] | Richmond | Pot hole for depths
[18 empty] | Richmond | Pot hole for depths
| 76-40201- |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1976-07-02 | 1976-07-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Richmond | Inspection a/c rerun service & c/o 15' of main a/c leakage
|  |  |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | El Cerrito | 2" distibution main was laying on top of T.P. main. This was raised and plastic wedges installed; 0' exposed transmission main while check 2" dis. main for leak #79-40165-1
|  |  |  | 20 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | El Cerrito | O" exposed 20" dis. main while looking for leak #79-40165-1 this while checking 2" dis crossing
| 76-20820-1 |  |  | 0.75 | Other |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1976-06-07 | 1976-09-09 | Other |  | Steel/Wrought Iron |  | El Cerrito | No excavation, no paving & no inspection report; Bar tested area and found no leaking soap tested meter. set & found small leak on elbow above inlet serviced. Repaired by tightening.
| 81-20144-1 |  |  |  | Other |  | Meter |  |  | Material Failure |  | 1998-02-19 | 1981-02-25 | Replace Pipe and/or Service |  | Other |  | El Cerrito | Turned over to service dept. D.L.T. leak no.; Leak on 1-A curb meter to 6317 Stockton meter replaced by service dept.; No elect. U.G.
28 | 74-20657-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-10-02 | 1974-10-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Albany | 3% water mtr. Box middle sidewalk; Found 2" two meter manifold in curb box laying on dirt on bottom of box, badly pitted & leaking. Replaced manifold at a higher elevation off of bottom of curb box.
28 | 76-00081-1 |  |  | 0.75 | Other | house line | Body of Pipe |  |  | Corrosion |  | 1976-04-15 | 1976-05-03 | Clamp |  | Steel/Wrought Iron |  | El Cerrito | Found leak under ground customer house line; Installed 3/4" Adams leak clamp; Notified customer to have per repairs made.
| 76-60618-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-10-18 | 1977-01-13 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | El Cerrito | Greased valve G14 found and leak with J.W. or soap test; Welded 6" patch on side of main.
28 | 74-20626-1 |  |  | 0.75 | Other |  | Fitting |  |  | Construction Defect |  | 1974-10-01 | 1974-10-30 | Other |  | Steel/Wrought Iron |  | Richmond | 10% F.O. 1' from building 15' from curb
| 76-60610-1 |  |  | 10 | Distribution Feeder Main |  | Tap Connection |  |  | Corrosion |  | 1976-10-18 | 1977-01-25 | Patch Welded |  | Steel/Wrought Iron |  | El Cerrito | Removed abondoned 3/4" & de tap that was leaking. Welded patch over hole. Welded patches over four deep pits at this location
| 76-60611-1 |  |  | 10 | Distribution Feeder Main |  | Other |  |  | Other |  | 1976-10-18 | 1977-01-21 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | El Cerrito | Welded three 6"x8" cans on top of main to cover three 3" couplings with plugs (old bag holes?)
| 76-60612-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-10-18 | 1977-01-20 | Patch Welded |  | Steel/Wrought Iron |  | El Cerrito | Welded on two 8"x10" patches to stop leak
28 | 74-20624-1 |  |  | 0.75 | Other |  | Fitting |  |  | Construction Defect |  | 1974-10-01 | 1974-10-30 | Other |  | Steel/Wrought Iron |  | Richmond | Replaced leaking fitting on meter
| 76-60609-1 |  |  | 10 | Distribution Feeder Main |  | Girth Weld |  |  | Corrosion |  | 1976-10-18 | 1977-01-03 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | El Cerrito | Welded sleeve over leaking weld. Welded 8 coupons over deep pits in main
| 76-60608-1 |  |  | 10 | Distribution Feeder Main |  | Girth Weld |  |  | Corrosion |  | 1976-10-18 | 1977-01-03 |  |  | Steel/Wrought Iron |  | El Cerrito | Welded sleeve over leaking weld on main. Welded & coupons over deep pits in main.
28 | 72-40320-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-05-18 | 1972-05-24 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | El Cerrito | Installed one 8'x24" can
| 79-40305- |  |  | 20 | Transmission |  | Other Welds |  |  | Construction Defect |  | 1979-06-15 | 1979-06-21 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Richmond | Installed patch and welded 18" band over acy. weld
28 |  |  |  | 24 | Distribution Feeder Main | [6 empty] | 1982-04-21 | 1982-04-21 |  |  | Steel/Wrought Iron |  | Richmond | Exposed 9' of 24" stl. Gas main could not find any leaking at this location. (inspection only)
28 |  |  |  | 24 | Distribution Feeder Main |  | Other |  |  | Other |  | 1982-03-18 | 1982-03-18 |  |  | Steel/Wrought Iron |  | Richmond | Exposed 9' of 24" stl. Gas main could not find any leaking at this location. This is for main inspection only.
28 | 82-20357-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1982-03-09 | 1982-05-07 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Richmond | Inst. 48".L.x20" welding band can over old gas weld, leakage & heavy pits on 20" T.P. gas main
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1977-11-16 |  | Other |  | Steel/Wrought Iron |  |  | Installed a new service 1/2" plastic
|  |  |  | 3 | Other |  | Other |  |  | Other |  | 1978-11-10 |  | Bell Joint Seal |  | Other |  | Albany | Installed 1/2" plastic service
28 | 95-80158-1 |  |  | 24 | Transmission |  | Valves |  |  | Other |  | 1995-06-03 | 1995-06-03 | Other |  | Steel/Wrought Iron |  | Richmond | Greased Valve
28 | 97-21073-1 |  |  | 8 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1997-07-10 | 1997-07-10 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Richmond | Repair leak
28 | 95-80155-1 |  |  | 24 | Transmission |  | Valves |  |  | Other |  | 1995-06-03 | 1995-06-03 | Other |  | Steel/Wrought Iron |  | Richmond | Greased valve
28 | 95-80156-1 |  |  | 24 | Transmission |  | Valves |  |  | Other |  | 1995-06-03 | 1995-06-03 | Other |  | Steel/Wrought Iron |  | Richmond | Greased valve
|  |  |  | 24 | Transmission |  | Other |  |  | Other |  |  | 1978-01-31 | Other |  | Steel/Wrought Iron |  | El Cerrito | Condition of main anid wrade good. Depth is 41" at this location. 24" main is starting to dive in this location; Paving 3.5'x3'x8"
28 | 95-80157-1 |  |  | 24 | Transmission |  | Valves |  |  | Other |  | 1995-06-03 | 1995-06-03 | Patch Welded |  | Steel/Wrought Iron |  | Richmond | Greased Valve
|  |  |  | 1 | Service |  | Other |  |  | Damage by Natural Forces |  |  | 1974-05-31 | Other |  | Other Plastic |  | Richmond | Stubbed new service 197' e/o Isabel st. a/c of interfering with contractors grade to be completed at a later date in coordination with contractor. Estimate no dept. to make pre arragement.
2/ | 72-40212-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-04-17 | 1972-06-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Kensington
28 | 77-40108-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1977-03-29 | 1977-04-21 | Replace Pipe and/or Service |  | Steel |  | El Cerrito | Reran service to repair. 3/4" M-2 ftg. 6' from main a/c customer would not allow new aggregate to be broken.
|  |  |  | 3 | Service |  | Other |  |  | Other |  | 1976-08-26 |  | Other |  | Steel/Wrought Iron |  | El Cerrito
28 | 72-20252-1 |  |  | 0.75 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-03-15 | 1972-09-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | El Cerrito
28 | 74-40426-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-01-02 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | El Cerrito | Reran branch service to 650 & Albemaple-El Cerrito to make permanent repairs
28 | 76-60239-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-07-12 | 1972-07-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Kensington | Found Leaking in service reran using 1/2" plastic in old service cassing
28 | 72-40458-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-08-10 | 1972-08-17 | Replace Pipe and/or Service |  |  |  | Kensington | leak was in serv. Rerun service to make permanent repair
28 | 80-60102-1 |  |  | 0.75 |  |  | Body of Pipe |  |  | Corrosion |  | 1980-03-07 | 1981-02-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Kensington | Repaired 301 in service. No elect U.G by rerunning service to #32 Highlands
| 76-60384-1 |  |  | 0.75 | Other |  | Other Welds |  |  | Corrosion |  | 1976-07-29 | 1976-12-03 | Patch Welded |  | Steel/Wrought Iron |  | Kensington | Made permanent repairs to weld on c/o 3/4" muller service tee. Exposed 4' of main for inspection; 3" stl. main at this location is pitted condition although pits are not deep at this time
| 76-60596-1 |  |  | 0.75 | Other |  | Fitting |  |  | Corrosion |  | 1976-12-01 | 1976-12-01 | Replace Pipe and/or Service |  | Cast/Ductile Iron |  | Kensington | Found old 3/4" stl muller service tee leaking. A/C cap destroyed from corrosion. Permanenent repairs maintained buy inst. new 3/4" cap. Service had been c/o previously at this location.
| 75-40015- |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1975-01-10 | 1975-01-10 | Patch Welded |  | Steel/Wrought Iron |  | Kensington | Leaking on cut off serv. tee. Repairs by installing patch.
28 |  |  |  | 3 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Kensington
| 76-40285-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Corrosion |  | 1976-10-04 | 1976-10-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | El Cerrito | Reran Service to 7427 Sea View to Elimenate leakage
28 | 72-40369-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-06-16 | 1972-06-30 | Patch Welded |  | Steel/Wrought Iron |  | El Cerrito
28 | 74-40514 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-09-09 | 1974-09-12 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Kensington | Inspection report A/C of rerun service. A/C leakage.
28 | 72-00137-1 |  |  | 0.75 | Service |  | Other |  |  | Corrosion |  | 1972-01-19 | 1972-01-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Kensington | Replaced 3/4" service with 1/2" plastic.
28 | 72-40303-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-05-12 | 1972-05-19 | Patch Welded |  | Steel/Wrought Iron |  | Berkeley | The main was in top of a water service and welded one patch in the main
28 | 93-20097-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1994-04-27 | 1994-04-27 | Patch Welded |  | Steel/Wrought Iron |  |  | Welded 2 patches over leaks and 4 patches over deep corrosion areas
| 75-40144 |  |  | 1.25 | Other |  | Tap Connection |  |  | Construction Defect |  | 1975-04-18 | 1975-04-21 | Other |  | Steel/Wrought Iron |  | Berkeley | Tightened cap on old cut off 11/4 tee acct, of small leak.
28 | 72-40421-1 |  |  | 0.75 | Other |  | Tap Connection |  |  | Corrosion |  | 1972-07-18 | 1972-07-27 | Other |  | Steel/Wrought Iron |  | ABLANY | Old c/o tee was fitted and leaking at cap area. c/o fitted section of pipe & welded on new cap. Installed 9lb anode at location
| 81-60109 |  |  | 4 | Other | 4" Blow Off | Fitting |  |  | Other |  | 1981-09-29 | 1981-09-29 | Other |  | Steel/Wrought Iron |  | Albany | Repaired 301 by doping & tightening.
28 | 72-20299-1 |  |  | 0.75 | Other |  | Other |  |  | Corrosion |  | 1972-03-17 | 1973-05-23 | Other |  | Steel/Wrought Iron |  | Albany | FOUND NIPPLES LEAKING ON GURD METER. REPLACED NIPPLE STOPPED LEAKAGE
28 | 80-30159-1 |  |  | 2 | Other |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1980-11-30 | 1981-07-16 | Other |  | Steel/Wrought Iron |  | Albany | Found leak on houseline. Temp repairs made, customer to fix.
28 | 75-20467 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-07-11 | 1975-08-25 | Patch Welded |  | Steel/Wrought Iron |  | Albany | Welded (2) patches; Main in good condition.
|  |  |  | 3 | Other |  | Other |  |  | Other |  |  | 1978-09-05 | Bell Joint Seal |  | Other |  | Berkeley | Installed new service
28 | 72-40031-1 |  |  | 2 | Distribution Main |  | Physical/Mechanical Joint |  |  | Corrosion |  | 1972-01-27 | 1972-03-13 | Clamp |  | Steel/Wrought Iron |  | Berkeley
28 | 96-21204-1 |  |  | 2 | Service |  | Valves |  |  | Other |  | 1996-04-17 | 1997-08-22 | Other |  | Other |  | Berkeley | 3/4" valve on meter set leaking. Tightened nut on valve to fix leak.
28 | 87-60152-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1982-07-20 | 1982-07-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Berkeley | R/R 3/4" Steel T.P. service to #699.
28 | 85-20083-1 |  |  | 3 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1985-02-06 | 1985-02-06 | Patch Welded |  | Steel/Wrought Iron
| 76-60328 |  |  | 0.5 | Other | GAS LAMP CUSTOMER OWNED | Body of Pipe |  |  | Corrosion |  | 1976-07-01 | 1976-07-01 | Other | Cut it off, with manager's approval | Steel/Wrought Iron |  | Berkeley | We cut off 34' 1/2' steel run to gas lamp because of leakage. Approval customer owned lamp system. #1 leak repaired by c/o of customer owned gas piping in panted area wear meter set. We had gotten gas readings over 2" service so we dug two holes over service but found no leakage. This was verrifed on 7/2/76 with flame pac.
28 | 92-00045-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1992-01-30 | 1992-01-30 | Patch Welded |  | Steel/Wrought Iron |  | Berkeley | Put patch on main where storm drain crosses.
28 | 78-60137-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-07-07 | 1978-07-07 | Patch Welded |  | Steel/Wrought Iron |  | Berkeley | Found leakage on 2" homemade tee and on 4' T.P. main used existing 4" B.T. P.C.F to stop off D/E C/O service and c/o 7' of 4" main. Found no other leakage.
|  |  |  | 4 | Transmission |  | Other |  |  | Other |  |  | 1978-07-10 | Other |  | Steel/Wrought Iron |  | Berkeley | Plug hole tee salvage 2" T.P. valve. 4" T.P. main in good condition. Gas main and wrap in Plug hole to salvage 2" T.P. and 4" T.P. main in good condition. Gas main & wrap in good condition.
|  |  |  | 4 | Transmission |  | Other |  |  | Other |  |  | 1978-07-07 | Other |  | Steel/Wrought Iron |  | Beerkeley | Gas main and wrap in good condition.
28 | 93-20023-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1993-02-02 | 1994-01-10 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  |  | Fix relief valve on TP service.
28 | 92-20018-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1992-01-24 | 2000-11-30 | Other |  | Steel |  | B | GREASE VALVE.
[18 empty] | Berkeley | No leaks; Inst. E.T.S lead & V.F.&C.
| 75-40425 |  |  | 2 | Other |  | Body of Pipe |  |  | Corrosion |  | 1975-11-11 | 1975-11-11 | Other |  | Steel/Wrought Iron |  | Berkeley | Closed 2" valve on 2" main acct. of leakage, and not in use, Note, This is UC pipe and property.
28 | 75-20001-1 |  |  | 0.75 | Other |  | Regulator |  |  | Material Failure |  | 1975-05-05 | 1975-05-12 | Other |  | Steel/Wrought Iron |  | Berkeley | Repaired fuzz leak on Reg. on by tightening screws is same.
28 | 83-20343-1 |  |  | 0.75 | Other |  | Meter |  |  | Construction Defect |  | 1983-02-01 | 1983-06-22 | Other | Replaced Nipple | Steel/Wrought Iron |  | Berkeley | Replaced leak on Nipples.
28 | 83-20344-1 |  |  | 0.75 | Other |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1983-02-01 | 1983-06-22 | Other | Replaced Nipples | Steel/Wrought Iron |  | Berkeley | Replaced leak on Nipple.
28 | 82-60157-1 |  |  | 0.75 | Other |  | Meter |  |  | Other |  | 1982-07-21 | 1983-06-13 | Other |  | Steel/Wrought Iron |  | Berkeley | Repaired leak on meter
28 | 73-20930-1 |  |  | 0.75 | Other |  | Other |  |  | Other |  | 1973-10-09 |  |  |  | Steel/Wrought Iron |  | Berkeley | Leak on costumers house line. Talked to them and they should have a plumbercome and fix it.
28 | 94-80443-1 |  |  | 20 | Transmission |  | Girth Weld |  |  | Corrosion |  | 1994-12-15 | 1994-12-15 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Albany | Welded band (wedding) on leaking Girth weld.
28 | 82-40402-1 |  |  | 0.75 | Other | House Line |  |  |  | Corrosion |  | 1982-08-30 |  |  |  | Steel/Wrought Iron |  | Alb. | Clocked houseline found 21/2 CFH leak. Shut off and issued hazard notice 62-3010; House line leaking.
28 | 72-40063-1 |  |  | 3 | Distribution Main |  | Physical/Mechanical Joint |  |  | Corrosion |  | 1972-01-18 | 1972-01-28 | Patch Welded |  | Steel/Wrought Iron |  | Berkeley | Installed 4"x3" patch.
[5 empty] | Other |  | Other |  |  | Other |  | 1973-07-26 | 1973-07-26
26 | 72-- |  |  | 8 | Distribution Main |  | Other |  |  | Other |  | 1972-05-03 | 1972-05-03 | Other |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 0.75 | Other |  | Other Welds |  |  | Construction Defect |  |  | 1981-06-04 | Weld Over Sleeve or Can |  | Copper
26 |  |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-02-25 | 1972-02-25 | Clamp |  | Steel/Wrought Iron |  | OAKLAND | THIS MAIN IS CONPLETELY ROTTEN. HAD TO INSTALL (9) FULL CIRCLE CLAMPS ON MAIN IN 6FT. SECTION. MAIN LOOKS LIKE SWISS CHEESE. ESTIMATING DEPT. HAD BETTER GET ON THIS ONE S.A.P. THIRD TIME THIS SECTION OF MAIN HAS BEEN DUG UP & CLAMPED IN DRIVEWAY & CUSTOMER GETTING IRRATATED ABOUT DIGGING THIS MAIN UP ALL THE TIME.
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1977-05-06 | Other |  | Steel/Wrought Iron |  | OAKLAND | INSTALLED 3/4" SERVICE.
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron
26 | 74-5505-5 |  |  |  | Other |  | Physical/Mechanical Joint |  |  | Other |  |  | 1974-02-26 | Other
| 74-48714- |  |  | 0.75 | Other | SERVICE TEE | Girth Weld |  |  | Construction Defect |  | 1974-06-03 | 1974-06-05 | Weld Over Sleeve or Can |  | Steel/Wrought Iron
| 99-10666- |  |  | 0.5 | Gathering |  | Fitting |  |  | Other | SERVICE TEE CRACKED |  | 1999-06-25 | Other | REPLACED SERVICE TEE | Aldyl A (Tan or Gray) |  |  | OLD EXISTING BULT ON SERVICE TEE LEAKING REPLACED WITH NEW SERVICE TEE.
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1973-11-15 | 1973-11-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  |  |  | 2 | Service |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron
26 | 77-48996- |  |  | 3 | Distribution Feeder Main |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1977-09-28 | 1977-11-15 | Other |  | Steel/Wrought Iron |  |  | DOPED & TIGHTENED COMPLETE PLUGS & CAPS ON (2) SAVE-A-VALVE AT LOOSE
1 | 96-25235-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 1996-01-10 | 1996-01-10 | Clamp |  | Steel/Wrought Iron |  |  | TIGHTENED EXISTING (HOSE) 4" SKINNER LEAK CLAMP.
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1973-11-02 | 1973-11-02 | Patch Welded |  | Steel/Wrought Iron
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron
[5 empty] | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Other Plastic
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Other Plastic
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Other Plastic
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Other Plastic
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Other Plastic
| 74-48892-1 |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-07-11 | 1974-07-11 | Patch Welded |  | Steel/Wrought Iron |  | OAK. | DUG 8' X 6' BELL HOLE AND TUNNELED UNDER STORM DRAIN TO REPAIR 16" H.P. MAIN ARCH WELEDED EIGHT PATCHES AND WELDED OVER ABOUT TWENTY PITTS. MAIN IN BAD CONDITION.
| 03-80295-1 |  |  | 2 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2003-11-14 | 2004-01-26 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | Berkeley | Clamp main two belt skinner clamp.
1 |  |  |  | 2 | Other | [10 empty] | Steel/Wrought Iron |  | Berkeley | No leakage. Inspection report only.
28 | 77-40209-1 |  |  | 0.5 | Service |  | Fitting |  |  | Material Failure |  | 1977-07-07 | 1977-07-07 | Replace Pipe and/or Service |  | Copper |  | Berkeley | This service should be relocated A/C of house is settling and 1/2" copper service has stress. Also relocating may be a problem because of property lines; Repaired 1/2" copper service.
28 | 72-40477-1 |  |  | 3 | Distribution Feeder Main |  | Fitting |  |  | Material Failure |  | 1967-08-16 | 1972-08-17 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Berkeley | Pl. fuzz weld. To much tension on Pl. pipe.
28 |  |  |  | 30 | Other |  | Other |  |  | Other |  | 1981-09-21 |  | Bell Joint Seal |  | Steel/Wrought Iron |  | Berkeley | Installed 1/2" plastic service
28 | 72-40601-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-11-10 | 1972-12-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Berkeley | Replaced 1" service with 1/2" plastic.
28 | 72-40316-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-05-25 | 1972-06-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Berkeley | Replaced 1" service with 1/2" plastic.
|  |  |  | 0.75 | Service | [6 empty] | 1974-09-04 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Berkeley
|  | 105-A | 42.91 | 4.5 | Transmission |  |  |  |  | Damage by 3rd Party | [5 empty] | Steel/Wrought Iron |  | Berkeley | SEE STRENGTH TEST REPORT FOR TESTING 33' OF 4" STL. PIPE.
| 00-80038-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Digin |  | 2000-01-28 | 2000-01-28 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Berkeley | Installed button on 4" TP main.
[12 empty] | 1988-10-31 | [5 empty] | Berkeley | Installed 2-4" PCF & 1-4" zone valve/4" Kero test fitting
28 | 73-00164-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-06-04 | 1974-02-08 | Patch Welded |  | Steel/Wrought Iron |  | Berkeley | Found leak on 4" TP main. Deu to bad field wrapp. Installed 8"x24" can and anode.
28 | 93-80301-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1993-08-03 | 1993-08-03 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Berkeley | Installed weld can over main.
|  |  |  | 3 | Distribution Feeder Main |  | Other |  |  | Other |  | 1976-11-04 |  | Other |  | Steel/Wrought Iron
|  |  |  | 3 | Distribution Feeder Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron |  | Berkeley
28 | 92-80047-1 |  |  | 6 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1992-02-25 | 1992-02-25 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Berkeley | Cleaned cap & replaced gasket.
28 | 96-80401-1 |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Digin |  |  | 2000-10-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Berkeley | Stop off 3/4" stage line at tee and replace 35' of 3/4" steel and lower serv.
| 75-40262 |  |  | 0.75 | Other |  | Other |  |  | Other |  | 1975-07-11 | 1975-07-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Berkeley | Found leak on reg & nipple through qall on meter set leaking. Installed new reg & replaced Iron conn. Did not dig up main
| 74-60675-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-12-10 | 1974-12-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Berkeley | 10percent over 4" main in the intersection.
|  |  |  | 12 | Transmission | [6 empty] | 1972-01-31 |  |  |  | Steel/Wrought Iron
28 |  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Berk
28 |  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Berk
28 |  |  |  | 20 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Berkley
28 |  |  |  | 20 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Berkley
28 |  |  |  | 20 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | BERKLEY
28 |  |  |  | 20 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Berkley
28 |  |  |  | 20 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Berkley
| 76-60011-1 |  |  | 4 | Distribution Main |  | Valves |  |  | Construction Defect |  | 1976-01-02 | 1976-01-07 | Other |  | Steel/Wrought Iron |  | Berk | 4" valve leaking at flange. Had to replace gasket.
28 |  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Berkley
28 |  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Berkley
28 |  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Berk
28 |  |  |  | 8 | Distribution Main |  |  |  |  | Other |  | 1978-09-15 | 1978-09-15 | Other |  | Steel/Wrought Iron |  | Berkeley
28 | 91-20613-1 |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1991-09-27 | 1991-10-02 | Patch Welded |  | Steel/Wrought Iron |  | Berkeley | INST. WELD PATCH ON 16" MAIN TO REPAIR LEAKAGE
[18 empty] | Berkeley | Installed ETS head on 8" mains.
| 75-60047-1 |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1975-01-31 | 1975-01-31 | Patch Welded |  | Steel/Wrought Iron |  | B | INST. (3) WELD PATCHES ON 16" HP MAIN 15' OUT ON E/S OF MCGEE 81' N/O HEARST, IN ORDER TO ELIMINATE LEAKAGE CAUSED BY ELECTROLYSIS. "PERMANENT REPAIR"
28 | 82-32042-1 |  |  | 1.25 | Other |  | Meter |  |  | Material Failure |  | 1982-03-19 | 1983-01-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Berkeley | Repaired leak on glass & plugged old houseline.
28 | 73-40648-1 |  |  | 0.75 | Other |  | Meter |  |  | Material Failure |  | 1973-11-22 | 1973-12-10 | Other |  | Steel/Wrought Iron |  | Berkeley | Made repairs on leaking meter.
28 | 1 |  |  | 3 | Transmission | [10 empty] | Steel/Wrought Iron |  | Berk | Welded 3/4 tee for service.
|  |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  | 1976-08-27 |  | Other |  | Steel/Wrought Iron |  | Berk | Contact with water main.
28 | 75-20562-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1975-07-31 | 1975-08-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Berkeley | Manifold in curb meter box was corroded & leaking in serveral places repair was to replace manifold.
28 | 97-21171-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1997-09-06 | 1997-09-16 | Other |  | Steel/Wrought Iron |  | Berk. | Repair leaks on nipples & T.P. service valve.
28 | 81-40696-1 |  |  | 0.75 | Other | Chart line | Body of Pipe |  |  | Corrosion |  | 1981-12-16 | 1982-01-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Berkeley | 3/4' Chart line was previously c/o but not at tee. Yes U.G. Ele. c/o 3/4" chart line at new chart lines.
28 | 72-20744-1 |  |  | 0.75 | Other |  | Meter |  |  | Material Failure |  | 1972-11-06 | 1973-02-28 | Other |  | Steel/Wrought Iron |  | Berkeley | NO LEAKAGE OVER SERVICE OR MAIN. SWIVEL LEAKING ON METER. TIGHTENED SWIVEL STOPPED LEAKAGE.
28 | 72-20745-1 |  |  | 0.75 | Other |  | Meter |  |  | Material Failure |  | 1972-11-06 | 1973-02-28 | Other |  | Steel/Wrought Iron |  | Berk
28 | 77-20556-1 |  |  | 1.25 | Other |  | Regulator |  |  | Construction Defect |  | 1977-04-18 | 1977-04-21 | Other |  | Steel/Wrought Iron |  | Berkeley | Leak in meter box on regs repaired 4/21/77
28 | 83-20307-1 |  |  | 0.75 | Other |  | Physical/Mechanical Joint | Meter |  | Construction Defect |  | 1983-01-31 | 1983-06-24 | Other | Found Manifold Replaced. | Steel/Wrought Iron |  | Berkeley | Leak in manifold 6/23/83. Found new manifold no leakage
28 | 73-40530-1 |  |  | 0.75 | Other |  | Fitting |  |  | Damage by outside Forces |  | 1973-09-14 | 1973-09-14 | Other |  | Steel/Wrought Iron |  | Berkeley | nipple broken on pilot line to C.B.V. regulator on large meter set. Repaired 1/2" broken fitting; Replaced 1/2" nipples.
| 81-40058 |  |  | 0.5 | Service |  | Other Welds |  |  | Other |  | 1981-01-28 | 1981-01-28 | Replace Pipe and/or Service |  | Copper |  | Berkeley | Maid temp. repair to 1/2" copper serv. by installing 24" of plastic at main from eclipse ftg.
28 | 72-40414-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-07-12 | 1972-07-14 | Patch Welded |  | Steel/Wrought Iron |  | Berkeley | Found fitting on top section of main. Installed two 6" weld patches & 9lb mag. anode.
28 | 40054 |  |  | 1.25 | Distribution Feeder Main |  | Fitting |  |  | Other |  |  |  | Other | Dresser Coupling | Steel/Wrought Iron |  | Berkeley | The thread was broken at the valve removed valve installed 2' 11/4'" dressser coupling.
28 | 83-20286-1 |  |  | 2 | Distribution Main |  | Valves |  |  | Other |  | 1983-01-28 | 1983-05-10 | Other |  | Steel/Wrought Iron |  | Berkeley | Soap test & greased valve. Could not find a 301 on valve. ordered rechecked.
28 | 75-60111-1 |  |  | 0.75 | Other |  | Meter |  |  | Other |  | 1975-02-26 | 1975-02-26 | Replace Pipe and/or Service | T.C. | Steel/Wrought Iron |  | Berkeley | Leaks on meter set temp repaired 2/26/75. Replaced service/manifold meters 2/28/75
|  |  |  | 1.25 | Service | [8 empty] | Replace Pipe and/or Service |  | Other Plastic |  | Berkeley
28 | 84-20167-1 |  |  | 8 | Transmission |  |  |  |  | Other |  | 1984-01-26 | 1984-02-13 |  |  | Steel/Wrought Iron |  | Berk | Found fuzz leak on flange on s/o valve. Job leak in pit repaired by M&C acceptable main to be replaced in near future.
28 | 84-20167-1 |  |  | 8 | Transmission |  | Valves |  |  | Other | Gasket | 1984-01-26 | 1984-02-13 | Other | Replaced gasket | Steel/Wrought Iron |  | Berk | Found fuzz leaking flange on s/o valve. Fuzz leaking in reg pit repaired by Mac. Leak on flange acceptable main to be replaced.
28 | 93-80041-1 |  |  | 3 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1993-01-22 | 1993-09-22 | Other |  | Steel/Wrought Iron |  | Berkeley | Greased valve.
| 02-80099-1 |  |  | 0.75 | Service |  | Other |  | TP TO HIGH REG. SET | Construction Defect |  | 2002-03-30 | 2002-03-30 | Other |  | Steel/Wrought Iron |  | Berkeley
| 80-40883- |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1980-11-17 | 1980-11-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Berkeley | Install 3/4" TP serv. to b48 curb box & reg set. 1" pl from curb box (high to high set) to meter set in back.
28 | 96-21087-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  |  | 1996-08-29 | Other |  | Steel/Wrought Iron |  |  | 301 in curb box on regs. made repairs
28 | 73-60289-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-03-15 | 1973-05-25 | Other |  | Steel/Wrought Iron
| 01-80441-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 2001-07-14 | 2001-07-25 | Other |  | Steel/Wrought Iron |  | Berkeley | REPLACED 3/4" T.P. VALVES ON BLOW OFF/GAUGE TAPS.; REPLACED GAUGE TAP VALVE IN VPC 0.9 H-14
| 99-21019-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  |  | 2000-07-28 | Other |  | Steel/Wrought Iron |  | Berkeley | Tightened stoperer.
28 | 92-80237-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1992-07-30 | 1992-07-30 | Other |  | Steel/Wrought Iron |  | Berk | Shutdown service rewelded new 3/4 nipples for by pass
| 87--1 |  |  | 10 | [11 empty] | Steel/Wrought Iron |  | Berk | Installed new 3/4" stl. serv. & curb box.
28 | 79-30054-1 |  |  | 2 | Other |  |  |  |  | Corrosion |  | 1979-06-22 |  |  |  | Steel/Wrought Iron |  | Berkeley
28 | 74-20515-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  |  | 1974-09-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Berkeley | 10 PERCENT F.O. GAS COVER 1' FROM FRONT BLDG. 10' FROM CURB. MAIN WAS NOT EXPOSED. 301 ON 1" NIPPLE (HOUSELINE) IN CURB BOX REPLACED TO REPAIR
| 99-21089-1 |  |  | 1.25 | Service |  | Regulator |  |  | Other | Loose | 1999-10-13 | 1999-10-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Berkeley | Tightened diaphragm case.
28 | 91-50015-1 |  |  | 2 | Service |  | Fitting |  |  | Atmospheric Corrosion |  | 1991-04-11 |  | Other |  | Steel/Wrought Iron |  | Berkeley | Repaired 301 on metric plug. Need M&C repair fuzz ball on threads going into 2" valve (marked yellow)
| 99-21088-1 |  |  | 8 | Distribution Main |  | Valves |  |  | Other | Grease | 1999-10-13 | 1999-10-14 | Other | Grease | Other | Unknown main type | Berkeley | GREASED 8" BYPASS VALVE
28 | 88-20105-1 |  |  | 4 | Distribution Feeder Main |  | Tap Connection |  |  | Other |  | 1988-02-24 | 1988-02-29 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Berk. | Tightened leaking 4" TP cap.
28 | 85-40210-1 |  |  | 0.5 | Transmission |  | Fitting |  |  | Construction Defect |  | 1985-08-20 | 1985-08-28 | Other |  | Steel/Wrought Iron |  |  | Repaired 301's on 1/2 gauge stations.
| 80-60212- |  |  | 8 | Distribution Main |  | Other |  |  | Material Failure |  | 1980-11-06 | 1980-02-02 |  |  | Steel/Wrought Iron |  | Berkeley | GREASED VALVE & TIGHTENED FLANGES
|  |  |  | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | Berkeley | Installed E.T.S. on 10" T.P. main.
28 | 74-20539-1 |  |  | 1.25 | Other |  | Meter |  |  | Material Failure |  | 1974-09-18 | 1975-01-07 | Other |  | Steel/Wrought Iron |  | Berkeley | Leaking nylon, bushing installed 3/4" Ell, nylon bushing not need for this meter set insulated with union
28 | 72-20851-1 |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-11-20 | 1973-12-20 | Patch Welded |  | Steel/Wrought Iron |  | Berkeley | ARC welded patches on 4 leaks-Welded 5 patches on deep pits at this location
1 |  |  |  | 3 | Transmission | [10 empty] | Steel/Wrought Iron |  | Berkeley | Reran 3/4" stl TP service
28 | 88-20101-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1988-02-23 | 1988-02-23 | Patch Welded |  | Steel/Wrought Iron |  | Berkeley | Patch weld TP main
28 | 97-21140-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1997-09-18 | 1997-09-19 | Other |  | Steel/Wrought Iron |  | Berkeley | Fix Leak on reg & nipples
28 | 83-00076-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-01-12 | 1984-04-17 | Patch Welded |  | Steel/Wrought Iron |  | Berleley
| 76-60019-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-01-02 | 1976-12-02 | Patch Welded |  | Steel/Wrought Iron |  | Berkeley | Installed one weld patch 26' e/o of spaulding from west pil. Leak was on bottom of main
78-60105-1 |  |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-05-18 | 1978-05-18 | Patch Welded |  | Steel/Wrought Iron |  | Berkeley | Welded (2) patches on 8" TP main at below location; Main in good condition.
28 | 78-20056-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-02-02 | 1978-04-12 | Patch Welded |  | Steel/Wrought Iron |  | Berkeley | Welded (2) patches on 8" TP main at below location; Main in good condition.
28 | 80-20077-1 |  |  | 80 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1980-02-06 | 1981-02-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Berkeley | No elect U.G. Patched 8" T.P. arced welded two 9"x12aaaaa' patch
28 | 83-00078-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-01-12 | 1984-01-19 | Other |  | Steel/Wrought Iron |  | Berkely | Installed 12"x24" can over patch and pitting
28 | 71-30650-1 |  |  | 8 | Transmission |  | Body of Pipe | Valves |  | Corrosion |  | 1971-10-28 | 1972-01-07 | Patch Welded |  | Steel/Wrought Iron |  |  | Installed patch on 8" HP. main-19' out on n/s Allston way. 16' e/o/w/s of Bonar st. Leak caused by electrolysis
1 | 80-60116- |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1980-04-09 | 1980-09-12 | Clamp |  | Steel/Wrought Iron |  | Berkeley | Installed (1) skinner leak clamp on small pit elimating leakage
28 | 82-40381-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1982-08-19 | 1982-08-20 | Patch Welded |  | Steel/Wrought Iron |  | Berkeley | Dug 7'x5' bellhole over main, & drilled holes to vent overnight. 8-19 should be marked 8-20-82. Temp clamp 8/20/82. Installed 1-6"x6" pc of A-53grb, 35,000 470 lb test to seamless patch on 8" T.P. main
28 | 85-40290-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1985-09-09 | 1985-09-09 | Patch Welded |  | Steel/Wrought Iron |  | Berkeley | Installed (1) 8" patton patch over leaking pit on top of main, Installed (8) cold patches over pit
28 | 73-21001-1 |  |  | 2 | Other |  | Meter |  |  | Material Failure |  | 1973-10-16 | 1974-09-25 | Other |  | Steel/Wrought Iron |  | Berkeley | leak in curb box
28 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
28 | 94-00049-1 |  |  | 12 | Distribution Main |  | Valves |  |  | Other |  | 1994-01-18 | 1994-04-25 | Other |  | Steel/Wrought Iron |  | Berkeley | Refer to M&C Dept on C-Tag. Greased Valve; 301 in reg pit. 301 on 12" inlet valve
28 | 94-80123-1 |  |  | 2 | Service |  | Valves |  |  | Material Failure |  | 1994-01-18 | 1994-01-18 | Other |  | Steel/Wrought Iron |  | Berkeley | Greased 2" inlet valve & tightened plug on regulator
28 | 72-20829-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-11-16 | 1973-02-22 | Patch Welded |  | Steel/Wrought Iron
28 | 73-40114-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-02-21 | 1973-02-22 | Patch Welded |  | Steel/Wrought Iron |  | Berkeley | Found leakage on 8" T.P. main 18' out on n/s of Allston. Perm repairs made on main by welding patch over leakage. Installed 5lb anode 15' w/o E/L 10th st.
| 74-20533-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-09-18 | 1974-09-25 | Patch Welded |  | Steel/Wrought Iron |  | Berkeley | Installed 3 patches on 8" T.P. main. 18' out on n/s Allston way 85-88 & 92 w/o 9th st.
28 | 72-60004-1 |  |  | 8 | Transmission |  | Valves |  |  | Material Failure |  | 1972-01-30 | 1972-03-20 | Other |  | Steel/Wrought Iron |  | Berkeley | Found 8" T.P valve leaking. Reg crew greased valve and stopped leak. Did not do any digging
28 | 71-00297-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1971-06-08 | 1971-11-30 | Patch Welded |  | Steel/Wrought Iron |  | Berkeley | Welded patch over pit
;
28 |  |  |  | 12 | [11 empty] | Steel/Wrought Iron |  | Berk.
28 | 84-20073-1 |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1984-01-20 | 1984-01-20 | Other |  | Steel/Wrought Iron | ; | Berkeley | Rpaired 301 in curb meter box by reading iron connections and tightening tang packing. Nut on 3/4" insulated stopcock.
|  |  |  | 6 | Distribution Feeder Main | [7 empty] | 1972-09-05 |  |  | Steel/Wrought Iron |  | Berkeley | Cutt off 3/4" serg
28 | 89-20033-1 |  |  | 4 | Transmission |  | Physical/Mechanical Joint |  |  | Other |  | 1989-02-24 | 1989-02-24 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Berkeley | Found leak in reg pit. Referred tp M&C dept
28 | 96-21315-1 |  |  | 12 | Distribution Feeder Main |  | Other |  |  | Other |  | 1996-11-07 | 1998-03-19 | Other |  | Steel/Wrought Iron |  |  | Tightened fitting
28 | 96-21314-1 |  |  | 12 | Distribution Feeder Main |  | Other |  |  | Other |  | 1996-11-07 | 1998-03-19 | Other |  | Steel/Wrought Iron |  |  | Tightened Fitting
28 | 86-30101-2 |  |  | 24 | Transmission |  | Valves |  |  | Other |  | 1986-12-03 | 1986-12-03 | Other |  | Steel/Wrought Iron |  | Berkeley | Found 301 on blow off stack
1 | 81-40081- |  |  | 20 | Transmission |  | Valves |  |  | Corrosion |  | 1981-01-20 | 1981-02-02 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Berkeley | WELDED CAN OVER 2" VALVE TO 20" MAIN-BECAUSE OF SIZE OF CAN (22" HIGH). PAVED 6" CONCRETE T.P. MAIN TO PROTECT CAN. DIG INS.
28 | 72-20809-1 |  |  | 0.75 | Other |  | Meter |  |  | Material Failure |  | 1972-11-15 | 1973-03-06 | Other |  | Steel/Wrought Iron |  | Berkeley | Only leakage i could locate was 3/4" plug in 3/4" stop cock on manifold doped & tightened plug stopped leakage
28 | 72-20811-1 |  |  | 1.5 | Other |  | Meter |  |  | Material Failure |  | 1975-11-15 | 1973-03-08 | Other |  | Steel/Wrought Iron |  | Berkeley | Found 11/2 union leaking in meter set. Tightened union stopped leakage. No leakage over service or main
28 | 75-20231-1 |  |  | 1.25 | Other |  | Other |  |  | Other |  | 1975-06-16 | 1975-07-14 | Other |  | Steel/Wrought Iron |  | Berkeley | Found 11/4" screwed plug on meter set leaking
| 74-48039- |  |  | 0.34 | Other | SAV-A NIPPLE | Fitting |  |  | Material Failure |  | 1974-01-10 | 1974-01-10 | Other | TIGHTENED UP CAP. | Steel/Wrought Iron |  |  | FOUND 3/4 SAV-A-NIPPLE LEAKING TIGHTENED UP BRASS PLUG & CAP TO STOP LEAKAGE.
| 82-10254- |  |  |  | Other |  | Other |  |  | Other |  | 1982-02-25 | 1983-04-14 | Other |  | Other |  |  | D-68 # 312485-3001 CURB METER. B-76 # 323375-1122 CURB METER, TIGHTENED BRASS NUT ON 3/4" COCK TO CORRECT LEAKAGE IN CURB BOX.
26 | 91-40413-1 |  |  | 3 | Gathering |  | Fitting |  |  | Corrosion |  | 1991-05-03 | 1991-06-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  |  | TIGHTENED LOOSE PLUG & CAP ON 3/4" SAVE-A-VALVE & CAP ON 2" PCF (NO LEAKING) STOPPED LEAKAGE.
|  |  |  | 0.03 | Distribution Feeder Main | [6 empty] | 1972-06-01 |  | Other |  | Steel/Wrought Iron |  | OAKLAND
| 74-55114- |  |  | 3 | Other | FOR GAUGE | Physical/Mechanical Joint |  |  | Other |  | 1974-04-11 | 1974-04-11 | Other | TIGHTENED | Steel/Wrought Iron
26 | 74-5505-4 |  |  | 0 | Other |  | Other |  |  | Other |  |  |  | Clamp |  | Other
26 | 72-30831-1 |  |  | 3.51 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-03-15 | 1972-05-18 |  |  | Steel/Wrought Iron
|  |  |  | 2 | Other |  | Other |  |  | Corrosion |  | 1972-11-13 |  | Other |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 2 | Other |  | Other |  |  | Other |  | 1972-11-08 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND
| 73-48036- |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-01-10 | 1973-01-17 | Clamp |  | Steel/Wrought Iron
25 | 81-40203- |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-03-23 | 1981-06-16 | Other |  | Other |  | OAK. | MAIN/SERV NOT EXPOSED CLEARED 301 ON INSUL S/O VALVE.
1 | 72-48154-A |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-08-15 | 1972-08-15 | Patch Welded |  | Steel/Wrought Iron
1 | 72-48154-A |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-08-15 | 1972-08-15 | Patch Welded |  | Steel/Wrought Iron
26 | 73-49641- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-12-17 | 1973-12-17 | Clamp |  | Steel/Wrought Iron |  |  | FOUND LEAK AT OLD CURB VALVE WITH THREADS CORRODED. USED SKINNER LEAK CLAMP TO STOP LEAKAGE.
|  |  |  | 3 | Distribution Feeder Main |  | Other |  |  | Other |  | 1974-01-30 | 1974-01-30 |  |  | Steel/Wrought Iron |  | OAKLAND;
|  |  |  | 3 | Other |  | Other |  |  | Other |  |  | 1977-04-22 | Other |  | Steel/Wrought Iron |  | OAKLAND | BONDED OVER 3" DRESSOR COUPLING.
| 81-30002- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1982-01-09 | 1982-01-21 | Other | P/R (SECTION | Steel/Wrought Iron |  |  | MADE PERM. REPAIRS BY REPLACING 16' OF LEAKING 3/4" STL SERV W/ 1/2 PL. INSERT /S.T. 1-21-82.
26 | 82-30002-1 |  |  | 3 | Distribution Main | [6 empty] | 1982-01-18 | 1982-01-21 |  |  | Steel/Wrought Iron |  |  | DUG DRY HOLE OVER MAIN MARKED BY FLAME PACK, LOCATED LEAK ON SERV TO 6901 BALSAM. MADE PERM. REPAIRS BY REPLACING 16' OF 3/4" STL SERV W/ 1/2" PL INSERT.
26 | 73-55143- |  |  | 0.5 | Service |  | Other Welds |  |  | Construction Defect |  | 1973-03-13 | 1973-03-14 | Replace Pipe and/or Service |  | Copper |  |  | REPLACED LEAKING COPPER SOLDIER JOINT BY REPLACING WITH 1' OF 1/2" PLASTIC.
| 02-10045- |  |  | 1 | Service |  | Fitting |  |  | Construction Defect |  | 2002-02-08 | 2002-02-27 | Tighten Cap or Bolt |  | Aldyl A (Tan or Gray) |  | EMERYVILLE | TIGHTEN 1 1/4" SERV. VALVE ON RISER.
| 87--1 |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1987-01-13 | 1987-01-13 | Other | C/O 3/4" STL MADE MAIN INS | Steel/Wrought Iron |  | EMERYVILLE | MAIN IN VERY GOOD CONDITION MADE C/O ON 3/4 STL SLEEVE.
26 |  |  |  | 6 | Transmission
| 90-10032-5 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Digin |  | 1990-01-26 | 1990-01-26 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | EMERYVILLE; | BACKHOE BROKE 3/4" STUB OFF 3/4" SERVICE TEE. INSTALL 3" CANN ON 4" T.P. MAIN OVER SER. TEE.
26 | 94-23550-1 | [10 empty] | 1994-02-04 | [5 empty] | OAKLAND
| 98-10378-1 |  |  | 0.25 | Service |  | Fitting | Valves |  | External Corrosion |  | 1998-09-22 | 1998-09-22 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EMERYVILLE
| 97-14991-1 |  |  | 0.75 | Service |  | Valves |  |  | Material Failure |  | 1997-07-24 | 1997-07-24 | Other |  | Steel/Wrought Iron |  | Emeryville
1 | 94-12429-1 |  |  | 3 | Service |  | Valves |  |  | Other |  | 1994-02-04 | 1994-02-04 | Other |  | Steel/Wrought Iron |  | EMERYVILLE | GREASED VAKVE SERVICE TO BE CUT OFF EXPOSED AT SERVICE TEE.
1 | 90-10342-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1990-06-15 | 1990-06-18 | Patch Welded |  | Steel/Wrought Iron |  | EMERYVILLE | DRILLED HOLES - DOWN GRADED TO #2. ARC WELDED PATCH OVER HOLES IN 4" STEEL MAIN.
[12 empty] | 1993-10-21 | 1993-10-21 |  |  |  |  | EMERYVILLE
EMERYVILLE
|  |  |  | 4 | Distribution Main | [7 empty] | 1974-08-30 |  |  | Steel/Wrought Iron
|  |  |  | 4 | Distribution Feeder Main |  | Other |  |  | Other |  | 1974-05-30 | 1974-05-30 | Other | NEW SERVICE | Steel/Wrought Iron
| 00-11407- |  |  | 0.75 | Service |  | Fitting |  |  | Construction Defect |  | 2000-12-05 | 2000-12-05 | Other | TEMP REPAIRS. FITTINGS LEAKING. | Steel |  | EMERYVILLE | TURNED VALVE OFF AT INLET SIDE OF HIGH TO HIGH SET. TEMPORARY REPAIRS PER SUPERVISOR.
26 | 94-23551-1 |  |  | 0.75 | Service |  | Fitting |  |  | Material Failure |  | 1994-02-04 | 1995-06-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | OAKLAND | TIGHTENED METRIC VALVE THAT WAS LEAKING. REPAIRED LEAKY REG.
| 80-48879- | [7 empty] | MF |  |  | 1980-11-10 | 1980-11-10 | Other |  |  |  |  | REG CREW CALL LEAK IN. FOUND LEAK ON 2" GAS VALVE REG TOOK CARE OF IT.
| 80-48521- |  |  | 0.75 | Other | REGULATORS | Body of Pipe |  |  | Corrosion |  | 1980-06-05 | 1980-06-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | REPLACE HIGH TO HIGH SET DUE TO LEAKAGE ON OLD ONE. ALL SCREWED FITTINGS WERE LEAKING.
| 00-11196-1 |  |  | 0.25 | Distribution Main |  | Other |  | STATIC LINES | Digin |  | 2000-06-09 | 2000-06-09 | Other | SQUEEZED OFF VENT LINGS ON STACK -- S/O VENT IN STATION | Steel/Wrought Iron |  | EMERYVILLE | CAR HIT RECORDER ON VENT STACK - BREAKING PRESS LINES TO REGULATOR S/O DISCONNECTED LINE.
| 80-48084- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Construction Defect |  |  | 1980-01-22 | Other | C/O | Steel/Wrought Iron |  |  | C/O SERVICE AND CHANGED PIN OFF SERV TEE ON TP MAIN.
|  |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  |  |  | Other
25 | 77-- |  |  | 6 | Distribution Feeder Main |  | Other |  | None, re-wrap main | Other | NONE | 1977-10-31 | 1977-10-31 | Other |  | Steel/Wrought Iron |  | Emeryville
71--
| 00-51001-1 |  |  | 30 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 2000-06-20 | 2000-06-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Emeryville
26 | 93-22825-1 | [10 empty] | 1995-01-23 | [5 empty] | Emeryville
26 | 92-22446-1 | [10 empty] | 1992-07-16 |  |  |  | Other
26 | 87-20050-1 |  |  | 2 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-02-05 | 1988-03-17 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Emeryville
|  |  |  | 2 | Transmission | [6 empty] | 1977-06-24 | [5 empty] | Emeryville
| 93-12086-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1993-06-18 | 1993-06-18 | Replace Pipe |  | TR 418 |  | Emeryville
26 | 89-20356-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1989-02-07 | 1990-05-03 | Patch Welded |  | Steel/Wrought Iron |  | EMERYVILLE
| 97-14958-1 |  |  | 0.75 | Service |  | Valves | Body of Pipe |  | External Corrosion |  | 1997-07-15 | 1997-07-15 | Other | GREASED VALVE + REPAIRED IRON CONNECTIONS | Steel/Wrought Iron |  | EMERYVILLE
| 97-15009-1 |  |  | 0.75 | Service |  | Fitting |  |  | External Corrosion |  | 1997-08-05 | 1997-08-05 | Replace Pipe | PULLED MANIFOLD. INST NEW SERVICE VALVE | Steel/Wrought Iron |  | EMERYVILLE
| 71-20118-1 |  |  | 6 | Distribution Main |  | Physical/Mechanical Joint |  |  | Corrosion |  |  | 1971-04-22 | Other |  | Steel/Wrought Iron
| 01-10234 |  |  | 4 | Transmission |  | Valves |  |  | External Corrosion |  | 1982-02-17 | 1982-11-02 | Other |  | Steel/Wrought Iron
|  |  |  | 6 | [13 empty] | EMERYVILLE | CUT OFF 3/4" SERVICE; (AROUND SER/ TEE)
| 99-10632 |  |  | 1.25 | Service |  | Riser |  |  | Digin |  | 1999-05-07 | 1999-05-07 | Replace Pipe | REPLACED 11/4" RISER | TR 418 |  | EMERYVILLE
| 98-10438- |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1988-02-09 | 2008-02-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EMERYVILLE | LEAK IN HIGH TO HIGH BOX. HAD METER CREW GREASE VALVE AND TIGHTEN UNION TO STOP LEAK.
| 95-13603-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Digin |  | 1995-08-23 | 1995-08-23 | Other |  | Steel/Wrought Iron |  | EMERYVILLE
| 90-10646-1 |  |  | 0.75 | Service |  | Valves |  |  | Digin |  | 1990-12-20 | 1990-12-20 | Other |  | Steel/Wrought Iron |  | OAKLAND
26 | 72-21074-1 |  |  | 02.5P | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-08-10 | 1970-10-26 |  |  | Steel/Wrought Iron
26 | 72-21398-1 |  |  | 3 | Transmission |  | Valves |  |  | Material Failure |  | 1972-12-21 | 1973-03-26 | Weld Over Sleeve or Can |  | Steel/Wrought Iron
26 | 95-50186-1 |  |  | 1.25 | Service |  | Valves |  |  | Material Failure |  |  | 1995-12-20 | Other | GREASED VALVE | Steel/Wrought Iron |  | EMERYVILLE
| 76-48560-1 |  |  | 0.34 | Other |  | Valves |  |  | Material Failure |  | 1976-05-19 | 1976-05-20 | Other |  | Steel/Wrought Iron |  | EMERYVILLE
| 97-14836-1 |  |  | 2 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1997-04-21 | 1997-04-21 | Replace Pipe |  | Steel/Wrought Iron |  | EMERYVILLE | M.THOMAS
26 | 93-22802-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other |  | 1993-01-27 | 1994-03-11 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EMERYVILLE
| 02-20157-1 |  |  | 2 | Service |  | Valves | Valves |  | Construction Defect |  | 2002-08-06 | 2004-02-05 | Other | GREASED FLANGE VALVE | Steel/Wrought Iron |  | EMRYVILLE
| 02-20157-1 | [16 empty] | EMERYVILLE
| 97-14942-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1997-07-07 | 1997-07-07 | Replace Pipe |  | Aldyl A (Tan or Gray) |  | EMERYVILLE
26 | 95-24349-1 |  |  | 0.75 | Service |  | Fitting |  |  | Construction Defect |  | 1995-01-18 | 1995-11-27 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EMERYVILLE
7 |  |  |  | 4 | Transmission | [7 empty] | 1986-06-30 |  |  | Steel/Wrought Iron |  | Emeryville | MAINTENANCE... INSTALLED...
| 93-12189-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Digin |  | 1993-08-20 | 1993-08-20 | Replace Pipe |  | Other Plastic |  | Emeryville | Replaced 1' of 1" plastic. Services.
1 | 93-12148-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Digin |  | 1993-07-30 | 1993-07-30 | Other |  | Aldyl A (Tan or Gray) |  | Emeryville | INSIDE PROPERTY. OVER GAS SERVICE. REPLACED 18' SECTION OF AIDYL "A" WITH TR 418 1" PLASTIC. REPLACED 18" SECTION A/C DIGIN (TR-418)
Emeryville
| 93-12148-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Digin |  | 1993-07-30 | 1993-07-30 | Replace Pipe |  | Aldyl A (Tan or Gray) |  | Emeryville | CONTRACTOR HIT SERVICE IN PROPERTY. INSTALLED 2 1' PELMASERT COUPLINGS AND REPLACED APPROX 2' OF 1" PIPE; REAPIRED D.S. 7/30/88.
1 | 90-10464-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Digin |  | 1990-09-07 | 1990-09-07 | Replace Pipe |  | Aldyl A (Tan or Gray) |  | Emeryville | OVER SERVICE. REPLACED 2' SECTION OF 1" PL SERVICE. REPLACED 2' SECTION OF DAMAGED 1" PLASTIC PIPE.
26 | 88-20005-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other |  | 1988-02-20 | 1989-01-10 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Emeryville | LOOSENED, REDOPED, AND TIGHTENED FOR PERM REPAIRS.
Emeryville
|  |  |  | 4 | Transmission | [7 empty] | 1981-05-15 | Other | SERVICE VALVE | Steel/Wrought Iron |  | Emeryville | ...
Emeryville
|  |  |  | 4 | Distribution Main | [7 empty] | 1974-05-02 |  |  | Steel/Wrought Iron |  | Emeryville | HERE ON A SERVICE RERUN.
Emeryville
|  |  |  | 4 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1975-02-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Emeryville | INSTALL 1 1/4 SERV. AND 50' OF 1 1/4... HIGH 5 HIGH REG... NO PAVING.
Emeryville
|  |  |  | 4 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1975-03-14 | Other |  | Steel/Wrought Iron |  | Emeryville
Emeryville
|  |  |  | 4 | [13 empty] | EMERYVILLE | MAIN ON WEST SIDE OF HORTON STREET. 36' SOUTH OF 53RD STREET.
Emeryville
26 | 88-20006-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1988-02-10 | 1989-01-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Emeryville | OP 3/4 SUC VALVE. TIGHTENED NUT IN BACK OF VALVE FOR PERM REPAIRS.
Emeryville
2 | 88-11070-C |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1988-12-13 | 1988-12-14 | Replace Pipe |  | Steel/Wrought Iron |  | Emeryville | REPLACED 25' PF 4" TP MAIN DUE TO LEAKAGE. 12-14-88.
Emeryville
|  |  |  | 4 | Transmission | [12 empty] | Emeryville | INSTALL 5' OF 3/4" STL SERVICE AND SET HI TO HI SET.
Emeryville
1 | 89-60091-F |  |  | 2 | Transmission |  | Fitting |  |  | Other |  | 1989-10-26 | 1989-10-26 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Emeryville | 30' LEFT OF DOORWAY STL.; REDOPED AND TIGHTENED CAPS ON 2" M2 FITTING AND SAVE A VALVE. STOPPED LEAKAGE.
Emeryville
|  |  |  | 4 | Transmission | [12 empty] | Emeryville | DEMOLITION C/O 3/4" T.P. SERV. DEMOLITION C/O SERV. A DIN-OFF TEE.
Emeryville
26 | 82-10239- |  |  | 4 | Transmission |  | Fitting |  |  | Material Failure |  | 1982-02-18 | 1982-09-22 | Other |  | Steel/Wrought Iron |  | Emeryville | FOUND LEAK ON BLOW OFF 286' N/O 53RD STREET. CUT OFF MAIN 80' N/O M3RD STREET. (W/O 47369-A 1224 2000)
Emeryville
|  |  |  | 4 | Transmission |  | Other |  |  | Other |  | 1973-11-30 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron
Emeryville
| 02-10284- |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 2002-09-25 | 2002-09-25 | Service Partially Replaced |  |  |  | Emeryville | REPLACED 3' OF 1/2" PLASTIC PIPE
26 | 96-25252-1 |  |  | 2 | Service |  | Valves |  |  | Material Failure |  | 1996-01-09 | 1996-10-18 | Other |  | Steel/Wrought Iron |  | Emeryville | REPLACED 2" SERVICE VALVE
26 | 96-25251-1 |  |  | 0.75 | Service |  | Body of Pipe | Valves |  | Corrosion |  | 1996-01-09 | 1996-10-18 | Replace Pipe | Tighten Cap or Bolt | Steel/Wrought Iron |  | Emeryville | REPAIRED SERVICE VALVE AND REBUILT IRONS.
26 | 93-22765-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Material Failure |  | 00/23/1993 | 1994-03-14 | Other |  | Steel/Wrought Iron |  | Emeryville
1 | 94-12411-1 |  |  | 0.75 | Service |  | Fitting |  |  | External Corrosion |  | 1994-01-25 | 1994-01-25 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Emeryville | SCREWED FITTINGS ON HIGH TO HIGH SET. LEAKING AT THREADS. BYPASSED SET AND REDOPED AND RETIGHTENED FITTINGS. STOPPED LEAKAGE.
1 | 94-12416-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1994-01-25 | 1994-01-25 | Other |  | Steel/Wrought Iron |  | Oakland | CURB BOX. GREASED INLET VALVE AND BYPASS VALVE ON HIGH TO HIGH SET.
26 | 88-20000-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1988-02-10 | 1989-01-23 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Emeryville | HIGH TO HIGH SET INSIDE ... B BOX. TIGHTENED CAPS ON METRIC VALVE. REPAIRING LEAKAGE.
26 | 88-20002-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1988-02-10 | 1989-01-23 | Other |  | Steel/Wrought Iron |  | Emeryville | HIGH TO HIGH SET. GREASED 2-VALVES ON TP SIDE OF SET. STOPPED LEAKAGE ON VALVES.
26 | 88-20001-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1988-02-10 | 1989-01-17 | Other |  | Steel/Wrought Iron |  | Emeryville
26 | 89-20355-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1989-02-07 | 1990-04-14 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Emeryville | ON MAIN ST AREA. WELDED PATCH FOR PERM REPAIRS.
26 | 96-50209-1 |  |  | 2 | Service |  | Fitting |  |  | Material Failure |  | 1996-01-25 | 1996-11-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  |  | TIGHTEN...
26 | 96-25254-1 |  |  | 2 | Service |  | Fitting |  |  | Corrosion |  | 1996-01-08 | 1996-10-09 | Tighten Cap or Bolt | Other | Steel/Wrought Iron |  | Emeryville | GREASED VALVE AND TIGHTEN 2" UNION.
26 | 95-25248-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1996-01-09 | 1996-10-15 | Replace Pipe |  | Steel/Wrought Iron |  | Emeryville | REBUILT HIGH TO HIGH SET.
26 | 94-12546-1 |  |  | 0.75 | Service |  | Regulator |  |  | Material Failure |  | 1994-03-02 | 1994-03-02 | Other |  | Steel/Wrought Iron |  | Emeryville | HIGH TO HIGH SET. SHUTOFF INLET VALVE. REMOVED EXISTING HIGH TO HIGH SET. PLUGGED OFF VALVE.
26 | 88-20009-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1988-02-10 | 1989-01-23 | Other |  | Steel/Wrought Iron |  | Emeryville | CURB BOX ELBOW AT NIPPLE. TIGHTENED NIPPLE INTO ELBOW ON SERVICE INSIDE CURB BOX. REPAIRED LEAKAGE.
26 | 95-24352-1 |  |  | 0.75 | Service |  | Valves | Fitting |  | Material Failure |  | 1995-01-15 | 1995-11-28 | Other |  | Steel/Wrought Iron |  | Emeryville | GREASED VALVE + TIGHTENED FITTINGS
26 | 93-22822-1 |  |  | 1 | Service |  | Fitting | Valves |  | Corrosion |  | 1993-01-25 | 1994-03-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Emeryville | RISER AT BYPASS NIPPLE AND VALVE. TIGHTENED NIPPLE TIE AT BYPASS A/C LEAKAGE. TIGHTENED CONE ON VALVE A/C TEST BYPASSING. STOPPED LEAKAGE.
| 88-10587-D |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1988-04-12 | 1988-04-12 | Replace Pipe and/or Service |  | Aldyl A (Tan or Gray) |  | Emeryville | REPLACED 2' SECTION OF 1/2...
|  |  |  | 4 | [11 empty] | Steel/Wrought Iron |  | Emeryville
| 72-45053-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-03-17 | 1972-03-22 | Other | CANS | Steel/Wrought Iron |  | Emeryville | ALTHOUGH THIS 4" TP MAIN IS WELDABLE IN SPOTS IT NEEDS TO BE REPLACED. WRAP IS WET AND 50MM CAUSING LARGE AND DEEP PITS UNDER THE WRAP.
| 72-45053- |  |  | 4 |  |  | Body of Pipe |  |  | Corrosion |  | 1972-03-07 | 1972-03-20 | Clamp | Replace Pipe and/or service | Steel/Wrought Iron |  |  | DUE TO 8" C.I. WATER MAIN MAKING CONTACT W/ 4" TP MAIN AT PT. OF GAS LEAKAGE IT WAS NEC. TO INST (2) 4" B.T.P.C.F.S. SER. 30 & 10' OF 4" X-TERCOAT PIPE. ELIMINATED (4) OTHER LEAKS IN IMMED. AREA ALSO. INST (1) PATCH & 10' OF 4" X-TEV COAT PIPE TO ELIMINATE LEAKAGES.
26 | 89-11666-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1989-11-02 | 1985-12-01 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Emeryville | WELEDED 2" SAVE-A-VALVE OVER PIT AND CAPED IT OFF.
26 | 89-20354-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1989-02-07 | 1990-04-14 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Emeryville
2 | 92-40299-5 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1990-04-14 | 1990-04-14 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Emeryville | INSTALLED 4" SOLE WELDED FOR PERM REPAIRS. 4-14-90.
| 89-11666- |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1989-11-02 | 1989-12-01 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Emeryville | DOWNGRADE TO #2 11-2-1989 DRILLING AND VENTING REBUILT. WELDED CAN OVER PIT.
| 88-10425-F |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1988-01-27 | 1988-01-27 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Emeryville | WELDED CAN ... LARGE PIT ON 4" STEEL GAS MAIN.
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | Emeryville
|  |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  | 1972-03-15 |  | Other |  | Steel/Wrought Iron |  | Emeryville
26 | 93-22823-1 |  |  | 0.75 | Service |  | Valves |  |  | Corrosion |  | 1993-01-25 | 1994-03-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Emeryville | AT BYPASS VALVE; REDOPED AND TIGHTENED VALVE.
| 73-48213- |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-02-13 | 1973-02-15 | Patch Welded |  | Steel/Wrought Iron |  | Emeryville | ARC WELD (2) 4 AMD 8" PATCHES ON MAIN. MAIN AT THIS LOCATION IN GOOD CONDITION.
26 | 88-20008-1 | [10 empty] | 1988-02-10 | 1989-05-10 |  |  |  |  | Emeryville | NEED REG CREW TO BYPASS HIGH TO HIGH SET AND REPLACE REGULATOR.; + SCREWED 3/4" NIPPLE AT REGULATOR. (TAPED AT THREADS)
26 | 93-22767-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Material Failure |  | 00/13/1993 | 1994-03-14 | Replace Pipe |  | Steel/Wrought Iron |  |  | RE-PIPED & RE-DOPED REG. PIT.
|  |  |  | 4 | [13 empty] | EMERYVILLE | INSTALL SERVICE TO ADDRESS & STL. & 1 1/4" PI.
|  |  |  | 4 | Transmission | [7 empty] | 1979-05-23 | Other | NEW SERVICE | Steel/Wrought Iron |  | EMERYVILLE | EXPOSED MAIN N/E NEW 3/4" STL.SERVICE
26 | 96-25258-1 |  |  | 0.75 | Service |  | Valves | Fitting |  | Corrosion |  | 1996-01-08 | 1996-10-09 | Other |  | Steel/Wrought Iron |  | EMERYVILLE | REPAIRED VALVE + 3/4" UNION
26 | 96-25257-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1996-01-08 | 1996-10-09 | Clamp |  | Steel/Wrought Iron |  | Emeryville | INSTALLED 3/4" THREAD CLAMP ON 3/4" NIPPLE.
26 | 95-24354-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Internal Corrosion |  | 1995-01-18 | 1995-01-11 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Emeryville | OVER SERVICE.; TIGHTEN AND GREASED 3/4 T.P. VALVE. HIGH TO HIGH.
26 | 96-25253-1 |  |  | 0.75 | Service |  | Valves |  |  | Corrosion |  | 1996-01-09 | 1996-09-08 | Other |  | Steel/Wrought Iron |  | Emeryville | HIGH TO HIGH CURB BOX. GREASED VALVE. REGULATOR CREW REBUILT. HIGH TO HIGH SET.
26 | 96-25249-1 |  |  | 2 | Service |  | Valves |  |  | Material Failure |  | 1996-01-09 | 1996-10-15 | Other |  | Steel/Wrought Iron |  | Emeryville | REPAIRED 2" VALVE AND 1 1/4" BYPASS VALVE.
|  |  |  | 3 | Transmission | [10 empty] | Steel/Wrought Iron |  | Emeryville
26 | 82-10135- |  |  | 0.75 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1984-02-01 | 1982-02-24 | Other |  | Steel/Wrought Iron |  | Oakland | SVC VALVE .07%; LOOSE NUT ON 3/4 VALVE. TIGHTEN NUT...
INST. 6" CAN OVER LEAKING 2"X1 TEE IN 2" MAIN @ 112 W/W/L OF LOWELL ST. ON 2 LP 10 N/S/L OF 54TH ST.
26 | 82-10127- |  |  |  | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1982-02-01 | 1982-02-18 | Clamp |  | Steel/Wrought Iron |  | Oakland | SVC VALVE .1%; ...
INSTALL 6" CAN OVER LEAKING 2"X1 TEE OM 2" MAIN @ 112 W/W/L OF LOWELL ST. ON 2 LP @ N/S/L OF 54TH ST.
26 | 82-10129- |  |  |  | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1980-02-01 | 1982-02-19 | Other |  | Steel/Wrought Iron |  | Oakland | ... TIGHTEN UP TO TAP SERVICE.
INST. 6" CAN OVER LEAKING 2x1 TEE OM 2" MAIN @ 112 W/W/L OF LOWELL ST. ON 2 LP 10 N/S/L OF 54TH ST.
1 |  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  | 1977-10-04 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | EXPOSED PIPE TO MAKE TIE IN AND CUT OFF. 54TH ST. 5' FROM SAN PABLO ON THE EAST SOUTH SIDE.
ON 4" LP 19' S/S 54TH ST INST 1-4" PCF AT 2' E/E/L SAN PABLO. C/O ON ABAND 3" C.I.- 19' S/S 54TH ST FROM 3' E/E/L SAN PABLO AVE TO 2' W/W/L GASKILL ST. INST. 4" LP 21' (STL.) S/S 54TH STREET FROM 3' E/E/L SAN PABLO AVE TO 2' W/W/L GASKILL STREET. THIS WORK DONE DUE TO HAZARDOUS GAS LEAKAGE. ON 6" LP 27' W/S SAM PABLO AVE. INST. 10-6" LC.S. AT 8'-20'-32'44' S/S AMD 4'-16'-28' N/S/L AND AT 10'-22'-34'- S/N/L 54TH.
1 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1977-10-04 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Oakland | EXPOSED PIPE TO MAKE TIE IN AND CUT OFF.
| 77-48217- |  |  | 0 | Other |  | Fitting |  |  | Construction Defect |  | 1977-02-28 | 1977-02-28 | Other |  | Other |  | Oakland | FOUND 30' ON METER ... PIT TO REPAIR 30' BAN TEST SERVICE.
|  |  |  | 6 | Other | [10 empty] | Cast/Ductile Iron
1 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1977-09-28 | 1977-09-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Oakland | NO WELDING. ON THE WEST DIFE OF SAN PABLO AVE. 95' SOUTH OF 53RD ST. EXPOSED PIPE TO MAKE CUT OFF.
1 |  |  |  | 6 | Distribution Main |  | Other |  |  | Other |  | 1977-09-27 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Oakland | 48TH ST AND SAN PABLO 6" NORTH OF 48TH ST.
1 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1977-10-04 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Oakland | SAN PABLO AVE 15' OUT AT 54TH ST ON SOUTH WEST SIDE.
1 | 70-45164-A |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-06-26 | 1972-06-26 |  |  | Steel/Wrought Iron |  |  | MADE REPAIR TO ... MAIN. WORK IN AND PREY TAPS.
1 | 70-45164-A |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-06-26 | 1972-06-26 |  |  | Steel/Wrought Iron |  |  | MADE REPAIR TO ... MAIN. WORK IN AND GREY TAPE.
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other | [5 empty] | Steel
|  |  |  | 4 | Distribution Main |  | Other |  |  | Other | [5 empty] | Steel/Wrought Iron
| 76-35108- |  |  | 0 | Other |  | Meter |  |  | Material Failure |  | 1976-06-28 | 1976-06-25 | Replace Pipe and/or Service |  | Other |  | Oakland | LEAK ON METER; METER HAS BEEN CHANGED. 6/25/1976.
1 | 72-31122- |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-05-10 | 1972-05-10 |  |  | Steel/Wrought Iron |  |  | INSTALL 10" LC AND TAPED THE REST TO ... TO WELD.
|  |  |  | 2 | Other |  | Other |  |  | Other |  | 1974-07-01 | 1974-07-01
| 74-00064- |  |  | 16 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-01-09 | 1974-01-28 | Patch Welded |  | Steel/Wrought Iron |  |  | PATCH WELDED 2" BLOW OFF FROM 16" HP MAIN.
1 | 02-00597- |  |  | 16 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1982-08-31 | 1982-09-28 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Oakland | ARC WELD OVER CORROSION LEAK 16" H.P. MAIN WHERE MAIN IS UNDER R/R TRACKS. STL CASING. 11" X 12" STL. PATCH INSTALLED 23' S/O OF N/W CORNER OF 47TH ST. REPAIRED CORRISION LEAK ON 16" H.P. MAIN ARC WELD 11" X 12" STL. PATCH PVER CORROSION LEAK, WHERE 16" MAIN IS UNDER R/R TRACKS. NO STL CASING OVER 16" H.P. MAIN.
|  |  |  | 2 | Distribution Main |  | Other |  |  | Corrosion |  | 1973-11-01 | 1973-11-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | MAIN AND SERVICE.
1 |  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1976-04-13
|  |  |  | 8 | Distribution Feeder Main | [7 empty] | 1975-02-14 |  |  | Steel/Wrought Iron |  |  | WO 4148-13.
|  |  |  | 12 | Distribution Feeder Main | [7 empty] | 1974-08-14 |  |  | Steel/Wrought Iron |  |  | INISTALLED 12" INSULATING FLANGE - TEST LEAK.
26 |  |  |  |  | Other |  | Physical/Mechanical Joint |  |  | Other |  | 1972-05-04 |  |  |  | Cast/Ductile Iron |  | Oakland
| 02-20113- |  |  | 0.5 | Service |  | Plastic Tee Cap |  |  | Material Failure |  | 2002-02-05 | 2002-06-25 | Other | OVERCAP KIT | Aldyl A (Tan or Gray) |  | Oakland | WATERBOX ON SIDEWELD AND SERVICE.
26 | 74-49383- |  |  | 11 | Service |  | Other |  |  | Damage by outside Forces |  | 1974-11-06 | 1974-11-06 | Other |  | Other Plastic |  | Oakland | TWO 1 1/8 AMP-FIT COUPLING, INST. 10' PLASTICE PIPE.
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1975-04-20 | 1975-04-29 |  |  | Steel/Wrought Iron |  | Oakland
| 76-48835- |  |  | 6 | Distribution Main |  | Valves |  |  | Other |  | 1976-08-03 | 1976-08-03 | Other |  | Steel/Wrought Iron |  | Oakland | VALVE HAS BEEN REPAIRED ALREADY.; DUCT SEAL + TAPE ON TOP AND BOTTOM OF 6" VALVE IN REG. SIT.
| 76-20175-1 |  |  |  | Other |  | Other |  |  | Other |  | 1976-03-17 |  | Other |  |  |  | Oakland | 5255 COLLEGE. X CLIFTON ST. AT CURB VALVE. CURB VALVE OK NO LEAK; CHECLED CURB VALVE W/ LEAK DETECTOR FOUND NO LEAKAGE. PLEASE HAVE FLAMMAR CONFIRM. NO PAVEMENT. NO SAW.
| 76-20380-1 |  |  |  | Other |  | Other |  |  | Other |  | 1976-04-07 |  | Other |  |  |  | Oakland | #3 N/L. 5576 - COUNTRY CLUB. OVER MAIN IN LAWN 5' UP FROM ETS STATION ON WESTMINSTER. FOUND NO READINGS. PROBED OVER MAINS AND SERVICE COULD NOT FIND ANY LEAKAGE.
26 | 76-20192-1 |  |  | 0.34 | Other |  | Fitting |  |  | Material Failure |  | 1976-03-18 | 1976-07-21 | Other |  | Steel/Wrought Iron |  | Oakland | 5592 LAWTON K-VIRMAR. AT INS. BUSHING; FOUND NYLON BUSHIND LEAKING. REPAIRED BY MOVING METER SET FROM UNDER HOUSE AND REPLACING NYLON BUSHING.
26 | 76-20191-1 |  |  | 0.34 | Other |  | Fitting |  |  | Material Failure |  | 1976-03-18 | 1976-07-21 | Other |  | Cast Iron |  | OAKLAND | 5592 LAWTON K-VIRMAR. AT INS. BUSHING; FOUND GAS LEAK ON METER SET OF NYLON BUSHING REPLACED BUSHING TO STOP LEAGAKE. USED BYA CHANGER TO SUPPLY GAS WHILE i CHANGED NYLON BUSHING. M SILVA. 2 MEN 1 1/2 MRU PAINTED METER SET 7/21/1976.
26 | 72-30837-1 |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-03-15 | 1972-04-21 |  |  | Copper | Steel |  | GROUND THREADS; 4-25-72 OLIVEIRS OK. MADE TEMP REPAIRS WITH DARK SEAL. TAPE TO STA LEAKAGE?
|  |  |  | 6 | Transmission |  | Other |  |  | Other |  |  | 1975-08-20 | Patch Welded |  | Cast/Ductile Iron
|  |  |  | 6 | Transmission |  | Other |  |  | Other |  |  | 1975-08-20 | Patch Welded |  | Cast/Ductile Iron
26 | 72-30843-1 |  |  | 6 | Distribution Feeder Main | [6 empty] | 1972-03-15 | 1972-05-25 |  |  | Cast Iron |  |  | FOUND NO LEAKAGE HERE IN THIS BUILT HERE.
| 73-49077- |  |  | 1.5 | Other |  | Body of Pipe |  |  | Corrosion |  | 1973-09-09 | 1973-08-13 | Clamp |  | Steel/Wrought Iron |  | Oakland | JUST ONE 1 1/2" ADAMS LEAK CLAMP ON BLOW OFF PIPE FROM DRIP POL. NO PAVING.
| 76-48817- |  |  | 0.34 | Other | Gas Lamp #4 | Valves | Other | PL. Bushings | Material Failure |  | 1976-07-29 | 1976-07-30 | Other |  | Steel/Wrought Iron |  | Oakland | GAS LAMP #4. LK REPAIR.
| 76-48817- |  |  | 0.34 | Other | Gas Line #13 | Valves | Other | Leaking PL Bushings. | Material Failure |  | 1976-07-29 | 1976-07-30 | Other |  | Steel/Wrought Iron |  | Oakland | GAS LAMP #13.
| 76-48817- |  |  | 0.34 | Other | Gas Lamp #5 | Valves | Other | PL Bushings | Material Failure |  | 1976-07-29 | 1976-07-30 | Other |  | Steel/Wrought Iron |  | Oakland | GAS LAMP #5; CK / REPAIR.
| 76-48817- |  |  | 0.34 | Other | Gas Lamp #9 | Valves | Other | PL. Bushings Leaking | Material Failure |  | 1976-07-29 | 1976-07-30 | Other |  | Steel/Wrought Iron |  | Oakland | GAS LAMP # 9.
| 76-48817- |  |  | 0.34 | Other | Gas Lamp #6 | Valves | Other | PL. Bushings | Material Failure |  | 1976-07-29 | 1976-07-30 | Other |  | Steel/Wrought Iron |  | Oakland | GAS LAMP #6.
| 76-48817- |  |  | 0.34 | Other |  | Valves | Other | Plastic Bushings | Material Failure |  | 1976-07-29 | 1976-07-30 | Other |  | Steel/Wrought Iron |  | Oakland | GAS LAMP #14.
| 76-48817- |  |  | 0.34 | Other | Gas Mapl #2 | Valves | Other | Leaking PL Bushing and CU Compression fitting. | Material Failure |  | 1976-07-29 | 1976-07-30 | Other |  | Steel/Wrought Iron |  | Oakland | GAS LAMP #2; CK REPAIR.
26 | 86-20226- |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  | 1986-05-16 | 1987-08-28 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | OAKLAND | Leak on 850 hotline. Tightened cap.
26 | 75-48495-1 |  |  | 0.5 | Service |  | Fitting |  |  | Material Failure |  | 1975-06-16 | 1975-06-16 | Other |  | Other Plastic |  | Oakland | Nut on top of copper insert riser; Tightened nut on riser insert.
26 | 74-55017- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-01-13 | 1974-01-15 | Clamp |  | Steel/Wrought Iron |  |  | Used smith-blair clamps to stop leakage on 3/4" steel service. Found (3) corrosion leaks with a 4ft. area.
26 | 73-48200 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-02-13 | 1973-02-13 | Patch Welded |  | Steel/Wrought Iron |  | Berkeley
| 76-21439-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-08-26 | 1977-02-16 | Patch Welded |  | Steel/Wrought Iron |  | Oakland | Arc welder welded patch on 20" tp main. A/C corrosion leakage also dug 1 dry hole.
| 76-21439-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-08-26 | 1977-02-16 | Patch Welded |  | Steel/Wrought Iron |  | Oakland | Dug 1 hole-found leak in adjoining hole and repaired w/a welded patch.
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1973-11-21 | 1973-11-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  |  | 1975-03-27 | Other |  | Steel/Wrought Iron
|  |  |  | 8 | Distribution Main |  | Other |  |  | Other |  |  | 1975-02-27 | Other |  | Steel/Wrought Iron
|  |  |  | 8 | Distribution Main |  | Other |  |  | Other |  |  | 1975-03-27 | Other |  | Steel/Wrought Iron
|  |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-07-31 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | R/R service with 1/2" plt.
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1977-01-21 | 1977-02-02 | Other |  | Steel/Wrought Iron |  | Piedmont | Canned 3" dresser for cathodic protection purposes.
| 80-48795- |  |  | 0.75 | Service |  | Fitting |  |  | Material Failure |  | 1980-10-20 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | Install new 3/4" insolated service valve, due to leakage.
| 82-10263 |  |  | 0.14 | Other |  | Valves |  |  | Construction Defect |  | 1982-03-04 | 1983-04-14 | Other |  | Wrought Iron |  | OAK; S | 301 ON 1/4" METRIC GAUGE VAL. PLUG REMOVE PLUG & TIGHTEN PLUG. VAL. -# E-70 VFC
26 | 74-55071 |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-03-08 | 1974-03-10 | Patch Welded |  | Steel/Wrought Iron
| 77-20036-1 |  |  | 0.34 | Other |  | Fitting |  |  | Other |  | 1977-02-07 | 1977-07-13 | Other |  | Steel/Wrought Iron |  | Oakland | Loosened, doped and retightened 3/4" muller valve in casing. Stopped leakage.
| 76-55148 |  |  |  | Other |  | Meter |  |  | Other |  | 1976-10-08 | 1976-10-15 | Other | Replaced Meter | Steel/Wrought Iron |  | Oakland
|  |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-05-28 | 1974-05-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  |  |  | 0.03 | Distribution Feeder Main | [6 empty] | 1972-06-27 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Oakland
|  |  |  | 16 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1982-11-04 | Other |  | Steel/Wrought Iron |  |  | Installed 9 ft. riser D.B. installed reg in box, installed 9 mm
26 | 82-00059- |  |  | 1.25 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1982-01-27 | 1982-01-27 | Clamp |  | Steel/Wrought Iron |  | Oakland | Install 3/4 skinner clamp 450' E/O coi tee.
|  |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  |  | 1972-10-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Oakland
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1973-12-06 | 1973-12-06 | Replace Pipe and/or Service |  | Other Plastic |  | Oakland
| 80-20276 |  |  | 0.75 | Service |  | Fitting |  |  | Material Failure |  | 1980-03-21 | 1980-04-21 | Other | Tighten up nut on 3/4" service valve. | Steel/Wrought Iron |  | Oakland | Found leak on 3/4" service valve. Tightened up not on back of 3/4" service valve.
26 | 73-55088 |  |  | 0.5 | Service |  | Other Welds |  |  | Construction Defect |  | 1973-02-14 | 1973-02-15 | Replace Pipe and/or Service |  | Copper |  |  | Solder joint on 1/2 copper was separated 1 inch. Made repairs by replacing copper with (2) ft. of 1/2 plastic.
|  |  |  | 3 | Service |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron
|  |  |  | 4 | Other |  | Other |  |  | Other |  | 1973-07-23 | 1973-07-23 | Other |  | Steel/Wrought Iron
|  |  |  | 3 | Other |  | Other |  |  | Other |  | 1973-12-20 | 1973-12-20 | Other |  | Steel/Wrought Iron |  | OAKLAND | Tie in stl top H
| 71- | [16 empty] | Oakland | INSTALLED ELECTROLYSIS TEST STATION. BELL ALL CLEAR.
| 72-05097-1 |  |  | 2 | Transmission |  | Fitting |  |  | Material Failure |  |  | 1972-11-17 | Other | C/O Main | Steel/Wrought Iron |  | Oakland | C/O MAIN; FOUND 3/4 PLUG AT END OF TP MAIN TO BE LEAKING. RECEIVED W04414-H-1224-9000.
|  |  |  | 3 | Transmission |  | Other |  |  | Other |  |  | 1975-01-23 |  | ALTERED SERV. | Steel/Wrought Iron |  | Oakland | N/END OF WAKE AVE. ALTERED SERVICE; ALTERED SERV TO E.B. WATER... CENTER A/C CONSTRUCTION.
2 | 87-11635-C |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1987-11-21 | 1987-11-21 | Other |  | Steel/Wrought Iron |  | Oakland | CURB BOX (VALVE). GREASED T.P. PRESSURE INLET VALVE.
|  | 105C |  | 24 | [13 empty] | Oakland | C/O 2" TP MAIN AND REG PIT.
| 71- | [10 empty] | 1971-10-05 | [5 empty] | Oakland
1 |  |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Material Failure |  | 1977-03-02 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Oakland | 4" PIPE UPRATED BY MIKE SILVA 2-4-77.
| 71- | [10 empty] | 1971-10-18 | [5 empty] | Oakland | INSTALLED ELECTROLYSIS TEST STATION. WATER MAIN AND C/O T.P. LINE.
|  |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-10-17 | 1974-10-17 |  |  | Steel/Wrought Iron |  | Oakland | 7901 SUNKIST ST; (LEAK IN BP AT SERVICE, SERVICE REPLACED)
|  |  |  | 0.02 | Distribution Feeder Main | [6 empty] | 1972-06-28 |  |  |  | Steel/Wrought Iron |  | Oakland
26 | 73-48165- |  |  | 16 | Other |  | Other |  |  | Other |  | 1972-08-14 | 1972-08-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Oakland | CEMENTED OPEN ENDS OF OLD 16" ABANDONED MAIN.
26 | 72-45070-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-03-30 | 1972-04-07 | Clamp |  | Steel/Wrought Iron |  | Oakland | LEAKAGE IN THIS AREA ON POLE SIDE OF MAIN. BADLY PITTED TO CLOSE TO POLE TO WELD. PERMANENT REPAIRS MADE WITH CLAMPS AND POLYSKIN TAPE.
|  |  |  | 20 | Transmission | [6 empty] | 1976-09-23 | [5 empty] | Oakland | DUG UP VALVE FRAME AND COVER TO CHECK GREASE FITTINGS ON 20" VALVE. DUG UP VALVES X-61 AND X-L2 IN ORDER TO GET TO GREASE FITTINGS TO GREASE VALVES ON LINE 105. 2-MAN 6 HRS 9-29-76.
26 | 92-11392-1 |  |  | 20 | Transmission |  | Valves |  |  | Other |  | 1992-04-01 | 1993-06-09 | Other | Greased valve | Steel/Wrought Iron |  | Oakland | GREASED VALVE.
26 | 91-21566-1 |  |  | 6 | Transmission |  | Valves |  |  | Material Failure |  |  | 1992-09-02 | Other |  | Steel/Wrought Iron |  | Oakland | ON BLOW OFF VALVE IN PIT. GREASED VALVE.
1 | 89-64003-1 | 105B |  | 6 | Transmission |  | Valves |  |  | Atmospheric Corrosion |  | 1985-10-23 | 1991-01-22 | Other |  | Steel/Wrought Iron |  | Oakland | GREASED VALVE; VALVE IN VAULT.
| 75-21496-1 |  |  | 0.34 |  |  | Fitting |  |  | Corrosion |  | 1975-10-05 | 1976-05-06 | Other |  | Steel/Wrought Iron |  | Oakland | 2520 WEST ST, X-SYCAMORE ST. 109% AT CURB METER BOX; REPLACED 3/4" NIPPLE ON HOUSELINE UNDERGROUND NEXT TO BUILDING (PITTED OUT). REMOVED RISER/ A METER. AND SETUP, WRAPPED HOUSELINE UNDERGROUND. DUG 2'X1'X1' DEEP HOLE IN SIDEWALK TO MAKE REPAIRS ON HOUSELINE.
| 73-48175- |  |  | 2 | Distribution Main |  | Fitting |  |  | Corrosion |  | 1973-02-07 | 1973-02-22 | Other |  | Steel/Wrought Iron |  | Oakland | LEAKING CAP AND PUNCH HOLE IN 2" PIPE THAT IS NOTED AS DEAD ON PLAT SHEET. CUT AND THREADED AT POINT A AND INSTALLED NEW CAP.
|  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  | 1973-12-31 | 1973-12-31 |  |  | Steel/Wrought Iron |  | Oakland
|  |  |  | 0.03 | Distribution Main |  | Other |  |  | Other |  | 1975-03-04 |  |  |  | Steel/Wrought Iron |  | Oakland
| 73-21226- |  |  |  | Other |  | Other |  | CURB METER | Other |  |  | 1973-10-15 | Other | REPLACE VALVE |  |  |  | IA CURB METER. LEAKING AT DIAL
1 | 72-45170-A |  |  | 05LP | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-07-10 | 1972-07-10 |  |  | Steel/Wrought Iron | RUST |  | MADE PERMANENT REPAIR WITH ...
| 72-48373- |  |  | 2 | Distribution Main |  | Tap Connection |  |  | Corrosion |  | 1972-10-19 | 1972-10-19 | Other |  | Steel/Wrought Iron |  |  | USED GRAY, DUCT SEAL, FRICTION TAPE TO MAKE TEMP REPAIRS.
26 | 76-48806- |  |  | 1.75 | Service |  | Fitting |  |  | Material Failure |  | 1976-07-14 | 1976-07-20 | Other |  | Steel/Wrought Iron |  |  | TIGHTENED CONTROL NUT ON MAIN VALVE TO STOP LEAK
| 0-- |  |  | 3 | Distribution Main |  | Other |  |  | Other |  |  | 1976-03-19 | Other | CUT OFF | Steel/Wrought Iron |  | OAKLAND | EXPOSED AIC OF C/O 2" SERVICE
| 73-48160 |  |  | 2 | Other | HOUSELINE |  |  |  | Corrosion |  | 1973-02-05 | 1973-02-05 | Other | GREY TAPE NOTIFIED COST TO REPAIR LINE 2-5-72 | Steel/Wrought Iron |  |  | 301 AT THREADS OF NIPPLE. 6" FROM METER BOX. NOTIFIED COST OF THIS LEAKING AND ... FIXING IT. I GREY TAPED THREADED HOUSELINE TO MAKE SAFE.
26 | 72-21165- |  |  | 2 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1972-08-16 |  | Other |  | Steel/Wrought Iron |  |  | FOUND NO CURB VALVE AT B256 OR 58...
26 | 72-45189-1 |  |  | 3 | Other | N | [5 empty] | 1972-07-31 | 1972-10-27 |  |  | Cast Iron |  | OAKLAND
26 | 75-48437-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  |  | 1975-06-17 | Clamp |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 2 | Distribution Feeder Main | [6 empty] | 1973-02-28 | 1973-03-02 |  |  | Steel/Wrought Iron
|  |  |  | 2 | Distribution Feeder Main | [6 empty] | 1973-02-28 | 1973-03-02 |  |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 3 | Distribution Feeder Main |  | Other |  |  | Other |  | 1974-01-07 | 1974-01-07 |  |  | Steel/Wrought Iron
26 | 71-30149-1 |  |  | 0.34 | Other |  | Physical/Mechanical Joint |  |  | Material Failure |  |  | 1973-11-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | FOUND LEAK ON NIPPLE + UNION. REDOPED + TIGHTENED NIPPLE + UNION IN METER BOX.
|  |  |  | 20 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1977-01-18 | Other |  | Steel/Wrought Iron
|  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  | 1974-01-07 | 1974-01-07 |  |  | Steel/Wrought Iron |  | OAK
1 | 72-48232-A |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-08-28 | 1972-09-01 | Other |  | Steel/Wrought Iron
1 | 80-48336-F |  |  | 0.12 | Service |  | Physical/Mechanical Joint |  |  | Other |  | 1980-05-13 | 1980-06-24 | Other |  | Copper |  |  | TIGHTENED CAP ON SERVICE TEE
1 | 72--A |  |  | 025P | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-10-05 | 1972-10-05 | Patch Welded |  | Steel/Wrought Iron
26 | 79-48533- |  |  | 1.25 | Service |  | Valves |  |  | Material Failure |  | 1979-06-22 | 1979-06-22 | Other |  | Steel/Wrought Iron |  | Oakland | MADE REPAIRS ON VALVE, NUT WAS LEAKING.
|  |  |  | 0.03 | Distribution Feeder Main | [6 empty] | 1972-07-07 |  |  |  | Steel/Wrought Iron |  | Oakland
|  |  |  | 0.03 | Distribution Feeder Main | [6 empty] | 1972-07-07 |  |  |  | Steel/Wrought Iron |  | Oakland
| 82-10630- | [11 empty] | 1983-07-22 |  |  |  |  | OAKLAND | TIGHTENED FITTING IN CURB BOX TO CORRECT 30/. 49970 J 9455 & 491798 - 72.27 CURB METERS
26 | 82-10630- |  |  |  | Other |  | Other |  |  | Other |  | 1982-05-07 | 1983-07-22 | Other |  | Other |  | Oakland
| 85-20238-F |  |  | 8 | [8 empty] | 1986-06-24 |  |  |  |  | Oakland | GREASED 4" VALVE IN ...
26 | 72-00017-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-02-08 | 1972-03-23 | Other |  | Steel/Wrought Iron |  | Oakland | ARC WELDED (1) 6" X 8" PATCH OVER BLOWEN OUT PIT TO MAKE PERM REPAIRS. INST. (1) 9 LB MAGNESIUM A NODE.
|  |  |  | 20 | Transmission |  | Other |  |  | Other |  | 1981-07-08 |  | Other |  | Steel/Wrought Iron |  | Oakland | TEMPORARY 20" CAP.
|  |  |  | 20 | Transmission | [7 empty] | 1975-10-14 |  |  | Steel/Wrought Iron |  | Oakland
|  |  |  | 8 | Distribution Main |  | Other |  |  | Other |  | 1980-09-22 |  | Other |  | Steel/Wrought Iron |  | Oakland | AREA EXPOSED TO MAKE TIE IN. EXPOSED MAIN TO TIE-IN NEW 3" P/S MAIN AND C/O OLD MAIN.
|  |  |  | 8 | Distribution Main |  | Other |  |  | Other |  | 1980-09-18 |  | Other |  | Steel/Wrought Iron |  | Oakland | AREA EXPOSED TIE-IN. EXPOSED MAIN TO TIE-IN NEW 3" P/S MAIN.
|  |  |  | 1 |  |  | Other |  |  | Other |  |  | 1980-09-15 | Other | Ran new service. | Plastic |  | Oakland | HOUSE IS AS REBUILT AND NEW SERVICE WAS NEEDED.
| 74-25167-1 |  |  | 0 | Other | Meter | Meter |  |  | Material Failure |  | 1974-10-16 | 1975-04-28 | Replace Pipe and/or Service |  | Other |  |  | 1337 CURB METER, PERALTA 1A CURB. 1' FROM BUILDING. FIRE HYDRANT 1TH ST. SIDE. 2% GAS AT CURB METER BOX; FOUND 30`1 ON 1A CURB METER. REFERRED TO SERVICE DEPT. FOR METER CHANGE.
|  |  |  | 0.02 | Distribution Feeder Main | [6 empty] | 1972-05-17 |  | Other |  | Steel/Wrought Iron |  | Oakland
26 | 74-49520- |  |  | 4 | Distribution Main |  | Fitting |  |  | Material Failure |  | 1974-12-16 | 1975-01-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Oakland | INST NEW SERV. VALVE TO... 2 MEN CREW 4 HRS.
|  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron
|  |  |  | 4 | [11 empty] | Steel/Wrought Iron |  | OAK. | CUT SERVICE AT MAIN. A/C NONUSE
|  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron |  | Oakland
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1972-06-06 |  |  |  | Steel/Wrought Iron |  | Oakland
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1976-05-24 | 1976-05-24 | Other |  | Steel/Wrought Iron |  | Oakland | VAULT LOT 17' OUT H.P. MAIN INSPECTION C/O MAIN ON UNION ST. BETWEEN 18TH AND 19TH ST ON WO C/375-C
1 | 72-45111-A |  |  | 4 | Distribution Feeder Main |  |  |  |  | Corrosion |  | 1972-05-12 | 1972-05-12 |  |  | Cast/Ductile Iron |  | Oakland | C/O HOUSE LINE TO MAKE REPAIRS TO BE DONE BY CUSTOMER.
|  |  |  | 4 | Distribution Feeder Main |  | Other |  | NEW SERV. | Other | NEW SERV. |  | 1972-08-21 | Other | RAN NEW SERV. | Steel/Wrought Iron |  | Oakland | RAN NEW 1/2" SERV. BARE TO 1401 FILBERT ST. OAK.
1 | 81-40660- |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1981-10-16 | 1981-10-16 | Other |  | Steel/Wrought Iron |  | Oakland | REPAIRED 301 ON 6" VALVE #X75 NY TIGHTEN BOLTS.
1 | 81-40661- |  |  | 3 | Transmission |  | Valves |  |  | Other |  | 1981-10-16 | 1981-10-16 | Other |  | Steel/Wrought Iron |  | Oakland | 3" VALVE # X 53. 3" VALVE BY TIGHTEN BOLTS AND TURN VALVE OFF. LEAKS WHEN OFF.
| 71- | [17 empty] | INSTALLED ELECTROLYSIS TEST STATION. FOUND 3" PIPE IN THE TRENCH.
| 74--1 |  |  | 24 | Transmission | [7 empty] | 1974-04-04 |  |  | Steel/Wrought Iron |  | Oakland | FILE ONLY.
| 71- | [17 empty] | INSTALLED ELECTROLYSIS TEST STATION. 3" PIPE IN TRENCH 10' 2/O T.P.
|  |  |  | 0.04 | Distribution Feeder Main | [6 empty] | 1972-05-31 | [5 empty] | OAKLAND
| 78-49032-F |  |  | 0.75 | Service |  | Fitting |  |  | Material Failure |  | 1978-11-30 | 1978-11-30 | Other | TIGHTEN UP FITTING | Steel/Wrought Iron |  | Oakland | TIGHTEN UP 3/4" VALVE. TIGHTEN UP 3/4 SERVICE VALVE DUE TO LEAKAGE.
|  |  |  | 6 | Distribution Feeder Main | [7 empty] | 1973-03-21 | Patch Welded |  | Cast/Ductile Iron |  | Oakland
26 | 77-55039- |  |  | 3 | Service |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1977-05-17 | 1977-05-17 | Replace Pipe and/or Service |  | Other Plastic |  | Oakland | Edge of street broken off and broke 3/4" plastic ell repaired by Grove st yard.
26 | 77-55039-1 |  |  | 3 | Distribution Main |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1977-05-05 | 1977-05-18 | Replace Pipe and/or Service |  | Other Plastic |  | Oakland
77--1 | [17 empty] | Oakland
26 | 77-55040 |  |  | 3 | Distribution Main |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1977-05-18 | 1977-05-20 | Replace Pipe and/or Service |  | Other Plastic |  | Oakland | Found 60 percent leaking water box 1425, 90 percent w-b 1420, 40 percent w-b 1427, 50 percent water box 1433.
|  |  |  | 4 | Distribution Feeder Main |  | Other |  | New serv. | Other | New serv. |  | 1972-08-21 | Other | Ran new serv. | Steel/Wrought Iron |  |  | Ran new 1/2" plt. service bare.
1 | 81-40660 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1981-10-16 | 1981-10-16 | Other |  | Steel/Wrought Iron |  | OAKLAND | repaired 301 on 6" valve #x75 by tightened bolts.
1 | 71-40661- |  |  | 3 | Transmission |  | Valves |  |  | Other |  | 1981-10-16 | 1981-10-16 | Other |  | Steel/Wrought Iron |  | Oakland | 3" valve by tightened bolts and turn valve on. Leaks when off.
1 | 71- | [16 empty] | oakland | Installed Electroylsis test station; Found 3" pipe in wire trench
| 74--1 |  |  | 24 | Transmission | [7 empty] | 1974-04-04 |  |  | Steel/Wrought Iron
1 | 71- | [16 empty] | Oakland | Installed electroylsis test station; 3" pipe in trench 10' 2/0 t.p.
|  |  |  | 0.04 | Distribution Feeder Main | [6 empty] | 1972-05-31 |  |  |  | Steel/Wrought Iron |  | Oakland
| 78-49032-F |  |  | 0.75 | Service |  | Fitting |  |  | Material Failure |  | 1978-11-30 | 1978-11-30 | Other | Tightened up fitting | Steel/Wrought Iron |  | Alameda | Tightened up 3/4" service valve, due to leakage
|  |  |  | 6 | Distribution Feeder Main | [7 empty] | 1973-03-21 | Patch Welded |  | Cast/Ductile Iron |  | OAKLAND
26 | 77-55039 |  |  | 3 | Service |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1977-05-17 | 1977-05-17 | Replace Pipe and/or Service |  | Other Plastic |  | Oakland | Edge of street broken off and broke 3/4" plastic ell. Repaired by Grove yard.
26 | 77-55040 |  |  | 3 | Distribution Main |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1977-05-18 | 1977-05-20 | Replace Pipe and/or Service |  | Other Plastic |  | Oaklnad | Found 60 percent repairing water box 1425, 90 percent w-b 1420, 40 percent w-b 1427, 50 percent water box 1433
|  |  |  | 1.2 | Distribution Feeder Main | [7 empty] | 1972-01-03 | Other |  | Cast/Ductile Iron
|  |  |  | 2 |  |  | Other |  |  | Other |  |  | 1976-03-17 | Other |  | Other Plastic |  | West & E 15th st. | Plastic installed in 4" CI
26 | 0 |  |  | 6 | Distribution Main |  | Other |  |  | Other |  |  | 1976-03-19 | Other | Cut off | Cast/Ductile Iron |  | Oakland | Main not cleaned off. It appeared quite rusty.
26 | 73-48626 |  |  | 1 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1973-05-11 | 1973-05-11 | Replace Pipe and/or Service |  | Other Plastic |  | Oakland | Used two (2) 1" amp fitting to connect two ft (2) of 1" plastic service that was damage by backhoe; Replaced torn piece with new 2ft piece of plastic.
26 | 76-49010 |  |  | 1 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-09-13 | 1976-09-14 | Other |  | Other Plastic |  | Oak | Used heating irons to repair break in plastic service.
26 | 76 |  |  | 4 | Distribution Main |  | Longitudinal Weld |  |  | Material Failure |  | 1976-09-13 | 1976-09-14 | Other |  | Other Plastic |  | Oak | Installed new service tee in line with existing service.
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  |  | 1972-02-10 | Other |  | Cast/Ductile Iron
|  |  |  | 4 | Transmission |  | Other |  |  | Other |  | 1974-04-19 | 1974-04-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Oakland
|  |  |  | 0.04 | Distribution Feeder Main | [6 empty] | 1972-06-30 |  |  |  | Steel/Wrought Iron |  | Oakland
1 |  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  | 1976-07-13 | 1976-07-13 | Other |  | Steel/Wrought Iron |  |  | Exposed maint to make cut off
|  |  |  | 1.25 | Service |  | Other |  |  | Other |  |  | 1973-07-27 | Other | C/O Service | Steel/Wrought Iron
|  |  |  | 6 | Other |  | Other |  |  | Other |  | 1980-03-06 | 1980-03-06 | Other |  | Steel/Wrought Iron |  | Oakland
| 74-48625 |  |  | 0.75 | Other |  | Other |  |  | Damage by outside Forces |  |  | 1974-05-13 | Other |  | Steel/Wrought Iron |  |  | Broken meter 3/4" nipple on installed servicemen reparied houseline. replaced meters.
26 | 76-49300-1 |  |  | 0.34 | Other |  | Fitting |  | 3/4" tee | Corrosion |  | 11/15/0196 | 1976-11-15 | Other | installed 3/4" steel plug | Steel/Wrought Iron |  | Oakland | installed 3/4" steel plug.
|  |  |  | 24 | Distribution Main |  | Other |  |  | Other |  |  | 1976-12-01 | Other |  | Steel/Wrought Iron |  | Oakland | C/O service at main & left valve at meter location backfiller curb meter box
26 | 76-48349-1 |  |  | 12 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1976-04-14 | 1976-08-04 | Bell Joint Clamp |  | Cast/Ductile Iron |  | Oakland | Used 12 skinner
| 76-21139-1 |  |  |  | Other |  | Body of Pipe |  |  | Other |  | 1976-06-23 | 1976-11-29 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | 10 PERCENT AT MTR. BOX OFF BLDG.; 3 C.F.N. LEAK ON CUST. U.G. HOUSELINE. CUST. TO REPLACE LINE PER SERVICEMAN
|  |  |  | 2 | Distribution Feeder Main | [6 empty] | 1972-06-01 |  |  |  | Steel/Wrought Iron |  | OAKLAND
| 80-48808- |  |  | 0.75 | Service |  | Fitting |  |  | Material Failure |  | 1980-10-22 | 1980-10-22 | Other | TIGHTEN UP FITTING | Steel/Wrought Iron |  | OAKLAND | TIGHTEN UP SERVICE VALVE DUE TO LEAKAGE. M.A. 10-22-80
26 | 74-55514- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-01-03 | 1974-01-03 | Clamp |  | Steel/Wrought Iron |  | OAKLAND | USED SMITH- BLAIR CLAMO TO STOP LEAKAGE ON BRANCH SERVICE. 1" SMITHS BLAIR CLAMP HAD BEEN INSTALLED PREVIOSULY TURNED...PLACEMENT. ES. MOOD 1-2-73
26 | 73-49108- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-08-21 | 1973-08-22 | Clamp |  | Steel/Wrought Iron |  | OAKLAND | USED FIVE(S) SMITH-BLAIR CLAMPS TO CLOSE OFF APPROXIMATELY (13) HOLES IN 2 1/2 FT. AREA. MAIN IS VERY DEEPLY PITTED, LEAKAGE WILL BREAK LOOSE AGAIN, SHOULD BE REPLACED AS SOON AS POSSIBLE
26 | 76-49321- |  |  | 6 | Distribution Main |  | Fitting |  |  | Material Failure |  | 1976-11-18 | 1976-11-19 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | CANNED 6" INSULATED COUPLING AT FRONT OF REG. PIT.
26 | 73-49111- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-08-22 | 1973-08-22 | Clamp |  | Steel/Wrought Iron |  |  | USED LONG SKINNER CLAMP TO MAKE REPAIRS ON 3/4" SERVICE WITH (4) FOUR HOLES ON BOTTOM
26 | 75-49122- |  |  | 0 | Other |  | Other |  |  | Other |  | 1975-12-16 |  | Other |  | Other |  | OAKLAND | DUG HOLE AT ARROW NEAR SERVICE TO 4190 SERVICE PIPE NOT AT THIS LOCATION. ...ALSO ...INNERT, FOUND NO LEAKAGE AT THIS MARK CALLED FOR FLAME PAK TO RETURN.
| 74-49517- |  |  | 3 | Other |  | Other |  |  | Other |  | 1974-12-18 | 1974-12-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron
26 | 81-40632-F |  |  | 0.75 | Service |  | Fitting |  |  | Material Failure |  | 1981-09-30 | 1981-09-30 | Other | NEW VALVE | Steel/Wrought Iron |  | OAKLAND | INSTALL NEW INSULATED 3/4" SERVICE VALVE, DUE TO OLD VALVE WAS LEAKING. M.A. 9-30-81
|  |  |  | 2 | Distribution Feeder Main |  |  |  | NONE |  | NONE |  | 1972-12-07 |  |  | Steel/Wrought Iron |  |  | NO LEAKAGE; MAIN + SERVICE NOT LEAKING BUT VERY RUSTY + CORRODED. HAD TO CHANGE...STOP LEAK.
| 73-20191-M |  |  |  | Service |  |  |  |  | Other |  | 1973-01-26 | 1973-01-31 |  |  | Steel/Wrought Iron |  | OAKLAND | NO LEAKAGE FOUND;...
|  |  |  | 0.75 | Distribution Main |  | Other |  |  | Other |  | 1974-05-09 | 1974-05-09 |  | ALTER SERVICE | Steel/Wrought Iron |  |  | INSPECTION WHILE ALTERING GAS...NEW METER LOCATION.
29 | 74-48974- |  |  | 0.75 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-07-29 | 1974-07-29 | Clamp |  | Steel/Wrought Iron |  |  | INSTALL 3/4" SKINNER LEAK CLAMP ON 3/4" SERVICE . sERVVICE 44' TO MAIN FROM MAIN TO LEAK CLAMP 26'.
26 | 74-49217- |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-09-25 | 1974-09-26 | Other |  | Other Plastic |  |  | USED ONE (1) AMP FITTING TO RECONNECT BROKEN PLASTIC SERIVCE. E.S. MOODY; INSTALLEN ONE (1) AMP FITTING TO CONNECT BROKEN 1/2" PLASTIC.
26 | 74-49214- |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-09-25 | 1974-09-26 | Other |  | Other Plastic |  |  | USED ONE (1) AMP FITTING TO RECONNECT BROKEN PLASTIC SERVICE. E. S. MODDY; INSTALLED ONE (1) AMP FITTING TO CONNECT BROKED 1/2" PLASTIC
26 | 74-49233- |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-09-27 | 1974-09-30 | Other |  | Other Plastic |  |  | INSTALLED TWO (2) AMP FITTING AND 22FT. OF 1/2 PLASTIC TO REPAIR DAMAGED SECTION OF SERVICEL USED AMP FITTING TO INSTALL 28FE OF 1/2 PLASTIC.
|  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  |  | 1973-01-10 | Other |  | Steel/Wrought Iron |  | OAKLAND | SERV R/R NO LEAK
|  |  |  | 2 | Other |  | Other |  |  | Other |  | 1976-01-19 | 1976-01-20 | Other |  | Steel/Wrought Iron |  | OAKLAND | INSTALL NEW VENT FROM CASING AT MIDDLE HARBOR RD.
26 | 94-23876-1 |  |  |  | Distribution Main |  | Valves |  |  | Other |  | 1994-05-23 | 1995-08-14 | Other |  | Steel/Wrought Iron |  | OAKLAND | C-18 GREASED VALVE TO STOP LEAK, OK
26 | 93-22841-1 |  |  | 1 | Service |  | Fitting |  |  | Construction Defect |  | 1993-11-26 | 1994-04-20 | Other |  | TR 418 |  |  | REPLACED 1" ELBOWS AT SERVICE TEE A/C LEAKAGE. ; REPLACED LEAKING FITTINGS 2' FROM SERVICE (1" ELBOW)
26 | 89-21162-1 | [10 empty] | 1989-08-21 | [5 empty] | ALAMEDA
26 | 89-21163-1 | [10 empty] | 1989-08-21 | [5 empty] | ALAMEDA
1 | 90-10651-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1990-12-12 | 1990-12-12 | Patch Welded |  | Steel/Wrought Iron |  | ALAMEDA | E/S MARINER SQUARE DRIVE SOUTH, 530' S/O MARINA VILLAGE PARKING. ARC WELDED 12 X 12" PATCH OVER HOLES AND LARGE PIT; ARC WELDED PATCH OVER HOLES AND ... PITT IN 12" STEEL T.P. GAS MAIN.
26 | 87-11009-S |  |  | 2 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-01-09 | 1987-01-09 | Patch Welded |  | Steel/Wrought Iron |  | ALAMEDA | E/S MARINER SQUARE DRIVE S'OUT. 530' S/O MARINA VILLAGE PARKING. ARC WELDED 12" X12" PATCH OVER HOLES AND LARGE PIT. ; ARC WELDED PATCH OVER HOLES AND ... PIT IN 12" STEEL T.P. GAS MAIN.
1 |  |  |  | 12 | Distribution Feeder Main |  | Other |  |  | Other |  | 1976-03-05 |  |  |  | Steel/Wrought Iron
|  |  |  | 2 | Distribution Main | [7 empty] | 1978-02-28 |  |  | Steel/Wrought Iron |  | ALAMEDA | TIE IN HOLE FOR MAIN...
|  |  |  | 12 | Transmission |  | Other |  | LEAK ON SERVICE | Corrosion |  | 1972-02-17 | 1972-02-22 | Other |  | Steel/Wrought Iron |  |  | RETESTED 4-24-72 JESSON, OK.
26 | 93-22853-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1993-01-26 | 1994-04-06 | Other |  | Steel/Wrought Iron |  | ALAMEDA | VALVE PIT T-67. TIGHTEN HIGH TO HIGH SET UP OFF T.P. LINE.
26 | 93-22851-1 |  |  | 0.75 | Service |  | Physical/Mechanical Joint |  |  | External Corrosion |  | 1993-01-26 | 1994-04-19 | Replace Pipe |  | Steel/Wrought Iron |  |  | T.P. VALVE BOX. REPAIR HIGH TOO HIGH SET.; CURB BOX
| 94-40708-1 |  |  | 0.75 | Service |  | Body of Pipe | Valves | FITTING | External Corrosion |  | 1994-04-01 | 1994-04-01 | Replace Pipe | OTHER | Steel/Wrought Iron |  | ALAMEDA | REBUILT HIGH TO HIGH SET.
| 93-22852-1 |  |  | 0.5 | Transmission |  | Riser |  |  | Corrosion |  | 1993-01-28 | 1994-03-25 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ALAMEDA | VALVE BOX. REDOPED PLUG ON METRIC; RISER
| -48233- |  |  | 2 | Transmission |  | Other |  |  | Damage by outside Forces |  |  | 1974-02-15 | Other |  | Steel/Wrought Iron |  |  | C/O ...OF 2" T.P. GAS MAIN ...GRADE
|  |  |  | 12 | Distribution Feeder Main
|  |  |  | 12 | Distribution Feeder Main | [6 empty] | 1975-07-07 | 1975-07-07
|  |  |  | 2 | Transmission |  | Other |  |  | Other |  |  | 1976-03-12 | Other |  | Steel/Wrought Iron |  |  | AT THE END OF ... ON POSSY LOOP ON E/SIDE OF ....
|  |  |  | 2 | Transmission |  | Other |  |  | Other |  |  | 1976-03-12 | Other |  | Steel/Wrought Iron |  |  | AT END OF W...ON POSSY LOOP..E/SIDE...
| 94-12559-1 |  |  | 0.75 | Service |  | Fitting |  |  | External Corrosion |  | 1994-03-11 | 1994-03-11 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ALAMEDA | ...PLUG IN CURB BOX. REDOPED AND TIGHTENED PLUG IM HIGHT TO HIGH SET- OTHER 30... ON FITTING UNABLE TO REPAIR NEED M.C. MECHANICS ON ...AREA REPAIR PERMANENT.
26 | 72-40062-1 | [10 empty] | 1972-03-07 | [6 empty] | SOAP TESTED...
26 | 93-22850-1 |  |  | 8 | Transmission |  | Fitting |  |  | Other |  | 1993-01-29 | 1994-03-17 | Other |  | Steel/Wrought Iron |  | OAKLAND | MAIN HOLE FOR R-99. METRIC VALVE LOOSE ON T.P. LINE- RE-DOPED VALVE AND PLUG...OK
| 04-14093- | 105 |  | 2 | Transmission |  | Body of Pipe |  |  | Digin |  | 2004-03-31 | 2004-03-31 | Replace TP Main |  | Steel/Wrought Iron |  | ALAMEDA | CUT OUT BAD PIPE REPLACE W/NEW PRETESTED PIPE.; DRILLING RIG BORED THROUGH PIPE. CUT OUT AND REPLACED.
| 91-11191-1 |  |  | 0.75 | Service |  | Fitting |  |  | Construction Defect |  | 1991-12-13 | 1991-12-05 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ALAMEDA | IN HIGH TO HIGH SET. TIGHTENED FITTINGS AMP GREASED VALVE.
| 01-55000-1 | DFM |  | 8 | Transmission |  | Valves |  |  | Other | GASKET | 2001-02-02 | 2001-02-03 | Other | REPLACE; | Steel/Wrought Iron |  | OAKLAND | REPLACED VALVE X-33 8" GASKET AND REMOVED VALVES, INSTALLED NEW FITTINGS AND SPOOL
|  |  |  | 2 | [8 empty] | 1990-08-02 |  |  | Steel/Wrought Iron |  | OAKLAND | REMOVE VALVE D-50 FROM SERVICE & C/O 2" T.P. MAIN THAT FEED REG. STATION AND CANNED TEE.
26 | 93-22849-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1993-02-28 | 1994-03-16 | Other |  | Steel/Wrought Iron |  | OAKLAND | OUTSIDE V/B ON T.P. LINE. TIGHTENED VALVE & PLUG.
|  |  |  | 12 | Distribution Feeder Main |  | Other |  | N/S | Other | N/S; | 1976-08-24 | 1976-09-16 | Other | N/S | Steel/Wrought Iron |  |  | NO LEAK # REQUIRED; INSTALLED 3/4 TP SERV. MAIN AT THIS LOCATION IN EXCELLENT CONDITION.
26 | 80- |  |  | 2 | Transmission |  | Valves |  |  | Material Failure |  | 1980-11-06 | 1980-12-26 | Other | GREASED | Steel/Wrought Iron
| 75-50078- |  |  | 12 | Transmission |  | Fitting |  |  | Corrosion |  | 1975-08-15 | 1975-08-15 | Other |  | Steel/Wrought Iron |  | OAKLAND | CUT OFF BLOWOFF (3/4" STEEL LINE) AT 12" T.P. STEEL GAS MAIN. 2'OUT P.L...WELDED...; CUT OFF 3/4" BLOW OFF AT MAIN. WELEDED CAN...
26 | 71-00444-1 |  |  | 4 | Distribution Main |  | Bell Joint |  |  | Corrosion |  | 1972-03-01 | 1972-03-07 | Bell Joint Clamp |  | Cast Iron
26 | 88-10530-1 |  |  | 2 | Distribution Feeder Main |  | Girth Weld |  |  | Other |  | 1988-02-03 | 1989-01-17 | Replace Pipe |  | Steel/Wrought Iron |  | OAKLAND | 187' N/O END OF STREET. CUT OUT OLD WELD AND REPLACED WITH 4' OF NEW 2" MAIN.
26 | 88-10535-1 |  |  | 2 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1988-02-17 | 1989-01-17 | Replace Pipe |  | Steel |  | OAKLAND | 186' N/O END OF STREET. CUT OUT PCF & INSTALLED 4' OF NEW 2" MAIN.
[5 empty] | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ... T.P. 245285. NO ROOM FOR CURB VALVE. INST. 175" OF 1" PL. PIPE.
1 | 94-12915-1 |  |  | 8 | Distribution Main |  | Valves |  |  | Internal Corrosion |  | 1994-07-25 | 1994-07-25 | Other |  | Steel/Wrought Iron |  | OAKLAND | ZONE VALVE F-36. GREASED VALVE
[13 empty] | 1990-07-24 |  |  |  |  | OAKLAND | C/O 2" TP MAIN AND CAN TEE.
| 72-20223- |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  |  | 1972-10-25 | Patch Welded |  | Steel/Wrought Iron |  |  | PATCH WELDED HERE, ALSO 1-9 16 MAG ANODE.
|  |  |  | 2 | Distribution Feeder Main | [6 empty] | 1972-07-17 |  |  |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 2 | Distribution Feeder Main | [6 empty] | 1972-07-14 |  |  |  | Steel/Wrought Iron |  | OAKLAND
| 01-15187-1 | [10 empty] | 2001-06-28 | [5 empty] | OAKLAND | MAIN; DRIVEWAY; DRIVEWAY; IN STREET, NO GAS IN SIDEWALK AND SEWER.
|  |  |  | 4 | Distribution Feeder Main | [7 empty] | 1975-02-25 |  |  |  |  | OAKLAND
FOUND 2" STREET ...LEAKING ON OLD STUBED OFF...LINE.
26 | 75- -1 |  |  | 2 | Transmission |  | Other |  |  | Other | RE-WRAPPED MAIN | 1975-07-28 | 1975-07-28 | Other | RE-WRAPPED MAIN | Steel/Wrought Iron |  | OAKLAND | 8TH AVE. & EMBARCADERO. NO LEAK NUMBER NEEDED, MAIN INSPECTED.; RE-WRAPPED MAIN PER CONTRACTOR (3/4 MAN HOUR)
26 |  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | INSTALLED 3/4" SERVICE
1 | 71- | [16 empty] | OAKLAND | CUT SERVICE OFF AT THIS LOCATION DUE TO NON USE.
1 | 71-00319- |  |  | 4 | Other |  | Other |  | P | Corrosion |  | 01/22/0000 | 1971-02-16 | Patch Welded |  | Steel/Wrought Iron |  | OAKLAND | INST. 5-PATCHES AND 1-8" X30" CAN
1 |  |  |  | 4 | Transmission |  | Other |  |  | Other |  | 1976-09-14 |  |  |  | Steel/Wrought Iron |  | OAKALND
26 | 93-23084-1 |  |  | 4 | Transmission |  | Valves |  |  | Corrosion |  | 1993-06-07 | 1994-06-15 | Other |  | Steel/Wrought Iron |  | OAKLAND | VFC- VALVE NO C-18 REPLACED GREASED BUTTON HEAD
| 87-10287-C |  |  | 8 | Transmission |  | Valves |  |  | Other |  | 1987-09-22 | 1987-09-22 | Tighten Cap or Bolt |  | Steel |  | OAKLAND | GREASE VALVE ... LEAK =10-20-87 DUG UP VALVE AND TIGHEN NUTS TO STOP LEAK PROJECT.
|  |  |  | 4 | Transmission |  | Body of Pipe |  |  | Other |  | 1974-02-14 | 1974-02-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 4 | Distribution Feeder Main |  | Other |  |  | Other |  | 1975-01-29 | 1975-01-29 |  |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-08-17 | 1976-08-17 | Patch Welded |  | Steel/Wrought Iron |  | OAKLAND | WELDED 11 PATCHES ON 8" T.P. MAIN; 22 M.H.
1 | 97-14858-1 |  |  | 4 | Transmission |  | Fitting |  |  | Other |  | 1997-05-05 | 1997-05-05 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | OAKLAND | VALVE X89. REFERED TO VALVE CREW. FOUND PLUG LOOSE ON T.P. VALVE BODY ... DOWN TIGHTENED. RWB
|  |  |  | 20 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | OAKLAND | PAVING - NO SAW.; INSTALLED 30' OF 3/4" STL. SERV. WITH 2" STL. RISER.
|  |  |  | 1.14 | Transmission |  | Other |  |  | Other |  |  | 1975-05-22 | Other |  | Steel/Wrought Iron |  | OAKLAND
1 | 71- | [17 empty] | NO LEAK.
|  |  |  | 2 | Transmission |  | Other |  |  | Other |  | 1974-10-25 | 1974-10-25 | Other |  | Steel/Wrought Iron
1 |  |  |  | 4 | Transmission |  | Fitting |  |  | Corrosion |  | 1976-08-31 | 1976-08-31 |  |  | Steel/Wrought Iron |  | ;
26 | 76-48942- |  |  | 8 | Distribution Main |  | Fitting |  |  | Material Failure |  | 1976-08-26 | 1976-08-26 | Other |  | Steel/Wrought Iron |  | OAKLAND | 10%+ OVER SERVICE TEE IN STREET. (251-5TH AVE.); USED HIGH PRESSURE STOPPING... TO REMOVE INSERT PLUG TO RE-DOPE AND REPLACE.
26 | 82-10749- | [10 empty] | 1982-06-01 | 1983-08-16 |  |  |  |  | OAKLAND | PATCH WELDED 3' N/P N. TRACK W.P. R/R; INST. (1) 4" X 4" WELDED PATCH ON MAIN.
|  |  |  | 8 | Service | [7 empty] | 1981-12-17 |  |  | Steel/Wrought Iron |  | OAKLAND | USED...INST. NEW PIN OFF TEE AND CURB ...TEST AT 500LBS WITH NITRO.
26 | 97-26562-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Material Failure |  | 1997-05-05 | 1998-05-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | OAKLAND | REPAIRED T.P. VALVE
1 | 97-26559-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other |  | 1997-05-05 | 1997-05-06 | Other |  | Steel/Wrought Iron |  | OAKLAND | FOUND 301 ON 3/4" UNION AT MTR. ET. MADE PERMANENT REPAIRS BY TIGHTENING FITTING.
26 | 92-22183-1 |  |  | 0.75 | Service |  | Valves |  |  | Construction Defect |  | 1992-05-20 | 1993-06-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | OAKLAND | BELOW SVC. VALVE. REDOPED AND TIGHTENED VLAVE.
1 | 93-11799-1 |  |  | 2 | Service |  | Body of Pipe |  |  | Digin |  | 1993-01-06 | 1993-01-06 | Other |  | Steel/Wrought Iron |  | OAKLAND | RISER. CUT OFF 2" SERVICE AT MAIN. A/C CONTRACTORS GRADING AND HIT GAS LINE.
1 | 93-12335-1 |  |  | 3 | Distribution Feeder Main |  | Valves |  |  | External Corrosion |  | 1993-11-30 | 1993-12-02 | Other |  | Steel/Wrought Iron |  | OAKLAND | VFC. GREASED
26 | 71-00709-1 |  |  | 24 | Transmission | [6 empty] | 1971-04-15 |  |  |  | Steel/Wrought Iron |  |  | NO LEAKAGE 4-10-72 JOHN H. WILLIAMS.
26 | 78-48311- |  |  | 3 | Distribution Main |  | Fitting |  |  | Corrosion |  | 1978-03-23 | 1978-03-27 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | OAKLAND
[7 empty] | Other |  | NONE | Other | NONE | 1980-04-09 | 1980-04-10 | Other | CHANGED METER LOCATION |  |  | OAKLAND | ALTERED SERVICE AND METER LOCATION. W, L/ WARREN 4-10-80 MAN ... 2 PERSON 12 HRS.
|  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron
|  |  |  | 8 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron
26 | 75-1 |  |  | 1.14 | Transmission |  | Other |  |  | Other | NO LEAKAGE ON MAIN | 1975-12-15 | 1975-12-15 | Replace Pipe and/or Service | MADE OFF SET ON 1 1/4" TP MAIN | Steel/Wrought Iron |  |  | NO LEAK NUMBER MADE ALTERATION PER ANOTHER LEAK NUMBER; SOAP TESTED.; MADE OFF SET ON 1 1/4" MAIN LOWERED MAIN 12" TO MAKE ROOM FOR STROM DRAIN.; SEE ABOVE.
26 | 75-49096-1 |  |  | 0.34 | Service |  | Fitting |  |  | Damage by outside Forces | PULLED SERVICE & BROKE HIGH TO HIGH REG. SET | 1978-12-12 | 1975-12-12 | Other |  | Steel/Wrought Iron |  | OAKLAND | MADE SMALL ALTERATION ON SERVICE RISER TO MAKE ROOM FOR STORM DRAIN.
1 |  |  |  | 1.25 | Distribution Feeder Main | [6 empty] | 1976-09-23 |  |  |  | Steel/Wrought Iron |  | OAKALND
26 | 96-25608-1 |  |  | 16 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1996-04-05 | 1997-03-17 | Other |  | Steel/Wrought Iron |  | OAKLAND | MAN HOLE. GREASED 16" VALVE TO STOP LEAK IN MAN HOLE.
|  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron
| 78- |  |  | 20 | Distribution Feeder Main | [6 empty] | 1978-06-02 | 1978-06-02 |  |  | Steel/Wrought Iron |  | OAKALND | INSTALL E.T.S. ON 20" MAIN, TO VALVE FRAME
| 78- |  |  | 20 | Distribution Feeder Main | [6 empty] | 1978-06-09 | 1978-06-09 |  |  | Steel/Wrought Iron |  | OAKLAND | INSTALL E.T.S. ON 20" MAIN.
|  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1975-06-28 |  |  |  | Steel/Wrought Iron
| 76-55052- |  |  | 20 | Transmission |  | Other |  |  | Other |  |  | 1976-02-25 | Other |  | Steel/Wrought Iron |  | OAKLAND | DUG 2 BELL HOLES 6 X 7 AND 6X 8. FOUND NO LEAKAGE MAIN IS 7' TO TOP.; DUG 2 BELL HOLES FOUND NO LEAKAGE.
26 | 76-55052- | 105 |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-02-23 | 1976-03-03 | Patch Welded |  | Steel/Wrought Iron |  | OAKLAND | FOUND LEAK ON BOTTOM OF 20" TRANSMISSION MAIN LINE 105. DUG A 6' X 9' X 10' AND 6'X 15' X 10' TO FIND LEAKAGE. BAR TESTED AREA FOUND TO OTHER LEAKAGE AREA CLEAR.; INSTALLED WELD PATCH OVER LEAK.
26 | 75-48164- | 105 |  | 20 | Transmission |  | Girth Weld |  |  | Corrosion |  |  | 1975-02-24 | Patch Welded |  | Steel/Wrought Iron |  | OAKLAND | FOUND LEAK ON SEAM, ON LINE 105. INSTALLED PATCH OVER SEAM.; INSTALLED PATCH ON SEAM OF PIPE.
| -48223- |  |  | 16 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1980-03-14 | Other |  | Cast Iron |  |  | EXPOSED AREA PROOF CEMENT BLOCK. SOAP TESTED AND HAD FLAME PACK... BOTH SIDES OF BLOCK...BROKEN OVER LINE.
| 80-48011- |  |  | 16 | Distribution Feeder Main |  |  |  | NO LEAK |  | NO LEAK |  |  |  | NO LEAK | Cast Iron |  | OAKLAND | NO LEAK AT THIS LOCATION. MAIN LOOKS BAD. SHOULD BE R/R. BROKE AWAY DUCT FROM ...TO...
| 80-48221- |  |  | 16 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1980-03-07 | Bell Joint Clamp Replacement |  | Cast Iron |  | OAKLAND | REPLACED LEAK CLAMP % VERY BADLY CORRODED. CLAMP WAS NOT LEAKING.
| 80-48326- |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  |  | 1980-04-02 | Other | AVON SEAL | Cast Iron |  | OAKLAND | REPLACED LEAKING BELL JOINT. LEAK CLAMP WITH AVON SEAL
| 80-48327- |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1980-04-02 | 1980-04-02 | Other | AVON SEAL | Cast Iron |  | OAKLAND | REPLACED LEAKING BELL JOINT WITH AVON SEAL.
|  |  |  | 16 | Distribution Feeder Main |  | Other |  |  | Other |  | 1980-03-25 | 1980-03-25 | Other |  | Cast Iron |  | OAKLAND | EXPOSED LEAK PROOF CEMENT BLOCK. SOAP RESTED AND HAD FLAME PACK TEST BOTH SIDES OF BLOCK AROUND C.I. PIPE. FOUND LEAKS CEMENTED OLD... BROKEN OVER LINE
26 | 73-20991- |  |  |  | Other |  | Other |  |  | Other | [5 empty] | Other
26 | 75-55240- |  |  | 2 | Other |  | Body of Pipe |  |  | Corrosion |  | 1975-12-11 | 1975-12-12 | Clamp |  | Steel/Wrought Iron |  | OAKLAND | MADE LEAK SURVEY FROM... SECTION OF MAIN... NEEDS REPLACING.; OLD 2" SERVICE CUT OFF LEAKING AT STUB (CORRODED). INST. CLAMP AND ...TAPED SEVERAL FITTINGS ON MAIN STEEL...CAAST IRON BELL JOINT LEAK CLAMP LEAKING UNABLE TO STOP ALL LEAKAGES.
| 79-20608- |  |  | 16 | Distribution Feeder Main |  | Other |  |  | Other |  | 1979-10-10 | 1980-01-29 | Clamp | AVON SEAL BELL | Cast Iron |  | OAKLAND | REMOVE OLD LEAK CLAMP AND AVON SEAL BELL
| -48171- |  |  | 16 | Distribution Feeder Main |  | Other |  | SERV TEE LEAKING | Corrosion |  |  | 1980-02-01 | Replace Pipe and/or Service | REPLACE SERV. TEE | Cast Iron |  | OAKLAND | REMOVE LEAKING SERV. TEE AND INST. 16" X 14" SEAV.. SADDLE AND 1 1/2" SERV TEE AND 1' OF '" PL. P.P. PE
| 80-48012- |  |  | 16 | Distribution Feeder Main |  |  |  | NO LEAK |  | NO LEAK |  | 1980-01-04 |  | NO LEAK | Cast Iron |  | OAKLAND | EXPOSED LEAK PROOF CEMENT BLOCK. SOAP TESTED AND HAD FLAME PACK TEST...SIDES OF BLOCK AROUND C.I. PIPE FOUND NO LEAKS. CEMENT OLD...
| 80-48013- |  |  | 16 | Distribution Feeder Main |  |  |  | NO LEAK |  | NO LEAK |  | 1980-01-04 |  | NO LEAK | Cast Iron |  | OAKLAND | NO LEAK FOUND AT THE LOCATION. BROKE OLD P.T. & T. DUCT LINE FROM BANK TO BANK AND CEMENTED ALL DUCT.
26 | 74-00746- |  |  | 2 | Other |  | Regulator |  |  | Material Failure |  | 1974-02-28 | 1974-10-30 |  |  | Steel/Wrought Iron |  |  | 2" LINE FILTER LEAKING AT RINGS. ...
26 | 79-55024-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1979-03-28 | 1979-03-28 | Other |  | Steel/Wrought Iron |  | OAKALND | MADE TEMPORARY REPAIRS WITH GRAY TAPE & DUCT SEAL. MAIN IN BAD CONDITION SHOULD BE REPLACED.
26 | 79-55024-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1979-03-25 | 1979-03-25 | Other |  | Steel/Wrought Iron |  |  | ...GAS MAIN...AREA IN...CLAMP. HAD TO ...SEAL.
26 | 74-55025- |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-01-22 | 1974-01-24 | Clamp |  | Steel/Wrought Iron |  |  | BAD MAIN. DUCT SEAL AND TAPE; THIS SHOULD BE REPLACED...REPAIRS TO ...LEAK...
1 |  |  |  | 1 | Distribution Feeder Main |  | Other |  |  | Other | [5 empty] | Steel/Wrought Iron
|  |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other | [5 empty] | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other | [5 empty] | Steel/Wrought Iron
1 |  |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other | [5 empty] | Steel/Wrought Iron
|  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel |  | OAKLAND
1 |  |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other | [5 empty] | Steel/Wrought Iron
| 81-40287-F |  |  | 1.25 | Service |  | Fitting |  |  | Material Failure |  | 1981-04-21 | 1981-04-21 | Replace Pipe and/or Service | NEW VALVE | Steel/Wrought Iron |  | OAKLAND | INSTALL NEW 3/4" INSULATED SERVICE VALVE, DUE TO LEAKAGE 4-21-81 M.A.
1 |  |  |  | 6 | Distribution Feeder Main |  | Other | [8 empty] | Steel/Wrought Iron
1 |  |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other | [5 empty] | Steel/Wrought Iron
| -20782- |  |  | 6 | Distribution Main |  | Other |  |  | Other |  | 1973-07-16 | 1973-07-18 | Other |  | Steel/Wrought Iron |  | OAKLAND | DRY HOLE. P.O. CLEANED WRAP NEAR SEWER BUT MAIN OK P.O.D.
|  |  |  | 3 | Transmission |  | Other |  |  | Other |  |  | 1996-09-25 | Replace Pipe |  | Steel/Wrought Iron |  |  | INSTAL (1) 3" KEROTEST, (2) 3" LINE STOPPERS, (2) 3/4" SAVER NIPPLES, (1) VALVE FRAME & COVER ETS.
|  |  |  | 3 | Distribution Feeder Main | [6 empty] | 1973-03-25 | 1973-03-27 |  |  | Steel/Wrought Iron |  | OAKLAND
1 | 72-40142-A |  |  | 3.5 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-05-03 | 1972-05-03 |  |  | Steel/Wrought Iron |  |  | INSTALL 3"...
| 73-48653- |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-05-17 | 1973-05-22 | Clamp |  | Steel/Wrought Iron |  |  | REPAIRED LEAK (C) ON 3" STP. MAIN 1/4" DIAMETER. LEAK WAS 2" BELOW 1" COPPER WATER SERVICE (A) AND 3" BELOW TWO (2) 3" DRAINS (B). PERMENANT REPAIRS MADE WITH SKINNER CLAMP.
| 80- |  |  | 1.25 | Service |  | Other |  |  | Other |  | 1980-04-22 | 1980-04-22 | Other | CUT OFF RISER | Steel/Wrought Iron |  | OAKLAND | CUT OFF OLD 1 1/4" RISER FROM UNDER HOUSE- APPROX 50' OF GAS LINE. PER CUSTOMER REPORT 4-22-80 M.A.
26 | 73-20809- |  |  | 1.25 | Service |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1973-07-18 | 1973-07-20 | Other |  | Steel/Wrought Iron |  |  | 1 1/4" GATE TYPE CURB VALVE LEAKING AT POINT (A). REPAIRED BY TIGHTENING THIS NUT. NEW FRAME AND COVER INSTALLED.
|  |  |  | 12 | Distribution Feeder Main | [8 empty] | Other |  | Steel
|  |  |  | 1.25 |  |  | Other |  |  | Other |  |  | 1974-01-16 | Other |  | Other Plastic |  | OAKLAND | ... NO LEAKAGE
|  |  |  | 6 | Distribution Feeder Main | [10 empty] | Cast Iron |  | OAKALND | MAIN DUG UP ON A/C OF INSTPECTING C.I. MAIN GRAPHITIGATION.
26 | 72-40079-1 |  |  | 3 | Distribution Main |  | Tap Connection |  |  | Corrosion |  | 1972-03-24 | 1972-03-27 | Other |  | Steel/Wrought Iron |  |  | DUE TO POOR CONDITION OF SERV. TEE AT POINT NO. 1 SERV. TEE WAS CUT OFF AT TOP HALF AND REPLACED WITH 1 1/8STACK SERVICE WAS RE-RAN BEFORE REPAIRS WERE MADE ON OLD TEE.
26 | 74-20982- |  |  | 0 | Other |  | Other |  |  | Other |  | 1975-11-05 | 1975-12-01 | Other |  | Other |  |  | FOUND NO LEAKAGE AT THIS ADDRESS.... AND SOAP TESTED. CUSTOMER CLAIMS SERVICE MAIN HAD...WITHIN THE LAST MONTH TO ... AN APPLAINCE AND HAD ASKED HER IF SHE SMELLED LEAK...THIS SERVICE MAN FIXED THE LEAK IN... 12-1-75; SOAP TESTED RISER AND RELATED FITTINS ON ...
26 | 75-50144- |  |  | 1.25 | Other |  | Meter |  |  | Construction Defect |  | 1975-11-04 | 1975-12-02 | Other |  | Cast Iron |  | ALAMEDA | FOUND LEAK IN 1A CURB METER GLASS REPAIRED BY USING METER GLASS SEALANT.; FOUND LEAK ON 1A CURB METER GLASS REPAIRED BY USSING METER GLASS SEALANT. HAD TO RETURN TO YARD TO PICK UP SEALANT 3 MIN 3 HRS EA.
| 74-23439- |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1974-10-22 | 1974-10-22 |  |  | Steel/Wrought Iron |  | ALAMEDA | LEAK IN BP OF SERVICE. SERVICE REPLACED.
| 73-48068-1 |  |  | 0.34 | Service |  | Other |  |  | Other |  |  | 1973-01-02 | Other |  | Steel/Wrought Iron |  | ALAMEDA | DRY HOLE.
26 | 74-48345-1 |  |  | 0.75 | Other | BLOW OUT | Valves |  |  | Other | TIGHTENED PLUG | 1974-03-13 | 1974-03-13 | Other |  | Steel/Wrought Iron |  | ALAMEDA | 3/4"...CONCRETE VALVE..; INSTALLED 3/4" SCREWED PLUG INTO VALVE...REPAIR LEAKAGE.
|  |  |  | 3 | Distribution Feeder Main | [6 empty] | 1972-06-12 | 1972-06-12 | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  |  |  | 3 | Distribution Feeder Main | [6 empty] | 1972-06-12 | 1972-06-12 | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  |  |  | 30 | Transmission |  | Other |  |  | Other |  | 1981-07-15 | 1981-07-15 | Other |  | Steel/Wrought Iron |  | OAKALND
|  |  |  | 30 | Transmission | [7 empty] | 1972-01-27 |  |  | Steel/Wrought Iron |  | OAKLAND | VALVE FRAME AND TEST LEADS OVER MAIN IN DIRT AREA NEXT TO STATE FENCE LINE.; EXPOSED 30" T.P. LINE TO INST. ETS WIRES CAD WELDED ON MAIN.
| 97-14692-1 |  |  | 4 | Transmission |  | Valves |  |  | Material Failure |  | 1997-02-19 | 1997-02-19 | Other |  | Steel/Wrought Iron |  | OAKLAND | GREASED VALVE D-96
|  |  |  | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLAND | INSTALLED WIRES ON EACH SIDE OF ...2" FLANGED VALVE- EXTENDED CASING UP TO STREET LEVEL. DRAWING ON BACK. SHOWS CORRECT SERVICE DATING LOCATION 4-12-77
26 | 75-48270- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1975-04-03 | 1975-04-07 | Clamp |  | Steel/Wrought Iron |  |  | ABOVE
|  |  |  | 2 | Distribution Feeder Main | [6 empty] | 1972-05-19 |  |  |  | Steel/Wrought Iron |  | OAKALND
1 | 73-49138-A |  |  | 0.75 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-08-30 | 1973-08-31 | Replace Pipe and/or Service |  | Steel/Wrought Iron
26 | 93-23042-1 | [10 empty] | 1993-04-12 | [5 empty] | OAKLAND
26 | 94-23747-1 | [10 empty] | 1994-04-04 | [5 empty] | OAKLAND
26 |  |  |  | 30 | Transmission | [6 empty] | 1972-01-25 |  |  |  | Steel/Wrought Iron |  | OAKLAND
1 | 81-10224- |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1981-06-17 | 1981-08-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 3 | Other | [6 empty] | 1972-09-27 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND
26 | 75-48671- |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1975-08-13 | 1975-08-14 | Clamp |  | Steel/Wrought Iron
|  |  |  | 28 | Transmission | [7 empty] | 1979-10-02 |  |  | Steel/Wrought Iron
|  |  |  | 26 | Transmission | [7 empty] | 1979-12-20 |  |  | Steel/Wrought Iron |  | OAKLAND | INSP. MADE DURING SERV. % INSP. CONSISTING OF AREA DIRECTLY AROUND SERV. TEE.
26 | 96-26000-1 |  |  | 3 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1996-08-09 | 1997-08-04 | Other | GREASED VALVE TO STOP LEAK. OK! RWB | Steel/Wrought Iron |  | OAKLAND
26 | 89-21230-1 |  |  | 24 | Transmission |  | Valves |  |  | Other |  | 1989-10-12 | 1990-12-13 | Deactivate #TP Main |  | Steel/Wrought Iron |  | OAKLAND | GREASED VALVES IN PINHOLE
26 | 89-21230-1 |  |  | 24 | Transmission |  | Valves |  |  | Other |  | 1989-10-12 | 1990-12-13 | Other | GREASED VALVES IN MAN HOLE. | Steel/Wrought Iron |  | OAKLAND
26 | 88-20142-1 |  |  |  | Transmission |  | Valves |  |  | Material Failure |  | 1988-05-26 | 08/15/0000 | Other |  | Steel/Wrought Iron | UNABLE TO MAKE REPAIRS ON VALVE IN VAULT. DUX SEALED. VALVE TO BE REPLACED. | OAKLAND
1 | 93-12128-1 |  |  | 0.3 | Transmission |  | Valves |  |  | Other |  | 1993-07-19 | 1993-07-20 | Tighten Cap or Bolt | TIGHTEN BOLT ON FLANGE | Steel/Wrought Iron |  | OAKLAND
26 |  |  |  | 26 | Transmission | [6 empty] | 1972-01-26 |  |  |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 2 | Distribution Feeder Main | [6 empty] | 1972-06-05 |  |  |  | Other Plastic |  | OAKLAND
|  |  |  | 0.04 | Distribution Feeder Main | [6 empty] | 60/15/1972 |  |  |  | Steel/Wrought Iron |  | OAKLAND
26 |  |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  |  | 1972-08-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron
26 | 73-21760 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-09-27 | 1973-09-27 | Clamp |  | Steel/Wrought Iron
26 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1980-01-28 | 1980-01-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | INST. 1/2" PL SERVICE D.P. WRAP ON MAIN VERY POOR.
26 | 74-49545 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-12-26 | 1974-12-26 | Clamp |  | Steel/Wrought Iron
1 | 79-48485 |  |  | 1.25 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-07-23 | 1979-07-23 | Other |  | Other Plastic |  | ALAMEDA
| 94-12980-1 |  |  | 0.5 |  | FORM MARKED WITH "X" | Valves |  |  | Construction Defect |  | 1994-08-29 | 1994-08-29 | Other |  | Aldyl A (Tan or Gray) |  | ALAMEDA | REPAIRED SERVICE VALVE
| 94-23923-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1994-06-01 | 1996-01-27 | Other |  | Steel/Wrought Iron |  | OAKLAND
1 | 95-13460-1 |  |  | 0.25 | Service |  | Valves |  |  | Corrosion |  | 1995-06-06 | 1995-06-06 | Tighten Cap or Bolt |  | Cast/Ductile Iron |  | OAKLAND | REMOVED 3/4" SQUEAK PLUG FROM BYPASS VALVE RECTOR SEAL + RETRIEVED TO VALVE & TIGHTEN OK AT THIS TIME.
| 93-23086-1 |  |  | 0.75 | Service |  | Regulator |  |  | Material Failure |  | 1993-06-07 | 1994-06-14 | Replace Pipe |  | Steel/Wrought Iron |  | OAKLAND | REPLACED REGULATOR IN LEAKING HIGH TO HIGH BOX
| 93-23085-1 |  |  | 0.75 | Service |  | Valves |  |  | Construction Defect |  | 1993-06-07 | 1994-06-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | OAKLAND | TIGHTENED (LEAKING) NEEDLE VALVE AT THREADS
| 94-12791-1 |  |  | 0.75 | Service |  | Valves |  |  | External Corrosion |  | 1994-06-06 | 1994-06-06 | Other |  | Steel/Wrought Iron |  | OAKLAND | SHUT OFF 3/4" SERVICE; INSTALL BY-PASS AND (2) 3/4 300 PSI DROP VALVES.
| 95-13731-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Digin |  | 1995-10-31 | 1995-11-01 | Replace Pipe |  | Steel/Wrought Iron |  | OAKLAND | REPAIRED 49' OF 3/4" TP SERVICE HIT BY CONTRACTOR
|  |  |  | 30 | Transmission |  | Other |  |  | Other |  | 1982-05-11 | 1982-05-11 | Other |  | Steel/Wrought Iron |  | OAKLAND | SERVICE % HOLE. WELDED 4" CAN OVER 3/4" PIN-OFF TEE
| 89-11536-F | [11 empty] | 1989-08-04 |  |  |  |  | OAKLAND | GREASED VALVE (3 STICKS) CLEARED 30L.
| 74-48268 |  |  |  | Other |  | Valves |  |  | Other |  |  | 1974-02-27 | Other |  | Steel/Wrought Iron
26 | 73-49083 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-08-10 | 1973-08-13 | Clamp |  | Steel/Wrought Iron
| 97-26893-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1997-08-13 | 1999-01-25 | Other |  | Steel/Wrought Iron |  | OAKLAND | GREASED VALVE TO STOP LEAK
26 | 73-49129- | [5 empty] | Body of Pipe |  |  | Corrosion |  | 1973-08-28 | 2010-10-25 | Clamp |  | Steel/Wrought Iron
| 88-10829-5 |  |  | 0.75 | Gathering |  | Fitting |  |  | Other |  | 1988-07-26 | 1988-07-26 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | OAKLAND | RETIGHTENED 3/4" PLUG (LEAKING AT THREADS) ONTO 3/4 COUPLING WELDED TO 3" STL MAIN. STOPPED LEAKAGE
| 93-23166-1 |  |  | 0.75 | Service |  | Valves |  |  | Material Failure |  | 1993-06-08 | 1993-06-12 | Other | GREASED VALVE | Steel/Wrought Iron |  | OAKLAND | GREASED VALVE
| 93-23167-1 | [10 empty] | 1993-06-08 | [5 empty] | OAKLAND
| 90-21314-1 |  |  | 0.75 | Service |  | Valves |  |  | Material Failure |  | 1990-06-28 | 1991-03-18 | Other | GREASED VALVE ON HI TO HI SET | Steel/Wrought Iron |  | OAKLAND | GREASED VALVE ON HI TO HI SET.
| 90-21315-1 |  |  | 0.75 | Service |  | Valves |  |  | Material Failure |  | 1990-06-28 | 1991-03-18 | Other | GREASED VALVE | Steel/Wrought Iron |  | OAKLAND | GREASED VALVE
| 78-48467 |  |  | 1.25 | Service |  | Fitting |  |  | Corrosion |  |  | 1978-05-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | REPLACED HIGH/HIGH SET
| 96-25289-1 |  |  | 0.75 | Service |  | Valves |  |  | Construction Defect |  | 1996-01-22 | 1990-11-10 | Other | REQUIRED TP SERVICE | Steel/Wrought Iron |  | OAKLAND | REQUIRED TP SERVICE
| 96-25737-1 |  |  | 0.75 | Service |  | Valves |  |  | Material Failure |  | 1996-06-03 | 1997-06-04 | Other | GREASED 3/4" VALVE | Steel/Wrought Iron |  | OAKLAND | GREASED 3/4" VALVE
26 | 96-25291-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 1996-01-22 | 1996-11-15 | Tighten Cap or Bolt | REPLACED METRIC FITTING IN REG PIT | Steel/Wrought Iron |  | OAKLAND | REPAIRED METRIC FITTING
|  |  |  | 2 | [8 empty] | 1990-03-27 |  |  |  |  | OAKLAND | REPLACED STOPS
26 | 77-48663 |  |  | 0.34 | Service |  | Fitting |  |  | Corrosion |  | 1977-07-15 | 1977-07-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ALAMEDA
26 | 77-48663 |  |  | 0.34 | Service |  | Valves |  |  | Corrosion |  | 1977-07-15 | 1977-07-15 | Other |  | Steel/Wrought Iron |  | ALAMEDA | REPLACED SERVICE VALVE
|  |  |  | 3 | Distribution Feeder Main |  |  |  | N/A |  | N/A | 1978-07-11 | 1997-06-04 |  | GREASED 3/4" VALVE | Steel/Wrought Iron |  | OAKLAND | EXPOSED 3" MAIN IN ORDER TO CLEAR CORROSION CONTACT. THIS IS IN PARKING LOT IN FONT OF HANGER #. NO PAVING IS NEEDED. 7/11/78
| 96-13728-1 |  |  | 2 | Gathering |  | Other |  |  | Damage by outside Forces |  | 1995-10-24 | 1995-10-24 | Replace Pipe |  | Cast/Ductile Iron |  | OAKLAND | REPAIRED WITH 2-2" MEPFIT FITTING &1-2" PL 18" LONG
| 73-48754 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Construction Defect |  | 1973-06-05 | 1973-06-05 | Clamp |  | Steel/Wrought Iron |  |  | REPAIRED BADLY PITTED LEAK ON 3/4" RISER BELOW SER. VALVE WITH SKINNER CLAMP (TEMP)
26 | 73-49427 |  |  |  | Distribution Feeder Main |  | Other Welds |  |  | Other |  | 1973-11-13 | 1973-11-27
|  |  |  | 24 | Transmission | [7 empty] | 1972-01-28 |  |  | Steel/Wrought Iron
| 74-23200 |  |  | 2 | Other |  | Other |  |  | Other |  | 1975-01-16 | 1975-01-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1974-05-15 | 1974-05-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND
| 78-20061-1 |  |  | 0.34 | Other | [6 empty] | 1978-04-17 |  |  |  | Steel/Wrought Iron
26 | 74-48655 |  |  | 6 | Transmission |  | Other |  |  | Corrosion |  | 1974-05-17 | 1974-05-21 | Patch Welded |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1980-12-19 |  | Other |  | Steel/Wrought Iron
|  |  |  | 6 | Transmission |  | Other |  |  | Other |  | 12/00/1980 |  | Other |  | Steel/Wrought Iron
|  |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1980-12-19 |  | Other |  | Steel/Wrought Iron |  | OAKLAND
26 |  |  |  | 6 | Transmission |  | Other |  |  | Other |  |  | 1977-03-22 | Other
26 |  |  |  | 6 | Transmission |  | Other |  |  | Other |  |  | 1977-03-22 | Other |  | Steel
| 88-10538-1 |  |  |  | Transmission |  | Valves |  |  | Other |  | 1988-02-17 | 1988-03-17 | Other |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 24 | Transmission |  | Other |  |  | Other |  | 1976-11-17 | 1976-11-17 |  |  | Steel/Wrought Iron
1 |  |  |  | 24 | Transmission |  | Other |  |  | Other |  | 1976-11-17 | 1976-11-17 |  |  | Steel/Wrought Iron
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1974-05-13 | 1974-05-13 | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLAND
[5 empty] | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLAND
| 48-094- |  |  | 0.5 | Service |  | Other |  | MARKED "ST" SCRAPPER TAP | Material Failure |  |  |  | Replace Pipe and/or Service |  | Other Plastic |  | OAKLAND
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1972-08-09 | [5 empty] | OAKLAND
|  |  |  | 4 | Distribution Feeder Main |  | Other |  |  | Other |  | 1974-08-02 | 1974-08-02 | Other |  | Other Plastic |  | OAKLAND
1 | 79-48656 |  |  | 03.HD | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 2000-08-10 | 08/11/0000 |  |  | Steel/Wrought Iron |  | OAKLAND
1 | 74-48656- |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1979-08-09 | 1979-08-10 |  |  | Steel/Wrought Iron
| 78-48357 |  |  | 0.75 | Service |  | Fitting |  |  | Material Failure |  | 1978-04-14 | 1978-04-14 | Other | REPLACE 3/4" VALVE | Steel/Wrought Iron |  | OAKLAND
| 73-- |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-09-19 | 1973-09-19
26 | 73-55405 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-10-29 | 1973-10-29 | Clamp |  | Steel/Wrought Iron
| 81-10261 |  |  | 2 | Distribution Main | ALSO MARKED "G" GATHERING | Fitting |  |  | Material Failure |  | 1981-06-29 | 1981-09-03 | Clamp |  | Steel/Wrought Iron |  | OAKLAND
| 81-10261 |  |  | 0.75 | Other | DRIP POT | Body of Pipe |  |  | Corrosion |  | 1981-06-29 | 1981-09-11 | Other | CUT OFF | Steel/Wrought Iron |  | OAKLAND
26 | 73-49664 |  |  | 4 | Distribution Feeder Main |  | Other |  |  | Other |  | 1973-12-19 |  | Other |  | Steel/Wrought Iron
ILLEGIBLE | 73-49309 |  |  | 02.5P | Distribution Feeder Main |  | Other |  |  | Other |  | 73/10/2018 |  | Other |  | Steel/Wrought Iron
26 | 73-49310 |  |  | 02.5P | Distribution Feeder Main |  | Other |  |  | Other |  | 73/10/2019 |  |  |  | Steel/Wrought Iron
26 | 73-49317 |  |  | 03.5P | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-10-23 | 1973-10-23 |  |  | Steel/Wrought Iron
| 73-00170-1 |  |  |  | Other | MARKED "C" | [5 empty] | 1975-08-17
26 | 81-00126 |  |  | 0.5 |  |  | Fitting |  |  | Material Failure |  | 1981-06-18 | 1982-05-14 | Other |  | Other Plastic
|  |  |  | 2 |  |  | Body of Pipe |  |  | Corrosion |  |  | 1973-02-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND
1 | 73-00154-A |  |  | 3 |  | ILLEGIBLE CODE ENTERED | Body of Pipe |  |  | Corrosion |  | 1973-04-10 | 1973-06-14 | Patch Welded |  | Steel/Wrought Iron
26 | 74-48188 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-02-07 | 1974-02-08 | Clamp |  | Steel/Wrought Iron
26 | 73-49582- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Construction Defect |  | 1973-12-06 | 1973-12-06 |  |  | Steel/Wrought Iron
26 | 75-50155 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1975-09-27 | 1975-09-27 | Other |  | Other Plastic
26 | 73-49043 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1973-08-02 | 1973-08-02 | Clamp |  | Steel/Wrought Iron
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-11-20 | 1974-11-20 |  |  | Steel/Wrought Iron
26 | 74-49528 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Construction Defect |  | 1974-12-17 | 1974-12-17 | Other |  | Steel/Wrought Iron
26 | 73-55431-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Construction Defect |  | 1973-01-16 | 1973-11-19 | Replace Pipe and/or Service |  | Plastic
26 | 73-55444-A |  |  | 02.5P | Distribution Feeder Main |  | Body of Pipe | Fitting | FO | Corrosion | MF | 1973-11-18 | 1973-11-23 |  |  | Steel/Wrought Iron
26 | 77-49141 |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  | 1977-11-02 | 1977-11-03 | Other |  | Steel/Wrought Iron |  | OAKLAND
26 | 73-49346 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-10-22 | 1973-10-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron
1 | 73-49237-A |  |  | 0.25P | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-09-23 | 1973-10-03 | Patch Welded |  | Steel/Wrought Iron
26 | 72-48316- |  |  | 2 | Distribution Feeder Main | DISTRIBUTION | Body of Pipe |  |  | Corrosion |  | 1972-09-21 | 1972-09-22 | Clamp |  | Steel/Wrought Iron
| 72-20349-1 |  |  | 0 | Other |  | Other |  |  | Other |  |  |  | Other |  | Other |  | OAKLAND
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-05-15 | 1974-05-15 |  |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  | 1974-12-27 |  | Other |  | Steel/Wrought Iron
28 | 10-81972-1 | 105B | 0 | 6 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | Other |  | 2010-10-12 | 2011-03-08 | Fill Weld - Weld |  | Steel |  | CROCKETT | WATER. FOLLOW WATER PIPE.; GAS MECHANIC WELDED CRACK
28 | 10-81972-1 | 105B | 0 | 6 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | Other |  | 2010-10-12 | 2011-03-08 | Fill Weld - Weld |  | Steel |  | CROCKETT | WATER. FOLLOW WATER PIPE.; GAS MECHANIC WELDED CRACK
28 | 10-81126-1 | 1 |  | 1.25 | Single Service |  | Curb Valve |  |  | Other |  | 2010-10-07 | 2011-03-02 | Tighten Cap or Bolt | GREASED | Steel |  | SAN PABLO | O/M NEAR SVC T@PATCH IN S/WK. DOWN GRADED-IK IN ST 50' E/O TRACKS NO OD.; ON 1 1/4" CURB VALVE DUG UP 1 1/4 CURB VALVE/REPLACED LEAKING FLANGE AND RE-GREASED ROCKWELL VALVE. ; REPAIRED LEAKING 1 1/4 ROCKWELL CURB VALVE ON SERVICE RE-TIGHTENED FLANGE BOLTS AND GREASED.
28 | 10-81301-1 | 1 |  | 6 | Distribution Main <= 60 PSIG |  | Fitting |  | SAVA NIPPLE CAP | Other |  | 2010-10-08 | 2011-03-08 | Replace TP Main | TIGHTEN CAP/BOLT - FITTING | Steel |  | PINOLE | ON MAIN @TIE IN M2 IN AREA DISTRIBUTION; SAVA NIPPLE ON 6" MAIN CAP ON HAND TIGHT. REMOVE RE-DOPED AND RE-TIGHTENED CAP ON SAVA NIPPLE.; FOUND SAVA VALVE CAP HAND TIGHT, REMOVED, REDOPED, TIGHTENED, AND WRAPPED CAP. STARTED JOB 3-7 WK 10HRS FINISHED MSA AIR MONITOR USED FORMS ATTACHED.
26 | 10-81164-1 | 105N | 32.1 | 2 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-04 | 2011-03-07 | Patch Weld - Weld |  | Steel |  | OAKLAND | ON L/P LINE; NOT ON TP. 301 ON LP 2" MAIN.; ON MAIN AT TIE-IN 2" ON TOP 4" GAS MAIN ARC WELDED PATCH ON TEE.; HAD ARC WELDER PATCH 2" MAIN TEE OFF 4" LP MAIN.
26 | 10-81186-1 | 153 | 27.11 | [8 empty] | 2010-10-05 | [5 empty] | OAKLAND | DLE OF INTER. OFF ALICE STREET ABO. SAME/NOT TP LEAK. NO READS OVER MAIN
26 | 10-81192-1 | 153 | 26.96 | [8 empty] | 2010-10-05 | [5 empty] | OAKLAND | 7' EAST OF BLDG WALL 16' S OF N CURB INT. NOT ON TP. DRILL HOLES AND NO READING.
26 | 10-81190-1 | 153 | 20.27 | [8 empty] | 2010-10-05 | [5 empty] | OAKLAND | SAME NOT ON TP; ON SVC
26 | 10-81190-1 | 153 | 20.27 | 0.75 | Branch Service |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-05 | 2011-02-10 | Replace Entire Service |  | Steel |  | OAKLAND | SAME NOT ON TP; ON SVC; ON SERVICE R/R BRANCH SERVICE WITH 1/2" PLASTIC; R/R BRANCH SERVICE WITH 1/2" PLASTIC (INSERTED)
26 | 10-81200-1 | 153 | 26.19 | 4 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-06 | 2011-02-09 | Skinner Clamp - Clamp |  | Steel |  | OAKLAND | SAME. DISTRIBUTION MAIN; ON MAIN, CLAMP MAIN; CLAMP MAIN
26 | 10-81195-1 | 153 | 26.68 | [8 empty] | 2010-10-05 | [5 empty] | OAKLAND | SAME; REFER TO T&R ON SERVICE; NO LEAK FOUND EVIDENCE SHOW LEAK HAS BEEN REPLAIRED
26 | 10-81213-1 | 153 | 24.61 | 0.75 | Single Service |  | Fitting |  | NIPPLE IN CANS | No/Deteriorated Pipe Dope |  | 2010-10-07 | 2011-02-14 | Other |  | Steel |  | OAKLAND | SAME; ON FITTING NOT TRANSMISSION; IN CANS 3/4" NIPPLE BETWEEN REG AND VALVE WAS REPLACED.; NIPPLE REPLACED IN CMB BETWEEN REG & VALVE.
26 | 10-81188-1 | 153 | 20.22 | 0.75 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion | WELD FAILURE | 2010-10-05 | 2011-02-08 | Replace Entire Service |  | Steel |  | OAKLAND | SAME; TP BETWEEN 9330 & 9340; NOT ON TP ON SVC; D2D2 FOR READ; NOT ON TP ON SVC; ON BRANCH SERVICE. RE-RAN BRANCH SERVICE; RERAN BRANCH SERVICE AT 9340 & 9330 CORAL RD.
26 | 10-81191-1 | 153 | 27.03 | 2 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other |  | 2010-10-05 | 2011-03-03 | Greased - Other |  | Steel |  | OAKLAND | SAME; SAME/ NOT ON TP; ON VALVE 2" GREASED VALVE.; UNCOVER VFC LEAK ON GREASED FITTING ON 2" FLANGE VALVE.
26 | 10-81197-1 | 153 | 26.93 | [8 empty] | 2010-10-05 | [5 empty] | OAKLAND | 9' W OD EAST BLDG WALL/ 16' S. OF NORTH C.; SAME; LEAK REPAIRED BY LEAK #10-81191-1 202 2ND AVE.
26 | 09-90221-1 | [10 empty] | 2009-04-01 | [5 empty] | OAKLAND | VFC IN STREET; VFC IN STREET; VFC IN STREET; NO LK FOUND
| 05-80372-1 |  |  | 1.25 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2005-12-15 | 2006-03-09 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | RICHMOND | ON MAIN; INSTALLED WELD CAN OVER LEAK
| 05-80068-1 |  |  | 2 | Gathering |  | Fitting |  |  | Unknown |  | 2005-02-25 | 2005-03-10 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | RICHMOND | ON MAIN AT BOTTOM TAPL RELINE PLUG AND CAP
| 05-21004-1 |  |  | 1.25 | Service |  | Fitting |  |  | Unknown |  | 2005-01-31 | 2005-04-22 | Other | TIGHTEN FITTING | Steel/Wrought Iron |  | BERKELEY | IN CMB, TIGHTEN 1 1/4" UNION; ALL IN CMB
| 05-80085-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2005-03-08 | 2005-03-08 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | PINOLE | E/S 4TH AVE, 10' OUT, 295' S/O SAN PABLO AVE. INST. (1) 2' BOLT SKINNER LEAK CLAMP; INSTALLLED (1) 2" SKINNER LEAK CLAMP
| 08-10002-1 | 105A | 45 | 0.25 | Transmission |  | Tap Connection |  |  | Unknown |  | 2008-04-26 | 2008-08-07 | Other | REPLACED 1/4" FITTINGS AND NIPPLE TO CLEAR LEAKAGE | Steel/Wrought Iron |  | RICHMOND | ON 105A MAIN LINE VLV X-21 (MP45.;
| 08-25390-1 |  |  | 0.75 | Single Service |  | Other |  | T.P. TO H.P. REG PIT. | External Corrosion |  | 2008-08-15 | 2008-11-04 | Other | REPLACED T.P. TO H.P. REG SET | Steel/Wrought Iron |  | RICHMOND | REBUILT T.P. TO H.P. REG SET.; 301 ON PIPES IN T.P. TO H.P. REG SET. REBUILT SET TO REPAIR 301S
| 08-21020-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Unknown |  | 2008-04-23 |  |  |  | Steel/Wrought Iron |  | BERKELEY | IN CURB METER BOX; GREASED VALVE IN CMB
| 08-30080-1 |  |  | 0.75 | Transmission |  | Tap Connection |  |  | Unknown |  | 2008-10-02 | 2008-10-03 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | PINOLE | INSTALLED NEW PLUG AND STL. CAP; LEAK THOUGHT TO BE ON 6" HP..., FOUND ON T.P. MAIN NEXT DAY REPAR MADE. VENTED ON DAY FOUND!! SOAP TESTED AFTER REPAIR...MONITOR WHIL BRINING PRESSURE BACK UP.
| 09-95203-1 |  |  | 0.5 | Transmission |  | Valves |  |  | Other |  | 2009-01-29 | 2009-04-30 | Other |  | Steel/Wrought Iron |  | RICHMOND | SHUT OFF 1/2" GAUGE VALVE AND REDOPED 1/2" RING; FOUND GAS LEAK ON 1/2" PLUG ON 1/2" VALVE FOR T.P. GAUGING IN VFC N-174. VALVE WAS IN THE ON POSITION. SHUT VALVE OFF AND REDOPED PLUG. TIGHTENED TO REPAIR LEAKAGE.
| 09-80049-1 |  |  | 0.75 | Single Service |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2009-05-20 | 2009-05-20 | Other | CUT & RETHREADED RISER | Steel/Wrought Iron |  | RICHMOND | CUT & RETHREADED; ALL ABOVE GROUND
| 09-95642-1 |  |  | 0.75 | Branch Service | TRANSMISSION | Valves |  |  | Unknown |  | 2009-06-11 | 2009-08-31 | Other | GREASED VALVES IN CMB | Steel/Wrought Iron |  | BERKELEY | GREASED VALVES IN CMB T.P. TO H.P. REG SET.
| 09-95637-1 |  |  | 0.75 | Branch Service |  | Other |  | GAUGE TAP | Unknown |  | 2009-06-10 | 2009-08-18 | Other |  | Steel/Wrought Iron |  | BERKELEY | REDOPED AND TIGHTENED; REDOPED AND TIGHTENED 1/4" METRIC GAUGE TAP VALVE.
| 09-15038-1 |  |  | 6 | Transmission |  | Other Welds |  |  | Weld Failure |  | 2009-03-17 | 2009-04-24 | Deactivate #TP Main | REPLACE TP MAIN | Steel/Wrought Iron |  | ALAMEDA | LEAK ON MAIN; LEAK ON MAIN VENTED; RAN 12' TP AROUND LEAK SITE FOR STREET WIDENING PROJECT
| 09-15066-1 |  |  | 0.75 | Single Service |  | Fitting |  |  | Construction Defect |  | 2009-04-15 | 2009-04-15 | Tighten Cap or Bolt | TIGHTENED FITTINGS | Steel/Wrought Iron |  | OAKLAND | TIGHTENED FITTINGS
| 09-90863-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Material Failure |  | 2009-06-23 | 2009-09-21 | Other | GREASED VALVE | Steel/Wrought Iron |  | OAKLAND | T.R. GREASE VALVE TO STOP LEAK
| 09-80061-1 |  |  | 0.5 | Transmission |  | Girth Weld |  |  | Other | WELD NOT FINISHED | 2009-06-15 | 2009-09-10 | Fill Weld - Weld |  | Steel/Wrought Iron |  | HERCULES | FINISHED OFF WELD THAT WAS INCOMPLETE; SOAP TEST ONLY
| 10-25647-1 |  |  | 0.5 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2010-08-20 | 2010-09-10 | Other | Gasket + Valve | Steel/Wrought Iron |  | Berkeley | IN VF&C REPLACED GASKET TO FLANGE & 1/2" BLOW OFF VALVE
| 10-99063-1 |  |  | 1975-10-01 | Single Service |  | Other |  | Leak on 3/4" plug | Other | Loose plug | 2010-08-12 | 2010-08-12 | Other | Tightened 3/4" plug in coupling after regulated | Steel/Wrought Iron |  | Berkeley | Gas leak on 3/4" plug into a 3/4" couplig after regulator. Meter had been disconnected and plug installed
| 03-21023-1 |  |  | 6 | Distribution Main |  | Valves |  |  | Unknown |  | 2003-03-05 | 2010-05-03 | Other | Greased and tunned valve | Steel/Wrought Iron |  | El Sobrante | Had M&C greased and tunned valve
| 03-25266-1 |  |  | 3 | Transmission |  |  |  |  | Other | Steel cap | 2003-09-23 | 2010-05-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Richmond | Tightened completion plug, re-doped and tightened steel cap
| 08-10001-1 | 105A |  | 16 | Transmission |  | Valves |  |  | Other | Grease | 2008-04-26 | 2010-10-16 | Other | Greased vlv | Steel/Wrought Iron |  | Richmond | Greased valve
| 10-11029- | 153 | 25.34 | 24 | Transmission |  | Girth Weld |  |  | External Corrosion |  | 2010-02-23 | 2010-02-25 | Other | REPLACE SECTION OF 24" PIPE | Steel/Wrought Iron |  | OAKLAND
| 10-81201-1 | 153 | 25.83 | 21 | Transmission |  | Body of Pipe |  |  | Construction Defect |  | 2010-10-06 | 2010-10-21 | Replace Dist Main < 100 ft | REPLACED SECTION OF PIPE | Steel/Wrought Iron |  | OAKALND | REPLACED 11.5' OF MAIN;
| 10-11029- | 153 | 25.34 | 24 | Transmission |  | Girth Weld |  |  | External Corrosion |  | 2010-02-23 | 2010-02-25 | Other | REPLACE SECTION OF 24" PIPE | Steel/Wrought Iron |  | OAKLAND | REPLACE OF 24" T.P. PIPE
| 05-21124-1 |  |  | 24 | Transmission |  | Longitudinal Weld |  |  | Construction Defect |  | 2005-04-18 | 2006-10-07 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | OAKLAND | INSTALLED 24" STEEL SLEEVE
| 05-11091- |  |  | 0.75 | Service |  | Valves |  |  | Construction Defect |  | 2005-04-29 | 2005-04-29 | Other | GREASED FITTING | Steel/Wrought Iron |  | EMERYVILLE | GREASED 3/4" VALVE
| 05-41039-1 | [10 empty] | 2005-06-06 | [5 empty] | ALAMEDA | IN SEWER CLEAN-OUT CLOSE TO DOOR BLDG 4, NO READING.
| 05-21254-1 |  |  | 8 | Service |  | Valves |  |  | Other | VALVE | 2005-10-10 | 2006-03-24 | Other | GREASE VALVE | Steel/Wrought Iron |  | OAKLAND | GREASE AND TURN VALVE
| 05-21004-1 |  |  | 0.75 | Service |  | Fitting |  |  | Construction Defect |  | 2005-04-13 | 2006-10-04 | Other | TIGHTEN UNION | Steel/Wrought Iron |  | OAKLAND | TIGHTEN 3/4" UNION
| 94-23724-1 |  |  | 0.75 | Service |  | Valves |  |  | Other | VALVE; | 1994-04-13 | 2006-10-06 | Other | GREASED VALVE | Steel/Wrought Iron |  | OAKLAND | GREASED 3/4" T.P. VALVE
| 05-21006-1 |  |  | 0.75 | Service | TRANSMISSION | Valves |  |  | Other | VALVE | 2005-04-13 | 2006-10-04 | Other | CLOSED VALVE | Steel/Wrought Iron |  | OAKLAND | CLOSED VALVES ON HIGH TO HIGH REG. SET.; CLOSED VALVES IN HIGH TO HIGH SET. TO STOP LEAK IN C.M.B.
| 06-42056-1 |  |  | 1.25 | Single Service |  | Body of Pipe |  |  |  |  | 2006-06-27 | 2006-06-27 | Replace Partial Service |  | Aldyl A (Tan or Gray) |  |  | INSTALLED 12" OF 1 1/4" PLASTIC PIPE AND TWO 11/4" MET FIT COUPLINGS.; CONTRACTOR DID NOT EXPOSE SERVICE BY HAND; WHEN I ARRIVED ON JOB SITE I FOUND THAT A CONTRACTOR HAD BROKE OUR 1 1/4" PLASTIC GAS SERVICE.
| 06-12206-1 | [10 empty] | 2006-07-17 | [5 empty] | EMERYVILLE
| 06-12028- |  |  | 1 | Single Service |  | Body of Pipe |  |  |  |  | 2006-01-25 | 2006-01-25 | Other | COUPLING | TR 418 |  | ALAMEDA | 1 MET-FIT COUPLING 3' FROM SIDEWALK; LOOKS LIKE THEY WERE DRILLING HOLES FOR SOME KIND OF LIGHTING AND HIT GAS SERVICE. NO USA VISABLE.
| 05-21044-1 |  |  | 1.25 | Service |  | Valves |  |  | Construction Defect |  | 2005-04-09 | 2006-10-02 | Other | REPAIRED BY PASS VALVE | Steel/Wrought Iron |  | OAKLAND | REPAIRED 1 1/4" BY-PASS VALVE
| 05-21045-1 | 105N |  | 4 | Transmission |  | Other Welds |  |  | Construction Defect |  | 2005-04-09 | 2006-10-09 | Patch Weld - Weld |  | Steel/Wrought Iron |  | OAKLAND | REWELD PATCH WELD
| 05-21009-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2005-04-19 | 2006-10-18 | Other | GREASED VALVE | Other | VALVE | OAKLAND | OVER SVC BART LG BOC IN SIDEWALK; OVER SVC BARY LG BOX IN SIDEWALD; OVER SVC BART LG BOX IN SIDEWALK; GREASED 3/4" T.P. VALVE
| 06-22053-1 | 105 |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2006-04-21 | 2006-05-24 | Other | GREASED VALVE; | Steel/Wrought Iron |  | OAKLAND | GREASED VALVE
| 06-12119- |  |  | 0.75 | Service |  | Riser |  |  | External Corrosion |  | 2006-04-21 | 2006-04-21 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | OAKLAND | INSTALLED CLAMP ON SERVICE
| 05-21008-1 |  |  | 0.75 | Service | TRANSMISSION | Valves |  |  | Other | LEAKING VALVE | 2005-04-19 | 2006-10-04 | Other | GREASED VALVE | Steel/Wrought Iron |  | OAKLAND | OVER SVC BY FENCE; OVER SVC BY FENCE; OVER SVC BY FENCE; GREASED VALVE TO STOP LEAK; REPAIRED LEAK ON HIGH TO HIGH SET AT P.L.
| 07-25076-1 |  |  | 6 | Transmission |  | Valves |  |  | Other | VALVE STEM | 2007-03-06 | 2007-04-25 | Other |  | Steel/Wrought Iron |  | OAKLAND | GREASED VALVE TO STOP LEAK; GREASED VALVE TO LEAK
| 07-25077-1 | [10 empty] | 2007-03-06 | [5 empty] | OAKLAND
| 05-21255-1 | [10 empty] | 2005-10-11 | [5 empty] | OAKLAND | ALAMED AVE AND JENSEN N SIDE OF INT.; ALAMEDA AVE AND JENSEN N SIDE OF INT.; IN VFC
| 05-21255-1 | [10 empty] | 2005-10-11 | [5 empty] | OAKLAND | ALAMEDA AVE AND JENSEN N SIDE OF INT.; ALAMEDA AVE AND JENSEN N SIDE OF INT; IN VFC; NO GAS FOUND
| 05-21256-1 |  |  | 0.75 | Service |  | Riser | Valves |  | Construction Defect |  | 2005-10-11 | 2007-04-11 | Other | REPAIRED VALVE | Steel/Wrought Iron |  | OAKLAND | REPAIRED SERVICE VALVE
| 05-21253-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other | LEAKS ON FITTINGS | 2005-10-07 | 2007-04-05 | Other | TIGHTENED FITTINGS | Steel/Wrought Iron |  | ALAMEDA | M&C CREW TIGHTENED FITTINGS; TIGHTENED FITTINGS ON HIGH TO HIGH SET
| 05-21251-1 | 105 |  | 3 | Transmission |  | Valves |  |  | Other |  | 2005-10-06 | 2006-04-04 | Other | GREASED VALVE | Steel/Wrought Iron |  | OAKLAND | 100' E/O ADDRESS FV-05; 100' E/O ADDRESS FV-07; EV-07; GREASED VALVE
| 05-21250-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2005-10-06 | 2007-04-05 | Other | GREASED VALVE | Steel/Wrought Iron |  | OAKLAND | HIGH TO HIGH BOX; HIGH TO HIGH BOX; HI TO HI BOX; GRESED T.P. VALVE REARKED HP VALVE
| 06-22051-1 |  |  | 0.75 | Distribution Main |  | Valves |  |  | Other | LOOSE VALVE | 2006-04-19 | 2007-10-05 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | OAKLAND | CURB VALVE; CURB VALVE; TIGHTENED STEMS ON VALVE.
| 08-20144-1 | 153 |  | 20 | Transmission |  | Valves |  |  | Unknown |  | 2008-05-20 | 2008-07-29 | Other |  | Steel/Wrought Iron |  | OAKLAND | GREASED VALVE X-36; WORK DONE IN VAULT
| 08-20145-1 | 153 |  | 20 | Transmission |  | Fitting |  |  | Unknown |  | 2008-05-20 | 2008-07-29 | Tighten Cap or Bolt | OTHER | Steel/Wrought Iron |  | OAKLAND | TIGHTEN FITTING ON VALVE X-82; EXPOSED IN MANHOLE!
| 08-20146-1 |  |  | 4 | Distribution Main |  | Valves |  |  | Unknown |  | 2008-05-20 | 2008-07-29 | Other |  | Steel/Wrought Iron |  | OAKLAND | GREASED VALVE; WORK DONE IN V.F. & C VALVE A57
| 06-22320-1 |  |  | 2 | Distribution Main |  | Fitting | Other | 2" B.T.P.C.F. CAP | Construction Defect |  | 2006-10-11 | 2008-04-03 | Tighten Cap or Bolt |  | Cast/Ductile Iron |  | OAKLAND | REMOVE AND DOTED 2" CAP TIGHTEN FOR PERM REPAIRS
| 08-20070-1 | 105 | 0.43 | 6 | Transmission |  | Valves |  |  | Other |  | 2008-02-13 | 2008-05-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EMERYVILLE | UPSTREAM OF FIRE VALVE @ EGG STATION
26 | 89-20924-1 | [10 empty] | 1989-06-26 | [5 empty] | OAKLAND
| 01-80441-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 2001-07-14 | 2001-07-25 | Other |  | Steel/Wrought Iron |  | BERKELEY | REPLACED 3/4" T/P/ VALVES ON BLOW OFF/GAUGE TAPS; REPLACED GAUGE TAP VALVE IN FFC AT H-14
| 04-80320-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 2004-11-17 | 2004-11-17 | Other |  | Steel/Wrought Iron |  | RICHMOND | TIGHTENED UNION ON T.P. ZONE VALVE X-23; TIGHTENED UNION ON T.P. VALVE X-23
| 05-80372-1 |  |  | 1.25 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2005-12-15 | 2006-03-09 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | RICHMOND | INSTALLED WELD CAN OVER LEAK
| 06-80096-1 |  |  | 2 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2006-03-24 | 2006-05-09 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | RICHMOND | INSTALLED WELD CAN OVER PITS IN AND; INSTALLED WELD CAN OVER CORROSION LEAK AND E75
| 06-80240-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2006-10-19 | 2007-03-30 | Other | PLIDCO CLAMP | Steel/Wrought Iron |  | BERKELEY | INST. T.P. CLAMP TO REPAIR LEAK (PLIBCO); PLIBCO 16" CLAMP
| 08-10001-1 | 105A |  | 16 | Transmission |  | Valves |  |  | Other | GREASE | 2008-04-26 | 2010-10-16 | Other | GREASED VLV | Steel/Wrought Iron |  | RICHMOND | ZONE VLV X-23 TO DFM- CALLED ...; ON ZONE VALVE X-23 TO DFM-CALLED CREW; 5 VALVE IN AREA VALVE X-22 IN VAULT LEAK.
| 08-10002-1 | 105A | 45 | 0.25 | Transmission |  | Tap Connection |  |  | Unknown |  | 2008-04-26 | 2008-08-07 | Other | REPLACED 1/4" FITTINGS AND NIPPLES TO CLEAR LEAKAGE | Steel/Wrought Iron |  | RICHMOND | IB 105A MAINLINE VLV X-21 (MP 45.)
| 08-30080-1 |  |  | 0.75 | Transmission |  | Tap Connection |  |  | Unknown |  | 2008-10-02 | 2008-10-03 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | PINOLE | INSTALLED NEW PLUG & STL CAP; LEAK THOUGHT TO BE ON 6" HP. DOWNSTEADED, FOUND ON T.P. MAIN NEXT DAY REPAIR MADE, VENTED ON DAY FOUND!! SOAP TESTED AFTER REPAIR...MONITOR WHILE BRINGING PRESSURE BACK UP.
| 09-95203-1 |  |  | 0.5 | Transmission |  | Valves |  |  | Other |  | 2009-01-29 | 2009-04-30 | Other |  | Steel/Wrought Iron |  | RICHMOND | SHUT OFF 1/2" GAUGE VALVE AND REDOPED 1/2" PLUG; FOUND GAS LEAK ON 1/2" PLUG ON 1/2" VALVE FOR T.P. GAUGING IN VFC N-174. VALVE WAS IN THE ON POSITION SHUT VALVE OFF AND REDOPED PLUG. TIGHTENED TO REPAIR LEAKAGE.
| 10-25647-1 |  |  | 0.5 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2010-08-20 |  |  |  | Steel/Wrought Iron |  | BERKELEY | IN VF&C REPLACED GASKETTE TO FLANGE & 1/2" BLOW OFF VALVE.
28 | 97-21038-1 |  |  | 24 | Transmission |  | Valves |  |  |  |  | 1997-04-17 | 1998-09-23 | Other | GREASED | Steel/Wrought Iron |  | RICHMOND | VALVE GREASED LEAKAGE...
28 | 97-21152-1 |  |  | 24 | Transmission |  | Valves |  |  | Other |  | 1997-09-17 | 1999-08-17 | Other |  | Steel/Wrought Iron |  | BERKELEY | ALREADY COMPLETED (VALVE FREASED BY M&C ... LONE AGO
| 99-21032-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1999-02-26 | 2000-06-21 | Other | GREASED FITTING | Steel/Wrought Iron |  | HERCULES | LEAK ON GREASE FITTING
| 99-21082-1 | [10 empty] | 1999-07-30 | 2000-12-11 | Tighten Cap or Bolt |  |  |  | RICHMOND | CHARGE REPAIR TO DM 4003398; TIGHTENED PLUG
28 | 74-20569-1 |  |  | 0.75 | Other |  | Meter |  |  | Material Failure |  | 1974-09-24 | 1974-10-30 | Other |  | Steel/Wrought Iron |  | RICHMOND | AND SOAP TESTED CURB METER & IRONS; ELECT. U.G. & PT&T IN AREA IN 23RD ST. SEE OVER; VACANT LOT CHECKED METER BOX TO 757 NO LEAKS FOUND. D ENOCHS CHANGED LEAKING METER AT 767 23RD ST.
|  |  |  | 0.02 | Distribution Feeder Main |  | Other |  |  | Other |  | 1976-08-19 | 1976-08-19 | Other |  | Steel/Wrought Iron |  | RICHMOND
|  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  | 1976-08-19 | 1976-08-17 | Other |  | Steel/Wrought Iron |  | RICHMOND
| 75-60331-1 |  |  | 1 | Other |  | Fitting |  |  | Corrosion |  | 1975-06-23 | 1975-07-03 | Other |  | Steel/Wrought Iron |  | RICHMOND | INSTALLED (2) 3" M FITTINGS TO REMOVE ABANDONED 1" SCREWED SERVICE TEE
28 | 72-40329-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-05-30 | 1972-05-31 | Patch Welded |  | Steel/Wrought Iron |  | RICHMOND | FOUND LEAKAGE ON 3" MAIN. 12' W/E LINE HUMBOLDT ST. INSTALLED 3" WELD PATCH & 9LB MAG. ANODE.
28 | 72-40423-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-07-16 | 1972-07-17 | Clamp |  | Steel/Wrought Iron |  | RICHMOND | INSTALLED 3 SKINNER CLAMPS EACH 2 BOLTS AND 2 ANODES 3" P.C.F WAS LEAKING ON THE WELD
|  |  |  | 3 | Distribution Feeder Main | [7 empty] | 1974-03-04 |  |  | Steel/Wrought Iron |  | RICHMOND | HAD TO RAISE THE RISER FOR THE CUSTOMER
28 |  |  |  | 2 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | SAN PABLO
28 |  |  |  | 2 | Distribution Feeder Main | [7 empty] | 1974-05-31 |  | REPLACEMENT | Steel/Wrought Iron |  |  | REPLACE 1" SERV. WITH 1/2 PL.
28 | 76-20151-1 |  |  | 0.75 | Other |  | Regulator |  |  | Material Failure |  | 1976-03-08 | 1976-05-04 | Replace Pipe and/or Service |  | Other |  | SAN PABLO | UNDERGROUND IN AREA NONE KNOWN; REPLACED LEAKING REGULATOR. BAR TESTED SERVICE AND FOUND NO OTHER INDICATION OF LEAKAGE.
| 74-60338-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-06-12 | 1974-06-13 | Clamp |  | Steel/Wrought Iron |  | RICHMOND | FOUND TWO 301'S IN PARKING STRIP IN FRONT OF 2851 LOWELL MADE PERMANENT REPAIRS BY INSTALLING TWO 3" SKINNER PERM. LEAK CLAMPS. INSTALLED 9LB MAG. ANODE
28 | 76-20078-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1976-03-01 | 1976-06-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN PABLO | UNDERGROUND IN AREA NONE KNOWN; INSTALLED 22' OF 1/2" PLASTIC SERVICE TO REPAIR 301.
| 80-40579- |  |  | 2 | Other | STUB | Body of Pipe |  |  | Corrosion |  | 1980-07-14 | 1980-07-15 | Other |  | Steel/Wrought Iron |  | RICHMOND | INST. 2" M-2 & CUT OFF STUB.
28 | 82-40011-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1982-01-07 | 1982-01-07 | Replace Pipe and/or Service |  | Other Plastic |  | RICHMOND | INST. APPROX. 1' 1/2" PL PIPE & 2. 5/8" AMP COUP TO REPAIR LEAKAGE ON SERV.; REPAIRED BROKEN 1/2" PLASTIC SERVICE
| 75-20666-1 |  |  | 0.75 | Other |  | Fitting |  |  | Construction Defect |  | 1975-10-26 | 1975-11-20 | Other |  | Steel/Wrought Iron |  | SAN PABLO | PT&T UG IN AREA ELECT. UG IN AREA PIT MARKED; REBUILT IRONS AT REGULATOR AND TIGHTENED BACKING NUT TO MAKE REPAIRS. 3/4" INSULATED UNION LEAKING.; NO MAIN OR SERVICE INSPECTION A/C LEAKAGE ON IRON CONNECTIONS
28 | 96-21245-1 |  |  | 4 | Transmission |  | Other Welds |  |  | Corrosion |  | 1996-09-16 | 1996-09-16 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | RICHMOND | INST. 4" TP CAN OVER MAIN
28 | 96-21246-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1996-09-19 | 1996-09-19 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | RICHMOND | INST 4" CAN FOR 4" TP MAIN
28 | 89-20111-1 |  |  | 4 | Distribution Main |  | Valves |  |  | Other |  | 1989-05-22 | 1989-05-22 | Other |  | Steel/Wrought Iron |  | RICHMOND | GREASED VALVE ON 4" TP MAIN.; DID NOT HAVE TO UNCOVER VALVE.
28 | 81-60178-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1981-12-17 | 1982-01-15 | Patch Welded |  | Steel/Wrought Iron |  | RICHMOND | POST TO PIPELINE SURVEY MAPS SHEET 7 105A; VENTED DOWN GRADED. INST. (1) 6"X6"-20" WELD PATCH ON BOTTOM OF T.P. MAIN.
|  |  |  | 20 | Transmission |  | Other |  |  | Other |  |  | 1976-12-01 | Other |  | Steel/Wrought Iron
| 75-40279- |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-07-28 | 1975-08-01 | Patch Welded |  | Steel/Wrought Iron |  | RICHMOND | EXPOSED 12' OF 20" T.P. MAIN FOUND (32) ELECTROLYSIS PITS RANGING IN SIZE FROM 1" TO 3" IN DIAMETER AND UP .31" DEEP. REPAIRED 20 PITS WITH A 42" LONG SLEEVE FROM 20' OUT TO 33.6' N/O S/PL OF RIPLEY. WELDED PATCHES OVER THE REMAINING 12 PITS
28 | 89-32104-1 |  |  | 2 | Transmission |  | Valves |  |  | Other |  | 1989-11-09 | 1990-01-03 | Other |  | Steel/Wrought Iron |  | R | GREASED 2" TP VALVE TO MAKE PERMANENT REPAIRS; GREASED NEW 2" TP VALVE (OFF 105 24") NO LEAKAGE PER FLAMPAK
|  |  |  | 4 | Transmission |  | Other |  |  | Other |  |  | 1973-03-07 | Clamp |  | Steel/Wrought Iron |  | RICHMOND | MADE CUT WITH HACKSAW IN ORDER TO DRAIN WATER OUT OF MAIN INST 2 BOLT SKINNER CLAMP & 5# ZINC ANODE
28 | 73-20493-1 |  |  | 0.75 | Other |  | Meter |  |  | Material Failure |  | 1973-03-22 | 1973-03-22 | Other |  | Steel/Wrought Iron |  | RICHMOND | REF. TO SERVICE DEPT FOR REPAIRS
|  |  |  | 20 | Transmission |  | Other |  |  | Other |  |  | 1976-12-01 | Other |  | Steel/Wrought Iron |  | RICHMOND
26 | 80-40698-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1980-09-12 | 1980-09-12 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | RICHMMOND | EXPOSED MAIN TO REPLACE LEAKING 3/4" STL. GAS SERV.
28 | 88-00104-1 | 105A |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1988-02-09 | 1988-01-09 | Patch Welded |  | Steel/Wrought Iron |  | RICHMOND | PATCH WELDED 301 ON 20" TP MAIN.
28 | 73-20457-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-03-01 | 1974-06-19 | Clamp |  | Steel/Wrought Iron |  | RICHMOND | INSTALLED ONE 2" (4BOLT) SKINNER PERMANENT LEAK CLAMP AND ONE 9LB MAG. ANODE AT LOCATION INDICATED ON SKETCH. THIS MAIN IS IN POOR CONDITION AND SHOULD BE REPLACED IN THE FUTURE.
|  |  |  | 2 | Distribution Feeder Main |  | Other | Other |  |  |  | 1976-10-26 |  | Other |  | Steel/Wrought Iron |  | RICHMOND
|  |  |  | 2 | Distribution Feeder Main |  | Other |  |  |  |  | 1976-10-26 |  | Other |  | Steel/Wrought Iron
|  |  |  | 3 | Distribution Feeder Main |  | Other |  |  |  |  | 1976-10-15 |  | Other |  | Steel/Wrought Iron |  | RICHMOND
28 | 73-20464-1 |  |  | 0.5 | Service |  | Other Welds |  |  | Construction Defect |  | 1973-03-01 | 1974-06-20 | Replace Pipe and/or Service |  | Copper |  | RICHMOND | REPAIRED LEAKING 1/2" COPPER SERVICE AT TEE BY REPLACING ONE FOOT COPPER SERVICE
| 73-20464-1 |  |  | 0.5 | Service |  | Other Welds |  |  | Construction Defect |  | 1973-03-01 | 1974-06-21 | Replace Pipe and/or Service |  | Copper |  | RICHMOND | REPAIRED LEAKAGE ON 1/2" COPPER SERVICE TO 2901 CENTER BY RESOLDERING CONNECTION AT MAIN AND INSTALLING NEW COUPLING AT POINT ON A SKETCH SHOWN. A/C STAND UP DID NOT HOLD.
|  |  |  | 20 | Distribution Feeder Main | [6 empty] | 1976-10-21 |  |  |  | Steel/Wrought Iron |  | RICHMOND
|  |  |  | 2 | Distribution Feeder Main | [6 empty] | 1976-10-21 |  |  |  | Steel/Wrought Iron |  | RICHMOND
|  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1976-10-20 |  |  |  | Steel/Wrought Iron |  | RICHMOND
1 | 82-20530-1 |  |  | 4 | Other |  | Valves |  |  | Material Failure |  | 1982-04-07 | 1983-03-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | RICHMOND | GREASED 4" OUTLET VALVE
28 | 82-20511-1 |  |  |  | Other | HOUSE LINE | Body of Pipe |  |  | Corrosion |  | 1982-04-07 | 1982-04-07 | Other | SHUT DOWN CUSTOMER HOUSELINE LEAKING | Steel/Wrought Iron |  | RICHMOND | HOUSELINE LEAKING 1 1/2 CUBIC FOOT PER HOUR. SHUT CUSTOMER OFF. BAR TESTED OVER MAIN & SERVICE NO LEAKAGE FOUND. REFERRED TO SERVICE DEPT.
| 76-40187- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1976-06-28 | 1976-07-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | RICHMOND | INSPECTION REPORT A/C RERUN SERVICE
28 | 81-40400-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1981-06-15 | 1981-06-15 | Other |  | Steel/Wrought Iron |  | RICHMOND | LEAK ON HOUSELINES CUSTOMERS SHUT OFF BY SERVICE DEPT.
28 | 72-60094-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-05-25 | 1972-05-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | RICHMOND | WELDED HALF SOUL OVER PITTED AREA OF 8" HP MAIN; INSTALLED 4" CAN OVER OLD 1 1/2" NIPPLE WITH THREADED PLUG; INSTALLED 9# ANODE
28 | 77-40285-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1977-08-18 | 1977-08-18 | Clamp |  | Steel/Wrought Iron |  | EL CERRITO | REPAIRED MAIN BY INSTALL ONE 2-BOLT SKINNER PERMANENT LEAK CLAMP; INSPECTION REPORT A/C REPAIR MAIN.
| 79-20136- |  |  | 0.5 | Other |  | Fitting |  |  | Other |  | 1979-02-06 | 1979-02-08 | Other |  | Other Plastic |  | RICHMOND | RECHECKED REQUIRED; LEAK ON FITTINGS IN CURB MTR BOX
| 75-60161-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1975-04-01 | 1975-04-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | RICHMOND | FOUND HEAVY CORROSION ON 4MM IN CURB BOX. REPLACED MANIFOLD WITH A NEW ONE - REMOVED METER TO 12141 SAN PABLO AVE AT REQUEST OF RICHMOND CITY INSPECTOR DUE TO LEAKAGE IN HOUSE LINES.
|  |  |  | 0.75 | Other |  | Valves |  |  | Material Failure |  | 1978-07-05 | 1978-07-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | EL CERRITO | INSPECTION REPORT A/C RERUN OLD AGE SERVICE WITH LEAKING STOP-COCK.
28 | 77-40331-1 |  |  | 0.5 | Service |  | Fitting |  |  | Material Failure |  | 1977-09-20 | 1977-09-20 | Other |  | Other Plastic |  | ELL CERRITO | DUG UP SERVICE RISER ONLY TO REPAIR 1/2" PLASTIC SERVICE AT TRANSITION CTG.; RISER ONLY
28 | 82-21254-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1982-07-07 | 1983-06-17 | Other |  | Steel/Wrought Iron |  | EL CERRITO | NO UG ELEC. INST. 3 CLAMPS ON 3/4" BLOW OFF ON 3" MAIN. INST. TWO 3" M/2 FITTINGS AND REMOVED BLOW OFF
|  |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-08-26 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | EL CERRITO | EXPOSED MAIN ACCT. OF RERUN SERVICE TO 1822 ARLINGTON
|  |  |  | 24 | Transmission |  | Other |  |  | Other |  | 1975-06-02 | 1975-06-02 | Other |  | Steel/Wrought Iron |  | RICHMOND | WATER CO. SCRAPED WRAP ON 24" TP MAIN REWRAPED SAME
28 | 97-21038-1 |  |  | 24 | Transmission |  | Valves |  |  | Other |  | 1997-04-17 | 1998-09-23 | Other | GREASED | Steel/Wrought Iron |  | R | VALVE GREASED NO LONGER LEAKING
28 | 94-20277-1 | 105 |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1994-03-25 | 1994-04-01 | Other |  | Steel/Wrought Iron |  | RICHMOND | REPAIRED CORE ON 3/4" BLOW OFF - GREASED & TIGHTENED
28 | 96-21284-1 |  |  | 24 | Transmission |  | Other |  |  | Other |  | 1996-10-02 | 1997-10-31 | Other |  | Steel/Wrought Iron |  | R | TIGHTEN PLUG
28 | 72-40051-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-01-14 | 1972-01-19 | Other |  | Steel/Wrought Iron |  | RICHMOND | FOUND MAIN PITTED ON TOP SECTION; REPAIRED: BY INSTALLING (1) 12" X 24" CAN & I WELD PATCH
28 | 73-20610-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-06-22 | 1973-08-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | RICHMOND | LEAK HOME MADE TEE ALSO IN BODY OF SERVICE. INST (2) M/2 3" WITH IN OTHER TO REMOVE HOME MADE TEE ONE 70' S/O SO28TH ST THE OTHER ONE 74' S/O SO28TH ST.
[5 empty] | Transmission | [10 empty] | Steel/Wrought Iron |  | RICHMOND | WELDED 3/4 TEE NEW SERV
28 | 92-00082-1 | [10 empty] | 1992-02-13 | [5 empty] | RICH | JOB COMPLETED ON GM 4857918
INVESTIGATED/DOWNGRADED THIS MAIN IS IN FOR REPLACEMENT
28 |  |  |  | 6 | [11 empty] | Steel/Wrought Iron
28 | 96-21272-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1996-10-03 | 1998-03-31 | Other | ; | Steel/Wrought Iron |  | R | MADE REPIARS ON IRON CONNECTIONS #2 1/2 CURB
| 79-40132- |  |  | 1.25 | Service |  | Valves |  |  | Material Failure |  | 1979-03-14 | 1979-03-14 | Other |  | Steel/Wrought Iron |  | RICHMOND | REPLACED CURB VALVE DUE TO LEAKAGE.
|  |  |  | 6 | [13 empty] | RICHMOND | PROSPECT MAIN FOR DEPTH
|  |  |  | 6 | [13 empty] | RICHMOND | PROSPECT MAIN FOR DEPTH
|  |  |  | 6 | [13 empty] | RICHMOND | PROSPECT MAIN FOR DEPTH
28 | 86-60065-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1986-03-26 | 1986-04-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | RICHMOND | C/O SERV AT CURB VALVE TO ELIMINATE LEAKAGE.; R/R WITH 3/4" STL.
28 | 83-40310-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1983-07-05 | 1983-07-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | RICHMOND | ALTER 76' 3/4" T.P. SERV.
28 |  |  |  | 20 | Other |  | Other |  |  | Other |  | 1982-10-05 |  | Other |  | Steel/Wrought Iron |  | RICHMOND | INSTALLED A 1/2" PL. SERVICE
|  |  |  | 20 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | RICHMOND | INST. 1/2" PL. SERVICE - USED 3/4" MULLER SERV. TEE
28 | 92-00082-1 | [10 empty] | 1992-02-13 | [5 empty] | RICHMOND | JOB COMPLETED ON GM 4857918; INVESTIGATED/DOWNGRADED THIS MAIN IS FOR REPLACEMENT
28 |  |  |  | 6 | [11 empty] | Steel/Wrought Iron
28 | 96-21272-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1996-10-03 | 1998-03-31 | Other |  | Steel/Wrought Iron |  | RICHMOND | MADE REPAIRS ON IRON CONNECTIONS #2 1/2 CURB
| 79-40132- |  |  | 1.25 | Service |  | Valves |  |  | Material Failure |  | 1979-03-14 | 1979-03-14 | Other |  | Steel/Wrought Iron |  | RICHMOND | REPLACED CURB VALVE DUE TO LEAKAGE.
|  |  |  | 6 | [13 empty] | RICHMOND | PROSPECT MAIN FOR DEPTH
|  |  |  | 6 | [13 empty] | RICHMOND | PROSPECT MAIN FOR DEPTH
|  |  |  | 6 | [13 empty] | RICHMOND | PROSPECT MAIN FOR DEPTH
28 | 86-60065-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1986-03-26 | 1986-03-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | RICHMOND | C/O SERV AT CURB VALVE TO ELIMINATE LEAKAGE. R/R WITH 3/4" STL.
28 | 83-40310-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1983-07-05 | 1983-07-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | RICHMOND | ALTER 76' 3/4" T.P. SERV.
28 | 93-20795-1 |  |  | 6 | Distribution Feeder Main |  | Fitting |  |  | Other |  |  | 1993-09-17 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | PT. RICHMOND | REPAIRED 2 LEAKS IN VAULT
28 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1981-09-24 | 1981-09-24 |  |  | Other Plastic |  | PT. RICHMOND | EXPOSED TO INST. NEW 1" PL. GAS SERV.
28 | 84-40347-1 |  |  | 1.25 | M |  | Body of Pipe |  |  | Digin |  | 1984-09-03 | 1984-09-03 | Other |  | Aldyl A (Tan or Gray) |  | PT. RICHMOND | C/O15' OF 1 1/4" MAIN & SERVICE DUE TO CUSTOMER DIGGING UNDER FOUNDATION. WILL CALL TO HAVE SERVICE RESTORED.
28 | 82-21095-1 |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1982-06-15 | 1983-05-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | E.C. | 8 YES UG ELEC; NOTE: 115,000 VOLT ELECT. UG. IN AREA; REPLACED 3/4" SERVICE WITH 1/2" PLASTIC
28 | 72-20361-1 |  |  | 2 | Distribution Feeder Main |  | Other Welds |  |  | Other |  | 1972-03-24 | 1972-11-29 | Clamp |  | Steel/Wrought Iron |  | E.C.
28 | 74-20607-1 |  |  | 0.75 | Other |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1974-09-30 | 1974-10-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | RICHMOND | WORK WITHIN ONE WEEK FROM DATE FOUND; ELECTRIC & PT&T U.G. IN AREA; REPLACED LEAKING FITTINGS ON METER SET IN CURB METER BOX; 10% F.O. 2' FROM BUILDING 15' FROM CURB.
| 04-80021-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2004-01-14 | 2004-01-15 | Patch Welded |  | Steel/Wrought Iron |  | RICHMOND | 301 ON MAIN UNDER 4" STL PLATE; INSTALLED 1 WELD PATCH;
[18 empty] | RICHMOND | C/O 2" SERVICE AT MAIN
28 |  |  |  | 4 | [11 empty] | Steel/Wrought Iron |  | RICHMOND
|  |  |  | 4 | [13 empty] | RICHMOND | E/SIDE HARBOUR WAY 34' OUT 12' N/OF HALL AVE C/O SERV. AT MAIN; C/O SERV
26 | 71-40084-1 |  |  | 1.25 | Other |  | Fitting |  |  | Damage by outside Forces |  | 1971-07-27 | 1972-02-10 | Other |  | Steel/Wrought Iron |  |  | REPLACED NYLON BUSHING ON OUT LET SIDE OF A 20-B-METER
|  |  |  | 2 | [11 empty] | Steel/Wrought Iron |  | OAK.
26 | 76-21163-1 |  |  | 2 | Other | MANIFOLD | Other |  |  | Other |  | 1976-06-30 | 1976-11-03 | Other | FOUND NO LEAKAGES | Steel/Wrought Iron | X STATEN | OAKLAND | .05% AT MTR. BOX IN S/W.; FOUND WO LEAKAGE
26 | 76-21164-1 |  |  | 2 | Other | MANIFOLD | Other |  |  | Other |  | 1976-06-30 | 1976-11-03 | Other | SOAP TESTED FOUND NO LEAKAGE | Steel/Wrought Iron | X STATEN | OAKLAND | .1% AT CURB BOX 1' OFF BLDG.; NO LEAK; SOAP TESTED MANIFOLD FOUND NO LEAKAGE; SOAP TEST METERS AND MANIFOLD AND FOUND NO LEAKAGE
| 73-49283-1 |  |  |  | Other |  | Other |  |  | Other |  | 1973-10-10 | 1973-10-11 | Other |  | Other |  | OAKLAND | NO GAS READINGS OR TRACE OF LEAKAGE IN AREA.; NO GAS READINGS OR TRACE OF LEAKAGE IN AREA.
|  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  | 1982-01-26 | 1982-01-27 | Other |  | Steel/Wrought Iron |  | OAK | INST. 2" - 2" - M2'S TO C/O 2" VALVE. TIE-IN-MAIN WITH 2" STL.
|  |  |  | 8 | Distribution Feeder Main |  | Other |  |  | Other |  | 1974-01-02 | 1974-01-02 |  |  | Cast/Ductile Iron
26 | 82-40819- |  |  | 0.04 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1982-01-07 | 1982-01-18 | Clamp |  | Cast/Ductile Iron |  | OAKLAND | INSTALL 4" BJ LEAK CLAMP TO STOP THIS LEAKAGE 280' S/O HUBERT OR GROSVENOR PL.
|  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  | 1975-04-14 |  | Other |  | Steel/Wrought Iron
| 73-20026-1 |  |  |  | Other |  | Other |  |  | Other | NONE |  | 1973-01-15 | Other |  | Other |  |  | NO LEAKAGE
| 73-20178- |  |  | 3 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1973-01-24 | 1973-01-26 |  |  | Steel/Wrought Iron |  | OAKLAND | GREASED VALVE TO STOP LEAKAGE
|  |  |  | 4 | Service |  | Other |  |  | Other |  | 1975-04-17 |  | Other |  | Steel/Wrought Iron
26 | 94-13090-1 |  |  | 6 | Gathering |  | Girth Weld |  |  | Construction Defect |  | 1994-10-24 | 1995-12-28 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | OAKLAND | ARC WELDED CAN OVER 4" PCF (SIDE TAP)
|  |  |  | 3 | Distribution Feeder Main |  | Other |  |  | Other |  | 1975-04-17 |  |  |  | Steel/Wrought Iron
26 | 73-49560- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1973-12-04 | 1973-12-05 | Clamp |  | Steel/Wrought Iron |  |  | USED SKINNER CLAMP TO REPAIR LEAK NEXT TO BUILDING ABOVE SEWER TO HOUSE.
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  |  | 1974-02-13 |  |  | Steel/Wrought Iron
|  |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-03-14 | 1972-03-16 | Patch Welded |  | Steel/Wrought Iron |  |  | PIPE BADLY PITTED ON BOTTOM. LEAKAGE PROBABLY CAUSED BY ROCKY FILL PERMANENT REPAIRS MADE BY WELDER.
|  |  |  | 3 | Distribution Main | [6 empty] | 1976-01-13 |  |  |  | Steel/Wrought Iron |  | OAK. | RERAN SERVICE
| 73-21010- |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1973-01-19 | 1973-07-12 | Other |  | Steel/Wrought Iron |  | OAK
| 73-48083-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-01-18 | 1973-01-29 | Replace Pipe and/or Service |  | Steel/Wrought Iron
R/R 1/2" PLI SERV.
|  |  |  | 12 | Other |  | Other |  |  | Other |  | 1974-07-12 | 1974-07-12 | Replace Pipe and/or Service |  | Steel/Wrought Iron
26 | 73-48288-1 |  |  | 0 | Other |  | Other |  |  | Other |  |  | 1973-03-14 | Other |  | Other |  | OAKLAND | CHECKED AREA WITH GAS DETECTOR AND FLAME PACK. NO LEAKAGE FOUND.
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1973-07-09 | 1973-07-09 |  |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 0.06 | Distribution Feeder Main | [6 empty] | 1972-06-08 |  |  |  | Steel/Wrought Iron |  | OAK
|  |  |  | 2 | Distribution Main | [10 empty] | Steel/Wrought Iron
|  |  |  | 2 | [13 empty] | OAK. | INSTALLED 60 FEET 1/2" PLASTIC SERVICE TO #3515 BUTTERS.
26 | 89-20721-1 |  |  | 2 | Distribution Main |  | Valves |  |  | Other |  | 1989-05-08 | 1990-07-13 | Other |  | Steel/Wrought Iron |  | OAKLAND | GREASED BY VALVE CREW
1 |  |  |  | 8 | Distribution Main |  | Other |  |  | Other |  | 1977-10-19 |  | Replace Pipe and/or Service |  | Cast/Ductile Iron |  | OAKLAND
1 |  |  |  | 6 | Distribution Main |  | Other |  |  | Other |  | 1977-10-19 |  | Replace Pipe and/or Service | ; | Cast/Ductile Iron |  | OAKLAND
1 |  |  |  | 8 | Distribution Main |  | Other |  |  | Other |  | 1977-10-19 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND
1 | 72-48067-A |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-05-10 | 1972-05-10 |  |  | Cast/Ductile Iron |  |  | INSTALL 1 1/4 DRESSER
1 | 72-48065-A |  |  | 4 | Distribution Feeder Main |  | Fitting |  |  | Construction Defect |  | 1972-05-09 | 1972-05-09 |  |  | Cast/Ductile Iron |  |  | INSTALL 5'1" PLASTIC TO STOP LEAKAGE & RESTORE SERVICE NO PAVING
1 | 72-45081-A |  |  | 06LP | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-04-12 | 1972-04-12 |  |  | Steel/Wrought Iron |  |  | MADE PERMANENT REPAIR TO PIPE TO RODDEN TO WELD ON.
| 93-11836-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1993-01-25 | 1993-01-28 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | OAKLAND | INSTALLED TWO HALF SOLE PATCHS - INSTALLED E.T.S. STATION
| 80-48980- |  |  | 16 | Distribution Feeder Main |  |  |  |  | Corrosion |  | 1980-12-30 | 1981-07-02 | Patch Welded |  | Steel/Wrought Iron |  | OAKLAND | FOUND LEAKAGE ON 16' FEEDER MAIN MADE REPAIR ARC WELDER PATCHS MAIN. (MAIN IS HEAVY PITTED)
|  |  |  | 3 | Distribution Feeder Main |  | Other |  | NEW SERV. | Other | NEW SERV. |  | 1972-10-31 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | RAN NEW 1 1/4" SERV. BARE. INSTALLED CURB VALVE WITH 2" COCK. USED 2" PIPE FOR RISER.
|  |  |  | 20 | Transmission |  | Other |  |  | Other |  | 1981-06-25 |  | Other |  | Steel/Wrought Iron |  | OAKLAND
2 |  |  |  | 2 | [13 empty] | OAKLAND
| 72-45259-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-10-12 | 1972-10-13 | Clamp | & CAN | Steel/Wrought Iron |  |  | WRAP IN POOR SHAPE. WATER GETTING UNDER WRAP. WRAP LOOSE.; INST. (1) 48" CAN & (2) PATCHES
| 76-49436- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-11-13 | 1976-12-13 | Other |  | Steel/Wrought Iron |  | OAKLAND | ARC WELDED PATCH ON 2" T.P. MAIN, MAIN IN GOOD CONDITION.
|  |  |  | 8 | Distribution Main |  | Other |  |  | Other |  |  | 1978-08-17 | Other |  | Steel/Wrought Iron |  | OAKLAND | NO WELDING; REPAIRED CONTACT ON GAS MAIN
26 | 86-50023- | 153 |  | 24 | Transmission |  | Valves |  |  | Other |  | 1986-03-31 | 1987-05-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | REPLACED VALVE ON "GAUGE TAP WEST" BY VALVE D-84 CENTER OF 2ND & JEFFERSON
|  | 153 |  | 2 | Transmission | [7 empty] | 1979-02-09 |  |  | Steel/Wrought Iron |  | OAKLAND | TIED 2" PLASTIC INTO 2" STEEL. 2" VALVE D84, BLOCK VALVE BETWEEN T.P & H.P
| 71-00527-1 |  |  | 20 | Other |  | Fitting |  |  | Other |  | 02/03/0000 | 1971-07-28 | Other |  | Steel/Wrought Iron |  | OAKLAND | FOUND BONNET BOLTS LOOSE ON VALVE, TIGHTENED BOLTS TO STOP LEAKAGE.; NO PAVING
26 | 93-23347-1 |  |  | 6 | Transmission |  | Valves |  |  | Construction Defect |  | 1993-08-23 | 1995-01-25 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | OAKLAND | X-38 BYPASSING GREASED & TIGHTEN BLANK HEAD. X-36 LEAKING AT PACKING GREASED.
2 | 88-11051-C |  |  | 8 | Transmission |  | Valves |  |  | Corrosion |  | 1988-12-09 | 1988-12-09 | Other |  | Steel/Wrought Iron |  | OAKLAND | VAULT; REPLACED GASKET OF VALVE
26 | 86-30046-C |  |  | 24 | Transmission |  | Fitting |  |  | Corrosion |  | 1986-05-08 | 1987-08-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | 1/4" METRIC ON LINE 153 LEAKING REMOVED & INSTALLED NEW METRIC NO FURTHER LEAKAGE
26 | 88-10532-1 |  |  | 30 | Transmission |  | Valves |  |  | Corrosion |  | 1988-02-17 | 1988-02-17 | Other |  | Steel/Wrought Iron |  | OAKLAND | VALVE X-39 GREASED
26 | 88-10526-1 |  |  | 30 | Transmission |  | Valves |  |  | Corrosion |  | 1988-02-03 | 1988-02-03 | Other |  | Steel/Wrought Iron |  | OAKLAND | VALVE X-39 GREASED
26 | 92-11617-1 |  |  | 24 | Transmission |  | Valves |  |  | Corrosion |  | 1992-08-18 | 1993-10-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | OAKLAND | TIGHTENED PLUG ON VALVE
|  | 153 |  | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLAND | PROSPECTED MAIN FOR CONTRACTOR AT THIS LOCATION.
| 75-48008- |  |  | 0.75 | Other | BLOWOFF | Body of Pipe |  |  | Corrosion | POOR BACKFILL MATERIAL | 1975-01-02 | 1975-01-02 | Other |  | Steel/Wrought Iron | STEEL |  | INSTALLED 1-3/4" SKINNER LEAK CLAMP ON 3/4" BLOWOFF TO 24" SHP MAIN, 3RD& BRUSH ST. PIPE FAILURE DUE TO POOR BACKFILL MATERIAL.
|  |  |  | 3 | Distribution Feeder Main |  | Other |  | NEW SERV. | Other | NEW SERV. |  | 1972-08-30 | Other | NEW SERV. | Steel/Wrought Iron |  |  | NEW SERV.; RUN NEW 1' PIT SERV. INSTALL CURB VALVE.
|  |  |  | 3 | Distribution Feeder Main |  | Other |  | NEW SERV. | Other | NEW SERV. |  | 1972-10-06 | Other | NEW SERV. | Steel/Wrought Iron |  |  | RAN NEW 1' PIT SERV TO BLDG NO. 1 INSTALLED CURB VALVE
|  |  |  | 0.03 | Distribution Feeder Main | [6 empty] | 1972-05-31 |  | Other |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 2 | Transmission |  | Other |  |  | Other |  | 1974-10-04 | 1974-10-04 | Other |  | Steel/Wrought Iron |  | OAKLAND
26 | 94-24123-1 |  |  | 6 | Transmission |  | Valves |  |  | Material Failure |  | 1994-09-01 | 1995-08-28 | Other |  | Steel/Wrought Iron |  | OAKLAND | GREASED VALVE IN PIT
26 | 94-24124-1 |  |  | 6 | Transmission |  | Valves |  |  | Material Failure |  | 1994-08-01 | 1995-08-28 | Other |  | Steel/Wrought Iron |  | OAKLAND | GREASED VALVE X-39 A/C LEAKAGE IN VALVE PIT; GREASED VALVE X-39 STOPPED LEAKAGE.
|  |  |  | 12 | Distribution Main |  | Other |  |  | Other |  |  | 1976-03-18 | Other |  | Cast/Ductile Iron |  | OAKLAND | C/O 1 1/4 SERVICE
|  |  |  | 24 | Transmission |  | Other |  |  | Other |  | 1973-01-25 |  | Other |  | Steel/Wrought Iron |  |  | TIE IN 2" MAIN
|  |  |  | 24 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | OAKLAND | PROSPECTED MAIN AT THIS LOCATION FOR CONTRACTOR
| 92-11515-1 |  |  | 0.5 | Service |  | Physical/Mechanical Joint |  |  | Digin |  | 1992-06-08 | 1992-06-08 | Replace Pipe and/or Service |  | TR 418 |  | OAKLAND | CUT IN 1' 1/2" PLASTIC TR418 INSTALLED 2 PERMASERT FITTINGS
26 | 94-24121-1 |  |  | 16 | Transmission |  | Valves |  |  | Other |  | 1994-08-01 | 1995-08-15 | Other |  | Steel/Wrought Iron |  | OAKLAND | GREASED VALVE #X46
|  |  |  | 8 | [11 empty] | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 6 | Transmission | [7 empty] | 1981-09-23 | Other | MAIN C/OFF | Steel/Wrought Iron |  |  | CUT/OFF MAIN DUE TO FUTURE DEMOLITION OF BLDGS.
|  |  |  | 4 | Transmission | [7 empty] | 1986-10-09 |  |  | Steel/Wrought Iron |  | OAKLAND | REPLACED DFM VALVE ON T.P 4" BRIDLE.
26 | 94-24117-1 |  |  |  | Transmission |  | Valves |  |  | Other |  | 1994-07-29 | 1995-08-15 | Other |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 4 | Distribution Feeder Main |  | Other |  | NEW SERV | Other | NEW SERV |  | 1972-08-31 | Other | NEW SERV | Steel/Wrought Iron
1 |  | 105B |  | 30 | Transmission |  | Other |  |  | Other |  | 1976-02-27 |  |  |  | Steel/Wrought Iron
26 | 95-50201-1 | [10 empty] | 1995-06-27 | [5 empty] | OAKLAND
26 | 97-26751-1 |  |  | 12 | Transmission |  | Fitting |  |  | Other |  | 1997-06-12 | 1998-07-14 | Other |  | Steel/Wrought Iron |  | OAKLAND | GREASE; GREASE VALVE FITTING TO STOP LEAK.
26 | 97-26750-1 |  |  | 12 | Transmission |  | Fitting |  |  | Other |  | 1997-06-12 | 1998-07-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | OAKLAND | RE-DOPED PLUG ON VALVE IN HOPE.
|  |  |  | 20 | Transmission | [12 empty] | OAKLAND
|  |  |  | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 3 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1973-04-05 | Other |  |  |  |  | GM474101-1224-1000 INST. 4" MAIN
|  |  |  | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | INSPECTION ONLY; EXPOSED MAIN FOR MAPPING PURPOSE 1603 #10
|  |  |  | 8 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1972-12-01 | Patch Welded |  | Steel/Wrought Iron |  |  | STEAM CUT OFF; C/O 2" STEAM SERV. AT MAIN
|  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  |  | 1977-01-27 | Other |  | Cast/Ductile Iron |  |  | NOT NEEDED; CHECK 4" ci MAIN FOR LEAKAGE ALSO HAD TO TIE UP MAIN A/C. CONTRACTOR. INST. P.T.T. MANHOLE
| 75-48175- |  |  | 4 | Other | MAIN NOT IN USE | Bell Joint |  |  | Material Failure |  | 1975-03-03 | 1975-03-11 | Other | BUT OFF 278' OF 4" C.I. |  |  | OAKLAND | WO 4589B-75; NONE; INST. TWO 4" LINE STOPPERS AND CUT OFF 278' OF 4" MAIN, WHICH WAS NOT REQUIRED IN THE SYSTEM FROM 11TH ST TO 10TH ST. (1) LINE STOPPER ON 11TH ST IS 25' E/WL OF WASHINGTON. 21' OUT S/S OF 11TH ST. (2) 25' N/SL OF 10TH ST. 21' E/WL OF WASHINGTON. 14 M.D.
|  |  |  | 20 | Distribution Feeder Main |  | Other |  | C/T | Other | C/T |  | 1976-10-06 | Other | C/T | Steel/Wrought Iron |  | OAKLAND | #1425 HARRISON; NO NUMBER REQ. ; CT & T SERV. AT THIS LOCATION - MAIN IN GOOD SHAPE
|  |  |  | 4 | Distribution Feeder Main |  | Other |  | NEW SERV. | Other | NEW SERV. |  | 1972-10-17 | Other | NEW SERV. | Cast/Ductile Iron |  |  | RAN NEW 2" STEEL SERV. INSTALLED METER BOX IN SIDEWALK
|  |  |  | 2 | Service |  | Other |  |  | Other |  | 1977-06-07 | 1977-06-07 |  |  |  |  | OAK | ALTER SERV. 1622 - HARRISON; C.P.A WORK; ALTER SERV A/C C.P.A. CONTACT BROWGHT REG & RISEN TO OUTSIDE LOCATION
|  |  |  | 6 | Distribution Main |  |  |  |  | Other |  |  |  | Other |  |  |  | OAKLAND
|  |  |  | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLAND | ;
| 82-00070-F |  |  | 0.5 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1982-02-02 | 1982-02-02 | Patch Welded |  |  |  | OAKLAND | INSD. 1) 1/2 AM FITTING TO RESTOR SERVICE
| 76-49009- |  |  | 2 | Other | MANIFOLD | Body of Pipe |  |  | Corrosion |  | 1976-09-13 | 1976-09-13 | Replace Pipe and/or Service | REPLACED 2" MANIFOLD | Steel/Wrought Iron |  | OAKLAND | NO NUMBER NEEDED; METER LOCATION NOT EXPOSED; REPLACED 2" MANIFOLD
26 | 73-40033- |  |  | 16 | Other |  | Bell Joint |  |  | Corrosion |  | 1973-02-07 | 1973-02-09 | Clamp |  | Cast/Ductile Iron |  | OAKLAND
1 |  |  |  | 4 | Distribution Feeder Main | [7 empty] | 1976-07-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND
1 |  |  |  | 4 | Distribution Feeder Main |  |  |  |  | Other |  |  | 1976-07-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND
| 71-40025-2 |  |  | 4 | Distribution Main |  | Physical/Mechanical Joint |  |  | Other |  | 07/08/0000 | 1971-05-06 | Other |  | Steel |  | OAKLAND | INSTALLED 18" CAN OVER LOCK RING COUPLING AND WELDED 3"x3" PATCH OVER LARGE PIT HOLE IN STEEL MAIN.; INSTALLED 18" CAN OVER 4" INCH LOCK RING C.I. TO STEEL COUPLING; WELDED 3"x3" PATCH OVER LARGE PIT HOLE; 3"x3" PATCH OVER PIT HOLE; INSTALLED 18" CAN OVER LOCK RING C.I. TO STEEL COUPLING; CAST IRON MAIN & STEEL MAIN BOTH LOOK IN GOOD SHAPE.
| 71- |  |  | 4 | Other |  | Bell Joint |  |  | Corrosion |  |  | 1971-04-30 | Bell Joint Clamp |  | Copper |  | OAK. | BELL JOINT LEAKING- INSTALLED BELL JOINT CLAMP
| 71-40025- |  |  | 4 | Distribution Main |  | Bell Joint |  |  | Corrosion |  |  | 1971-07-23 | Bell Joint Clamp |  | Copper |  |  | REMOVED OLD BALL CLAMP AND INSTALLED ONE 4" TO STOP LEAKAGE
1 |  |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Material Failure | [5 empty] | Other Plastic |  | OAKLAND | R/R SERV
2 |  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  | 1982-01-26 | 1982-01-26 |  |  | Steel/Wrought Iron |  | OAKLAND | INSTALL 2-2" MD'S AND REMOVED 2" VALVE.; INSTALLED 2-2" M2'S AND BY PASS DUE TO D-E MAIN. C/O 2" VALVE THAT WAS DAMANGED
| 72-40280-1 |  |  | 3 | Service |  | Other |  |  | Other |  |  | 1972-08-22 | Other |  | Steel/Wrought Iron
| 73-49164- |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-09-06 | 1973-09-06 | Patch Welded |  | Steel/Wrought Iron |  |  | ARCED METAL PATCH
| 73-49163- |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-09-06 | 1973-09-06 | Patch Welded |  | Steel/Wrought Iron |  |  | ARCED METAL PATCH
| 73-49165- |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-09-06 | 1973-09-06 | Patch Welded |  | Steel/Wrought Iron |  |  | ARCED METAL PATCH
| 73-49162- |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-09-06 | 1973-09-06 | Patch Welded |  | Steel/Wrought Iron |  | ; | ARCED METAL PATCH
| 73-49166- |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-09-06 | 1973-09-06 | Patch Welded |  | Steel/Wrought Iron |  |  | ARCED METAL PATCH
| 73-49161- |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-09-06 | 1973-09-06 | Patch Welded |  | Steel/Wrought Iron |  |  | ARCED METAL PATCH
| 73-49160- |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-09-06 | 1973-09-06 | Patch Welded |  | Steel/Wrought Iron |  |  | ARCED METAL PATCH
| 73-49157- |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-09-06 | 1973-09-06 | Patch Welded |  | Steel/Wrought Iron |  |  | ARCED METAL PATCH
| 73-49158- |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-09-06 | 1973-09-06 | Patch Welded |  | Steel/Wrought Iron |  | ; | ARCED METAL PATCH
| 73-49156- |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-09-06 | 1973-09-06 | Patch Welded |  | Steel/Wrought Iron |  |  | ARCED METAL PATCH
| 73-49155- |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-09-06 | 1973-09-06 | Patch Welded |  | Steel/Wrought Iron |  |  | ARCED METAL PATCH
| 73-49154- |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-09-06 | 1973-09-06 | Patch Welded |  | Steel/Wrought Iron |  |  | ARCED METAL PATCH
1 | 79-48858- |  |  | 0.5 | Service |  | Body of Pipe |  |  | Other | COMPANY EMPLOYEE | 1979-10-29 | 1979-10-29 | Replace Pipe and/or Service |  | Copper |  | OAKLAND
|  |  |  | 0.02 | Distribution Feeder Main | [6 empty] | 1972-06-19 |  |  |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  |  | 1973-04-19 |  |  | Steel/Wrought Iron |  |  | R/R 1/2" PL7 INSERT TO 3843 PARK BLVD. ;
25 | 77-49103- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1977-10-20 | 1977-10-28 | Clamp |  | Steel/Wrought Iron |  | OAKLAND | MAIND SHOULD BE REPLACED A.S.A. SEVERAL TEMP REPAIRS.. MUI BEED MADE WITH IN ONE BLOCK.
|  |  |  | 1.14 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1973-09-06 | Other |  | Other Plastic |  | OAKALND | NO LEAK AT MAIN
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1974-05-28 | 1974-05-28 | Other |  | Steel/Wrought Iron |  | OAKLAND | R/R SERVICE
| 72-40268- |  |  | 0.75 | Other | SERVICE TEE | Fitting |  |  | Material Failure |  | 1972-06-26 | 1972-10-27 | Replace Pipe and/or Service |  | Steel |  |  | FOUND LEAK AT THIS LCATION OF 3/4" SERV. TEE; REPLACED SCREWED FITTING OF OLD ASANDONED SERVICE TEE
26 | 72-40219-1 |  |  |  | Other |  | Other |  |  | Other |  | 1972-06-01 | 1972-10-06 | Other |  | Other |  |  | LEAK ON 3/4" MAIN BELOW REG. SHUT DOWN 3 CUSTOMER AND PUT IN 2 NEW 3/4" MAIN AND WAS INSULATIONED AND RETIGHTE CUSTOMERS BACK UP. LEAK WAS IN METER BOX IN STREET.; LEAK NEW UNION TO MAKE REPAIRS TO SERV LINE.
|  |  |  | 6.9 | Distribution Feeder Main |  | Other |  |  | Other |  | 1973-02-22 |  | Replace Pipe and/or Service |  | Cast Iron |  | OAKLAND
1 |  |  |  | 1.25 | Distribution Feeder Main |  | Other |  |  | Other | [5 empty] | Other Plastic |  | OAKLAND
28 | 89-20028-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1989-02-22 | 1989-09-28 | Patch Welded |  | Steel/Wrought Iron |  | BERKELEY | ON MAIN AT DRIVEWAY; INSTALL PATCH WELD 3' E/O P.C.F.
28 | 90-80397 | 105A |  | 16 | Transmission |  | Longitudinal Weld |  |  | Corrosion |  | 1990-11-06 | 1990-11-06 | Patch Welded |  | Steel/Wrought Iron |  | BERKELEY | INST. WEDDING BAN AND HALF SOLE.
28 | 90-20055-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1990-01-23 | 1990-01-23 | Other |  | Steel/Wrought Iron |  | BERKELY | FOUND LEAK ON VALVE IN REG. PIT. REFER TO M & C DEPARTMENT. TIGHTEN VALVE ON SERV.
28 | [12 empty] | 1990-03-28 |  |  | Wrought Iron |  | BERKELY | LOWERED 10' OF 16" T.P. FOR CONFLICT WITH SEWER CROSSING.
|  |  |  | 16 | [11 empty] | Steel/Wrought Iron |  | BERKELEY
28 |  |  |  | 16 | [8 empty] | 1990-03-28 |  |  | Steel/Wrought Iron |  | BERKELEY | WELDED 4" VALVE TO 16" T.P. FOR A BLOW OFF POINT FOR SHUT DOWN OPERATIONS. TO GO ALONG WITH LOWERING MAIN AT NINTH AND HEINZ.
1 | 71-00342-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1971-05-11 | 1972-01-03 | Other |  | Steel/Wrought Iron |  | ; BERKELEY | FOUND VALVES LEAKING. GREASED VALVE STOPPED LEAKAGE.
28 | 73-60194-1 |  |  | 3 | Distribution Feeder Main |  | Valves |  |  | Damage by outside Forces |  | 1973-07-26 | 1973-08-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | INST. CAN OVER LEAKING 3" VALVE TO STOP LEAKAGE.
28 | 97-21150-1 |  |  | 3 | Distribution Main |  | Valves |  |  | Other |  | 1997-09-07 | 1997-09-17 | Other |  | Steel/Wrought Iron |  | BERKELEY | GREASED VALVE
28 | 93-35029-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1993-11-09 | 1993-12-01 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | BERKELEY | WELDED CAN ON MAIN
28 | 84-40426-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-10-22 | 1984-10-22 | Other |  | Steel/Wrought Iron |  |  | INST. CHAIN CLAMP. TEMP. PATCH WELDED LEAK. D. HARRISON.
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1979-04-20 |  | Other |  | Steel/Wrought Iron |  | BERK
28 | 97-21152-1 |  |  | 24 | Transmission |  | Valves |  |  | Other |  | 1997-09-17 | 1999-08-17 | Other |  | Steel/Wrought Iron |  | BERKELEY | ALREADY COMPLETED (VALVE GREASED BY M & c DEPARTMENT LONG AGO).
28 | 90-20001-1 |  |  | 24 | Transmission |  | Valves |  |  | Other |  | 1990-01-11 | 1990-09-28 | Other |  | Steel/Wrought Iron |  | BERKELEY | TIGHTENED AND GREASED VALVE TO REPAIR LEAKAGE.; EVERYTHING CROSSED OUT;
28 | 82-20099-1 |  |  | 2 | Other |  | Other Welds |  |  | Other |  | 1982-02-02 | 1983-02-18 | Other |  | Steel/Wrought Iron |  | BERKELEY | REPAIRED LEAK ON METER SET 2-18-83
28 | 86-20074-1 |  |  | 16 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1986-02-25 | 1986-02-25 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | BERKELEY | WELDED (2) PATCHES ON TP MAIN AT GC ABOVE
|  |  |  | 4 | Other | [7 empty] | 1972-04-24 |  |  | Steel/Wrought Iron |  |  | CUT OFF 2 - 2" H.P. SERVICES
| 80-60015- |  |  | 0.5 | Service |  | Body of Pipe | Valves |  | Material Failure |  | 1980-01-16 | 1980-01-16 | Other |  | Other Plastic |  | BERKELEY | REPLACED 6" SECTION OF PLASTIC SERVICE AND INSTALLED TWO AMP AT COUPLING CLOSE TO RISER.
28 | 96-21076-1 |  |  | 3 | Distribution Main |  | Valves |  | GREASED | Other |  | 1996-02-15 | 1997-05-06 | Other |  | Steel/Wrought Iron |  |  | FOUND NO LEAK WITH FLAME PAC....GREASED
|  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1973-03-28 |  |  |  | Steel/Wrought Iron
28 | 92-00037-1 |  |  | 2 | Transmission |  | Valves |  |  | Other |  | 1992-01-27 | 1992-12-09 | Other |  | Steel/Wrought Iron |  | BERKLEY | REPLAIRED BLOW DOWN STACK AND VALVE IN PIT.
28 | 93-80492-1 |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1993-11-30 | 1993-11-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | BERKELEY | ISNTALLED 3' OF HALF SOLE PIPE.
28 |  |  |  | 16 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | BERKLEY | DONE ON WO42269B-84
28 |  |  |  | 16 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | BERK | DONE ON WO47269B-84
28 |  |  |  | 16 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | BERKLEY | DONE ON WO47269B-84
28 |  |  |  | 16 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | BERKLEY | DONE ON WO47269B-84
28 |  |  |  | 16 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | BERKELEY | DONE ON WO47269B-84
28 |  |  |  | 16 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | BERKELEY | DONE ON WO47269B-84
28 | 92-20020-1 |  |  | 16 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1992-01-29 | 1992-01-29 | Patch Welded |  | Steel/Wrought Iron |  | BERK | WELDED TWO PATCHES ON MAIN.
|  |  |  | 16 | Distribution Feeder Main | [7 empty] | 1974-11-18 |  | MAIN INSPECTION | Steel/Wrought Iron |  | BERKELEY | MAIN INSPECTION THIS TIE-IN LOCATION. INSTALLED 2" VALVE AND TERMINATED ANODE. LOCATING WIRES IN 8" V/F & C; TIE IN OF 2" PL MAIN THIS LOCATION
28 | 92-80211-1 |  |  | 4 | Distribution Feeder Main |  | Tap Connection |  |  | Construction Defect |  | 1992-07-13 | 1992-09-11 | Patch Welded |  | Steel/Wrought Iron |  | BERK | WELD SHUT PINHOLE ON 4" LSF
28 | 85-20034-1 |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1985-01-31 | 1985-01-31 | Bell Joint Clamp |  | Cast Iron |  | BERKELEY | 301 ON BELL JOINT. INST. BELL CLAMP 2-1-85 PERM REP. VEGA.
28 | 95-80185-1 |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1995-07-03 | 1995-07-06 | Patch Welded |  | Steel/Wrought Iron |  | BERKELEY | MEND HALF SOLE ON CORROSION LEAK
28 |  |  |  | 3 | Distribution Feeder Main |  | Other Welds |  |  | Construction Defect |  | 1973-07-13 | 1973-07-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | BERKELEY
28 | 74-20098-1 |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1974-07-26 | 1974-11-11 | Other |  | Cast Iron |  | BERKELEY | CAUTION: E.B.M.U.D. IN AREA; FOUND SMALL FUZZ LEAK ON 3/4" FTG AT METER LOCATION PERM REPAIR MAINTAINED.
|  |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  | 1980-03-11 | 1980-03-11 | Patch Welded |  | Steel/Wrought Iron
|  |  |  | 16 | Distribution Main | [7 empty] | 1977-04-08 |  |  | Steel/Wrought Iron |  | BERKELEY
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  |  | 1978-09-08 | Bell Joint Seal |  | Steel/Wrought Iron |  | BERKELEY | INSTALLED NEW SERVICE
28 | 84-60081-1 |  |  | 30 | Transmission | [6 empty] | 1984-05-25 |  |  |  | Steel/Wrought Iron |  | BERK. | DRILLED HOLES OVER MAIN TO VENT TO ATMOSPHIRE. DUG DRY HOLE OVER 30" T.P.
28 | 84-60081-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1984-05-25 | 1984-06-04 | Clamp |  | Steel/Wrought Iron |  | BERKELEY | INST. ONE 4" 2-BOLT SKINNER LEAK CLAMP
28 | 77-40098-F |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1977-03-24 | 1977-03-24 | Patch Welded |  | Steel/Wrought Iron |  |  | LEAK ON 4" T.P. MAIN TEMP. CLAMPS MADE PERM REPAIRS 3/25/77
28 | 82-20004-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1982-01-14 | 1982-12-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | BERKELEY | REPLACED 4' OF 4" STEEL PIPE TO MAKE PERMANENT REPAIRS; PIPE WAS STRENGTH TESTED ON 3-2-82 PER WO 43531-A; REPLACED 4' OF 4" STEEL TESTED PIPE TO MAKE REPAIRS TO T.P. MAIN LEAKING ON WELD (CORROSION)
28 | 98-21006-1 |  |  | 2 | Service |  | Girth Weld |  |  | Corrosion |  | 1998-01-27 | 1998-01-27 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | BERKELEY | ON ELBOW CUTLET SIDE OF INLET VALVE TRANSMISSION PRESSURE SHUT DOWN SERVICE & WELDED ELBOW.; SHUT DOWN TRANSMISSION (HIGH TO HIGH) METER SET TO REWELD LEAKING 2" ELBOW. LEAKAGE DUE TO CORROSION AT WELD
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1976-10-19 |  |  |  | Wrought Iron |  | BERKELEY
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1976-10-19 |  |  |  | Steel/Wrought Iron |  | BERKELEY
28 |  |  |  | 16 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | BERKELEY
28 | 93-35049-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1993-11-23 | 1994-02-01 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | B | INSTLLED 2' OF HALF SOLE OVER LEAKING PITTS
| 78-20613-1 |  |  | 3 | Distribution Main |  | Valves |  |  | Material Failure |  | 1978-05-03 | 1978-05-31 | Other |  | Steel/Wrought Iron |  | BERKELEY | REPAIRED 301 ON METER VALVE IN VALVE FRAME AND COVER. FOUND NO OTHER LEAK AT THIS TIME.; NO DIGGING REQUIRED TO FIX LEAK NO PAVING REQUIRED.
28 | 72-40225-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-04-24 | 1972-05-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | BERKELEY | REPLACE TWO 1 1/4" SERVICE WITH 1" PLASTIC. THESE SERVICE WERE BALANCING ALL OF THE SERVICES SHOULD OR RETURN IN...BLOCK AND SOME BELL JOINTS MAY BE LEAKING...REACHING ALL ALONG THE BLOCK.
28 |  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | BERKELEY | 1 1/4" SERV. TO 339 GROVE ST. LOCATING BONDED TO RISER, WRAPED AROUND SERV. TEE, 9LB ANODE BONDED TO 1 1/4STL. RISER.
28 | 77-40177-1 |  |  | 0.5 | Service |  | Other Welds |  |  | Corrosion |  | 1977-06-10 | 1977-06-10 | Replace Pipe and/or Service |  | Copper |  | BERKELEY | INSPECTION REPORT A/C RERUN SERVICE. INSPECTION REPORT A/C RERUN SERVICE
28 |  |  |  | 6 | Distribution Feeder Main | [7 empty] | 1983-05-31 |  |  | Steel/Wrought Iron |  | PINOLE | INSPECTED MAIN WHILE INSTALLING NEW SERVICE.
28 | 87- -1 |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  | 1987-03-26 | 1987-03-26 | Other | PROSPECT | Steel/Wrought Iron |  | PINOLE | PROSPECT 6" GAS MAIN FOR DEPTH. MAIN IS 32" BELOW EXISTING R.C.F.
|  |  |  | 8 | Distribution Feeder Main | [7 empty] | 1972-09-27 |  |  | Steel/Wrought Iron |  | PINOLE
|  |  |  | 6 | Distribution Feeder Main | [7 empty] | 1973-07-05 |  |  | Steel/Wrought Iron |  | PINOLE | RE CONNECTED 3/4" SERV. AND EXTENDED IT 160' TO NEW BUILDING USING 1 1/4" STL
| 76-40152- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-04-16 | 1976-05-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PINOLE | INSERTED 14' OF 11/4" PL. THROUGH OLD STL. 2" MAIN AT THIS LOCATION. MAIN WAS BURIED IN CONCRETE AROUND STORM DRAIN AND LEAKING. NO WAY TO RUN STEEL MAIN AROUND THIS LOCATION.
28 | 89-25004-1 |  |  | 22 | Transmission |  | Other Welds |  |  | Other |  | 1989-03-23 | 1989-03-27 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | CROCKETT | WELD OVER LEAKING PATCH ON 22" TP MAIN. LOWERED PRESURE TO MAKE WELD
28 |  | 2 |  | 22 | [8 empty] | 1988-03-03 |  |  | Steel/Wrought Iron |  | CROCKETT | INSTALLED 2 -#10 WIRES TO MAIN AND TERMINATED M&O ETS
28 |  |  |  | 22 | [8 empty] | 1988-03-03 |  |  | Steel/Wrought Iron |  | CROCKETT | CAD WELDED 2-#13 TAN WIRES TO 22" STAN PAC MAIN AND TERMINATED WIRES INTO GS WFC
28 | 74-40424-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-06-28 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CROCKETT | RERUN OLD LEAKING 3/4" STEEL SERVICE WITH 1/2" PLASTIC USING OLD PIPE AS CASING
28 | 77-60346-1 |  |  | 0.5 | Service |  | Other Welds |  |  | Material Failure |  | 1977-09-15 | 1977-09-15 | Other |  | Copper |  | PORT COSTA | REPAIRED 1/2" COPPER SERVICE AT ECLIPSE FTG.
26 | 90-10473-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1990-09-13 | 1990-11-07 | Other |  | Steel/Wrought Iron |  | OAKLAND | GRAY TAPE 15' OF 2" STL. MAIN JOB BEING PREPAIR TO TRANFER ALL SERVICE TO TP MAIN. (CUT OFF MAIN AT MARKET & BAKER ST.)
1 | 72-60049-A |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-08-23 | 1972-08-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | INSTALL 3" 6" PATCHES TO STOP THIS LEAKAGE
26 | 86- |  |  | 1.25 | Other | M | Body of Pipe |  |  | Digin |  | 1986-07-30 | 1986-07-30 | Replace Pipe and/or Service |  | Aldyl A (Tan or Gray)
26 | 76-48292- |  |  | 1.12 | Other |  | Body of Pipe |  |  | Corrosion |  | 1976-03-12 | 1976-04-16 | Other |  | Steel/Wrought Iron |  | OAKLAND | LEAK FROM HOUSLINE FOLLOWING SEWER NEXT TO MAIN DUG 5 DRY HOLES OVER 16" C.F. MAIN AND 2 DRY HOLES OVER PLASTIC SERV. FOUND LEAK ON 1 1/2" HOUSING SHUT DOWN METER AND NOTIFIED OAKLAND PUBLIC SCHOOL TO MAKE REPAIRS
|  |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  |  | 1973-05-04 | Bell Joint Clamp Replacement |  | Cast Iron |  |  | REPLACED 16" BJ LEAK CLAMP
|  |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  |  | 1973-05-04 | Bell Joint Clamp Replacement |  | Cast Iron |  |  | REPLACED 16" BELL JOINT LEAK CLAMP
|  |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  |  | 1973-05-07 | Bell Joint Clamp Replacement |  | Cast Iron |  |  | REOKACED 16" BELL JOINT LEAK CLAMP
|  |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  |  | 1973-05-04 | Bell Joint Clamp Replacement |  | Cast Iron |  |  | REPLACED 16" BELL JOINT LEAK CLAMP
|  |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  |  | 1973-05-04 | Bell Joint Clamp Replacement |  | Cast Iron |  |  | REPLACED 16" BELL JOINT LEAK CLAMP
|  |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  |  | 1973-05-07 | Bell Joint Clamp Replacement |  | Cast Iron |  |  | REPLACED 16" BELL JOINT LEAK CLAMP
|  |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  |  | 1973-05-07 | Bell Joint Clamp Replacement |  | Cast Iron |  |  | REPLACED 16" BELL JOINT LEAK CLAMP
|  |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  |  | 1973-05-08 | Bell Joint Clamp Replacement |  | Cast Iron |  |  | REPLACED 16" BELL JOINT LEAK CLAMP
|  |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  |  | 1973-05-08 | Bell Joint Clamp Replacement |  | Cast Iron |  |  | REPLACED 16" BELL JOINT LEAK CLAMP
|  |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  |  | 1973-05-09 | Bell Joint Clamp Replacement |  | Cast Iron |  |  | REPLACED 16" BELL JOINT LEAK CLAMP
|  |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  |  | 1973-05-08 | Bell Joint Clamp Replacement |  | Cast Iron |  |  | REPLACED 16" BELL JOINT LEAK CLAMP
|  |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  |  | 1973-05-03 | Bell Joint Clamp Replacement |  | Cast Iron |  |  | REPLACED 16" BELL JOINT LEAK CLAMP
|  |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  |  | 1973-05-09 | Bell Joint Clamp Replacement |  | Cast Iron |  |  | REPLACED 16" BELL JOINT LEAK CLAMP
| 80-20587- |  |  | 16 |  |  | Bell Joint |  |  | Material Failure |  | 1980-03-04 | 1980-03-04 | Other | REPLACED LEAKING CLAMP WITH AVON SEAL | Cast Iron |  |  | REPLACED LEAKING B.J. LEAKING CLAMP WITH AVON SEAL AC. PAVING 5', P" X 7' 7"
| -48212- |  |  | 16 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1980-03-04 | Other | AVON SEAL | Cast Iron |  |  | REPLACED OLD RUSTED LEAK CLAMP WITH ONLY 2-BOLTS THERES AND ROTED OUT WITH AVON SEAL; NO LEAK NO.
|  |  |  | 16 | Other |  | Other |  |  | Other |  |  | 1975-04-10 | Other |  | Cast Iron
| 80-00027- |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1980-03-31 | 1980-03-31 | Weld Over Sleeve or Can | AVON SEAL | Cast Iron |  | OAKLAND | REPLACED LEAKING BELL JOINT CLAMP WITH AVON SEAL.
| 80-00027- |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1980-03-31 | 1980-03-31 | Other | AVON SEAL | Cast Iron |  | OAKLAND | REPLACED LEAKING BELL JOINT CLAMP WITH AVON SEAL
| 80-48214- |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  |  | 1980-03-31 | Other | AVON SEAL | Cast Iron |  | OAKLAND | REPLACED LEAKING BELL JOINT CLAMP WITH AVON SEAL
| 80-48214-F |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1980-03-06 |  | Other | PUNCH HOLES TO AIR OUT BELL JOINT | Cast Iron |  | OAKLAND | FOUND SERVERAL BELL JOINT LEAKING ON 16" ...C.I. MAIN BELL JOINT SHOULD BE CLAMP. DRY HOLE OVER TELEPHONE LINE TO AIR OUT.
| 80-48097-F |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1980-03-10 | 1980-03-31 | Other | PUNCH HOLES BELL JOINT TO AIR OUT | Cast Iron |  |  | FOUND SEVERAL LEAKAGE OVER 16" SHP. C.I. MAIN BELL JOINT SHOULD BE CLAMP. DRY HOLE OVER TELEPHONE LINE TO AIR OUT GAS.
| 80-48097- |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1980-03-31 | 1980-03-31 | Other | AVON SEAL | Cast Iron |  | OAKLAND | REPLACE LEAKING BELL JOINT CLAMP, WITH AVON SEAL
| 80-00025-1 |  |  | 4 | Other |  | Fitting |  |  | Other |  | 1980-11-24 | 1980-11-24 | Other |  | Steel/Wrought Iron |  | OAKLAND | TIGHTENED BRASS PLUG AND CAP ON 3/4" SABRENIPPLE (LEAKING) STOPPED LEAKAGE.
|  |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  |  | 1973-05-09 | Bell Joint Clamp Replacement |  | Wrought Iron |  |  | REPLACED 16" BELL JOINT LEAK CLAMP
|  |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  |  | 1973-05-10 | Bell Joint Clamp Replacement |  | Cast Iron |  |  | REPLACED 16" BELL JOINT LEAK CLAMP
|  |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  |  | 1973-05-10 | Bell Joint Clamp Replacement |  | Cast Iron |  |  | REPLACED 16" BELL JOINT LEAK CLAMP
|  |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  |  | 1973-05-10 | Bell Joint Clamp Replacement |  | Cast Iron |  |  | REPLACED 16" BELL JOINT LEAK CLAMP;
|  |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  |  | 1973-05-09 | Bell Joint Clamp Replacement |  | Cast Iron |  |  | REPLACED 16" BELL JOINT LEAK CLAMP
|  |  |  | 8 | Distribution Main |  | Other |  |  | Other |  | 1974-08-27 |  | Other |  | Cast Iron
26 | 72-05095-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-05-05 | 1972-05-24 |  |  | Steel/Wrought Iron |  |  | INSTALL 12" L.C. TO STOP LEAKAGE TO ...TO WELD ON;
| 73-55209- |  |  | 8 | Distribution Feeder Main |  | Other |  | BLOW OFF (2') | Material Failure | 8" DRESSER |  | 1973-04-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | CUT OUT 8" DRESSER AND 2" BLOW OFF. INST. 3" FT OF 8" PIPE TO TIE-IN MAIN AGAIN
| 75-48772- |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  |  | 1975-09-30 | Patch Welded |  | Steel/Wrought Iron |  | OAKALND | ARC WELDED TWO PATCHES ON 2" T.P. 5' W.W.L CYPRESS ST. 28' OUT N/S OF 5TH ST.
| 75-48772- |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1975-09-30 | Other | NO LEAK | Steel/Wrought Iron |  | OAKLAND | FOUND 60% GAS READINGS IN SIDEWALK. DUG BELL HOLE OVER 2" T.P. MAIN FOUND NO LEAK, 6' OUT S/S OF 5THST. 5' W/WL OF CYPRESS ST.
|  |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Other |  | 1973-02-08 | 1973-02-20 | Replace Pipe and/or Service |  | Cast Iron |  | OAKLAND
|  |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Other |  | 1973-02-08 | 1973-02-20 | Replace Pipe and/or Service |  | Cast Iron |  | OAKLAND
26 | 72-45051- |  |  | 4 | Other | I | Bell Joint |  |  | Corrosion |  | 1972-05-26 | 1972-06-23 | [5 empty] | CUT OUT 2 BELL JOINTS AND REPLACED SECTION ON C.I. MAIN WITH 10' OF 4" STEEL PIPE.
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1976-09-13 | Other |  | Steel/Wrought Iron |  | OAKLAND | MAIN IN POOR CONDITION BUT WELD ABLE EXPOSED A/C NEW SERVICE
|  |  |  | 6 | Distribution Feeder Main | [7 empty] | 1977-06-09 |  |  | Steel/Wrought Iron |  | OAKALND | CANNED 6" DRESSER COUPLING HERE FOR C.P.A. PURPOSES
26 | 77--1 |  |  | 6 | Transmission |  | Other |  | CPA CLEAR CONTACT | Other | NO LEAK | 1977-10-10 | 1977-10-10 | Other |  | Steel/Wrought Iron |  | OAKAND | EXPOSED 6" T.P. GAS MAIN TO CLEAR WATER AND GAS MAIN CONTACT.
1 |  |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1981-05-02 | 1981-07-06 |  |  | Cast Iron |  | OAKALND | C.I. MAIN
| 81-10052- |  |  | 1.25 | Service |  | Fitting |  |  | Material Failure |  | 1981-04-02 | 1981-06-17 | Other | TIGHTEN FITTING | Steel/Wrought Iron |  | OAKLAND | TIGHTEN UP NUT ON BACK OF IT SERVICE VALVE DUE TO LEAKAGE
26 | 77-49185- |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1977-11-14 | 1977-11-14 | Clamp |  | Steel/Wrought Iron |  | OAK. CAL. | FOUND LEAKAGE ON THE MAIN, INST. 1-3" CLAMP TO STOP LEAKAGE.
26 | 80-48959- |  |  | 6 | Distribution Feeder Main |  | Fitting |  |  | Material Failure |  | 1980-12-22 |  | Bell Joint Clamp |  | Cast Iron |  | OAK | INST. 6" BELL JOINT LEAK CLAMP TO STOP THE LEAK
|  |  |  | 6 | Distribution Main |  | Fitting |  |  | Corrosion |  | 1978-10-20 | 1978-10-25 | Replace Pipe and/or Service |  | Cast Iron
|  |  |  | 6 | Other | CI | Other |  |  | Other |  | 1979-07-11 | 1973-07-11 | Other |  | Other Plastic
|  |  |  | 20 | Transmission | [7 empty] | 1974-08-23 |  |  | Steel/Wrought Iron |  |  | REMOVED VALVE D-18 AND CANNED A 2' PREASSEMBLED PCF
|  |  |  | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | MAIN PROSPECT ONLY
26 | 75- -1 |  |  | 20 | Distribution Feeder Main |  | Other |  |  | Other |  | 1975-07-16 | 1975-07-16 | Other |  | Steel/Wrought Iron |  |  | ISNT. LEAD WIRE FOR CATHODIC PROTECTION
| 74-00711- |  |  | 8 | Distribution Main |  | Bell Joint |  |  | Material Failure |  |  |  | Bell Joint Clamp |  | Cast Iron
|  |  |  | 4 | Distribution Main |  | Bell Joint |  |  | Other | [5 empty] | Cast Iron
|  |  |  | 4 | Distribution Main |  | Bell Joint |  |  | Other | [5 empty] | Cast Iron
|  |  |  | 4 | Distribution Main |  | Bell Joint |  |  | Other |  |  |  | Bell Joint Clamp Replacement |  | Cast Iron
|  |  |  | 4 | Distribution Main |  | Bell Joint |  |  | Other |  |  |  | Bell Joint Clamp Replacement |  | Cast Iron
|  |  |  | 4 | Distribution Main |  | Bell Joint |  |  | Other |  |  |  | Bell Joint Clamp Replacement |  | Cast Iron
26 | 73-21181-1 |  |  |  | Other | CURB METER | Meter |  |  | Other | LOOSE DIAL FACE ON METER | 1973-08-27 | 1973-11-12 | Other | TIGHTENED LOOSE DIAL FACE |  |  |  | MAIN UN SERVICE NOT EXPOSED TIGHTENED LOOSE DIAL FACE METER
|  |  |  | 8 | Distribution Main |  | Bell Joint |  |  | Other |  |  |  | Bell Joint Clamp Replacement |  | Cast Iron
|  |  |  | 8 | Distribution Main |  | Bell Joint |  |  | Other |  |  |  | Bell Joint Clamp Replacement |  | Cast Iron
|  |  |  | 8 | Distribution Main |  | Bell Joint |  |  | Other |  |  |  | Bell Joint Clamp Replacement |  | Cast Iron
|  |  |  | 8 | Distribution Main |  | Bell Joint |  |  | Other |  |  |  | Bell Joint Clamp Replacement |  | Cast Iron
|  |  |  | 8 | Distribution Main |  | Bell Joint |  |  | Other |  |  |  | Bell Joint Clamp Replacement |  | Cast Iron
|  |  |  | 8 | Distribution Main |  | Bell Joint |  |  | Other |  |  |  | Bell Joint Clamp Replacement |  | Cast Iron
|  |  |  | 8 | Distribution Main |  | Bell Joint |  |  | Other |  |  |  | Bell Joint Clamp Replacement |  | Cast Iron
|  |  |  | 8 | Distribution Main |  | Bell Joint |  |  | Other |  |  |  | Bell Joint Clamp Replacement |  | Cast Iron
|  |  |  | 8 | Distribution Main |  | Bell Joint |  |  | Other |  |  |  | Bell Joint Clamp Replacement |  | Cast Iron
| 77-48530- |  |  | 20 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1977-06-03 | 1977-06-06 | Other |  | Steel/Wrought Iron
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1972-02-23 | Other |  | Steel/Wrought Iron
|  |  |  | 16 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1977-07-12 | Other | DRY HOLE | Steel/Wrought Iron |  |  | DUG OVER 16" HP MAIN NO LEAKAGE FOUND DRY HOLE.
1 | 71-00427-1 |  |  | 16.5 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-02-07 | 1972-02-23 | Other |  | Steel/Wrought Iron |  |  | NO WRAP LEFT ON THIS MAIN VERY HEAVY RUST AND SCALE
25 | 77-48193- |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1977-02-18 | 1977-02-28 | Patch Welded |  | Steel/Wrought Iron |  |  | INST/ (6) 10 X 16" PATCHED (12) 6 X 16" PATCHES AND WASHED OVER SEVERAL PITS TO STOP LEAKAGE. ALSO INST. (2) 32# MAG ANODES AND ETS STATION 1603-1
26 | 87-10210- |  |  | 2 | M |  | Body of Pipe |  |  | Corrosion |  | 1987-07-27 | 1987-07-27 | Clamp |  | Steel/Wrought Iron |  | OAKLAND | INSTALL SKINNER CLAMP AND LEAK FROM HOUSE (4071)
1 |  |  |  | 24 | Transmission | [6 empty] | 1976-03-04 |  |  |  | Steel/Wrought Iron
|  |  |  | 20 | Transmission | [10 empty] | Steel/Wrought Iron
26 | 73-48726- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-05-30 | 1973-07-17 | Clamp |  | Steel/Wrought Iron |  |  | LOCATED EIGHT (8) LEAKS OF VARIOUS SIZES IN A SEVEN FT. AREA. MAIN IS LADEN WITH PITS AND RUST; WILL HAVE TO BE CONSIDERED FOR REPLACEMENT IN NEAR FUTURE
26 | 76-49051- |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-09-21 | 1976-09-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | INSERTED 1/2" PLASTIC SERVICE TO STOP LEAKAGE.
26 | 72-20257-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-08-18 | 1972-08-07 | Clamp |  | Steel/Wrought Iron |  |  | INSTALLED 6" LEAK CLAMP + 1-9# MAGNESIUM ANODE AT SERVICE TEE LOCATION OF 2538 14TH AVE.
26 | 86-10129-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Digin |  | 1986-04-18 | 1986-04-18 |  |  | Aldyl A (Tan or Gray) |  | OAKLAND | SERVICE PULLED AWAY FROM TEE. INSTALLED APPROX 1' OF 11' PLASTIC
26 | 76-49247- |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-11-03 | 1976-11-29 | Clamp |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-10-11 | 1974-10-11 | Other | NEW SERVICE | Other Plastic |  | OAKLAND
26 | 73-49637- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-12-14 | 1973-12-14 | Clamp |  | Steel/Wrought Iron |  |  | MADE TEMP REPAIRS TO LEAKS IN 3/4" STEEL SERVICE WITH ...CLAMPS. TURNED IN FOR REPLACEMENT.
26 | 76-48874- |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-08-06 | 1976-08-09 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | OAKLAND | 17 MH ON LEAK
26 | 76-48898- |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-08-12 | 1976-08-13 | Patch Welded |  | Steel/Wrought Iron |  | OAKLAND | WELDED 10 PATCHES ON 8" T.P. MAIN ALL ON THE TOP.; 37 M.H.
26 | 76-48897- |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-08-12 | 1976-08-12 | Patch Welded |  | Steel/Wrought Iron |  | OAKLAND | 22 M.H.
|  |  |  | 12 | Other |  | Bell Joint |  |  | Material Failure |  |  | 1972-06-22 | Bell Joint Clamp |  | Cast Iron |  | OAKLAND | ISNT TWO 12" C.I. BELL JOINT CLAMPS PAVING CHANGED TO 16" MAIN AS IT WAS ONE BELL HOLE 12' X 5'. RETESTED 7/13/72
|  |  |  | 6.9 | Distribution Feeder Main |  | Other |  |  | Other |  | 1973-02-22 |  | Replace Pipe and/or Service |  | Cast Iron |  | OAKLAND
|  |  |  | 6.9 | Distribution Feeder Main |  |  |  |  | Other |  | 1973-02-22 |  | Replace Pipe and/or Service |  | Cast Iron |  | OAKLAND
|  |  |  | 6 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-03-01 |  | Bell Joint Clamp |  | Cast Iron |  | OAKLAND
|  |  |  | 6 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-03-01 |  | Bell Joint Clamp Replacement |  | Cast Iron |  | OAKLAND
|  |  |  | 6 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-03-01 |  | Bell Joint Clamp Replacement |  | Cast/Ductile Iron |  | OAKLAND
|  |  |  | 6.9 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-03-01 |  | Replace Pipe and/or Service |  | Cast/Ductile Iron |  | OAKLAND
|  |  |  | 6 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-03-01 |  | Bell Joint Clamp Replacement |  | Cast/Ductile Iron |  | OAKLAND;
|  |  |  | 6.9 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  |  |  | Bell Joint Clamp Replacement |  | Cast/Ductile Iron |  | OAKLAND
|  |  |  | 6.9 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-02-28 |  | Bell Joint Clamp Replacement | ; | Cast/Ductile Iron |  | OAKLAND
|  |  |  | 6.9 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-02-22 |  | Bell Joint Clamp Replacement |  | Cast/Ductile Iron |  | OAKLAND
|  |  |  | 6 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-03-06 | 1973-03-06 | Bell Joint Clamp Replacement |  | Cast/Ductile Iron |  | OAKLAND
|  |  |  | 6 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-03-06 |  | Bell Joint Clamp |  | Cast/Ductile Iron |  | OAKLAND
|  |  |  | 6.9 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-02-22 |  | Bell Joint Clamp Replacement |  | Cast/Ductile Iron |  | OAKLAND
|  |  |  | 6.9 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-02-22 |  | Bell Joint Clamp Replacement |  | Cast/Ductile Iron |  | OAKLAND
|  |  |  | 6 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-03-27 |  | Bell Joint Clamp Replacement |  | Cast/Ductile Iron |  | OAKLAND
|  |  |  | 6 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-03-27 |  | Bell Joint Clamp Replacement |  | Cast/Ductile Iron |  | OAKLAND
|  |  |  | 6 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-03-27 |  | Bell Joint Clamp Replacement |  | Cast/Ductile Iron |  | OAKLAND
|  |  |  | 20 | Transmission | [7 empty] | 1972-01-31 |  |  | Steel/Wrought Iron |  | OAKLAND | EXPOSED 20" T.P. LINE TO INST E.T.S. WIRES CADWELDED ON MAIN
26 | 73-00280- |  |  | 8 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1973-06-12 | 1973-06-13 | Other | REPLACED | Cast/Ductile Iron |  | OAKLAND | FOUND HAIRLINE CRACK IN 8' C.L. MAIN MADE REPAIRS BY USING POLYKIN TAPE AND DUC-SEAL
[7 empty] | Other |  |  | Other |  | 1980-07-08 |  | Other |  |  |  | OAKLAND | CAST IRON MAIN IS IN GOOD CONDITION
26 | 86-50091-1 |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1986-05-14 | 1986-05-14 | Bell Joint Seal |  | Cast/Ductile Iron |  | OAKLAND | INSTALLED ONE AUON IV P.S.I KIT ON 1-16" B.J MILLER PIPELINE R.S
|  |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-03-05 |  | Bell Joint Clamp Replacement |  | Cast/Ductile Iron |  | OAKLAND
|  |  |  | 16 | Distribution Feeder Main | [6 empty] | 1980-05-19 | 1980-05-19 |  |  | Cast/Ductile Iron |  | OAKLAND | INSPECT 1. 16" BELL JOINT ON CAST IRON. FOUND NO LEAKAGE. BELL JOINT LEAK CLAMP LOOK IN GOOD SHAPE 05-19-1980 M.A.
1 | 72-00317-A |  |  | 16 | Distribution Feeder Main |  | Fitting |  |  | Material Failure |  | 1972-05-16 | 1972-05-16 | Other |  | Cast/Ductile Iron |  | OAKLAND
|  |  |  | 16.6 | Distribution Feeder Main |  | Other |  | SERV TEE THREAD LEAKING | Corrosion |  |  | 1980-02-01 | Other | REPLACE SERV TEE | Cast/Ductile Iron |  | OAKLAND | REPLACE SERV. TEE; REPLACE LEAKING SERV. TEE & INST 16" X1&" SERV. SADDLE & 14" SERV. TEE & 1' PL. PIPE. SHUTDOWN & RELIGHT
| 79-20610 |  |  | 16 | Distribution Feeder Main |  | Other |  |  | Other |  | 1979-10-10 | 1980-01-31 | Other | AVON SEAL BELL | Cast/Ductile Iron |  | OAKLAND | nO LEAKAGE ON BELL JOINT AS PER FLAME PACK. CEMENTED OPEN ENDS OF ABANDONED 8 WAY DUCT LINE. REMOVE OLD LEAK CLAMP AND AVON SEAL BELL
| 80-48404 |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1980-05-01 | 1980-05-01 | Other | AVON SEAL | Cast/Ductile Iron | ; | OAKLAND | REP. LEAKING CLAMP. WITH AVON SEAL. BROKE & CEMENTED & WAY PT&T DUCT
| 80-48388- |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1980-04-25 | 1980-04-28 | Other | AVON SEAL | Cast/Ductile Iron |  | OAKLAND | REP. LEAKING BELL JOINT CLAMP WITH AVON SEAL CEMENTED 8 AWAY PT&T DUCT
| 80-48387- |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1980-04-22 | 1980-04-28 | Other | AVON SEAL | Cast/Ductile Iron |  | OAKLAND | REP. LEAKING BELL JOINT CLAMP WITH AVON SEAL CEMENTED 8 WAY PT& T DUCT
| 80-48356- |  |  | 16 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1980-04-03 | Other |  | Cast/Ductile Iron |  | OAKLAND | OPEN UP OVER BELL JOINT CLAMP FOUND NO LEAK. REPLACED 3-BOLTS
| 80-48359 |  |  | 16 | Distribution Feeder Main |  | Other |  |  | Other |  | 1980-04-14 | 1980-04-15 | Other |  | Cast/Ductile Iron |  | OAKLAND | OPEN OVER BELL JOINT LEAK CLAMP. FOUND NO LEAK. HAD TO REPLACE THREE BOLTS BROKEN & CEMENTED & AWAY PT&T DUCT
| 79-48981 |  |  | 16 | Distribution Feeder Main |  |  |  | NO LEAK |  | NO LEAK |  | 1979-12-21 |  | NO LEAK | Cast/Ductile Iron |  | OAKLAND | BELL JOINT LEAK CLAMP AT THIS LOCATION NOT LEAKING. CLAMP IN VERY GOOD CONDITION. THIS MAIN IN POOR CONDITION & SHOULD BE R/R. CEMENTED OLD & WAY BROKEN DUCT LINE
26 | 74-49144 |  |  | 16 | Distribution Main |  | Other |  |  | Other |  | 1974-09-03 | 1974-09-04 | Other |  | Cast/Ductile Iron |  | OAKLAND; | DUG BELL HOLE OVER 16" BELL JOINT A/C HIGH READING BELL JOINT ALREADY CLAMPED COULD FIND NO LEAKAGE ON CLAMP, EVEN WITH FLAME PAK. LEAKAGE BELIEVED TO BE COMING FROM ; SERVICE TEE TO 2038 FOOTHILL SEE LK #4860 FOR FURTHER INFORMATION.; EXCAVATED HOLE OVER BELL JOINT FOUND NO LEAKAGE HAD FLAME PAK SPOT PAINT AREA TO DIG FOR LEAKAGE.
| 80-48357 |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1980-04-09 | 1980-04-11 | Other | AVON SEAL |  |  | OAKLAND | REPLACED LEAKING BELL JOINT CLAMP WITH AVON SEAL.
| 80-48377 |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1980-04-18 | 1980-04-22 | Other | AVON SEAL; | Cast/Ductile Iron |  | OAKLAND | REPAIRED LEAKING BELL JOINT CLAMP WITH AVON SEAL.
| 80-48010 |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1979-12-19 | 1979-12-21 | Bell Joint Clamp Replacement |  | Cast/Ductile Iron |  | OAKLAND | LEAKING ALL AROUND BELL JOINT. INST BELL JOINT LEAK CLAMP ON 16" MAIN. THIS MAIN IN POOR CONDITION SHOULD BEND. CEMENTED OLD 8 WAY BROKEN DUCT LINE.
| 79-48981-1 |  |  | 16 | Distribution Feeder Main |  | Other |  |  | Other |  | 1979-12-11 | 1980-02-21 | Other | REPLACE SERV. SADDLE & TEE | Cast/Ductile Iron |  | OAKLAND | REPLACED LEAKING SERV. TEE WITH NEW 16" X 1 1/4" SERV. SADDLE & TEE. A. FORM HAS BEEN TURNED IN.
| 80-48408 |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1980-04-30 | 1980-05-02 | Other | AVON SEAL; | Cast/Ductile Iron |  | OAKLAND | REP LEAKING BELL JOINT CLAMP WITH AVON SEAL. BROKEN EMENTED 8 WAY PT&T DUCK
| 80-48169 |  |  | 16 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1980-02-08 | Other |  | Cast/Ductile Iron |  | OAKLAND | OPEN UP OVER TIE IN & 3" VALVE FOUND NO LEAK. DUCK LINE WAS NOT BROKEN IN THIS BELL HOLE.
| 79-48968 |  |  | 16 | Distribution Feeder Main | [10 empty] | Cast/Ductile Iron |  | OAKLAND | EXPOSED LEAKS PROOF CEMENT BLOCK SOAP TESTED & HAD FLAME PACK TEST BOTH SIDES OF BLOCK AROUND C.I. PIPE. FOUND NO LEAKS. CEMENTED OLD 8 WAY BROKEN DUCT LINE.
| 80-48170 |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1980-01-08 | 1980-01-22 |  |  | Cast/Ductile Iron |  | OAKLAND | FOUND LEAK ON BOTTOM OF B.J. LEAK CLAMP. REPLACED WITH AVON SEAL PATCH 8 WAY DUCT LINE.
| 80-48391 |  |  | 16 | Distribution Feeder Main |  | Other |  |  | Material Failure |  | 1980-04-29 | 1980-04-29 | Other |  | Cast/Ductile Iron |  | OAKLAND | FOUND 3/4" PLUG LEAKING ON 16" C.I. MAIN REP. BY RE DOPEING AND TIGHTING.
| 79-20603 |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1979-10-10 | 1979-12-26 | Bell Joint Clamp Replacement |  | Cast/Ductile Iron |  | OAKLAND | REPLACED LEAKING BELL JOINT LEAK CLAMP. MAIN OF THIS LOCATION IN BAD CONDITION. SHOULD BE R/P. BROKE OLD 8 WAY DUCT FROM BAHLTO BONK & CEMENTED ALL HOLES.
| 80-48426 |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1980-05-06 | 1980-05-07 | Other | AVON SEAL; | Cast/Ductile Iron |  | OAKLAND | REP. LEAKING BELL JOINT CLAMP WITH AVON SEHL ALSO BROKE AND CEMENTED 10 WAY P T&T DUCT.
| 80-48427 |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1980-05-05 | 1980-05-07 | Other | AVON SEAL | Cast/Ductile Iron |  | OAKLAND | REP. LEAKING BELL JOINT CLAMP WITH AVON SEAL. ALSO BROKE & CEMENTED 10 WAY PT &T. DUCT
| 86-50097-1 |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1986-04-14 | 1986-04-24 | Bell Joint Seal |  | Cast/Ductile Iron |  | OAKLAND | INSTALLED 1 CONES AVON IV P.S.I. B.J KIT ON 1"-16" B.J MILLER PIPELINE
| 75-48462 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1975-06-04 | 1975-06-04 | Replace Pipe and/or Service |  |  |  |  | USED (2) TWO 1/2 AMP FITTINGS TO INSTALL 4 FT OF PLASTIC TO REPLAI DIG-IN
| 77-48517 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1977-04-01 | 1977-04-12 | Clamp |  | Steel/Wrought Iron |  | OAKLAND | USED SKINNER CLAMP TO STOP LEAK WITH HEAVY PITTAGE, ALSOSOLDERED CAPER SERVICE TO STOP LEAKAGE
| 73-48323 |  |  | 3 | Other |  | Other |  |  | Other |  | 1973-07-06 | 1973-07-06 | Replace Pipe and/or Service |  |  |  | OAKLAND
|  |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  |  | 1973-08-13 | Patch Welded |  | Steel/Wrought Iron
|  |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-05-22 | 1974-05-22 |  |  | Steel/Wrought Iron |  | OAKLAND
| 75-48661 |  |  | 3 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-08-12 | 1975-08-12 | Clamp |  | Steel/Wrought Iron |  | OAKLAND | INST (2) 3" LEAK CLAMPS
|  |  |  | 4 | [13 empty] | EMERYVILLE | CUT OFF SERVICE. DEMO CANNED
26 | 75-20794 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-06-09 | 1975-06-09 | Clamp |  | Steel/Wrought Iron |  |  | USED ADAMS ALUM. CLAMPS (3) TO MAKE REPAIRS TO THREE CORROSION LEAKS ON BOTTOM OF 1 1/4 SCREWED LP SERVICE
| 75-207941 | [10 empty] | 1975-04-09 | [6 empty] | DUPLICATE TAG FOUND. JOB HAS BEEN CONE BY SOMEONE ELSE
|  |  |  | 2 | Distribution Feeder Main |  | Other | [5 empty] | 1973-03-17 |  | REPLACED | Steel/Wrought Iron
|  |  |  | 0.02 | Distribution Feeder Main |  | Other |  |  | Corrosion |  | 1973-03-17 |  |  | REPLACED | Steel/Wrought Iron |  | OAKLAND
|  | 105 |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-08-08 |  | Other | 10' PIECE | Steel/Wrought Iron |  | OAKLAND
| 79-00021-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-01-09 |  | Weld Over Sleeve or Can | TEMP SPIDER & GRAY TAPE | Steel/Wrought Iron |  | OAKLAND | FOUND 301 ON 20" TP MAIN MADE TEMP REPAIRS GC TO MAKE PERMANENT REPAIRS
| 72-05354-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  |  | 1972-09-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | INSERT MOVE METER OUT FROM UNDER HOUSE
26 | 77-48630 |  |  | 0.34 | Service |  | Body of Pipe |  |  | Corrosion |  | 1977-07-04 | 1977-07-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | REPLACED SERVICE TO STOP LEAKAGE USED COPPER RISER FIT
26 | 74-48263 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-02-25 | 1974-02-26 | Clamp |  | Steel/Wrought Iron |  |  | USED 3/4" SKINNER CLAMP TO MAKE TEMP. REPAIRS TO STEEL SERVICE. PIPE IS BADLY PITTED, TURNED IN FOR REPLACEMENT
|  |  |  | 2 | Distribution Feeder Main |  | Other |  | NEW SERV | Other | NEW SERV |  | 1972-09-06 | Other |  | Steel/Wrought Iron
26 | 76-21438-1 |  |  | 1.14 | Other |  | Fitting |  |  | Material Failure |  | 1976-08-26 | 1977-02-09 | Other |  | Steel/Wrought Iron |  | OAKLAND
26 | 86-50090-1 |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1986-05-05 | 1986-05-05 | Bell Joint Seal |  | Cast/Ductile Iron |  | OAKLAND | ; INSTALLED ONE AVON IV P.S.I KIT ON 1-16" B.J; MILLER PIPELINE
1 | 76-48895 |  |  | 0.75 | Other |  | Other |  |  | Corrosion |  | 1976-08-11 | 1976-11-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | TEMP REPAIRS TO 4 MM W 3/4" UC CLP ON 10-27. 4 1/4" 4RS 10-28-1976 REPLACED 2" (4 MM) 47 OC. IRONS FOR PERM. REPAIRS WO-425-1228-7H. 10-29 & 11-10-76 REPAIRED CIBOX & REPLACED (5) LIDS-1608-7 HRS NOPAVING NO ANODE.
26 | 74-48333 |  |  | 12 | Distribution Feeder Main |  | Other |  |  | Other |  | 1974-03-08 |  | Other |  | Steel/Wrought Iron
| 74-48333 |  |  | 12 | Transmission |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron |  |  | NO LEAK FOUND AT THIS LOCATION. PAVING TURNED IN ON OTHER LEAK.
1 | 73-48879-A |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-07-03 | 1973-07-03 | Clamp |  | Steel/Wrought Iron
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1980-03-07 |  | Other |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1980-03-07 |  | Other |  | Steel/Wrought Iron |  | OAKLAND | EXCAVATED BELL HOLE TO TIE IN MAIN ONLY
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1980-03-07 |  | Other |  | Steel/Wrought Iron |  | OAKLAND | EXCAVATED BELL HOLE TO TIE IN MAIN
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1976-02-06 | Other |  | Steel/Wrought Iron |  | OAKLAND | INSTALLED 1-850 HOT LINE
26 | 73-55382 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-10-02 | 1973-10-02 | Clamp |  | Steel/Wrought Iron |  |  | LOCATED FOUR (4) CORROSION LEAKS ON 3" MAIN, (3) PIN HOLES AND ONE HOLE 1/4" IN DIAMETER. PERMANENT REPAIRS MODE WITH SKINNER LEAK CLAMPS ANODE ATTACHED.
26 | 73-49117 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-08-23 | 1973-08-23 | Clamp |  | Steel/Wrought Iron |  |  | DUG UP CORROSION LEAK IN DRIVEWAY ON 3" S+P MAIN. LEAKAGE APPEARS TO BE CAUSED BY LARGE ROCK ON BOTTOM OF MAIN. REPAIR MODE WITH PERMANENT SKINNER LEAK CLAMP.
|  |  |  | 1 | Other | HOUSE | Fitting |  |  | Damage by outside Forces |  | 1976-10-18 | 1976-10-18 | Other | SEE REMARKS | Steel/Wrought Iron |  | OAKLAND | LEAK ON UNDER GROUND HOUSE LINE CUST. WAS NOTIFIED & IS TO REPAIR HIMSELF
| 77-48783 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-08-12 | 1977-08-12 | Other |  | Steel/Wrought Iron |  | OAKLAND | CUT OFF 33' OP 2" SH. MAIN FOR PERMANENT REPAIR DUE TO BROKEN MAIN BY THIRD PARTY PRIOR TO DATE ABOVE (1) 2" LINE STOPER WAS INSTALLED TO MAKE C/O
| 73-00007-A |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-03-20 | 1973-03-21 | Clamp |  | Steel/Wrought Iron |  |  | INSTALL 4% C & TIGHTEN ANOTHER CC. CLOSE BY TO STOP LEAKAGE
| 74-49492-1 |  |  | 2 | Gathering |  |  |  | DUG (1) AS PER FLAME PAC FOUND NO LEAK |  |  | 1975-08-19 | 1976-03-12 |  |  | Steel/Wrought Iron
| 73-20405-1 |  |  |  | Gathering | [6 empty] | 1975-08-19
| 73-00007-A |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-03-20 | 1973-03-21 | Clamp |  | Steel/Wrought Iron |  |  | INSTALL 4% C + TIGHTEN ANOTHER C.C. CLOSE BY TO STOP LEAKAGE
| 77-48783 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-08-12 | 1977-08-12 | Other |  | Steel/Wrought Iron |  | OAKLAND | CUT OFF 33' OP 2" SH. MAIN FOR PERMANENT REPAIR DUE TO BROKEN MAIN BY THIRD PARTY PRIOR TO DATE ABOVE. 2" LINE STOPER WAS INSTALLED TO MAKE C/O
|  |  |  | 1 | Other |  | Fitting |  |  | Damage by outside Forces |  | 1976-10-18 | 1976-10-18 | Other | SEE REMARKS | Steel/Wrought Iron |  | OAKLAND | LEAK ON UNDER GROUND HOUSE LINE CUST. WAS NOT FIXED & IS TO REPAIR HIMSELF
26 | 73-49117 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-08-23 | 1973-08-23 | Clamp |  | Steel/Wrought Iron |  |  | DUG UP CORROSION LEAK IN DRIVEWAY ON 3" S+P MAIN. LEAKAGE APPEARS TO BE CAUSED BY LARGE RACK ON BOTTOM OF MAIN. REPAIR MADE WITH PERMANENT SKINNER LEAK CLAMP.
26 | 73-55382 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-10-02 | 1973-10-02 | Clamp |  | Steel/Wrought Iron |  |  | LOCATED FOUR (4) CORROSION LEAKS ON 3" MAIN (3) PIN HOLES AND ONE HOEL 1/4" IN DIAMETER. PERMANENT REPAIRS MODE WITH SKINNER LEAK CLAMPS ANODE ATTACHED
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other | ; |  | 1976-02-06 | Other |  | Steel/Wrought Iron |  | OAKLAND | INSTALLED I-850 HOT LINE
26 |  |  |  | 0.2 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1982-02-03 | Other |  | Cast/Ductile Iron |  | OAKLAND | C/O 3/4 SERVICE TO 345 20" STROUD 80 S/O 20' STROUD ON WEBSTER;
| 74-01168 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  |  | 1974-08-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | INST E.T.S. STATION IN PARKING AREA IN 8" VALVE FRAME WITH (2) #10 TEST LEADS
|  |  |  | 3 |  |  | Other |  |  | Other |  | 1974-07-03 | 1974-07-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron
| 73-45039 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Construction Defect |  | 1973-03-02 | 1973-03-06 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | LEAK AT WELD ON 3/4" SERV. REPAIR MADE BY WELD OVER WITH ARE WELDER
26 | 86-11327-1 |  |  | 8 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1986-09-29 | 1986-10-06 | Bell Joint Seal |  | Cast/Ductile Iron |  | OAKLAND | CALKED BELL FOR REMP REPAIR. PERM REPAIR INSTALLED AVON SEAL
26 | 78-48957 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1978-11-03 | 1978-10-26 | Other |  | Steel/Wrought Iron |  | OAKLAND | REMOVED RFT SECTION OF CORRODED PIPE
| 86-30178-1 |  |  | 4 |  |  | Bell Joint |  |  | Corrosion |  | 1986-09-10 | 1987-10-21 | Bell Joint Clamp |  | Cast/Ductile Iron |  | OAKLAND | REPAIRS COMPLETED BY MILLER PIPELINE APPX 2 WEEKS AGO. NO FURTHER INDICTATION OF LEAKAGE BELL JTS.
|  |  |  | 3 | Distribution Main |  | Other |  |  | Corrosion |  | 1973-10-29 | 1973-10-29 | Replace Pipe and/or Service
| 80-48364 |  |  | 2 | Other |  | Body of Pipe |  |  | Corrosion |  | 1980-04-17 | 1980-04-18 | Clamp | SKINNER CLAMP |  |  | OAKLAND | FOUND AND REPAIRED ANOTHER 301 APPROXIMATLY 12' AWAY FROM PRIVIOUS 301 IN FRONT OF 1166. (2) BOLT SKINNER CLAMP W/ 5 LB MAG. ANODE WAS USED FOR PERM. REP. MAIN SHOULD BE CONSIDERED FOR REPLACEMENT THERE ARE A FEW PATCHES ON SIDEWALK
| 89-11417-F |  |  | 1.5 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1989-05-30 | 1989-05-30 | Clamp |  | Steel/Wrought Iron |  | OAKLAND | INSTALLED TWO SKINNER LEAK CLAMPS OVER HOLES IN 1 1/2" STUB SERVICE. CORROSION LEAK.
|  |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-06-03 | 1974-06-03 |  |  | Steel/Wrought Iron
| 77-484001 |  |  | 0.34 | Other |  | Fitting |  |  | Material Failure |  | 1977-04-22 | 1977-10-20 | Other |  | Steel/Wrought Iron |  | OAKLAND | REPAIRED A SMALL LEAK ON A 3/4" BELL WHERE HOUSE LINE CONNECTS TO OUTLETS SWIVEL OF 1A CURB MTR-LOOSEEND CALK & TIGHTENED NIPPLE INTO ALL AFTER DOPING NIPPLE.
| 89--5 |  |  | 1.25 | Gathering |  | Fitting |  |  | Other |  | 1989-01-16 | 1989-01-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | OAKLAND | TIGHTENED 1 1/4" SCREWED PLUG IN 3" STEEL MAIN A/C LOOKING. STOPPED LEAKAGE.
26 | 73-48694 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-05-24 | 1973-05-25 | Clamp |  | Steel/Wrought Iron |  |  | REPAIRED LEAK ON 2" LD MAIN WITH CLAMP. MAIN IS BADLY PITTED WITH HEAVY RUST.
26 | 73-48696- |  |  | 1 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-05-24 | 1973-05-30 | Clamp |  | Steel/Wrought Iron |  |  | CLAMPED LEAK ON 1" LP SERVICE NOT TURNING IN FOR REPLACEMENT DUE TO CONDITION OF MAIN AND NO OTHER LEAKAGE DETECTED ON SERVICE.
1 |  |  |  | 4 | Distribution Feeder Main |  | Other |  |  | Other |  | 1972-02-29 | 1972-02-29 |  |  | Cast/Ductile Iron
| 77-49197 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1977-11-14 | 1977-11-16 | Clamp |  | Steel/Wrought Iron |  | OAKLAND | INST 2-2" CLAMPS IN SAME TO STOP LEAKING
| 77-49189 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1977-11-14 | 1977-11-16 | Clamp |  | Steel/Wrought Iron |  | OAKLAND | INST. 1-CLAMP ON 2" MAIN. THERE IS 1/2" WATER SERVICE CROSSING TRENCH 3" DEEP
| 73-55281 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-06-27 | 1973-06-28 | Clamp |  | Steel/Wrought Iron |  |  | USED SKINNER CLAMP TO REPAIR LEAK ON 1 1/4" SERVICE. CORROSION HOLE APPROX. 1/8" IN DIAMETER. SKINNER CLAMP WILL BE PERMANENT REPAIR.
|  |  |  | 24 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  |  | EXPOSED TO INSTALL E.TS. ONLY
1 | 73-49193-A |  |  | 2 | Distribution Feeder Main |  | Physical/Mechanical Joint |  |  | Damage by outside Forces |  | 1973-09-13 | 1973-09-13 | Patch Welded |  | Steel/Wrought Iron
|  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1973-07-15 | 1973-07-16 |  |  | Steel/Wrought Iron
| 73-49486 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-11-23 | 1973-11-23 | Clamp |  | Steel/Wrought Iron |  |  | USED SMITH-BLAIR CLAMP TO REPAIR CORROSION LEAK, 3/8" IN DIAMETER IN 2" HO MAIN. MAIN SHOULD BE REPLACED SOMETIME IN FUTURE.
26 | 74-48015 |  |  | 0.75 | Service |  | Fitting |  |  | Material Failure |  | 1973-01-02 | 1973-01-02 | Other | REPLACED | Steel/Wrought Iron |  |  | LOCATED LEAKAGE ON SERVICE SADDLE WHERE TIED TO MAIN, ALSO FOUND LEAK ON ST. ALL GOING IN TO SCREWED SERVICES. SERVICE IS TURNED IN FOR REPLACEMENT. MADE TEMP REPORT WITH GRAY TAPE AND DUC. SEAL.
|  |  |  | 6 | Distribution Feeder Main | [7 empty] | 1977-10-19 | Other | C/OFF | Steel/Wrought Iron |  | OAKLAND | C/OFF IN ORDER TO REMOVE REGULATION STATION.
|  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  | 1974-08-23 |  | Other |  | Cast/Ductile Iron
26 | 73-55038 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Material Failure |  | 1974-02-04 | 1974-02-06 | Clamp |  | Steel/Wrought Iron |  |  | FOUND GAS BLOWING FROM AROUND EVISTING 6" SKIMMER CLAMP MADE REPAIRS BY RETIGHTENING CLAMP AND WRAPPING MAIN.
395 | 71-40181- |  |  | 8 | Distribution Main | [6 empty] | 1971-02-17 | 1971-03-09 | Patch Welded |  | Steel/Wrought Iron |  | Richmond | ARCED PATCH ON 8" MAIN AND ELIMINATED LEAKAGE; MEASUREMENTS TAKEN FROM TRAIN SIGNAL.
28 | 72-60080-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-05-09 | 1972-05-09 | Patch Welded |  | Steel/Wrought Iron |  |  | MAIN IS IN VERY POOR CONDITION. HEAVY PITTS AND POOR WRAP. FOUND LEAK ON 8" TP WELDED PATCH AND ELIMINATED LEAKAGE.
28 | 72-40295-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-05-11 | 1972-05-11 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | FOUND SEEM SPLIT. WELDING PATCH ON TO ELIMINATE LEAKAGE.
28 | 95-80565- |  |  | 0.75 | Service |  | Meter |  |  | Digin |  | 1995-11-01 | 1995-11-01 | Other |  | Steel/Wrought Iron |  | Richmond | HAD M&C DEPT REBUILD SET
28 | [17 empty] | Richmond | LOC #3. 72" DEEP (OVER CONTROL FITTING).
28 | [17 empty] | Richmond
28 | [17 empty] | Richmond
28 | [11 empty] | 1989-11-17 | 1989-12-20 |  |  |  |  | Richmond | N/SIDE ATLAS 9' W/ OF R.R. AT VALVE. C/O VALVE AND OLD SERVICE TO PINDLE STEEL; OLD SERVICE... STEEL. C/O AT ... REMOVED EXIST. VALVE.
28 | [11 empty] | 1989-11-17 | 1989-11-17 |  |  |  |  | Richmond | N/SIDE ATLAS EDGE OF PAVEMENT 140' E/OF R.R. VENT. INSTALLED NEW 1" SERV/ TO POINT PINDLE STEEL/ (2" SERVICE TEE)
28 | 72-40342-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-05-08 | 1972-05-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Richmoond | REMOVED 1 1/2 BLOW OFF AND WELDED 2" CAP OVER HOLE. INSTALLED 8" PATCH AND ELIMINATED LEAKAGE.
[5 empty] | Transmission | [6 empty] | 2004-08-30 |  |  |  | Steel/Wrought Iron |  | Richmond | WELD ON ONE ONE INCH SAVE-A-VALVE.
28 | 72-60095-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-05-09 | 1972-05-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Richmond | WELDED 8" PATCH AND ELIMINATED LEAKAGE.
28 | 87-00287-1 |  |  | 8 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1987-03-24 | 1987-03-25 | Patch Welded |  | Steel/Wrought Iron |  | Richmond | DRILL... FOUND LEAK ON 8" MAIN. WELDED PATCH OVER MAIN; ALSO WELDED HALF-SOL OVER 36" OF AREA OF MAIN.
28 | 85-20452-1 |  |  | 2 | Distribution Main |  | Valves |  |  | Other |  | 1985-03-27 | 1986-03-04 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Richmond | INTERSECTION... REPAIRED 301 ON 2" FLANGE VALVE - RETIGHTENED BOLTS.
|  |  |  | 8 | [11 empty] | Steel/Wrought Iron |  | Richmond | WELD ON ONE ONE INCH SAVE-A-VALVE.
26 | 80-40791-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-10-20 | 1980-10-21 | Other |  | Copper |  | San Pablo
1 | 79-00123-1 |  |  | 8 | Distribution Feeder Main |  | Regulator |  |  | Material Failure |  | 1979-01-19 | 1979-01-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | C.C. COUNTY | YES ELEC J6. NO HOT OIL. WORK S.A.D; REPAIRED GAS LEAK IN DIST. REGULATOR STATION.
28 | 72-40005-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-01-04 | 1972-01-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Richmond | INSTALLED 2" WELD PATCH 161' N/O PAYNE DR. ALSO RERAN SERV. USING 1/2" PLASTIC INSIDE OLD CASING.
|  | 105B |  | 24 | [7 empty] | 2002-05-29 | 2002-05-29 |  |  | Steel/Wrought Iron |  | Richmond | INST. SIDETAP ON 24' TP MAIN LINE 105B. 3" STL VALVE INSTALLED PER R. BILLUPS. 5 STL VALVE USED FOR S105 TAP.
28 |  |  |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | Richmond
28 |  |  |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | Richmond
28 |  |  |  | 20 | [8 empty] | 1988-03-02 |  |  | Steel |  |  | CAD WELDED 2-#10 TAN WIRES TO THE 20" STAN PAC MAIN AND TERMINATED THOSE WIRES INTO A 6-5 W.C. INSTALLED 2-#10 WIRES ON MAIN & TERMINATE IN G-5 VFC.
1 | 81-40195-1 |  |  | 0.5 | Service |  | Other |  | Non Corrodible Riser | Material Failure |  | 1981-03-19 | 1981-03-19 | Replace Pipe and/or Service |  | Other Plastic | Non Corrodible Riser | El Sobrante | REPLACED LEAKING NON CORRODIBLE RISER.
1 | 81-40196-1 |  |  | 0.5 | Service |  | Other |  | Riser | Material Failure |  | 1981-03-19 | 1981-03-19 | Replace Pipe and/or Service |  | Other Plastic | Non corrodial riser at 1164 Kelvin. Leak #81-40196-1. | El Sobrante | REPLACED LEAKING NON CORRODIBLE RISER AT 1164 KELVIN. LEAK #40195. THIS CLEARED THIS LEAK UP.
28 | 92-80197-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1992-06-21 | 1992-06-26 | Patch Welded |  | Steel/Wrought Iron |  | El Sobrante | INSTALLED 4X4 WELD PATCH ON MAIN.
| 76-60332- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1976-07-09 | 1976-07-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | San Pablo | INSPECTION REPORT. A/C RERUN SERVICE.
|  |  |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | San Pablo | PROSPECTED FOR DEPTH AND CONDITION.
|  |  |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | San Pablo | PROSPECTED FOR DEPTH AND CONDITION.
|  |  |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | San Pablo | PROSPECTED FOR DEPTH AND CONDITION ONLY.
|  |  |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | San Pablo | PROSPECTED FOR DEPTH AND CONDITION.
28 |  |  |  | 22 | [8 empty] | 1988-03-01 |  |  | Steel |  | San Pablo | INSTALLED 2 - #10 TAN WIRES TO 22" STEEL STAN-PAC MAIN BY CALD WELDING. TERMINATED WIRES IN V.F.C; INSTALLED ETS STATION.
| 75-20644-1 |  |  | 0.75 | Other |  | Fitting |  |  | Construction Defect |  | 1975-10-20 | 1975-11-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Richmond | USA CONTACTED DATE 10/30/75. TICKET #7379. REBUILT IRON CONNECTIONS TO MAKE REPAIRS. LEAKAGE AT REGULATOR AND STOPCOCK. REBUILT IRON CONNECTIONS TO MAKE REPAIRS.
28 | 77-60344-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1977-09-12 | 1977-09-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | San Pablo | RERAN SERVICE TO MAKE REPAIRS. RERAN SERVICE.
| 75-60607-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-10-08 | 1975-10-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | San Pablo | INSPECTION REPORT A/C. R/R SERVICE A/C LEAKAGE.
28 | 76-20043-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-01-30 | 1976-03-20 | Clamp |  | Steel/Wrought Iron |  | Richmond | IWK FOLLOW-UP FROM DATE FOUND; INST. 2" SKINNER. LEAK CLAMP @ 31'...
| 77-40017- |  |  | 0.75 | Other |  | Other |  |  | Other |  | 1977-01-14 | 1977-01-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | El Sobrante | S/S OF SANTA RD... 7/19 W/O DESERT...
| 78-20181-1 |  |  | 20 | Transmission |  | Valves |  |  | Other |  | 1978-03-10 | 1979-02-08 | Other |  | Steel/Wrought Iron |  | San Pablo
28 |  |  |  | 24 | [8 empty] | 1996-08-28 |  |  | Steel |  | Richmond | PROSPECT DEPTJ 24" TP GAS LINE. DEPTH IS 74"; 24" TP GAS MAIN IS 74" DEEP.
28 | 76-20723-1 |  |  | 0.75 | Other |  | Meter |  |  | Material Failure |  | 1976-05-27 | 1976-11-04 | Other |  | Other |  | No. Richmond | NO KNOWN U.G. NO ELECTRIC UNDERGROUND.
|  |  |  | 22 | Transmission | [6 empty] | 1972-02-28 |  |  |  | Steel/Wrought Iron
|  |  |  | 0.75 | Other |  | Fitting |  |  | Damage by outside Forces |  | 1972-04-18 | 1972-04-18 | Other |  | Steel/Wrought Iron |  | No. Richmond | C/O SERVICE UNMARKED. CONT. PULLED CAP FROM END OF C/O ... STOPPED OFF BY INSERTING PITMAN STOPPER. RETHREADED AND ...
28 | 84-31019-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-01-09 | 1984-03-28 | Patch Welded |  | Steel/Wrought Iron |  | North Richmond | ARC WELDED 2 PATCHES ON MAIN.
28 | 95-80143-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1995-05-22 | 05/22/0000 | Replace Pipe and/or Service |  | Other Plastic |  | N. Richmond | INST. 25' OF 1/2" PLASTIC WITH 2 - PLASTIC COUPLINGS.
| 76-40136- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-05-01 | 1976-05-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron
| 74-40564- |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-10-08 | 1974-10-09 | Other |  | Steel/Wrought Iron |  | San Pablo | 1/4 STUB ON PREVIOUS ... SERV. LEAKING CUT OUT AND SECTION AND INST. 3/4" SCREWED CAP.
28 | 76-20320-1 |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1976-03-29 | 1976-06-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | San Pablo | REPLACED AND DOPED LEAKING CAP ON C/O SERVICE TEE.
| 76-60401-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1976-07-20 | 1976-11-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | San pablo | RERAN SERVICE TO 1719 DOVER TO ELIMINATE LEAKGAGE.
|  |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-07-05 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | San Pablo | RERAN 1" PLASTIC SERVICE TO MAKE PERM REPAIRS - REG AND METER OUTSIDE.
28 | 73-00137-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-05-30 | 1974-02-11 | Other |  | Steel/Wrought Iron |  | San Pablo | 3/4 STATIC LINE TO REG PIT WAS LEAKING. PERMANENT REPAIR WAS CIT TO 74' OF 3/4 STATIC LINE OFF. OTHER MEANS FOR STATIC LINE WAS DONE IN PIT BY REG CREW.
28 | 91-80222-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1991-07-02 | 1991-09-14 | Patch Welded |  | Steel/Wrought Iron |  | San Pablo | REPAIRED CORROSION LEAK WITH 10"X10" PATCH CUT FROM 16" .375 WT X 42 PIPE - SEE ATTACHED STRENGTH PRESSURE TEST REPORT.
28 | 91-80222-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1991-07-02 | 1991-09-14 | Patch Welded |  | Steel/Wrought Iron |  |  | INST. A 10"X10" WELD PATCH ON 16" TP MAIN TO REPAIR LEAKAGE.
28 | 83-20789-1 |  |  | 2 | Other | House Line | Other |  |  | Other | Unknown | 1983-03-18 | 1983-03-18 | Other | Isolated school to make repairs. | Steel/Wrought Iron |  | San Pablo | FOUND 301 ON CUST. HOUSELINE. ISOLATED PROBLEM & TURNED OVER TO DISTRICT SCHOOL PLUMBER.
28 | 81-60043- |  |  | 0.75 | Other | Stub never used | Body of Pipe |  |  | Corrosion |  | 1981-05-06 | 1981-05-09 | Other | C/off | Steel/Wrought Iron |  | San Pablo | C/OFF LEAK & SERVICE STUB ...
28 | 81-60043- |  |  | 0.75 | Other |  | Other Welds |  |  | Construction Defect |  | 1981-05-06 | 1981-05-07 | Patch Welded |  | Steel/Wrought Iron |  | San Pablo | OLD C/OFF WELD LEAKING; ... WAS BUSTING C/OFF. REPAIRED LEAKING WELD ON OLD C/O TEE.
| 76-60426- |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-08-28 | 1976-08-31 | Clamp |  | Steel/Wrought Iron |  | Richmond
28 | 85-40040-1 |  |  | 20 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1985-01-22 | 1985-01-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | San Pablo | REPLACED DAMAGED SECTION OF PIPE W/ 41" OF NEW 20" PIPE.
| 80-60157 |  |  | 0.75 | Other | Stub Service | Body of Pipe |  |  | Corrosion |  | 1980-03-19 |  | Other | C/O STUB | Steel/Wrought Iron |  | San Pablo | NO ELECT UG. C&T BRANCH SERV. TO #3455-51, NO LEAKAGE. FOUND LEAKAGE ON OLD 3/4" STUB SERV TEE. C/O AT MAIN & WELDED ON 3/4" STL CAP.
1 |  |  |  | 3 | Distribution Feeder Main |  | Fitting |  |  | Corrosion |  |  | 1981-03-06 |  |  | Steel/Wrought Iron |  | Contra Costa County | EXPOSED 3' OF 3" STEEL PIPE INSPECTED FOR LEAKAGE. FOUND NO LEAKAGE ON MAIN.
28 | 71-30640-1 |  |  | 3 | Distribution Feeder Main |  | Tap Connection |  |  | Construction Defect |  | 1971-12-10 | 1971-12-22 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | LEAK IN WELD WHOSE C.O. STUB WAS WELDED. REWELDED. BEAU PIVAGE.
| 76-60405- |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1976-08-18 | 1976-08-26 | Other |  | Steel/Wrought Iron |  | San Pablo | NO ELECT UG; CUT-OFF SERVICE TEE LEAKING. REMOVED TEE. (OLD TEE NOT IN USE).
|  | 105A |  | 20 | Transmission |  | Other |  |  | Corrosion |  | 1980-09-15 | 1980-09-15 | Other |  | Steel/Wrought Iron |  | Richmond | WO 42419 REPLACE SECTION 105A.
28 | 87-20872-1 |  |  | 3 | Service |  | Valves |  |  | Other |  | 1987-06-23 | 1987-06-24 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Richmond | TIGHTEN BOLTS ON FLANGE.
28 | 73-60186-1 |  |  | 20 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-07-26 | 1973-07-30 | Patch Welded |  | Steel/Wrought Iron |  | Richmond | INST. 12" X 12" WELD PATCH.
| 79-00113-1 |  |  | 20 | Transmission |  | Valves |  |  | Other | 3/3" Valve Loose | 1979-01-18 | 1980-05-28 | Other | Tightened valve | Steel/Wrought Iron |  | Richmond | UPGRADED NO.3 LEAK. NOT A PIPE WHICH CARREIS GAS PRESSURE SET FROM PRINTOUT AND FILE IN DEPTH SKETCH FOLDER FOR RECORDS ONLY. PER K.P. YES ELECT UG; 3/4" VALVE OFF FLANGE LEAKING (WAS DOPED AND RETIGHTENED). NOT EXPOSED.
28 | 96-21027-1 |  |  | 0.75 | Service |  | Meter |  |  | Other |  | 1996-02-05 | 1996-02-05 | Other |  | Steel/Wrought Iron |  | No. Richmond | RE-BUILT FITTINGS
28 | 91-00100-1 |  |  | 0.75 | Transmission |  | Tap Connection |  |  | Corrosion |  | 1991-01-24 | 1991-07-23 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Richmond | TIGHTENED LEAKING CAP ON PRESS. TAP FITTING. VALVE X-31.
| 76-60566- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1976-11-18 | 1976-11-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | N. Richmond
28 |  |  |  | 22 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Richmond
28 | 95-30002-1 |  |  | 2 | Transmission |  | Other Welds |  |  | Other |  | 1995-04-11 | 1995-10-12 | Patch Welded |  | Steel/Wrought Iron |  | Richmond | NO UG ELEC; WELDED OVER LEAKING WELD ON 2" ELBOW.
28 | 93-35002-1 |  |  | 4 | Distribution Feeder Main |  | Other Welds |  |  | Corrosion |  | 1993-01-04 | 1993-02-03 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Richmond | WELDED OVER WELDS AND CANNED 3/4" NIPPLE W/ PLUG ON TOP OF CAN; MADE REPAIR ON EXISTING CAN.
28 | 94-80060-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Other | EXISTING CLAMP LEAKING. |  | 1994-02-11 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Richmond | WELDED CAN OVER LEAK AT WATER MAIN CROSSING; DOWNGRADE ON 2" STEEL MAIN. EXISTING 4" CLAMP LEAKING. WELDED CAN OVER LEAK. 4" T.P. 13' OUT.
28 | 73-60087-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-03-19 | 1974-05-15 | Patch Welded |  | Steel/Wrought Iron |  | N. Richmond
28 | 76-20722-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-05-27 | 1976-11-03 | Patch Welded |  | Steel/Wrought Iron |  | No. Richmond | NO KNOWN U.G. ELECTRIC; INSTALLED 4" PATTON WELD PATCH. LEAK CAUSED BY SEWER INSTALATION.
28 | 95-21431-1 |  |  | 4 | Distribution Main |  | Other Welds |  |  | Corrosion |  | 1995-05-16 | 1995-05-16 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | S.P.
|  |  |  | 20 | Transmission | [6 empty] | 1973-03-13 |  |  |  | Steel/Wrought Iron
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1973-03-13 |  |  |  | Steel/Wrought Iron
|  |  |  | 3 | [13 empty] | N. Richmond | C/O 27' OF 3" TP MAIN & 25' OF 3" SERVICE P/C NON USE. (DONE ON WO 43434A-81).
28 | 97-50002-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  |  | 1997-01-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Richmond | BYPASSED AND REPLACED BAD REG.
28 |  |  |  | 3 | Distribution Feeder Main |  | Other |  |  | Other |  | 1982-02-16 | 1982-02-16 | Other |  | Steel/Wrought Iron |  | Richmond | EXPOSED... INST. 3/4" STL TP GAS SERV.
|  |  |  | 2 | Other | [10 empty] | Steel/Wrought Iron |  |  | WO 4633 B, 3-11-75.
|  |  |  | 3 | Other | [10 empty] | Steel/Wrought Iron |  |  | WO 4633 B, 3-11-75.
|  |  |  | 4 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | RICHMOND
28 | 88-20615-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1988-06-02 | 1988-06-02 | Patch Welded |  | Steel/Wrought Iron |  | R. | INST. 3"-4" PATCHES ON PIPE ON 4" TP MAIN. ALSO INST. 8" CAN ON MAIN.
28 | 93-20341-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1993-04-14 | 1994-05-24 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | R | WELDED PATCH AND 40" CAN OVER CORROSION LEAK AND PITS.
|  |  |  | 4 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | RICHMOND
28 |  |  |  | 2 | [7 empty] | 1990-03-30 | 1990-04-19 |  |  |  |  | RICHMOND | REPLACED INOPERABLE 2" ZONE VALVE (B-53)
28 | 73-40172-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1973-03-28 | 1973-03-28 | Patch Welded |  | Steel/Wrought Iron |  | RICHMOND | JUST 1-WELD PATCH IN ORDER TO REPAIR PULLED UP ABANDON 1 1/4" TEE COUPON.
28 | 73-60056-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-03-27 | 1973-03-28 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | RICHMOND | ELECTROLYSIS ON MAIN WHERE SEVER LINE CAME IN CONTACT WITH MAIN.
28 | 87-20862-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1987-06-22 | 1987-07-14 | Patch Welded |  | Steel/Wrought Iron |  | RICHMOND | INSTALLED 2 PATCHES (ARC WELDER)
28 | 87-00281-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1987-03-17 | 1988-03-16 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | R/SP
28 | 73-60045-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-03-26 | 1973-03-26 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Richmond | MAIN IS CROSSING ABANDONED SEWER LATERAL. WRAPPING WAS DAMAGED BY TRENCHING EQUIPM. REST OF MAIN IS OK.
28 | 73-60129-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-04-06 | 1973-04-09 | Patch Welded |  | Steel/Wrought Iron |  | Richmond | 1 -4" WELD PATCH ON MAIN, 4-9-73.
28 | 74-60011-1 |  |  | 4 | Distribution Feeder Main |  | Tap Connection |  |  | Damage by outside Forces |  | 1974-01-28 | 1974-01-28 | Patch Welded |  | Steel/Wrought Iron |  | N. Richmond
28 | 73-60120-1 |  |  | 4 | Transmission |  | Other Welds |  |  | Construction Defect |  | 1973-04-05 | 1973-04-09 | Other |  | Steel/Wrought Iron |  | Richmond | INST 1 -8" WELD CAN OVER LEAKING VERTICAL WELD ON 4" PIPE 4-9-73.
| 82-20695-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1982-04-27 | 1983-06-13 | Patch Welded |  | Steel/Wrought Iron |  | NO. Richmond | LEAK ON 4" STEEL T.P. MAIN. PATCH WELDED TO REPAIR.
|  |  |  | 4 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Richmond | EXPOSED MAIN LOOKING FOR LEAK "DRY HOLE".
|  |  |  | 4 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Richmond
28 | 85-20368-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1985-03-13 | 1986-03-31 | Patch Welded |  | Steel/Wrought Iron |  | No. Richmond
|  |  |  | 2 | Other | [10 empty] | Steel/Wrought Iron |  | Richmond | WO 4633 B, 3-11-75
|  |  |  | 2 | Other | [12 empty] | Richmond | WO 4633 B , 3-11-75
28 |  |  |  | 22 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | Richmond
| 06-21020-1 |  |  | 0.75 | Single Service |  | Mechanical Joint |  |  | Unknown |  | 2006-02-09 | 2009-05-21 | Other | Redoped all pipe fittings | Steel/Wrought Iron |  | Berkeley | TIGTHEN FITTING. ALL IN CMB.
| 05-21012-1 |  |  | 0.75 | Branch Service |  | Other |  | UNION ON ROTARY METER. | Unknown |  | 2005-01-31 | 2009-03-05 | Other |  | Steel/Wrought Iron |  | Berkeley | TIGHTENED UNION; TIGHTENED OUTLET UNION ON ROTARY METER TO REPAIR GAS LEAK IN CMB. M VASARHERY, 03-05-09.
| 08-21031-1 |  |  | 0.75 | Single Service |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2008-02-10 | 2009-04-15 | Other | Nipple | Steel/Wrought Iron |  | Berkeley | NEED TO GO TO M+C REG. MON SET LEAKING ON 3/4" NIPPLE PAINTED IN YELLOW JLAS 4-13-09. REPLACED NIPPLE ON METER SET 3/4" STEEL. COMPLETED BY F. DECONTE/ REENTRY ON 4/15/09.
| 04-21022-1 |  |  | 1.25 | Single Service |  | Fitting |  |  | Unknown |  | 2004-02-10 | 2009-04-13 | Other | TIGHTEN REDUCER. | Steel/Wrought Iron |  | Berkeley | TIGHTEN 1 1/4" X 3/4" REDUCER. ALL IN CMS.
| 99-21031-1 |  |  | 6 | Distribution Main |  | Valves |  |  | Other |  | 1999-02-26 | 1999-03-04 | Other | GREASED VALVE. | Steel |  | Rodeo | GREASED VALVE.
28 | 96-25623-1 |  |  | 2 | Distribution Main |  | Regulator |  |  | Other |  | 1996-09-27 | 1996-09-27 | Other |  | Steel/Wrought Iron |  | Rodeo | REPAIR INTERNAL LEAK ON PILOT REG.
28 | 96-21184-1 |  |  | 6 | Distribution Main |  | Valves |  |  | Other |  | 1996-03-28 | 1996-03-28 | Other |  | Steel/Wrought Iron |  | Rodeo | GREASED VALVE.
| -94 |  |  | 4 | Distribution Main |  | Other |  |  | Other | [5 empty] | Steel/Wrought Iron |  |  | DELETE.
|  |  |  | 12 | Distribution Feeder Main |  | Other |  |  | Other |  | 1981-05-04 |  | Other |  | Steel/Wrought Iron |  | Rodeo
|  |  |  | 6 | Transmission | [6 empty] | 1972-03-28
28 | 77-60134- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-05-23 | 1977-05-23 | Replace Pipe and/or Service |  | Plastic |  | Rodeo | REPLACED 5' OF 2" PLASTIC PIPE BROKEN BY ELECTRIC DEPT. INSTALLING STREET LIGHTING.
28 |  | 105 |  | 24 | [11 empty] | Steel |  | Hercules | PROSPECT DEPTH AND EDGE OF LINE 105
28 |  | 105 |  | 24 | [11 empty] | Steel |  | Hercules | PROSPECT LINE 105 FOR DEPTH AND EDGE.
28 |  | 105 |  | 24 | [11 empty] | Steel |  | Hercules | PROSPECT DEPTH OF LINE 105. DEOTH OF MAIN IS 72 INCHES. INSTALLED ORANGE MAIN MARKER AT THIS LOCATION.
28 |  | 105B |  | 24 | [11 empty] | Steel |  | Hercules | PROSPECT DEPTH OF LINE 105B; UNION MID LINE 5' DEEP FROM T/C.
28 |  | 105B |  | 24 | [11 empty] | Steel |  | Hercules | APROSPECT DEPTH OF LINE 105. DEPTH OF MAIN IS 72 INCHES. INSTALLED ORANGE MAIN MARKER AT THIS LOCATION.
28 |  | 105 |  | 24 | [11 empty] | Steel |  | Hercules | PROSPECT EDGE OF LINE 105 AND DEPTH.
28 |  | 105B |  | 24 | [11 empty] | Steel |  | Hercules | UNION OIL LINE 5' DEEP FROM T/C.
28 | 92-80252-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1992-08-12 | 1992-08-17 | Patch Welded |  | Steel/Wrought Iron |  | Hercules | PATCH WELDED LEAK ON 6" T.P. MAIN.
| 77-60397-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1997-11-15 | 1977-11-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Hercules | RECORDS ONLY. REPLACE 6' OF 6" STL MAIN A/C LEAKAGE. AUGER DUG INTO 6" TP MAIN.
1 |  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Rodeo | MAIN INSPECTION ONLY. NO LEAKAGE. WO4160 D ('77).
28 |  |  |  | 6 | Transmission | [6 empty] | 1985-08-21 | 1985-08-21 |  |  | Steel/Wrought Iron |  | Hercules | TIE IN NEW 2" STL MAIN TO EXISTING 2" TP PIN OFF TEE.
|  |  |  | 6 | [13 empty] | Hercules | INSTALLED 6" BOTTOM TAP FOR MAIN ALTERATION.
|  |  |  | 6 | [13 empty] | Hercules | INSTALLED 6" BOTTOM TAP FOR MAIN ALTERATION.
28 | 88-20714-1 |  |  | 2 | Distribution Main |  | Regulator |  |  | Other |  | 1988-06-23 | 1988-06-23 | Other |  | Steel/Wrought Iron |  | Pinole | REPAIR 301 ON FILTER IN REG. PIT; REPAIRED 301 INSIDE IN REGULATOR VAULT ON FILTER.
28 |  |  |  | 8 | [8 empty] | 1990-01-11 |  |  | Steel |  | Rodeo | PROSPECT DEPTH OF GAS MAIN (4" STEEL DFM IN 8" CASING). EXPOSED CASING ONLY; PROSPECT DEPTH OF CASING 50" DEEP.
28 |  |  |  | 24 | [8 empty] | 1990-01-11 |  |  | Steel |  | Rodeo | PROSPECT DEPTH OF STAND-PAC 3 GAS LINE; PROSPECT DEPTH OF 24" STEEL STAN PAC 3 102 " DEEP. NO CASING UNDER HIGHWAY.
28 |  | 105B |  | 30 | [8 empty] | 1990-01-17 |  |  | Steel |  | Rodeo | PROPSECT DEPTH OF LINE 105 B FOR CAL-TRANS; PROSPECT DEPTH OF CASING 117" DEEP.
28 | 85-60011-1 |  |  | 8 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1985-02-13 | 1985-02-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Pinole | TIGHTENED FLANGE BOTLS AND GREASED VALVE.
28 | 75-20729-1 |  |  | 1 | Other |  | Other |  |  | Other |  | 11/05/0197 |  | Replace Pipe and/or Service |  | Other Plastic |  | Pinole | THIS LEAK HAS BEEN REPAIED ON WO 4054-C. D SARSFIELD, 12-12-75.
28 | 74-20322-1 |  |  | 0.5 | Other |  | Valves |  |  | Construction Defect |  | 1974-08-15 | 1974-09-04 | Other |  | Steel/Wrought Iron |  | Pinole | WORK WITHIN ONE WEEK OF DATE FOUND; 10% SHUT OFF COCK (DEAD SAVES) LEAKAGE, 8-22-74. OK TO DO LATER. 8/24/74. 1) REPLACED 3/4 COCK ON SERVICE. 2) REBUILT METER SETUP.
28 |  |  |  | 8 | [8 empty] | 1990-02-01 |  |  | Steel |  | Hercules | INSTALLED 32 LB MAG ANODE AND BROUGHT WIRE UP INTO VFC.
28 | 89-00222-1 |  |  | 24 | Transmission |  | Valves |  |  | Other |  | 1989-02-16 | 1989-10-12 | Other |  | Steel/Wrought Iron |  | Pinole | GREASED VALVE TO STOP 301.
|  |  |  | 2 | [13 empty] | Hercules | RELOCATE T.P. MAIN.
|  |  |  | 2 | [13 empty] | Hercules | RELOCATE 2" TP MAIN.
28 |  |  |  | 24 | [7 empty] | 1998-08-14 |  |  |  | Steel |  | Hercules | PROSPECT STANPAC#3; ... MAIN 6' OFF FENCE.
1 | 87-- |  |  | 24 | Transmission |  | Other |  |  | Other |  |  |  | Other |  | Steel |  | Hercules
28 | 96-80183-1 |  |  | 0.75 | Distribution Main |  | Other |  |  | Other |  |  | 1996-05-14 | Other |  | Steel/Wrought Iron |  | Hercules | REMOVE REDRESS AND RETIGHTENED FITTINGS ON REG UNIONS; DOPE AND RETIGHTENED.
28 | 96-21208-1 |  |  | 0.75 | Distribution Main |  | Other |  |  | Other |  | 1996-05-13 | 1996-05-14 | Other |  | Steel/Wrought Iron |  | Hercules | REPAIRED LEAKS ON UNION; REPAIRED LEAK.
28 | 89-20151-1 |  |  | 0.75 | Distribution Main |  | Physical/Mechanical Joint |  |  | Other |  | 1989-07-01 | 1989-12-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Hercules | REFER TO M&C DEPART. FOUND LEAK ON TP VALVE IN REG PIT. G. THOMAS 12-29; TIGHTEN FTGS, LEAK SLOWED DOWN. REPLACED FITTINGS IN REG PIT...
28 | 92-80005-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other |  | 1997-01-06 | 1997-01-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Hercules | INST. NEW CAP ON 3/4" FITTING FOR 3/4" PIN OFF TP.
28 |  |  |  | 24 | [11 empty] | Steel |  | Hercules | WELDED AND TAP 1" SERVICE TEE ON MAIN AT THIS LOCATION; WELDED 1 SERVICE TEE VALVE AND MONITOR REGULATOR.
28 |  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1986-07-08 | 1986-07-08 |  |  | Steel/Wrought Iron |  | Pinole | INSTALLED 1 1/4" SERVICE TEE FOR NEW SERVICE.
|  |  |  | 4 | Transmission |  | Other |  |  | Other |  |  | 1978-08-22 | Other |  | Steel/Wrought Iron |  | Pinole | PROSPECTED GAS MAIN AT LOCATION INDICATED BELOW. GAS MAIN AND WRAPS IN GOOD CONDITION.
|  |  |  | 4 | Transmission |  | Other |  |  | Other |  |  | 1978-08-22 | Other |  | Steel/Wrought Iron |  | Pinole | PROSPECTED GAS MAIN AT LOCATION INDICATED BELOW. GAS MAIN IN GOOD CONDITION. GAS MAIN AND WRAPS IN GOOD CONDITION.
28 |  |  |  |  | Distribution Feeder Main | [7 empty] | 1986-10-01 |  |  | Steel/Wrought Iron |  | Pinole | PROSPECT MAIN DEPTH (SAND & ROCK TOWARD VALVE B61)
|  |  |  | 4 | Distribution Feeder Main | [7 empty] | 1986-10-01 |  |  | Steel/Wrought Iron |  | Pinole | PROSPECT MAIN DEPTH.
28 | 98-21016-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1998-03-26 | 1999-05-10 | Other |  | Steel/Wrought Iron |  | Pinole | GREASED VALVE.
|  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1986-10-27 | 1986-10-27 |  |  | Steel/Wrought Iron |  | Pinole | NEW SERVICE; WELD INSPECT. INSTALLED 2' SERVICE TEE FOR NEW SERVICE 1 1/4" PL.
28 | 74-60457-1 |  |  | 4 | Transmission |  | Fitting |  |  | Material Failure |  | 1974-04-04 | 1974-08-12 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Pinole | REPLACED LEAKING 4" TP VALVE WITH NEW VALVE ...
28 |  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1986-11-06 | 1986-11-06 |  |  | Steel/Wrought Iron |  | Pinole | INSPECT AND REWRAP.
28 |  |  |  | 6 | Distribution Feeder Main | [7 empty] | 1986-11-07 |  |  | Steel/Wrought Iron |  | Pinole | NEW SERVICE; MAIN LOCATED UNDER EAST CURB OF TRAFFIC ISLAND. INSTALLED 1 1/4 SERV TEE. ALSO BONDED 2 BLACK ETS WIRES TO MAIN AND INSTALLED VALVE FRAME AND COVER EAST SIDE OF TRAFFIC ISLAND.
28 |  |  |  | 4 | Transmission | [6 empty] | 1986-10-31 | 1986-10-31 |  |  | Steel/Wrought Iron |  | Pinole | WELD INSPECT. C/O 1 1/4" SERVICE. INSTALLED ETS WIRE LEADS 222' N/O MICHAEL (WHITE WIRE).
28 |  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1986-10-29 | 1986-10-31 |  |  | Steel/Wrought Iron |  | Pinole | AT TEE LOCATION MAIN RUN AT SLIGHT ANGLE PARALLEL W/ CURB ON TRAFFIC ISLAND EAST SIDE. ETS WIRES BONDED 4' AWAY. WELD INSPECT LRH. C/O 1 14" SERVICE TEE INSTALLED ETS.
28 |  |  |  | 4 | Transmission | [6 empty] | 1986-11-06 | 1986-11-06 |  |  | Steel/Wrought Iron |  | Pinole | MAIN LOCATED 4' BEHIND CURB. RELOCATE PIPE ... ELBOW.
| 77-40005-1 |  |  | 0.5 | Service |  | Fitting |  |  | Material Failure |  | 1977-01-04 | 1977-01-04 | Other |  | Copper |  | El Sobrante | INSPECTION REPORT A/C REPAIR COPPER SERVICE.
28 | 76-20162-1 |  |  | 0.75 | Service |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1976-03-10 | 1976-05-14 | Other |  | Steel/Wrought Iron |  | Richmond
28 | 76-20160-1 |  |  | 0.75 | Service |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1976-03-10 | 1976-05-14 | Other |  | Steel/Wrought Iron |  | Richmond | SEALED FUZZ LEAK, GODWIN. UNDERGROUND IN AREA; ELECT; PT&T; CABLE TV; NONE KNOWN ... X
28 | 76-20159-1 |  |  | 0.75 | Service |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1976-03-10 | 1976-05-14 | Other |  | Steel/Wrought Iron |  | Richmond | SEALED FUZZ LEAK, GODWIN.
28 | 76-20161-1 |  |  | 0.75 | Service |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1976-03-10 | 1976-05-14 | Other |  | Steel/Wrought Iron |  | Richmond | SEALED FUZZ LEAK.
28 | 76-20158-1 |  |  | 0.75 | Service |  | Fitting |  |  | Construction Defect |  | 1976-03-10 | 1976-05-14 | Other |  | Steel/Wrought Iron |  | Richmond
28 | 76-20157-1 |  |  | 0.75 | Service |  | Fitting |  |  | Construction Defect |  | 1976-03-10 | 1976-05-14 | Other |  | Steel/Wrought Iron |  | Richmond | SEALED FUZZ LEAK AND SERVICE REG, GODWIN.
1 | 71-30401-1 |  |  | 0.75 | Service |  | Fitting |  |  | Corrosion |  | 1971-07-13 | 1972-01-07 | Patch Welded |  | Steel/Wrought Iron |  |  | LEAK AREA REPLACED TEE.
1 | 78-40045-1 |  |  | 0.5 | Service |  | Other Welds |  |  | Other |  | 1978-01-23 | 1978-01-23 | Other |  | Copper |  | El Sobrante | REPAIRED 1/2" CU AT ECLIPSE FITTING (RESOLDERED).
|  |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  | 1976-10-04 |  | Other |  | Steel/Wrought Iron |  | Hercules | GM 492572
|  |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  | 1976-10-01 |  | Other |  | Steel/Wrought Iron |  | Hercules
28 |  |  |  | 4 | Distribution Feeder Main | [7 empty] | 1985-06-03 |  |  | Steel/Wrought Iron |  | Richmond | STL TO POSI HOLD 700. INST. 4" M2 FITTING AND 4" PL TO SH POSI HOLD TO TIE IN NEW PAIN PER GM 4333381,1224,04. GI- 9259.
28 | 95-50040-1 |  |  | 4 | Service |  | Valves |  |  | Other |  | 1995-07-26 | 1996-12-19 | Other |  | Steel/Wrought Iron |  |  | GREASED FOUR VALVES AND TIGHTENED FITTINGS.
28 | 95-50041-1 |  |  | 4 | Service |  | Valves |  |  | Other |  | 1995-07-26 | 1997-01-16 | Other |  | Steel/Wrought Iron
28 | 84-60072-1 |  |  | 3 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-04-30 | 1984-05-03 | Patch Welded |  | Steel/Wrought Iron |  |  | ... PATCHED LEAK...
28 | 83-60145-1 |  |  | 3 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-10-17 | 1984-05-03 | Patch Welded |  | Steel/Wrought Iron |  | Port Costa
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | Port Costa | MEASUREMENT TAKEN FROM S/W CORNER OF LARGE BUILDING IN BRICKYARD.
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | Port Costa | 356 ft. C/O ELEC...
28 | 81-60169-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1981-12-03 | 1981-12-16 | Patch Welded |  | Steel/Wrought Iron |  | Port Costa | ROCKY SOIL CAUSING DAMAGE TO PIPE WRAP. ROAD SUBJECT TO HEAVY VEHICLES. WELD PATCH OVER PIT IN MAIN.
28 | 89-20028-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1989-02-22 | 1989-09-28 | Patch Welded |  | Steel/Wrought Iron |  |  | INST. PATCH WELD 3' C/O PCF. INST. PATCH WELD ON 4" TP.
28 | 90-80397-1 |  |  | 16 | Transmission |  | Longitudinal Weld |  |  | Corrosion |  | 1990-11-06 | 1990-11-06 | Patch Welded |  | Steel/Wrought Iron |  | Berkeley | INST. 1/2 SOLE AND WEDDING BAN ON TP MAIN.
28 | 90-20055-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1990-01-23 | 1990-01-23 | Other |  | Steel/Wrought Iron |  | Berkeley | FOUND LEAK ON VALVE IN REG PIT. REFER TO M&C DEPARTMENT. TIGHTEN VALVE ON STUD.
28 |  |  |  | 16 | [8 empty] | 1990-03-28 |  |  | Steel/Wrought Iron |  | Berkeley | LOWERED 10' OF 16" TP FOR CONFLICT WITH SEWER CROSSING.
|  |  |  | 16 | [11 empty] | Steel/Wrought Iron |  | Berkeley | INSTALLED NEW 3/4" TP SERVICE. INSTALLED ETS AND SERVICE.
28 |  |  |  | 16 | [8 empty] | 1990-03-18 |  |  | Steel |  | Berkeley | WELDED 4" VALVE TO 16" TP FOR A BLOW OFF POINT FOR SHUT DOWN OPERATIONS.
1 | 71-00342-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1971-06-11 | 1972-01-03 | Other |  | Steel/Wrought Iron |  | Berkeley | FOUND VALVES LEAKING. GREASED VALVES TOPPED LEAKAGE.
28 | 73-60194-1 |  |  | 3 | Distribution Feeder Main |  | Valves |  |  | Damage by outside Forces |  | 1973-07-26 | 1973-08-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron
28 | 97-21150-1 |  |  | 3 | Distribution Main |  | Valves |  |  | Other |  | 1997-09-17 | 1997-09-17 | Other |  | Steel/Wrought Iron |  | Berkeley | GREASED VALVE.
28 | 93-35029-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1993-11-19 | 1993-12-01 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Berkeley
28 |  |  |  | 3 | Distribution Feeder Main |  | Other Welds |  |  | Construction Defect |  | 1973-07-13 | 1973-07-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Berkeley | RERUN 7' X 3" STL MAIN.
28 | 84-40426-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-10-22 | 1984-10-22 | Patch Welded |  | Steel/Wrought Iron |  | Berkeley | INST. CHAIN CLAMP. TEMP. PATCH WELDED LEAK, 10-30-84 D. HARRISON.
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1979-04-20 |  | Other |  | Steel/Wrought Iron |  | Berkeley
28 | 97-21152-1 |  |  | 24 | Transmission |  | Valves |  |  | Other |  | 1997-09-17 | 1999-08-17 | Other |  | Steel/Wrought Iron |  | Berkeley | ALREADY COMPLETED. (VALVE GREASED BY M&C DEPT. LONG AGO)
28 | 90-20001-1 |  |  | 24 | Transmission |  | Valves |  |  | Other |  | 1990-01-11 | 1990-09-28 | Other |  | Steel/Wrought Iron |  | B | TIGHTEN AND GREASED VALVE TO REPAIR LEAKAGE
28 | 82-20099-1 |  |  | 2 | Other |  | Other Welds |  |  | Other |  | 1982-02-02 | 1983-02-18 | Other |  | Steel/Wrought Iron |  | BERKELEY | REPAIRED LEAK IN METER SET
28 | 86-20074-1 |  |  | 16 |  |  | Body of Pipe |  |  | Corrosion |  | 1986-02-25 | 1986-02-25 | Weld Over Sleeve or Can |  |  |  | BERK | WELDED (2) PATCHES ON TP MAIN AT 60
|  |  |  | 4 | [8 empty] | 2002-04-24 | [5 empty] | REPAIRED DATE NOT LEGIBLE
| 80-60015 |  |  | 0.5 |  |  | Body of Pipe |  |  | Material Failure |  | 1980-01-16 | 1980-01-16 | Other |  |  |  | Berkeley | Replaced 6" Section of Plastic Service & installed two AMP fit coupling close to riser.
28 | 96-21076-1 |  |  | 3 | Distribution Main |  | Valves |  | GREASED | Other |  | 1996-02-15 | 1997-05-06 | Other |  | Steel/Wrought Iron |  | B | FOUND NO LEAKAGE WITH FLAME PAK. FRESHLY GR CASED (NOT LEGIBLE)
|  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1973-03-28
28 | 92-00037-1 |  |  | 2 | Transmission |  | Valves |  |  | Other |  | 1992-01-27 | 1992-12-09 | Other |  | Steel/Wrought Iron |  | B | REPAIRED BLOW DOWN STACK & VALVE IN PIT
28 | 93-80492-1 |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1993-11-30 | 1993-11-30 | Weld Over Sleeve or Can |  | Steel |  | BERK | INSTALLED 3' OF HALF SOLE PIPE
28 |  |  |  | 16 | Distribution Feeder Main | [12 empty] | BERKELEY | DONE ON WO 47269 B-84
28 |  |  |  | 16 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | BERK | DONE ON WO 47269 B-84
28 |  |  |  | 16 | Distribution Feeder Main | [12 empty] | BERKLEY | DONE ON WO 47269 B-84
28 |  |  |  | 16 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | BERKLEY | DONE ON WO 47269 B-84
28 |  |  |  | 16 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | BERKLEY | DONE ON WO 47269 B-84
28 |  |  |  | 16 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | BERKLEY | DONE ON WO 47269 B-84
28 | 92-20020-1 |  |  | 16 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1992-01-29 | 1992-01-29 | Patch Welded |  | Steel/Wrought Iron |  | BERK | WELDED TWO PACHES ON MAIN.
28 | 84-60081-1 |  |  | 30 | Transmission | [6 empty] | 1984-05-25 |  |  |  | Steel/Wrought Iron |  | BERK | DRILLED HOLES OVER MAIN TO VENT TO ATMOSPHIRE. 5-30-1984 DUG DRY HOLE OVER 30" T.P.
28 | 84-60081-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1984-05-25 | 1984-06-04 | Clamp |  | Steel/Wrought Iron |  | BERKELEY | INST. ONE 4" 2-BOLT SKINNER LEAK CLAMP. GENRING
28 | 77-40098-F |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1977-03-24 | 1977-03-24 | Patch Welded |  | Steel/Wrought Iron
28 | 82-20004-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1982-01-14 | 1982-12-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | BERKELEY | REPLACE 4' OF 4" ...
28 | 98-21006-1 |  |  | 2 | Service |  | Girth Weld |  |  | Corrosion |  | 1998-01-27 | 1998-01-27 | Weld Over Sleeve or Can |  |  |  | B | SHUT DOWN SERVICE REWELDED ELBOW
28 |  | 105A |  | 30 | Transmission | [6 empty] | 1987-02-17 |  |  |  | Steel/Wrought Iron |  | BERKELEY | EXPOSED 2" SERVICE AND 30" MAIN - SOAPED AND FLAME PACKED SERVICE, EXCELLENT / MAIN DID NOT BRAKE WRAP
28 | 81-40202-1 |  |  | 4 | Distribution Main |  | Other |  |  | Other |  | 1981-03-23 | 1982-03-18 | Other | Tighten existing leak clamp | Steel/Wrought Iron |  | BERKELEY | E-4-24 YES ELEC 4G; NO HOT OK 1-19-82; TIGHTEN EXISTING 4" SKINNER CLAMP FOR PERM REPAIR. (BAR TESTED AREA)
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1976-10-19 |  |  |  | Steel/Wrought Iron |  | BERKELEY
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1976-10-19 |  |  |  | Steel/Wrought Iron |  | BERKELEY
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  |  | 1978-09-08 | Bell Joint Seal |  | Steel/Wrought Iron |  | BERKELEY | INSTALLED A NEW SERVICE
|  |  |  | 16 | Distribution Main | [7 empty] | 1977-04-08 |  |  | Steel/Wrought Iron |  | OAKLAND / BERKLEY
28 | 74-20098-1 |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1974-07-26 | 1974-11-11 | Other |  | Cast/Ductile Iron |  | BERKELEY | UNABLE TO READ THE NOTE ON SECOND PAGE
|  |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  | 1980-03-11 | 1980-03-11 | Patch Welded |  | Steel/Wrought Iron |  |  | UNABLE TO READ LEAK SOURCE, LEAK CAUSE, DATE FOUND AND REPAIRED DATE.
28 | 85-20034-1 |  |  | 16 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1985-01-31 | 1985-01-31 | Bell Joint Clamp |  | Cast/Ductile Iron |  | BERKELEY | 30' ON BELT JOINT. INST. BELL CLAMP 2-1-85 PERM. REP VEGA
28 | 95-80185-1 |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1995-07-03 | 1995-07-06 | Patch Welded |  | Steel |  | BERK | WELDED HALF SOLE ON CORROSION LEAK.; 2 REPAIR DATE FOUND.
|  |  |  | 16 | Distribution Feeder Main | [7 empty] | 1974-11-18 |  | MAIN INSPECTION | Steel/Wrought Iron |  | BERKELEY | MAIN INSPECTION THIS TIE-IN LOCATION; INSTALLED 2" VALVE AND TERMINATED ANODE & LOCATING WIRES IN 8" VF & C
28 | 92-80211-1 |  |  | 4 | Distribution Feeder Main |  | Tap Connection |  |  | Construction Defect |  | 1992-07-13 | 1992-09-11 | Patch Welded |  | Other Plastic |  | BERK | WELD SHUT PIN HOLE ON 4" L58 (NOT LEGIBLE)
28 |  |  |  |  | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  |  | UNABLE TO READ LINE SIZE
28 | 93-35049-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1993-11-23 | 1994-02-01 | Weld Over Sleeve or Can |  | Steel |  | B | INSTALLED 2' OF HALF SOLE OVER LEAKING PITTS
| 78-20613-1 |  |  | 3 | Distribution Main |  | Valves |  |  | Material Failure |  | 1978-05-03 | 1978-05-31 | Other |  |  |  | BERKELEY | UNABLE TO READ COMMENTS AND LINE MATERIAL
28 | 72-40225-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-04-24 | 1972-05-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | BERKELEY | replaced too 1 1/4" service with 1" plastic these service were... (UNABLE TO READ PART OF THE COMMENT)
28 |  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | BERKELEY | 83' W/O 62nd ST. ON GROVE INST 1 1/4" SERV. TO 3339 GROVE ST. LOCATING BONDED TO RISER, WRAPED ARROUND SERV. 9 LB ANODE BONDED TO 1 1/4 STL, RISER. 9/5/79 R. WHITE (COMMENT PARTIALLY NOT LEGIBLE)
28 | 77-40177-1 |  |  | 0.5 | Service |  | Other Welds |  |  | Construction Defect |  | 1977-06-10 | 1977-06-10 | Replace Pipe and/or Service |  | Copper |  | BERKELEY | INSPECTION REPORT H/C RERUN SERVICE
28 |  |  |  | 6 | Distribution Feeder Main | [7 empty] | 1983-05-31 |  |  | Steel/Wrought Iron |  | Pinole | Inspected main while installing new service; 2 repaired date found.
28 | 87--1 |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  | 1987-03-26 | 1987-03-26 | Other | PROSPECT | Steel/Wrought Iron |  | PINOLE | PROSPECT 6 GAS MAIN FOR... (LAST WORD NOT LEGIBLE) ; MAIN IS 32" BELOW EXISTING...(LAST WORD NOT LEGIBLE)
|  |  |  | 8 | Distribution Feeder Main | [7 empty] | 1972-09-27 |  |  | Steel/Wrought Iron |  | PINOLE | C/O 3/4" SERVICE
|  |  |  | 6 | Distribution Feeder Main | [7 empty] | 1973-07-05 |  |  | Steel/Wrought Iron |  | PINOLE | RE CONNECTED 3/4" SERV. & ENTENDED IT 160' TO NEW BUILDING USING 1 1/4' STL (COMMENT PARTIALL NOT LEGIBLE)
| 76-40152 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-04-16 | 1976-05-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PINOLE | INSERTED 14' OF 1 1/4" PL. THROUGH OLD STL 2" MAIN AT THIS LOCATION. MAIN WAS BURIED IN CONCRETE AROUND STORE DRAIN AND LEAKING. NO WAY TO RUN STEEL MAIN AROUND THIS LOCATION. (COMMENT PARTICALLY NOT LEGIBLE)
28 | 89-25004-1 |  |  | 22 | Transmission |  | Other Welds |  |  | Other |  | 1989-03-23 | 1989-03-27 | Weld Over Sleeve or Can |  | Steel |  | CROCKETT | AFTER FURTHER INVESTAGATION DETERMINED THIS TO BE A #2, WORK TO CONTINUE
28 |  |  |  | 44 | [8 empty] | 1988-03-03 |  |  | Steel |  | CROCKETT | INSTALLED 2 - #10 WINES TO MAIN AND TERMINATED INTO ETS
|  |  |  | 22 | [7 empty] | 1988-03-03 | 1988-03-03 |  |  | Steel |  | CROCKETT | CAD WELDED 2 - #10 TAN WIRES TO 22" STAN PAC MAIN AND TERMINATED WIRES INTO GS WFC
28 | 74-40424-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-06-28 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CROCKETT | RERAN OLD LEAKING 3/4" STEEL SERVICE WITH 1/2" PLASTIC USING OLD PIPE CASING (COMMENT PARTIALLY NOT LEGIBLE)
| 00-80541-1 |  |  | 6 | Distribution Main |  | Valves |  |  | Other |  | 2000-09-29 | 2001-02-01 | Other |  | Steel/Wrought Iron |  | CROCKETT | HAD M&C GREASED VALVE ON VALVE. (COMMENT NOT LEGIBLE)
28 | 77-60346-1 |  |  | 0.5 | Service |  | Other Welds |  |  | Material Failure |  | 1977-09-15 | 1977-09-15 | Other |  | Copper |  | PORT COSTA | REPAIRED 1/2" COPPER SERVICE AT ECLIPSE LTG.; RESOLDERED 1/2" COPPER ECLIPSE LTG. TO MAKE REPAIRS
26 | 76-20702-1 |  |  | 1 | Other |  | Valves |  |  | Material Failure |  | 1976-05-03 | 1976-09-16 | Other |  | Steel/Wrought Iron |  | PIEDMONT | TIGHTENED COCK AND CORE TO STOP LEAKAGE
| 72-21293- |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-12-11 | 1972-12-12 | Clamp |  | Steel/Wrought Iron |  |  | COMMENT NOT LEGIBLE.
26 | 76-49209 |  |  |  | Other |  | Other |  | NO LEAKAGE | Other |  | 1976-10-29 | 1976-11-04 | Other |  | Other |  |  | UNABLE TO READ THE CITY AND THE THE COMMENT PART.
26 |  |  |  | 4 | Other |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron
|  |  |  | 4 | Other |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron
|  |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-05-23 | 1974-05-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  |  |  | 2 | Other |  | Other |  |  | Other |  | 1979-09-18 | 1979-09-18 | Other |  | Steel/Wrought Iron |  | OAKLAND | MAIN INSPECTION ONLY. INST 1/2" PLASTIC SER D.B.
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1975-05-12 | 1975-05-12 | Other |  | Steel/Wrought Iron |  | OAKLAND
26 | 73-45033 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-02-22 | 1973-02-22 | Clamp |  | Steel/Wrought Iron
| 73-00550-1 |  |  |  | Other |  | Other |  |  | Other |  | 1975-06-27 |  | Other |  | Other |  | OAKLAND | NO GAS READINGS. AREA CLEAR. (UNABLE TO READ THE REST OF THE COMMENT)
26 | 89-20398-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1989-03-06 | 1990-03-29 | Other |  | Steel |  | EMERYVILLE | GREASED BUTTON HEAD VALVE FOR PERM REPAIRS (COMMENT NOT LEGIBLE)
26 | 89-20399-1 |  |  | 2 | Distribution Main |  | Valves |  |  | Other |  | 1989-03-06 | 1990-03-29 | Other |  |  |  | EMERYVILLE | GREASED BLOW OFF WIRE
| 91-10832-1 |  |  | 2 | Service |  | Body of Pipe |  |  | External Corrosion |  | 1991-04-05 | 1991-04-08 | Weld Over Sleeve or Can |  | Steel |  | OAKLAND | WELD 2" STL CAN OVER 301 SERVICE (REMARKS PARTIALLY NOT LEGIBLE)
26 | 91-11149-1 |  |  | 1.25 | Service |  | Tap Connection |  |  | Construction Defect |  | 1991-11-06 | 1992-12-21 | Tighten Cap or Bolt |  | Steel |  | EMERYVILLE | TIGHTENED CAP SERV. TEE
|  |  |  | 0.16 | Distribution Feeder Main | [6 empty] | 1972-05-28 |  |  |  | Steel/Wrought Iron |  |  | UNABLE TO READ THE DATE FOUND.
1 |  |  |  | 6 | Distribution Main |  | Other |  |  | Other |  | 1976-07-19 | 1976-07-19 | Other |  | Cast/Ductile Iron
1 | 81-40660- |  |  | 20 | Transmission |  | Other |  |  | Other |  | 1981-12-01 | 1981-12-03 | Other |  | Steel/Wrought Iron |  | OAKLAND | REPAIRED 301 ON 24" CAN OVER 3" BY PASS VALVE T.P. LINE 105 REPAIRED WAS MADE BY ARC. WELDER REWELDED.
1 | 73-- |  |  |  | Distribution Feeder Main | [6 empty] | 1973-05-11 | 1973-05-11 |  |  | Steel/Wrought Iron |  |  | UNABLE TO READ THE LINE SIZE. DATE FOUND, REPAIRED NOT CLEAR.
26 | 80-48901- |  |  | 1.14 | Service |  | Body of Pipe |  |  | Corrosion |  | 1980-11-24 | 1980-11-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | INSERTED 45 FT. OF 1/2" OF SERVICE.
26 | 73-48277- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-03-08 | 1973-03-08 | Clamp |  | Steel/Wrought Iron |  |  | CORROSION LEAK ON BOTTOM OF SERVICE. REPAIR MADE BY USING CLAMP.
26 | 74-49139- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-09-11 | 1974-09-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | INSTALLED 3/4" LEAK CLAMP. RECOMMEND R/R ON SERVICE.
26 | 73-48460- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-04-12 | 1973-04-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | SERVICE WITH 1/2" PLASTIC.; COMMENT ON THE TOP OF SECOND PAGE IS NOT LEGIBLE.
26 | 73-20399- |  |  | 1.14 | Service |  | Valves |  |  | Other |  | 1973-02-09 | 1973-02-16 | Other |  | Steel/Wrought Iron |  |  | LEAK CAUSE, CORE OF VALVE.; UNABLE TO READ COMMENT ON SECOND PAGE.
| 88-11009-C |  |  | 2 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1988-11-08 | 1988-11-08 | Other |  | Steel/Wrought Iron |  | OAKLAND | CUT OFF 2" BLOW OFF AT 6" STEEL GAS MAIN. ...
| 75-49034- |  |  | 0.12 | Other |  | Other |  |  | Other |  |  | 1975-11-25 | Other |  | Steel/Wrought Iron |  | OAK | NO CO. ONNED LINE EXPOSED. 2 MEN - 1 HR. EA. 11-25-75
| 75-48319-1 |  |  | 1.25 | Other |  | Fitting |  |  | Corrosion |  | 1975-04-18 | 1975-04-18 | Other |  | Steel/Wrought Iron |  | OAKLAND | UNABLE TO READ THE COMMENT ON SECOND PAGE.
|  |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-01-11 | 1974-01-11 |  |  | Steel/Wrought Iron
1 |  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1976-09-08 |  |  |  | Steel/Wrought Iron |  | ALAMEDA
1 |  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1976-09-10 |  |  |  | Steel/Wrought Iron |  | ALAMEDA
|  |  |  | 3 | Other |  | Other |  |  | Other |  | 1973-07-19 | 1973-07-19 |  |  | Steel/Wrought Iron
|  |  |  | 3 | Other |  | Other |  |  | Other |  | 1973-07-19 | 1973-07-19 |  |  | Steel/Wrought Iron
|  |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion | [5 empty] | Steel/Wrought Iron |  | OAKLAND
26 | 87-11520- |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1987-07-18 | 1987-08-17 | Clamp |  | Steel/Wrought Iron |  | OAKLAND | ABLE TO READ COMMENT ON SECOND PAGE.
|  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1973-05-18 | 1973-05-18 |  |  | Cast/Ductile Iron
| 78-20548-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-08-25 | 1979-07-06 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | INSTALLED ONE (1) 16" X 30" CAN MAIN TO REPAIR 301 (COMMENT NOT LEGIBLE)
| 78-20549-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-08-25 | 1979-07-06 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | INSTALLED ONE (1) 16" X 30" CAN ON MAIN TO REPAIR 30' (COMMENT NOT LEGIBLE)
| 78-20547-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-08-25 | 1978-07-06 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | INSTALLED ONE (1) 16" X 30" CAN ON MAIN TO REPAIR 301 (COMMENT NOT LEGIBLE)
| 73-20042-1 | [5 empty] | Other |  |  | Other |  |  | 1973-01-15 | Other |  | Other
|  |  |  | 2 |  |  | Body of Pipe |  |  | Corrosion |  | 1975-03-21 |  |  |  | Steel/Wrought Iron |  |  | UNABLE TO READ LINE USE
|  |  |  | 2 | Service |  | Other |  |  | Other |  |  | 1977-05-13 | Other |  | Steel/Wrought Iron |  | GAS METER SHOP | UNABLE TO READ THE COMMENT ON SECOND PAGE.
|  |  |  | 6 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  |  | 1976-03-23 | Bell Joint Clamp |  | Cast/Ductile Iron |  | OAK | SAME BELL HOLE AS FOR SERVICE R/R/ NO LEAK NUMBER REQUIRED.
| 81-10209- |  |  | 0.34 | Other |  | Meter |  |  | Other |  | 1981-06-03 | 1981-08-05 | Other |  | Steel/Wrought Iron |  | OAK | REPLACED LEAKING 1A CURB METER. (COMMENT NOT LEGIBLE)
26 | 72-20602-1 |  |  | 1.25 | Other |  | Other |  |  | Other |  | 1972-12-27 | 1973-03-12 | Other |  | Other
26 | 75-48194- |  |  | 8 | Transmission |  | Valves |  |  | Other |  | 1975-03-06 | 1975-06-16 | Other | GREASED VALVE | Steel/Wrought Iron
| 95-13757-1 |  |  | 2 | Gathering |  | Other |  |  | Damage by outside Forces |  | 1995-11-07 | 1995-11-07 | Replace Pipe |  | Steel |  | OAKLAND | WELDED NEW PIECE OF S" STL MAIN 2' LONG
| 76-20362-1 |  |  |  | Other |  | Other |  |  | Other |  | 1976-04-06 |  | Other |  | Other |  | OAK | 3% AT TEST JP;E PVER SER. AT EAST SIDE OF ST.; PROBED OVER MAIN & SERVICE, COULD NOT FIND ANY LEAKAGE.;
|  |  |  | 16 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
| 71-1183- |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  |  | 1971-11-15 | Patch Welded |  | Steel/Wrought Iron |  |  | WELDED SEVERAL PATCHES AND WELDING (UNABLE TO READ THE REST OF THE COMMENT)
| 81-40286 |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1981-04-20 | 1981-07-02 | Patch Welded |  | Steel/Wrought Iron |  | OAKLAND | FOUND LEAKAGE ON 16" FEEDER ARC WELD PATCH. CLEARED READY OVER SERVICE. 7-2-81 (COMMENT NOT LEGIBLE)
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1977-12-04 | 1973-12-04 | Other |  | Steel/Wrought Iron
|  |  |  | 3 | Distribution Feeder Main | [6 empty] | 1973-03-22 | 1973-03-23 |  |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 60 | Distribution Feeder Main | [10 empty] | Cast/Ductile Iron |  | OAKLAND
|  |  |  | 6.9 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-02-02 |  | Bell Joint Clamp Replacement |  | Cast/Ductile Iron
|  |  |  | 6.9 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-02-02 |  | Bell Joint Clamp Replacement |  | Cast/Ductile Iron |  | OAKLAND
|  |  |  | 6.9 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-02-13 |  | Bell Joint Clamp - Cast Iron |  | Cast/Ductile Iron
|  |  |  | 6.9 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-02-13 |  | Bell Joint Clamp Replacement |  | Cast/Ductile Iron |  | OAKLAND
|  |  |  | 6.9 |  |  | Bell Joint |  |  |  |  | 1973-02-09 |  | Bell Joint Clamp Replacement |  | Cast/Ductile Iron
|  |  |  | 6.9 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-02-12 |  | Bell Joint Clamp Replacement |  | Cast/Ductile Iron |  | OAKLAND
|  |  |  | 6.9 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-02-12 |  | Bell Joint Clamp Replacement |  | Cast/Ductile Iron
|  |  |  | 6.9 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  |  |  | Bell Joint Clamp Replacement |  | Cast/Ductile Iron
|  |  |  | 6.9 | Distribution Feeder Main |  | Fitting |  |  | Material Failure |  | 1973-02-20 |  | Replace Pipe and/or Service |  | Cast/Ductile Iron |  | OAKLAND
|  |  |  | 6.9 | Distribution Feeder Main |  | Other |  |  | Other |  | 1973-02-12 |  | Replace Pipe and/or Service |  | Cast/Ductile Iron
|  |  |  | 6.9 | Distribution Feeder Main |  | Bell Joint | [6 empty] | Bell Joint Clamp Replacement |  |  |  |  | UNABLE TO READ DATE FOUND.
|  |  |  | 6.9 | Distribution Feeder Main |  | Other |  |  | Other |  | 1973-02-20 |  | Replace Pipe and/or Service |  | Cast/Ductile Iron |  | OAKLAND | UNABLE TO READ THE COMMENT ON SECOND PAGE.
26 | 72-00243-1 |  |  | 6 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1972-03-08 | 1972-03-09 | Clamp |  | Cast/Ductile Iron |  |  | LEAKAGE AT BELL JOINT. REPAIRS MADE BY INSTALLING BELL JOINT CLAMP.
| 82-10661- |  |  | 2 | Other |  | Fitting |  |  | Corrosion |  | 1982-05-28 | 1982-05-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | FOUND LEAKAGE ON 2" CAP OF C/O REPLACE CAP TO STOP LEAKAGE. 5-28-82
| 96-13918-1 |  |  | 0.75 | Distribution Main | TRANSIMMISION MAIN | Body of Pipe |  |  | Damage by outside Forces |  | 1996-01-17 | 1996-01-17 | Replace Pipe |  | Steel |  | OAKLAND | RE BUILT HIGH TO HIGH.; DATE REPAIRED NOT LEGIBLE.
| 96-25-1 | 105A |  | 0.75 | Service |  | Body of Pipe |  |  | Internal Corrosion |  |  | 1996-01-17 | Replace Pipe |  | Steel |  | OAK | UNABLE TO READ LEAK NUMBER.; RE BUILT HIGH TO HIGH SET.
26 | 94-23503-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1994-01-27 | 1995-03-31 | Clamp |  | Steel |  | EMERYVILLE | INSTALLED LEAK CLAMP OVER HOLES IN SERVICE.
|  |  |  | 6 | Transmission | [6 empty] | 1973-03-14 | 1973-03-15 | Other |  | Steel/Wrought Iron |  |  | CUT OFF 3/4" STEEL SERVICE A/O RELOCATION BLDG
26 | 82-10274- |  |  | 1.25 | Other | OLD C/O SERV 1' FROM MAIN | Body of Pipe |  |  | Corrosion |  | 1982-02-22 | 1982-12-08 | Other | C/O SERV AT MAIN | Steel/Wrought Iron |  | OAK | COMMENT NOT LEGIBLE.
26 | 73-00538- |  |  | 2.06 | Other |  | Body of Pipe |  |  | Corrosion |  | 1973-08-20 | 1973-08-21 | Clamp |  | Steel/Wrought Iron |  |  | MADE REPAIRS TO CORROSION LEAK ON 2" STP MAIN WITH STANDARD SKINNER LEAK CLAMP.
26 | 76-55122-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-07-31 | 1976-07-31 | Clamp |  | Steel/Wrought Iron |  | OAKLAND | INST. LEAK CLAMP AS TO STOP GAS LEAK ALSO INST. 1LB. ANODE.
1 | 73-21696-A |  |  | 03SP | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-09-25 | 1973-10-05 | Clamp |  | Steel/Wrought Iron |  |  | INSTALL...
|  |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-07-26 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | R/R 1/2" PLT. METER OUT FROM UNDER HOUSE
26 | 74-55061- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-02-23 | 1974-02-25 | Clamp |  | Steel/Wrought Iron |  |  | MADE REPAIR TO COROSION HOLE 1/16" IN DIAMETER BY USING
|  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  | 1974-05-29 | 1974-05-29 |  |  | Steel/Wrought Iron |  | OAKLAND
| 75-20194-1 |  |  |  | Distribution Feeder Main | [6 empty] | 1975-02-21 | 1975-10-03
26 | 73-49621- |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1973-12-12 | 1973-12-12 | Replace Pipe and/or Service |  | Copper |  |  | STOPPED
26 | 74-25053- |  |  | 0 | Other |  | Other |  |  | Other |  | 1974-10-10 | 1974-11-27 | Other |  | Other |  |  | .03% IN CURB METER BOX; TESTED CURB BOX AND RELATED AREA FOUND NO LEAK OR GAS READINGS; TESTED CURB BOX WITH J.W. INDICATOR ZERO READING - SOAP TESTED ENTIRE BOX AND RELATED FITTINGS, FOUND NO LEAKAGE - PROBE TESTED AROUND BOX ZERO READINGS, HAD FLAME PAK RETEST BOX AND RELATED AREA AND FITTINGS - ZERO READINGS; POSSIBLY SOME ONE REMOVED THE LEAKING METER OR SHUT DOWN A LEAKING HOUSELINE SINCE FIRST READINGS INDICATED
26 | 74-04023-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-12-30 | 1974-12-30 | Clamp |  | Steel/Wrought Iron
26 | 73-55413- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-11-07 | 1973-11-08 | Clamp |  | Steel/Wrought Iron |  |  | USED SKINNER LEAK CLAMP TO REPAIR HOLE 1/4" IN DIAMETER ON 2"STP MAIN
1 | 72-40102-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-04-11 | 1972-04-11 | Clamp |  | Steel/Wrought Iron |  |  | LEAKAGE AT THIS LOCATION; MAIN BADLY PITTED PROBABLY DUE FOR REPLAMCENT. DUE TO MAIN CONDITONING PERMAENT REARS MADEWITH SKINNER CLAM
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1973-09-14 | 1973-09-14 | Other |  | Steel/Wrought Iron |  | OAKLAND
26 | 72-30888-1 | [10 empty] | 1972-03-20
26 | 76-48570- |  |  | 0.34 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-05-21 | 1976-05-24 | Other |  | Steel/Wrought Iron |  | OAKLAND | CUT OFF 3/4"
|  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  | 1973-07-05 | 1973-07-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND
| 76-48533- |  |  | 0.34 | Other |  | Body of Pipe |  |  | Corrosion |  | 1976-05-18 | 1976-05-19 | Other |  | Steel/Wrought Iron |  | OAKLAND | CUT-OFF ABANDONED& LEAKING 3/4 STUD SERVICE A/C CORROSION LEAK - ALSO DUG /DRY HOLE
26 | 73-55248- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-06-08 | 1973-06-08 | Clamp |  | Steel/Wrought Iron |  |  | SMALL HOLE IN 2" IP MAIN REPAIRED WITH SKINNER LEAK CLAMP. LEAK CAUSED BY EXTREMELY ROCKY SOIL IN AREA.
| 75-55232- |  |  | 2 | Other |  | Body of Pipe |  |  | Corrosion |  | 1975-12-05 | 1975-12-06 | Other |  | Steel/Wrought Iron |  | OAKLAND | FOUND & REPAIRED LEAKAGE ON CUST. H/L. BY ABANDON THE DAMAGED SECTION WHICH WAS NOT NEEDED ANY LONGER TO THE CUST.
| 74-55214- | [5 empty] | Body of Pipe |  |  | Corrosion |  | 1974-08-06 | 1974-08-08
26 | 74-48099- |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-01-21 | 1974-01-22 | Clamp |  | Steel/Wrought Iron |  |  | MADE REPAIRS TO PINHOLE WITH ____ PIT IN ____ PIPE. USED SKINNER CLAM TO STOP LEAKAGE. THREE REPAIRS HAVE BEEN MADE TO THIS HOLE BEFORE.
26 | 73-55396- |  |  |  | Other |  | Regulator |  |  | Other |  | 1973-10-12 |  | Other |  |  |  |  | ON STATIC LINES IN REG PIT - REPAIRS MADE
|  |  |  | 4 | Distribution Feeder Main | [7 empty] | 1973-04-16 |  |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-10-23 | 1973-10-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  |  |  | 4 | Distribution Feeder Main |  | Other |  |  | Other |  | 1974-07-26 | 1974-07-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  |  | 1972-10-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | R/R 1/2" PLT. INSERT, ____ REG OUT FROM UNDER HOUSE
|  |  |  | 6 | Transmission |  |  |  | NONE |  | NONE |  | 1974-11-05 |  |  | Steel/Wrought Iron |  |  | INSULATED 6" FLANGE; ATTEMPTED TO INSULATE 6" VALVE #G19 INSULATION WAS NOT COMPLETE ON A/C OF BOTTS ON TOP & BOTTOM COULD NOT BE FULLY INSULATED
26 | 72-40100-1 |  |  | 6 | Distribution Main |  | Other Welds |  |  | Construction Defect |  | 1972-04-05 | 1972-04-06 | Other |  | Steel/Wrought Iron |  |  | LEAKAGE AT SOLDER JOINT DUG SERVICE AT MAIN TO STOP OFF. CLEANED COPPER AT SOLDER JOINT AND RE-SOLDERED.
|  |  |  | 8 | Distribution Feeder Main | [7 empty] | 1975-10-07 |  |  | Steel/Wrought Iron |  |  | INSTALLED__MAIN AT THE ___IN GOOD
26 | 74-55008- |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-01-14 | 1974-01-15 | Clamp |  | Steel/Wrought Iron |  |  | LEAK ON 3" STP MAIN WAS CAUSED BY HOLD 1/16 IN DIAMETER WITH VERY LARGE AND DEEP PIT AREA. ____CLAMP___TO STOP LEAK
|  |  |  | 2 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLAND | WRAPPED 6' OF 2" STP 22' N/S ROYAL OAKS AT APT 12' W/E_ ORINDA VISTA NO PAVING - NO ANODE
| 73-49282- |  |  | 2 | Service |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1973-10-10 | 1973-10-10 |  |  |  | STEEL & PLASTIC, COPPER |  | ____STEEL & PLASTIC; COOPER;NO PAVING; CUT WITH A ____; INSTALL_____
|  |  |  | 12 | Distribution Feeder Main | [7 empty] | 1974-09-16 |  |  | Steel/Wrought Iron |  |  | INST ETS. STATION IN PARKING AREA IN 8" VALVE FRAME WITH (2) #10 TEST LEADS.
|  |  |  | 12 | Distribution Feeder Main | [7 empty] | 1974-09-16 |  |  | Steel/Wrought Iron
|  | 81-40343-1 |  | 1.25 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1981-05-13 | 1981-05-13 | Other |  | Other Plastic |  | OAKLAND | BROKE 1 14" PL MAIN; FOR REPAIR OF 1 1/4" PL MAIN (OB) DAMAGED BY CONTRACTOR - 1- AMP. FIT COUP & 1 - AMP. FIT REPAIR WAS INSTALLED TO REPLACE 1' OF 1 14";
|  |  |  | 0.75 | Distribution Feeder Main |  | Other |  |  | Other |  | 1977-11-06 | 1977-11-06 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | OAKLAND | C/O 3/4" SERVICE AT ___ & RISER
26 | 73-48881- |  |  | 0.34 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-07-03 | 1973-07-06 | Clamp |  | Steel/Wrought Iron
1 | 73-48881-A |  |  | 0.5 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-07-06 | 1973-08-22 | Replace Pipe and/or Service |  | Other Plastic |  |  | INSTALL 1/2 PLASTIC SERVICE TO STOP LEAKAGE
|  |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-06-17 | 1972-06-17 | Clamp |  | Steel/Wrought Iron |  | OAKLAND | INST. 2- 1 1/4" CLAMP ON PITTED SERVICE.
26 | 74-22752- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-07-26 | 1974-07-26 | Clamp |  | Steel/Wrought Iron
|  |  |  | 3 | Other |  | Other |  |  | Other |  | 1980-03-19 |  | Other |  | Steel/Wrought Iron |  | OAKLAND | EXCAVATED BELL HOLE TO TIE IN MAIN
26 | 74- |  |  | 0.75 | Other |  | Fitting |  |  | Material Failure |  | 1974-07-29 | 1974-08-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | FOUND LEAKS ON METER SET AT TEE JUST ABOVE SHUT OFF AND AT TEE ON OUTLET OF METER. REBUILT METER SET TO STOP LEAKAGE; REPAIRED LEAKS ON METER SET & HOUSELINE BY REBUILDING SET.
26 |  |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Material Failure |  | 1972-04-13 | 1972-04-14 | Clamp |  | Steel/Wrought Iron |  |  | EXISTING 3/4" SKINNER CLAMP LEAKING CLAMP TIGHTENED; RETEST O.K.
26 | 74-25081- |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-10-10 | 1974-10-21 | Other |  | Steel/Wrought Iron |  |  | 7% IN CURB (BOX (METER); 301 ON CUST. HOUSELINE IN CURB METER BOX SERVICE DEPT. C/O GAS AND ISSUED HAZZARD TAG
26 | 73-49294- |  |  | 03SP | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-10-12 | 1973-10-15 |  |  | Steel/Wrought Iron |  |  | INSTALL ... PATCHES TO ...
|  |  |  | 8 | Distribution Feeder Main | [7 empty] | 1974-08-15 |  |  | Steel/Wrought Iron |  |  | INST (1) POLE MOUNTED RECTIFISH & LEADS IN 1"______ &I NST TEST LEADS ON 8" MAIN IN 1" PLASTIC DUCT.
26 | 73-49443- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-11-15 | 1973-11-19 | Clamp |  | Steel/Wrought Iron |  |  | DEEP PIT ON 2" MAIN OTHER THEN LEAK AREA MAIN LOOKS FINE
|  |  |  | 8 | Distribution Feeder Main | [7 empty] | 1974-08-21 |  |  | Steel/Wrought Iron |  |  | INST ETS STATION IN______TEST____
|  |  |  | 8 | Distribution Feeder Main | [7 empty] | 1974-08-22 |  |  | Steel/Wrought Iron |  |  | INST ETS. STATION IN _____ IN 8" VALVE FRME WITH 2# 10 TEST LEAKS.
|  |  |  | 8 | Distribution Feeder Main | [7 empty] | 1974-08-22 |  |  | Steel/Wrought Iron |  | OAKLAND | INST E.T.S. STATION IN PARKING AREA IN 8" VALVE FRAME, WITH (2) #10 ____LEADS.
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1973-11-08 | 1973-11-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron
26 | 72-20272-1 |  |  | 3 | Transmission |  | Other |  |  | Other |  | 1972-11-14 |  | Other |  | Steel/Wrought Iron |  |  | BATTERY CO. ON 98TH AVE. .5% WATER BOX AT BATTERY CO.; BAR TESTED OVER MAIN FOR A DISTANTS OF 50' IN EITHER DIRECTION OF WATER BOX. COULD GET NO GAS READINGS OVER MAIN OR IN WATER BOX.; COULD FIND ONO GAS LEAKAGE
| 80-48346-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-04-10 | 1980-04-10 | Other |  | Plastic |  | OAKLAND | USED 2 - AMP-FIT COUP. & 1' OR 1/2"PL TO REPAIR BROKE SERV
26 | 72-30909-1 |  |  | 3 | Distribution Main | [6 empty] | 1972-03-22 |  |  |  | Steel/Wrought Iron |  |  | PROBED FOR LEAKAGE OVER MAIN & SERVICE FOUND NO LEAKEGE.; DATE OF RECHECK 04-24-1972
| 78-- |  |  | 0.75 | Service |  | Fitting |  |  | Material Failure |  | 1978-02-27 | 1978-02-28 | Other | TIGHTEN UP FITTING | Steel/Wrought Iron |  | OAKLAND | LEAK BELOW SERVICE VALVE; MADE REPAIR BELOW SERVICE VALVE, BY TIGHTEN UP FITTING
|  |  |  | 12 | Distribution Feeder Main | [7 empty] | 1974-09-11 |  |  | Steel/Wrought Iron |  | OAKLAND | INST E.T.S. STATION IN PARKING AREA IN 8" VALVE FRAME WITH (2) #10 TEST LEADS.
|  |  |  | 2 | Other |  | Other |  |  | Other |  | 1975-01-13 | 1975-01-13 | Replace Pipe and/or Service |  | Steel/Wrought Iron
26 | 73-55310- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-07-12 | 1973-07-12 | Clamp |  | Steel/Wrought Iron |  |  | LOCATED (3) THREE LEAKS ON 3/4"STELL SERVICE THAT APPEARS TO HAVE BEEN RECENTLY CUT AND TESTED. USED SMITH-BLAIR TO MAKE REPAIRS.
20 | 73-49036- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-08-01 | 1973-08-01 | Clamp |  | Steel/Wrought Iron |  |  | LOCATED TWO(2) LEAKS IN 3FT. AREA, PIPE IS POSSIBLY IN POOR CONDITION THROUGHOUT. REPAIRS MADE WITH SMITH-BLAIR CLAMPS.
26 |  |  |  | 0.34 | Service | [6 empty] | 1982-02-19 | 1982-02-19 | Other |  | Steel/Wrought Iron |  | OAKLAND | MOVE SERVICE RISER
26 | 73-49614- |  |  | 0.75 | Service |  | Body of Pipe | Valves |  | Damage by outside Forces |  | 1973-12-11 | 1973-12-11 | Clamp |  | Steel/Wrought Iron |  |  | USED CLAMP TO STOP LEAKAGE ON 3/4" SER. LEAKAGE CAUSED BY BROKEN CURB VALVE AND CASING LAYING ON SERVICE.
26 | 73-55306- |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-07-10 | 1973-07-10 | Clamp |  | Steel/Wrought Iron |  |  | MADE REPAIRS ON 3" STP MAIN BY USING SKINNER LEAK CLAMP. CORROSION HOLE APPROX. 1/8" IN DIAMETER. ANODE ATTACHED.
26 | 74-22963- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-11-18 | 1974-11-18 | Clamp |  | Steel/Wrought Iron
26 | 72-40044-1 |  |  | 0.5 | Service |  | Other Welds |  |  | Corrosion |  | 1972-04-07 | 1972-04-10 | Replace Pipe and/or Service |  | Copper |  |  | LEAKAGE AT SOLDER JOINT ON RISER RISER ALSO VERY RUSTY. REPLACED RISER
| 73-55497-1 |  |  | 1.5 | Other |  | Physical/Mechanical Joint |  |  | Other |  | 1973-12-28 | 1973-12-28 | Other |  | Steel/Wrought Iron |  |  | FOUND 1 1/2" UNION LEAKING ON CURB METER SET. TIGHTENED UNION TO STOP LEAKAGE. CHECKED AREA, FOUND NO OTHER LEAKAGE; DID NOT DIG MAIN; TIGHTENED UNION TO STOP LEAKAGE.; ; ; ; ; ; ; ; ; FOUND 1 1/2" UNION LEAKING ON CURB METER SET. TIGHTENED UNION TO STOP LEAKAGE. CHECKED AEA, FOUND NO OTHER LEAKAGE.;;
1 | -20294- |  |  |  | Other |  | Other |  |  | Other |  |  | 1972-11-21 | Other |  | Steel/Wrought Iron |  |  | FOUND NO LEAKAGE. DID NOT DIG
|  |  |  | 8 | Distribution Feeder Main |  | Other | Other |  | Other |  |  | 1976-03-25 | Other |  | Steel/Wrought Iron |  | OAKLAND | INST. 9' OF #6 WIRE IN 1"PL. BOND 8" MAIN TO 2" MAIN.
26 | 72-20305-1 |  |  | 3 | Distribution Feeder Main |  | Other |  | NONE | Other | NONE | 1972-11-15 | 1972-11-28 | Other | NONE | Steel/Wrought Iron |  |  | CHECKED WATER BOXES 1 GAS SERV VALVE +4 GAS TANK FEEDER INLETS TO SERV STATION GAS TANKS AND FOUND NO LEAKAGE + BAR TEST HOLES OVER MAIN GOT NO READINGS SUGGEST RETEST WITH FLAME PACK MAIN NOT EXPOSED THERE IS NO GAS SERV TO 9868 MACARTHUR; MAIN OR SERV NOT INSPECTED
26 | 72- |  |  | 8 | Distribution Main |  | Other |  |  | Other |  | 1972-02-04 | 1972-02-04 | Other |  | Steel/Wrought Iron |  | OAKLAND | INST. TWO 8" P.C.F. BOTTOM TAPS CUT 8" MAIN FOR INSULATING INST. 2-8" FLANGES; ROUTINE WORK
26 | 74-23007- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-08-08 | 1974-11-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | 2% OVER SEE Y. IN STREET READINGS AT RISER & ACROSS GARGE DOOR INTRANCE VERY STRONG ODOR IN STREET SERV. PROBABLY; NEEDS TO BE RERAN; USED SKINNER-CLAMPS TO STOP LEAKAGE ON 3/4" SERVICE. HAVING SERVICE REPLACED DUE TO ADDITIONAL L.E.L. READINGS AND POOR CONDITION OF PIPE.
26 | 74-49455- |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-11-26 | 1974-11-27 | Clamp |  | Steel/Wrought Iron
| 74-23028- |  |  | 2 | Other |  | Other |  |  | Other |  | 1975-01-18 | 1975-01-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron
26 | 73-55345- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-08-27 | 1973-08-28 | Clamp |  | Steel/Wrought Iron |  |  | MADE REPAIRS TO CORROSION___ ON 2" STP MAIN WITH SKINNER LEAK CLAMP.
| 72-48477- |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  |  | 1972-11-28 |  |  | Steel/Wrought Iron |  | OAKLAND | R/R 1/2" ... 1# ANOID USED ASTMD 2513 PLT. INSERT.
26 | 82-00860- |  |  | 1 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1982-12-17 | 1983-01-31 | Other |  | Steel/Wrought Iron |  | OAKLAND | 301-ON SERV. VALVE;
| 72-48019- |  |  | 4 | Distribution Feeder Main |  |  |  |  | Corrosion |  | 1972-02-11 | 1972-02-11 | Clamp |  | Steel/Wrought Iron |  | 1972-02-11 | INST. (1) 4" SKINNER ON 4" TP 6' E/S PARK AT A PT ______
1 | 71- | [16 empty] | OAKLAND | TEST 2" SER TIE ON 12" TP MAIN GM465080-1224-11; GOOD
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLAND | ;
26 | 94-24103-1 |  |  | 12 | Transmission |  | Valves |  |  | Other |  | 1994-07-26 | 1995-08-15 | Other |  | Steel/Wrought Iron |  | OAKLAND | GREASED VALVE #X65
26 | 96-25293-1 |  |  | 20 | Transmission |  | Valves |  |  | Corrosion |  | 1996-01-22 | 1996-12-09 | Other |  | Steel/Wrought Iron |  | OAKLAND | REWORKED VALVE X1 WITH VALVE CREW
| 97-14679-1 |  |  | 6 | Transmission |  | Fitting |  |  | Corrosion |  | 1997-02-07 | 1997-03-12 | Other |  | Steel/Wrought Iron |  | OAKLAND | COUPING ON BLOW OFF VALVE ROTTED THROUGH.; REPLACED BLIND FLANGE ON VALVE W/ NEW ONE.
| 74-48684-1 |  |  | 24 | Transmission |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron |  |  | NO LEAK FOUND AT THIS_______
26 | 73-49278- |  |  | 1.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-10-09 | 1973-10-09 | Clamp |  | Steel/Wrought Iron |  |  | USED SKINNER CLAMP TO MAKE REPAIR ON LEAKING 1 1/4 UNTIL SERVICE CAN BE REPLACED
|  |  |  | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | NO ANODE
|  |  |  | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | INSPECTION & INST. 20" WEDDING BAND OVER 20" GAS WELD NO ANODE
| 79-49024- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-12-27 | 1980-01-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | INSERT 1/2" PLASTIC 3/4"CASING
26 | 75-20154- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-02-19 | 1975-02-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | INSTALLED NEW ... TO ELIMINATE LEAKAGE
| 79-48070-F |  |  | 0.75 | Service |  | Fitting |  |  | Material Failure |  | 1979-01-23 | 1979-01-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | REPLACE 3/4" SERVICE VALVE DUE TO ...
|  |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  |  |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | R/R 1/2" PLT SERVICE IN CASING
|  |  |  | 2 | Distribution Feeder Main | [6 empty] | 1972-04-07 |  |  |  | Steel/Wrought Iron
26 | 75-48471- |  |  | 4 | Service |  | Girth Weld |  |  | Damage by outside Forces |  | 1975-06-06 | 1975-06-09 | Other |  | Steel/Wrought Iron |  |  | WELDED 4" CAN OVER 4" LEAK CLAMP
26 | 73-48453- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-04-10 | 1973-04-10 | Patch Welded |  | Steel/Wrought Iron |  |  | PLACED TEMPORARY CLAMP ON RISER OF 3/4" SERVICE. SERVICE SHOULD BE REPLACED DUE TO APPARENT BAD CONDITON OF PIPE.
26 | 77-48849- |  |  | 0.84 | Service |  | Body of Pipe |  |  | Corrosion |  | 1977-08-30 | 1977-08-30 | Clamp |  | Steel/Wrought Iron |  | OAKLAND | MADE REPAIRS TO LEAKING STEEL SERVICE DID NOT ...
| 77-00050-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe | Valves |  | Corrosion |  | 1977-04-22 | 1977-08-17 | Clamp |  | Steel/Wrought Iron |  | OAKLAND | FOUND LEAK 3" H MAIN INST (1) 3X4 SKINNER CLAMP TO STOP LEAK. MAIN IS VERY BADLY PITTED & SHOULD BE REPLACED S.AP
|  |  |  | 1.14 | Distribution Feeder Main |  | Other |  |  | Other |  | 1972-04-04 | 1972-04-05 | Weld Over Sleeve or Can |  | Plastic
|  |  |  | 0.04 | Distribution Feeder Main | [6 empty] | 1972-06-23 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-05-21 | 1974-05-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND
2 | 87-40500-F |  |  | 16 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1987-02-10 | 1987-02-10 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | OAKLAND | 301 ON METRIC - PIPE DOPE AND TIGHTEN
|  |  |  | 16 | Distribution Feeder Main | [6 empty] | 1976-11-05 |  | Other |  | Steel/Wrought Iron |  |  | INSTALLED E.T.S STATION OPPOSITE DRIVEWAY TO 196 GLENWOOD GLADE.; GM-492295-1224; 5-4000
26 | 77- |  |  | 16 | Distribution Feeder Main |  | Other |  |  | Other |  | 1977-07-25 | 1977-07-26 | Other |  | Steel/Wrought Iron |  | OAKLAND | 2' S/S P/L OF BDWY. TERR. & 3' W/E P/L OF GLENWOOD GLADE; EXPOSED MAIN TO ALTER TELEMETER TRANSMITTER SERV. LINE.
|  |  |  | 16 | Distribution Feeder Main | [6 empty] | 1976-11-09 | 1976-11-09 |  |  | Steel/Wrought Iron |  | OAKLAND | INSTALLED E.T.S STATION & TWO TESTED LEADS FROM 16" HP MAIN.
|  |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-12-11 | 1971-12-12 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | REPLACED 5' OF 3/4" SERV
26 | 73-45036- |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-02-28 | 1973-03-02 | Patch Welded |  | Steel/Wrought Iron |  |  | FOUND TWO (2) CORROSION LEAKS ON 3/4" SERVICE; REPAIR WITH SKINNER CLAMP.
26 | 73-48325- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-03-16 | 1973-03-16 | Clamp |  | Steel/Wrought Iron |  |  | (3) THREE LEAKS ON 3/4" S/P SERVICE TEMPORARY REPAIRS MADE WITH CLAMPS. THIS MAKES (5) FIVE REPAIRS MADE ON SERVICE; SHOULD BE RE-RUN.
|  |  |  | 4 | Distribution Feeder Main |  | Other |  | NEW SERV. | Other | NEW SERV. |  | 1972-08-16 | Other | NEW SERV | Steel/Wrought Iron |  |  | RAN NEW SERVICE TO 6861 BROADWAY TERR
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  |  | 1973-05-25 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | SERV R.R. DUE TO LEAK ON STEP ... UNDER HOUSE
| 73-22061- |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-12-19 | 1973-12-20 |  |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  |  | 1972-10-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | R/R 1/2"PLT. SERV. INSERT
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-02-04 | 1974-02-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron
25 | 77-48926- |  |  | 0.75 | Other |  | Other |  |  | Other |  | 1977-09-13 | 1977-09-15 | Other |  | Steel/Wrought Iron |  |  | SERV. BLOWING OUTSIDE CURB BOX AT 4051 WAT'S; REG. HIGH TO HIGH; FOUND 3/4____
1 | 80-20017-1 |  |  | 0.34 | Other | BLOW OFF VALVE | Fitting |  |  | Corrosion |  | 1980-01-04 | 1980-02-28 | Replace Pipe and/or Service | NEW FITTING | Steel/Wrought Iron |  | OAKLAND | (STRONG ODOR) AT SERV. ALSO AT VALVE IN STREET; LEAKING 1 1/2"X 3/4" SCREWED FITTING IN E.T.S. DUG UP V.F.&C. & REPLACED OLD FITTING ON SERV. VALVE TO STOP LEAKAGE.
| 74-55104- |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-04-01 | 1974-04-02 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | OAKLAND | INST 4 PATCHES OVER LEAKING PITS ALSO FOUND OTHER PITS TO 190 DEPTH ON MAIN AND WELDED SMALL PATCHES OVER PITTED AREA MAIN SHOULD BE PUT UNDER CATOTHATIC PROTECTION AS SOON AS POSSIBLE
|  |  |  | 16 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1973-04-16 | Other | OVER AREA | Steel/Wrought Iron |  |  | SLIDE AREA; ___ 1 1/4 SERV TEE AND 1 1/4 MUELLER ______TIE IN TO 3"___IN CASE OF SLIDE
26 | 74-55098- |  |  | 0.34 | Other | C/O | Other |  | C/O SERV | Corrosion |  | 1974-03-22 | 1974-03-23 | Other |  | Steel/Wrought Iron |  |  | C/O PIPE + RE CAPPED
1 | 80-20010-1 |  |  | 1.14 | Other |  | Tap Connection |  |  | Construction Defect |  | 1980-01-03 | 1980-03-07 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | OVER MAIN, IN W/B NEAR MAIL BOX STRONG ODOR IN AIR; INST. 3" CAN OVER LEAKING 1 1/4" STEEL COUPLING TO REPAIR LEAKAGE. MAIN 3" STEEL 64" DEEP
1 | 72-45124-H |  |  | 02.5H | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-05-18 | 1972-05-19 | Clamp |  | Steel/Wrought Iron |  |  | INSTALL 2 ... 9# ANODE
| 71-01146-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-08-01 | 1972-08-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | R/R 1/2" P.L.T SERVICE IN CASING MOVE OUT FROM UNDER HOUSE. 21' OF HOUSE LINE
|  |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-08-01 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | R/R 1/2" PLT. SERVICE INCASING MOVE METER OUT FROM UNDER HOUSE. 21' OF HOUSE LINE
26 | 78-48002-1 |  |  | 0.34 | Service |  | Fitting |  |  | Damage by outside Forces |  | 1978-01-03 | 1978-01-03 | Replace Pipe and/or Service | EARTH SHIFT; MADE REPAIR TO SERV. DID NOT EXPOSE MAIN. | Steel/Wrought Iron |  | OAKLAND
| 73-01215- |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1973-12-17 | 1974-01-23 | Other | DRY HOLE | Steel/Wrought Iron |  | OAKLAND | DUG ... HOLE EXCAVATING ...
| 73-01216- |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1973-12-17 | 1974-01-28 | Other |  | Steel/Wrought Iron |  | OAKLAND | DUG DRY HOLE HUNTING LEAK HOLE 3X43.
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other | [5 empty] | Steel/Wrought Iron
|  |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-10-18 | 1974-10-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | (LEAK IN BP OF SERVICE.) SERVICE REPLACED
| 74-20388- |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-05-24 | 1974-05-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 3 | Distribution Feeder Main |  | Other |  | NEW SERVICE | Other | NEW SERV. |  | 1972-08-28 | Other | RUN NEW SERV. | Steel/Wrought Iron
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-05-20 | 1974-05-20 |  |  | Steel/Wrought Iron |  | OAKLAND
26 | 73-48618- |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-05-11 | 1973-05-21 | Patch Welded |  | Steel/Wrought Iron |  |  | REPAIRED CORROSION LEAK ON BOTTOM OF 3" STP BY USING SKINNER CLAMP. ANODE ATTACHED.
26 | 72-48331-A |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-09-25 | 1972-10-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | R/R 1/2" PLT. INSERT USED 1# & 6# ANOID USED ASTM D 2513 PLT. BELL HOLE IN ST. 2 1/2X3 1/2'X6"
| -22124- |  |  | 0.5 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-06-27 | 1974-06-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 3 | Distribution Feeder Main |  | Other |  | NEW SERV | Other | NEW SERV. |  | 1972-11-21 | Other | RAN NEW SERV. | Steel/Wrought Iron |  | OAKLAND | RAN NEW 1/2" PLT. SERV. BARE
|  |  |  | 3 | Distribution Feeder Main | [6 empty] | 1973-05-16 | 1973-05-16 |  |  |  |  | OAKLAND
26 | 97-26924-1 |  |  | 0.75 | Service |  | Fitting |  |  | Construction Defect |  | 1997-08-04 | 1998-10-29 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | OAKLAND | TIGHTEN FITTING ON 3/4" FITTING ELBOW
| 77-49249- |  |  | 12 | Transmission |  | Other |  |  | Material Failure |  |  | 1977-11-29 | Other |  | Steel/Wrought Iron |  |  | ...
|  |  |  | 10 | Transmission | [7 empty] | 2000-12-13 |  |  | Steel/Wrought Iron |  | OAKLAND | CADWELDED (2) ETS ... 10" T.P. LINE TO TREASURE ISLAND PER ....
|  |  |  | 12 | Transmission | [7 empty] | 1986-12-23 |  |  | Steel/Wrought Iron |  |  | CADWELDED (2) ETS_____TO T.P. LINE ____
|  |  |  | 12.75 | [13 empty] | OAKLAND
1 | 95-13424-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Other |  | 1995-05-15 | 1995-05-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | REPLACED AND REROOTED 33' OF 3/4 T.P. GAS SERVICE A/C DIGIN AND GAS LINE IN SERVICE OF FACILITES
26 | 71- |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1971-12-20 | 1971-12-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | RERAN SERVICE DUE TO COPPER SERVICE NOT DESIGNED FOR T.P. PRESSURE. RERAN WITH STEEL.; R/R SERVICE
|  |  |  | 6 | Distribution Feeder Main | [5 empty] | MAIN EXTENSION & DOWN GRADE |  | 1973-08-24 |  |  | Steel/Wrought Iron |  |  | MAIN (6" T.P.) IINSPECTED AT LOCATION OF SERV. TEE., WRAP IN GOOD SHAPE - NO LEAKAGE DETECTED. SERV. TRANS. TO 2# ___. PLASTIC.
|  |  |  | 6 | Distribution Feeder Main | [7 empty] | 1977-08-24 | [5 empty] | MAIN EXTENSION & DOWN GRADE; MAIN (6"T.P.) INSPECTED AT LOCATION OF SERV. TEE, WRAP IN GOOD SHAP-NO LEAKAGE DETECTED. SERV. TRANSFERRED TO 2' PLASTIC.
|  |  |  | 6 | Distribution Feeder Main | [7 empty] | 1973-08-24 |  |  | Steel/Wrought Iron |  |  | MAIN EXTENSION & DOWN GRADE; MAIN (6'__) INSPECTED AT THIS LOCATION-FOUND NO LEAKAGE - WRAP IN GOOD SHAPE
| 73-- |  |  | 4 | Distribution Feeder Main |  | Other |  |  | Other |  | 1973-05-17 | 1973-05-17 |  |  | Cast Iron |  |  | C/O THIS SERVICE TO ____
26 |  |  |  | 2 | Other |  | Other |  |  | Other |  | 1972-08-11 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND
26 |  |  |  | 2 | Other |  | Other |  |  | Other |  | 1972-08-11 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND
26 |  |  |  | 2 | Other |  | Other |  |  | Other |  | 1972-08-11 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 8 | Transmission | [6 empty] | 1973-01-19 |  |  |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 8 | Transmission | [6 empty] | 1973-01-19 |  |  |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 8 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1973-08-10 | Other |  | Steel/Wrought Iron
26 |  |  |  | 4 | Other |  | Other |  |  | Other |  | 1972-08-11 |  | Replace Pipe and/or Service |  | Cast Iron
26 |  |  |  | 2 | Other |  | Other |  |  | Other |  | 1972-08-11 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND
26 |  |  |  | 2 | Other |  | Other |  |  | Other |  | 1972-08-11 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 2 | Other |  | Other |  |  | Other |  | 1972-08-11 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron
| 82-00135- |  |  | 0.34 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1982-03-04 | 1982-03-04 | Other | C/O SERV | Steel/Wrought Iron |  |  | C/O 3/4' TP SERV ___TEE INSTALLED CAN OVER TEE
26 | 89-20370-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1989-02-15 | 1990-05-11 | Other |  | Steel/Wrought Iron |  | EMERYVILLE | C/O 3/4" STL SERVICE TO CLEAR LEAK
| 95-13512-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1995-07-10 | 1995-07-10 | Patch Welded |  | Steel/Wrought Iron |  | EMERYVILLE | ARC WELDED PATCH OVER HOLE IN 6" STEEL T.P. GAS MAIN (ON BOTTOM OF MAIN AT 4 OCLOCK) CORROSION LEAK. (SMALL PIN HOLE, NICKLE PIT)
1 | 95-13527-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1995-07-11 | 1995-07-11 | Patch Welded |  | Steel/Wrought Iron |  | OAKLAND | ARC WELDED PATCH OVER HOLE IN 6" STEEL T/P MAIN CORROSIONLEAK ON BOTTOM 29' _____
| 95-13534-1 |  |  | 6 | Distribution Feeder Main |  | Tap Connection |  |  | Digin |  | 1995-07-13 | 1995-07-13 | Patch Welded |  | Steel/Wrought Iron |  | EMERYVILLE | SHUT -DOWN MAIN AND WELDED PATCH OVER 1/2" HOLE IN MAIN.
26 | 7348310-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-03-14 | 1973-03-15 | Patch Welded |  | Steel/Wrought Iron |  |  | WELDED PATCH TO MAIN FOR PERMANENT REPAIRS
26 | 86-20043- |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1986-02-18 | 1987-02-05 | Patch Welded |  | Steel/Wrought Iron |  | EMERYVILLE | ARC WELDED PATCH OVER HOLE & SEVERAL PITTS IN 3" STEEL GAS MAIN; CORROSION LEAK
26 | 88-20096-1 | [10 empty] | 1988-03-23 | [5 empty] | EMERYVILLE
| 03-12186- |  |  | 1.25 | Service |  | Valves |  |  | Construction Defect |  | 2003-08-01 | 2003-08-01 |  | REPLACED VALVE | Steel/Wrought Iron |  | EMERYVILLE | CHANGED BY - PASS VALVE
26 | 73-484281- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1973-04-05 | 1973-04-05 | Clamp |  | Steel/Wrought Iron |  |  | 130 PSI; INSTALLED 2" SKINNER LEAK CLAMP
| 75-21292-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-10-21 | 1976-02-19 | Clamp |  | Steel/Wrought Iron |  | EMERYVILLE | 10% + AT W/B & .03% AT CURB MTR. BOX IN S/W.; FUZ LEAK ON SERV. CLAMPED. SERV IN GOOD CONDITION
26 | 88-20097-1 |  |  | 0.75 | Service |  | Fitting |  |  | Material Failure |  | 1988-03-23 | 1984-04-11 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EMERYVILLE | REDOPED AND TIGHTENED SERVICE VALVE UNION
| 98-10436- |  |  | 2 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1998-11-17 | 1998-11-17 | Patch Weld - Weld |  | Steel/Wrought Iron |  | ; EMERYVILLE
26 | 97-26943-1 |  |  | 0.75 | Service |  | Tap Connection |  |  | Construction Defect |  | 1997-08-06 | 1998-12-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EMERYVILLE | SVC TEE; REPAIRED TEE
|  |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1972-04-25 | Other |  | Steel/Wrought Iron |  |  | NEW SERVICE & CUT-OFF.
| 72-45083- |  |  | 1.25 | Service | TRANSMISSION | Body of Pipe |  |  | Corrosion |  | 1972-04-13 | 1972-04-14 | Clamp |  | Steel/Wrought Iron
26 | 73-48364-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-03-26 | 1973-03-27 | Patch Welded |  | Steel/Wrought Iron |  |  | ... 8"X5" ... TO MAIN
26 | 73-48363-1 |  |  | 6 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 1973-03-26 | 1973-03-27 | Patch Welded |  | Steel/Wrought Iron |  |  | WELDED OVER ___ 6" PCF
26 | 74-21634- |  |  | 6 | Distribution Main |  | Fitting |  |  | Corrosion |  | 1974-05-24 | 1974-11-18 | Other |  | Steel/Wrought Iron |  |  | GAS VALVE IN STREET 5' FROM CORNER; EXISTING 6" PCF; .3% IN STREET VALVE ON S/W COERN & .02% IN SEWER.; WELDED CAN OVER A LEAKING 6" P.C.F. ALSO CANNED A 6" VALVE & 6" MAIN TEE A/C ____ NEEDED TO INST. CAN.
| 01-15101-C |  |  | 0.75 | Service | TRANSMISSION | Regulator |  |  | Construction Defect | MATERIAL FAILURE | 2001-03-16 | 2001-03-16 | Other |  | Steel/Wrought Iron |  | EMERYVILLE | HIGH-HIGH SHUT OFF. SET TO BE REMOVED - REBUILT - RELOCATED
| 02-20155-1 |  |  | 0.75 | Service |  | Valves |  |  | Construction Defect |  | 2002-08-06 | 2004-02-02 | Other | REPAIRED VALVE | Steel |  | EMERYVILLE | REPAIRED TP SERVICE VALVE
|  |  |  | 4 | [11 empty] | Steel |  | EMERYVILLE | 107' OF 8" CASING WAS ALSO INSTALLED
|  |  |  | 6 | Transmission
|  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | EMERYVILLE
| 75-21288-1 |  |  |  | Other |  | Other |  |  | Other |  | 1975-12-05 |  | Other |  | Other
|  |  |  | 6 | [11 empty] | Steel |  | EMERYVILLE | EXISTNG 1 1/4" DRIP LEAKING AT (UNABLE TO READ THE REST OF THE COMMENT)
| 84-20207-F |  |  | 6 | [8 empty] | 1984-04-30 |  |  | Steel |  | EMERYVILLE | INST. 6" 3 BOLT SKINNER CLAMP OVER GAS LEAK FOR TEMP. REPAIRS 4/25/84 MADE PERM. BY WELD PATCHING LEAK, & WELDING OVER LEAK ON WELD JOINT, 4-30-84 EN COMPLETE (COMMENT NOT LEGIBLE)
|  |  |  | 6 | [8 empty] | 1995-07-14 |  |  | Steel |  |  | DUG UP 6" (UNABLE TO READ THE REST OF THE COMMENT)
26 | 88-12000-1 | [10 empty] | 1988-01-15 | [5 empty] | EMERYVILLE | FOUND REPAIRS RECENTLY MADE AT CURB BOX.
|  |  |  | 4 | Distribution Feeder Main |  | Other |  | NEW SERVICE |  |  |  | 1975-04-17 |  |  | Steel/Wrought Iron |  |  | NEW SERVICE
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron
26 | 75-48960-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1975-11-07 | 1976-01-30 | Patch Welded |  | Steel/Wrought Iron |  | EMERYVILLE | GAS LEAK AT MAIN (UNABLE TO READ THE REST OF THE COMMENT); 4" T.P. MAIN IS 18" BELOW 6" SEWER LINE 22M H TOTAL
26 | 88-20103-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other |  | 1988-03-28 | 1989-04-14 | Tighten Cap or Bolt |  | Steel |  | OAKLAND | LOOSENED DOPED AND TIGHTENED FOR PERM REPAIRS
26 | 88-20104-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other |  | 1988-03-28 | 1989-04-14 | Tighten Cap or Bolt |  | Steel |  | EMERY | LOOSENED UNION DOPED NIPPLE AND TIGHTENED FOR PERM REPAIRS
26 | 73-21427-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-09-10 | 1973-11-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | EMERYVILLE | GAS VALVE IN PAVING AT END OF STREET.; UNABLE TO READ THE COMMENT ON SECOND PAGE.
| 75-21295-1 |  |  | 0.75 | Service |  | Valves |  |  | Material Failure |  | 1975-10-21 | 1976-02-06 | Other |  | Steel/Wrought Iron |  | EMERYVILLE | FOUND LEAK ON 2" VALVE GREASED TO STOP.
| 92-11497-1 | 105A |  | 2 | Transmission |  | Fitting |  |  | External Corrosion |  | 1992-06-01 | 1992-06-02 | Tighten Cap or Bolt |  | Steel |  | EMERYVILLE | TIGHTENED PLUG & CAP.
|  |  |  | 2 | [11 empty] | Steel/Wrought Iron |  | EMERYVILLE | C/O 7'2' OF 2' TP MAIN. C/O 5' OF 1 1/4" SERVICE INSTALLED 22'8" OF 3/4" STEEL SERVICE
|  |  |  | 4 | [13 empty] | EMERYVILLE | STPO OF 3/4" T.P. SERVICE TO REPLACE 3/4" SERVICE JAL
26 | 72-00065-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-02-15 | 1972-10-27 | Patch Welded |  | Steel/Wrought Iron |  |  | WELDED PATCH ON T.P. MAIN HERE ALSO 1-91B MAG ANODE.
| 03-12242-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Other |  | 2003-09-25 | 2003-09-25 | Other | C/O GAS SERV | Steel/Wrought Iron |  | EMERYVILLE | C/O SERV AFTER HI TO HI SET
| 94-13039-1 |  |  | 2 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1994-09-27 | 1994-09-07 | Weld Over Sleeve or Can |  | Steel |  | EMERYVILLE | INST. 1-2" CAN OVER CLAMP ON T.P. MAIN
| 75-21291-1 |  |  |  | Other |  | Other |  |  | Other |  | 1975-12-05 | 1976-02-11 | Other |  | Other |  |  | LEAK# NOT NEEDED A/C METER REPAIR
|  |  |  | 2 | [13 empty] | EMERYVILLE | THIS 2" T.P. MAIN IS INSERTED IN A 4" STL. MAIN (ABANDONED)
| 73-48428-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-04-05 | 1973-04-19 | Patch Welded |  | Steel/Wrought Iron |  |  | INSTALLED 2 WELD PATCHES OVER LEAKS ON MAIN
26 | 92-40531-1 | [10 empty] | 1992-07-21 | 1993-02-22 |  |  |  |  | EMERYVILLE | CUSTOMER REPAIRED LINE. NO LEAKAGE FOUND.; UNABLE TO READ THE REPAIR DATE
| 98-10323-1 |  |  | 0.75 | Service |  | Valves |  |  | Material Failure |  | 1998-08-13 | 1998-08-13 | Other |  | Steel |  | EMERYVILLE | REPAIRED THREADS ON RISER & TIGHTEN VALVE. (REMARK NOT LEGIBLE)
26 | 86-10400-F |  |  | 0.35 | Service |  | Fitting |  |  | Damage by outside Forces |  | 1986-11-12 | 1986-11-12 | Other |  | Steel/Wrought Iron |  | EMERYVILLE | INSTALL NEW HIGH TO HIGH.
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | EMERYVILLE | INSTALLED 5 FT OF 3/4" PIPE FOR T.P. SERVICE TO SERVE ABOVE ADDRESS
2 |  |  |  | 1.25 | [7 empty] | 1999-04-28 |  |  |  | Steel |  | EMERYVILLE
|  |  |  | 6 | [7 empty] | 1990-08-08 |  |  |  | Steel |  | EMERYVILLE
|  |  |  | 12.75 | [11 empty] | Steel |  | OAKLAND
|  |  |  | 6.63 | [11 empty] | Steel |  | OAKLAND
|  |  |  | 6 | [11 empty] | Steel |  | OAKLAND | LARGE PITSON W/S MAIN.; SMALL ROCKS ARE PENATRATING THROUGH WRAP AND COUSING RANGE PITTS.; ARC WEKDED HALF SOLE ON BOTTOM SIDE OF MAIN PITTED VERY BAD.; BOTTOM OF MAIN WAS PITTED FROM 10% TO 90% ROCKS ARE PROTRUEPING THROUGH WRAP AND COUSING PITT. (OTHER PERTINENT INFORMATION PART IS NOT LEGIBLE)
| 85-30066-M |  |  | 6 | [8 empty] | 1985-01-23 |  |  | Steel |  | OAK | INST 12" LONG PIECE OF 6" 1/2 SOLE OF REPAIR 301. MAIN IN GOOD CONDITION EXECEPT WHERE WRAP WAS DEMAGED BY FILL. (PERTINENT INFORMATION IS NOT LEGIBLE)
[5 empty] | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 6 | Transmission | [7 empty] | 1975-11-11 |  |  | Steel/Wrought Iron
| 03-12185 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Construction Defect |  | 2003-07-31 | 2003-07-31 | Other | RE-THREADED & CHANGED VLAVE | Steel/Wrought Iron |  | EMERYVILLE | AT RISER. ; RE-THREADED & CHANGED VALVE
|  |  |  | 3 | Transmission | [7 empty] | 2003-08-26 | Other | C/O SERV. @ MAIN | Steel/Wrought Iron |  | EMERYVILLE | C/O SERV. (A) OLD SERV. T.
1 | 92-11523-1 |  |  | 3 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1992-06-15 | 1992-06-15 | Other |  | Steel/Wrought Iron |  | EMERYVILLE | CUT OUT LEAKING 3" LATERAL & 25' OF 3" LEAKING MAIN. WELDED CAP ON END OF MAIN. (REMARKS NOT LEGIBLE)
26 | 87-11045-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1987-02-05 | 1987-02-05 | Weld Over Sleeve or Can |  | Steel |  | EMERYVILLE | ARC WELDED CAN OVER 3" STEEL MAIN. SEVERAL HOLES & PITTS IN MAIN. CORROSION LEAK.
26 | 89-20369-1 |  |  | 0.75 | Service |  | Physical/Mechanical Joint |  |  | Damage by Natural Forces |  | 1989-02-15 | 1990-03-15 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EMERYVILLE | TIGHTENED UNION FITTING IN MTR. BOX LOCATION THUS MAKING PERMANENT REPAIRS.
1 | 89-11766-F |  |  | 2 | Service |  | Fitting |  |  | Other |  | 1989-12-14 | 1989-12-14 | Other |  | Steel/Wrought Iron |  | EMERYVILLE | 301 ON 2" VALVE ON MTR SET - GREASED VALVE (PERTINENT INFORMATION NOT LEGIBLE)
1 | 98-10109-1 |  |  | 0.5 | Service |  | Fitting |  |  | Material Failure |  | 1998-03-02 | 1998-03-02 | Replace Pipe |  | TR 418 |  | OAK | REPLACED COUPLING AT RISER (REMARK NOT LEGIBLE)
| 89-11404-C |  |  | 1 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1989-05-22 | 1989-05-22 | Replace Pipe and/or Service |  | Aldyl A (Tan or Gray) |  | EMERYVILLE | CONTRACTOR PUNCH HOLE IN 1" PLASTIC SER. INSTALL 2 - 1" COUPLING & 2' OF 1" PLASTIC.
1 | 90-10442-1 |  |  | 2 | Gathering | TRANSMISSION MAIN | Riser |  |  | External Corrosion |  | 1990-08-21 | 1990-08-21 | Replace Pipe |  | Steel/Wrought Iron |  | EMERY | CUT OFF T.P. SERVICE - RERUN NEED DAY
26 | 96-25266-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1996-01-09 | 1996-10-09 | Other |  | Steel/Wrought Iron |  | EMERYVILLE | LEAK CAUSE NOT LEGIBLE.; GREASED VALVE INSIDE (UNABLE TO READ THE REST OF THE REMARK)
26 | 96-25267-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1996-01-09 | 1996-12-02 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EMERYVILLE | BYPASS SET. REDOPE FITTINGS TIGHTEN UNION. NO LEAKS LOCK UP GOOD ON HIGH TO HIGH (UNABLE TO READ THE REST OF THE REMARK)
|  |  |  | 30 | [13 empty] | EMERYVILLE | CUT OFF 3/4" SERVICE (UNABLE TO READ THE REST OF THE PERTINENT INFORMATION)
26 | 89-20368-1 |  |  | 0.75 | Service |  | Fitting |  |  | Corrosion |  | 1989-02-15 | 1990-03-23 | Other |  | Steel/Wrought Iron |  | OAKLAND | TIGHTEN CAP ON SERVICE TEE.
26 | 96-25268-1 |  |  | 0.75 | Service |  | Fitting |  |  | Construction Defect |  | 1996-01-09 | 1997-02-21 | Replace Pipe |  | Steel/Wrought Iron |  | EMERYVILLE | LEAK CAUSE NOT LEGIBLE.; REBUILT H-H SET
26 | 96-25269-1 | [10 empty] | 1996-01-09 | 1997-02-21 |  | Replaced valve to clear leak |  |  | Emeryville
| 93-12337-1 |  |  | 0.75 | Service |  | Fitting |  |  | Construction Defect |  |  | 1994-01-04 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EMERYVILLE | UNABLE TO READ THE REMARKS.; LEAK CAUSE NOT LEGIBLE.
|  |  |  | 30 | Transmission |  | Other |  |  | Other |  | 1981-01-18 | 1981-03-12 | Other |  | Steel/Wrought Iron |  | OAK | INST. 3/4" SERV.
| 03-22012-1 |  |  | 0.75 | Service | TRANSIMISSION | Valves |  |  | Other |  | 2003-01-14 | 2003-01-22 | Other |  | Steel/Wrought Iron |  | OAKLAND | CURB VALVE ON HOLLIS ST. FOR BEST BUY.; GREASED VALVE.
26 | 98-20000-1 |  |  | 1 | Service |  | Valves | Fitting | REGULATOR | Other |  | 1998-01-06 | 1999-05-19 | Other |  | TR 418 |  | OAKLAND | UNABLE TO READ THE REMARKS.
|  |  |  | 2 | Transmission | [6 empty] | 1978-02-10 |  |  |  | Steel/Wrought Iron |  | EMERYVILLE | EXPOSE 2" TP MAIN IN ORDER TO INSTALL 1' VALVE TEE, CAN OLD 3/4" SERVICE TEE.
26 | 88-20112-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1988-03-28 | 1989-03-29 | Other |  | Steel/Wrought Iron |  | EMERY | VALVE GREASED FOR PERM REPAIRS. (REMARK NOT LEGIBLE)
26 | 88-20111-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1988-03-28 | 1989-03-31 | Other |  | Steel/Wrought Iron |  | EMERY | GREASED 2 VALVES TIGHTENED AND REDOPED 2 3/4" UNION FOR PERM REPAIRS.
| 96-14391-1 |  |  | 0.75 | Service |  | Valves | Body of Pipe |  | External Corrosion |  | 1996-09-17 | 1996-09-17 | Other |  | Steel/Wrought Iron |  | EMERYVILLE | REPAIRED VALVES - SHUT OFF SERVICE & CAP 3/4" PIPE. (REMARK NOT LEGIBLE)
1 | 94-13200-1 |  |  | 0.75 | Service |  | Valves |  |  | Material Failure |  | 1994-12-28 | 1994-12-28 | Other |  | Steel/Wrought Iron |  | EMERYVILLE | GREASED 3/4" VALVE ON HIGH TO HIGH SET. A/C LEAKAGE.
1 | 94-13201-1 |  |  | 0.75 | Service |  | Fitting |  |  | Construction Defect |  | 1994-12-28 | 1994-12-28 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EMERYVILLE | LEAK CAUSE NOT LEGIBLE.; UNABLE TO READ THE REMARKS.
| 94-12911-1 |  |  | 0.75 | Service |  | Valves |  |  | Construction Defect |  | 1994-07-22 | 1994-07-22 | Other |  | Steel/Wrought Iron |  | EMERYVILLE | GREASED INLET VALVE ON HIGH TO HIGH SET TO CLEAR 301.
1 | 94-12755-1 |  |  | 0.75 | Service |  | Valves |  |  |  |  | 1991-04-25 | 1994-04-25 | Other |  | Steel/Wrought Iron |  | EMERYVILLE | 301 ON 3/4" VALVE IN HIGH PRESS (UNABLE TO READ THE REST OF THE REMARK)
26 | 88-20114-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other |  | 1988-03-28 | 1989-04-10 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EMERY | LOOSENED UNION DOPED AND TIGHTENED FOR PERM REPAIRS.
| 04-14020 |  |  | 0.5 | Service |  | Riser |  |  | Digin |  |  | 2004-01-20 | Service Partially Replaced |  | Aldyl A (Tan or Gray) | STEEL/WROUGHT IRON | EMERYVILLE | REPLACED RISER AND REPAIRED MAIN (UNABLE TO READ THE LAST WORD)
| 92-11479-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 1992-05-22 | 1992-05-22 | Clamp |  | Steel/Wrought Iron |  | EMERYVILLE | INST 4" SKINNER CLAMP 90' N/O PL.;
|  |  |  | 4 | Distribution Feeder Main |  | Other Welds |  |  | Other |  | 1987-09-30 | 1987-09-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | EMERYVILLE | INSTALLED CAN OVER OLD 1 1/4" TEE FOR PERMANENT C/O AND FIX LEAK ON TEE.
|  |  |  | 3 | Distribution Feeder Main |  |  |  |  | Construction Defect | [5 empty] | Steel/Wrought Iron
26 | 88-20109-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other |  | 1988-03-28 | 1989-04-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EMERY | LOOSENED DOPED AND TIGHTENED FOR PERM REPAIRS.
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron
26 | 73-21372-1 |  |  | 0.34 | Service |  | Fitting |  |  | Material Failure |  | 1973-09-11 | 1973-12-11 |  |  | Steel/Wrought Iron |  |  | TIGHTENED 3/4" INSULATING UNIONS TO ELIMINATE LEAKAGE.
26 | 72-05322-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-07-03 |  | Patch Welded |  | Steel/Wrought Iron
|  |  |  | 6 | [13 empty] | EMERYVILLE | INSTALL SERVICE TO ADDRESS.
26 | 87-30284-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1987-08-13 | 1988-10-28 | Patch Welded |  | Steel/Wrought Iron |  | EMERYVILLE | UNABLE TO READ REMARKS.; UNABLE TO INSERT THE LAST DIGIT OF THE LEAK NUMBER.
| 74-48740- |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1974-06-05 | Other | DRY HOLE | Steel/Wrought Iron
| 72-45222-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-10-03 | 1972-10-04 | Patch Welded |  | Steel/Wrought Iron |  |  | INST. (1) PATCH ON TOP WHERE MAIN WAS BENT UPON INSTALLATION.; INST. (1) PATCH ON 2" TP MAIN.
26 | 88-20110-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other |  | 1988-03-28 | 1989-04-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EMERY | LOOSENED, DOPED TIGHTENED FOR PERM REPAIRS.
26 | 95-24323-1 | [16 empty] | EMERY
| 72-00063-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Corrosion |  |  | 1972-07-07 | Other | CAN | Steel/Wrought Iron |  |  | CANNED LEAKING 2" VALVE.
26 | 72-45007-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-01-13 | 1972-01-14 | Patch Welded |  | Steel/Wrought Iron |  | EMERYVILLE | THIS MAIN SHOULD BE SURVEYED FOR IMMEDIATE REPLACEMENT. AREA ODOR FOR 2 BLOCK AREA.
2 |  |  |  | 0.75 | [8 empty] | 1998-06-25 | Other |  | Steel/Wrought Iron |  | EMERYVILLE | C/O SERV AT MAIN
| 00-11162-1 |  |  | 0.75 | Service |  | Fitting | Riser |  | Material Failure |  | 2000-05-05 | 2000-05-05 | Other | REPLACED FITTING | Steel/Wrought Iron |  | EMERYVILLE | REPLACED 3/4" COUPLING ON A/C LEAKING.; RISER ABOVE GROUND BELOW VALVE (COUPLING) (SOAP TEST)
26 | 93-22813-1 |  |  | 0.75 | Service |  | Fitting |  |  | Construction Defect |  |  | 1994-03-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EMERYVILLE | TIGHTENED FITTINGS INSIDE HIGH TO HIGH BOX A/C LEAKAGE. TIGHTENED NIPPLE AT UNION.; UNABLE TO READ THE FOUND DATE.
26 | 88-20113-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1988-03-28 | 1989-04-10 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EMERY | GREASED AND TIGHTENED BOLTS ON BODY OF VALVE FOR PERM REPAIRS. (REMARK NOT LEGIBLE)
| 72-00064- |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  |  | 1972-07-10 | Patch Welded |  | Steel/Wrought Iron |  |  | INSTL 9 LBS MAG. ANODE IN HOLE.
|  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  | 1975-03-06 | 1975-03-06 | Other |  | Steel/Wrought Iron |  | OAKLAND
| 79-20144- |  |  | 4 | [7 empty] | 1979-05-24 | 1979-08-23 |  |  | Copper
| 72-21294- |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-12-12 | 1972-12-13 | Clamp |  | Steel/Wrought Iron |  |  | INSTALLED 1-3" LEAK CLAMP TO STOP LEAKAGE.
|  |  |  | 3 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
|  |  |  | 2 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
|  |  |  | 2 | Distribution Feeder Main |  |  |  |  | Construction Defect |  | 1974-04-16 |  |  |  | Steel/Wrought Iron
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  |  | 1973-05-30 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAK | SERV R/R ONLY NO LEAK AT MAIN.
|  |  |  | 12 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1977-03-29 | Other |  | Steel/Wrought Iron |  |  | INSTL (2) WIRES ON 12" LP MAIN ALSO INST ETS STATION. GM495425 - 1224-5
26 | 73-48507- |  |  | 3 | Distribution Main |  | Fitting |  |  | Corrosion |  | 1973-04-24 | 1973-04-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | PLUG IN 1 1/4" ST. ELL COMPLETELY CORRODED AWAY CAUSING EXTREMELY STRANGE AREA ODOR. REPAIRED BY REPLACING ST. ELL AND PLUG. (REMARK NOT LEGIBLE)
26 | 72-48351-A |  |  | 1 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-10-09 | 1972-10-09 | Other |  | Steel/Wrought Iron |  |  | INSTALL 1' AMP FITTING TO STOP LEAKAGE. (COMMENT NOT LEGIBLE)
1 | 73-48229- |  |  | 2 | Distribution Main |  | Fitting |  |  | Corrosion |  | 1973-02-21 | 1972-02-21 | Other |  | Steel/Wrought Iron |  |  | INSTALL 2-2" (UNABLE TO READ THE REST OF THE COMMENT)
| 76-48771-1 |  |  | 0.34 | Other |  | Body of Pipe |  |  | Corrosion |  | 1976-07-21 | 1976-07-21 | Clamp |  | Steel/Wrought Iron |  | OAKLAND | COMMENT NOT LEGIBLE ON SECOND PAGE.
1 | 72-45165-A |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-06-27 | 1972-06-27 | Bell Joint Clamp Replacement |  | Cast/Ductile Iron | COPPER |  | INSTALL 8' BELL JOINT LEAK CLAMP.
|  |  |  | 0.75 | Distribution Main |  | Other |  |  | Other |  |  | 1973-07-24 | Other | C/O 3/4" SERVICE | Steel/Wrought Iron |  |  | CUT OFF 3/4" SERVICE DUE TO HOUSE BEING WRECKED.
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1973-05-29 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAK | SERV R.R AND C/O ONLY NO LEAK ON MAIN.
|  |  |  | 12 | Distribution Feeder Main | [6 empty] | 1973-07-03 | 1973-07-03 | Other |  | Cast/Ductile Iron |  | OAKLAND
| 79-48987-1 | [5 empty] | Other |  |  | Material Failure |  | 1979-12-13 | 1980-02-28 | Other |  |  |  | OAKLAND | SOAP TESTED ALL FITTINGS AND METERS BETWEEN SERVICE COCK AND HOUSE LINES. FOUND & REPAIRED MINOR LEAK ON 1 1/4" NIPPLE. FOUND ONE TIN METER LEAKING AT INDEX GLASS REPLACED WITH NEW METER.
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1971-11-04 | Other |  | Steel/Wrought Iron |  | OAKLAND | UNABLE TO READ COMMENT ON SECOND PAGE.
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  |  | 1976-08-06 | Other | C/0 | Steel/Wrought Iron |  | OAKLAND | UNABLE READ COMMENT ON SECOND PAGE.
|  |  |  | 12 | [7 empty] | 1975-08-01 | 1975-08-01 |  |  | Steel/Wrought Iron |  |  | LINE USE NOT LEGIBLE.
|  |  |  | 12 | Distribution Main |  | Other |  |  | Other |  |  | 1976-08-05 |  |  | Steel/Wrought Iron |  | OAKLAND | UNABLE TO READ PERTINENT INFORMATION.
1 | 72-45114-A |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-05-10 | 1972-05-11 |  |  | Steel/Wrought Iron |  |  | UNABLE TO READ COMMENT.
26 | 72-48491- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-11-21 | 1972-11-28 | Clamp |  | Steel/Wrought Iron |  |  | LEAKAGE CAUSED AT POINT WHERE 2" PIPE IS RESTING ON ROCK. PERMENENT REPAIRS MADE WITH SKINNER CLAMP. ANODE INSTALLED.
1 |  |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-07-16 | 1972-07-16 | Patch Welded |  | Steel/Wrought Iron |  |  | UNABLE TO READ COMMENT.
| 77-48284- |  |  | 2 | Distribution Main |  | Fitting |  |  | Corrosion |  | 1977-03-22 | 1977-03-22 | Patch Welded |  | Steel/Wrought Iron |  | PIEDMONT | FOUND LEAK HEAD DIGGING UP FOR % OF 1 1/4" SERV. ; ARC WELDER WELDED PATCH OVER 2" (UNABLE TO READ THE REST OF THE COMMENT)
|  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | OAKLAND
26 | 77-49149 |  |  | 1.25 | Other |  | Fitting |  |  | Corrosion |  | 1977-11-03 | 1977-11-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | REPLACED 1 1/4" CAP ON C/O SERVICE AND INSTALLED (1) 1 1/4 CLAMP ON STUB TO MAKE REPAIRS 11-3-77
|  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  | 1973-05-10 | 1973-05-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1973-05-23 | 1973-05-23 | Bell Joint Clamp Replacement |  | Cast/Ductile Iron
| 81-40339-F |  |  | 0.5 | Service |  | Fitting |  |  | Material Failure |  | 1981-05-07 | 1981-05-12 | Other | TIGHTEN VALVE | Plastic |  | OAK | TIGHTEN 3/4" SERVICE VALVE, DUE TO LEAKAGE.
26 | 76-48749- |  |  | 1.14 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-06-21 | 1976-06-21 | Other |  | Steel/Wrought Iron |  | OAKLAND | USED 1" PLASTIC TO REPAIR (UNABLE TO READ THE REST OF THE COMMENT)
26 | 76-48666 |  |  | 0.34 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-06-17 | 1976-06-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAKLAND | USED 1/2" PLASTIC AND (3) COMPRESSION FITTINGS (WITH 1 LB ANODE ATTACHED) TO REPAIR RUPTURED STEEL & PLASTIC SERVICE.
26 | 74-49395- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-11-11 | 1974-11-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | UNABLE TO READ COMMENT ON SECOND PAGE.
|  |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Other |  |  |  | Bell Joint Clamp Replacement |  | Cast/Ductile Iron |  | OAKLAND | LEAK SOURCE NOT LEGIBLE.
|  |  |  | 8 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  |  | 1973-03-08 | Bell Joint Clamp Replacement |  | Cast/Ductile Iron |  | OAKLAND
26 |  |  |  | 3 | Distribution Main | [6 empty] | 1982-05-21 | 1982-06-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron
1 | 73-48788-A |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  |  | 1973-06-06 | Other |  | Steel/Wrought Iron |  |  | UNABLE TO READ REMARK.
|  |  |  | 2 | Other |  | Other |  |  | Other |  |  | 1972-03-07 | Other |  | Steel/Wrought Iron |  |  | PROSPECTING MAIN (REMARK NOT LEGIBLE)
25 | 81-40120 |  |  | 0.75 | Service |  | Fitting |  | SERV. VALVE | Material Failure |  | 1981-02-23 | 1981-02-23 | Other | TIGHTEN FITTING | Steel/Wrought Iron |  | OAKLAND | TIGHTEN NUT OR BACK OF 3/4 SERVICE VALVE, DUE TO LEAKAGE. (PERTINENT INFORMATION NOT LEGIBLE)
| 72-00308-1 |  |  | 0.02 | Distribution Feeder Main |  |  |  |  | Corrosion |  | 1972-07-11 |  |  |  | Plastic |  | OAKLAND
1 | 78-48672-F |  |  | 3 | Distribution Feeder Main |  | Fitting |  |  | Construction Defect |  | 1978-07-26 | 1978-07-27 | Other | WELD CAN OVER | Steel/Wrought Iron |  | OAKLAND | FOUND LEAK ON 3" IN LINE TEE: CAN TEE TO REPAIR
26 | 73-49554 |  |  | 3.5 | Distribution Feeder Main |  | Body of Pipe | Fitting |  | Corrosion |  | 1973-12-03 | 1973-12-07 |  |  | Steel/Wrought Iron |  |  | LINE SIZE NOT CLEAR.; INSTALL 3 WAY TEE TO STOP LEAKAGE.
1 | 73-20690-H |  |  | 2 | Distribution Main |  |  |  |  | Corrosion |  | 1973-03-01 | 1973-03-01 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | UNABLE TO READ LEAK NUMBER. UNABLE TO READ LEAK SOURCE. UNABLE TO READ REMARKS.
| 79-48247- |  |  | 1.25 | Service |  | Body of Pipe | Fitting |  | Corrosion |  | 1979-03-20 |  | Other | DUX SEAL PUNCH HOLES OVER SERV. 4/12/79 REPLACED. | Steel/Wrought Iron |  | OAKLAND | PLACE DUX SEAL AROUND THREADS ON RISER - ALSO PUNCH HOLES ON SERV. TO AIR OUT. (COMMENT NOT LEGIBLE)
|  |  |  | 2 | Other |  | Other |  |  | Other |  |  | 1972-03-15 | Other |  | Steel/Wrought Iron |  |  | UNABLE TO READ THE COMMENT.
| 78-48491 |  |  | 0.34 | Other | N | Body of Pipe |  |  | Corrosion |  | 1978-06-05 | 1978-06-05 | Clamp |  | Steel/Wrought Iron |  | OAKLAND | INSTALLED (2) 3/4" LEAK CLAMPS.
| 79-48983-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1979-12-12 | 1979-12-13 | Clamp |  | Steel/Wrought Iron |  | OAKLAND | INSTALLED 10 (TEN) 2" SKINNER CLAMPS ON 2" S.H.P. MAIN 2 (TWO) FEET OUT.
1 | 73-48788-A |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  |  | 1973-06-06 | Other |  | Steel/Wrought Iron |  |  | UNABLE TO READ COMMENT.
|  |  |  | 2 | Other |  | Other |  |  | Other |  |  | 1972-03-07 | Other |  | Steel/Wrought Iron |  |  | PROSPECTING MAIN 9 (UNABLE TO READ THE REST OF THE COMMENT)
25 | 81-40120- |  |  | 0.75 | Service |  | Fitting |  |  | Material Failure |  | 1981-02-23 | 1981-02-23 | Other | TIGHTEN FITTING | Steel/Wrought Iron |  | OAKLAND | TIGHTEN NUT OR BACK OF 3/4 SERVICE VALVE, DUE TO LEAKAGE.
| 72-00308-1 |  |  | 0.02 | Distribution Feeder Main |  |  |  |  | Corrosion |  | 1972-07-11 |  |  |  | Plastic |  | OAKLAND
| 77-48660- |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1977-07-14 | 1979-07-19 | Patch Welded |  | Steel/Wrought Iron |  | OAKLAND | DUG OUT TO REPLACE BAD SECTION OF MAIN OUT FOUND REPAIR HAD BEEN MADE WITH CLAMP AND MAIN NOT TOO BAD. (COMMENT NOT LEGIBLE)
26 | 77-48660- |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1977-07-14 | 1977-07-15 | Other |  | Steel/Wrought Iron |  | OAKLAND | PIPE AT THIS LOCATION IS BEYOND REPAIR. TEMP REPAIRS INCLUDED DUC SEAL AND GRAY TAPE. GAS MAIN SHOULD BE CONSIDERED FOR REPLACEMENT AS SOON AS POSSIBLE. (COMMENT NOT LEGIBLE)
26 | 77-49030 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1977-10-04 | 1977-10-04 | Clamp |  | Steel/Wrought Iron |  | OAKLAND | USED SKINNER CLAMP TO STOP LEAKAGE. MAIN SHOULD BE REPLACED. (COMMENT NOT LEGIBLE)
| 80-48937-F |  |  | 1.25 | Service |  | Fitting |  |  | Material Failure |  | 1980-12-10 | 1980-12-10 | Other | TIGHTEN UP 1 1/4" SERV. VALVE | Steel/Wrought Iron |  | OAKLAND | TIGHTEN UP 1 1/4" SERVICE VALVE DUE TO LEAKAGE.
26 | 75-48186-F |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  |  |  | Other |  | Steel/Wrought Iron |  |  | UNABLE TO READ COMMENT.
|  |  |  | 2 | Distribution Main |  | Other |  |  | Corrosion |  | 1973-10-30 | 1973-10-30 | Replace Pipe and/or Service |  | Steel/Wrought Iron
| 80-48497-1 |  |  | 2 | Other |  | Fitting |  |  | Other |  | 1980-05-13 | 1980-05-14 | Other |  | Steel/Wrought Iron |  | OAKLAND | REMOVED SCREWED MANIFOLD AT RISER (NON USE) LEAKING INSTALLED 2" SCREWED PLUG.
| 74-48856 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Other |  |  | 1974-07-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAK
26 | 74-22068-1 |  |  |  | Other |  | Other |  |  | Other |  | 1974-06-14 | 1974-10-10 | Other |  | Other |  |  | COMMENT NOT LEGIBLE.
26 | 79-48658- |  |  | 2 | Other |  | Fitting |  |  | Other |  | 1979-08-13 | 1979-08-13 | Other |  | Steel/Wrought Iron |  | OAK. | REPAIRED LEAKS AT METER SET. TIGHTENED FITTINGS 8-13-79
1 |  |  |  | 3 | Distribution Feeder Main |  |  |  |  | Other | [5 empty] | Plastic |  | OAKLAND | 3" PLASTIC D.F.
1 |  |  |  | 3 | Distribution Feeder Main |  |  |  |  | Other | [5 empty] | Plastic |  | OAKLAND | COMMENT NOT LEGIBLE.
| 73-49019-1 |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-07-30 | 1973-08-20 | Patch Welded |  | Steel/Wrought Iron |  |  | COMMENT NOT LEGIBLE.
|  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1975-06-30 |  |  |  | Steel/Wrought Iron
|  |  |  | 10 | Distribution Feeder Main | [6 empty] | 1975-06-27 |  |  |  | Steel/Wrought Iron
|  |  |  | 10 | Distribution Feeder Main | [6 empty] | 1975-06-27 |  |  |  | Steel/Wrought Iron
|  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1975-06-30 |  |  |  | Steel/Wrought Iron
26 |  |  |  | 3 | Transmission | [6 empty] | 1974-07-16 |  |  |  | Steel/Wrought Iron |  | OAKLAND | FOUND PIN IN 1" PIN OFF TEE SCREWED DOWN RESTRICTING GAS FLOW SCREWED PIN UP HAVE FULL FLOW.
|  |  |  | 2 | Transmission |  | Other |  | RERUN SERVICE | Other |  | 1974-03-20 | 1974-03-20 |  |  | Steel/Wrought Iron |  | OAK
| 94-12471-1 |  |  | 0.75 | Service |  | Other |  |  | Construction Defect |  | 1994-01-20 | 2004-01-20 | Other |  | Steel/Wrought Iron |  | OAKLAND | REPAIRED DATE NOT LEGIBLE.
26 | 97-26405-1 |  |  | 0.75 | Service |  | Fitting |  |  | Material Failure |  | 1997-02-21 | 1998-03-03 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | OAKLAND | TIGHTENED FITTINGS ON RISER.
26 | 97-26404-1 |  |  | 0.75 | Service |  | Fitting |  |  | Material Failure |  | 1997-02-21 | 1998-03-03 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | OAKLAND | REPLACED REGULATOR & TIGHTENED FITTINGS ON RISER A/C LEAKAGE.
|  |  |  | 2 | [14 empty] | RE RUN SERVICE, CUT OFF EXISTING 3/4" T.P. SM (COMMENT NOT LEGIBLE)
26 | 93-22908-1 |  |  | 0.75 | Service |  | Fitting |  |  | Corrosion |  |  | 1994-04-12 | Other |  | Steel/Wrought Iron |  |  | TIGHTEN 3/4" UNION (REMARK NOT LEGIBLE); UNABLE TO READ MOST OF THE INFORMATION.
| 93-22907-1 |  |  | 0.75 | Service |  | Valves |  |  | Material Failure |  |  | 1994-04-12 | Other |  | Steel/Wrought Iron |  |  | GREASED VALVE.
| 74-22131- |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  |  | 1974-06-27 | Patch Welded |  | Steel/Wrought Iron
|  |  |  | 2 | Other |  | Other |  |  | Other |  | 1971-11-06 |  | Other |  | Steel/Wrought Iron |  |  | UNABLE TO READ COMMENT.
1 |  |  |  | 2 | Distribution Feeder Main |  |  |  |  | Other | [5 empty] | Steel/Wrought Iron |  | OAKLAND
| 73-49169- |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-09-06 | 1973-09-06 | Other |  | Steel/Wrought Iron |  |  | ARCED METAL PATCH.
| 73-49168- |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-09-06 | 1973-09-06 | Other |  | Steel/Wrought Iron |  |  | ARCED 16" WELDING BAND
| 73-49167 |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-09-06 | 1973-09-06 |  |  | Steel/Wrought Iron |  |  | ARCED 16" WELDING BAND.
| 81-10039- |  |  | 1.25 | Service |  | Fitting |  |  | Material Failure |  | 1981-03-26 | 1981-05-14 | Other | TIGHTEN VALVE | Steel/Wrought Iron |  | OAKLAND | TIGHTEN 3/4" SERVICE VALVE DUE TO LEAKAGE.
26 | 98-20114-1 |  |  | 3 | Distribution Feeder Main | DISTRIBUTION MAIN | Valves |  |  | Other |  | 1998-02-26 | 1999-05-14 | Other |  | Steel/Wrought Iron |  | OAKLAND | GREASED VALVE TO STOP LEAK, OK!
1 |  | 105 |  | 2 | [13 empty] | OAKLAND
OAKLAND
| 93-22786-1 |  |  | 0.75 | Service |  | Valves |  |  | Construction Defect |  | 00/22/1993 | 1994-03-08 | Other |  | Steel/Wrought Iron |  |  | GREASED VALVE
26 | 93-22785-1 | [10 empty] | 1993-12-22 | [5 empty] | OAK | UNABLE READ MOST OF THE INFORMATION ON THE FORM.
|  |  |  | 20 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  |  | 16 | Distribution Feeder Main | [6 empty] | 1975-06-25 |  |  |  | Steel/Wrought Iron
|  |  |  | 24 | Distribution Feeder Main |  | Other |  |  | Other |  | 1973-11-02 | 1973-11-03 | Other |  | Steel/Wrought Iron |  | OAKLAND
|  |  |  | 24 | Transmission |  | Other |  |  | Other |  | 1981-11-10 | 1981-11-10 | Other |  | Steel/Wrought Iron |  | OAKLAND | SERVICE C/O HOLE.
| 88-10885-C |  |  | 0.75 | Service |  | Body of Pipe |  |  | Construction Defect |  | 1988-08-30 | 1988-08-30 | Other |  | Steel/Wrought Iron |  | OAKLAND | CUT OFF 22' OF 3/4" STEEL SERVICE A/C LEAKAGE. RELOCATED RISER & MANIFOLD.
| 93-22784-1 | [10 empty] | 00/22/1993 | [5 empty] | OAKLAND
26 | 97-26314-1 |  |  | 2 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1997-02-12 | 1998-01-08 | Other |  | Steel/Wrought Iron |  | OAKLAND | CHANGED GREASE FITTING & GREASED VALVE TO STOP LEAK.
|  |  |  | 30 | Transmission |  | Other |  |  | Other |  | 1978-07-14 | 1978-07-14 | Other | SERVICE C/O | Steel/Wrought Iron |  | OAKLAND | SERVICE C/O.
|  |  |  | 24 | Transmission |  | Other |  |  | Other |  | 1978-07-14 | 1978-07-14 | Other | SERVICE C/O | Steel/Wrought Iron |  |  | SERVICE C/O
|  |  |  | 20 | Transmission |  | Other |  |  | Other |  |  | 1981-07-27 | Other |  | Steel/Wrought Iron |  |  | INSTALLED E.T.S. STATION NEAR 16TH AV. OVERPASS END E.T.S. STATION 330 FEET W/O 5TH AV.
|  |  |  | 30 | Transmission | [6 empty] | 1973-01-30 |  |  |  | Steel/Wrought Iron |  | OAK
|  |  |  | 24 | Transmission | [6 empty] | 1973-01-30 |  |  |  | Steel/Wrought Iron |  | OAK
|  |  |  | 24 | Transmission |  | Other |  | NONE | Other | NONE | 1972-01-03 |  |  | NONE | Steel/Wrought Iron |  |  | WRAP & PIPE IN EXCELLENT CONDITION.
26 |  |  |  | 0.3 | Other |  | Other |  |  | Other |  |  | 1974-03-21 | Other |  | Steel/Wrought Iron |  |  | LINE SIZE NOT CLEAR. DATE REPAIRED NOT LEGIBLE.
| 74-22082- |  |  | 0.34 | Service |  | Regulator |  |  | Construction Defect |  |  | 1974-06-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | OAK
| 74-22083 |  |  | 0.75 | Distribution Main |  | Other |  |  | Other |  | 1974-06-18 | 1974-06-25 | Other | REDOPED & TIGHTENED | Steel/Wrought Iron |  | OAK | FOUND SERV TEE CAP LEAKING REMOVED CAP DOPED & REPLACED CAP TO REPAIR.
|  |  |  | 20 | [11 empty] | Steel |  | OAK | BADLY PITTED AT BOTTOM LEAKING. ARC WELDED 12" X 20" PATCH OVER LEAKS, 8" X 8" PATCH OVER LARGE PIT.
|  |  |  | 20 | [11 empty] | Steel |  | OAK | BADLY PITTED AT BOTTOM LEAKING
26 |  |  |  |  | Transmission |  | Other |  |  | Other |  |  | 1974-03-21 | Other |  | Steel/Wrought Iron
26 | 73-49622- |  |  | 6 | Distribution Feeder Main |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1973-12-12 | 1973-12-31 | Replace Pipe and/or Service |  | Steel/Wrought Iron | CAST IRON | OAK | COMMENT NOT LEGIBLE.
26 | 73-55053- |  |  | 1.14 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-01-25 | 1973-01-26 | Clamp |  | Steel/Wrought Iron |  |  | INSTALLED 1 1/4 SKINNER CLAMP & ANODE.
1 | 93-12126-1 |  |  | 0.75 | Service |  | Valves | Valves |  | Corrosion |  | 1993-07-19 |  | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | Alameda
|  |  |  | 12 | Distribution Feeder Main |  | Other |  |  | Other |  | 1972-04-07 | 1972-04-10 |  |  | Steel/Wrought Iron
26 | 93-23148-1 |  |  | 2 | Service |  | Valves |  |  | Other |  | 1993-07-19 | 1994-12-12 | Other |  | Steel/Wrought Iron |  | Alameda | GREASED VALVE
| 79-48196 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1979-03-02 | 1979-03-05 | Other |  | Steel/Wrought Iron
| 78-48791 |  |  | 1 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-09-06 |  | Replace Pipe and/or Service |  | Other Plastic
|  |  |  | 2 | Transmission |  | Other |  |  | Other |  |  | 1980-03-19 | Other |  | Steel/Wrought Iron |  | MARINER LOOP
26 | 72- |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-03-01 | 1972-03-03 |  |  | Steel/Wrought Iron
|  |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-03-01 | 1972-03-03 | Patch Welded |  | Steel/Wrought Iron |  | ALAMEDA
|  |  |  | 1 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1991-07-17 | 1991-07-17 | Replace Pipe and/or Service |  | TR 418 |  | ALAMEDA
|  |  |  | 2 | Transmission | [7 empty] | 1997-10-04 | [5 empty] | INSERTED 1" BRANCH SERVICE AND MOTHER SERVICE TIED IN TO 2" STL TRANSMISSION MAIN
26 | 74-49232 |  |  | 0.75 | Service |  | Longitudinal Weld |  |  | Construction Defect |  | 1974-09-27 | 1974-09-27 | Other | weld over weld | Steel/Wrought Iron
| 81-10046 |  |  | 1.25 | Service |  | Fitting |  |  | Material Failure |  | 1981-03-31 | 1981-06-12 | Replace Pipe and/or Service | New Valve | Steel/Wrought Iron |  |  | Install new 3/4" insulated service valve due to leakage
| 81-11004-5 |  |  | 0.75 | Service |  | Girth Weld |  |  | Material Failure |  | 1981-03-31 | 1981-06-16 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Oakland | found leak on weld on "3/4" RISER. Crew repair small leak with weld over
|  |  |  | 6.9 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-02-01 |  | Replace Pipe and/or Service |  | Cast/Ductile Iron
|  |  |  | 6.9 | Distribution Feeder Main |  | Bell Joint |  |  | Other |  | 1973-02-09 |  | Other |  | Cast/Ductile Iron
|  |  |  | 6.9 |  |  | Other |  |  | Other |  | 1973-02-01 |  | Replace Pipe and/or Service |  | Cast/Ductile Iron
26 | 72-00258-1 |  |  | 6 | Distribution Main |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1972-03-10 | 1972-03-10 | Other |  | Cast Iron
|  |  |  | 3 | Distribution Feeder Main |  | Other |  | New Serv. | Other | NEW SERV. |  | 1973-02-15 | Other | New serv. | Steel/Wrought Iron |  |  | Ran new 1/2; Ran new 1/2" plt serv. bare to 4045 lyon st. oak used 1lb auoid
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1980-04-23 | Other |  | Steel |  | Oakland
|  |  |  | 2 | Distribution Main | [10 empty] | Steel |  |  | Lock ring coupling needs to be canned. Used dux soap and gray tape to make perm. repairs. Wire brushed and soaped fitting. Found no indication of leakage. Primed, wrapped and backfilled.
26 | 73-49415 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-11-08 | 1973-11-12 | Clamp |  | Steel/Wrought Iron |  |  | MADE REPAIR ON 3/4" SERVICE IN DRIVEWAY, DUE TO EXTREME DIP
|  |  |  | 16 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1976-10-19 | Other |  | Steel |  |  | Inst ETS Station put V.F.C. in parking strip
26 |  |  |  | 0.04 | Distribution Feeder Main | [6 empty] | 1972-05-15 |  |  |  | Steel/Wrought Iron
|  |  |  | 16 | Distribution Feeder Main | [7 empty] | 1976-10-07 | Other | C.P.A. | Steel |  |  | Inst. O.T.S.
| 01-15034 |  |  | 0.75 | Gathering | Service | Body of Pipe |  |  | Material Failure |  | 2001-02-05 | 2001-02-13 | ABANDON | SERVICE ENTIRELY REPLACED | Steel/Wrought Iron |  | Oakland | Over svc. R/R entire gas serv .75 1/2" TR418 Pl. Pipe
26 | 73-49010 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-07-25 | 1973-07-25 | Clamp |  | Steel/Wrought Iron
1 | 77-48826 |  |  | 0.34 | Other | 3/4" blow of valve | Fitting |  |  | Other | LOOSE-FITTING |  | 1977-08-23 | Other | TIGHTEN-FITTING |  |  | Oakland | Tighten 3/4" service valve to stop leakage on serv. valve.
|  |  |  | 16 | Distribution Main |  | Other |  |  | Other |  |  | 1976-10-08 | Other |  | Steel |  | Oakland | INST ETS STATION
26 | 75-48053 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-01-14 | 1975-02-03 | Clamp |  | Steel/Wrought Iron
26 | 72-40061-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-03-02 | 1972-03-06 | Clamp |  | Steel/Wrought Iron
26 | 72-45334 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-12-11 | 1972-12-22 | Clamp |  | Steel/Wrought Iron
|  |  |  | 3 | Other |  | Other |  |  | Other |  | 1973-07-20 | 1973-07-20 | Other |  | Steel/Wrought Iron
| 74-48928-1 |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1974-07-19 | Other |  | Steel/Wrought Iron
| 74-48927-1 |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1974-07-19 | Other |  | Steel/Wrought Iron
26 | 72-00371-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Material Failure |  | 1972-05-22 | 1972-06-02 |  |  | Steel
| 71-40159 |  |  | 16 | Other |  | Physical/Mechanical Joint |  |  | Corrosion |  |  | 1971-05-19 | Patch Welded |  | Steel |  | Oakland
2 |  | 105 |  | 30 | [11 empty] | Steel |  | Oakland
2 |  | 105 |  | 30 | [7 empty] | 1995-06-23 |  |  |  | Steel |  | Oakland
26 |  |  |  | 24 | Transmission | [10 empty] | Steel |  | Oakland
|  |  |  | 8 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1993-05-22 | Other | serv c/o | Steel |  | Alameda
26 | 74-20892 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1975-09-18 | 1975-10-21 | Replace Pipe and/or Service |  | Steel |  | Alameda | Hence line on curb meter found leaking, service shut off by service dept 10/21/1975
| 76-55057 |  |  | 0.34 | Other | houseline | Body of Pipe |  |  | Corrosion |  | 1976-02-27 | 1976-03-01 | Clamp |  | Steel |  | Alameda | Check between 432-436 found 3% gas reading in elect pull box in wackway turn in for crew 3/1/1976. found leak on 3/4" house line by electric box. installed (2) 3/4" adoms clamps
|  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  |  | 1973-08-24 | Other |  | Copper |  | Oakland
|  |  |  | 3 |  |  | Other |  |  | Other |  | 1973-11-27 |  | Replace Pipe and/or Service
| 78-48850-1 |  |  | 0.75 | Other | Stub service | Body of Pipe |  |  | Corrosion |  | 1978-09-29 | 1978-12-15 | Patch Welded |  | Steel |  | Alameda | Found stub service leaking, also not in use. cut stub off at main location
26 | 77-48757-0 |  |  | 2 | Other | Customer House Line | Body of Pipe |  |  | Corrosion |  | 1977-08-05 | 1977-08-09 | Other | Tape | Steel |  | Alameda | Taped 2" houseline- customer owned
| 79-55050-0 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-09-08 | 1979-09-10 | Replace Pipe and/or Service |  | PE 100 |  | Alameda | Repaired broken serv with two (2) 1/2" amp. Fit. couplings & one (1) foot of 1/2" pl pipe
26 | 73-49376 |  |  | 8 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-10-31 | 1973-10-31 |  |  | Steel
|  |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  |  | 1973-03-17 |  |  | Steel
|  |  |  | 0.02 | Distribution Feeder Main | [6 empty] | 1972-05-16 |  |  |  | Steel
|  |  |  | 0.02 | Distribution Feeder Main | [6 empty] | 1972-05-16 |  |  |  | Steel
26 | 73-49620 |  |  | 03.5P | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-12-12 | 1973-12-20 |  |  | Steel |  |  | Inserted 50' of 2" plastic
|  |  |  | 6 | Distribution Feeder Main |  | Longitudinal Weld | [8 empty] | Steel |  | Oakland
|  |  |  | 4 | Distribution Feeder Main |  | Other |  |  | Other |  | 1982-01-05 | 1982-01-06 |  |  | Steel |  | Oakland | Main filled w/ water. had to inst 4" fitting & squeeze pl. & inst 4" x 1" tee to drain water. Also 2- services at 2218-20-2232 seminary Jo B was completed.
|  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  | 1974-05-16 | 1974-05-16 |  |  | Cast Iron |  | Oakland
| 79-48752-0 |  |  | 1.25 | Service |  | Other |  | none | Other | none | 1979-09-13 | 1979-10-02 | Other |  | Steel |  | Oakland
26 | 73-49379 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-11-02 | 1973-11-02 | Clamp |  | Steel
26 | 82-00216 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1982-04-01 | 1982-04-15 | Clamp | 2" skinner | Steel |  | Oakland | Inst 2-2" skinner clamp to clear leakage
| 79-48748 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1977-08-05 | 1979-12-13 | Replace Pipe and/or Service |  | Steel
|  |  |  | 2 | Distribution Feeder Main | [6 empty] | 1973-08-09 | 1973-08-10 |  |  | Steel
|  |  |  | 0.06 | Distribution Feeder Main | [6 empty] | 1972-05-26 |  |  |  | Steel |  | Oakland
26 | 74-48952 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-07-24 | 1974-07-24 | Other |  | PE2406/2708 (Yellow)
|  |  |  | 3 | Distribution Feeder Main | [6 empty] | 1973-08-06 | 1973-08-07 |  |  | Steel
|  |  |  | 4 | Other |  | Other |  |  | Other |  | 1974-07-15 | 1974-07-15 | Replace Pipe and/or Service |  | Copper
26 | 77-48702 |  |  | 1.14 | Service |  | Body of Pipe |  |  | Corrosion |  | 1977-07-27 | 1977-07-27 | Clamp |  | Steel |  | Oakland
26 | 75-48857 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1975-10-14 | 1975-10-17 | Replace Pipe and/or Service |  | Steel
26 | 74-55074 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-03-08 | 1974-03-08 | Clamp
26 | 73-49052 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-08-06 | 1973-08-07 | Clamp |  | Steel
|  |  |  | 3 | Other |  | Other |  |  | Other |  | 1973-07-23 | 1973-07-23 |  |  | Steel
26 | 73-48743 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-06-04 | 1973-06-04 | Clamp |  | Steel
26 | 77-49148 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Other | FO | 1977-11-03 | 1977-11-03 | Clamp |  | Steel |  | Oakland | inst. 1-2" clamp to stop leakage
26 | 73-49142 |  |  | 2 | Service |  | Fitting |  |  | Damage by outside Forces |  | 1973-08-28 | 1973-08-29 | Replace Pipe and/or Service |  | Steel
26 | 83-11001 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1983-10-10 | 1983-10-11 | Clamp |  | Steel |  | Oakland | replaced service at 5737 pipe in extremely bad condition. needs replacement.
1 | -10545 |  |  | 1.25 | Service |  | Tap Connection |  |  | Construction Defect |  | 1990-10-25 | 1990-10-25 | Tighten Cap or Bolt |  | Steel |  | Oakland | tightened cap on service tee stopped leakage
26 | 94-23960-1 |  |  | 3 | Service |  | Valves |  |  | Material Failure |  | 1994-06-10 | 1995-08-22 | Tighten Cap or Bolt |  | Steel |  | Oakland | Excavated valve D-94. Replaced grease plug, tightened packing nuts & greased valve
26 | 79--1 |  |  | 30 | Transmission |  | Other |  |  | Other |  | 1979-03-19 |  | Other |  | Steel |  | Oakland | main was exposed to install 3/4" service to 6201 San Leandro St.
|  |  |  | 30 | Transmission | [7 empty] | 1973-02-06 |  |  | Steel
26 | 97-26752-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Other |  | 1997-06-13 | 1998-09-01 | Other |  | Steel |  | Oakland | greased valve to stop leakage
|  |  |  | 24 | Transmission | [10 empty] | Steel
|  |  |  | 30 | Transmission | [8 empty] | Other |  | Steel |  | Oakland | c/o service to 5885 oakport canned 3/4" pin-off tee
26 | 88-20121-1 | [10 empty] | 1988-04-12 | [5 empty] | Oakland
26 | 87-20594-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1987-11-18 | 1988-08-16 | Other |  | Steel |  | Oakland | c/o service at main canned service tee
26 | 95-24549-1 | [10 empty] | 1995-04-28 | [5 empty] | Oakland
26 | 95-24660-1 | [10 empty] | 1995-04-28 | [5 empty] | Oakland
26 | 93-23043-1 |  |  | 0.75 | Service |  | Fitting |  |  | Construction Defect |  | 1993-04-15 | 1994-06-01 | Tighten Cap or Bolt |  | Steel |  | Oakland | redoped & tightened union
|  |  |  | 16 | Distribution Feeder Main |  | Other |  |  | Other |  | 1972-05-30 |  | Other |  | Steel
|  | 153 |  | 20 | Transmission |  | Other |  |  | Other |  |  | 1981-07-31 | Other |  | Steel |  | Oakland | Installed ETS station
| 89-11223-F |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1989-03-09 | 1989-03-20 | Replace Pipe and/or Service |  | Steel |  | Oakland | Replaced 3/4" steel gas service with 1/2" plastic insert a/c corrosion leakage
| 02-20093-1 |  |  | 10 | Distribution Main |  | Valves |  |  | Other | Needed more pipe dope | 2002-04-30 | 2002-07-19 | Other | RE-DOPE & TIGHTEN VALVE AND PLUG TO STOP LEAK | Steel/Wrought Iron |  | Oakland
| 98-20210-1 | 153 |  | 10 | Transmission |  | Drip | Fitting | VALVES | Material Failure |  | 1998-04-20 | 1998-10-13 | Tighten Cap/Bolt - Fitting | GREASE VALVES | Steel/Wrought Iron |  | Oakland | Grease valve fittings to stop leaks & tightened fittings
26 |  |  |  | 16 | Transmission | [6 empty] | 1972-01-18 |  | Other |  | Steel
|  |  |  | 16 | Distribution Feeder Main |  | Other |  |  | Other |  | 1972-07-13 |  | Other |  | Steel
|  |  |  | 0.16 | Distribution Feeder Main | [6 empty] | 1972-06-14 |  |  |  | Steel |  | Oakland
|  |  |  | 12 | Distribution Feeder Main | [7 empty] | 1972-01-19 |  |  | Steel
|  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  | 1974-04-25 | 1974-04-25 | Replace Pipe and/or Service |  | Steel |  | Oakland
|  |  |  | 24 | [7 empty] | 1996-02-16 |  |  |  | Steel |  | Oakland
|  |  |  | 24 | Transmission | [10 empty] | Steel
26 | 74-23268-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1975-09-29 | 1975-10-23 | Other |  | Other |  | Alameda | 2827 Marina Dr; over serv at corner of porch leak at 3/4" nord. serv. valve; repaired leak at this location
| 09-23300-1 |  |  | 0.75 | Single Service |  | Other |  | R.T. | Construction Defect |  | 2009-09-21 | 2010-10-28 | Other | R.T. | Steel | Steel/Wrought Iron | Concord | Riser Threads; Tightened svc valve
| 10-40136 | 114 |  | 0.5 | Single Service |  | Body of Pipe |  |  | Construction Defect |  | 2010-10-08 | 2010-10-10 | Replace Partial Service |  | Aldyl A (Tan or Gray) |  | Brent Wood | 30 Ft from home; Leak on middle street on Fairview. Dug up 35' and put new piece of 1/2 pipe.
| 10-40145 |  |  | 1.25 | Gathering |  | Body of Pipe | Other |  | External Corrosion | Material Failure | 2010-10-03 | 2010-10-03 |  |  | Steel |  | Antioch | Drilled and punched hole over svc. Air tested cust. pool line & determinded it was leaking. Capped line, then informed cust. they would have to have it repaired!
30 | 10-43426-B | 191 |  | 0.75 | Single Service | Hi to Hi set | [6 empty] | 2010-12-15 | Other |  | Steel |  |  | I look at Hi to Hi set. Soaped regulator and fitting down and did not find leak on Hi to Hi set.
| 09-93601-1 | [17 empty] | Soap tested
| 09-26674 |  |  | 1.25 | Single Service |  | Threads |  |  | Construction Defect |  | 2009-10-01 | 2010-11-29 | Other |  |  |  | Danville | Tightened svs valve and doped
| 09-26645 |  |  | 1.25 | Single Service | A.C. | Threads |  |  | Construction Defect |  | 2009-10-01 | 2010-11-29 | Other |  | Steel |  | Danville | Tightened svs valve
| 10-81213-1 | 191-1 | 20.94 | 0.75 | Single Service |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-06 | 2010-11-23 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | Walnut Creek | Same-marked over TP main ifo 212 over service to #211 Los Cerros Ave; Soap test @ 3/4" full circle 2 bolt clamp w/anode
30 | 11-43006-1 |  |  |  | Transmission >= 20% SMYS |  | Other |  | OTHER WELDS | Other | Greased | 2011-01-05 | 2011-03-28 | Greased - Other |  | Steel |  | Walnut Creek | Greased Valve
30 | 11-43005-1 |  |  | 0.75 | Transmission |  | Other Mechanical Joint |  |  | Other | Grease | 2011-01-05 | 2011-03-31 | Replace Main Valve < 2-inch |  | Steel |  | Concord | REPAIRED 3/4" VALVE ON REGULATOR #13 DUE TO LEAKING PACKING STAND OPERATED PIN T'S THAT CONTROL REG #21-22, OPERATED VALVES STOPED THEM FROM LEAKING
30 | 11-43051-B |  |  | 2 | Distribution Main > 60 PSIG |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2011-03-04 | 2011-03-04 | Other |  | Steel |  | Walnut Creek | Removed M-Fitting, Cap-Redoped & Replace Cap
30 | 11-43154-B | 191 | [15 empty] | Martinez
30 | 11-43148-A | SP-3 | [15 empty] | Concord
30 | 11-43151-A | 419 | [15 empty] | Martinez
30 | 11-43132-B | 191 | [15 empty] | Martinez
30 | 05-26003-1 |  |  | 8 | Distribution Main >60 PSIG and <20% SYMS |  | Other Welds |  |  | Construction Defect |  | 2005-02-01 | 2011-06-13 | Fill Weld - Weld |  | Steel |  | Moraga | Fill Well
30 | 11-43132-B | 191 | 32.7 | 2 | Transmission >= 20% SMYS |  | Other |  |  | Other | Needs lube | 2011-05-07 | 2011-06-16 | Greased - Other |  | Steel |  | Martinez | Greased Valve (2) in pit
30 | 10-81244-1 | 191A | 206 | 0.75 |  |  | Fitting |  |  | Other |  | 2010-03-12 | 2011-03-12 | Other |  | Steel |  | Lafayette | Cap on set tighten
30 | 11-43133-A | STANPAC3 | 468 | 2 | Transmission >= 20% SMYS |  | Other |  | Loose meters | Other | Loose meter bolts on cust reg pit | 2011-05-12 | 2011-07-07 | Tighten Cap or Bolt |  | Steel |  | Martinez | Loose meter bolts on cust reg pit
30 | 11-43151-1 | 419 |  | 12 | Transmission |  | Other |  |  | Other |  | 2011-07-19 | 2011-07-19 | Other |  | Steel |  | Martinez | Replaced "O" ring on MTR-body
| 84-45434-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1984-10-25 | 1984-11-08 | Clamp |  | Steel |  |  | INST. PERM. CLAMP.
30 | 86-45984-1 |  |  | 3 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1986-06-27 | 1986-06-27 | Other |  | Steel |  | ORINDA | HOSE LINE LEAK ONLY
30 | 86-46141-1 |  |  | 0.5 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1986-12-02 | 1986-12-02 | Replace Pipe and/or Service |  | Copper |  | ORINDA | INSTALL 2' OF PL PIPE TO REPLACE LEAK ON 1/2 @ SERVS BY SERVS TEE USED: ALDYIR PIPE
30 | 76-20715-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1976-09-10 | 1977-03-14 | Other |  | Steel |  | LAF | DUG OUT AROUND V-4.82 50 M&C MECH. COULD SERVICE LEAKING PACKING THIS VALVE IS IN CASED IN LARGE MAN HOLE
30 | 81-22119-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Construction Defect |  | 1981-06-26 | 1984-02-07 | Weld Over Sleeve or Can |  | Steel |  | ORD
30 | 71-40433-1 |  |  | 2 | Distribution Feeder Main |  | Fitting |  |  | Corrosion |  | 1971-12-22 | 1972-01-12 | Patch Welded |  | Steel |  | OR
|  |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1990-08-13 | 1990-08-13 |  |  | Steel |  |  | ACROSS FROM ADRESS 156 LOMBARDH LN TAR WRAP FELL OF T.P.: REWRAP T.P. MAIN-INSPECT E.B.M.V.P. TRENCHING
30 | 80-21934-1 |  |  | 2 | Transmission |  | Other Welds |  |  | Construction Defect |  |  | 1982-04-29 | Weld Over Sleeve or Can |  | Steel |  | ORINDA
30 | 76-20716-1 |  |  | 2 | Transmission |  | Valves |  |  | Other |  | 1976-09-10 | 1976-12-07 | Other |  | Steel |  | LAF | VALVE WAS GREASED (SHOULD BE CHECKED AGAIN) ISSUED NEW FORM a ON 4/11/77 CAL.
|  |  |  | 0.5 | Service | [6 empty] | 01/22/0892 | 1982-01-22 | Replace Pipe and/or Service |  | Copper |  | ORINDA | C/O OLD SERVICE MUD SLIDE
30 | 01-22844-1 |  |  | 0.5 | Distribution Main | SERVICE | Girth Weld |  |  | Material Failure |  | 1986-11-15 | 1987-01-14 | Patch Welded |  | Copper |  | ORINDA | THIS A COPER SERVICE. THERE WAS FAILURE MY REPORT WAS 1/3 OF 1/2 PLASTIC TRANS FITTING TO STOP
30 | 01-22844-1 |  |  | 0.5 | Distribution Main | SERVICE | Girth Weld |  |  | Material Failure |  | 1986-11-15 | 1987-01-14 | Patch Welded |  | Copper |  | ORINDA | THIS A COPER SERCIE THERE WAS FAILURE MY REPORTS WAS 1/3 OF 1/2 PLASTIC TRANS FITTING TESTED
| 86-45970-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1986-06-06 | 1986-06-06 | Replace Pipe and/or Service |  | Copper |  | ORINDA | INSTALLED NON CORRODIBLE RAISER TO REPAIR BROKEN GAS LINE
30 | 79-21815-1 |  |  | 2 | Other |  | Tap Connection |  |  | Other |  | 1979-11-14 | 1983-10-14 | Other |  | Steel |  | ORINDA
| 86-46092-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  |  | 1986-10-30 | Replace Pipe and/or Service |  |  | A | OR | REPAIR 1/2 SERVS USED 2 1/2 CUP & TWO FEET OF PL PIPE
30 | 76-20712-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1976-09-10 | 1977-02-18 | Other |  | Steel |  | LAF | CAP LEAKING ON PIN-OFF TEE FOR SERV TO #56 TIGHTENED CUP
30 | 80-44000-1 |  |  | 0.6 | Service | TRANSMISSION | Fitting |  |  | Material Failure |  |  | 1980-04-16 | Replace Pipe and/or Service |  | Copper |  | ORINDA | SEVERAL LNS ON HIGH REG SET AT P/L. & ON INSULATOR AT REG SET INSTALLED 1' 1/3 PL TO CU & TRANS FITTING K TYPE COUPLING GAS MECH REPAIRED LK'S ON REG SET
30 | 86-22852-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1986-12-02 | 1986-12-04 | Clamp |  | Steel |  | ORINDA
30 | 78-43314-1 |  |  | 2 | Transmission |  | Tap Connection |  |  | Other |  |  | 1978-12-13 | Other |  | Steel |  |  | REDOPED & TIGHTENED CAP.
|  |  |  | 8 | Transmission |  | Other |  |  | Other |  |  | 1978-12-13 | Other |  | Steel |  | ORINDA
30 | 75-42382-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1975-10-14 | 1976-01-20 | Other |  | Steel |  | ORINDA | BARTESTED INTERSECTION OF ORINDA WAY & CAMINO SOBRANTE - USED JW (LEL) 4% SCALE; NO READINGS -; GREASED VALVE #6.32 ON 6" LINE 191A AS IT WAS LEAVING
30 | 86-22858-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1986-12-20 | 1987-07-23 | Patch Welded |  | Steel |  | ORINDA REG | REPAIRED LEAK AT TEE OFF 2" BY PASS MAIN TEE FEEDS CHART STAT
30 | 77-21148-1 |  |  | 8 | Transmission |  | Valves |  |  | Other |  | 1977-09-20 | 1978-05-05 | Other |  | Steel |  | ORINDA | FOUND 10/10 READING COMEING FROM VALVE FRAME.
30 | 86-46113-1 |  |  | 0.5 | Distribution Main |  | Body of Pipe |  |  | Digin |  | 1986-11-12 | 1986-11-12 | Replace Pipe and/or Service |  | Plastic |  | ORINDA | REPAIR 1/2 PL SERVS USED: 1' OF 1/2" PL PIPE AND TWO MECH FITT
30 | 86-46111-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1986-11-10 | 1986-11-10 | Other |  | Plastic |  | ORINDA | CONTRACTOR KING'S LEAK
30 | 86-46081-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Digin |  | 1986-10-23 | 1986-10-23 |  |  | Plastic
30 | 79-43780-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-12-20 | 1979-12-27 | Other |  | Other |  | MDR
30 | 87-46363-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-09-25 | 1987-09-25 | Replace Pipe and/or Service |  | Plastic |  | MORAGA | REPAIR 1/2 PL PIPE USED. TWO MECH. & 2' OF PL PIPE
30 | 87-46368-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1987-10-07 | 1987-10-07 |  |  |  | A | MORAGA | REPAIR 1 1/4 PL MAIN USED 4' OF PL PIPE & ONE TEE & TWO CUPL
| 80-23184-1 |  |  | 0 | [5 empty] | Other |  | 1980-01-08 | 1983-10-21 | Other |  |  |  | MARTINEZ | 70 PPM IN COLD TEST HOLE. & VER MAIN IN STREET MARKED WITH YELLOW PAINT; LOUIES REPAIRED 1979; NOTE: READINGS IN PT&T FRENCH RUNNING PARALLEL TO PG&E MAIN IN STREET...
30 | 81-46229-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-02-03 | 1981-08-26 | Other |  | Other |  | MARTINEZ | 15% GAS OVER MAIN TIE IN AREA. ON MARINA VISTA MARKED W/ YELLOW PAINT. 20% GAS
30 | 80-23259-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-02-01 | 1981-02-03 | Other |  | Other |  | MARTINEZ | .07% GAS OVER MAIN OLD SVC TEE AREA (CUT OFF) EDGE OF ROADWAY MARKED WITH YELLOW PAINT.
30 | 80-23260-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-02-01 | 1981-02-03 | Other |  | Other |  | MARTINEZ | .05% GAS OVER MAIN NEAR PG&E ANODE ON LAGUNA ST .1% GAS OVER MAIN NEARBY. EDGE OF ROAD MARKED BOTH LOCATIONS WITH YELLOW PAINT.
| 76-42737-1 |  |  | 12 | Other |  | Body of Pipe |  |  | Corrosion |  | 1976-05-07 | 1976-05-12 | Patch Welded |  | Steel |  | MARTINEZ | NO. 2 LEAK; GET JOB NO @ SLEAM PLANT - HOUSE LINE LEAK; INST #4 PATCHES 6" X 6" X 1/4'
30 | 72-20448-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-12-04 | 1972-12-13 | Weld Over Sleeve or Can |  | Steel |  | MT2 | FOUND 5% GAS OVER SERVICE. FOUND LEAK 1 1/4" BEHIND BANK OF AMERICA MECH WELDED ON A CAN.
30 | 74-41142-1 |  |  | 0.5 | Service |  | Physical/Mechanical Joint |  |  | Other |  | 1974-03-13 | 1974-03-15 | Other |  | Plastic
30 | 73-20483-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-08-06 | 1973-08-08 | Replace Pipe and/or Service |  | Steel |  | MARTINEZ | FOUND 301 AT RISER LOCATION INSTALLED TEMP CLAMP AND ALSO HAD TO GRAY TAPE AND DUCT SEAL SMALL LEAKS AT RISER BEND, SERVICE NEEDS RERUN.; RERUN SERV.
30 | 76-42936-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Corrosion |  | 1976-10-28 | 1976-11-04 | Replace Pipe and/or Service |  | Steel |  | MARTINEZ | NO. 2 LEAK ODOR IN STORE
30 | 80-23157-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-02 | 1980-12-08 | Other |  | Other |  | MARTINEZ | .02% GAS OVER MAIN IN STREET YELLOW PAINT
30 | 81-23591-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-07-30 | 1983-07-15 | Other |  | Other |  | MARTINEZ
30 | 81-23595-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-08-03 | 1983-07-15 | Other |  | Other |  | MARTINEZ
30 | 80-23159-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-02 | 1980-12-10 | Other |  | Other |  | MARTINEZ | .02% GAS OVER MAIN IN STREET. YELLOW PAINT
30 | 80-23158-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-02 | 1980-12-10 | Other |  | Other |  | MARTINEZ | .02% GAS OVER MAIN IN STREET. S/TEE AREA. YELLOW PAINT
30 | 79-23154-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-12-27 | 1980-12-08 | Other |  | Other |  | MARTINEZ | .1% GAS OVER MAIN IN ST. S/TEE AREA STRONG AREA ODOR. MARKED IN YELLOW PAINT. 0% GAS PER CREW REPAIRS...
30 | 79-23155-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-12-27 | 1980-06-25 | Other |  | Other |  | MARTINEZ | 10% + GAS IN WATER BOX MARKED IN YELLOW PAINT.
30 | 74-41795-1 |  |  | 0.75 | Other |  | Meter |  |  | Other |  | 1974-12-05 | 1974-12-12 | Other |  | Steel |  | MTZ | .2% IN 6MM CURB BOX
30 | 79-22798-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-03-20 | 1982-02-23 | Other |  | Other |  | MARTINEZ | .035 GAS IN OLD BELL HOLE OVER MAIN. SUC TEE AREA
30 | 71-60183 |  |  | 4 | Transmission |  |  |  |  | Other |  | 1971-11-24 | 1971-11-24 | Other |  | Steel |  | MTZ | REWRAP DUE TO INST. OF WATER MAIN
30 | 72-00000-0 |  |  | 4 | Transmission |  | Other |  |  | Other |  | 1972-01-07 | 1972-01-07 | Other | REWRAP | Steel |  | MTZ | REWRAP MAIN EXPOSED BY CONTRACTOR TO INSTALL STORM DRAIN
30 | 78-43629-1 |  |  | 6 | Other | VALVE TO D MAIN | Valves |  |  | Other | GREASE NIPPLE | 1978-01-24 | 1978-01-26 | Other |  | Steel |  | MARTINEZ | INSTALLED NEW GREASE NIPPLE, RESOCKED VALVE, ALL TESTS NEGATIVE; WHILE ON MAIN INSPECTION FOUND ODOR IN VALVE, GREASED SOME AND RESEARCHED AT 2:30PM TIN 25% G IN
30 | 79-23145-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-12-18 | 1980-12-08 | Other |  | Other |  | MARTINEZ | LEAK REPAIRED ON 80-44943; .7% GAS OVER MAIN. S/TEE AREA OF STREET, MARKED IN YELLOW PAINT; 0% GAS PER CREW REPAIRS
30 | 74-41609-1 |  |  | 1.5 | Other |  | Other |  |  | Other |  | 1974-10-09 | 1974-10-09 | Other |  | Steel |  | MARTINEZ | BARTESTED HOUSELINE FOUND 100 DEGREES TO g. AND BLOWING OVER OLD BELL HOLE WHERE OLD HOUSE LINE AND NEW ONE CONNECT. NOTIFIED CUSTOMER, ADVISED TO SHUT OFF OLD HOUSELINE. RECHECKED AFTER 20 MINUTES FOUND ALL TESTS NEGATIVE
30 | 78- |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1978-02-08 | 1978-02-08 | Other |  | Steel |  | MTZ | REWRAPPED MAIN DUE TO CONSTRUCTION OF
30 | 80-23180-1 |  |  | 0 |  |  | Other |  |  | Other |  | 1980-01-08 | 1982-11-23 | Other |  |  |  | MARTINEZ | 50 PPNI AT BASE OF RISER
30 | 80-46094-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-12-10 | 1981-03-17 | Other |  | Other |  | MARTINEZ | UPGRADED FROM 80-23160
30 | 80-23182-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-08 | 1982-11-23 | Other |  | Other |  | MARTINEZ | 40 PPM IN OLD BELL HOLE. EVER MAIN 75' RIGHT OF DRIVEWAY ENTRANCE. SVC TEE AREA TO 1127 ACROSS THE STREET; 0% CREW REPAIRS?
30 | 80-46108-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-12-18 | 1981-03-17 | Other |  | Other |  | MARTINEZ | UPGRADED FROM 80-23183
30 | 75-21137- |  |  | 2 | Other |  | Body of Pipe |  |  | Corrosion |  | 1975-04-22 | 1976-12-13 | Clamp | SKINNER | Steel |  | MTZ | UPGRADED & REPAIRED ON 76-42956; INST (2) 2" SKINNER CLAMP TO REPAIR LEAK 2" MAIN. EXPOSED 50" OF MAINE AND FOUND THAT PIPE IS IN VERY BAD CONDITION ALL SECTION OF PIPE EXPOSED PITTING IS HEAVY AND CORRODED BUT MAIN IS 22" DEEP; .1% GAS LEFT SIDE OF DRIVEWAY OVER MAIN ODOR IN AIR; NO LEAK
30 | 76-42956-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-12-09 | 1976-12-09 | Clamp | SKINNER | Steel |  | MARTINEZ | INSTALLED (2) 2" LEAK CLAMP SKINNER; 2" MAIN IN VERY BAD CONDITION. THE 48" OF PIPE EXPOSED WERE ALL PRETTY BAD AND HEAVY CORROSION
30 | 80-23176-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-07 | 1981-12-23 | Other |  | Other |  | MARTINEZ
30 | 82-24112-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-07-23 | 1983-07-15 | Other |  | Other |  | MTZ
30 | 80-44964-1 |  |  | 0.5 | Service |  | Tap Connection |  |  | Material Failure |  | 1980-02-27 | 1980-02-28 | Replace Pipe and/or Service |  | Copper |  | MARTINEZ | RERAN 1/2" COPPER LOOKING SER WITH 1/2" PL PIPE
30 | 79-23128-1 |  |  | 0.5 | Distribution Main |  | Tap Connection |  |  | Material Failure |  | 1979-12-07 | 1980-02-27 | Replace Pipe and/or Service |  | Copper |  | MARTINEZ | FOUND 1/2" COPPER TO 3/4 STL SERV TEE LEAKING. RERAN SERV WITH 1/2" PL. 2-26-80
30 | 79-23111-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-12-05 | 1981-11-20 | Other |  | Other |  | MARTINEZ
30 | 79-23119-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-12-07 | 1981-11-20 | Other |  | Other |  | MARTINEZ
30 | 79-23108-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-12-05 | 1981-11-20 | Other |  | Other |  | MARTINEZ
30 | 80-23216-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-18 | 1980-12-04 | Other |  | Other |  | MARITNEZ
| 77-43173-1 |  |  | 12 | Distribution Feeder Main |  | Valves | Body of Pipe |  | Corrosion |  | 1977-04-19 | 1977-04-22 | Weld Over Sleeve or Can |  | Steel |  | MARTINEZ | INST. 8" X 24" CAN ON TOP OF MAIN & 12" X 12" FULL ENCIRCLEMENT SLEEVE (.375 W.T.)
30 | 77-43173-1 |  |  | 12 | Distribution Feeder Main |  | Valves |  |  | Corrosion |  | 1977-04-19 | 1977-04-22 | Weld Over Sleeve or Can |  | Steel |  |  | INST CAN OVER 1" VALVE ON MAIN; TO ENTER GO TO SHELL MAIN GATE AT HOWE RD E/O PACHECO BLVD. ASK TO HAVE SECURITY MAN OPEN GATE #62 AND ENTER FROM JEFFERSON STREET OFF SHELL AVE
30 | 80- |  |  | 12 | Transmission |  | Other |  |  | Other |  | 1980-11-13 | 1980-11-13 | Other | T.P. MARKERS | Steel |  | MARTINEZ | INSTALLED 3 T.P. MAIN MARKERS AT 2 ANGLE POINT DUE TO RECONSTRUCTION OF ROAD SEE ATTACHED PLAT SHEET
30 | 80-23222-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-21 | 1982-11-24 | Other |  | Other |  | MARTINEZ
30 | 81-23637- |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-09-24 | 1982-01-13 | Other |  | Other |  | MARTINEZ | 25% GAS OVER SVC... SLIGHT ODOR; THIS IS NOT A DUPLICATE OF
30 | 80-23250-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-29 | 1980-12-18 | Other |  | Other |  | MARTINEZ
30 | 80-23248-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-29 | 1980-12-18 | Other |  | Other |  | MARTINEZ
30 | 80-23246-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-02 | 1980-12-18 | Other |  | Other |  | MARTINEZ
30 | 79-23135-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-12-12 | 1980-12-16 |  |  | Other |  | MARTINEZ | 0% GAS IN WATER BOX CHECKED TEST HOLES OVER SVC & MAIN IN STREET (3) WITH FLAME PACK... NEGATIVE RESULTS
30 | 79-23134-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-12-12 |  | Other |  | Other |  | MARTINEZ | BARTESTED MAIN FOR 400' AND HAD NEGATIVE READINGS. ALSO BARTESTED 8 SERVICES AND HAD NEGATIVE RESULTS. NOTE: SHOULD BE RECHECKED WITH FLAME PACK; CHECKED WITH JILL ON 4% RESULTS NEGATIVE 1-4-80 D. BRITT
30 | 83-24406-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-03-24 | 1983-06-17 | Other |  | Other |  | MARTINEZ | 0% OVER SVC & MAIN 2% - 3% IN SHUT SEE VALVE COVER IN LAWN... (BUBBLES VISABLE); MADE OUT C-TAG...
| 89-43058-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1989-06-16 | 1989-06-20 | Weld Over Sleeve or Can |  | Steel |  | CONCORD | PIPELINE SURVEY DWG #8485 SHT 1 OF 1 POSTED E. WITH LINE 191 IN WM65 PLAT CABINET
30 | 76- |  |  | 12 | Transmission |  | Other |  |  | Other |  | 1976-08-11 | 1976-08-11 | Other | INSPECTION | Steel |  | CONCORD-AVON | S FEE RAILROAD TRENCHING FOR STORM DRAIN 6' DEEP. 12 T.P. MAS NOT EXPOSED, NO REWRAP NEEDED ALL CONDITIONS O.K.
30 | 77- |  |  | 12 | Transmission |  | Other |  |  | Other |  | 1977-08-10 | 1977-08-10 |  | REWRAP | Steel |  |  | REWRAP OF 12" T.P. MAIN DUE TO ISNTALLATIONO F 20" STORM DRAIN BY C.C.C. FLOOD CONTROL
30 | 81-46340-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1981-06-17 | 1981-09-10 | Patch Welded |  | Steel |  | CONCORD | UPGRADED #80-23382; WELDED PATCH ON 12" MAIN SUPPLYING TOSCO
30 | 80-23199-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-16 | 1981-12-16 | Other |  | Other |  | MARTINEZ | 50 PPM IN OLD BELL HOLE IN STREET HEAR OLD LEAK MARK...12-16-1980 R. O'CONNOR
30 | 80-23200-1 |  |  | 0 | Other |  | Other |  |  | Other |  |  | 1982-11-24 | Other |  | Other |  | MARTINEZ
30 | 80-23430-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-11-06 | 1981-11-17 | Other |  | Other |  | MARTINEZ | I BELIEVE THIS IS A DUPLICATE A-FORM
30 | 81-23656-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-11-06 | 1982-11-17 | Other |  | Other |  | MARTINEZ | 0% ... CREW REPAIRS?; NOTE: THIS IS A DUPLICATE A-FORM... I HAVE ALREADY RE THIS LEAK OUT
30 | 80- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1980-01-23 | 1980-01-23 | Other |  | Steel |  | MARTINEZ | REWRAP T.P. 10" GM; REWRAP DUE TO INST OF GASOLINE LINE FOR CHEVRON OIL COMPANY
30 | 72-20212-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-04-13 | 1973-02-13 | Clamp |  | Steel |  | MTZ
30 | 72-20211-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-04-13 | 1973-01-20 | Clamp |  | Steel |  | MTZ | INST. 2" SKINNER CLAMP ON 2" MAIN
30 | 80-23172-1 |  |  | 0 | Other |  | Other |  |  | Other |  |  | 1980-12-10 | Other |  | Other |  | MARTINEZ
30 | 80-23173-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-04 | 1980-12-11 | Other |  | Other |  | MARTINEZ
30 | 82-46940-1 |  |  | 0.5 | Service |  | Fitting |  |  | Material Failure |  | 1982-10-13 | 1982-10-28 | Replace Pipe and/or Service |  | Copper |  | MARTINEZ | CUSTOMER CONCERNED; 100% GAS OVER MAIN SVC TEE AREA MIGRATION... FLAME OUT IN WATER BOYES TO CALLED FOR CREW; VERY STRONG ODOR
30 | 73-00000-0 |  |  | 0 | Other |  | Other |  |  | Other |  | 1973-11-08 | 1973-11-08 | Other |  | Other |  | MTZ | AREA OF LEAK IS IN HOUSING DEVELOPMENT ON ESTADILLO ST. NOT OUR LINES CONTRACTOR DIGGING UP AREAS TO INSERT PLASTIC. ARE DOES HAVE
| 08-23624-1 |  |  | 0.5 | Single Service |  | Body of Pipe |  |  | Construction Defect |  |  | 2009-02-13 | Replace Entire Service |  | Steel/Wrought Iron |  | MARTINEZ | REPLACED COPPER SERVICE INSTALLED 1/2 PL
30 | 80-23215-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-18 | 1981-12-21 | Other |  | Other |  | MARTINEZ
30 | 80-23219-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-21 | 1981-12-16 | Other |  | Other |  | MARTINEZ
30 | 80-23218-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-21 | 1981-11-17 | Other |  | Other |  | MARTINEZ
30 | 79-23124-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-12-07 | 1981-11-20 | Other |  | Other |  | MARTINEZ
30 | 80-23211-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-18 | 1981-12-16 | Other |  | Other |  | MARTINEZ
30 | 80-23208-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-18 | 11/00/0000 | Other |  | Other |  | MARTINEZ
30 | 83-47272-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-10-05 | 1983-10-18 | Other |  | Other |  | MARTINEZ
30 | 74-41307-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-08-05 | 1974-06-07 | Replace Pipe and/or Service |  | Steel |  | MARTINEZ | REPLACED SERVICE WITH 1/2" PL SERVICE PIPE
30 | 74-20769-1 |  |  | 0.75 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-03-27 | 1974-08-09 | Replace Pipe and/or Service |  | Steel |  | MARTINEZ | LEAK TAS HAS ALREADY BEEN MADE OUT FOR THIS ADDRESS- TALLEY THIS MAIN IS ALL SCREWED FITTINGS AND SHOULD BE REPLACED
| 02-23021-1 | [16 empty] | MARTINEZ
| 80-23203-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-16 | 1982-11-24 | Other |  | Other |  | MARTINEZ
|  |  |  | 4 | Gathering |  | Other |  |  | Other |  |  | 1979-09-10 | Other | INST E.T.S. | Steel |  | MTZ | NO LEAK.
30 | 80-23235-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-24 | 1982-03-03 | Other |  | Other |  | MARTINEZ
30 | 73-20481-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-06-21 | 1973-08-06 | Clamp |  | Steel |  | MARTINEZ | FOUND LEAKING 2" MAIN INST. 2" SKINNER CLAMP
30 | 72-20231-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-04-17 | 1974-02-15 | Clamp |  | Steel |  | MARTINEZ | BAR TESTED FOUND 30% GAS OVER MAIN AND 20% GAS IN WATER VALVE; INSTALLED PERMANENT REPAIR CLAMP
30 | 80-23234-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-23 | 1981-03-12 | Other |  | Other |  | MARTINEZ
30 | 77- |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Damage by outside Forces |  | 1977-03-08 | 1977-03-08 | Other | REWRAP | Steel |  | MARTINEZ | REWRAP DUE TO INST OF WATER MAIN CITY OF MARTINEZ; CONDITION OF PIPE & WRAP VERY POOR
30 | 80-23228-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-21 | 1981-01-02 | Other |  | Other |  | MARTINEZ
30 | 80-23232-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-22 | 1981-12-15 | Other |  | Other |  | MARTINEZ
30 | 80-23231-1 |  |  | 0 | Other |  | Other |  |  | Other |  |  | 1981-12-15 | Other |  | Other |  | MARTINEZ
30 | 80-23258-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-31 | 1981-03-12 | Other |  | Other |  | MARTINEZ
30 | 73-40910-1 |  |  | 22 | Transmission | [6 empty] | 1973-11-08 |  | Other |  | Steel |  | MARTINEZ | LOCATED & PINPOINTED LEAK ON STANPAC 22" MAIN SO THEY CAN HAVE THEIR CREW REPAIR IT. REFERRED TO STANPAC THEY WILL REPAIR
30 | 80-23245-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-28 | 1980-12-19 |  |  | Other |  | MARTINEZ
30 | 80-23244-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-28 | 1981-12-21 | Other |  | Other |  | MARTINEZ
30 | 73-40739-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1973-06-29 | 1973-06-29 | Replace Pipe and/or Service |  | Copper |  | CON | MADE TEMP REPAIRS REPLACED 15' OF SERV PIPE RECEMEND RERUN SERV AT LATER DATE
30 | 80-23193-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-10 | 1980-12-04 | Other |  | Other |  | MARTINEZ
30 | 74-41470-1 |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1974-08-15 | 1974-08-15 | Other |  | Steel |  | MTZ | BAR TESTED T.P. AND D MAIN ALSO SERVICES, CHECKED SEMER AND VINE HILL ROY. STATION. NO ODOR IN AIR ALL IN GROUND TEST NEGATIVE CALLED GUS DISPATCH FOR FLAME PACK COSTUMER CLAIMS STRONG ODOR IN BACK ROOM OF WORK SHOP
30 | 77- |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1977-03-25 | 1977-03-25 | Other | INSTALLING T.P. MARKERS | Steel |  |  | INSTALLED NEW TYPE T.P. WARMING MARKED ON OLD EXISTING STAKES AND POLES.
30 | 73-40479-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-01-19 | 1973-01-22 | Patch Welded |  | Steel |  | PACHECO | BUBBLES NEAR VINE METER STA
30 |  |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1976-04-26 | 1976-05-03 | Other |  | Steel |  | MARTINEZ | WRAPPED MAIN DAMAGED BY ELECT DEPT
30 | 76- |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1976-09-03 | 1976-09-03 | Other | REWRAP | Steel |  | MARTINEZ | REWRAP DUE TO INST. OF DEW LINE.
30 | 80-23277-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-02-07 | 1981-01-06 | Other |  | Other |  | MARTINEZ
| 10-43067- | [10 empty] | 2010-02-24 | [5 empty] | MARTINEZ
30 |  |  |  | 6 |  |  | Body of Pipe |  |  | Damage by outside Forces |  |  | 1977-08-02 | Replace Pipe and/or Service |  | Steel |  | MTZ | NOTE: RETAIN IN FILE: UNUSED PIPE DAMAGED BY OUTSIDE PARTY.
30 | 72- |  |  | 12 | Transmission |  | Other |  | REWRAP | Other |  | 1972-09-01 | 1972-09-01 | Other | REWRAP | Steel |  | CONCORD | REWRAP DUE TO CONTRACTOR INSTALLING NEW PIPE LINE FOR PHILLIPS OIL CO. ALEX ROBERTSON CONST. WALLBERG CONST
30 | 80-23275-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-02-06 | 1982-01-15 | Other |  | Other |  | MARTINEZ
30 | 80-23276-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-02-06 | 1981-02-06 | Other |  | Other |  | MARTINEZ
| 72-00000-0 |  |  | 10 | Transmission |  |  |  | NONE |  | NONE |  |  | Other |  | Steel |  | MARTINEZ
30 | 75- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1975-01-29 | 1975-01-29 | Other | REWRAP | Steel |  | MARTINEZ | REWRAP OF 10" T.P. MAIN DUE TO INST OF OIL PIPE LINE BY CONSTRUCTOR
30 | 83-24206-1 |  |  | 0.5 | Other | C/O SERV. | Fitting |  | C/O SERV. TEE | Corrosion |  | 1968-01-26 | 1983-04-25 | Other | C/O SERV. TEE | Steel | C/O SERV. TEE | MTZ | C/O ABANDONED SERV. TEC
30 | 83-24205-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-01-25 | 1983-04-06 | Other |  | Other |  | MTZ | BAR TESTED SERVICE 0% OVER SERVICE
30 | 80-23274-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-02-05 | 1981-02-06 | Other |  | Other |  | MARTINEZ
30 | 81-23583-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-07-23 | 1981-12-10 | Other |  | Other |  | MARTINEZ
30 | 75-00409-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1975-02-05 | 1981-08-12 | Other |  | Other |  | MTZ
30 | 74-41343-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-06-25 | 1974-06-25 | Clamp |  | Steel |  | MARTINEZ | WHILE RERUNNING SERVICE AT THIS ADDRESS FOUND MAIN LEAKING. INST "1-2" SKINNER CLAMP
30 | 74-41811-1 |  |  | 1.5 | Other |  | Fitting |  |  | Material Failure |  | 1974-12-17 | 1974-12-18 | Other |  | Steel |  | MTZ | REPAIRED 2- FUSS LEAKS IN DIST REG PIT
30 | 75- |  |  | 1.25 | Transmission | [7 empty] | 1975-06-27 | Other |  | Steel/Wrought Iron |  | MARTINEZ | INSTALLED 2" FIRE VALVE IN 1 1/4" T.P. LINE TO ORLEANS DISTRIC REGULATOR STATION
30 | 72-40394-1 |  |  | 0.5 | Other |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1972-10-25 | 1972-10-25 | Other |  | Steel |  | MARTINEZ | UPON ARRIVAL FOUND STATIC LINE TO LARGE METER SET BROKEN BROKEN BY PID REPARIED SAME BY REPLACING NIFFPLE & ELLS. ALSO REPAIRED 2" FLAMES LEAKING AT BOLTS AFTER MAKING REPAIRS CHECKED FUMOU FOUND O.K.
30 | 80-23313-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-03-13 | 1982-02-23 | Other |  | Other |  | MARTINEZ
30 | 77- |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1977-12-01 | 1977-12-01 | Other | REWRAP | Steel |  | PACHECO | REWRAP DUE TO INST. OF SEWER LATERAL TO NEW BUILDING; TRANSMISSION MAIN EXCELLENT CONDITION
30 | 76- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1976-07-21 | 1976-07-21 | Other | REWRAP | Steel |  | PACHECO | REWRAP OF 10" T.P. DUE TO INSTALLATION OF WATER MAIN 2' CLEARANCE BETWEEN WATER MAIN AND GAS MAIN
30 | 74- |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1974-08-13 | 1974-08-13 | Other | INSTALL T.P. MARKERS | Steel |  | PACHECO | INSTALLED 5 T.P. MARKERS ON PACHECHO BLVD OVER 6" T.P. MAIN ON JUTER SECTION OF PACHECO BLVD & BLUM RD
30 | 00- |  |  | 2 | Transmission |  | Other |  |  | Other |  | 1973-05-07 |  | Other |  | Steel |  | MTZ | REPLACED VALVE FRAME & COVER GREASED VALVE
30 | 75- |  |  | 2 | Transmission | [7 empty] | 1975-01-23 | Other |  | Steel/Wrought Iron |  | PACHECO | INSTALLED TRAFFIC VALVE FRAME AND COVER OVER VALVE #C-86
|  |  |  | 6 | [11 empty] | Steel |  | PACHECO | INSTALLED 2 #10 WIRES ON 6" MAIN. MAIN EXPOSED DUE TO WORK BY CONTRACTOR INSTALLING FIBER OPTIC CONDUIT.
30 | 76- |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1976-07-26 | 1976-07-26 | Other | REWRAP | Steel |  | PACHECO | WRAP T.P. GAS MAIN DUE TO INST OF POWER POLE PG&E
30 |  |  |  | 6 | Distribution Feeder Main | [12 empty] | PH | INST 2-3/4" GAUGE LINES TESTED AT 640PSIG FOR 1HR. TAPPED WITH 1/4" BIT USED 1" VALVE TEE
30 | 83-24311- |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-03-11 | 1983-04-01 | Other |  | Other
|  |  |  | 10 | Transmission | [7 empty] | 1981-06-09 | Other |  | Steel |  | MTZ | REPAIRED DAMAGED WARP, CAUSED BY BROKEN WATER MIN & TREE ROOT DAMAGE
30 | 72-20273-1 |  |  | 2 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-04-20 | 1973-01-15 | Patch Welded |  | Steel |  | MTZ
30 | 75-21259-1 |  |  | 4 | Transmission |  | Longitudinal Weld |  |  | Corrosion |  | 1975-09-19 | 1975-09-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | MARTINEZ | FOOT SURVEY FOUND LEAK WITH F.P. NOTIFIED ME. I REPLACED WITH J.W. AND FOUND 10% GUS CA 10' E/S OF CREEK SEE SKETH WAS REPAIRED ON TAG
30 | 76- |  |  |  | Transmission | [7 empty] | 1976-11-24 | Other |  | Steel/Wrought Iron |  | MTZ
30 | 75-21259-1 |  |  | 4 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 1975-09-18 | 1975-09-19 | Other |  | Steel/Wrought Iron |  | MTZ | WELDED OVER SMALL PIN HOLE LEAK ON 45° WELD- ELL. FOR PERMANENT REPAIRS
30 | 80-23263-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-02-01 | 1982-01-18 | Other |  | Other |  | MARTINEZ
| 10-43285-1 | [10 empty] | 2010-08-09 | [5 empty] | MARTINEZ
30 | 86-47923-1 |  |  | 0.75 | Service |  | Valves |  |  | Material Failure |  | 1986-06-14 | 1986-06-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | MTZ | BLOW OFF TO HITOHI SET WENT OFF FIEXED REPLACEING HI TO HI SET
30 | 86-48005-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1986-09-22 | 1986-09-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | MTZ | INST (2) F" CAPS ON END OF MAIN
30 | 73-00000-0 |  |  | 0.75 | Distribution Feeder Main | [8 empty] | Other |  | Steel/Wrought Iron |  |  | RAISED VALVE FRAME & COVER; GREASED VALVE.
30 | 80-45003-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-03-28 | 1980-08-07 | Other |  | Other |  | MARTINEZ | AT THIS TIME THERE IS NO SIGN OF ANY LEAKAGE AT THIS SPOT. FURTHER INVESTIGATION WITH FLAME PACK PROVED NEGATIVE LEAK RE-CHECK: 8-7-80
30 | 82-46609-1 |  |  | 0 |  |  | Other |  |  | Other |  | 1982-02-23 | 1982-06-29 | Other |  |  |  | MARTINEZ | UPGRADED #80-23305; 0%... CREW REPAIRS?
30 | 82-46607-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-02-23 | 1982-06-29 | Other |  | Other |  | MARTINEZ | UPGRADED #8023307; 0%...CREW REPAIRS?
30 | 80-23299-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-02-28 | 1981-02-13 | Other |  | Other |  | MARTINEZ
30 | 80-23301-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-02-28 | 1981-02-13 | Other |  | Other |  | MARTINEZ
30 | 80-23300-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-02-28 | 1982-01-13 | Other |  | Other |  | MARTINEZ
30 | 80-23296-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-02-28 | 1980-03-06 | Other |  | Other |  | MARTINEZ | BARTESTED AFTER (2) LEAKS WERE REPAIRED 40' FROM THIS LOCATION. HAD NEGATIVE READINGS. ALL CLEAN.; CLEARED ON LEAK #80-232971
30 | 72-40220-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-02-18 | 1972-02-23 | Patch Welded |  | Steel/Wrought Iron |  | MARTINEZ
30 | 72-40220-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-02-18 | 1972-02-23 | Patch Welded |  | Steel/Wrought Iron |  | MTZ | CHECK SEWER LIQUID HOLE AT CENTER & ROLLING HILL WAY MARTINEZ & FOUND 100% TEE IN SOME. CHECKED HOUSE TOP VENTS AT 100 % & 100% ROLLING HILL WAY & FOUND NEGATIVE NOTIFIED CUSTOMERS OF SOME AT 650P.M. ALSO SERVICE DISK.
30 | 80-23308-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-03-03 | 1982-02-23 | Other |  | Other |  | MARTINEZ
30 | 80-23303-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-02-28 | 1982-01-13 | Other |  | Other |  | MARTINEZ
30 | 80-23349-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-04-22 | 1981-03-09 | Other |  | Other |  | MARTINEZ | BELL HOLE NEXT DOOR OVER MAIN (CREW REPAIR?) STREET OVELAY...
30 | 81-23478-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-03-11 | 1981-11-19 | Other |  | Other |  | MARTINEZ | CLEARED WHEN REPAIRED LEAK AT 555 VINE HILL WY
30 | 81-23478- |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-04-25 | 1981-11-19 | Other |  | Other |  | WALNUT CREEK | RECLASSIFY TO #2 GAS LEAK 45% GAS...3-11-81; MARKED WITH YELLOW PAINT.; CLEARED THIS LEAK WHEN REPAIRED LEAK AT 555 VINE HILL WY
30 | 76-21798-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-11-16 | 1976-12-10 | Patch Welded |  | Steel/Wrought Iron |  | MTZ | 70 PPM IN WATER BOX LEAKING 2" MAIN. REPAIRED
30 | 78-22572-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1978-11-10 | 1980-09-19 | Other |  | Other |  | MARTINEZ | 50 PPM IN SEWER MAN-HOLE
30 | 74-00376-1 |  |  | 3 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-04-26 | 1974-05-02 | Patch Welded |  | Steel/Wrought Iron |  | MARTINEZ | N/S OF CCC FLOOD CONTROL DIST. AT BIRCH TREE BETWEEN DRIVE & SIDEWALK. 30% GAS ON OPPOSITE SIDE OF STREET.
30 | 76-21806-1 |  |  | 4 | Other |  | Body of Pipe |  |  | Corrosion |  | 1976-11-24 | 1976-12-07 | Clamp | SKINNER | Steel/Wrought Iron |  | MTZ | .1% GAS IN WATER BOX; 0% GAS IN WATER BOX; INSTALLED (1) 12" SKINNER CLAMP AND (1) 6" SKINNER CLAMP TO REPAIR LEAK. 4" MAIN; MAIN AT POINT OF EXCAVATION IN GOOD CONDITION.
30 | 76-21805-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-11-24 | 1976-12-02 | Clamp | SKINNER | Steel/Wrought Iron |  | MTZ | .02% GAS OVER SERVICE; 10' BACK OF SIDEWALK SLIGHT ODOR; REPAIRED 2 LEAKS 4" MAIN INSTALLING (2) 4" SKINNER CLAMPS.; NO LEAKS; GAS MAIN ABOUT 3" ON TOP SEWER LINE.
30 | 81-23469- |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-03-05 | 1981-09-25 | Other |  | Other |  | MARTINEZ | RE-CLASSIFY TO #2 GAS LEAK 15% - 20% GAS... 3-5-81; 0% GAS... CREW REPAIRS? 9-24-81; MAIN SVC. TEE AREA. 2' RIGHT OF DRIVEWAY. BACK EDGE OF SIDEWALK.
30 | 80-23331-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-04-07 | 1982-03-03 | Other |  | Other |  | MARTINEZ | 0% GAS... 3-3-82
30 | 80-23319-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-03-18 | 1983-02-28 | Other |  | Other |  | MARTINEZ
30 | 81-23464-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-02-24 | 1981-10-16 | Other |  | Other |  | MARTINEZ | FOUND 20% ON 4% LEL READING
30 | 80-23292-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-02-25 | 1981-01-09 | Other |  | Other |  | PACHECO
30 | 79-22884-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-05-16 | 1982-04-14 | Other |  | Other |  | PLEASANT HILL | .05% GAS PVER SUC TO SCHOOL NEXT TO PG&E SHUT-OFF VALVE ___ VALVE COVER. I BELIEVE THIS AREA HAS ALREADY BEEN CONFORMED TO HAVE NATIVE GAS. A SPECIAL SURVEY IS DONE BY MYSELF IN ___ AND IS KEPT TRACK OF IN A SPECIAL SECTION IN SCHOOL SURVEY LOG BOOK.
30 | 79-22883-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-05-16 | 1982-04-14 | Other |  | Other |  | PLEASANT HILL | 50 PPM IN SEWER MANHOLE IN STREET. MARKED WITH YELLOW PAINT
30 | 79-22882-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-05-16 | 1982-04-14 | Other |  | Other |  | PLEASANT HILL | 70 PPM IN SEWER MAN HOLE IN STREET. MARKED WITH YELLOW PAINT
30 |  |  |  | 6 | Transmission |  | Other |  |  | Other |  |  | 1980-01-18 | Other |  | Steel/Wrought Iron |  | PACHECO | VIEW SERVICE INSTALLATION
30 | 74- |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1974-11-22 | 1974-11-22 | Other | REWRAP | Steel/Wrought Iron |  | PAC. | REWRAP DUE TO INST. OF TREE DRAINS.
30 | 79-22900-1 |  |  | 6 | Distribution Feeder Main |  | Fitting |  |  | Material Failure | LEAK ON CAP 2" L.S.F. |  | 1979-08-27 | Other | TIGHTENED CAP | Steel/Wrought Iron |  | PACHECO | 10% GAS (FLAME-OUT) OVER 6" TP MAIN 45' FROM BRIDGE CROS. TO ASPIN DR MARKED WITH; FOUND CAP ON 2" L.S.F. LEAKING USED TEFLON TAPE AND TIGHTENED CAP.
30 | 74-41418-1 |  |  | 2 | Distribution Feeder Main |  | Valves |  |  | Corrosion |  | 1974-07-30 | 1974-07-31 | Other |  | Steel/Wrought Iron |  | PACHECO | .1% GAS OVER MAIN; TIGHTEN PACKING COVER BOLTS ON 2" BLOCK VALVE INSTALLED BY G.C. FOR TEMP USE.
30 | 73-00000- |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1973-06-13 |  |  |  | Steel/Wrought Iron |  |  | RAISED V.F.&C. GREASED VALVE DID NOT DAYLIGHT MAIN
30 | 74- |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1974-06-27 | 1974-06-27 | Other |  | Steel/Wrought Iron |  | PACHECO | REMAP DUE TO INST OF STORM DRAIN; VALLEY ENGINEERS
30 | 00- |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1976-04-07 |  |  |  | Steel/Wrought Iron |  | PACHECO | PROSPECT DEPTH 6" T.P.
30 | 79-22880-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-05-16 | 1982-04-14 | Other |  | Other |  | PLEASANT HILL | .02% GAS IN OLD TEST HOLE NEXT TO PG&E VALVE. 70PPM IN PT&T MANHOLE COVER NEARBY. MEASURED BOTH ___IONS WITH YELLOW PAINT
30 | 74-41688-1 |  |  | 2 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 1974-10-17 | 1974-11-11 | Other |  | Steel/Wrought Iron |  | MTZ | 101% GAS TIE IN 2" TO 10" G.M.; FOUND CAP ON 2" PIN OFF TEE LEAKING - REPAIRED SAME.
30 | 77- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1977-12-07 | 1977-12-07 | Other | REWRAP; | Steel/Wrought Iron |  | MTZ
30 | 77- |  |  | 10 | Transmission |  | Other |  |  | Damage by outside Forces |  | 1977-07-18 | 1977-07-18 | Other | REWRAP | Steel/Wrought Iron |  | MARTINEZ | REWRAP DUE TO INST OF PIT DUCTS R.H. SHEETS CONST
30 | 80-23377-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-06-09 | 1980-12-18 | Other |  | Other |  | MARTINEZ | 0% GAS WITH FLAME PACK AT OLD LEAK MARK ALSO IN WATER BOX 0%. NO ODOR IN AREA... BUSH OF POISON OAK CLEARED AWAY NEXT TO LEAK MARK... CAN'T SEE ANY TRACE OF HP R&G SGT...
30 | 77-43069-1 |  |  | 2 | Transmission | VALVE | Valves |  |  | Other | NEEDS GREASE | 1977-01-04 | 1977-01-07 | Other | GREASED VALVE | Steel/Wrought Iron |  | MARTINEZ | NO. 2 LEAK; GREASED VALVE AND RECHECKED ALL CONDITIONS O.K.
330 | 75-42042-1 |  |  | 10 | Transmission |  | Fitting |  |  | Other |  | 1975-03-28 | 1975-03-28 | Other | INSTALLED V.F.C. | Steel/Wrought Iron |  |  | UNCOVERED VALVE INSTALLED V.F.C. VALVE TEE LEAKING AT CAP. REPAIRED LEAKAGE
30 | 79-44668-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Construction Defect |  | 1979-06-11 | 1979-07-19 | Other |  | Steel/Wrought Iron |  | MARTINEZ | INSTALLED 1" SAVA VALVE ON 10" T.P. MAIN ON ALHAMBRA VALLEY RD. 104' N/C GILBERT CT. TO BY PASS AROUND VALVE E 10 IN ORDER TO REPAIR LEAK AT INLET THREADS.
30 | 77- |  |  | 10 | Transmission | [6 empty] | 1977-07-25 | 1977-07-25 | Other | REWRAP | Steel/Wrought Iron |  | MARTINEZ | REWRAP DUE TO INST OF PIT DUCTS SHEETS CONST; NONE
30 | 75- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1975-12-16 | 1975-12-16 | Other | REWRAP | Steel/Wrought Iron |  | MARTINEZ | REWRAP DUE TO INST OF SEWER LOTERAL MEWELL DOWN CONST.
30 | 74- |  |  | 0.75 | Transmission |  | Other |  |  | Other |  |  | 1974-04-12 | Other |  | Steel/Wrought Iron |  | MTZ | UNCOVERED VALVE - RAISED V.F.C.
30 | 73-00000-0 |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RAISED UNION BOX AND SET FR ____ IN CONCRETE
30 | 72-00000-1 |  |  | 4 | Transmission |  | Other |  |  | Other |  | 1972-10-17 | 1972-10-17 | Other | REWRAP | Steel/Wrought Iron |  | MARTINEZ | REWRAP DUE TO INST OF SEWER LINE
30 | 81-23640-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-10-09 | 1983-10-05 | Other |  | Other |  | MARTINEZ
30 | 73-40865-1 |  |  | 0.5 | Single Service |  | Body of Pipe |  |  | Other |  | 1973-10-08 | 1973-10-09 | Replace Pipe and/or Service |  | Other |  | MARTINEZ | ELECTR. DEPT. WORKING ON ELECTR. BURN OUT, NOTICED STRONG GAS ODER, BUT TESTED MAIN & SERVICE, ALSO METER BOX AND SEWER FOUND 100% G IN BELLYHOLE AND 10% ' G IN WATERBOX CALLED FIELD FORMAN FOR CREW TO MAKE REPAIRS.; FOUND LEAK IN 1/2" PL SERV. PIPE REPAIRED SAME LEAK CAUSED BY BURN OUT OF ELECT N.G. LINES.
30 | 74- |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1974-06-25 | 1974-06-25 | Other |  | Steel/Wrought Iron |  | PACHECO | REWRAP 6" T.P. DUE TO INST. OF WATER MAIN
30 | 79- |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1979-07-16 | 1979-07-16 | Other | REWRAP | Steel/Wrought Iron |  | PACHECO | REWRAP DUE TO INSTALLATION OF FIRE HYDRANT BY C.CC.WD.
30 | 74- |  |  | 6 | Transmission |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1974-03-08 | 1974-03-08 | Other |  | Steel/Wrought Iron |  | PACHECO | RECHECK OF VENT AFTR 4" FLANGE WAS REPLACED BECAUSE OF MATERIAL FAILURE. ALL TESTS NOW NEGATIVE.
30 | 74- |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1974-06-04 | 1974-06-04 | Other | REWRAP | Steel/Wrought Iron |  | PAC. | REWRAP DUE TO INST. OF FIRE HYDRANT. C.C.C.W.D.
30 | 74- |  |  | 10 | Transmission | [6 empty] | 1974-11-06 |  |  |  | Steel/Wrought Iron |  | V | INST. 3/4" GAUGE TAP DRILLED 1/4" TESTED 920 PSIG 1 HRS.
30 | 82-23687-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-05 | 1982-12-31 | Other |  | Other |  | MTZ | THERE IS A PATCH OVER SVC. TEE AREA AND NO READINGS SO I ASSUME IT HAS BEEN FIXED.
30 | 77- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1977-09-30 | 1977-09-30 | Other | REWRAP | Steel/Wrought Iron |  | MARTINEZ | REWRAP DUE TO INST OF PTT DUCTS; REWRAPPED 3 TIMES, (3 COATS)
30 | 77- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1977-10-06 | 1977-10-06 | Other | REWRAP | Steel/Wrought Iron |  | MARTINEZ | REWRAP OF 10" T.P. DUE TO INSTALLATION OF PT.T MANHOLD
30 | 77- |  |  | 10 | Transmission |  | Other |  |  | Other | REWRAP | 1977-06-20 | 1977-06-20 | Other | REWRAP | Steel/Wrought Iron |  | MARTINEZ | REWRAP 2' OF 10" GAS MAIN TRANSMISSION EXPOSED BY SHEETS CONST.
| 09-93828-1 |  |  | 0.75 | Single Service |  | Fitting |  |  | Weld Failure |  | 2009-11-16 | 2009-11-16 | Other |  | Steel/Wrought Iron |  | MARTINEZ | REBUILT REG SET; EXCAVATED HIGH TO HIGH SET CONCRETE BOX EXPOSED SET REPAIRED SET
30 | 77- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1977-06-24 | 1977-06-24 | Other | REWRAP | Steel/Wrought Iron |  | MARTINEZ | REWRAP DUE TO INSTALLATION OF P.T.T. FACILITIES
30 | 79- |  |  | 10 | Transmission |  | Other |  |  | Damage by outside Forces |  | 1979-02-09 | 1979-02-09 | Other |  | Steel/Wrought Iron |  | MTZ | REWRAP T.P. MAIN WEST VALLEY CONST.; REWRAP DUE TO INST. OF PTT DUCTS TO POLE.
30 | 77- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1977-06-29 | 1977-06-29 | Other | REWRAP | Steel/Wrought Iron |  | MARTINEZ | REWRAP 2' OF 10" T.P. G.M. EXPOSED BY SHEETS CONST.
30 | 73-00000-0 |  |  | 10 | Transmission | [10 empty] | Steel/Wrought Iron
30 |  |  |  | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | MARTINEZ | EXPOSED 10" TP LINE 101 TO C/O 3/4 STL. SVC.
30 | 72-00000-0 |  |  | 10 | Transmission | [10 empty] | Steel/Wrought Iron
30 | 72-00000-1 |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1972-08-21 |  | Other |  | Steel/Wrought Iron |  | MARTINEZ | INSTALLED SERVICE OFF 10" MAIN
30 | 77- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1977-06-21 | 1977-06-21 |  | REWRAP | Steel/Wrought Iron |  | MARTINEZ | REWRAP DUE TO INSTALLATION OF PTT FACILITIES
30 | 82-23757-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-02-16 | 1983-01-19 | Other |  | Other |  | PH
30 | 82-23759-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-02-17 | 1982-09-08 | Other |  | Other |  | MARTINEZ | CHECKED FOR LEAKAGE AT BASE OF RISE & OVER MAIN IN STREET... NEGATIVE READINGS... FOUND LEAK ON SIDE PLUG TO NO 1 A MTR CALLED SVC DPT FOR MTR CHANGE... ALL OTHER TESTS AT THIS LOCATION PROVED NEGATIVE...
30 | 76-42650-1 |  |  | 4 | Other | VALVE C69 | Valves |  |  | Other | NEED GREASE | 1976-01-13 | 1976-02-11 | Other |  | Steel/Wrought Iron |  | P.H. | NO. 2 LEAK; VALVE C 69 GREASED AND RECHECKED, ALL TESTS NEGATIVE
30 | 79-23038-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-11-02 | 1981-11-30 | Other |  | Other |  | PLEASANT HILL | .03% OVER MAIN IN STREET. S/TEE AREA IN PATCH. MARKED IN YELLOW PAINT; (NEXT DOOR TO 541 KIKI DR); ANNUAL LEAK SURVEY
30 | 77-21882-1 |  |  | 2 | Other |  | Body of Pipe |  |  | Corrosion |  | 1977-02-11 | 1977-03-04 | Clamp | SKINNER | Steel/Wrought Iron |  | P.HILL | .5% GAS AT PT&T U.G. SPLICE BOX 50' INTO TEME CT MARKED W/ YELLOW PAINT, OVER MAIN; 0% GAS AT BELLHOLE ON BARTUST; INSTALLED (1) 2" SKINNER LEAK CLAMPS TO REPAIR LEAK
30 | 77-21928-1 |  |  |  | Distribution Main |  | Fitting |  |  | Other |  | 1977-02-28 | 1976-03-29 | Other |  | Steel/Wrought Iron |  | P.HILL | .02% GAS AT RISER SLIGHT ODOR IN AIR; LEAKING 3/4" PLUG IN HOUSE LINE TEE - WAS REDOPED. BART TESTED SERV. NO READ - OK; NO. 2 LEAK
30 | 77-21884-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1977-02-11 | 1980-09-15 | Other |  | Other |  | P.HILL | .33% GAS IN WATER BOX, W/BOX IS OVER SERVICE; LEAK RE-CHECK: 4-25-78 .1% GAS IN WATER BOX OVER SOC.
30 | 72-20172-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1971-12-02 | 1972-01-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PH | RERUN 3/4" SERV.
30 | 81-23648-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-10-30 | 1981-11-19 | Other |  | Other |  | MARTINEZ
30 | 82-46946-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-10-22 | 1983-10-05 | Other |  | Other |  | MARTINEZ | .03%... NOTE: CUSTOMER ___ HIT BY TRUCK 10-21-82... 0% ON MTR OR ___ IN YARD. ____ IS AT NEW BELL HOLE IN SIDEWALK...
30 | 81-23652-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-11-03 | 1983-03-25 | Other |  | Other |  | MARTINEZ
30 | 81-23675-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-12-14 | 1982-12-31 | Other |  | Other |  | MTZ
30 | 74-41527-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1974-09-05 | 1974-09-09 | Other |  | Other |  | MTZ | SOAPPED OUT METER SET & FOUND NYLON BURNING LEAKING. INSTALLED NEW ___ & STOPPED LEAK.
30 | 77-21857-1 |  |  |  | Distribution Main |  | Other |  |  | Other |  | 1977-01-28 |  | Other |  | Steel/Wrought Iron |  | MTZ | .02% GAS IN STORM DRAIN CATCH BASIN; BAR TESTED OVER MAIN & SERVICES; NO. 2 LEAK; UNABLE TO FIND ANY INDICATION OF LEAKAGE DID NOT UNCOVER GAS MAIN
30 | 78-22407-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1978-09-05 | 1981-08-12 | Other |  | Other |  | MARTINEZ | 1% GAS IN OLD BELL HOLE OVER MAIN. RIGHT EDGE OF DRIVEWAY, SUC. TEE ARIA TO 6841 ACROSS STREET. MARKED WITH YELLOW PAINT
30 | 81-23678-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-12-22 | 1983-10-05 | Other |  | Other |  | MARTINEZ | DOWN GRADE TO #3 LEAK... 30 PPM AT BASE OF RISER (INSERT)...10-13-82; OVER SVC 2' FROM RISER; 20% GAS OVER SVC 10' FROM RISER 6' FROM GARAGE DEADE IVE... 5/11/82; ODOR... REFER CREW
30 | 82-23770-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-03-16 | 1982-08-06 | Other |  | Other |  | MARTINEZ
30 | 82-24124-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-08-03 | 1982-08-19 | Other |  | Other |  | MARTINEZ
30 | 75-42240-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-07-31 | 1975-08-11 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | MTZ. | RERAN SERVICES TO 131, 133 AND 135, WAVERLY CT SERVICES ON END OF MAIN.
30 | 82-23808-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-03-16 | 1983-10-05 | Other |  | Other |  | PH | OVER MAIN SVC T AREA
30 | 77-21943-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1977-03-03 | 1980-04-01 | Other |  | Other |  | P.HILL | 100 PPM IN PT&T SPLICE BOX, OVER SERVICE; 0% PPM IN PT&T SPLICE BOX OVER SERVICE; LEAK RE-CHECK: 4-24-78; .02% GAS IN PT&T BOX OVER SVC.
30 | 82-23806-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-03-15 | 1983-08-22 | Other |  | Other |  | PH | DOWN - GRADE TO # 3 LEAK; .02% GAS... 8-16-82
30 | 82-23812-1 |  |  | 0 | Other |  | Other |  |  | Corrosion |  | 1982-03-16 | 1983-09-22 | Other |  | Other |  | PH | OVER MAIN NEAR BASE OF SIGN
30 | 82-23813-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-03-16 | 1983-10-05 | Other |  | Other |  | PH | OVER SVC 5' RIGHT OF DRIVEWAY
30 | 77-21940-1 |  |  | 0.75 | Service |  | Other Welds |  |  | Construction Defect |  | 1977-03-03 | 1977-03-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | P.HILL | .03% GAS OVER SERVICE 7' FROM RISER, SLIGHT ODOR IN AIR; RERAN #2 SERVICES ONE A BRANCH. LEAK ON WELD ON SERV. TEE TO BRANCH SERV.; NO. 2 LEAK
30 | 82-46925-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-10-21 | 1983-06-27 | Other |  | Other |  | PLEASANT HILL | LEAK WAS CLEARED; UPGRADED FROM 82-23804
30 | 76-21428-1 |  |  | 2 | Other |  | Body of Pipe |  |  | Corrosion |  | 1976-01-30 | 1976-03-18 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | P HILL | .2% GAS OVER MAIN 4' RIGHT OF LARGE TREE IN FRONT YARD REPAIRED 2" LEAKING MAIN. INST. 12" X 3" CAN
30 | 75-42488-1 |  |  | 2 | Other |  | Body of Pipe |  |  | Corrosion |  | 1975-11-25 | 1975-12-12 | Clamp |  | Steel/Wrought Iron |  | P.HILL | 10% GAS 1' LEFT OF DRIVEWAY OVER SVC TEE DEAD SPOT IN GRASS, ODOR IN AIR; NO. 2 LEAK; INST. 2" X 8' SKINNER CLAMP
30 | 82-46602-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-02-12 | 1983-05-27 | Other |  | Other |  | P.H. | DOWN - GRADE TO #3 LEAK 3% - 7% GAS... 6-28-87; 0%... CREW REPAIRS? SVC R/R TO 267... 5-27-83
30 | 80-23431-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-11-07 | 1981-11-30 | Other |  | Other |  | PLEASANT HILL
30 | 82-24137-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-10-29 | 1983-09-22 | Other |  | Other |  | PH | OVER MAIN SVC & AREA TO ___ ACROSS ST
30 | 72-20432-1 |  |  | 1.25 | Distribution Feeder Main |  | Valves |  |  | Other |  |  | 1972-11-20 | Other |  | Steel/Wrought Iron |  |  | GREASED 5 VALVES IN DIST. REG. STA, ELIMINATING LEAKAGE.
|  |  |  | 6 | Transmission | [12 empty] | P.H. | CLEANED CONTACT & INSTALLED ETS STATION
30 | 74- |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1974-10-11 | 1974-10-11 | Other | REWRAP | Steel/Wrought Iron |  | P.H. | REWRAP OF 6" T.P. MAIN DUE TO INST. OF 36" WATER MAIN BY C.C.C.W.D.
30 | 74- |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1974-10-11 | 1974-10-11 | Other |  | Steel/Wrought Iron |  | P.H. | REWRAP DUE TO INST WATER MAIN.
30 | 81-23488-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-03-19 | 1982-02-12 | Other |  | Other |  | PLEASANT HILL | PLEASANT HILL
30 | 82-23851-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-03-24 | 1983-02-28 | Other |  | Other |  | PH
30 | 82-23852-1 |  |  | 0 | Other |  | Other |  |  | Other |  |  | 1982-09-01 | Other |  | Other |  |  | 0% GAS... THE ONLY REGISTRATION I COULD GET WITH FLAME PACK WAS A LEAK ON 1" PLUG TO BY-PASS STOP COCK...MADE OUT C-TAG...
3 |  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | PH | USE CATHODIC & REG FISK WIRES
30 | 73-00000-1 |  |  | 6 | Transmission |  | Other |  |  | Other | REWRAP | 1973-01-22 | 1973-01-22 | Other | REWRAP | Steel/Wrought Iron |  | PH | REWRAP DUE TO INST OF WATER MAIN CCCWD
30 | 73-00000-1 |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1973-01-23 | 1973-01-23 | Other | REWRAP | Steel/Wrought Iron |  | P.H. | REWRAP DUE TO INST OF 20" STEEL WATER MAIN. ALSO INSULATED GAS MAIN FROM WATER LINE BY USING MERCORDA FOR INSULATION. CCCWD
30 | 80-45013-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-04-14 | 1980-09-16 | Other |  | Other |  | LAF. | .301 SERVICE SEE C-TAG
30 | 82-24121-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-08-02 | 1983-08-23 | Other |  | Other |  | MARTINEZ
30 | 82-23768-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-03-16 | 1983-02-28 | Other |  | Other |  | MTZ
30 | 82-23775-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-03-17 | 1983-02-28 | Other |  | Other |  | MTZ
30 | 81-23681-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-12-28 | 1982-12-01 | Other |  | Other |  | MARTINEZ | IN OLD BELL HOLE OVER MAIN; CLEARED ___ LEAK WAS REPAIRED
30 | 82-23772- |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-03-16 | 1983-02-28 | Other |  | Other |  | MTZ
30 | 82-23769-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-03-16 | 1982-08-06 | Other |  | Other |  | MARTINEZ
30 | 72-20388-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-07-21 | 1972-12-12 | Patch Welded |  | Steel/Wrought Iron |  | MTZ
30 | 77-21990-1 |  |  | 2 | Distribution Main | [6 empty] | 1977-03-18 | 1977-04-18 | Other |  | Other Plastic |  | P.HILL | LEAK REPAIRED ON 77-2199; .03% GAS IN E.U.G. SPLICE BOX IN SIDEWALK AT SERVICE TEE AREA
| 05-23068-1 |  |  | 2 |  |  | Plastic Tee Cap |  |  | Material Failure |  | 2005-04-22 | 2006-10-09 | Other | REPAIR KIT | Aldyl A (Tan or Gray) |  | MARTINEZ | BLACK CAP TEE REPAIR - INSTALLED ETS IN G-5 BOX SAME LOCATION; REPAIR ON BLACK CAP TEE
30 | 82-46857-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-08-23 | 1983-08-23 | Other |  | Other |  | PLEASANT HILL
30 | 82-23831-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-03-24 | 1982-08-13 | Other |  | Other |  | P.H.
30 | 82-23837-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-03-26 | 1983-09-21 | Other |  | Other |  | PLEASANT HILL
30 | 76-42635-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1976-01-24 | 1976-02-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | P. HILL | 10% GAS AT RISER. RERUN SERVICE; RERAN SERV. 2-4-76 CH GODDARD
30 | 76-42635-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1976-02-03 | 1976-02-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PH | STRONG ODOR; INSERTED 1/3" PL PIPE IN 3/4' STL CASING 2-4-76 CH GODDARD; BAR TESTED SERVICE TO MAIN, FOUND 40% GAS ON RISER, ODOR STRONG, WINDOW OVER RISER PE... TO SEEP INTO HOUSE, RERAN SERVICE, PL INSERT, 2-4-76
30 | 82-23873-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-08 | 1983-09-20 | Other |  | Other |  | PLEASANT HILL
30 | 82-23871-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-07 | 1983-04-04 | Other |  | Other |  | PLEASANT HILL
30 | 82-23841-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-03-26 | 1983-09-20 | Other |  | Other |  | PLEASANT HILL
30 | 82-23867-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-06 | 1983-04-04 | Other |  | Other |  | PLEASANT HILL
30 | 82-23865-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-06 | 1983-04-04 | Other |  | Other |  | PLEASANT HILL
30 | 82-23863-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-06 | 1983-09-20 | Other |  | Other |  | PLEASANT HILL | 0%... CREW REPAIRS... SVC. R/R AT 1901 NEAR-BY... 9-20-93 R. O'CONNOR
30 | 73-40773-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-07-27 | 1973-07-31 | Clamp |  | Steel/Wrought Iron |  | P. HILL | REPAIR ON 7-30-73 OR 7-31-83; INST. 2" SKINNER CLAMP. BACK FILLED HOLE. 7-31-73 CH GODDARD; FOUND NO SIGN OF GAS IN AREA; BAR TESTED AND FOUND GAS WHERE WATER SERV CROSSES PUT ON LEAK CLAMP REPAIRS 7-27-73
30 | 82-23842-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-03-26 | 1983-08-26 | Other |  | Other |  | P.H. | DOWNGRADE 10 # 3 LEAK .08%... 8-25-82 R O'CONNOR
30 | 81-23550-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-05-27 | 1981-12-17 | Other |  | Other |  | P.H. | INSOLATED SVC
30 | 78-43799-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1978-05-09 | 1978-05-17 | Patch Welded |  | Steel/Wrought Iron |  | PLEASANT HILL | 10% GAS OVER MAIN 6' BACK OF CURB. CENTER OF DRIVEWAY SVC TEE ARIA TO 53 ACROSS STREET. CUSTOMER SMELLED GAS WHEN SHE ROTO. FILLED ALONG EDGE OF DRIVEWAY. MARKED WITH YELLOW PAINT. FOUND LEAKING 1/2" COPPER SERV AND 2" LEAKING MAIN. COPPER LEAKING SURVEY. NO. 2 LEAK. LEAK RE-CHECK SEE ATTACHED A-FORM
30 | 82-24029-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-05-12 | 1983-05-10 | Other |  | Other |  | PH
30 | 74- |  |  | 2 | Other | 2" FROM 10" TP TO REGULATOR | Other |  |  | Other |  | 1974-09-19 | 1974-09-19 | Other | REWRAP | Steel/Wrought Iron |  | P.H | REWRAP OF 2" FEEDER FROM 6" T.P. TO REGULATOR ON C/O VIVIAN & CONTRA COSTA BLVD. DUE TO INSTALLATION OF 36" WATER MAIN BY J&M CONSTRUCTION.
30 | 74- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1974-09-19 | 1974-09-19 | Other | REWRAP | Steel/Wrought Iron |  | P.H. | REWRAP OF 10" T.P. MAIN DUE TO INSTALLATION OF 36" WATER MAIN BY J&M CONSTRUCTION.
30 | 74- |  |  | 2 | Transmission | [7 empty] | 1974-12-16 | Other |  | Steel/Wrought Iron |  | P.H. | REPLACED BROKEN E.T.S. BOX 12-16-74 H. SHIELDS
30 | 72-20433-1 |  |  | 1.25 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1972-11-17 | 1972-11-20 | Other |  | Steel/Wrought Iron |  | P. HILL | GREASED 5 VALVES IN DIST REG. STATION ELIMINATING LEAKAGE
30 |  |  |  | 6 | Transmission | [7 empty] | 1974-09-20 |  |  | Steel/Wrought Iron |  | P.H. | INSTALLED E.T.S. AND 1-15 LB. ZINC ANODE, AND 1-1 LB. ZINC REFERENCE ANODE; INST. ON GM436777
30 | 82-24031-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-05-13 | 1983-05-12 | Other |  | Other |  | PH | 12%... LONG SIDE SVC TEE AREA TO 167 ACROSS STREET... 5-7-83 R.O'CONNOR
30 | 74- |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1974-09-26 | 1974-09-26 | Other |  | Steel/Wrought Iron |  | P.H. | REWRAP DUE TO INST. OF WATER MAIN J.M. CONST.
30 | 82-00650-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-03-05 | 1983-02-23 | Other |  | Other |  | PH
30 |  |  |  | 2 | Transmission | [10 empty] | Steel/Wrought Iron |  | P.H. | INSTALLED E.T.S. AND 1-15 LB ZINC ANODE, AND 1-1 LB ZINC REFERENCE ANODE; INST. ON GM482777
|  |  |  | 6 | Transmission | [7 empty] | 1974-09-24 |  |  | Steel/Wrought Iron |  | P.H. | INSTALLED E.T.S. AND 1-1LB ZINC ANODE.
30 | 74 |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | P.H | INSTALLED E.T.S. & 1-1LB ZINC ANODE; INST. ON GM482777
30 | 79-44452-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-04-04 | 1980-04-01 | Other |  | Other |  | P.H. | ON ROUTINE LEAK SURVEY I SMELLED SOME GAS ODOR IN THE AREA, CSEDLED MANHOLES AND WODEBOXES AND FORT 5% LEL IN WATERBOX, SEWER IS CLEAR. CHECKED W/BOX, PT&T BOX, 2MM CURB BOX, ELECT. BOX, SERVICE & MAIN W/FLAME PACK W/NEGATIVE RESULTS 4-1-80 GDU
30 |  |  |  | 6 | Transmission | [7 empty] | 1974-09-23 |  |  | Steel/Wrought Iron |  | P.H. | INSTALLED E.T.S. AND 1-1LB. ZINC REFERENCE ANODE.; INST. ON GM482777
30 | 74- |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1974-09-12 | 1974-09-12 | Other |  | Steel/Wrought Iron |  | P.H. | REWRAP DUE TO INST. OF 36" WATER MAIN J.M. CONST.; REWRAP
[5 empty] | Distribution Feeder Main | [10 empty] | Plastic |  |  | EXPOSED 2' OF 1 1/4' HP PH MAIN STUB. INSTALLED 37' 1/2" PL SERV. PIPE INSTALLED 3/4" STEEL RISER W/COCK.
30 | 81-46408-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-08-25 | 1983-06-30 | Other |  | Other |  | PLEASANT HILL | ILLEGIBLE DUE TO FADING
30 | 75-21067-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1975-01-31 | 1981-10-16 | Other |  | Other |  | P. HILL | .07% GAS 35' RIGHT SIDE OF MAILBOX, OVER MAIN. LEAK RE-CHECK 8-17-77 R.O'CONNOR .04% 35' RIGHT SIDE OF MAIL BOX OVER MAIN 09-08-78 FOUND 0.5% GAS AT 55' RIGHT OF MAIL BOX
30 | 77-20811-1 |  |  | 0.5 | Service |  | Fitting |  |  | Construction Defect |  | 1977-01-10 | 1977-05-11 | Replace Pipe and/or Service |  | Copper |  | LAF. | LEAK AT SERV TEE & INSER; REPLACED RISER & 3 FT OF PL & REPAIRED 2 FT OF COPPER W/PL AT SERV TEE.
30 | 82-23962-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-28 | 1983-03-24 | Other |  | Other |  | PH
30 | 82-23966-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-29 | 1983-04-04 |  |  | Other |  | PH | SVC T AREA 2' B/O CURB 2' L/O DRWAY
30 | 82-23959-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-27 | 1983-03-28 | Other |  | Other |  | P.H.
30 | 82-23960-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-28 | 1983-03-24 | Other |  | Other |  | PH
30 | 82-23957-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-27 | 1983-03-28 | Other |  | Other |  | PH
30 | 82-23965-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-29 | 1983-04-04 | Other |  | Other |  | PH
30 | 82-23963-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-28 | 1982-09-10 | Other | ; | Other |  | P.H. | 0%... CREW REPAIRS? NOTE... FRESH PATCH IN DRIVE-WAY NEAR WATER BOX... 9-10-82 R. O'CONNOR
30 | 75-21197-1 |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1975-07-17 | 1976-03-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | P. HILL | 1% GAS 13' BEHIND SIDEWALK OVER SERVICE NEAR WHITE ROCKS. RERAN #2 SERVICES TO 341 AND BRANCH SERV TO 335 INST. 1/2" PL INSERT 3-23-76 CH GODDARD
30 | 82-24004-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-29 | 1983-04-04 | Other |  | Other |  | P.H.
30 | 82-23975-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-27 | 1983-04-04 | Other |  | Other |  | PH
30 | 82-23979-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-28 | 1983-05-27 | Other |  | Other |  | PH | 0%... CREW REPAIRS? 5-27-83 R. O'CONNOR (DUPLICATE)
30 | 82-23974-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-27 | 1982-09-14 | Other |  | Other |  | W.C. | 0%... I COULD NOT GET ANY REGISTRATION WITH FLAME PACK... 9-14-82 R. O'CONNOR NOTE: 100% GAS AT 119 NEXT DOOR...
30 | 77-43346-1 |  |  | 4 | Distribution Main | [6 empty] | 1977-10-25 |  |  |  | Steel/Wrought Iron |  | P.H. | WHILE LOCATING GAS MAIN FOUND STRONG ODOR OFF THAT CORNER. COULD NOT GET ANY READS.
30 | 79-22902-1 |  |  | 0 | Other |  | Other |  |  |  |  | 1979-06-15 | 1981-11-30 | Other |  | Other |  | PLEASANT HILL | 10% GAS (FLAME-OUT) IN OLD BELL HOLE OVER MAIN IN STREET MARKED WITH YELLOW PAINT. THIS LEAK SHOULD BE DOWNGRADED 11-7-79 ANORMAL LEAK SURVEY. NO. 2 LEAK. RE-CHECK 11-9-79 FOUND LEAK NEXT DOOR SUC TEE AREA MADE OUT ADDITIONAL A-FORM R O'CONNOR
30 | 80-45037-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-06-04 | 1983-01-19 | Other |  | Other |  | PLEASANT HILL | DOWNGRADED TO #3
30 | 78-43704-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1977-05-10 | 1978-02-20 | Patch Welded |  | Steel/Wrought Iron |  | P. HILL | 6" + 3" PATCH; UPGRADED LEAK TO M-2; .03% GAS, 5 BACK OF CURB, 12' RIGHT OF YARD LIGHT OVER MAIN; MADE TEMP. REPAIRS BY INSTALLING LEAK CLAMP 3/17/78; REPAIRED LEAK BY INSTALLING 6" X 3" PATCH OVER LEAK 3/20/1978; NO 2; REPAIRED 3-20-78; BAD FIELD MAP WHERE LEAK WAS. A PATCH HAD BEEN WELDED NEAR LEAK
| 76- |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-05-04 | 1976-05-05 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | PLEASANT HILL | TWILL ENCIRCLEMENT WITH SLEEVE; WHILE DIGGING FOR A NEW WATER LINE BURNS CONSTRUCTION CROSSING OVER 8" TP MAIN PUT IN 15% DENT IN MAIN REPAIRED WITH 8" HALF SCLE 2PCS. (FULL ENCIRCLEMENT), REWRAPPED AND BACK FILLED WITH 5 TONS OF SAND. (NOTE THE MAIN WAS NOT LEAKING AFTER IT HAD BEEN DAMAGE); NO PUNCTURE
30 | 83-47223-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-07-08 | 1983-07-28 | Other |  | Other |  | PLEASANT HILL | FOLLOW-UP AFTER GAS BREAK... ; .45% GAS
30 | 73-00000-0 |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1973-09-20 | 1973-09-20 | Other |  | Steel/Wrought Iron |  | P.H. | REWRAP DUE TO INSTA OF WATER MAIN PETER COLE JENSEN
30 | 80-23404-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-05-13 | 1981-09-25 | Other |  | Other |  | PLEASANT HILL | READS ARE ORGANIC; CLEARED - NO READINGS; CURB MTR BOX OLD LEAK MARK
30 | 74- |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1974-10-09 | 1974-10-09 | Other |  | Steel/Wrought Iron |  | P.H. | WRAPPED 8" TP
30 | 74-41132-1 |  |  | 6 | Distribution Main |  | Valves |  |  | Other |  | 1974-03-05 | 1974-03-08 | Other |  | Steel/Wrought Iron |  | P.H | FOUND READINGS OF 15% LEL IN VALVE FRAME & 10% GAS IN PATCH S/O VALVE FRAME. RAISED VALVE FRAME & CORNER. 3-7-74 INST 4" CEMENT AROUND FRAME; CAUTION PTT HONEY CARVE DUCT 1' BELOW AN 2' ON NORTH SIDE OF 6" MAIN AND VALVE # C-65 VALVE NO #; FOUND LEAK IN 6" FLANGE ON INSULATED SIDE OF VALVE. (6") MECH - WAS ABLE TO TIGHTEN BOLTS AND STOP LEAK. SOAPTESTED EVERYTHING OUT. GREASED VALVE REPLACED GREASE PLUG.
30 | 76-42732-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1976-04-27 | 1976-05-05 | Other |  | Steel/Wrought Iron |  | P.H | RAISED VALVE FRAME AT INTERSECTION OF N.MAIN & BOYD RD. PH VALVE CORNER PAINTED YELLOW
30 | 72-20431-1 |  |  | 0.75 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1972-11-17 | 1972-11-20 | Other |  | Steel/Wrought Iron |  | P. HILL | GREASED 3/4 INLET VALVE ELIMINATING LEAKAGE
| 01-43293 |  |  | 1.25 | Service |  | Tap Connection |  |  | Digin |  | 2001-10-23 | 2001-10-23 | Other | C/O 1 1/4" GM | Steel/Wrought Iron |  | PLEASANT HILL | C/O 1 1/4" GM @ 6" T.P. MAIN; C/O GAS MAIN ONLY NO STUB SERVICE ATTACHED TO HI TO HI SET. C/O IN 1982; C/O 1 1/4" @ 6" TP MAIN
30 | 77-22194-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1977-07-21 | 1981-10-16 | Other |  | Other |  | P. HILL | .04% GAS IN METER BOX IN FRONT OF "RED CARPET" FOWLERS WOODCRAFT; RESEKED 09-11-78 FOUND 0.4% G IN CURB METER
30 | 76-42631-1 |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1976-01-29 | 1976-01-29 | Other |  | Steel/Wrought Iron |  | P.H. | BAR TESTED MAIN VALVES WATER BOXES SEWER, ALL TESTED N
30 | 72-20424-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1972-11-14 | 1972-11-15 | Other |  | Steel/Wrought Iron |  | PH | GREASED 6" VALVE
30 | 82-24093-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-06-17 | 1983-05-27 | Other |  | Other |  | PLEASANT HILL | 0% SELL REPAIRS? 5-27-83 (DUPLICATE)
30 | 80-23411-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-10-07 | 1983-09-20 | Other |  | Other |  | PLEASANT HILL | .02% GAS IN PT&T BOX
30 | 82-23745-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-29 | 1982-12-31 | Other |  | Other |  | P H
30 | 82-23743-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-29 | 1982-06-09 | Other |  | Other |  | PLEASANT HILL | O% GAS ... CREW REPAIRS? 6-9-82 R. O'CONNOR
30 | 82-23744-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-29 | 1983-01-06 | Other |  | Other |  | P H
30 | 81-23485-1 |  |  | 0 | Distribution Main |  | Other |  |  | Other |  | 1981-03-19 | 1982-02-12 | Other |  | Other |  | P.H. | 0%... CREW REPAIRS? 2-12-82 R. O'CONNOR
30 | 74-41140-1 |  |  | 1.25 | Service |  | Other |  |  | Damage by outside Forces |  | 1974-03-13 | 1974-03-14 | Replace Pipe and/or Service |  | Plastic |  | P.H. | A.P. PIPELINE CONSTRUCTION CO. OPERATOR A. RODRIGUEZ 1PM - 3-13-74; BROKEN 1 1/4" MAIN BY BACK HOE REPLACED 3' 1 1/4 PL PIPE ALSO PULLED 1 1/4 CONTINENTAL TEE LOOSE REPLACED TEE; SEE - C-RAG. N. BOX 3-13-74 1:35PM; A.R # J-74-3215-D1 D/C 26526-E
30 | 79-23044-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-11-05 | 1980-10-07 | Other |  | Other |  | PLEASANT HILL | REPAIRED LEAK AT #2965 BONNIE LN. FOUND NO OTHER LEAKAGE; 1% IN WATER METER BOX 2' LEFT OF DRIVEWAY EAST/SIDE OF STREET. MARKED IN YELLOW PAINT; 0% GAS IN WATER BOX. ALSO 0% GAS IN OLD BELLHOLE AT 2965. LEAK RECHECKED: 10-7-80 R. O'CONNOR; REPAIRED LEAK AT #2965 BONNIE LN. FOUND NO OTHER LEAKAGE.
30 | 82-24073-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-06-10 | 1982-11-01 | Other |  | Other |  | WALNUT CREEK | 0%... CREW REPAIR? SVC R/R ... 11-1-82 R.O'CONNOR
30 | 80-23402-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-05-13 | 1981-09-25 | Other |  | Other |  | PLEASANT HILL | ALL CLEAR; I BELIEVE THIS LEAKAGE HAS ALREADY BEEN DETERMINED AS SWAMP GAS.. IN ACCORDANCE TO CHART GRAPH IN SCHOOL LOG BOOK
30 | 77-22181-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1977-06-14 | 1979-10-24 | Other | WELDED 12" CAN OVER LEAK | Steel/Wrought Iron |  | PLEASANT HILL | .5% GAS EDGE OF SIDEWALK OVER SERVICE TEA AREA; LEAK RE-CHECK 8-8-78 .05% GAS OVER MAIN 3' LEFT OF DRIVEWAY BACK EDGE OF SIDEWALK. MARKED WITH YELLOW PAINT. 0% GAS OVER SUC TEE R. O'CONNOR; INST. 12" CAN OVER LEAK
30 | 81-00603- |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-04-10 | 1983-02-23 | Other |  | Other |  | PLEASANT HILL | 15% GAS OVER MAIN NEAR PG&E VALVE COVER 3' RIGHT OF DRIVEWAY BACK EDGE OF SIDEWALK MARKED WITH YELLOW PAINT; DOWNGRADE TO #3; 30-70PPM... 9-24-81 CREW REPAIR? R.O'CONNOR; NON GREASE TYPE VALVE
30 | 80-23401- |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-05-13 | 1983-05-16 | Other |  | Other |  | PH
30 | 82-23988-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-05-03 | 1983-05-16 | Other |  | Other |  | PH
30 | 75-42063-1 |  |  | 2 | Distribution Main | VALVE | Valves |  |  | Other |  | 1975-04-11 | 1975-04-14 | Other | GREASED VALVE | Steel/Wrought Iron |  | P. HILL | GREASED VALVE AND RECSECKED W/ D.W. ALL TESTS NEGATIVE.; 60PPM IN GAS VALVE FRAME & COVER; GREASE VALVE
|  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  | 1980-09-18 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  |  |  | 2 | Distribution Feeder Main |  | Other Welds |  |  | Other |  | 1980-08-12 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | WC
|  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  | 1980-08-12 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | WALNUT CREEK
|  |  |  | 4 | Distribution Feeder Main |  |  |  |  | Other |  | 1980-09-09 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  | 1980-09-16 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  | 1980-09-24 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | WALNUT CREEK
| 82-24091-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-06-16 | 1983-06-10 | Other |  | Other |  | PLEASANT HILL | 0%, I COULD NOT ON THE STREET.. THERE IS A NO LEAK MARK AT ... PAINT AWAY ON GIVING A APPEARANCE... 6-10-83 R. O'CONNOR
| 00- |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1974-12-18 |  | Other |  | Steel/Wrought Iron |  | WC
30 |  |  |  | 2 | Distribution Main | [6 empty] | 1975-05-05 |  |  |  | Steel/Wrought Iron |  | WC | PROSPECT MAIN DEPTH
30 | 83-24390-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-03-18 | 1983-06-17 | Other |  | Other |  | WC
30 | 75-21109-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 1975-04-09 | [5 empty] | P.HILL | MANIFOLD; BAR TESTED OVER SERVICE NO INDICATION OF LEAKAGE. SOAPED MANIFOLD SET. SMALL LEAK AT INSULATING UNION - MADE OUT C THG - 2 MAN CRETOR BY PASS HOSE.; .02% GAS AT RISER AT APT BLDG 42 TO 48, 4MM; NO. 2 LEAK
30 | 75-21110-1 |  |  | 0.75 | Distribution Main | [6 empty] | 1975-04-09 |  |  |  | Steel/Wrought Iron |  | P.HILL | SOAPED MANIFOLD BAR TESTED SERVICE NO INDICATION OF LEAKAGE; .3% GAS AT RISER AT APT. BLDG 9 TO 17, 4MM; NO. 2 LEAK
30 | 83-24394-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-03-21 | 1983-06-17 | Other |  | Other |  | WC
30 | 81-22109-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1981-06-16 | 1981-12-17 | Other |  | Steel/Wrought Iron |  | LAF. | GRAND VALVE IS EXERCISED
30 | 87-26187-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-02-20 | 1989-11-22 | Weld Over Sleeve or Can | PATCH WELDED | Steel/Wrought Iron |  | LAF | WELDED VARIOUS PATCHES OVER NUMEROUS LEAKS ON 8" TP; APROX. 10' S/O 29.35 V 29.4; INSTALLED 32 LOS HNODE AT LOCATION
30 | 87-26188-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-02-20 | 1989-11-22 | Weld Over Sleeve or Can | PATCH WELDED | Steel/Wrought Iron |  | LAF | WELDED VARIOUS PATCHES OVER NUMEROUS LEAKS ON 8" TP NONWRAP, NOT UNDER PROTECTION; INSTALLED 32 LBS ANODE AT LOCATION
30 | 74-41644-1 |  |  | 8 | Transmission |  | Fitting |  |  | Material Failure |  | 1974-04-26 | 1974-04-29 | Other |  | Steel/Wrought Iron |  | LAF.
30 | 77-42883-1 |  |  | 1.75 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-07-25 | 1977-07-25 | Replace Pipe and/or Service |  | Plastic |  | LAF. | REPLACED 18" OF 1 1/4 PL PIPE; REPLACED 18" OF DAMAGED 1 1/4 PL MAIN
| 81-22131-1 |  |  | 0 | Other |  | Meter |  |  |  |  | 1981-07-28 | 1981-07-30 | Other |  | Steel/Wrought Iron |  | LAF | .5% AT RISER
| 82-23752-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-02-02 | 1983-01-19 | Other |  |  |  | LAFAYETTE
30 | 82-23748-1 |  |  | 0 | Other |  | Other | Valves |  | Other |  | 1982-02-01 | 1983-01-19 | Other |  | Other |  | LAF
30 | 82-23749-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-02-01 | 1983-01-19 | Other |  | Other |  | LAF
30 |  |  |  | 6 | Transmission |  | Other |  |  | Other |  |  | 1977-09-07 | Other |  | Steel/Wrought Iron |  | LAF | 6" WATER MAIN LAYING ON TOP OF 6" GAS MAIN
30 | 77-42822-1 |  |  | 4 | Distribution Main |  |  |  |  | Other |  | 1977-01-18 |  |  |  | Steel/Wrought Iron |  | WALNUT CREEK | EXPOSED 3 TO 4" MAIN AT TIE IN NO LEAK FOUND
30 | 82-23691-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-12 | 1982-12-31 | Other |  | Other |  | WC
30 | 81-44354-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-01-30 | 1982-12-31 | Other |  | Other |  | LAF
30 | 77-20820-1 |  |  | 4 | Distribution Main | [6 empty] | 1977-01-18 |  |  |  | Steel/Wrought Iron |  | WC | 10/10 IN PATCH TO SERVICE (MARKED)
30 | 81-44358-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1981-02-06 |  | Replace Pipe and/or Service |  | Plastic |  | W.C. | BROKEN GAS LINE; LINE BROKEN BY OUTSIDE CONSTRUCTION INST ST LIGHT BASE INST. 2' 144" PL GAS PIPE FOR REPAIRS
30 | 82-23691-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-15 | 1982-12-31 | Other |  | Other |  | WALNUT CREEK
30 | 82-23698-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 01/15/0982 | 1982-12-31 | Other |  | Other |  | WC
30 | 82-23706-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-18 | 1982-12-31 | Other |  | Other |  | WC
30 |  |  |  | 3 | Distribution Feeder Main |  | Other |  |  | Other |  | 1973-05-16 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron
30 | 82-23708-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-18 | 1982-12-31 | Other |  | Other |  | WC
30 | 82-23705-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-18 | 1982-12-31 | Other |  | Other |  | WC
30 | 82-23695-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-15 | 1982-12-31 | Other |  | Other |  | WC
| 82-23694-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-15 | 1982-12-31 | Other |  | Other |  | WC
30 | 83-24393-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-03-21 | 1983-06-15 | Other |  | Other |  | WC
30 | 82-23712-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-21 | 1982-12-31 | Other |  | Other |  | WC
30 | 82-23711-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-21 | 1982-12-31 | Other |  | Other |  | WC
30 | 82-23699-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-15 | 1982-12-31 | Other |  | Other |  | WC
30 | 82-23700-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-18 | 1982-12-31 | Other |  | Other |  | WC
30 | 82-23728-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-25 | 1982-07-20 | Other |  | Other |  | WALNUT CREEK | 0% AT THRIFT SHOP; ODOR NOTE: 70% GAS IN BELL HOLE (SVC R/R) ACROSS STREET, 1531 AT "NORTH MAIN TOW"...MARKED THIS LEAK HAS MIGRATED VERY SHORT SVC... 6-8-82 R. O'CONNOR; NEW ADDRESS 1531; DUPLICATE U/# 23702
30 | 82-23729-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-25 | 1982-07-20 | Other |  | Other |  | WALNUT CREEK | 15% - 20% NEXT TO STORM DRAIN MARKED... 6-8-82 R.O' CONNOR; DUPLICATE; ADMIRAL VAN & STORAGE
30 | 82-23731-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-25 | 1983-01-05 | Other |  | Other |  | WC | O%... CREW REPAIRS?
30 | 82-23720-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-25 | 1983-01-05 | Other |  | Other |  | WC | O%.. CREW REPAIRS? 1-5-83 R. O'CONNOR;
30 | 82-23738-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-27 | 1982-06-25 | Other |  | Other |  | WALNUT CREEK | O%... CREW REPAIRS 6-25-82 R.O'CONNOR
30 | 82-46743-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-23 | 1982-07-01 | Other |  | Other |  | PLEASANT HILL | DUPLICATE SEE 82-23739. INST. CANON 2"STL MAIN 14I W/O ARENDS/N.; 100% GAS OVER MAIN SEE ATTACHED SKETCH... NON MIGRATING AT PRESENT TIME... CUSTOMER COMPLAINT TAG... 7%... TEST HOLE HAVE VENTED THIS LEAK DOWN AT PRESENT TIME... 5-27-82 R.O'CONNOR; DUPLICATE A-FORM; 4% READINGS ONLY HIRED OUT 4-29-82
30 | 82-23737-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-27 | 1982-06-08 | Other |  | Other |  | WALNUT CREEK | O%... CREW REPAIRS? 6-8-82 R. O'CONNOR
30 | 82-23718-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-25 | 1983-01-05 | Other |  | Other |  | WC | O%... CREW REPAIRS? 1-5-83 R.O'CONNOR
30 | 82-23717-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-25 | 1983-01-05 | Other |  | Other |  | WC
30 | 82-23726-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-01-25 | 1983-01-05 | Other |  | Other |  | WC | O%.. CREW REPAIRS? (SVC R/R...)
30 | 82-23763-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-02-22 | 1982-08-13 | Other |  | Other |  | W.C.
30 | 82-23762 |  |  | 0 | Other |  | Other |  |  | Other |  | 02/22/0198 | 1982-08-13 | Other |  | Other |  | WALNUT CREEK | 10% T FLAME OUT OVER RISER MIGRATION... ADMIRAL VAN & STORAGE
30 | 75- |  |  | 4 | Transmission |  | Other |  |  | Other |  | 1976-01-29 | 1976-01-29 | Other | REWRAP | Steel/Wrought Iron |  | WALNUT CREEK | FUTURE WATER LINES
|  |  |  | 6 | Distribution Feeder Main |  | Regulator |  |  | Other |  | 1980-08-04 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | WALNUT CREEK
30 | 74 |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1974-01-24 |  | Other |  | Steel/Wrought Iron |  | W.C | EXCAVATED VALVE - STRAIGHTENED VF.C.
|  |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  | 1980-08-14 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | WALNUT CREEK
30 | 73-41371-1 |  |  | 0.75 | Other |  | Meter |  |  | Material Failure |  | 1973-10-30 | 1973-11-08 | Other |  | Steel/Wrought Iron |  | WAL CREEK | GOT SEVERAL READS FROM METER SEAMS .03 TO 1. A POSSIBLE METER CHANGE TYPE 675 SPRAGUE. ALSO READS FROM BOTH SWIVELS & A READ FROM BOTTOM OF REG. ODOR IN AIR - CUST CONCERN; REPLACE PLUG IN SIDE OF REGULATOR
30 | 77-20850-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1977-02-14 | 1981-10-16 | Other |  | Other |  | WALNUT CREEK | REST OF SERVICE CLEAR. 2-28-78 FLAME PAC
|  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | LAFAYETTE | LINE 191A EXPOSED DURING
30 | 81-23586-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-07-23 | 1983-06-29 | Other |  | Other |  | LAFAYETTE
3 | 93-26201-1 |  |  | 0.75 | Service |  | Valves |  |  | Material Failure |  | 1993-10-15 | 1993-10-18 | Other |  | Steel/Wrought Iron |  | LAF. | LEAK FOUND IN HIGH TO HIGH BOX; SHUT OFF "PIN-OFF" TEE. ELIMINATED 301. MADE OUT "C" TAG FOR M&c DEPT. TO REPAIR 10/19/93
| 09-98170-1 | [10 empty] | 2009-10-31 | [5 empty] | LAFAYETTE | NO LEAK FOUND
30 | 88-46019-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1988-02-10 | 1988-02-12 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | INSTALLED TEMP. CLAMP 2-10-88 WELDED PERMANENT CAN AND SLEEVE 2-12-88; INSTALLED TEMP. LEAK CLAMP TO; 1) INSTALLED 12" X 24" WELD CAN OVER FULL CIRCLE CLAMP - TESTED TO 450 PSI WITH NITROGEN 2) INSTALLED WELD SLEEVE AND SAVE A-NIPPLE OVER INDENTATION IN PIPE. TESTED TO 450 PSI WITH NITROGEN AND TAPPED SAVE-A NIPPLE; PERMANENT REPAIRS MADE ON 2-12-88
30 | 82-22188-1 |  |  | 8 | Transmission |  | Girth Weld |  |  | Corrosion |  | 1982-05-26 | 1982-07-28 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | Lafayette | INST. 8" CLAMP 6-4-82; INST. 8" SLEEVE AND 32 LB. ANODE 7-28-82
30 | 82-23797-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-03-09 | 1983-02-18 | Other |  | Other |  | LAFAYETTE
30 |  |  |  | 4 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1981-03-31 | Other |  | Steel/Wrought Iron |  | LAF. | INST. 1-4" LINE STOPPER, TO REPLACE TWO VALVES IN REG. PIT.
30 | 82-23796-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-03-09 | 1983-02-18 | Other |  | Other |  | LAFAYETTE
30 |  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | LAF | INSTALLED ETS STATION AT TIE IN OF 6" & 2" GAS MAIN
30 | 77-20877-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1977-03-07 | 1977-08-03 | Clamp |  | Steel/Wrought Iron |  | WALNUT CREEK | INSTALLED 2" SKINNER CLAMP ON MAIN; INSTALLED 2" LEAK CLAMP.; FOUND NO READS
30 | 82-23882-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-09 | 1983-03-24 | Other |  | Other |  | WC
30 | 82-23876-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-09 | 1983-03-24 |  |  | Other |  | WC | 0%.. CREW REPAIRS? 8-22-83
30 | 83-47116-1 |  |  | 0 | Other | [6 empty] | 1983-03-23 |  |  |  | Other |  | WC | UPGRADED SEE LK # 8647916; 10% GAS IN ... PIN-POINTER & MARKED... 5-27-83; 100%... ODOR RECLASSIFY TO #2 LEAK 6/4/86; NOTE: CUSTOMER CONCERNED ABOUT SUNKEN BELL HOLES (LEAK GRADED TO #3 A/C O)
30 | 75-20530-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1975-07-25 | 1981-10-16 | Other |  | Other |  | W.C | READ OF .3 OVER MAIN 7-5-79 K.F; FOUND 10 IN PROBE HOLE MARKED FLAME G.COLE 6-20-77
30 | 82-23897-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-20 | 1983-04-04 | Other |  | Other |  | WC
30 | 84-47468-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1984-05-24 | 1984-05-24 | Clamp |  | Steel/Wrought Iron |  | W. CREEK | 100% GAS, BARTESTED 2" MAIN; 5-25-85 BACK FILLED BELL HOLE & SOAP TESTED CLAMPS
30 | 82-23905-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-26 | 1983-04-04 | Other |  | Other |  | WC
30 | 82-46969-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-10-22 | 1983-01-05 | Other |  | Other |  | WALNUT CREEK | 20% - 4010... DUPLICATE A-FORM...
30 | 82-23902-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-22 | 1983-04-04 | Other |  | Other |  | WC
30 | 82-23903-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-22 | 1983-04-04 | Other |  | Other |  | WC
30 | 82-23901-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-22 | 1983-04-04 | Other |  | Other |  | WC
30 | 82-23893-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-21 | 1982-12-02 | Other |  | Other |  | W.C. | THIS IS THE SAME AS LEAK # 82-23892; 100%... OLD LEAK MARK; ODOR; NOTE: THIS LEAK IS THE SAME AS 82-23892... PAINTED.. MIGRATION (LAWN ARE #)
30 | 81-22106-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-06-10 |  | Other |  | Other |  | WALNUT CREEK
30 | 82-24089-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-06-16 | 1983-06-10 | Other |  | Other |  | WALNUT CREEK | .2% GAS IN P.T.&T. MANHOLE COVER
30 | 82-24087-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-06-16 | 1983-06-10 | Other |  | Other |  | WALNUT CREEK | .05% GAS IN P.T.&T. MANHOLE COVER
30 | 78-21436-1 |  |  | 0.75 | Other |  | Other |  |  | Other |  | 1978-07-12 | 1978-10-20 | Other |  | Steel/Wrought Iron |  | WALNUT CREEK
30 | 82-24086-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-06-16 | 1982-06-28 | Other |  | Other |  | W.C. | BARTESTED MAIN & SERVICE FOR 400' AFTER LEAK AT 243 WAS REPAIRED. HAD NEGATIVE READINGS. PLEASE HAVE READING FLAME PACKED AGAIN
30 | 82-23984-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-28 | 1983-04-04 | Other |  | Other |  | WC
30 | 82-23983-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-28 | 1983-04-04 | Other |  | Other |  | WC
30 | 82-23987-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-30 | 1983-04-04 | Other |  | Other |  | WC
30 | 73-00391-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-01-13 | 1973-09-07 | Clamp |  | Steel/Wrought Iron |  | WALNUT CREEK | SKINNER CLAMP ON 2" MAIN TESTED. SERVICE OK. REFLAMED STOP; GOT A .07 FRO; NO. 15 N-12895, TYPE IS A METER
30 | 73-00609-1 |  |  | 2 | Distribution Feeder Main | [6 empty] | 1973-01-29 |  |  |  | Steel/Wrought Iron |  | ORINDA | DUG UP 10' MAIN UNABLE TO LEAKAGE
30 | 76-20566-1 |  |  | 0.35 | Other |  | Physical/Mechanical Joint |  |  | Other |  | 1976-01-30 | 1976-02-24 | Other |  | Steel/Wrought Iron |  | ORINDA | ISSUED NEW FORM "A" ON 6/8/76 - ; CAP AND GRASS PLUG WAS LOOSE ON 3/4" SERVICE TEE TO #1 REDOPED AND RETIGHTEN - ; .07 PROBE HOLE OVER MAIN 6/7/76 F.P. D.G.
30 | 73-00611-1 |  |  | 2 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1973-01-29 | 1973-05-02 | Other |  | Steel/Wrought Iron |  | ORINDA | 2" VALVE BEARING GREASED
30 | 86-46149-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces | DIGIN | 1986-12-04 | 1986-12-02 | Replace Pipe and/or Service |  | Copper |  | LAFT.
30 |  |  |  | 0.5 | Other | PRESSURE GAUGE STATION - ABANDONED | [5 empty] | 1975-09-05 |  | Other |  | Copper |  | LAF | C/O 1/2" COPPER LINE AT TEE... ABANDONED PRESSURE... GAUGE STATION
| 82-23911-1 |  |  | 0 | Other |  | Other |  |  | Other |  |  | 1982-05-28 | Other |  | Other |  | LAF. | ZERO READINGS OVER SEWER TRENCH & SERVICE AREAS - 5-28-82 - ... TO #3
30 | 82-23910-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-12 | 1982-08-17 | Other |  | Other |  | W.C.
30 | 82-23923-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-16 | 1983-03-25 | Other |  | Other |  | LAF
30 | 83-24403-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-03-23 | 1983-06-17 | Other |  | Other |  | LAFAYETTE
30 | 80-21923-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-05-27 | 1981-10-16 | Other |  | Other |  | LAF
30 | 82-23922-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-15 | 1982-08-17 | Other |  | Other |  | LAFAYETTE
30 | 82-23930-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-19 | 1983-03-26 | Other |  | Other |  | LAF.
30 | 82-23934-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-20 | 1983-06-29 | Other |  | Other |  | LAFAYETTE | 2% OVER MAIN... TEE AREA... OLD LEAK ... 6-28-83 R.O'CONOR
30 | 82-23932-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-20 | 1982-12-03 | Other |  | Other |  | LAF. | 0%... CREW REPAIRS? NEW HOUSE NEW SVC...
30 | 82-23936-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-04-20 | 1982-08-17 | Other |  | Other |  | LAF
30 | 86-46161-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1986-12-12 | 1986-12-12 | Replace Pipe and/or Service |  | Plastic |  | LAF | BROKEN GAS LINE; ILLEGIBLE WRITING DUE TO FADING
30 | 83-47130-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-03-25 | 1983-06-17 | Other |  | Other |  | WC | CREW REPAIRS? 6-16-83 R.O'CONNOR; WAS #3 82.23944;
30 | 82-23976-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-28 | 1983-03-25 | Other |  | Other |  | WC
30 | 81-23608-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-09-09 | 1982-01-13 | Other |  | Other |  | LAFAYETTE
30 | 81-23609-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-09-09 | 1982-01-18 | Other |  | Other |  | LAFAYETTE
30 |  |  |  | 2 | Distribution Main | [8 empty] | Other | CUT OFF SERVICE | Steel/Wrought Iron |  | MARTINEZ | CUTT OFF SERVICE; CUT OFF SERVICE HOUSE DESTROYED BY FIRE
30 | 82-23941-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-22 | 1983-03-25 | Other |  | Other |  | WC
30 | 82-23862-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-06 | 1982-01-04 | Other |  | Other |  | W.C. | 75%... MARKED; INSERTED 1/2" PL IN 3/4" PIPE; CLEARED ON # 82-23860
30 | 83-47067-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-02-04 | 1983-05-05 | Other |  | Copper |  | WALNUT CREEK | NON-MIGRATING O%.. 5-5-83 R. O'CONNOR; SLIGHT ODOR
30 | 80-21912-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-05-14 | 1982-04-16 | Other |  | Other |  | WC | O%.. COULD FIND NO INDICATION OF A LEAK. MARK... I SURVEYED OVER MAIN 4 SVC.. NEGATIVE READINGS WITH FLAME PACK
30 | 83-24398-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-03-22 | 1983-06-17 | Other |  | Other |  | WC
30 | 82-23857-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-05 | 1983-04-05 | Other |  | Other |  | WC
30 | 77-20919-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1977-03-29 | 1983-04-05 | Other |  | Other |  | WAL CREEK | RECEIVED (.03) READING COMING FROM MARKED SPOT BY WATER VALVE, REST OF AREA CLEAR. 03-01-78 FLAME PAC; 4-5-83 FOUND .5% IN SEWER. .03% IN VALVE TO FIRE HYDRANT; ILLEGIBLE WRITING DUE TO FADING
30 | 94-26104-1 | [10 empty] | 1994-05-29 | 1995-07-10 |  |  |  |  | W.C. | 10-11-95 NO LEAKAGE DETECTED
30 | 79-43757-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-12-05 | 1979-12-06 | Other |  | Other |  | WALNUT CREEK | STRONG ODOR IN CURB METER BOX & FROM VENT ON ROOF; ODOR IN THE CURB METER BOX WAS ON A FITTING AND HAS BEEN ... ODOR FROM VENT ON ROOF WAS ANALYZED BY D.E.R. AND ISN'T NATURAL GAS
30 |  |  |  | 3 | Distribution Feeder Main |  | Other |  |  | Other |  | 1973-04-12 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | WALNUT CREEK
30 |  |  |  | 3 | Distribution Feeder Main |  | Other |  |  | Other |  | 1973-04-12 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | WALNUT CREEK
30 |  |  |  | 3 | Distribution Feeder Main |  | Other |  |  | Other |  | 1973-04-12 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | WALNUT CREEK
30 | 82-23972-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-27 | 1983-04-04 | Other |  | Other |  | WC
| 05-26096-1 | [10 empty] | 2005-10-20 | [5 empty] | WALNUT CREE
30 | 79-43533-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-06-15 | 1979-06-15 | Clamp |  | Steel/Wrought Iron |  | ORINDA | INST. 3/4" CLAMP TEMP; MADE PERMANENT REPAIRS TASER, MAY HAVE TO BE MOVE; REFERED TO FIELD FORMS (JOHN R.); SERVICE TO BE LOWERED WHEN NEW SERVICE IS INSTALLED TO NEW HOUSE UNDER CONSTRUCTION NEXT DOOR J.R. 7-13-79
30 |  |  |  | 2 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | WRITING ILLEGIBLE DUE TO FADING
30 | 73-41246-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-06-01 | 1973-06-11 | Clamp |  | Steel/Wrought Iron |  | LAF. | MAIN IN POOR CONDITION; 10/2/73 NO READ FOR 6# CREST RD.. FLAME-PAK; GOT A .04 FROM PATCH BY TAP.; INSTALLED 2 SKINNER CLAMPS ON MAIN.
30 | 87-46183-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Corrosion |  | 1987-01-12 | 1987-01-28 | Replace Pipe and/or Service |  | Copper |  | LAF | STRONG ODOR IN AIR; REPAIR 1/2 LB SERVS... 2' OR 1/2" PL PIPE ... & ONE MECH FIT. BY SERVS. TEE.
30 | 72-40571-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-01-27 | 1972-04-25 | Weld Over Sleeve or Can |  | Steel/Wrought Iron
1 |  |  |  |  | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1986-09-29 | 1986-09-30 | Patch Welded |  | Steel/Wrought Iron |  | LOFK. | THIS IS A BRANCH SERV. THERE IS A ...
30 | 77-42894-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1977-07-22 | 1977-08-01 | Clamp |  | Steel/Wrought Iron |  | LAF. | FOUND READS OVER SERVICE BY BLDG. NEXT TO SERVICE TEE; INSTALLED 2-4" SKINNER CLAMPS; INSTALLED 2'-4" SKINNER CLAMPS ON MAIN; MADE NEW FORM "A"" 11-11-77 m. ALMEDA
30 | 77-42895-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1977-07-22 | 1977-08-01 | Clamp |  | Steel/Wrought Iron |  | LAF. | INSTALLED 3-4" SKINNER CLAMPS; ILLEGIBLE WRITING DUE TO FADING; FOUND READS OVER SERVICE BY BLDG. NEXT TO TEE; INSTD. 3-4" CLAMPS; MADE NEW FORM 'A' 11-11-77 M.ALMENT
|  |  |  | 8 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1977-04-21 | Other |  | Steel/Wrought Iron |  | LAF. | EXPOSED ... TIE-IN, 4X6, INSPECTION, TO CLEAR CONTACT OF WATER MAIN.
|  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  |  | 1981-04-27 | Other |  | Steel/Wrought Iron |  | LAF. | C/O SERV. AT TEE; MAIN WAS IN POOR CONDITION.
| 09-96546-1 |  |  | 0.75 | Single Service |  | Other |  | SERVICE TEE STEEL CAP | Other | LOOSE SERVICE TEE CAP | 2009-07-16 | 2009-12-05 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | LAFAYETTE | TIGHTEN .75 SERVICE TEE CAP
30 | 79-21501-1 | [10 empty] | 1979-08-14 | [5 empty] | LAFT.
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | LAFAYETTE
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | LAFAYETTE
|  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | LAFAYETTE
|  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | LAFAYETTE
30 | 76-20761-1 |  |  | 0 | Distribution Main |  | Other |  |  | Other |  | 1976-10-13 | 1977-05-19 | Other |  | Steel/Wrought Iron |  | LAF. | BARTESTED MAIN AND SERVICES - FOUND NO LEAKAGE.; FOUND 10/10 IN PATCH ACROSS STREET FROM THIS ADDRESS.
30 | 86-46064-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Corrosion |  | 1986-10-13 | 1986-11-17 | Replace Pipe and/or Service |  | Copper |  | LAF | NOTE: SERVICE IS ON E. SIDE OF LAUREL DR. 118' SOUTH OF MAGNOLIA LN.; ILLEGIBLE WRITING DUE TO FADING
30 | 79-43464-1 |  |  | 2 | Other |  | Fitting |  |  | Other |  | 1979-04-03 | 1979-04-13 | Other |  | Steel/Wrought Iron |  | LAF. | BAR TESTED MAIN + SERVICES NO INDICATION OF LEAKAGE. FOUND ... ON 1" PLUG ON TOP OF FILTER POT + TWO METRIC VCALVES TIGHTENED ... FITTING 4-13-79; POSSIBLE LEAK ON MAIN
30 | 77-42896-1 |  |  | 4 | Distribution Main |  | Tap Connection |  |  | Corrosion |  | 1977-06-22 | 1977-08-04 | Other |  | Steel/Wrought Iron |  | WAL. CREEK | INSTALLED NEW TEE FOUND .3 COMIN FROM... FLAME PAC; FOUND 1/10 BY HYDRENT ALSO 10/10 IN TELEPHONE MANHOLE; INSTALLED NEW SERVICE TEE & 5 FEET OF 4... PL SERV. RE... SERV. TEE & 5' OF 1/2 CV. SERV. ; MADE NEW FORM "A" 11-17-1977 M.CLEMENT
30 | 77-42896-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1977-11-16 | 1979-11-26 | Other |  | Other |  | WAL. CREEK | FOUND .3 COMING FROM PATCH.
30 | 77-21006-1 |  |  | 2 | Distribution Main |  | Other Welds |  |  | Material Failure |  | 1977-05-16 | 1978-02-28 | Other |  | Steel/Wrought Iron |  | WALNUT CREEK | WIELD ON SERV. TEE LEAKING; .5 OVER SERVICE ALSO READS ON STOP COCK; SEAL LEAK AROUND YELLER SPAT
30 | 77-42829-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1977-05-20 | 1977-05-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | WALNUT CREEK | REPLACED 4 FT OF ... & INSTALLED ... ; EXP. ON LEL IN... ; REPLACED 4 ... & 2" L.S.F.
30 | 86-22819-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1986-06-24 | 1986-10-10 | Clamp |  | Steel/Wrought Iron |  | W.C | INST. ONE ... CLAMP..; WRITING ILLEGIBLE DUE TO FADING
30 | 78-43260-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1978-10-09 |  |  |  | Other |  | WALNUT CREEK | PROBE HOLE OVER MAIN (MARKED); WRITING ILLEGIBLE DUE TO FADING
30 | 72-40812-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-08-28 | 1972-12-26 | Clamp |  | Steel/Wrought Iron |  | WALNUT CREEK | CHECKED... FOUND ONE .2 & 2 10/10 ON SARANAD AVE. BULLSEYES FLAME-PAK 4/5/73; WRITING ILLEGIBLE DUE TO FADING
30 | 74-41771-1 |  |  |  | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1914-07-25 |  | Other |  | Steel/Wrought Iron |  | WALNUT CREEK | LEAK REPAIRED 8/1/74 ON LEAK # 7444823 (LEAK REPORT #74-44823 SHOWED INSPECTION ONLY) WAP 12-16-74
30 | 86-46106-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1986-11-07 | 1986-11-07 | Replace Pipe and/or Service |  | Plastic |  | LAF | 1/2" PL. SVC #W2590 E. SIDE OF CAROLYN CT. S. OF MEEK LN; BROKEN GAS LINE; REPAIR 1/2" PL SERVS. USED: 1' OF PL PIPE & TWO MECHANIC CAP. FITT.
30 | 73-41421-1 |  |  | 1.25 | Other |  | Meter |  |  | Material Failure |  | 1973-11-26 | 1973-12-12 | Other |  | Steel/Wrought Iron |  | WAL CREEK | GOT A 10/10 READ FROM CURB SET IN FRONT OF JOHN BULL LTD.; TIGHTEN SCREWS ON METER CASE
30 | 73-41422-1 |  |  | 1.25 | Other |  | Regulator |  |  | Construction Defect |  | 1973-11-26 | 1973-12-10 | Other |  | Steel/Wrought Iron |  | WAL CREEK | GOT A .5 FROM CURB SETS IN FRONT OF VAUGHNS MENS CLOTHING STORE; REDOPED FITTING
30 | 73-41423-1 |  |  | 1.25 | Other |  | Fitting |  |  | Construction Defect |  | 1973-11-26 | 1973-12-10 | Other |  | Steel/Wrought Iron |  | W.C. | GOT A 7 FROM CURB SETS IN FRONT OF CONTRA COSTA STATIONERS.; REDOPED FITTINGS
30 | 73-41424-1 |  |  | 1.25 | Other |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1973-11-26 | 1973-12-11 | Other |  | Steel/Wrought Iron |  | W.C | GOT A 10/10 READ FROM CURB SETS IN FRONT OF COLLIERS SPORTS VILLAGE; TIGHTEN TOP FITTING NUT ON STOP COCK
30 |  |  |  | 0.04 | Distribution Feeder Main |  | Other |  |  | Other |  | 1987-05-20 | 1987-05-20 | Patch Welded |  | Steel/Wrought Iron |  | WALNUT CREEK | C/O ONLY; 4" HP... ILLEGIBLE DUE TO FADING; THIS WAS A... PL SERVICE C/O...
30 | 86-22759-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Corrosion |  | 1986-04-04 | 1986-12-19 | Replace Pipe and/or Service |  | Copper |  | W.C. | WRITING ILLEGIBLE DUE TO FADING
30 | 76-20766-1 |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1976-10-15 | 1981-03-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | WAL. CREEK | LEAK ON UNION OF MANIFOLD; FOUND .1 OUT OF METER BOXES - MARKED; REPL. LEAKING UNION
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron |  | W.C. | SERV R/R NO LEAKAGE
| 09-43129- | [10 empty] | 2009-03-23 | [5 empty] | LAFAYETTE
30 |  |  |  | 8 | Distribution Main | [6 empty] | 1972-01-28 |  |  |  | Steel/Wrought Iron |  | LAF. | REWRAP 8" MAIN ON S/S MT. DIABLO BLVD OUT 17 FROM P.L. 300' W/O DOLORES DR.
30 | 75-42322-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1975-10-17 | 1975-10-24 | Clamp |  | Steel/Wrought Iron |  | LAF. | INSTALLED 1 1/4 X ... CLAMP & WRAPPED.; NO LEAK DETECTED 2/10/76 F.P. D.G.; .1 READING ON SERVICE, ELEC TRENCH CROSSING SERVICE POSSIBLE DAMAGE
30 | 86-46097-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1986-10-31 | 1986-10-31 | Replace Pipe and/or Service |  | Copper |  | LAFT | R/R 1/2 " C SERVS ON 11-31-86. USED. 59' OF 1/2 PL PIPE DATE 3-86 ALDYLA TEMP REPAIRS WERE MADE ON 10/31/86
30 | 79-43631-1 |  |  | 0.5 | Service |  | Fitting |  |  | Corrosion |  | 1979-09-12 | 1979-09-12 | Replace Pipe and/or Service |  | Copper |  | DAN. | WE MADE TEMP REPAIRS BY INSTALLING 2' OF 1/2" PLASTIC. (LEAKING AT COPPER COUPLING)
30 | 78-43106-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Construction Defect |  | 1978-01-17 | 1978-01-17 | Other |  | Steel/Wrought Iron |  | WALNUT CREEK | CAPS ON PIN OFF TEE WERE NOT DOPED WHEN THEY WERE INSTALLED
3 | 85-45560-1 |  |  | 0.75 | Transmission |  |  |  |  | Construction Defect |  | 1985-02-20 | 1985-02-20 | Other |  | Steel/Wrought Iron |  | WC. | REPAIRED LEAKAGE ON 2 SERVICE TEE GUGAE TAP SERVICE TEES AT VALVE 2-X37
1 |  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | LAFAFYETTE
30 | 81-44528-1 |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1981-08-05 | 1981-08-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | W.C | INSERTED SUC 83' PL. 1/2"; .1% OVER SERVICE APPROX 15' FROM METER SUT; RERAN SERVICE
30 |  |  |  |  | Distribution Feeder Main |  | Other |  |  | Other |  | 1986-11-02 | 1986-11-02 | Other |  |  |  | W.C | INSTALL 1/3 PL SERVICE. I DID NO J.T. (CUST REQUEST)
30 | 78-21265-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-03-21 | 1978-04-15 | Patch Welded |  | Steel/Wrought Iron |  | WALNUT CREEK | FOUND READING APPROX 100'' EAST OF 1781 COMING FROM SEWER GRATE (MARKED); WRITING ILLEGIBLE DUE TO FADING
30 | 86-22747-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1984-02-16 | 1986-02-11 | Clamp |  | Steel/Wrought Iron |  | W.C. | 301 WEST SIDE OF BRIDGE RD.; ... THERE IS A TP GAS MAIN 2" AWAY FROM THIS MAIN N/W CORNER
|  |  |  | 16 | [11 empty] | Steel/Wrought Iron |  | WALNUT CREEK
| 96-43278-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1996-09-25 | 1996-11-05 | Clamp |  | Steel/Wrought Iron |  | WALNUT CREEK | INST 2 BOLT LEAK CLAMP EXISTING 4 BOLT LEAK CLAMP 3" FROM LEAK
30 | 77-21056-1 |  |  | 0.5 | Service |  | Fitting |  |  | Material Failure |  | 1977-07-01 | 1978-04-17 | Replace Pipe and/or Service |  | Copper |  | WALNUT CREEK | FOUND 2/10 BY RISER, MARKED AREA 2-23-78 FLAME PAC. A.J.; 2/10 BY RISER ALONGSIDE WATER FOUNTAIN; 1/2" ... WRITING ILLEGIBLE DUE TO FADING
1 |  |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 86/09/2002 | 1986-09-02 | Patch Welded |  | Steel/Wrought Iron |  | W.C. | THIS IS 1/2 PL...
30 | 86-46145-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces | DIGIN | 1986-12-03 | 1986-12-03 | Patch Welded | PR | Aldyl A (Tan or Gray) |  | ORINDA | BROKEN GAS LINE; LOWER DOWN 1/2" PL SERVS AND REPAIR & USED 8' OR 1/2" PL & TWO MECHANIC FITT. USED ALDYL A PIPE
30 | 80-43955-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1980-03-04 | 1986-05-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | LAF. | INSERTED 113' OF 1/2 PL PIPE THRU - 3/4 ... PIPE
30 | 86-46116-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1986-11-13 | 1987-01-26 | Clamp |  | Steel/Wrought Iron |  | LAF | INST. 1-2" SKINNER CLAMP 310' ... WOODVIEW OV. LAF
30 | 98-43232-1 |  |  | 1.25 |  |  | Body of Pipe |  |  | Corrosion |  | 1998-09-28 | 1998-09-28 | Clamp |  | Steel/Wrought Iron |  | LAF. | INSTALLED 1-3 BOLT FULL CIRCLE PERM. REPAIR CLAMP
30 | 83-24701-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-11-08 | 1983-12-01 | Patch Welded |  | Steel/Wrought Iron |  | ILLEGIBLE DUE TO FADING | ... OF BLACK TOP AROUND MAIN
| 10-26099-1 |  |  | 0.75 | Single Service |  | Body of Pipe |  |  | Construction Defect |  | 2010-07-01 | 2010-09-27 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | MORAGE | INSTALLED 3/4" ADAMS CLAMP; INST 1-3/4" ADAMS CLAMP 288' FROM TEE
30 | 74-41537-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-02-12 | 1974-02-13 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | MORAGA | INCERT INST 2 - LSF, 2 - TRAINSITION FITTINGS, 2- 1 1/4" COUPLINGS, 99' PL PIPE; C/O 2" MAIN INCERT 1 1/4" PL
30 | 74-41540-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-02-13 | 1974-02-15 | Clamp |  | Steel/Wrought Iron |  | RHEEM | NO READ FLAME PAC; JUST SKINNER CLAMP ON 3" MAIN
| 09-97546-1 |  |  | 0.75 | Service |  | Riser |  |  | Construction Defect |  | 2009-09-03 | 2009-10-26 | Other | TIGHTEN/REDOPED | Steel/Wrought Iron |  | WALNUT CREEK | BY-PASS VALVE WAS LEAKING, REUSED VALVE VALVE IN GOOD CONDITION, REDOPED & TIGHTEN SOAP TEST NO LEAKS FOUND.
| 09-97545-1 |  |  | 0.75 | Service |  | Riser |  |  | Construction Defect |  | 2009-09-03 | 2009-10-26 | Other |  | Steel/Wrought Iron |  | WALNUT CREEK | BI-PASS ON RISER; REDOPED & TIGHTEN; LEAK WAS ON BI-PASS THREADS ON SERVICE. VALVE WAS IN GOOD CONDITION WHEN INSTALLED REDOPED THEN TIGHTEN SOAP TEST NO LEAKS FOUND.
30 | 79-21475-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-04-27 | 1979-11-28 | Other |  | Other |  | ORINDA
30 | 83-44975-1 |  |  | 0.5 | Service |  | Other Welds |  |  | Corrosion |  | 1983-03-30 | 1983-03-30 | Replace Pipe and/or Service |  | Copper |  | ORINDA | REPLACED CU SUC W/ ...
30 | 71-20047-1 |  |  | 2 | Other |  | Fitting |  |  | Material Failure |  | 1971-12-07 | 1972-02-16 | Other |  | Steel/Wrought Iron |  | RHEEM | LEAK ON METER SET; TIGHTENED FITTING ON METER SET
30 | 86-46120-1 |  |  | 0.5 | Service |  | Other |  |  | Corrosion |  | 1986-11-13 | 1986-11-13 | Replace Pipe and/or Service |  | Copper |  | LAFAYETTE | BROKEN GAS LINE; REPLACED 8 FT OF 1/2" COPPER WITH 1/2" PLASTIC - ALSO REPLACED RISER WITH 3/4" PREFAB RISER.
30 | 80-21948-1 |  |  | 2 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1980-07-29 | 1983-11-03 | Other |  | Steel/Wrought Iron |  | MOR. | TIGHTEN CAP ON SPLIT 2" P.C.F.; 301 COMING FROM VALVE & .1% COMING FROM PATCH MARKED; WRITING ILLEGIBLE DUE TO FADING
|  |  |  | 12 | Distribution Feeder Main | [6 empty] | 1982-09-16 |  |  |  | Steel/Wrought Iron |  | MORAGA
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1982-09-16 |  |  |  | Steel/Wrought Iron |  | ILLEGIBLE DUE TO FADING | ILLEGIBLE DUE TO FADING
30 | 78-43236-1 |  |  | 2 | Distribution Feeder Main |  | Longitudinal Weld |  |  | Construction Defect |  | 1978-08-29 | 1978-08-29 | Other |  | Steel/Wrought Iron |  | LAFAYETTE | ... LK ON WELD OF 2"... OF DRIFT WOOD DR.
30 | 80-43889-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-01-01 | 1980-01-01 | Other |  | Plastic |  | LAF. | HOLE IN PL 2" MAIN 6' FFROM END OF... C/O 6' 2" PL MAIN END ... MAIN ... 3 HRS
30 | 76-20771-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Other |  | 1976-10-18 | 1977-04-20 | Other |  | Steel/Wrought Iron |  | LAF. | .7 POSSIBLE MAIN TIE-IN (MARKED); LAP ON 2" P.C.F. WAS LEAKING. TIGHTENED TO STOP LEAK.; FOUND NO READ FLAME PAC
30 | 86-46135-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1986-11-24 | 1986-11-24 | Other |  | Aldyl A (Tan or Gray) |  | LAFAYETTE | BROKEN GAS LINE; CONTRACTOR... ILLEGIBLE DUE TO FADING
30 | 87-46365-1 |  |  | 0.5 | Service |  | Fitting |  |  | Construction Defect |  | 1987-09-28 | 1987-09-30 | Replace Pipe and/or Service |  | Aldyl A (Tan or Gray) |  | W.C. | REPLACED... TEE
30 | 77-42762-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1977-02-05 | 1977-02-05 | Clamp |  | Steel/Wrought Iron |  | ORINDA | GIVE TO W.C. CREW TO REPAIR 2-7-77; INSTALLED STAINLESS.. ILLEGIBLE DUE TO FADING; NO. 1 LEAK
30 | 86-46102-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1986-11-05 | 1986-11-05 | Replace Pipe and/or Service |  | Copper |  | ORINDA | ... SERVS USED 4' OF PL... ; ILLEGIBLE DUE TO FADING
30 | 96-26728-1 | [10 empty] | 1996-09-03 | [5 empty] | MORAGA | PROBED OVER SVC & GM - TOO SMALL TO PINPOINT; LEAK TOO SMALL TO PINPOINT
30 | 74-41772-1 |  |  |  | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-07-25 |  | Other |  | Steel/Wrought Iron |  | ORINDA | LEAK REPAIR ... ON LEAK # 7444824 ( LEAK REPORT #74-44824 WAS NO RECEIVED BY GAS MAPPING.) WHP 12-16-74; LEAKS REPAIRED ON 74-41717 & 74-41726
3 | 87-46205-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Construction Defect |  | 1987-02-11 | 1987-02-11 | Other |  | Steel/Wrought Iron |  | MORAGA | REPAIRED VALVE
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1982-09-16 |  |  |  | Steel/Wrought Iron |  | ILLEGIBLE DUE TO FADING
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1982-09-16 |  |  |  | Steel/Wrought Iron |  | ILLEGIBLE DUE TO FADING
30 | 80-21930-1 |  |  | 4 | Transmission |  | Valves |  |  |  |  | 1980-06-02 | 1980-09-04 | Other |  |  |  | MORAGA LAF
30 | 80-21949-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1980-08-27 | 1980-09-04 | Other |  | Steel/Wrought Iron |  | LAF | .. VALVES...
30 | 75-42264-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1975-08-15 | 1975-08-26 | Clamp |  | Steel/Wrought Iron |  | ORINDA | FOUND .05 IN PATCH OVER MAIN; INSTALLED 2' SKINNER LEAK CLAMP; NO LEAK DETECTED 12/5/75 FLAME PAK
30 |  |  |  | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | MOR
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1982-09-16 |  |  |  | Steel/Wrought Iron |  | MORAGA
|  |  |  | 12 | Distribution Feeder Main | [6 empty] | 1982-09-16 |  |  |  | Steel/Wrought Iron
30 | 79-43504-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1979-05-24 | 1979-11-14 | Other |  | Steel/Wrought Iron |  | MORAGA | THIS LEAK WAS... WAS REPLACED ON T.P. MAIN THE NIGHT OF FAILURE
30 | 77-21159-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1977-09-26 | 1977-10-07 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | MORAGA | INSTALLED... ILLEGIBLE DUE TO FADING
30 | 76- |  |  | 4 | Transmission | [7 empty] | 1976-12-16 | Other |  | Steel/Wrought Iron |  |  | INSTALLED 3-32 LB ... ANODES & E.T.S.
30 | 83-21472-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1983-04-21 | 1984-04-03 | Clamp |  | Steel/Wrought Iron |  | WEST PITTSBURG | 4" MAIN IN BAD SHAPE. REPAIRS MADE WITH 4" X 12" SKINNER CLAMP. INSTALLED 25' FROM RISER TO ALLIED CHEM. METER SET
30 | 77-40548-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1977-06-28 | 1977-11-04 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | WEST PITTSBURG | ...CAN AND...
3 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1983-06-30 | Other |  | Steel/Wrought Iron |  | WEST PITTSBURG | P.S. SERVICE MAIN HOUSE DUE...
1 | 80-21177- |  |  |  | Transmission |  | Valves |  |  |  |  | 1980-04-28 |  | Other |  | Steel/Wrought Iron |  | WEST PITTSBURG | ADVISED STAN. PAC OF THIS ON 7-9-80 ITS THEIR VALVE.
30 | 92-20032-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-01-31 | 1992-07-22 | Clamp |  | Steel/Wrought Iron |  | WEST PITTSBURG | ON MAIN NEXT TO POWER POLE, INSTALL 2" SKINNER LEAK CLAMP.
30 | 82-21312-1 |  |  | 6 | Distribution Main |  | Other Welds |  |  | Corrosion |  | 1982-01-13 | 1982-04-28 | Patch Welded |  | Steel/Wrought Iron |  | WEST PITTSBURG
30 | 80-21172- |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1980-04-17 | 1980-07-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | WEST PITTSBURG | GREASED VALVE
30 | 81-41176-1 |  |  | 0.5 | Service |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1981-12-28 | 1981-12-30 | Replace Pipe and/or Service |  | Other Plastic |  | WEST PITTSBURG | REPLACED RISER DUE TO LEAKAGE
3 |  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1975-07-01 |  |  |  | Steel/Wrought Iron
| 04-43362- | [10 empty] | 2004-11-30 | [5 empty] | ; CONCORD
|  |  |  | 0.1 | Distribution Feeder Main |  | Other |  |  | Other |  | 1985-06-24 |  | Other |  | Steel/Wrought Iron |  | CONCORD
3 |  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1975-06-30 |  |  |  | Steel/Wrought Iron
| 71-00000 |  |  | 12 | Transmission | [6 empty] | 1971-09-22 |  | Other | REWRAP | Steel/Wrought Iron |  |  | WRAPPED 12" TRANS MAIN & POSED BY CONTRACTOR TO INSTALL 10" SLUDGE LINE
| 98-23034-1 | [10 empty] | 1998-06-13 | [5 empty] | CONCORD | NO LEAK FOUND;
30 | 72-00000-0 |  |  | 2 | Other | HOUSE LINE |  |  |  | Corrosion |  | 1972-01-03 |  |  |  | Steel/Wrought Iron |  | CONCORD | FOUND LEAK BUBBLING IN WATER. ....LINE AND FOUND IT TO BE CUSTOMER HOUSE LINE.
30 | 76- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1976-05-21 | 1976-05-21 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP OF 10" T.P. DUE TO INSTALLATION OF STORM DRAIN BY MCDONNA CONSTRUCTION
30 | 76- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1976-05-21 | 1976-05-21 | Other | REWRAP; | Steel/Wrought Iron |  | CONCORD | REWARP OF 10" T.P. DUE TO INSTALLATION OF STORN DRAIN BY MCDONNA CONSTRUCTION
30 | 78- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1978-10-11 | 1978-10-11 |  |  | Steel/Wrought Iron |  | CONCORD | STATE HAS INSTALLED GATES TO FENCED IN INTERSCTION OF HY WAY 4 AND 24. I HAVE A HACKED A P.G. &E. CORPORATION LOCK SEE SKETCH.
30 | 80- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1980-06-03 | 1980-06-03 |  |  | Steel/Wrought Iron |  | CONCORD | REQRAP T.P. MAIN DUE TO INST. OF WATER SERVICE
30 | 80- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1980-06-03 | 1980-06-03 |  |  | Steel/Wrought Iron |  | CONCORD | REWRAP; REWRAP DUE TO INST. OF WATER SERVICE
30 | 80- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1980-06-03 | 1980-06-03 |  |  | Steel/Wrought Iron |  | CONCORD | ; REWRAP DUE TO INST. OF WATER SERVICES
30 | 76- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1976-07-28 | 1976-07-28 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP OF 10" T.P. DUE TO INSTALLATION OF SERV. LINE
30 | 74-41392-1 |  |  | 2 | Transmission |  | Valves |  |  | Other | LEAKING VALVES | 1974-07-12 | 1974-07-12 | Other | GREASED VALVES | Steel/Wrought Iron |  | ; CONCORD | FOUND STRANG ODOR IN REG. PITT. GREASED ALL 6 VALVES, AND RETESTED...J. W. 1 HR LATER ALL TEST NEGACTIVE. RETESTED REG. PITT 07.15.74 ALL TEST NEGATIVE
30 | 83-24413-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-03-31 | 1983-06-15 | Other |  | Other |  | CONCORD
30 | 76- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1976-03-17 | 1976-03-17 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP OF 10" T.P. MAIN DUE TO INSTALLATION OF STORM DRAIN BY MCDONNA CONSTRUCTION
30 | 76- |  |  | 10 | Transmission |  | Other |  | REWRAP | Other |  | 1976-05-10 | 1976-05-10 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP OF 10" T.P. DUE TO INSTALLATION OF STORN DRAIN BY MCDONNA CONSTRUCTION
30 | 76- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1976-03-11 | 1976-03-11 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP 10" T.P. DUE TO TREN DIG FOR STORM DRAIN BY CONTRACTOR
74-41570-1 |  |  |  | 0.5 | Other | HOUSELINE TO COM. DRYER | Other |  |  | Other |  | 1974-09-27 | 1974-09-27 | Other | DISCONNECTED LINE TO DRYER | Copper |  | CONCORD | ASSISTED SERVICE MAN IN FINDING LEAK ON HOUSELINE TO COMERCIAL DRYER. DISCONNECTED LINE TO SAME.
3 |  |  |  | 10 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | CONCORD
30 | 74- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1974-09-12 | 1974-09-12 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP 10" T.P. MAIN DUE TO INSTALLATION OF CASING FOR WATER LINE BY CONTRACTORS FOR C.C.C.W.D. CLEARING BETWEEN 10" T.P. MAIN AND CASING IS 16"
30 | 83-24476-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-05-04 | 1983-09-16 | Other |  | Other |  | CONCORD
30 | 78-22372-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1978-05-30 | 1982-04-14 | Other |  | Other |  | CONCORD | .2% GAS OVER MAIN SUC. TEE AREA. S' RIGHT OF DRIVEWAY BACK EDGE OF SIDE WALK MARKED WITH YELLOW PAINT
30 | 83-24486-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-05-06 | 1983-09-16 | Other |  | Other |  | CONCORD
30 | 83-24488-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-05-06 | 1983-09-16 | Other |  | Other |  | CONCORD | ;
30 | 83-24493-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-05-06 | 1983-09-16 | Other |  | Other |  | CONCORD
30 | 76-42753-1 |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1976-05-25 | 1976-05-25 | Other |  | Steel/Wrought Iron |  | CONCORD | CUSTOMER CALLED AND COMPLAINED ABOUT 2 BROWN SPOTS IN BACK YARD LAWN OVER 10" T.P. BAR TESTED OVER 10" AND FOUND ALL TESTS NEGATIVE INFORMED CUSTOMER OF SAME.
|  |  |  | 2 | Distribution Main | [6 empty] | 1975-06-10 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ;
30 | 83-24464-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-04-22 | 1983-08-29 | Other |  | Other |  | CONCORD | HAVE REPAIRED CHECK AND PIN POINT. COULD NOT PIN POINTS. BAR TESTED COUND NOT DETECT..
30 | 83-24459-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-04-22 | 1983-08-29 | Other |  | Other |  | CONCORD | HAVE... RECHECK AND BAR TESTED NO LEAKING
1 |  |  |  | 4 | Distribution Main | [6 empty] | 1975-07-21 | 1975-07-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron
30 | 78-22333-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1978-03-27 | 1983-04-05 | Other |  | Other
30 | 75-42065-1 |  |  | 0.75 | Other | METER | Meter |  |  | Material Failure |  | 1975-04-14 | 1975-04-14 | Other | METER REPLACED BY SERV. DEPT. | Steel/Wrought Iron |  | CONCORD | BARTESTED SERVICE TO MAIN, ALL TESTS NEGATIVE. COAP TESTED 5B METER AND FOUND FUSS LEAK ON LEFT SIDE ... NOTIFIED SERVIVE DEPT.
30 | 83-24468-1 |  |  | 0.75 | Other |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1983-04-28 | 1983-08-02 | Other |  | Other |  | CONCORD | REPAIRED LEAK ON CONTROL FITTING TO SERVICE AND PLUG TO SERVICE TO 3607 DUMBARTON ...
30 | 83-24469-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-04-28 | 1983-08-02 | Other |  | Other |  | CONCORD | DOWN... TO #3 A/C NEGATIVE....
30 | 83-24470-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-04-28 | 1983-08-02 | Other |  | Other |  | CONCORD | DOWN... TO #3 A/C NEGATIVE...
30 | 78-22544-1 |  |  | 00.00O | Other |  | Other |  |  | Other |  | 1978-10-25 | 1981-08-11 | Other |  | Other |  | COCNORD | .02% GAS IN WATER VALVE
30 | 78-22564-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1978-11-02 | 1980-03-20 | Other |  | Other |  | CONCORD | 40PPM IN SEWER MAN HOLE. MARKED WITH YELLOW PAINT
30 | 75- |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1975-07-31 | 1975-07-31 | Other |  | Steel/Wrought Iron |  | WALNUT CREEK | REWRAP 8" GAS MAIN.; REWRAP 8" GAS MAIN DAMAGED BY C.C.C.W.D. INSTALLING WATER MAIN
30 | 75- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1975-07-31 | 1975-07-31 | Other |  | Steel/Wrought Iron |  | WALNUT CREEK | REWRAP 10" MAIN.; REWRAP 10" GAS MAIN. DEAMAGED B. C.C.C.W.D. INSTALLING WATER MAIN
| 71-60088 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1971-03-24 | 1971-03-24 |  |  | Steel/Wrought Iron |  | CONCORD
30 | 81-23660-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Material Failure |  | 1981-11-20 | 1982-03-09 | Patch Welded |  | Steel/Wrought Iron |  | CONCORD | 10% + GAS OVER 10" T.P. LINE OLD BELL HOLE MARKED W/ YELLOW PAINT.; ARC WELD PATCH ON 10" GAS MAIN TO REPAIR GAS LEAK.
30 | 79-22814-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-04-06 | 1983-02-23 | Other |  | Other |  | CONCORD | 70PPM OVER SUC. TIE-IN AREA (BRANCH). 2' RIGHT OF DRIVEWAY BACK EDGE OF SIDE WALK AT SUC. MARKER.
30 | 83-24373-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-03-11 | 1983-06-27 | Other |  | Other |  | WALNUT CREEK
30 | 83-24370-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-03-10 | 1983-06-27 | Other |  | Other |  | WALNUT CREEK
30 | 78-21268-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1978-03-21 | 1978-06-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | WALNUT CREEK
| 71-00123 |  |  | 2 | M |  | Body of Pipe |  |  | Corrosion |  | 1971-08-04 | 1974-01-30 | Clamp |  | Steel/Wrought Iron |  | WALNUT CREEK | GOT FOUR READS OVER MAIN IN INTERSECTION FOR A DISTANCE OF 7', NO READ FROM MAIN TEE
30 | 83-24380-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-03-11 | 1983-06-27 | Other |  | Other |  | WALNUT CREEK
30 | 79-22835-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-04-19 | 1981-03-06 | Other |  | Other |  |  | .1% GAS OVER MAIN 20' RIGHT OF DRIVEWAY NEXT TO OLD LEAK MARK. .3% GAS AT ABOVE LOCATION ON BARTEST 4-2-80.; 0% GAS...3-6-81. BELL HOLE IN SIDE WALK NEAR POWER POLE CREW REPAIRS?
30 | 79-22836-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-04-19 |  | Other |  | Other |  | CONCORD | .10% GAS (FLAME-OUT) OVER MAIN 2' RIGHT OF APT. ENTRANCE WAY BACK EDGE OF SIDE WALK. .10% GAS (FLAME OUT) OVER MAIN 12' RIGHT OF APT. ENTRANCE MARKED BOTH LOCATION WITH YELLOW PAINT.
30 | 79-22837-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-04-19 |  | Other |  | Other |  | CONCORD | .10% GAS (FLAME OUT) OVER MAIN. 5' LEFT OF APT ENTRANCE WAY. NEAR POWER POLE. MAEKED WITH YELLOW PAINT.
30 | 78-44122-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1978-05-03 | 1982-03-12 | Other |  | Other |  | CONCORD | .7% GAS OVER MAIN RIGHT EDGE OF DRIVE WAY BACK EDGE OF CURB MARKED WITH YELLOW PAINT.
30 | 78-22653-1 |  |  | 0 | Other | [6 empty] | 1978-12-19 | 1980-03-19 |  |  | Other |  | CONCORD | .2% GAS ONVER MAIN 3' LEFT OF DRIVEWAY BACK EDGE OF SIDE WALK MARKED WITH YELLOW PAINT.
30 | 80-45015-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-04-08 | 1981-03-16 |  |  | Other |  | CONCORD | VERY SLIGHT READING
30 | 72-40354-1 |  |  | 0.75 | Other |  | Other |  |  | Other |  | 1972-09-06 | 1972-09-06 | Other |  | Steel/Wrought Iron |  | CONCORD | BAR-TESTED HOUSE LINE FOUND NEGATIVE. AFTER TESTED OVER & CLEAR...FOUND NEGATIVE. ADVISE... OF SAME. CHECK SERVICE TO 2 OF 24
30 | 78-22656- |  |  | 0 | Other |  | Other |  |  | Other |  | 1978-12-20 | 1980-03-21 | Other |  | Other |  | CONCORD | .02% GAS IN SEWER MAN HOLE. MARKED WITH YELLOW PAINT.
30 | 78-22579-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1978-11-16 | 1980-03-21 | Other |  | Other |  | CNCORD | .1% GAS OVER MAIN SVC. TEE AREA TO 2495 ACROSS STREET. MARKED WITH YELLOW PAINT
30 | 72-00000-0 |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1972-03-23 | 1972-03-23 | Other |  | Steel/Wrought Iron |  | CONCORD
30 | 79-22929- |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-07-27 | 1981-10-16 | Other |  | Other |  | CONCORD | .05% GAS OVER MAIN. 17' RIGHT OF SIDE WALK SUC. TEE AREA TO 3730 ACROSS STREET. MARKED WITH YELLOW PAINT.
30 | 79-22946- |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-08-03 | 1980-12-30 | Other |  | Other |  | CONCORD | .1% GAS IN WATER BOX OVER MAIN. 7' LEFT OF DRIVEWAY BACK EDGE OF SIDE WALK.
30 | 79-22963-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-08-28 |  |  |  | Other |  | CONCORD | 10% WAS (FLAME OUT) OVER MAIN BEHIND SAVINGS & LOAN CO. MARKED WITH YELLOW PAINT.
30 | 79-22964-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-08-28 |  | Other | ; | Other |  | CONCORD | 10% GAS (FLAMEOUT) IN OLD BELL HOLE. OVER MAIN. SUC. TEE AREA MARKED WITH YELLOW PAINT.
30 | 79-22962-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-08-28 | 1983-06-30 | Other |  | Other |  | CONCORD
30 | 82-46637-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-03-04 | 1983-02-22 | Other |  | Other |  | CONCORD
30 | 74-41230-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-04-22 | 1974-04-22 | Replace Pipe and/or Service |  | Other Plastic |  | CONCORD | INST. 4 1/2" PLASTIC PIPE AND #2 PLASTIC CRIMP TYPE COUPLINGS REHOOKED UP...
| 71-00000 |  |  | 8 | Transmission |  | Other |  |  |  |  | 1971-09-27 | 1971-09-27 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP DUE TO INST. OF SEWER ...CONST.
30 | 76- |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1976-08-10 | 1976-08-10 | Patch Welded |  | Steel/Wrought Iron |  | CONCORD | REWRAP 45" OF 8" T.P. GAS MAIN.; SLAVO RIGISICH CONTE. CO.
| 71-00000 |  |  | 6 | Transmission | [6 empty] | 1971-09-28 | 1971-09-28 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP DIE TO INST. OF SEWER...
| 71-00000 |  |  | 8 | Transmission | [6 empty] | 1971-10-04 |  | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP DUE TO INST. OF ELECTRIC UNDER GROUND. ..
30 | 77- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1977-04-07 | 1977-04-07 | Other |  | Steel/Wrought Iron |  | CONCORD | EXPOSED 10" T.P. GAS MAIN BY BALDWIN CONST. DUE TO INSTALLATION OF TELEPHONE DUCT.; REQRAP 2' OF 10" T.P. GAS MAIN
| 71-00000 |  |  | 8 | Transmission | [6 empty] | 1971-09-27 |  |  | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP DUE TO INST. OF SEVER LATERAL
30 |  |  |  | 8 | Transmission | [6 empty] | 1971-12-15 |  |  |  | Steel/Wrought Iron |  |  | PROSPECT 8" T.P. 64" COVER WRAP GOOD
30 | 72-00000-1 |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1972-08-22 | 1972-08-22 | Other | REWRAP; | Steel/Wrought Iron |  | CONCORD | REWRAP DUE TO INST. OF SEWER LATERAL. REQRIRED CONST.
30 |  |  |  | 8 | Transmission | [6 empty] | 1971-12-17 |  |  |  | Steel/Wrought Iron
30 | 72-00000-1 |  |  | 8 | Distribution Feeder Main |  | Other |  |  | Other |  | 1972-08-30 | 1972-08-30 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP DIE TO INST. OF E.U.G. FLAT LAND ELECT.
30 |  |  |  | 8 | Transmission | [6 empty] | 1971-12-14 |  |  |  | Steel/Wrought Iron
30 |  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron
30 |  |  |  | 8 | Transmission | [6 empty] | 1971-12-14 |  |  |  | Steel/Wrought Iron |  | ;
30 | 72-00000-1 |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1972-09-09 | 1972-09-09 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | INSTAL. SEWER LATERAL...
30 | 72- |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1972-09-07 | 1972-09-07 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP DUE TO INST. OF E.U.G. FLAT LAND ELECT.
30 | 72-00000-1 |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1972-11-02 | 1972-11-02 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP DUE TO INST. OF WATER LINE S & J ENGINERING
30 | 72-00000-1 |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1972-08-16 | 1972-08-16 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP OF 8" TRANS MAIN DUE TO INST. OF SEWER BY...
30 | 72-00000-1 |  |  | 8 | Transmission |  | Other |  |  | Other | REWRAP | 1972-08-14 | 1972-08-14 | Other |  | Steel/Wrought Iron |  | ; CONCORD | REWRAP T.M. DUE TO INST. OF SEWER LINE...
30 | 79-22969-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-09-04 | 1981-08-12 | Other |  | Other |  | CONCORD | .05% GAS OVER MAIN SUC. TEE AREA TO HOUSE ACROSS STREET. LEFT EDGE OF DRIVEWAY BACK OF RAOD WAY
30 | 79-22970-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-09-04 | 1981-08-12 | Other |  | Other |  | CONCORD | .02% GAS IN STORM DRAIN OVER MAIN. SUC. TEE ARA. 60' RIGHT OF DRIVEWAY FRONT EDGE OF CURB
30 |  |  |  | 8 | Transmission | [6 empty] | 1971-12-22 |  |  |  | Steel/Wrought Iron
30 | 72-00000-1 |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1972-08-24 | 1972-08-24 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP DUE TO INST. OF E.U.G. FLAT LAND ELECTRIC
30 | 73-00000-0 |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1973-03-27 | 1973-03-27 | Other |  | Steel/Wrought Iron |  | CONCORD | REWRAP DUE TO CONTRACTOR LOWERING PIT & ELECTRIC DUCTS. FLAT LAND ELETRIC
30 | 72-00000-1 |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1972-09-29 | 1972-09-28 | Other | REWRAP | Steel/Wrought Iron
30 | 72-00000-1 |  |  | 8 | Transmission | [6 empty] | 1972-09-22 | 1972-09-22 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP OF 8" TRANS MAIN DUE TO INST. OF SEWER BY...
30 |  |  |  | 8 | Transmission | [6 empty] | 1971-12-17 |  |  |  | Steel/Wrought Iron
30 |  |  |  | 8 | Transmission | [6 empty] | 1971-12-20 |  |  |  | Steel/Wrought Iron
30 |  |  |  | 8 | Transmission | [6 empty] | 1971-12-20 |  |  |  | Steel/Wrought Iron |  |  | 8" T.P. MAIN...MAIN & ...GOOD. PRODUCT...
30 | 72-00000-1 |  |  | 10 | Transmission | [6 empty] | 1972-08-11 |  | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP; REWRAP OF 10" TRANSM. LINE DUE TO INST. OF P.T.T. UNDERGROUND BYY FLAT LAND CONSTRUCTION.
30 | 72-00000-1 |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1972-08-16 | 1972-08-16 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP DUE TO INST. OF E.U.G. FLAT LAND ELECTRIC. CO.
30 | 73-00000-0 |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1973-03-12 | 1973-03-12 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP DUE TO INST. OF P.T.T. DUCTS AND EXLECT. U.G. FLAT LAND ELECTRIC. CO.
30 | 79-22981-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-09-12 | 1981-10-16 | Other |  | Other |  | CONCORD | .05% GAS OVER MAIN 50' RIGHT OF DRIVEWAY EDGE OF ...
30 | 74-20874-1 |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-10-25 | 1974-11-12 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CONCORD | W.M. BOX OFF SIDEWALK 1' FROM TELEPHONE POLE. FOUND 3/4" SERV. LEAKING WHERE 1" WATER LINE CROSSED SERVICE HAD BEEN HIT AND NOT WRAPPED REPLACED & SERVICE.
30 | 79-22982-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-09-12 | 1981-10-16 | Other |  | Other |  | CONCORD | 1% GAS OVER MAIN TIE-IN AREA. MARKED WITH YELLOW PAINT
30 | 79-22984-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-09-12 | 1980-09-09 | Other |  | Other |  | CONCORD | .07% GAS IN SLOT AT BASE OF RISER (INSERT) BELOW STOP COCK
30 | 79-22983-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-09-12 | 1980-09-09 | Other |  | Other |  | CONCORD | .1% GAS IN SLOT AT BASE OF RISER (INSERT) BELOW STOP COCK
30 | 87-26235-1 |  |  | 2 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 03/13/0187 | 1987-09-16 | Replace Pipe and/or Service |  | Wrought Iron |  |  | REPLACE VALVE STEML BUSHING AND O-RINGS ON EV-11 GATE VALVE 9/15/87 KENNEY
30 | 79-22989-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-09-17 | 1981-10-16 | Other |  | Other |  | CONCORD | .7% GAS IN OLD BELL HOLE OVER MAIN TIE-IN ...MARKED WITH YELLOW PAINT
30 | 79-23009-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-10-11 | 1981-10-16 | Other |  | Other |  | CONCORD | .7% GAS OVER MAIN SVC. TEE AREA 4' LEFT OF DRIVE WAY
30 | 79-22993-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-09-17 | 1981-08-12 | Other |  | Other |  | CONCORD | 100PM IN WATER VALVE NEAR END OF MAIN. RIGHT EDGE OF DRIVE WAY. MARKED IN YELLOW PAINT
30 | 79-23017-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-10-19 | 1981-10-16 | Other |  | Other |  | CONCORD | .2% GAS IN WATER BOX. LEFT EDGE OF DRIVE WAY OVER MAIN NEAR POWER POLE
30 | 73-00000-1 |  |  | 20 | Transmission |  | Other |  |  | Other |  | 1973-08-03 | 1973-08-03 | Other |  | Steel/Wrought Iron |  | CONCORD | WRAPPED 20" T.P. MAIN EXPOSED BY CONTRACTOR TO INSTALL STORM DRAIN
30 | 74-41835-1 |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1974-11-14 | 1975-01-02 | Other |  | Steel/Wrought Iron |  | CONCORD | TIGHTENED 1/4" PLUG TEE. REPAIR 1-2-75
30 | 77-43284-1 |  |  | 0.75 | Other | METER | Other |  |  | Other |  | 1977-09-13 | 1977-09-13 |  |  | Steel/Wrought Iron |  | CONCORD | CHECKED SERVICE, ALL READINGS NEGATIVE. SOAP TESTED METER FOUND LEAK ON BRASS VALVE. 1/14" ...NOTIFIED CUSTOMER O SAME
30 | 79- |  |  | 20 | Transmission |  | Other |  |  | Other |  | 1979-07-26 | 1979-07-26 |  | INSTALLING T.P. MARKER | Steel/Wrought Iron |  | CONCORD | INSTALLING T.P. MARKER; INSTALLED NEW ... MARKER
30 | 81-23438-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-01-06 | 1981-12-16 | Other |  | Other |  |  | .2% GAS IN OLD BELL HOLE OVER MAIN
30 | 79-44318-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1979-01-12 | 1979-01-12 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CONCORD | REPLACED AND CURB VALVE 3/4" STOP COCK WITH 3/4" NORG. STROM CURB VALVE. STOP COCK. WAS LEAKING NORDSTROM HAS GREASED FITTING
30 | 83-00927-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1983-03-30 | 1984-02-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | WALNUT CREEK | INSERTED ...
30 | 81-23456-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-02-09 | 1983-01-19 | Other |  | Other |  | CONCORD | ...LEFT EDGE OF DR. WAY...PWR. POLE...
30 | 81-23454-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-02-06 | 1983-01-19 | Other |  | Other |  | CONCORD | .05% GAS OVER MAIN FRONT EDGE OF CURB, LEFT EDGE OF DRIVEWAY ENTRANCE. SVC. TEE...TO 1780 ACROSS ST. SERVICE TO 1780 HAS BEEN REPLACED AS OF...LATE.
30 | 79-23074-1 |  |  | 0 | Other | [6 empty] | 1979-11-16 | 1980-06-23 | Other |  | Other |  | CONCORD | .10% GAS (FLAME OUT) 60' LEFT OF DRIVE WAY 3' BACK OF CURB. MARKED WITH YELLOW PAINT.
30 | 81-00601-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-04-06 | 1983-02-22 | Other |  | Other |  | CONCORD | I MADE OUT A C-TAG TO FREASE VALVE ...ALSO REPLACE LID.
30 | 82-46952-1 |  |  | 0.02 | Other |  | Other |  |  | Other |  | 1982-11-23 | 1983-03-18 | Other |  | Other |  | CONCORD | UPGRADE FROM 76-21827
30 | 79-23006-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-10-05 | 1980-09-16 | Other |  | Other |  | CONCORD | 70PPM. OVER MAIN SVC. TEE AREA 4' RIGHT OF DRIVEWAY 1' BACK OF SIDEWAY.
30 | 80-45099-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-09-12 | 1981-03-06 | Other |  | Other |  | CONCORD | .04% AT BOX UNDER SIDEWALD AND 0% AFTER SECOND READ
| 09-43430- |  |  | 0.5 | Branch Service |  | Plastic Tee Cap |  |  | Construction Defect |  | 2009-09-30 | 2009-09-30 | Tee Fused Over Defect - Plastic |  | Aldyl A (Tan or Gray) |  | CONCORD | SEE BELOW; TEE FUSED OVER DEFECT @"T" O/M
| 04-23074-1 |  |  | 0.5 | Branch Service |  | Plastic Tee Cap |  |  | Construction Defect |  | 2004-08-09 | 2009-09-30 | Tee Fused Over Defect - Plastic |  | Aldyl A (Tan or Gray) |  | CONCORD | SEE BELOW; TEE FUSED OVER DEFECT @ "T" O/M
30 | 76- |  |  | 20 | Transmission |  | Other |  |  | Other |  | 1976-12-21 | 1976-12-21 | Other | INST. T.P. MAIN MARKERS | Steel/Wrought Iron |  | CONCORD | INST. T.P. MAIN MARKER; REPLACED OLD T.P. MAIN MARKERS WITH NEW TYPE WARNING SIGNS AT 9 LOCATIONS IN CONCORD. SEE SKETCH 5 MARKERS AT STREET CROSSING. 4 MARKERS IN R/W AND BACK YARDS.
30 | 76- | 191 |  | 20 | Transmission |  | Other |  |  | Other |  | 1976-12-21 | 1976-12-21 | Other | INST. T.P. MAIN MARKERS | Steel/Wrought Iron |  | CONCORD | INST. T.P. MAIN MARKERS; REPLACED OLD T.P. MAIN MARKER WITH NEW TYPE WARNING SIGNS, AT 11 LOCATIONS IN CONCORD. SEE SKETCH 9 MARKERS AT STREET CROSSING,... MARKERS AT CREEK AND ONE IN OPEN FIELD
30 |  |  |  | 8 | Transmission | [6 empty] | 1971-12-24 |  |  |  | Steel/Wrought Iron
30 |  |  |  | 8 | Transmission | [6 empty] | 1971-12-21 |  |  |  | Steel/Wrought Iron |  | ;
30 | 72-00000-1 |  |  | 8 | Transmission | [6 empty] | 1972-09-12 | 1972-09-12 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP; REWRAP OF 8" TRANS MAIN DUE TO INST. OF P.T.T. UNDERGROUND BY FLAT LAND CONST.
30 | 73-00000-0 |  |  | 8 | Transmission |  | Other |  |  | Other |  | 03/23/0193 | 1973-03-23 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP; REWRAP DUE TO CONTRACTOR LOWERING P.T.T. & ELECTRIC DUCTS. FLAT LAND ELECT.
30 |  |  |  | 8 | Transmission | [6 empty] | 1971-12-28 |  |  |  | Steel/Wrought Iron
30 |  |  |  | 8 | Transmission | [6 empty] | 1971-12-28 |  |  |  | Steel/Wrought Iron
30 | 72-00000-1 |  |  | 8 | Transmission |  | Other |  | REWRAP | Other |  | 1972-08-28 | 1972-08-28 | Other |  | Steel/Wrought Iron |  | CONCORD | REWRAP DUE TO INST. OF SEWER LATERAL
30 | 81-23538-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-05-14 | 1983-04-05 | Other |  | Other |  | CONCORD
30 |  | 191 |  | 20 | Transmission | [8 empty] | Other | REWRAPPED EXPOSED. T.P. 191 | Steel/Wrought Iron |  | CONCORD | MAIN EXPOSED BY WEST VALLEY CONSTRUCTION CO. REWRAPPED MAIN. OK
30 | 79-22668-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-01-03 | 1980-12-31 | Other |  | Other |  | CONCORD | .10% GAS (FLAME OUT) OVER MAIN SVC TEE AREA RIGHT EDGE OF DRIVEWAY BACK AT SIDEWALD NEXT TO OLD LEAK MARK
30 | 79-22670-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-01-03 | 1980-12-31 | Other |  | Other |  | CONCORD | 10% GAS IN CENTER OF DRIVEWAY 6' FROM GARAGE DOOR. 10% GAS IN OLD LEAK MARK OUT FRONT.
30 | 78-22398-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1978-08-30 | 1980-12-31 | Other |  | Other |  | CONCORD | .03% GAS OVER TEE AREA. RIGHT EDGE OF DRIVEWAY 2' BACK OF SIDEWALK. MARKED WITH YELLOW PAINT.
30 | 78-22397-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1978-08-30 | 1980-12-31 | Other |  | Other |  | CONCORD | .5 GAS SVC TEE AREA. RIGHT EDGE AT DRIVEWAY BACK EDGE OF SIDEWALL. .1% GAS OVER SVC 6' BACK OF SIDEWALK. MARKED WITH YELLOW PAINT.
30 | 80-23434-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-12-31 | 1981-11-19 | Other |  | Other |  | CONCORD | 40% LEL READING IN WATER BOX 15' RIGHT OF DRIVEWAY. 0% """ CREW REPAIRS?
30 | 78-44058-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1978-11-17 |  | Other |  | Other |  | CONCORD | RE-CHECKED OLD GAS LEAK REPORTED AT THIS LOCATION WITH STEVE BECK AND CARL STROMBERG (D.E.T. BERKELEY). FUTURE ANALYSIS BY MR. STROMBERG WILL DETERMIN IF THIS IS GAS NATIVE TO THIS PARTICULAR AREA.
30 | 82-23993-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-05-13 | 1983-05-31 | Other |  | Other |  | CONCORD | I BELIEVE THIS WAS CONFIRMED NATIVE GAS.
30 | 82-23991-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-05-13 | 1983-05-31 | Other |  | Other |  | CONCORD | THIS IS NATIVE GAS
30 | 76- |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1976-03-22 | 1976-04-01 | Other |  | Steel/Wrought Iron |  | CONCORD | GREASED VALVE AND EXERCISED
30 | 79-22672-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-01-03 | 1981-12-31 | Other |  | Other |  | CONCORD | .1% GAS AT CRACK IN SIDWALK ACROOS STREET FROM 3101 FITXPATRICH DR. MARKED WITH YELLOW PAIN. NOTE: SEE ATTACHED GRAPH CHART.
30 | 79-22671-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-01-03 | 1980-12-31 | Other |  | Other |  | CONCORD | .10% GAS (FLAME-OUT) AT OLD LEAK MARK. OUT FROM .1% GAS IN CRAN IN DRIVEWAY 16' FROM GARAGE DOOR. FOLLOW UP: NATIVE GAS. 0% P.G.&E. GAS WITH CHROMATOGRAPHY 1-5-79. FOLLOW UP NOTE: SEE ATTACHED GRAPH CHART
30 | 78-22400-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1978-08-30 | 1980-04-14 | Other |  | Other |  | CONCORD | UPGRADED ON 79-44737; .1% GAS OVER MAIN 6' LEFT OF DRIVEWAY BACK EDGE OF SIDEWALK .03% GAS IN OLD BELL HOLE LEFT EDGE OF DRIVEWAY. MARKED WITH YELLO PAINT. CHECKED FOR NATIVE GAS PER CARL STROMBERG. THIS IS NATIVE DAS PER (D.E.R.)
30 | 76-42651-1 |  |  | 2 | Transmission |  | Valves |  |  | Other | NEED GREASE | 1976-02-02 | 1976-02-11 | Other |  | Steel/Wrought Iron |  | CONCORD | VALVE E-58 GREASED AND RECHECKED ALL TEST NEGATIVE
80 | 77-43356-1 |  |  | 0.75 | Other | METER (REG.) | Regulator |  |  | Material Failure |  | 1977-10-31 |  |  |  | Steel/Wrought Iron |  | CONCORD | A; INSPECTION PLUG LEAKING UNABLE TO STOP SAME. NEED SERV. MAN TO GAUGE REGULATOR
30 | 78-22430-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1978-09-13 | 1983-09-20 | Other |  | Other |  | CONCORD | .2% GAS OVER MAIN 8' RIGHT OF DRIVEWAY BACK EDGE OF SIDE WALK. MAKED WITH YELLOW PAINT
30 | 80-46019-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-10-01 | 1981-03-20 | Other |  | Other |  | CONCORD | UPGRADED FROM 78-22432; MADE TESTS WITH J.W. ALONG MAIN AND SERVICE TIE-IN. ALL WITH NEGATIVE READS.
30 | 79-22661- |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-01-02 | 1980-03-21 | Other |  | Other |  | CONCORD | 70PPM IN OLD BELL HOLE OVER MAIN SVC. TEE AREA (R/R) RIGHT EDGE OF DRIVEWAY FRONT EDGE OF SIDEWALK.
30 | 79-22667-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-01-03 | 1982-11-24 | Other |  | Other |  | CONCORD | .05% GAS OVER SVC. 9' BACK OF CURB. .03% GAS OVER SVC. AT EDGE OF CURB. MARKED WITH YELLOW PAINT.
30 | 79-22664-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-01-03 | 1981-12-15 | Other |  | Other |  | CONCORD | .02% GAS OVER MAIN TIE-IN AREA MARKED WITH YELLOW PAINT
30 | 79-22663- |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-01-02 | 1980-03-21 | Other | ; | Other |  | CONCORD | .05 GAS OVER MAIN FRONT EDGE OF CURB. CENTER OF DRIVEWAY. MARKED WITH YELLOW PAINT
30 | 79-22662-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-01-02 | 1981-12-16 | Other |  | Other |  | CONCORD | 100PPM OVER MAIN TIE-IN AREA. 12" RIGHT OF DRIVEWAY FRONT EDGE OF CURB
30 | 76-21656-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1976-05-11 | 1983-09-20 | Other |  | Other |  | CONCORD | .1% GAS IN WATER VALVE FRAME & COVER 15'INTO ELKWOOD CT. MARKED W/ YELLOW PAINT. 0% 9-20-83 R.O. CONNER. 50PPM IN WATER VALVE 15' INTO ELKWOOD CT. LEAK RECHECKED 8-8-77 R.O. CONNER
30 | 73-40648-1 |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-04-26 | 1973-05-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CONCORD | ; FOUND 3/4" SERV. LEAKING REPLACED 3/4" SERV. WITH 1/2" P/R SERV. STOP LEAKAGE. (INSERT)
30 | 74-41416-1 |  |  | 2 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-07-05 | 1974-07-25 | Other |  | Steel/Wrought Iron |  | CONCORD | H.P. OK. CUSTOMER HAS BAD LEAK. ON 2" ...SAID HE MOVED ... HELP FROM P.G.&E. TO REPAIR OR REPLACE. NOTIFIED... HOUSE LINE IN ...OVER.; ...SERVE..PLANT.; LOCATE, EXPOSED AND CLAMP LEAK ...
30 | 73-20556-1 |  |  |  | Other |  | Other |  |  | Other |  | 1973-10-05 | 1973-10-17 | Other |  | Other |  | CONCORD | NO LEAKAGE BELOW STOPCOCK; SOAED OUT...FITTING AND ...TIGHTENED SCREWS AND STOPPED LEAK.
30 | 73-20557-1 |  |  |  | Other |  | Other |  |  | Other |  | 1973-10-05 | 1973-10-16 | Other |  | Other |  | CONCORD | A; NO LEAKAGE BELOW STOPCOCK; SOAPED OUT 14 METERS & 2 REG. FOUND...SMALL LEAK ON...STOPPED LEAK. COULD FIND NO ...LEAKS.
30 | 73-20558-1 |  |  |  | Other |  | Fitting |  |  | Other |  | 1973-10-05 |  | Other |  | Steel/Wrought Iron |  | CONCORD | FOUND 1 1/4" UNION LEAKING, STOPPED LEAK. FOUND...FOUND LEAK BY SOAPING OIL FITTING IN CURB BOXES.
30 | 82-46727-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-05-11 | 1982-07-06 | Other |  | Other |  | CONCORD | THIS HAS BEEN ...
30 | 82-24049- |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-05-08 | 1982-06-07 | Other |  | Other |  | CONCORD | 100% GAS OVER MAIN IN OLD BELL HOLE NEXT TO CURB MTRS. MIGRATION TOWARD BLDGS. MARKED WITH YELLOW PAINT. STRONG AREA ODOR.L FOUND GAS LEAK ON HOUSE LINE TO "STARTLITE BAR" SHUT METER OFF AND ...NO LEAK ON SERVCE PROSSER.
30 | 73-20549-1 |  |  |  | Other |  | Other |  |  | Other |  | 1973-10-05 | 1973-10-23 | Other |  | Other |  | CONCORD | ...FOUND TOP OF CURB METER LEAKING. TIGHTENED SCREWS TO METER TIP AND STOPPED LEAKING. AT CURB METER
30 | 73-20551-1 |  |  |  | Other |  | Regulator |  |  | Other |  | 1973-10-05 | 1973-10-23 | Other |  | Steel/Wrought Iron |  | CONCORD | SAOPED AT METER...
30 | 73-20550-1 |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1973-10-05 | 1973-12-13 | Other |  | Steel/Wrought Iron |  | CONCORD | SOAPED METER AND ....AT CURB METER
30 | 73-20552-1 |  |  |  | Other |  | Other |  |  | Other |  | 1973-10-05 | 1973-10-23 | Other |  | Other |  | CONCORD | COAPED OUT METER + ALL FITTINGS FOUND ...STOPPED LEAK.
30 | 79-22897-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-06-07 | 1982-04-14 | Other |  | Other |  | CONCORD | A; .50PPM IN WATER VALVE IN STREET
30 | 75- |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1975-10-03 | 1975-10-03 | Other |  | Steel/Wrought Iron |  | CONCORD | WRAP GAS MAIN DUE TO INST. OF SEWER
30 | 80-23380-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-06-09 | 1981-10-16 | Other |  | Other |  | CONCORD | NOTE: FOUND LEAKAGE OVER MAIN NEAR AT#2. P.T.4.T LINE RUNDS PARALLEL TO 4" GAS MAIN IN STREET...
30 | 75- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1975-06-23 | 1975-06-23 | Other |  | Steel/Wrought Iron |  | CONCORD | REWRAP; REWRAP DUE TO INST. OF WATER MAIN
| 71-00000 |  |  | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | CONCORD | REWRAP 10" MAIN; REWRAP TRANSMISSION 10" EXPOSED BY C.C.C.W.D. TO CUT OFF WATER LINES
30 | 90-33033-1 |  |  | 6 | Distribution Feeder Main |  | Other Welds |  |  | Other | WELD | 1990-11-27 | 1991-05-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | CONCORD | ON 6" T.P. MAIN ON WELD. WELDED PATCH OVER 301
30 | 77-21894-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1977-02-17 | 1980-09-11 | Other |  | Other |  | CONCORD | .07% GAS 5' BACK OF CURB, RIGHT SIDE OF HOUSE SIDEWALK, OVER MAIN.
30 | 74- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1974-01-28 | 1974-01-28 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP DUE TO INST. OF SEWER LATER. AGAIN DUCT ....PLOW 537 HAYWARD 4044. NOTE: T-MAIN IS 30" DEEP IN THIS AREA...INSPECTION ...SHEET OVER TO BE CUT 26" FOR NEAR CURBS AND GUTTER.
30 | 73-00000-1 |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1973-08-14 | 1973-08-14 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP DUE TO INST. OF WATER HYDRANT. NEXT TO A.W. ROOT BEER ON MARKET ST.
30 | 74- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1974-01-22 | 1974-01-22 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD; | REWRAP DUE TO INST. OF SEWER LATERAL
30 | 74- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1974-03-18 | 1974-03-18 | Other |  | Steel/Wrought Iron |  | CONCORD | REWRAP DUE TO INST. OF WATER SEWER.
30 | 80- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1980-08-23 | 1980-08-23 | Patch Welded |  | Steel/Wrought Iron |  | CONCORD | REWRAP DUE TO INST. OF SEWER LATERAL
30 | 71-00000- |  |  | 12 | Transmission |  | Other |  |  | Other |  | 1971-12-15 | 1971-12-15 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD; | REWRAP 12" TRANSMISSION DUE TO INST. OF SEWER LEAN COVER CONST.
| 71-00002- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-01-11 | 1971-01-11 | Patch Welded |  | Steel/Wrought Iron |  | CONCORD | OUR 2" MAIN CROSS...
30 | 78-43895-1 |  |  | 0.75 | Other | LINE TO IP CHART | Other |  | HP PIN OFF TEE | Other | LEAKING CAP | 1978-06-30 | 1978-07-28 | Other | REDOPED CAP & RETIGHTENED | Steel/Wrought Iron |  | CONCORD | SEE ATTACHED SHEET. REDOPED CAP AND TIGHTENED
|  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | WALNUT CREEK
|  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1975-05-02 |  |  |  | Steel/Wrought Iron |  | WALNUT CREEK
30 | 74- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1974-07-17 | 1974-07-17 | Other | STAKING T.P. MAIN | Steel/Wrought Iron |  | CONCORD
30 |  |  |  | 4 | Transmission | [6 empty] | 1976-06-30 |  |  |  | Steel/Wrought Iron |  | CONCORD | VFC...W/O TERMINAL REG. USED TO PROTECT CASING VENT ON 8" CASING AROUND 4" T.P. RAIL. RAOD
30 |  |  |  | 8 | Other | CASING | [9 empty] | Steel/Wrought Iron |  | CONCORD | PROSPECTED CASING DEPTH FOR FUTURE CITY STREET RE-CONSTRUCTION
80 | 74- |  |  | 4 | Transmission |  | Other |  |  | Other |  | 1974-07-10 | 1974-07-10 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP DUE TO INST. OF P.T.T. DUCTS ...
30 | 73- |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1973-02-16 | 1973-02-16 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP DUE TO INST. OF WATER MAIN.
30 | 73- |  |  | 6 | Transmission |  | Other |  | REWRAP |  |  | 1973-05-04 | 1975-05-04 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP OF 6" T.P. GM. DUE TO INST. OF WATER MAIN BY C.C.W.D
30 | 73- |  |  | 6 | Transmission |  | Other |  |  | Other |  | 1973-02-15 | 1973-02-15 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | WRAPPED 6" T.P. GAS MAIN AND BORED BY WATER COMPANY TO MAKE DOG LEG ON WATER MAIN. ;
30 | 72-00000-1 |  |  | 6 | Transmission | [6 empty] | 1972-07-11 |  |  |  | Steel/Wrought Iron |  |  | PROSPECT MAIN DEPTH
30 | 72-00000-1 |  |  | 6 | Transmission | [6 empty] | 1972-07-10 |  |  |  | Steel/Wrought Iron
30 | 75-41883-1 |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-07-23 | 1975-02-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CONCORD | 10% GAS NEAR 24 MPN SIGN OVER MAIN. CERVICE TO 2500 ALMOND WAS LEAKING NEAR TEE. REPAIR SERV.
30 | 74-41879-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-07-23 | 1975-02-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CONCORD | .4% GAS 4' LEFT OF WATER BOX, 100PPM IN WATER BOX. FOUND 3/4" SERV LEAKING RERUN 1/2" PL. SERV. INSERT.
30 |  |  |  | 4 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | CONCORD | PROSPECTED MAIN DEPTH FOR FUTURE CITY STREET RE-CONSTRUCTION
1 |  |  |  | 6 | Transmission |  | Valves |  |  | Material Failure |  | 1975-04-21 | 1975-04-21 | Other |  | Steel/Wrought Iron |  |  | SMALL LEAK AT VALVE NEEDS GREASE GUN
30 | 75-42333-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1975-10-03 | 1976-07-29 | Other |  | Steel/Wrought Iron |  | CONCORD | VALVE; 10% (FLAME OUT) GAS IN GAS VALVE FRAME & COVER COLSEST TO EAST ST.; GREASED VALVE 4-29-95 AND 10-03-95 ...LEAKS AT 20:00AM AND 2:00PM ...NEED ...TO REPAIR.
30 | 76- |  |  | 4 | Other | VALVE | Valves |  |  |  |  | 1976-06-16 |  |  |  | Steel/Wrought Iron |  | CONCORD | GREASED VALVE, BUT UNABLE TO STOP LEAK. NEED CROM FOR REPAIR THIS IS A BY PASS VALVE
1 | 75- |  |  | 6 | Transmission |  | Valves |  |  | Material Failure |  | 1975-04-17 | 1975-04-18 | Other |  | Steel/Wrought Iron |  |  | NOTE: LIFTED VALVE FRAME AND COVERS TO GRADE OF STREET VALVE. C-28
1 | 75- |  |  | 4 | Transmission |  | Valves |  |  | Material Failure |  | 1975-04-18 | 1975-04-22 | Other |  | Steel/Wrought Iron |  | ; ; | NOTE: BROUGHT TWO VALVE FRAME AND COVERS UP TO GRADE THESE VALVES WE TO ABANDON REG. PIT. THEY SHOULD BE ELIMINATED IN FUTURE; LIFTED VALVE FRAME SO IT COULD BE GREASED.
30 | 74-41228-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-04-19 | 1974-04-19 | Clamp |  | Steel/Wrought Iron |  | CONCORD | FOUND POSITION...WATER BOXES AND OVER MAIN. J.CLARK FOUND LEAK, 4-19-74 AND INST. #1-2" TEMP LEAK CLAMP
30 | 74-41237-1 |  |  | 0.75 | Service |  | Tap Connection |  |  | Other |  | 1974-04-19 | 1974-04-30 | Other |  | Steel/Wrought Iron |  | CONCORD | FOUND & FIX LEAK...TEE CAPS...STOP LEAKAGE...
30 | 78-22445-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1978-09-25 | 1980-09-29 | Other |  | Other |  | CONCORD | .3% GAS OVER MAIN 25' LEFT OF DRIVEWAY BACK EDGE OF SIDE WALK. MARKED WITH YELLOW PAINT.
30 | 78-22444-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1978-09-25 | 1981-10-16 | Other |  | Other |  | CONCORD | 40PPM IN SEWER MAN-HOLE
30 | 72-20443-1 |  |  |  | Other | M | [5 empty] | 1972-11-27 |  |  |  | Steel/Wrought Iron |  | CONCORD; | RECHED ALL HOLES. DRILL IN GROUND FOUNF NO GAS READING
30 | 73-00000-1 |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 00/00/1973 |  | Other |  | Other |  | CONCORD | CUT OFF SERVICE
30 | 83-24616-1 |  |  | 0.75 | Other |  | Fitting |  |  | Construction Defect |  | 1983-10-12 | 1984-05-11 | Other |  | Steel/Wrought Iron |  | CONCORD | 10% (FLAME OUT) LOCATED & PIN-POINT ..MARKED...(SAME LOCATION.; ...
30 | 76-21450-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-02-05 | 1976-04-02 | Patch Welded |  | Steel/Wrought Iron |  | CONCORD | .05 GAS IN WATER BOX, SERVICE TEE TO 1730 6TH ST. ODOR IN ARIR. ISNT. 3 X 6 PACH ON MAIN (3")
30 | 86-47979-1 |  |  | 0.5 | Other | N | Body of Pipe |  |  | Digin |  | 1986-08-14 | 1986-08-14 | Replace Pipe and/or Service |  | Aldyl A (Tan or Gray) |  | CONCORD
30 | 81-23544-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-05-21 | 1983-04-06 | Other |  | Other |  | CONCORD
30 | 82-46611-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-02-22 | 1983-01-19 | Other |  | Other |  | CONCORD
30 | 73-20591-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-10-18 | 1973-10-26 | Clamp |  | Steel/Wrought Iron |  | CONCORD; | FOUND LEAK ON 2" MAIN INST. 2" X 4" AND A 2 X 10 SKINNER CLAMP 10-26-73 VERY CLOSE TO TEL-POLE.; INSTALLED (2) 2" PERMANENT REPAIR CLAMPS
30 | 80-46115-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-12-30 | 1981-04-01 | Other |  | Other |  | CONCORD | 10% GAS (FLAME OUT) OVER MAIN SVC. TEE AREA 8' LEFT OF DRIVEWAY BACK EDGE OF SIDEWALK MARKED WITH YELLOW PAINT.; NO READINGS W/ INDICATOR.
30 | 79-22709- |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-01-31 | 1980-03-24 | Other |  | Other |  | CONCORD | .03% GAS OVER MAIN 10' RIGHT OF DRIVEWAY FRONT EDGE OF CURB. MARKED WITH YELLOW PAINT
30 | 72-40241-1 |  |  | 2 | Other |  | Other |  |  | Construction Defect |  | 1972-04-06 | 1972-04-06 | Other |  | Steel/Wrought Iron |  | CONCORD | BAR TESTED ON & FOUND NEGATIVE. ALSO TESTED 2" HOUSE LINE FOUND NEGATIVES. HELPED SERVICE MAN REPAIR LEAKS ON HOUSE LINE.
30 | 74-41479-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-08-21 | 1974-08-21 | Other |  | Other Plastic |  | CONCORD | UPON ARRIVAL FOUND THAT SCHOOL MAINTENANCE HAD ...OVER 1 1/4" PLASTIC HOUSE LINE.
30 | 74-60465-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1974-07-26 |  | Other |  | Other | ; | CONCORD | .6% GAS 4' FROM ST. SIGN 1-22-76. 100PPM GAS 4' FROM ST. SIGN. LEAK RE-CHECKED 7-12-77...; .4% GAS OVER MAIN NEXT TO STREET SIGN.; FRONT EDGE OF CURB NEAR OLD LEAK MARK. MARKED WITH YELLOW PAINT.
30 | 78-22482-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1978-10-12 | 1983-01-19 | Other |  | Other |  | CONCORD | 50 PPM IN SEWER MAN HOLE
30 |  |  |  | 10 | Distribution Feeder Main | [8 empty] | Other |  | Steel/Wrought Iron |  | CONCORD | EXPOSED 10" D.F.M. FOR DENTH- FUTURE STORM DRAIN CONSTRUCTION IN AREA. INST. E.T.S. AT LOC. 2.
30 | 74- |  |  | 0.25 | Other |  | Body of Pipe |  |  | Corrosion |  |  | 1974-02-11 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CONCORD | REPLACED 1/4" TUBING WITH 3/4" WRAP PIPE TO GAUGE BOX
30 | 78-22483-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1978-10-13 | 1982-02-13 | Other |  | Other |  | CONCORD | ; 50PPM IN P.G.&E. GAS MARKER. RIGHT EDGE OF DRIVEWAY 3' BACK OF CURB
30 | 76-21486-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1976-02-23 | 1981-08-12 | Other |  | Other |  | CONCORD | .07% GAS 2' RIGHT OF DRIVEAY. LEAK RE-CHECK 8-2-77...
1 | 74-41098-1 |  |  | 2 | Other |  | Fitting |  |  | Other |  | 1973-02-14 | 1973-02-15 |  |  | Steel/Wrought Iron |  | CONCORD | ; FOUND + REPAIRED SMALL LEAK ON MANIFOLD. SOAPED OUT MANIFORD + FOUND LEAK. ALSO BAR TESTED SER. TEST. NEGATIVE.
30 | 81-23531-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-04-30 | 1983-02-22 | Other |  | Other |  | CONCORD | DOWN GRADE TO #3 LEAK
30 | 79-44816-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-05-02 | 1982-04-13 | Other |  | Other |  | CONCORD | 50PPM IN SEWER MAN HOLE. 0%...4-14-82 R.O. CONNOR; 40PPM WITH LAME DUCTS. SLIGHTLY DOWN WITH HYDROGEN...CHAGED FILTER (1-2% READ WITH J.W. ON 4% L.E.L.)
30 | 80-44981-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-03-21 | 1981-01-26 | Other |  | Other |  | CONCORD
30 | 78-22518-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-05-02 | 1980-06-27 | Other |  | Other |  | CONCORD | ; 40PPM IN SEWER MAN HOLE; SLIGHTLY BENNETH...
30 | 78-22632-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1978-12-14 | 1981-04-10 | Other |  | Other |  | CONCORD | 0% OLD BELL HOLE NEAR STREET SIGN. 0% GAS OLD BELL HOLE OVER SVC. TEE TO 15% ACROSS STREET OLD LEAK MARKS. CREW REPAIRES
30 | 73-20602-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Corrosion |  | 1973-10-25 | 1974-06-03 | Other |  | Steel/Wrought Iron |  | CONCORD | FOUND CAP LEAKING ON BLOW OFF NIPPLE AT END OF 2" MAIN. ; INST. 2" L.S.F. ON END OF 2" MAIN CUT OFF 1' OF END...LEAKING
30 | 76-21741-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-08-25 | 1977-03-10 | Clamp |  | Steel/Wrought Iron |  | CONCORD | FOUND AND MARKED SPOT WHERE GAS READINGS ARE...WAS AT.; CUSTOMER COMPLAINT; INST. 1 2" LEAK CLAMP
30 | 73-00000-0 |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1973-05-23 |  | Other |  | Steel/Wrought Iron |  | CONCORD | REPLACED SERVICE CUT OFF SERVICE
30 | 79-22737- |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-02-23 | 1980-12-31 | Other |  | Other |  | CONCORD | 50PPM IN SEWER MAN HOLE; NOTE: THERE IS A LEAK OVER MAIN AT 14:56 BARBIS WAY ACROSS FROM SEWER LOCATION.
30 | 79-22736- |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-02-23 | 1980-12-30 | Other |  | Other |  | COCNORD | .02% GAS OVER MAIN TIE-IN AREA. 5' OUT FROM CURB MARKED WITH YELLOW PAINT.
30 | 79-22727- |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-02-15 | 1980-03-21 | Other |  | Other |  | CONCORD | 70PPM IN SEWER MAN HOLE. RIGHT EDGE OF DRIVEWAY.
30 | 79-22728- |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-02-15 | 1980-03-21 | Other |  | Other |  | CONCORD | .02% GAS OVER MAIN. 5' BACK OF ROAD. 15' RIGHT OF DRIVE WAY. MARKED WITH YELLOW PAINT
30 | 79-22731- |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-02-15 | 1980-03-21 | Other |  | Other |  | CONCORD | .2% GAS IN WATER BOX. NEXT TO CURB METER'S. LEAK RE-CHECKED NOTE BUILDING TORN DOWN VACANT LOT.; NOTE: .03% GAS IN CURB METER NEAR CUSTOMER HOUSE LINE. MADE OUT CHANGE
30 | 79-22745- |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-02-28 | 1982-01-18 | Other |  | Other |  | CONCORD | .10% GAS (FLAME OUT) IN E.T.S VALVE COVER OVER MAIN 18' LEFT OF DRIVEWAY 11' BACK OF ROAD WAY.
30 | 72-00000-1 |  |  | 8 | Transmission | [6 empty] | 1972-07-28 |  | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | REWRAP; REWRAP OF 8" TRANS MAIN DUE TO INST. OF SEWER LINES BY DUTTER CONSTRUCTION
30 | 81-23546-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-05-22 | 1982-04-14 | Other |  | Other |  | CONCORD | 0% ...SVC. R/R AT 4024 AND 4511 NEXT DOOR CREW REPAIRS...
30 | 79-22766- |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-03-08 | 1980-03-21 | Other |  | Other |  | CONCORD | .05% GAS ON RISER BELOW STOP COCK BUBBLES COMMING THROUGH WRAP.
30 | 79-22747- |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-02-28 | 1980-03-24 | Other |  | Other |  | CONCORD | .3% GAS IN WATER BOX LEFT...EDGE OF SIDEWALK
30 | 79-22750-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-03-01 | 1981-08-12 | Other |  | Other |  | CONCORD | 10% AS (FLAME OUT) OVER MAIN SVC. TEE AREA MARKED WITH YELLOW PAINT.
30 | 79-22757- |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-03-21 | 1980-03-21 | Other |  | Other |  | CONCORD | .05% GAS OVER MAIN SVC. TEE AREA RIGHT EDGE OF DRIVEWAY BACK EDGE OF SIDEWALK
30 | 79-22756-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-03-05 | 1982-02-12 | Other |  | Other |  | CONCORD | 10% GAS (FLAME OUT) OVER MAIN. 12' RIGHT OF DRIVEWAY. BACK EDGE OF SIDEWALK. 27. GAS LEFT EDGE OF DRIVEWAY 70PPM IN STORM DRAIN NEARBY.
30 | 79-22764-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-03-05 | 1982-02-23 | Other |  | Other |  | CONCORD | .03% GAS OVER MAIN TIE-IN AREA AT BASE OF OLD STREET SIGHT FIXTURE. FRONT EDGE OF SIDEWALK
30 | 79-22763-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-03-05 | 1982-02-23 | Other |  | Other |  | CONCORD | .02% GAS IN OLD BELL HOLE, OVER MAIN
30 | 79-22762-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-03-05 | 1981-10-16 | Other |  | Other |  | CONCORD | 10% GAS (FLAME OUT) OVER MAIN. 5' RIGHT OF DRIVEWAY. FRONT EDGE OF SIDEWALK. 10% GAS (FLAME OUT) OVER MAIN. 2' RIGHT OF WALK WAY FRONT EDGE OF CURB (IN PARK STRIP)
30 | 79-22759- |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-03-05 | 1980-03-21 | Other |  | Other |  | CONCORD | 50PPM OVER SVC. 2' FROM RISER EDGE OF GARAGE AND DRIVEWAY
30 | 79-22784- |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-03-13 | 1980-03-21 | Other |  | Other |  | CONCORD | 70PPM OVER MAIN TIE-IN AREA BACK EDGE OF SIDEWALK CENTER OF DRIVEWAY ENTRANCE
30 | 79-22758- |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-03-05 | 1980-03-21 | Other |  | Other |  | CONCORD | 50 PPM IN SEWER MAN-HOLE
80 | 74-41119-1 |  |  | 0.75 | Single Service |  | Other |  |  | Other |  | 1974-02-22 | 1974-02-22 | Other |  | Steel/Wrought Iron |  | CONCORD | BAR TESTED MAIN AND SERVICE FOUND NEGATIVE. TESTED SEWER AND WATER BOXES FOUND NEGATIVES
30 | 74-60433-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1974-09-27 |  | Other |  | Other |  | CONCORD | CLEARED; .02 GAS OVER SERVICE EDGE OF SIDEWALK AND LAWN. LEAK..; RECHECKED 10/27/79 30PPM OVER SERVICE AND MAIN TEE; 100 PPM OVER SERVICE AT EDGE OF SIDEWALK AND LAWN; .02% OVER SVC. EDGE OF WALK WAY AND LAEN LEAK RE-CHECK 9-29-80
30 | 82-46682-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-04-19 | 1983-04-05 | Other |  | Other |  | CONCORD
30 | 78-43990-1 |  |  | 10 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1978-10-13 | 1978-10-13 | Other |  | Steel/Wrought Iron |  | CONCORD | FOUND LEAK ON 1/2" VALVE PLUG. REPAIRED BY TIGHTEN UP 1/2" PLUG
30 | 75-41928-1 |  |  | 0.75 | Other |  | Other |  |  | Other |  | 1975-01-24 | 1975-01-24 | Other |  | Steel/Wrought Iron |  | CONCORD | BAR TESTED HOUSE LINE IN PARKING AREA FOUND NEGATIVES. NOTIFIED ...OF SAME
30 | 73-20488-1 |  |  | 0.75 | Distribution Feeder Main |  | Fitting |  |  | Material Failure |  | 1973-08-08 | 1973-08-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PLEASANT HILL | PROBED SERVICE FOUND NEGATIVE READS LEAK IN VALVE BOX. NEED SKETCH OF SERVICE DO TO REG. PIT. SERVICE OFF 10" T.P. MAIN. SCHOOL HAS TO BE SHUT DOWN TO REAPIR LEAKAGE 8-16-73. BY PASSED T.P. REG PIT. TO REPAIR LEAKING 3/4" UNION IN T.P. VALVE PIT.- ALSO INSTALLED 17" X 30" BOX EXT. ON VALVE PIT. 8-17-73
30 | 74- |  |  | 8 | Transmission | [8 empty] | Other |  | Steel/Wrought Iron |  | PLEASANT HILL | INST. 3/4" GAUGE TAPS. TESTED 650 PSIG FOR 1 HOUR
30 | 79-23148-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-12-18 | 1980-12-02 |  |  | Other |  | PLEASANT HILL | 50PPM OVER SVC. 12' BACK OF CURB 4' RIGHT OF DRIVEWAY
30 | 79-22888-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-05-22 | 1982-04-14 | Other |  | Other |  | CONCORD | .02%GAS IN SEWER MAN HOLE COVER
30 | 75- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1975-06-08 | 1976-06-08 | Other | INSTALLING T.P. MARKERS | Steel/Wrought Iron |  | WALNUT CREEK | INSTALLED 10 NEW TYPE MAIN MARKERS OVER 10" T.P. SEE SKETCH
30 | 81-23577-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-07-16 | 1983-07-15 | Other |  | Other |  | CONCORD
30 | 81-23578-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-07-16 | 1983-07-15 | Other |  | Other |  | CONCORD
30 | 71-00000-0 |  |  | 10 | Transmission |  |  |  |  | Other |  | 1971-12-21 | 1971-12-21 | Other |  | Steel/Wrought Iron |  | CONCORD | REWRAP DUE TO INST. OF SEWER MAIN
30 | 72-00000-0 |  |  | 12 | Transmission |  | Other |  |  | Other |  | 1972-01-03 | 1972-01-03 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD | WRAPPED 12" TRANSMISSION MAIN ...BY MARTIN BLDS. TO INSTAL SEWER
30 | 82-46708-1 |  |  | 8 | Other |  | Other |  |  | Other |  | 1982-04-30 | 1983-03-25 | Other |  | Other |  | CONCORD
30 | 74- |  |  | 2 | Distribution Main | [6 empty] | 1974-02-20 | 1974-02-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CONCORD | ALTERED 2" MAIN FOR NEW STORM DRAIN LINE. INST. 2' LINE STOPPER FITTINGS 18' FROM P/L
30 | 77-22214-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1977-10-06 | 1981-10-16 | Other |  | Other |  | CONCORD | .05% GAS..BACK EDGE OF SIDE WALK. RIGHT EDGE OF DRIVEWAY SVC. BRANCH AREA
30 | 77-22215-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1977-10-11 | 1981-10-16 | Other |  | Other |  | CONCORD
30 | 77-22211-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1977-10-03 | 1981-10-16 | Other |  | Other |  | CONCORD | ... 1' BACK OF CURB. RIGHT EDGE OF DRIVEWAY OVER SVC.
30 | 82-46615-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-03-06 | 1983-06-30 | Other |  | Other |  | CONCORD; | DOWN GRASE TO #2 LEAK .07%
30 | 77-22206-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1977-10-03 | 1983-02-22 | Other |  | Other |  | CONCORD | .02% GAS... 4' LEFT OF DRIVEWAY FRONT OF SIDEWALK SVC TEE AREA.
30 | 75-42151-1 |  |  |  | Distribution Feeder Main | [6 empty] | 1975-03-06 | [5 empty] | CONCORD | .03 GAS IN WATER BOX. BAR TESTED AREA FOUND NO LEAKAGE.
30 | 81-23534-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-05-04 | 1983-04-05 | Other |  | Other |  | CONCORD;
30 | 81-23519-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1981-04-23 | 1983-02-22 | Other |  | Other |  | CONCORD | ;
30 | 80-23330-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-03-25 | 1980-03-25 | Other |  | Other |  | CONCORD | ...LIP CENTER OF DRIVE WAY AND ALONG BASE OF GARAGE DOOR
30 | 80-23326-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-03-25 | 1980-03-27 | Other |  | Other |  | CONCORD | LEAK REPAIRED ON 80-23325; ...
30 | 80-23327-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-03-25 | 1980-03-25 | Other |  |  | O; | CONCORD | LEAK REPAIRED ON 80-23325;... CLEARED ON # 80.23325
30 | 80-23328-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-03-25 | 1980-03-27 | Other |  | Other |  | CONCORD
30 | 80-23329-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-03-25 | 1980-03-27 | Other |  | Other |  | CONCORD
30 | 75 |  |  | 20 | Transmission | [7 empty] | 1975-11-04 | Other |  | Steel/Wrought Iron |  | CONCORD
| 75- |  |  | 20 | Transmission |  | Other |  |  | Other |  | 1975-05-13 | 1975-05-13 | Other | INSTALLING MAIN MARKERS | Steel/Wrought Iron |  | ; CONCORD
30 | 79-23025-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-10-29 | 1981-10-16 | Other |  | Steel/Wrought Iron |  | CONCORD
30 | 74-20952-1 |  |  | 0 | Transmission |  | Other | Other |  | Other |  | 1974-11-06 | 1980-11-05 | Other |  | Steel/Wrought Iron |  | CONCORD
30 | 80-46010-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-09-18 | 1981-01-09 | Other |  | Other |  | CONCORD
30 | 83-47199-1 |  |  | 0.75 | Other |  | Fitting |  |  | Corrosion |  | 1983-05-09 | 1983-05-13 | Replace Pipe and/or Service |  | Steel/Wrought Iron
30 | 79-23035-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-11-05 | 1981-11-18 | Other |  | Other |  | CONCORD
30 | 79-23051-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-11-07 | 1981-12-02 | Other |  | Other |  | CLAYTON
30 | 83-47255-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1983-08-31 | 1983-08-31 | Other |  | Other Plastic |  | W.C.
30 | 75- |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1975-08-04 | 1975-08-04 | Other |  | Steel/Wrought Iron |  | CONCORD
30 | 78- |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1978-12-08 | 1978-12-08 | Other | REWRAP | Steel/Wrought Iron |  | W.C.
30 | 30- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1978-12-08 | 1978-12-08 | Other |  | Steel/Wrought Iron |  | W.C.
30 | 84-47500-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1984-07-11 | 1984-07-11 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | WALNUT CREEK
30 | 74-00389-1 |  |  | 2 | Distribution Main | TRANSMISSION | [5 empty] | 1974-09-09 | 1974-09-11 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | CONCORD
| 95-23486-1 |  |  | 2 | Distribution Main |  | Valves |  |  | Other |  | 1995-08-17 | 1996-08-07 | Other |  | Steel/Wrought Iron |  | P.H.
30 |  |  |  | 10 | Transmission |  | Other |  |  | Other | REWRAP | 1979-01-16 | 1979-01-16 | Other | REWRAP | Steel/Wrought Iron |  | WALNUT CREEK
1 | 81-46486-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1981-10-29 | 1981-10-29 | Replace Pipe and/or Service |  | Other Plastic |  | W.C.
30 | 82-24144-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-12-13 | 1983-03-22 | Other |  | Other |  | WC
30 |  |  |  | 1 | Other |  | Other | Other |  | Other |  | 1981-11-16 | 1981-11-16 | Other |  |  |  | WALNUT CREEK
30 | 74- |  |  | 10 | Transmission |  | Other | Other |  | Other |  | 1974-10-24 |  | Other | REWRAP | Steel/Wrought Iron |  | WC
30 | 73-00000-0 |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1973-05-18 | 1973-05-18 | Other | REWRAP | Steel/Wrought Iron |  | CONCORD
30 | 74- |  |  |  | Transmission | [7 empty] | 1974-10-25 | Other |  | Steel/Wrought Iron |  | CONCORD
30 | 82-24154-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1982-12-23 | 1983-01-04 | Other |  | Other |  | WC
| 71-00000 | [10 empty] | 1971-09-28 |  | Other | REWRAP |  |  | WC
30 | 82-24168-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-12-27 | 1983-05-17 | Other |  | Other |  | WC
30 | 74- |  |  | 6 | Transmission |  | Other | Other |  | Other |  | 1974-01-24 |  | Other |  | Steel/Wrought Iron |  | WC
30 | 79-44774-1 |  |  | 1 | Service |  | Other |  | 1"x2" PL SERV. TEE | Material Failure |  | 1979-11-20 | 1979-11-20 | Replace Pipe and/or Service |  | Other Plastic |  | WC | REPLACED SERV TEE
30 | 80-23165-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-01-02 | 1982-11-24 | Other |  | Other |  | WALNUT CREEK
30 | 83-24218-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-02-01 | 1983-09-14 | Other |  | Other |  | WALNUT CREEK
| 83-24219- |  |  | 0 | Other |  | Other |  |  | Other |  |  | 1983-02-11 | Other |  | Other |  | WALNUT CREEK
|  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  | 1980-08-19 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | W.C.
|  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  | 1980-08-19 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  |  |  | 6 | Other |  | Other |  |  | Other |  | 1980-08-20 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  | 1980-08-20 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron
30 | 80-44078-1 |  |  | 0 | Gathering |  | Other |  |  | Other |  | 1980-06-27 | 1981-10-16 | Other |  | Copper |  | WC
30 | 83-24216-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-02-01 | 1983-07-01 | Other |  | Other |  | WC
30 | 83-24182-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-01-03 | 1983-04-25 | Other |  | Other |  | WC
30 | 76-42668-1 |  |  | 0.5 |  | FORM MARKED "C" | Other |  |  | Other |  | 1976-02-27 | 1976-02-27 | Other |  | Copper |  | WC
30 | 83-24226-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-02-04 | 1983-04-25 | Other |  | Other |  | WC
|  |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  | 1980-07-24 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1980-07-23 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron
30 | 83-24230-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-02-10 | 1983-04-25 | Other |  | Other |  | WC
1 |  |  |  | 10 | Transmission | [7 empty] | 1972-02-25 |  |  | Steel/Wrought Iron |  | WC
30 | 75- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1975-08-25 | 1975-08-25 | Other |  | Steel/Wrought Iron |  | WC
30 | 74- |  |  | 10 | Transmission |  | Other | Other |  | Other |  | 1974-11-14 | 1974-11-14 | Other | REWRAP | Steel/Wrought Iron |  | W.C.
30 | 00- |  |  | 10 | Transmission |  | Other | Other |  | Other |  | 1974-05-17 |  | Other |  | Steel/Wrought Iron |  | W.C.
30 | 74- |  |  | 10 | Transmission |  | Other |  |  | Other |  | 1974-09-19 | 1974-09-19 | Other | REWRAP | Steel/Wrought Iron |  | W.C.
30 | 74 |  |  | 10 | Transmission |  | Other | Other |  | Other |  | 1974-07-24 | 1974-07-24 | Other | REWRAP | Steel/Wrought Iron |  | LIVERMORE
30 | 74- |  |  | 8 | Transmission |  | Other | Other |  | Other |  | 1974-07-24 | 1974-07-24 | Other | REWRAP | Steel/Wrought Iron |  | LIVERMORE
30 | 75- |  |  | 10 | Transmission |  | Other | Other |  | Other |  | 1975-04-08 | 1975-04-08 | Other | REWRAP | Steel/Wrought Iron |  | WC
30 | 75- |  |  | 10 | Transmission |  | Other | Other |  | Other |  | 1975-05-05 | 1975-05-05 | Patch Welded |  | Steel/Wrought Iron |  | WC
30 | 75- |  |  | 10 | Transmission |  | Other | Other |  | Other |  | 1975-04-07 | 1975-04-07 | Other | REWRAP | Steel/Wrought Iron |  | W.C.
30 | 75- |  |  | 10 |  | FORM MARKED "TP" | Other | Other |  | Other |  | 1975-05-20 | 1975-05-20 | Other |  | Steel/Wrought Iron |  | WALNUT CREEK
30 | 75- |  |  | 8 | Transmission |  | Other | Other |  | Other |  | 1975-04-07 | 1975-04-07 | Other | REWRAP | Steel/Wrought Iron |  | W.C.
30 | 74- |  |  | 10 | Transmission |  | Other | Other |  | Other |  | 1974-04-10 | 1974-09-16 | Other | REWRAP | Steel/Wrought Iron |  | W.C.
30 | 78-22298-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1978-02-01 | 1983-01-19 | Other |  | Other |  | WALNUT CREEK
30 | 76- |  |  | 10 | Transmission |  | Other | Other |  | Other |  | 1976-04-02 | 1976-04-02 | Other |  | Steel/Wrought Iron |  | W.C.
30 |  |  |  | 2 | Other | [7 empty] | 1976-05-06 | Other |  | Steel/Wrought Iron |  | WALNUT CREEK
30 | 74- |  |  | 8 | Transmission |  | Other | Other |  | Other |  | 1974-09-19 | 1974-09-19 | Other |  | Steel/Wrought Iron |  | W.C.
30 | 73-00000-1 |  |  | 6 | Transmission |  | Other | Other |  | Other |  | 1973-06-11 |  | Other |  | Steel/Wrought Iron |  | WC
30 | 75-42322-1 |  |  | 20 | Transmission |  | Other | Other |  | Other | BLOWOFF | 1975-09-12 | 1975-09-12 | Other |  | Steel/Wrought Iron |  | W.C.
30 | 75- |  |  | 20 | Transmission |  | Other | Other |  | Other |  | 1975-11-20 | 1975-11-20 | Other | REPLACE T.P. MARKER | Steel/Wrought Iron |  | W.C.
30 | 76-42852-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-08-20 | 1976-08-23 | Patch Welded |  | Steel/Wrought Iron |  | WALNUT CREEK
30 | 74-00403-1 |  |  | 2 | Distribution Feeder Main |  | Girth Weld |  |  | Construction Defect |  | 1974-10-04 | 1975-01-03 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | WALNUT CREEK
30 | 75- |  |  | 20 | Transmission |  | Other | Other |  | Other |  | 1975-05-07 | 1975-05-07 | Other | RESTAKING T.P. | Steel/Wrought Iron |  | WC
30 | 75- |  |  | 20 | Transmission |  | Other | Other |  | Other |  | 1975-12-15 | 1975-12-15 | Other | INSTALLING T.P. MARKERS | Steel/Wrought Iron |  | W.C.
30 | 75- |  |  | 20 | Transmission |  | Other | Other |  | Other |  | 1975-11-19 | 1975-11-19 | Other | REWRAP | Steel/Wrought Iron |  | W.C.
30 | 79-23058-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1979-11-13 | 1980-03-11 | Other |  | Other |  | WALNUT CREEK
30 | 79-23060-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1979-11-13 | 1980-03-11 | Other |  | Other |  | WALNUT CREEK
30 | 79-23061-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1979-11-13 | 1980-03-11 | Other |  | Other |  | WALNUT CREEK
30 | 78-22310-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1978-02-09 | 1981-02-23 | Other |  | Other |  | WALNUT CREEK
30 | 87-48169-1 |  |  | 0.75 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1987-06-23 | 1987-07-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | W.C.
30 | 87-48169-1 |  |  | 0.5 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-06-23 | 1987-07-01 | Other |  | Steel/Wrought Iron |  | WALNUST CREEK
30 | 83-24331-1 |  |  | 20 | Transmission |  | Fitting |  |  | Material Failure |  | 1983-06-02 | 1983-06-24 | Other |  | Steel/Wrought Iron |  | WALNUT CREEK
30 | 83-24316-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-04-27 | 1983-05-04 | Other |  | Other |  | WALNUT CREEK
30 | 82-24000-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1982-05-18 | 1983-04-04 | Other |  | Other |  | W.C.
30 | 83-24237-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1983-02-14 | 1983-08-02 | Other |  | Other |  | WC
30 | 83-24243-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1983-02-15 | 1983-08-02 |  |  | Other |  | WC
30 | 75- |  |  | 20 | Transmission |  | Other | Other |  | Other |  | 1975-05-20 | 1975-05-20 | Other | INSTALLING MAIN MARKERS | Steel/Wrought Iron |  | W.C.
30 | 83-24271-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1983-02-17 | 1983-05-11 | Other |  | Other |  | WC
30 | 83-24279-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1983-02-18 | 1983-05-05 | Other |  | Other |  | WC
30 | 83-24280-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1983-02-18 | 1983-05-05 | Other |  | Other |  | WC
30 | 78- |  |  | 20 | Transmission |  | Other | Other |  | Other |  | 1978-07-03 | 1978-07-03 |  | REWRAP | Steel/Wrought Iron |  | W.C.
30 | 74-41147-1 |  |  | 0.75 | Service |  | Tap Connection |  |  | Corrosion |  | 1974-03-08 | 1974-03-10 | Other |  | Steel/Wrought Iron |  | WC
30 | 79-23070-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1979-11-15 | 1981-06-08 | Other |  | Other |  | WALNUT CREEK
30 | 82-46884-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1982-09-17 | 1982-09-27 | Other |  | Other |  | WALNUT CREEK | 100% GAS ...; ... 16' TP MAIN; NOTE: NO ODOR PRESENT. NATIVE ... BY LOS ALTOS... ; REQUEST THAT CARL TAKE SAMPLE.;
30 | 83-24288-1 |  |  | 0 | Service |  | Other |  |  | Other |  | 1983-02-22 | 1983-05-11 | Other |  |  |  | WC
30 | 74-41116-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other | CAP LEAKING | 1974-02-20 | 1974-02-22 | Other | RETIGHTENED CAP | Steel/Wrought Iron |  | W.C.
30 | 79-23063-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1979-11-15 | 1980-07-03 | Other |  | Other |  | WALNUT CREEK
30 | 82-24038-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1982-05-18 | 1983-05-17 | Other |  | Other |  | WC
30 | 83-24249-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1983-02-17 | 1983-04-25 | Other |  | Other |  | WC
30 | 82-23847-1 |  |  | 16 | Transmission |  | Valves | Other |  | Material Failure |  | 1982-04-05 | 1982-05-14 | Other |  | Steel/Wrought Iron |  | WALNUT CREEK
30 | 75- |  |  | 20 | Transmission |  | Other | Other |  | Other |  | 1975-05-20 | 1975-05-20 | Other | INSTALLING MAIN MARKERS | Steel/Wrought Iron |  | W.C.
30 | 79-23079-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1979-11-26 | 1980-06-04 | Other |  | Other |  | WALNUT CREEK
30 | 83-24350-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1983-02-24 | 1983-08-02 | Other |  | Other |  | WALNUT CREEK
30 | 83-24299-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1983-02-24 | 1983-05-06 | Other |  | Other |  | WC
30 | 74- |  |  | 20 | Transmission | [6 empty] | 1973-09-20 | 1974-02-19 | Other |  | Steel/Wrought Iron |  | W.C.
30 | 74- |  |  | 20 | [7 empty] | 1973-10-15 | 1974-02-19 | Other |  | Steel/Wrought Iron
30 | 79-23082-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1979-11-26 | 1980-10-08 | Other |  | Other |  | WALNUT CREEK
30 | 80-46039-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1980-10-08 |  | Other |  | Other |  | WALNUT CREEK
30 | 73-40472-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-01-15 | 1973-01-17 | Patch Welded |  | Steel/Wrought Iron |  | W.C.
30 | 79-23088-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1979-11-27 | 1981-12-02 | Other |  | Other |  | WALNUT CREEK
30 | 73-00000-1 |  |  | 20 | Transmission |  | Other | Other |  | Other |  | 1973-07-31 |  | Other |  | Steel/Wrought Iron |  | WC
30 | 79-23084-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1979-11-26 | 1980-09-15 | Other |  | Other |  | WALNUT CREEK
30 | 79-23093-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1979-11-28 | 1980-10-06 | Other |  | Other |  | WALNUT CREEK
30 | 79-23094-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1979-11-28 | 1980-10-06 | Other |  | Other |  | WALNUT CREEK
30 | 79-23096-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1979-11-28 | 1980-10-06 | Other |  | Other |  | WALNUT CREEK
30 | 80-23220-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1980-01-21 | 1980-12-04 | Other |  | Other |  | WALNUT CREEK
30 | 74-00410-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-10-04 | 1974-12-24 | Patch Welded |  | Steel/Wrought Iron |  | WALNUT CREEK
30 | 76-42606-1 |  |  | 0.75 | Other |  | Fitting |  |  | Material Failure |  | 1976-01-09 | 1976-01-12 | Other |  | Steel/Wrought Iron |  | WALNUT CREEK
30 | 79-23102-1 |  |  | 0 | Other |  | Other | Other |  | Other |  | 1979-12-04 | 1981-12-02 | Other |  | Other |  | WALNUT CREEK
30 |  |  |  | 0.75 | Other | P | [6 empty] | 1972-11-14 |  |  | Steel/Wrought Iron |  | WALNUT CREEK
30 | 86-22765-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1983-03-30 | 1986-05-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | W.C.
30 | 80-43924-1 |  |  | 0.75 | Other |  | Other |  |  | Other |  | 1980-02-01 | 1983-12-08 |  |  |  |  | WC
30 | 74-41895-1 |  |  | 0.75 | Other |  | Physical/Mechanical Joint |  |  | Other |  |  | 1975-02-21 | Other |  | Steel/Wrought Iron |  | WALNUT CREEK
30 | 86-22833-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1986-08-05 | 1986-10-28 | Clamp |  | Steel/Wrought Iron |  | W.C.
30 | 87-46373-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1987-10-09 | 1987-10-09 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | WALNUT CREEK
30 | 73-00533-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-01-23 | 1974-02-04 | Clamp |  | Steel/Wrought Iron |  | WALNUT CREEK
| 05-43278- |  |  | 0.5 | Service |  | Body of Pipe | Fusion Joint |  | Material Failure |  | 2005-10-01 | 2005-10-01 |  |  | Steel/Wrought Iron |  | WALNUT CREEK | REPL. RISER
| 05-43278- |  |  | 0.5 | Service |  | Body of Pipe | Fusion Joint |  | External Corrosion |  | 2005-10-01 | 2005-10-01 |  |  | Steel/Wrought Iron |  | WC
| 05-43278- |  |  | 0.5 | Service |  | Body of Pipe | Fusion Joint |  | Material Failure |  | 2005-10-01 | 2005-10-01 |  |  | Steel/Wrought Iron |  | WC
|  |  |  | 8 | Distribution Feeder Main |  | Other |  |  | Other |  | 1985-03-25 |  | Other |  | Steel/Wrought Iron |  | WALNUT CREEK
30 | 81-44639-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Material Failure |  | 1981-12-11 | 1981-12-11 | Replace Pipe and/or Service |  | Copper |  | WC
30 | 86-46150-1 |  |  | 0.5 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces | DIGIN | 1986-12-04 | 1986-12-04 | Replace Pipe and/or Service |  | Other Plastic |  | WALNUT CREEK
3 | 84-45303-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1984-06-19 | 1984-06-19 | Replace Pipe and/or Service |  | Other Plastic |  | WALNUT CREEK
|  |  |  | 0.5 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  |  | 1987-04-20 | Replace Pipe and/or Service |  | Copper |  | WALNUT CREEK
30 |  |  |  | 8 | Transmission | [6 empty] | 1972-01-15 | 1972-01-15 |  |  | Steel/Wrought Iron
30 | 86-46083-1 |  |  | 0.5 | Service |  | Fitting |  |  | Material Failure |  | 1986-10-23 | 1986-10-23 | Other |  |  | FORM MARKED "A" | WC
30 | 82-44720-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1982-02-26 | 1982-02-26 | Other |  | Other Plastic |  | W.C.
30 | 87-46364-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1997-09-28 | 1987-09-28 | Other |  | Aldyl A (Tan or Gray) |  | ALAMO
30 | 86-46104-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1986-11-07 | 1986-11-07 | Replace Pipe and/or Service |  | Aldyl A (Tan or Gray) |  | WALNUT CREEK
30 | 79-43532-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces | DIGIN | 06/15/0000 | 1979-06-15 | Replace Pipe and/or Service |  | Other Plastic |  | WALNUT CREEK
30 | 86-46146-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1986-12-03 |  | Replace Pipe and/or Service |  | Other Plastic |  | ALAMO
| 05-26102-1 |  |  | 4 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2005-11-09 | 2007-05-03 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ALAMO
|  |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1981-04-21 | 1981-04-21 | Other |  | Steel/Wrought Iron
|  |  |  | 4 | Distribution Feeder Main |  | Other |  |  | Other |  |  |  | Other |  |  |  | ALAMO | NO LEAKAGE. MAIN INSP ONLY.
30 | 82-44780-1 |  |  | 1.25 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1982-06-17 | 1982-06-17 | Replace Pipe and/or Service |  | Other Plastic |  | DAN.
| 99-36000 |  |  |  | Transmission | [10 empty] | Steel/Wrought Iron |  | DANVILLE
| 79-43750-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-11-28 | 1979-11-30 | Other |  | Other Plastic |  | ALAMO
|  |  |  | 2 | Distribution Main |  | Other | Other |  | Other |  |  |  | Other
30 | 74-00691-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-09-19 | 1975-01-07 | Clamp |  | Steel/Wrought Iron |  | DANVILLE
30 | 94-26093-1 | [10 empty] | 16/12/1994 | [5 empty] | DANVILLE | THIS LEAK MUST HAVE BEEN REPAIRED BECAUSE WE COULD NOT GET ANY READINGS AT ALL WITH FLAME PAK & J.W. AREA CLEAR.
30 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1985-09-27 | 1985-09-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | DANVILLE
|  |  |  | 2 | Other |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron |  | DANVILLE
|  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron
30 | 86-46013-1 |  |  | 0.5 | Other |  | Body of Pipe |  |  | Digin |  | 1986-08-04 | 1986-08-04 | Replace Pipe and/or Service |  | Aldyl A (Tan or Gray) |  | DANVILLE
30 | 74-41778-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-08-05 | 1974-08-07 | Other |  | Steel/Wrought Iron |  | DANVILLE
30 | 86-46065-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Digin |  | 1986-10-16 | 1986-10-16 | Replace Pipe and/or Service |  | Aldyl A (Tan or Gray) |  | DAN
30 | 75-20498-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-06-02 | 1976-01-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | DANVILLE
|  |  |  | 8 | Transmission | [10 empty] | Other Plastic |  | DANVILLE
30 | 77-42881-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1977-07-20 | 1977-07-20 | Clamp |  | Steel/Wrought Iron |  | DAN.
30 | 75-20501-1 |  |  | 0.75 | Service |  | Girth Weld |  |  | Construction Defect |  | 1975-06-04 | 1976-01-29 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | DANVILLE
30 | 74-00729-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Construction Defect |  | 1974-09-26 | 1975-01-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | DANVILLE
30 | 87-46391-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Digin |  | 1987-10-29 | 1987-10-29 | Replace Pipe and/or Service |  | Aldyl A (Tan or Gray) |  | DANVILLE
| 94-46071-1 |  |  | 1.25 |  | S | Tap Connection |  |  | Material Failure |  | 1994-05-10 | 1994-05-11 | Other |  | Aldyl A (Tan or Gray) |  | DANVILLE | INSTALLED (1) 11/4" SERVICE PUNCH TEE REPAIR KIT FOR PERMANENT REPAIR
30 | 73-41252-1 |  |  | 2 | Distribution Feeder Main |  | Other Welds |  |  | Corrosion |  | 1973-06-06 | 1973-06-07 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | DANVILLE
30 | 77-42790-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1977-03-23 | 1977-03-23 | Clamp |  | Steel/Wrought Iron |  | DANVILLE
30 | 79-21650-1 |  |  | 6 | Distribution Main |  | Other | Other |  | Other |  | 1979-10-22 | 1981-02-23 | Other |  | Steel/Wrought Iron |  | DANVILLE
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  |  | Replace Pipe and/or Service |  | Steel/Wrought Iron
30 | 79-21620-1 |  |  | 0.5 |  | N | Fitting |  |  | Construction Defect |  | 1979-10-25 | 1980-05-19 | Other |  | Other Plastic |  | SAN RAMON VLY BLVD
30 | 78-20801-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-10-09 | 1978-08-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PITTSBURG
3 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1982-04-09 | Other |  | Steel/Wrought Iron
30 | 78-20810-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1978-01-11 | 1978-03-29 | Clamp |  | Steel/Wrought Iron |  | PITTS
30 | 75-00217-1 |  |  | 0.75 | Other | RETIRED SERVICE TEE | Fitting |  |  | Corrosion |  | 1975-10-29 | 1976-03-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PITTSBURG
30 | 72-40100-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-12-20 | 1972-12-21 | Clamp |  | Steel/Wrought Iron |  | PITTSBURG
| 79-40863- |  |  |  | Other |  | Other |  |  | Other |  | 1979-09-10 | 1979-09-11 | Other
30 | 82-21329-1 |  |  | 0.5 | Service |  | Girth Weld |  |  | Material Failure |  | 1982-02-19 | 1982-05-11 | Replace Pipe and/or Service |  | Other Plastic |  | W. PITTS. CA
30 |  |  |  | 4 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1976-10-15 | Other |  | Steel/Wrought Iron |  | PITTSBURG
|  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | W. PITTS.
|  |  |  | 4 | Transmission | [6 empty] | 1976-09-17 |  |  |  | Steel/Wrought Iron |  | PITTSBURG | NO LEAK. NEW SERVICE.
1 |  |  |  | 4 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
30 | 77-20766-1 |  |  | 0.75 | Other |  | Fitting |  |  | Construction Defect |  | 1977-03-04 | 1977-03-07 | Other |  | Steel/Wrought Iron |  | PITTS
30 | 74-20148-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-02-12 | 1974-03-01 | Clamp |  | Steel/Wrought Iron |  | PITTSBURG
30 | 74-20149-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-02-12 | 1974-03-01 | Clamp |  | Steel/Wrought Iron |  | PITTSBURG
30 | 74-20174-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-02-19 | 1974-03-08 | Patch Welded |  | Steel/Wrought Iron |  | PITTSBURG
30 | 81-21264-1 |  |  | 0.5 | Service |  | Other |  |  | Other |  | 1981-06-04 | 1982-04-15 | Replace Pipe and/or Service |  | Copper |  | PITTSBURG
3 |  |  |  | 3 | Distribution Main |  | Valves |  |  | Other |  |  | 1982-05-14 | Other |  | Steel/Wrought Iron |  | PITTSBURG
30 | 83-21391- |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1983-01-13 | 1983-06-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PITTSBURG CA
30 | 83-21471-1 |  |  | 8 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1983-04-19 | 1984-02-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PITTS. CA | INSTALLED NEW VALVE IN LINE
30 | 74-40171-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-01-31 | 1974-02-01 | Patch Welded |  | Steel/Wrought Iron |  | PITTSBURG
30 |  |  |  | 12 | [8 empty] | 1991-08-23 |  |  | Steel/Wrought Iron |  | PITT | SLOT HOLES TO CHECK DEPTH OF 12" MAIN
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1984-03-30 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PITTSBURG
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1984-04-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PITTSBURG
30 | 82-21353-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1982-04-21 | 1984-03-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PITTS. CA | MAIN CUT-OFF ON GM 4323754
30 | 83-21442-1 |  |  | 0.75 | Other |  | Longitudinal Weld |  |  | Construction Defect |  | 1983-02-24 | 1983-10-01 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | PITTS. CA
3 |  |  |  | 6 | Distribution Main |  | Other |  |  | Other |  |  | 1984-03-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron
3 |  |  |  | 6 | Distribution Main |  | Other |  |  | Other |  |  | 1984-03-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PITTSBURG
3 |  |  |  | 6 | Distribution Main |  | Other |  |  | Other |  |  | 1984-03-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PITTSBURG
3 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1984-03-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PITTSBURG
3 |  |  |  | 6 | Distribution Main |  | Other |  |  | Other |  |  | 1984-03-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PITTSBURG
30 | 75-20403-1 |  |  | 2 | Distribution Feeder Main | [6 empty] | 1975-04-02 |  |  |  | Steel/Wrought Iron |  | PITTS | THE MAIN WAS BARTESTED AND RETESTED WITH FLAMNAK. NO LEAKAGE FOUND. TEST RESULTS NEGATIVE.
30 | 73-20103-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-10-02 | 1973-10-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PITTSBURG
30 | 73-40140-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-10-03 | 1973-10-10 | Clamp |  | Steel/Wrought Iron |  | PITT
30 | 80-40987-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1980-03-14 | 1980-07-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PITTSBURG CA
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTS
1 |  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG
1 |  |  |  | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG
30 | 83-21439- |  |  | 2 | Distribution Main |  | Fitting |  |  | Corrosion |  | 1983-10-01 | 1983-10-05 | Other |  | Steel/Wrought Iron |  | PITTSBURG
30 | 74-40176-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-03-13 | 1974-03-14 | Clamp |  | Steel/Wrought Iron |  | PITTSBURG
30 | 72-40070-1 |  |  | 8 | Distribution Feeder Main |  | Girth Weld |  |  | Corrosion |  | 1972-02-10 | 1972-02-17 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | PITTSBURG
30 | 83-21479- |  |  | 0.5 | Service | [6 empty] | 1983-05-11 |  | Other |  | Other Plastic |  | PITTS. CA
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1981-07-29 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PITTSBURG
30 |  |  |  | 24 | Transmission |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron
30 |  |  |  | 12 | Distribution Feeder Main | [7 empty] | 1988-06-20 |  |  | Steel/Wrought Iron |  |  | INSTALLED AN ETS
30 |  |  |  | 12 | Transmission |  | Other |  |  | Other |  |  | 1977-04-07 | Other |  | Steel/Wrought Iron |  | PITTSBURG
30 | 79-20987- |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1979-04-06 | 1979-10-11 | Other |  | Steel/Wrought Iron |  | PITTS
30 |  |  |  | 24 | Transmission |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron
30 | 73-40117-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-03-21 | 1973-03-22 | Clamp |  | Steel/Wrought Iron |  | PITTSBURG
30 |  |  |  | 12 | Transmission |  | Other |  |  | Other |  | 1972-08-03 |  | Other
30 |  |  |  | 24 | Transmission |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron |  | PITTSBURG
30 | 76-20713- |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-06-03 | 1976-07-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PITTS
30 | 81-21223-1 |  |  | 4 | Distribution Feeder Main |  | Girth Weld |  |  | Construction Defect |  | 1981-03-19 | 1982-02-02 | Other |  | Steel/Wrought Iron |  | PITTS CA
30 | 74-00717-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-09-25 | 1974-12-05 | Clamp |  | Steel/Wrought Iron |  | SAN RAMON
30 | 74-41807-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-09-03 | 1974-09-03 | Clamp |  | Steel/Wrought Iron
30 | 71-00040-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1971-09-08 | 1973-02-22 | Patch Welded |  | Steel/Wrought Iron |  | PITTS
30 | 71-00042-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1971-09-08 | 1973-01-22 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | PITTS
30 | 71-00041-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  |  | 1973-02-08 | Patch Welded |  | Steel/Wrought Iron |  | PITTS
30 | 81-21227-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1981-03-20 | 1982-01-29 | Patch Welded |  | Steel/Wrought Iron |  | ANTIOCH | 4" STL MAIN IN VERY POOR CONDITION. SHOULD BE RE-PLACED SOON AS POSSIBLE 1-29-82
30 | 81-21225-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1981-03-20 | 1982-02-03 | Other |  | Steel/Wrought Iron |  | ANTIOCH
30 | 82-41210-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1982-02-10 | 1982-02-10 | Patch Welded |  | Steel/Wrought Iron |  | ANTIOCH
30 | 79-20985-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1979-03-30 | 1980-12-18 | Patch Welded |  | Steel/Wrought Iron |  | ANTIOCH
30 | 80-40922-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1980-02-27 | 1980-03-03 | Patch Welded |  | Steel/Wrought Iron |  | ANTIOCH
30 | 79-20983- |  |  | 4 | Distribution Feeder Main |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1979-03-30 | 1979-05-18 | Other |  | Steel/Wrought Iron |  | ANT.
30 | 76-20718-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-06-03 | 1978-12-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PITTS
30 | 75-00209-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1975-10-28 | 1975-12-15 | Patch Welded |  | Steel/Wrought Iron |  | ANTIOCH
30 | 76-20716- |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-06-03 | 1976-07-15 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | ANTIOCH
30 | 76-20715- |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-06-03 | 1976-07-19 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | ANTIOCH
30 |  |  |  | 4 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
30 |  |  |  | 4 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
30 | 83-21342-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-05-30 | 1983-06-22 | Clamp |  | Steel/Wrought Iron
30 | 82-21342- |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1982-03-22 | 1983-06-22 | Clamp |  | Steel/Wrought Iron |  | PITTS CA
30 | 76-20714- |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-06-03 | 1976-07-15 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | PITTSBURG
30 | 77-40503-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1977-01-31 | 1977-03-23 | Clamp |  | Steel/Wrought Iron |  | PITTSBURG
30 | 77-40551-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1977-08-01 | 1977-10-11 | Patch Welded |  | Steel/Wrought Iron |  | ANTIOCH
30 | 81-21229-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1981-03-23 | 1984-03-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ANTIOCH
30 | 75-20477-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1975-06-11 | 1978-12-08 | Other |  | Steel/Wrought Iron |  | ANTIOCH
30 | 78-20870-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-04-26 | 1978-12-08 | Other |  | Steel/Wrought Iron |  | ANTIOCH
30 | 76-40429- |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-04-23 | 1976-04-27 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | ANTIOCH
30 | 74-40187-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-04-05 | 1974-04-08 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | ANTIOCH
30 | 76-20720-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-06-04 | 1976-12-07 | Patch Welded |  | Steel/Wrought Iron |  | ANTIOCH
30 | 80-21174-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Other |  | 1980-04-22 | 1981-02-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ANTIOCH
30 | 71-00076-1 |  |  | 2 | Distribution Feeder Main |  | Fitting |  |  | Construction Defect |  | 1971-09-13 | 1973-03-28 | Other |  | Steel/Wrought Iron |  | ANTIOCH
30 | 74-20201-1 |  |  | 0.25 | Transmission |  | Valves |  |  | Material Failure |  | 1974-02-21 | 1974-04-01 | Other |  | Steel/Wrought Iron |  | ANTIOCH
30 | 81-21234-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1981-04-20 | 1984-03-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ANTIOCH
30 | 82-21356-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1982-05-06 | 1984-03-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ANTIOCH
30 | 83-21468-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1983-04-18 | 1984-03-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ANTIOCH
30 | 75-20482-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1975-06-19 | 1975-09-05 | Other |  | Steel/Wrought Iron |  | ANTIOCH
30 | 80-21176-1 |  |  | 6 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1980-04-22 | 1981-01-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ANTIOCH
30 | 73-20099-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-02-13 | 1973-04-24 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | ANTIOCH
30 | 80-21175-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1980-04-22 | 1980-12-17 | Patch Welded |  | Steel/Wrought Iron |  | ANTIOCH
30 | 75-40286- |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1975-02-21 | 1975-02-24 | Patch Welded |  | Steel/Wrought Iron |  | ANTIOCH
30 | 74-20199-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-02-21 | 1974-03-29 | Clamp |  | Steel/Wrought Iron |  | ANTIOCH
30 | 84-21551-1 |  |  | 3 | Other |  | Fitting |  |  | Material Failure |  | 1984-01-18 | 1984-05-01 | Other |  | Steel/Wrought Iron |  | ANTIOCH
30 | 74-20195-1 |  |  | 0.25 | Other |  | Meter |  |  | Material Failure |  | 1974-02-21 | 1974-03-17 | Other |  | Steel/Wrought Iron |  | ANTIOCH
30 | 72-20071-1 |  |  |  | Transmission | [6 empty] | 1972-11-20 |  |  |  | Steel/Wrought Iron
30 | 74-40208-1 |  |  | 2 | Distribution Feeder Main |  | Fitting |  |  | Construction Defect |  | 1974-07-23 | 1974-07-23 | Other |  | Steel/Wrought Iron |  | ANTIOCH
| 09-20013-1 |  |  | 0.75 | Single Service |  | Riser |  |  | Construction Defect |  | 2009-02-27 | 2009-05-04 | Other |  | Steel/Wrought Iron |  | ANTIOCH | TIGHTENED VALVE
3 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1983-07-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ANTIOCH
30 | 90-40033-1 |  |  | 3 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1990-11-01 | 1990-11-01 | Replace Pipe |  | Plastic |  |  | REPLACED 5 FT OF 3" ACDYL A PLASTIC MAIN
30 | 74-20220-1 |  |  | 0.75 | Other |  | Fitting |  |  | Corrosion |  | 1974-02-22 | 1974-07-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ANTIOCH | FOUND LEAK ON HOUSE LINE TO 625 THIRD ST. REPLACED LEAKING ELBOW TO STOP LEAK.
30 | 84-21538-1 |  |  | 0.75 | Service |  | Other |  | TS | Corrosion |  | 1984-01-04 | 1984-04-30 | Other |  | Steel/Wrought Iron |  | ANTIOCH
30 | 73-20089-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1973-03-06 | 1973-03-06 | Clamp |  | Steel/Wrought Iron |  | PITTSBURG
30 | 81-21236-1 |  |  | 2 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1981-04-23 | 1982-02-09 | Other |  | Steel/Wrought Iron |  | PITTS. CA. | GREASED VALVE AT ENTRANCE TO REG. STA. FOR LEAK REPAIR
30 | 79-40855- |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1979-08-10 | 1979-08-14 | Patch Welded |  | Steel/Wrought Iron |  | PITTSBURG | WELDED 8" X 12" PATCH 100' E/O PG&E CO FENCE OF REG. STATION
30 |  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron |  | PITT. | EXPOSED 5' OF 4" STL MAIN TO INST. 1 1/4" SER TEE.
1 |  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  |  | 1981-03-18 | Other |  | Steel/Wrought Iron |  |  | INST 1" SERVICE
| 96-40069-1 |  |  | 2 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1996-09-13 | 1996-09-13 | Other |  | Aldyl A (Tan or Gray) |  | PITTSBURG
|  |  |  | 24 | Transmission |  | Other |  |  | Other |  |  | 1983-06-14 | Other |  | Steel/Wrought Iron |  | PITTSBURG + ANTIOCH | LIGHT RUST ON BOTTOM OF PIPE DUR TO WATER UNDERNEATH WRAP. REWRAPPED 6' OF 24" PIPE ALSO REPLACED ETS STATION BROKEN OFF BY HEAVY RUN OFF OF WATER.
30 | 94-20000-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1994-01-03 | 1995-06-08 | Clamp |  | Steel/Wrought Iron |  | Antioch | Installed 2" skinner leak clamp
30 | 71-00075 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Material Failure |  | 1971-09-01 | 1973-04-23 | Patch Welded |  | Steel/Wrought Iron |  | Antioch | Leaking in 2" main repairs made by welding on 2"x3" patch
1 | 79-40830-1 |  |  | 1.25 | Service |  | Valves |  |  | Damage by outside Forces |  | 1979-07-03 | 1979-07-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Antioch
30 | 74-20235-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-02-27 | 1974-05-17 | Patch Welded |  | Steel/Wrought Iron |  | Antioch | Leaking in 2" main repairs made by welding on 2"x3" patch
30 | 74-20291-1 |  |  | 0.75 | Other |  | Fitting |  |  | Material Failure |  | 1974-04-15 | 1974-05-01 |  |  | Steel/Wrought Iron |  | Antioch | Repaired leakage at this point
30 |  |  |  | 24 | Transmission |  | Other |  |  | Other |  | 1972-08-23 |  | Other |  | Steel/Wrought Iron
3 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1982-02-03 | 1982-02-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | Antioch | Lust 1/2" PLA Screws
30 | 72- |  |  | 24 | Transmission |  | Other |  |  | Other |  | 1972-03-02 |  | Other |  | Steel/Wrought Iron
3 | 82-41211-1 |  |  | 0.5 | Single Service |  | Body of Pipe |  |  | Corrosion |  | 1982-02-08 | 1982-02-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ANTIOCH
3 | 82-41212-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Corrosion |  | 1982-02-09 | 1982-02-09 | Replace Pipe and/or Service |  | Copper |  | ANTIOCH | C/O 1/2" CU SLTD 1/2" PLA
3 | 82-41233-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Other |  |  |  | Replace Pipe and/or Service |  | Copper |  |  | E/SIDE SYCAMORE DR. 176' N/O MADILL ST. (1) AMP FITTING AT RISER. (1) AMP FITTING AT TEE
3 | 82-41219-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1982-02-12 | 1982-02-12 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ANTIOCH | E/SIDE SYCAMORE DR. 176' N/O MADILL ST. (1) AMP FITTING AT RISER. (1) AMP FITTING AT TEE
3 | 82-41220-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Corrosion |  | 1982-02-12 | 1982-02-12 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ANTIOCH | (1) AMP FITTING AT RISER. (1) AMP FITTING AT TEE; R/R SERVICE
30 | 82-41221-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Corrosion |  | 1982-02-16 | 1982-02-16 | Replace Pipe and/or Service |  | Copper |  | ANTIOCH | (1) AMP FITTING AT RISER. (1) AMP FITTING AT TEE
3 | 82-41222-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Corrosion |  | 1982-02-12 | 1982-02-12 | Replace Pipe and/or Service |  | Copper |  | ANTIOCH | (1) AMP FITTING AT RISER. (1) AMP FITTING AT TEE
3 | 82-41223-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Corrosion |  | 1982-02-12 | 1982-02-12 | Replace Pipe and/or Service |  | Copper |  | ANTIOCH
30 | 79-20938-1 |  |  | 0.75 | Service |  | Fitting |  |  | Corrosion |  | 1979-01-31 | 1979-03-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ANTIOCH | RERUN SERVICE ... OF LEAK ON SERVICE TEE
1 | 74-41255-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-05-07 | 1974-05-10 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | CONCORD | WELDED 24"X20" SLEEVE
30 | 76- |  |  | 20 | Transmission |  | Other |  |  | Other |  | 1976-05-10 | 1976-05-10 | Other | INSTALLATION OF T.P. MARKERS | Steel/Wrought Iron |  | PITTSBURG | INSTALLED TWO NEW T.P. MARKERS FOR CONTRACTOR, MORE TO BE INSTALLED LATER
30 | 74-20231-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-02-27 | 1974-04-30 | Clamp |  | Steel/Wrought Iron |  | ANTIOCH | WATER BOX 3' FROM SIGN POLE; LEAK IN 2' MAIN REPAIRS MADE BY INSTALLING 2"X6" SKINNER CLAMP
3 |  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  |  | 1981-06-19 | Other |  | Steel/Wrought Iron |  |  | DONE WITH WO-41766-A
30 | 75-20488-1 |  |  | 3 | Distribution Feeder Main |  | Fitting |  |  | Construction Defect |  | 1975-06-23 | 1975-11-13 | Other |  | Steel/Wrought Iron |  | ANTIOCH | TEST NIPPLE ...
30 | 83-41373-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1983-09-22 | 1983-09-22 | Replace Pipe and/or Service |  | Other Plastic |  | ANTIOCH
30 | 79-44625-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1979-06-26 | 1981-06-01 | Other |  | Other |  | CLAYTON | 0% GAS IN TEST HOLES OVER MAIN IN STREET BETWEEN TWO LARGE BELL HOLES (OLD LEAK MARKS); I WOULD RECOMEND THIS LEAK SHOULD E DOWN GRADED TO A #3
30 | 74-00164-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Material Failure |  | 1974-03-22 | 1974-03-26 | Patch Welded |  | Steel/Wrought Iron |  | ANTIOCH | LEAK IN 2" MAIN REPAIRS MADE BY WELDING IN A 2"X4" PATCH
30 |  |  |  | 20 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1980-01-21 | Other |  | Steel/Wrought Iron |  |  | CADWELDER E.T.S ON MAIN
30 |  |  |  | 22 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1980-01-21 | Other |  | Steel/Wrought Iron |  |  | CADWELDER E.T.S ON MAIN
30 |  |  |  | 20 | Distribution Feeder Main |  | Other |  |  | Other |  | 1980-01-21 | 1980-01-21 | Other |  | Steel/Wrought Iron |  |  | CADWELDER E.T.S ON MAIN
30 | 80-40993-1 |  |  | 34 | Transmission |  | Other Welds |  |  | Material Failure |  | 1980-08-26 | 1980-08-26 | Weld Over Sleeve or Can | REPLACE PIPE AND/OR SERVICE | Steel/Wrought Iron |  | ANTIOCH
30 | 79-20982- |  |  | 5.5 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1979-03-29 | 1979-04-10 | Other |  | Steel/Wrought Iron |  | ANTIOCH | REPAIRED LEAK BY SERVICING
30 | 74-00193-1 |  |  | 1.25 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-03-29 | 1974-05-17 | Clamp |  | Steel/Wrought Iron |  | ANTIOCH | 11/4" MAIN LEAKING. REPAIR WITH 11/4"X4" SKINNER CLAMP. 11/4" MAIN TEE TOP PITTED & RISER
30 | 74-00180-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-03-27 | 1974-05-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ANTIOCH | CATCH BASIN BUILT OVER OUR 2' GAS MAIN
30 | 82-41296-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1982-08-19 | 1982-08-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ANTIOCH
3 | 86-41520- |  |  | 20.75 | Service |  | Body of Pipe |  |  | Corrosion |  |  | 1986-05-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron
30 | 90-40034-1 |  |  | 2 | M |  | Other |  |  | Construction Defect |  | 1990-01-06 | 1990-11-07 | Replace Pipe and/or Service |  | TR 418 |  | ANTIOCH | REPLACE 5FT OF 2" PL MAIN & INSTALL NEW SERVICE TEE. PUNCH TYPE
30 | 82-41291-1 |  |  | 8 | Distribution Feeder Main |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1982-08-02 | 1982-08-03 | Other |  | Steel/Wrought Iron |  | ANTIOCH | REPAIRED LEAK AT CAP
665 | 71-40033 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1971-05-26 | 1971-05-26 | Replace Pipe and/or Service |  | Copper |  | ANTIOCH | REPLACED 8" 1/2" COPPER WITH 2-1/2" COPPER COUPLING
1 |  |  |  | 34 | Transmission | [10 empty] | Steel/Wrought Iron
30 | 86-21723 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1986-03-18 | 1986-04-15 | Other |  | Steel/Wrought Iron |  | ANTIOCH | GREASED VALVE
30 | 80-21183-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1980-10-14 | 1981-06-10 | Other |  | Steel/Wrought Iron |  |  | GREASED VALVE TO STOP LEAK FOR REPAIRS; NO MAIN LEAK
1 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1981-06-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ANTIOCH
1 | 80-21170 |  |  | 0.14 | Other |  | Valves |  |  | Other |  | 1980-04-14 | 1980-05-13 | Other |  | Steel/Wrought Iron |  |  | LUBED VALVE A-91 STOPPED LEAK. CREW WILL HAVE TO DIG UP GAUGE TAP AT VALVE 15 TO REPAIR LEAK 25/100% B.F.
1 |  |  |  | 3.4 | Transmission |  | Other |  |  | Other |  | 1976-08-04 |  | Other |  | Steel/Wrought Iron |  | ANTIOCH | INST E.T.S STATION FOR CATHODIC PROTECTION
30 |  |  |  | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  | ANTIOCH | EXPOSED 6' OF 34" T.P. MAIN TO INST. 1" SER. TEE
1 |  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  |  | 1979-05-31 | Replace Pipe and/or Service |  | Steel/Wrought Iron
|  |  |  | 200 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Other Plastic |  | OAKLEY | INST 132' OF 2" PLA ON MAIN EXTENTION
3 | 82-41244-1 |  |  | 2 | Distribution Main |  | Other |  |  | Damage by outside Forces |  | 1982-04-08 | 1982-04-08 | Other |  | Other Plastic |  | OAKLEY | INST NEW 2" TRANSISION FITTING 12' N/S/L
| 97-40060-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Digin |  | 1997-07-18 | 1997-07-18 | Replace Pipe |  | TR 418 |  | ANTIOCH | SQUEEZED 2" PL. &FUSED ON NEW 2" PL. CAP
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1979-06-14 | Other |  | Steel/Wrought Iron |  | OAKLEY
30 |  |  |  | 2 | Service |  | Other |  |  | Other |  |  | 1978-03-22 | Replace Pipe and/or Service |  | Other Plastic |  | BRENTWOOD | C/O 1/2" COPPER SERVICE
|  |  |  | 0.5 | Service |  | Other |  |  | Other |  |  | 1978-03-16 | Replace Pipe and/or Service |  | Other Plastic |  |  | INST NEW 1/2" PLA SERVICE
30 | 72-40097-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-12-13 | 1972-12-14 | Replace Pipe and/or Service |  | Other Plastic |  | ANTIOCH | DUG IN MAIN REPLACE 4" 2" PIPE
30 | 73-20091-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1973-03-08 | 1973-03-08 | Clamp |  | Steel/Wrought Iron |  | BRENTWOOD | LEAK IN 2" MAIN CAUSED BY ROCK IN BACKFILL REPAIRED WITH SKINNER CLAMPS & 5# ZINC ANODE
30 | 76-40436- |  |  |  | Distribution Feeder Main |  | Other |  |  | Other |  | 1976-07-27 | 07/00/0000 | Other | NO LEAKAGE | Steel/Wrought Iron |  | BRENTWOOD | BAR TEST MAIN & CHECKED WITH ...
1 | 97-968-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1997-08-12 | 1997-08-12 | Replace Pipe |  | Other Plastic |  |  | INSTALLED NEW PLASTIC 2" PIPE TO MAKE REPAIRS
| 01-40013- |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Damage by 3rd Party |  | 2001-02-01 | 2001-02-17 | Other | REPLACED PIPE | TR 418 |  | BRENTWOOD | TWO FEET OF 3" PL. & 2, 3" COUPLING & 3" TEE
| 09-40120 | [5 empty] | Valves |  |  | Equipment Malfunction |  | 2009-07-14 | 2009-07-14 |  |  | Steel/Wrought Iron |  | BRENTWOOD | LEAK ON VALVE OFF T.P. MAIN
30 | 96-20022-1 |  |  | 0.5 | Distribution Feeder Main |  | Tap Connection |  |  | Construction Defect |  | 1996-05-10 | 04/00/1997 | Tighten Cap or Bolt |  | Aldyl A (Tan or Gray) |  | BRENTWOOD | CHANGED CAP ON TEE AT END OF MAIN (PURGE TEE)
30 | 84-41402-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1984-01-28 | 1984-01-28 | Replace Pipe and/or Service |  | Aldyl A (Tan or Gray) |  | BYRON
1 |  |  |  | 8 | Distribution Feeder Main |  |  |  |  | Other | [5 empty] | Steel/Wrought Iron |  | BYRON
30 | 74-40238-1 |  |  | 4 | Distribution Feeder Main |  | Other Welds |  |  | Material Failure |  | 1974-10-23 | 1974-10-23 | Replace Pipe and/or Service |  | Other Plastic |  | BYRON | BUTT FUSION PULLED APART. REPAIR MADE BY INSTALLING 4' OT 4" PL. & 2 4" PL
30 | 85-41479-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1985-08-07 | 1985-08-07 | Replace Pipe and/or Service |  | Other Plastic |  | DISCOVERY BAY | BROKEN 2" PL MAIN
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1979-07-10 | 1979-07-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | BYRON | INSTALLED NEW 117' 1/2" NEW SERVICE
|  |  |  | 8 | [11 empty] | Steel/Wrought Iron |  | HAYWARD | INSTALL E.T.S.
24 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | UNION CITY | INST. E.T.STATION AT THIS LOCATION
24 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | UNION CITY | INST. E.T. STATION AT THIS LOCATION
24 |  |  |  | 8 | Distribution Feeder Main | [7 empty] | 1978-09-01 |  |  | Steel/Wrought Iron |  | UNION CITY | MAIN EXPOSED TO C/O 3/4" T.P. SERVICE TO 31210 A AYRD NILES BLVD.
1 |  |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-03-14 | 1979-03-14 | Other |  | Steel/Wrought Iron |  |  | C/O SERVICE, WELDED 8" CAN OVER VALVE AT MAIN
24 |  |  |  | 8 | [7 empty] | 1996-05-29 |  |  |  | Steel |  | UNION CITY | MAIN IS 10' FROM EDGE OF PAVEMENT 33" DEEP. 14' FROM STATION 30+40
24 |  |  |  | 8 | [7 empty] | 1996-05-29 |  |  |  | Steel |  | UNION CITY | MAIN IS 5' FROM EDGE OF PAVEMENT 38" DEEP 8'3" FROM STATION 31+28
24 |  |  |  | 8 | [7 empty] | 1996-06-03 |  |  |  | Steel |  | UNION CITY | REWRAPPED MAIN- RUST REMOVED SOME PITTING WRAP NOT GOOD
24 |  |  |  | 8 | [7 empty] | 1996-06-03 |  |  |  | Steel |  | UNION CITY | REWRAPPED MAIN- MAIN IN GOOD SHAPE
24 |  |  |  | 30 | Transmission | [7 empty] | 1977-07-19 |  |  | Steel/Wrought Iron |  | UNION CITY | MAIN EXPOSED FOR LOCATING AND ENDINEERING STUDIES
24 |  |  |  | 30 | Transmission | [7 empty] | 1977-07-19 |  |  | Steel/Wrought Iron |  | UNION CITY | MAIN EXPOSED FOR LOCATION AND ENGINEERING STUDIES
24 |  |  |  | 30 | Transmission | [7 empty] | 1977-07-19 |  |  | Steel/Wrought Iron |  | UNION CITY | MAIN EXPOSED FOR LOCATING AND ENGINEERING STUDIES
24 |  |  |  | 30 | Transmission | [7 empty] | 1977-07-19 |  |  | Steel/Wrought Iron |  | UNION CITY | MAIN EXPOSED FOR LOCATING AND ENGINEERING STUDIES
|  | 105 |  | 24 | [11 empty] | Steel |  | UNION CITY | INSPECTED AT NO PROPERTY LINE OF JEAN AND LINE 105
1 | 00-00000-0 |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron |  |  | INST. 66' OF 3/4" STL. X-TRY-COAT NEW SERVICE REF TO W/O 448-G
|  |  |  | 0.75 | Service |  | Other |  | COMPRESSOR COMPONENTS | Material Failure |  | 1996-11-04 | 1996-11-04 |  |  | Steel/Wrought Iron |  | UNION CITY | REPLACE REG. EQEI-046
| 96-00001-1 |  |  | 0.75 | Service |  | Physical/Mechanical Joint |  |  | Corrosion |  | 1996-08-07 | 1996-11-08 | Other |  | Steel/Wrought Iron |  | UNION CITY | SERVICE HP VALVE RERUN M-75 HIGH SET
|  |  |  | 2 | [11 empty] | Steel |  | UNION CITY | C/O ONLY AT MAIN ETS INSTALLED
|  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1979-07-31 |  |  |  | Steel/Wrought Iron |  | UNION CITY
|  |  |  | 8 | Distribution Feeder Main | [7 empty] | 1986-10-28 |  |  | Steel/Wrought Iron |  | FREMONT | ...D.F.M. OUT OUT OLD...LINE VALVE 1' OFF MAIN.
|  |  |  | 8 | [11 empty] | Steel-Other |  | FREMONT
|  |  |  | 8 | [11 empty] | Steel-Other |  | FREMONT
24 | 76- |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | UNION CITY | SERVICE TO 35206 C/O AND TEE ON MAIN CANNED
24 | 94-41020-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1994-06-24 | 1994-06-29 | Patch Welded |  | Steel/Wrought Iron |  | FREMONT | WELD PATCH ON 2" STL. MAIN; WELD PATCH ON 2" STL D.F.M. MAIN
24 | 95-61124-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1995-11-08 | 1995-11-08 | Replace Pipe |  | Steel/Wrought Iron |  | FREMONT | MADE BRANCH SERV. WITH 35230 MILES RE. C/P TEMP P/L
24 | 77-61246-1 |  |  | 0.75 | Service |  | Tap Connection |  |  | Damage by outside Forces |  | 1977-11-29 | 1977-11-29 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | FREMONT
24 | 81-00006-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1981-02-18 | 1981-06-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | NILES | RERUN SERV. FOUND 8" MAIN TO P/L AT HTOH SAT. 8" IS D.F.M. MAIN. BACK FILLED WITH SAND AND RED ROCK.
24 | 93-61024-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1993-07-02 | 1993-07-08 | Replace Pipe |  | Steel/Wrought Iron |  | FREMONT | REMOVED 3/4" STEEL REPLACED WITH 1/2 PLASTIC DUE TO LEAKAGE (INSERTED); HI TO HI SET UP, NEXT TO THE MAIN. REPLACED BOTH SERVICES 839 X 857...ALL STEEL PIPE FOR HI TO HI PEGS WAS DECOTS PIPE TESTED PER CODE
24 |  |  |  | 1 | Service |  | Tap Connection |  |  | Other |  | 1993-07-06 | 1993-07-09 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | FREMONT | INSTALLED CAN OVER OLD HOME MADE TEE (ARC WELD) TO REPAIR FUZZ; CANNED HOME MADE SERVICE TEE FUZZ LEAK ONLY. TESTED PRESSURIZED CAN AT 124 PSI
24 | 93-61025-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1993-07-02 | 1993-07-08 | Replace Pipe |  | Steel/Wrought Iron |  | FREMONT | C/O OLD TEE ON THE TP 125 POUNS 2" MAIN ; CUT PFF TRANSFER MADE BRANCH WITH 1/2 PLASTIC. ALL PIPE ON HI TO HI SET UP WAS PICK UP AT SECORS PIPE LINE AND ISNTALLED
24 |  |  |  | 4 | [11 empty] | Steel |  | UNION CITY
24 | 77-21134-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1977-04-01 | 1977-04-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | FREMONT
|  |  |  | 6 | Distribution Feeder Main |  |  |  |  | Corrosion |  | 1979-07-31 |  |  |  | Steel/Wrought Iron |  | UNION CITY
24 |  |  |  | 8 | Distribution Feeder Main |  | Other |  |  | Other |  | 1975-02-19 | 1975-02-21 | Other |  | Steel/Wrought Iron |  | UNION CITY | C/O 3/4" SERV. AT 8" T.P. MAIN DUE TO HOUSE DING DEMOLISHED
1 |  |  |  | 8 | Distribution Feeder Main | [7 empty] | 1975-07-09 |  |  | Steel/Wrought Iron
24 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | NEW | FOUND NO LEAKAGE AT 8" D.F.M. AT THIS LOCATION
| 06-61016-1 |  |  | 0.5 | Service |  | Riser |  |  | Other | PIPED RISER | 2006-04-24 | 2006-04-24 | Other | REPLACE 1/2" RISER | Aldyl A (Tan or Gray) |  | FREMONT | CHANGE 1/2 NON CORROSION RISER WITH NEW 1/2 NON CORROSION RISER
24 | 76-64929-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-12-23 | 1976-12-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | FREMONT | REPLACED 3' OF 2" STEEL MAIN. 2" PCF'S, 3' EACH SIDE OF CENTER.; THIS WAS IN LOCATION OF SERV. TEE TO #__ FUZZY 2-1/2" COPPER SERC C/O MAIN AND SERV. NOT WRAPPED. INST. 2-2" PCFS AND REPLACED 3' FT OF MAIN. REST OF MAIN IN FAIR CONDITION.
24 |  |  |  | 12 | Distribution Feeder Main | [7 empty] | 1977-08-25 |  |  | Steel/Wrought Iron |  | FREMONT | MAIN EXPOSED TO FIND DEPTH
24 |  |  |  | 12 | Distribution Feeder Main | [7 empty] | 1977-08-25 |  |  | Steel/Wrought Iron |  | FREMONT | MAIN EXPOSED TO FIND DEPTH
24 |  |  |  | 12 | Distribution Feeder Main | [7 empty] | 1977-08-25 |  |  | Steel/Wrought Iron |  | FREMONT | MAIN EXPOSED TOFIND DEPTH
24 | 92-00013-1 |  |  | 0.75 | Service |  | Fitting |  |  | Construction Defect |  | 1992-11-24 | 1992-11-24 | Other |  | Steel/Wrought Iron |  | UNION CITY | PUT SET ON QUICK CHANGE TANK AND TIGHTEN VALVE TO CORRECT 301; PUT ON BACK C-TAG. AT RISER - FITTINGS LEAKING ABOVE GROUND.
4 | 92-00014-1 | [10 empty] | 1992-11-24 | [5 empty] | UNION CITY
24 | 92-00011-1 |  |  | 0.75 | Service |  | Valves |  |  | Material Failure |  | 1992-11-24 | 1992-11-24 | Other |  | Steel/Wrought Iron |  | UNION CITY | HPR. REG. SET AT 50PSIG. 50PSID POP OFF SET AT 50 PSIG. RPOP REG. ..40PSIF TO STOP POP OFF REG. FROM LEAKING.; PUT ON C-TAG
| 99-61003-1 |  |  | 2 | Distribution Main |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1999-06-24 | 1999-06-25 | Other | REPLACED PIPE | Steel/Wrought Iron |  | FREMONT | FOCRED LINE STOPPER, AND CUT OUT 2 2" DRESSORS...PLUG AND 2" SCREWED....
24 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel |  | FREMONT | INST. E.T.STATION AT THIS LOCATION
24 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | FREMONT | A; INST. E.T. STATION
24 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | FREMONT | ISNT. E.T. STATION
| 71-40296- |  |  | 1 | Service |  | Body of Pipe |  |  | Corrosion |  | 1971-09-15 | 1971-09-16 | Replace Pipe and/or Service | PLASTIC INSTERT | Steel/Wrought Iron |  | UNION CITY | LEAK IN ELBOW AT OLD FASHION TEE ON 1" SERVICE. INSTER 1/2" PLASTIC REPLACEMENT
| 71-60132- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-09-15 | 1971-09-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | FREMONT | INST. 2" PCF AND REPLACE 4' OF 2" PITTED AND LEAKING MAIN. PCF W/S 2ND 35' S/O G ST. DOCOTE DIST. UNION CITY
24 |  |  |  | 8 | Distribution Feeder Main | [7 empty] | 1979-12-13 |  |  | Steel/Wrought Iron |  | UNION CITY | CUT OFF OF 3/4 SERVICE AT MAIN
24 | 75- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1975-07-21 | 1975-07-23 | Patch Welded |  | Steel/Wrought Iron |  |  | MINOR SERVICE REPAIRS. DAMAGE ON TOP OF SERVICE PIPE WHERE STRCUK AND CUT BY POST...PATCH WELD AND POT WHILE SERVICE ON TEST OFF...FOR 20 INUTES TEST OK. TIDE BACK ONTO MAIN AFTER COMPLETED
24 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  |  | NONE
24 |  |  |  | 8 | Distribution Feeder Main | [7 empty] | 1977-06-08 |  |  | Steel/Wrought Iron |  | UNION CITY
24 |  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1974-07-05 |  |  |  | Steel/Wrought Iron
24 |  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1974-07-05 |  |  |  | Steel/Wrought Iron |  | UNION CITY
24 |  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1974-07-05 |  |  |  | Steel/Wrought Iron |  | UNION CITY
24 |  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1974-07-05 |  |  |  | Steel/Wrought Iron
24 | 77-21125-1 |  |  | 0.75 | Service |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1977-03-28 | 1977-04-29 | Other |  | Steel/Wrought Iron |  | UNION CITY | BAIL..SERVICE NO READING. SOAP TESTED RISER H&D METER SET., FOUND GREASE PLUG ON 3/4" NON STRUM VALVE ON RISER LEAKING. GREASED THIS VALVE TO CORRECT LEAKAGE. ; NO MAIN INSPECTION
24 |  |  |  | 0.75 | Service |  | Other |  |  | Other |  |  | 1975-04-23 | Other |  | Steel/Wrought Iron |  | UNION CITY | C/O 3/4" SERVICE
24 |  |  |  | 6 | [11 empty] | Steel/Wrought Iron |  | SUNOL | D.F.M. PRESSURE; C/O SERVICE AT...
|  |  |  | 2 | Distribution Feeder Main | [6 empty] | 1987-12-09 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | NILES
24 | [17 empty] | FREMONT
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT;
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT
|  |  |  | 8 | [11 empty] | Steel
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT
24 | 85-21521-1 |  |  | 1 | Service |  | Physical/Mechanical Joint |  |  | Corrosion |  | 1985-05-08 | 1986-07-29 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | FREMONT | FOUND LEAK AT RISER ON OLD 1" SCREWED TEE. CUT OFF SERVICE AND RERUN WITH TR418 1/2"PL TO MAKE REPAIRS
24 | 73-40149-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  | SEE OTHER SIDE | Corrosion |  | 1973-03-26 | 1973-03-29 | Replace Pipe and/or Service | SEE OTHER SIDE | Steel/Wrought Iron |  | NILES | DUE TO LEAKAGE... RED DOTS SHOW ON DRAWING... LEFT, IT WAS RECOMENDED THAT 2" PCF TO BE INSTALLED & OF 2" MAIN C/O AND ALOYS PLASTIC BE INSERTED AND FLAT CUT & TESTED PROCED OK. NEW 3/4" SET TO 337 AS IT WAS OLD 1" METER ... HOUSE WORK DONE ON WO4315-14. TEST OTHER SERVICE, FOUND OK & TRANSFERED TO NEW 1 1/4" AOLY PLASTIC MAIN.
24 | 77-40068-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1977-04-21 | 1977-04-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | MAIN ON SAME LEVEL AS 6" TRANS WATER & 13" APART
24 |  |  |  | 8.5 | [11 empty] | Steel |  | FREMONT
24 |  |  |  | 8 | [11 empty] | Steel |  | FREMONT
24 | 92-00017-1 |  |  | 0.75 | Service |  | Valves |  |  | Construction Defect |  | 1992-11-30 | 1992-11-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | FREMONT | TIGHTEN PLUG ON NEW VALVE TO CUTTENT LEAKAGE, BAR TEST SERVICE. NO LEAKAGE FOUND
24 | 92-00018-1 |  |  | 0.75 | Service | [6 empty] | 1992-11-30 | 1992-11-30 |  |  | Steel/Wrought Iron |  | FREMONT | SOAP TEST FITTINGS AND BAR TEST SERVICE. NO LEAKAGE FOUND
24 | 88-64538-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1988-11-30 | 1990-04-05 | Clamp |  | Steel/Wrought Iron |  | NILES | CLAMP D.F.M.
24 |  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1976-03-30 |  |  |  | Steel/Wrought Iron |  | FREMONT | AT THIS POINT, MAIN IS ONLY 9" BELOW 2" STEEL MAIN TYPE? REWRAP WHOLE SECTION OF EXPOSED MAIN.
24 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | FREMONT | INST. (1) 32LB BLOCK ANODE AT THIS LOCATION
24 | 81-61055-1 |  |  | 6 | Service |  | Valves |  |  | Other |  | 1981-10-08 | 1982-02-25 | Other |  | Steel/Wrought Iron |  | FREMONT | FOUND LEAKAGE ON 6" VALVE PLUG. GREASED TO CORRECT LEAKAGE.
24 |  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1980-10-31 |  |  |  | Steel/Wrought Iron |  | FREMONT | BOTH 8" & 3" D.F.M. WERE IN EXCELLENT CONDITION
24 | 92-44045-1 |  |  | 4 | Service |  | Riser |  |  | Internal Corrosion |  | 1992-10-21 | 1992-10-21 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | FREMONT | WELDED ON 4" M2 TO STOP OFF SERVICE ONE WELD ON 3/4" NIPPLE TO FIX 301 ON RISER
24 | 72-60246-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-12-06 | 1972-12-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | FREMONT | ANODE M.20.1.; FOUND BAD LEAKAGE ON SERVICE PIPE 3/4" STEEL APPROX. 4' FROM RISER C/O SERVICE AT TEE & PUSHED 1/2" ADLY PLASTIC PIPE THROUGH 3/4" CASING & INST. NEW RISER WITH ...COCK. 1# ANOID INSTALLED WAS NOT NECESSARY TO CUT AND TEST SER. AS LEAKAGE WAS FOUND BY DIGGING. NEW SERV. TESTED AT 50PSI.
24 |  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  |  | CLEAN OFF 2' OF WRAP TO CHECK MAIN- REWRAPED SAME
24 | 73-60315-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-12-29 | 1974-01-02 | Clamp | ; | Steel/Wrought Iron |  | FREMONT | LEAK CAUSED BY DAMAGE WRAP WHEN MAIN WAS INSTALLED IN 1959. INSTALLED SKINNER LEAK CLAMP FOR PERMANENT REPAIRS. RECHECKED FOR OTHER POSSIBLE LEAKS IN AREA- NOTHING FOUND- INST. 1-5" ANODE & REWRAP MAIN. BACKFILL WITH SAND AND ROCK. DEPTH OF MAIN 25"
24 |  |  |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | FREMONT | INST. G.T. STATION
2 |  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1981-10-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | ALTERED MAIN TO CLEAR FLOOD CONTROL CULVERTS. THIS JOB WAS DONE ON D&C 22723A
24 |  |  |  | 30 | Transmission | [6 empty] | 1978-06-16 |  |  |  | Steel/Wrought Iron |  | FREMONT
24 |  |  |  | 2 | Transmission | [6 empty] | 1978-06-16 |  |  |  | Steel/Wrought Iron |  | FREMONT
24 |  |  |  | 4 | Transmission | [6 empty] | 1978-06-16 |  |  |  | Steel/Wrought Iron |  | FREMONT
| 71-00116- |  |  | 0.5 | Service |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1971-06-28 | 1971-07-23 | Other |  | Copper |  | FREMONT | STEEL TO COPPER UNION ECLIPSE LOOSE UNION CONNECTION, TIGHTENED UNION -UNION WAS ONLY FINDER TIGHT. BASIC CAUSE OF LEAK
24 | 74-40916-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-08-28 | 1974-08-30 | Patch Welded |  | Steel/Wrought Iron |  | FREMONT | 4 PITS ON SIDE OF MAIN AT 3 O'CLOCK POSITION. ELECTRIC WELDED 3 PATCHES ON MAIN TO CORRECT LEAKAGE, INSTALLED #9ANODES ON MAIN.
24 |  |  |  | 4 | Transmission | [6 empty] | 1978-06-16 |  |  |  | Steel/Wrought Iron |  | FREMONT
24 |  |  |  | 2 | Transmission | [6 empty] | 1978-06-16 |  |  |  | Steel/Wrought Iron |  | FREMONT
24 |  |  |  | 4 | Transmission | [6 empty] | 1978-06-16 |  |  |  | Steel/Wrought Iron |  | FREMONT
4 |  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | INST. E.T.S. STATION.
4 |  |  |  |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | E.T.S. STATION AT EDGE OF PAVEMENT. 4" D.F.M. IS 10' DEEP AT BOTH LOCATIONS
24 |  |  |  | 4 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
24 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1975-06-26 | Other |  | Steel/Wrought Iron |  | SAN LEANDRO | NONE/ NEW SERVICE; INST. NEW SERVICE.
24 | 72-40552-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-07-05 | 1972-07-07 | Clamp |  | Steel/Wrought Iron |  |  | INST. ONE 2" SKINNER LEAK CLAMP ON MAIN. MAIN IN VERY BAD CONDITION.
24 |  |  |  | 0.5 | Service |  | Other |  |  | Other |  |  | 1975-03-03 | Other |  | Steel/Wrought Iron |  | SAN LEANDRO | REPLACE GAS SERV. A/C METER & RISER UNDER HOUSE
24 | 72-25006-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1972-01-28 |  | Other |  | Other |  |  | NO LEAKAGE PER ...
24 |  |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  | 1975-02-24 |  | Other |  | Steel/Wrought Iron |  |  | INST. 2 6" P.C.F. BT. TO LOWER 6" MAIN TO CLEAR CONTACT WITH 6" C.I. WATER MAIN. USED 6' - 6" STEEL PIPE. INST. E.T.S. STATION 1-VALVE TRAFFIC TYPE.
24 | 72-00002-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1972-04-04 |  | Other |  | Other |  |  | CHECKED ALL VALVES (P.G.&E.) AND WATER VALVES, ALSO ALL CULVENTS, MAN HOLES, AND WATER BOXES, AS WELL AS AREAS WHERE WORK HAD BEEN DONE PREVIOUSLY. NO INDICATION OF ANY LEAKAGE.
24 | 72-25004-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1972-01-28 |  | Other |  | Other |  |  | NO LEAKAGE PER...
| 71-60093- |  |  | 1 | Transmission |  | Other |  |  | Corrosion |  | 1971-04-10 | 1971-04-14 | Replace Pipe and/or Service | REPLACE 10' SECTION OF 1" MAIN | Steel |  | SAN LEANDRO | MAIN SHOULD BE REPLACED HAD TROUBLE TRYING TO STOP OF 2" P.C.F. BECAUSE OF THE DUST PACKED IN MAIN BIG ENOUGH TO INST. P.C.F. AND WRAP
| 71-40266- |  |  | 3 | Distribution Main |  | Fitting |  |  | Other |  | 1971-08-11 | 1971-08-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN LEANDRO | REPLACED 4FT OF 3" MAIN & H/T 2" MAIN A/C ...FITTINGS..TIES, AND CAPS & OF 3" VALVES...
24 | 72-25020-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1972-01-31 |  | Other |  | Other |  |  | NO LEAKAGE...
| 71-40265- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-08-10 | 1971-08-12 | Replace Pipe and/or Service |  | Steel |  | SAN LEANDRO | MADE PERMANENT REPAIR ON 2" MAIN UNDER CONCRETE CURB & GUTTER ARC WELDED 3 PATCHES AND ARC WELDED OVER OTHER SMALLER PITTSL
24 |  |  |  | 6 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron |  | SAN LEANDRO | C/O 3/4" SERV. A/C REMOVING HOUSE.
24 |  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  |  | NO LEAKAGE; LOOKING FOR CONTACT. DIDN'T FIND ANYTHING
24 | 00-00000-0 |  |  | 3 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron |  | SAN LEANDRO | INSTALL 3" M2 FITTING, AND 3/4" SAVER VALVE SO WE COULD CUT OUT HOME MADE TEE.
24 | 89-40049-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1989-11-07 | 1989-11-08 | Other |  | Other |  | SAN LEANDRO | NO GAS LEAKAGE IN AREA. POSSIBLY OF MINT SPRAY FUMES
24 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other | NONE |  | 1975-05-21 | Other |  | Steel/Wrought Iron |  | SAN LEANDRO | CUT SERVICES OFF TO #229-31-300 HASS AVE DUE TO HOUSES BEING WRECKED
25 | 00-00000-0 |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1975-02-25 | Other |  | Steel/Wrought Iron |  |  | NO LEAKAGE; CUT SERVICE OFF AT THIS LOCATION
24 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1976-03-25 |  | Other |  | Steel/Wrought Iron |  |  | C/O 3/4" SERV. A/C REMOVING HOUSE
24 | 00-00000-0 |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Other |  | SAN LEANDRO | CUT OFF SERVICE AT MAIN
24 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1976-02-06 | Other |  | Steel/Wrought Iron |  | SAN LEANDRO | CUT SERV. OFF AT MAIN
24 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1978-08-03 |  | Other |  | Steel/Wrought Iron |  | SAN LEANDRO | BUILDING TO BE TORN DOWN SERVICE CUT OFF.
24 |  |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1980-12-15 | 1981-02-06 |  |  | Steel/Wrought Iron |  | SAN LEANDRO | REMOVED WATER SERVICE CONTACT ON 8" T.P. MAIN PER CORROSION MECHANIC.
| 71-40338- |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-10-23 | 1971-10-26 | Patch Welded |  | Steel/Wrought Iron |  | SAN LEANDRO | ARC WELDER INST. FOUR PATCHES ON 3" MAIN OVER BIG PITS. (P.R.)
24 | 74-20343-1 |  |  | 0 | Other |  | Other | [8 empty] | Other |  | SAN LEANDRO | CUT + TESTED SERV. FOUND NO LEAKAGE.
| 07-40060-1 |  |  | 2 | Service |  | Riser |  |  | Damage by 3rd Party |  | 2007-10-06 | 2007-10-06 | Replace Valve >= 2 inch |  | Steel/Wrought Iron |  | SAN LEANDRO | REPAIRED 2" STL PLUG.; REPAIRED 2" STL. RISER. NOTE: THIS IS NOT A 3/4" STL RISER IT IS A 2" STL. RISER AND OUT MAIN IS INSIDE PROPERTY OF 1091 DOOLITLE.
24 |  |  |  | 24 | Transmission |  | Other |  |  | Other |  | 1979-12-05 |  | Other |  | Steel/Wrought Iron |  | SAN LEANDRO | MAIN IN CENTER OF ST. C/O HIGH TO HIGH SET.
24 |  |  |  | 2 | Distribution Main |  | Other | [5 empty] | 1975-05-21 | Other |  | Steel/Wrought Iron |  |  | INST. 1/2" PLA SERV. D.B.
| 99-40015- |  |  | 0.75 | Service |  | Fitting | Riser |  | Atmospheric Corrosion |  | 1999-03-05 | 1999-03-06 |  |  | Steel/Wrought Iron |  | SAN LEANDRO | RERAN SERVICE.
|  |  |  | 8 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1980-12-22 |  |  | Steel/Wrought Iron |  | HAYWARD | EBMUD INSTALL 4 PLASTIC PIPE OVER 8" D.F.M. TO ELIMINATE CONTACT ON D.F.M.
| 03-00000-1 |  |  | 0.75 | Service |  | Fitting |  |  | Unknown |  | 2003-10-21 | 2005-04-09 | Other | REPLACED HIGH TO HIGH SET. | Steel/Wrought Iron |  | SAN LEANDRO | REPLACED HIGH TO HIGH SET.; REPLACED HIGH TO HIGH SET. CHANGED HIGH PRESSURE 3/4" VALVE AT HIGH TI HIGH SET. SHUT OFF 3/4" MUELLER TEE AT MAIN TO CHANGE VALVE
1 |  |  |  | 6 | Transmission |  | Other |  |  | Other |  |  | 1980-02-20 | Other |  | Steel/Wrought Iron |  | SAN LEANDRO | MAIN INSPECTION ONLY
24 |  |  |  | 6 | Transmission |  | Other |  |  | Other |  |  | 1980-02-20 | Other |  | Steel/Wrought Iron |  | SAN LEANDRO | MAIN INSPECTION ONLY
24 |  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1980-02-26 |  |  |  | Steel/Wrought Iron |  | SAN LEANDRO | C/O 1/4" STEEL SERVICE ONLY NO LEAKS.
| 71-40126- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1971-03-23 | 1971-03-24 | Patch Welded |  | Steel/Wrought Iron |  | SAN LEANDRO | LEAK FOUND ON COPPER TO STEEL COUPLING. SERV. WAS REPAIR & INST. FOR PERMANENT REPAIR. 3' X 3' BELL HOLE CONDITION GOOD
24 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | SAN LEANDRO | MAIN INSPECT ONLY; INSTALLED NEW SERVICE ONLY. NO LEAKS.
24 |  |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  | 1973-12-03 |  | Other |  | Steel/Wrought Iron |  |  | MAIN INSPECTION ONLY; INST. NEW 1/2" PLASTIC SERV.
24 |  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | CASTRO VALLEY | INSTALLED 2 PCTS (B.T.) ... NO LEAKS.
24 |  |  |  | 10 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | HAYWARD | PROSPECT 10" GAS MAIN AT THIS LOCATION
24 |  |  |  | 10 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | HAYWARD | PROSPECT 10" GAS MAIN AT THIS LOCATION
71-40187- |  |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-05-24 | 1971-05-26 | Patch Welded |  | Steel/Wrought Iron |  | CASTRO VALLEY | FOUND LEAK ON 3" H.P.M. HAD ARC WELD PUT TWO PATCHES ON MAIN TO MAKE PERMANENT REPAIR 5' X 3' BELL HOLE, IN GOOD CONDITION .
24 | 72-60079- |  |  | 0.75 | Service |  | Other Welds |  |  | Material Failure |  | 1972-03-16 | 1972-05-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CASTRO VALLEY | 2226 READING; REPAIRED LEAK AT RISER ECLIPSE UNION.
24 | 75-42175-1 |  |  | 0.5 | Service |  | Other Welds |  |  | Corrosion |  | 1975-06-02 | 1975-06-04 | Replace Pipe and/or Service |  | Copper |  | CASTRO VALLEY | FOUND...WELL LEAKING AT PT. WHERE 1/2"...STEEL AT MAIN & REMOVED ...& REPLACED WITH 1/2" PL...
24 |  |  |  | 0.75 | Service |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron |  | SAN LEANDRO | CUT & TEST 3/4" SERV NO LEAKAGE
24 |  |  |  | 0.75 | Service |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron |  | SAN LEANDRO | CUT & TEST 3/4" SERV. NO LEAKAGE
| 71-40272- |  |  | 1 | Service |  | Body of Pipe |  |  | Corrosion |  | 1971-08-18 | 1971-08-31 | Replace Pipe and/or Service | RERAN 1/2" PLASTIC IN 1" CASING. | Steel/Wrought Iron |  | SAN LEANDRO | RERAN 1/2" PLASTIC SERV IN 1" CASING A/C OF LEAKAGE AN OLD 1" SERV
| 71-60102- |  |  | 0.75 | Service |  | COMPRESSOR COMPONENTS |  |  | Corrosion |  | 1971-05-03 | 1971-05-05 | Other |  | Steel/Wrought Iron |  | SAN LEANDRO | FOUND 3/4" STEEL SERVICE LEAKING. REPLACED 2 1/2' PIPE FOR PERMANENT REPAIRS. CUT & TESTED, OK. LAWN AREA SIDES OF BELL HOLE DAMP
| 71-60175- |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-09-07 | 1971-09-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN LEANDRO | INST. TWO 3" SKINNER LEAK CLAMPS ON 3" MAIN. MAIN IS VERY BAD CONDITION, ALSO THE WRAP AROUND MAIN.
24 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1975-02-21 |  | Other |  | Steel/Wrought Iron |  | ; ; | ISNT. 3" LINE STOPPER TO INST. 2 H.P. PL. MAIN (INSERT)
| 71-40285- |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-08-26 | 1971-09-02 | Replace Pipe and/or Service |  | Wrought Iron |  | SAN LEANDRO | INST. TWO 3" SKINNER LEAK CLAMPS ON OLD 3" STEEL MAIN. 3" MAIN IN VERY POOR CONDITION, PITTED VERY BAD WRAP IS ALSO IS DETERIORATED AROUND MAIN.
24 |  |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1977-08-31 |  | Other |  | Steel/Wrought Iron |  | HAYWARD | PROSPECTED FOR LEAKAGE NO LEAK
24 |  |  |  | 8 | Transmission |  | Other |  |  | Other |  | 1977-08-31 |  | Other |  | Steel/Wrought Iron |  | HAYWARD | PROSPECTED, FOR LEAKAGE NO LEAK
|  |  |  | 2 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | SAN LEANDRO
24 | 93-20155-1 |  |  | 4 | Other |  | Other |  |  | Other |  | 1993-04-07 |  | Other |  | Other |  |  | RECHECKED W/ FLAME PAK. FOUND 40% WATERBOXES .3 NEAT PATCH.
24 | 93-20155-1 |  |  | 4 | Other |  | Other |  |  | Other |  | 1993-04-07 |  | Other |  | Other |  |  | NO LEAK IN THIS AREA. RECHECK AT LATER DATE.
24 | 73-40138-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-02-20 | 1973-02-20 | Clamp | SKINNER CLAMPS | Steel/Wrought Iron |  |  | P.C. INST. ONE SHORT & ONE LONG SKINNER LEAK CLAMPS ON MAIN. P.C. INST. ONE SHORT & ONE LONG SKINNER LEAK CLAMPS ON MAIN. INST. ON #52 ON MAIN.
24 |  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  | 1975-04-01 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CASTRO VALLEY
24 |  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Corrosion |  | 1975-03-04 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CASTRO VALLEY
24 |  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Corrosion |  | 1975-03-14 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CASTRO VALLEY
24 |  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Corrosion |  | 1975-04-25 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CASTRO VALLEY
24 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  |  |  | Other
24 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1976-01-14 | Other |  | Steel/Wrought Iron |  | CASTRO VALLEY | NO LEAKAGE.
24 |  |  |  | 1 | Service |  | Other |  |  | Other |  |  | 1975-07-09 | Other |  | Other Plastic |  | SAN LEANDRO
|  |  |  | 12 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | HAYWARD | MAIN INSPECTION ONLY; LOCATED 12" D.F.M. FOR DEPTH
|  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | HAYWARD | MAIN INSPECTION ONLY; LOCATED 12" D.F.M. FOR DEPTH
|  |  |  | 12 | Distribution Feeder Main |  | Other |  |  | Corrosion |  | 1981-04-13 |  |  |  | Steel/Wrought Iron |  | HAYWARD
|  |  |  | 12 | Distribution Feeder Main |  | Other |  |  | Construction Defect |  | 1981-04-03 |  |  |  | Steel/Wrought Iron |  | HAYWARD
24 |  |  |  | 12 | Distribution Feeder Main | [7 empty] | 1981-01-13 | Other |  | Steel/Wrought Iron |  | HAYWARD | PROSPECT PVER 12" D.F.M. TO FIND OUT THE WALL THICKNESS. SEE W. TRILLMEGER FOR THE THICKNESS
24 |  |  |  | 12 | Distribution Feeder Main | [7 empty] | 1981-01-13 | Other |  | Steel/Wrought Iron |  | HAYWARD | PROSPECT OVER 12" D.F.M. TO FIND OUT THE WALL THICKNESS. SEE W. TRILLEMGER FOR THE THICKNESS;
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1981-06-02 |  |  |  | Steel/Wrought Iron |  | HAYWARD
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1981-06-02 |  |  |  | Steel/Wrought Iron |  | HAYWARD
|  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | HAYWARD | MAIN INSPECTION ONLY; LOCATED 12" D.F.M. FOR DEPTH
|  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | HAYWARD | MAIN INSPECTION ONLY; LOCATED 12" D.F.M. FOR DEPTH
|  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | HAYWARD | MAIN INSPECTION ONLY; LOCATED 12" D.F.M. FOR DEPTH
| 06-60032-1 |  |  | 1.25 | Service |  | Plastic Tee Cap |  |  | Unknown |  | 2006-10-05 | 2006-10-06 | Other | BLACK CAP REPAIR FITTINGS | Aldyl A (Tan or Gray) |  | HAYWARD | INSTALLED REPAIR CAP ON ALDY A SERVICE TEE. INSTALL BLACK CAP REPAIR FITTING.
|  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | HAYWARD | MAIN INSPECTION ONLY; LOCATED 12" D.F.M. FOR DEPTH
24 |  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | HAYWARD
| 71-60183- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1971-09-27 | 1971-09-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | HAYWARD | LEAK FOUND ON OUR SERVICE AND A LEAK FOUND ON HOUSE LINE CLOSE TO METER BOX APPROXIMATELY ONE CUBIC FOOT ...AND STILL A 1/2' CUBIC FOOT PER ...LEAK STILL IN HOUSE LINE SOME WHERE, SOAP TESTED AROUND APPLIANCES BUT UNABLE TO FIND IT AROUND THEM. FIELDS A SMALL ONE ON APPLIANCE ARCH AND ...FRAME IN FRONT SHOW ROOM,...DID NOT ELIMATE THE 1/2 CUDBIC FEET PRE...LEAK LEFT...METRIC WITH CUSTOMER
24 |  |  |  | 8 | Distribution Main | [7 empty] | 1977-10-03 |  |  | Steel/Wrought Iron |  | HAYWARD | MAIN INSPECTION REPORT; INSTALLED E.T.S.
24 |  |  |  | 8 | Distribution Feeder Main | [7 empty] | 1977-10-03 |  |  | Steel/Wrought Iron |  | HAYARD | MAIN INSPECTION REPORT; INSTALLED E.T.S.
|  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  |  | 1980-12-11 | Other |  | Other |  | HAYWARD | CAD WELDED WIRES 120' APART FOR E.T.S.
| 71-20237- |  |  | 3 | Other | M | Other |  |  | Corrosion |  | 1971-07-27 | 1971-07-30 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | HAYWARD | SERVERE ELECTROLYSIS ACTION ON 3" MAIN DUE TO ROCK BACK FILL OVER MAIN.
24 |  |  |  | 10 | Service | [7 empty] | 1977-10-07 |  |  | Steel/Wrought Iron |  |  | MAIN INSPECTION ONLY; INSTALLED E.T.S. STATION AT THIS LOCATION
24 |  |  |  | 10 | Distribution Feeder Main | [7 empty] | 1977-10-07 |  |  | Steel/Wrought Iron |  |  | MAIN INSPECTION ONLY; INSTALLED E.T.S. STATION AT THIS LOCATION
24 | 92-40076-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1992-10-22 |  | Other |  | Other |  |  | NO INDICATION OF GAS IN AREA 8-20-93
24 | 76-64665-1 |  |  | 0 | Other |  | Meter |  |  | Other |  | 1976-10-15 | 1977-05-13 | Other |  |  |  | HAYWARD | LEAK ON DIAL OF CURB METER.
| 71-20247- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-07-30 | 1971-09-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | HAYWARD | FOUND LEAK ON 2" MAIN WHERE SEWER CROSS UNDER GAS MAIN. MADE P.R. ARC WELDED INST. ...2"X 27" HALF SOLE AND TWO PATCHES ON MAIN. ;
| 71-20250- |  |  | 2 | Distribution Main |  | Fitting |  |  | Corrosion |  | 1971-07-30 | 1971-09-27 | Other |  | Steel/Wrought Iron |  | HAYWARD | P.R. ARC WELDER INST. 8" X 12" CAN ON 2" MAIN, TWO 2" X 1" SCREW TEE ON MAIN AND ...MADE 1" TEE WAS ALL LEAKING.
| 71-20253- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1971-08-02 | 1971-09-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | HAYWARD | REPLACED 3/4" SERV. WITH 1/2" PLSTIC INSERT A/C LEAKAGE
| 71-20252- |  |  | 2 | Distribution Main |  | Fitting |  |  | Corrosion |  | 1971-08-02 | 1971-09-24 | Other |  | Steel/Wrought Iron |  | HAYWARD | WELD THREADS ON 2" SCREW COUPLING ON MAIN LEAKING...REMOVED DRESSOR WITH 1 1/4" TEE AND VALVE LEAKING IN PLACE WITH STEEL PIN WELD
| 71-00033- |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1971-02-11 | 1974-03-29 | Weld Over Sleeve or Can |  | Ductile Iron |  | HAYWARD | INST. 2 X 3 WELD PATCH ON MAIN. REMOVED 3/4" C/O TEE A/C LEAKING; OM 5 X 3, 5 X 3, 3 X 4
|  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | HAYWARD | MAIN WAS EXPOSED TO FO UNDER FOR NEW SEWER.
24 | 75-00198-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-04-03 | 1976-01-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | HAYWARD | S.O.211573 MAIN REPLACEMENT REPAIR G.N. 488465 1/2 PL. REPL. (INSTERT)
| 71-00080- |  |  | 2 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 1971-08-05 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | HAYWARD | RE-DOPED AND TIGHTENED P.C.F. CAP TP CPRRECT LEAKAGE
| 71-60079- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1971-04-02 | 1971-04-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | HAYWARD | REPLACED 3/4" SERV. WITH 1/2" PLASTIC DUE TO LEAKAGE USED CASING
| 71-20268- |  |  | 0.75 | Service |  | Valves |  |  | Corrosion |  | 1971-08-20 | 1972-05-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | HAYWARD | RETEST AFTER 6-5-75; CURB VALVE TO 635 AND TESTED 3/4...FROM...TESTED 100PSI. RETESTED OK. S/O 133460
24 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1977-12-16 | 1977-12-19 | Other |  | Steel/Wrought Iron |  | HAYWARD | NONE; INST. NEW 1/2" PLASTIC SER. MAIN INSPECTION ONLY; NONE
24 |  |  |  | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | MAIN INSTALLED 1929 WHAT COULD SEE OF PIPE IS IN FAIR CONDITION OPEN TO CLEAR CONTAC BETWEEN 2" AND 20"
|  |  |  | 4 | Service |  | Other |  |  | Other | ABANDON |  |  | Other | ABANDON | Steel/Wrought Iron |  |  | C/O SVC @ MAIN
24 |  |  |  | 2 | Distribution Feeder Main |  | Other |  |  | Other |  | 1981-02-23 |  | Other |  | Plastic
24 | 90-20010-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1990-02-23 |  | Other |  | Other |  | CASTRO VALLEY | HOUSE LINE LEAKING 7-17-90
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1972-05-30 |  | Other |  | Steel/Wrought Iron |  | ; | ROUTINE SERVICE C/O MAIN INSPECTION
24 | 90-20701-1 |  |  | 0 | Other | [6 empty] | 1990-04-30 |  |  |  | Other |  | HAYWARD | HAVE FLAME PACK RECHED AREA 2-11-91 0% MAIN AND SERVICE. NO READINS WITH FLAME PACK.
| 71-40333- |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-10-19 | 1971-10-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | HAYWARD | INST. (3) WELD PATCHES ON 2" HP MAIN AND REPLACED 3/4" SERV. WITH 1/2" PLASTIC AT #28L2
24 |  |  |  | 1.25 | Distribution Main |  | Other |  |  | Other | NONE |  | 1975-08-06 | Other |  | Steel/Wrought Iron |  | HAYWARD | ISNT. NEW SER. TO #25385-UVRS CT
24 |  |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1975-05-28 | 1975-05-28 | Other |  | Steel/Wrought Iron |  | HAYWARD | MAIN INSPECT.; C/O 3/4" STEEL SERVICE ONLY NO LEAKS
24 | 72-30074-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1972-02-10 |  | Other |  | Other |  |  | COULD FIND NO LEAKAGE. RECORD ONLY
24 |  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  | 1975-11-24 | 1975-11-24 | Other |  | Steel/Wrought Iron |  | HAYWARD | EXPOSED 6' OF 4" HP MAIN FOR LEAKAGE FOUND NO LEAK.
24 |  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  | 1975-12-05 | 1975-12-05 | Other |  | Steel/Wrought Iron |  | HAYWARD | STOPPED 12' OF 4" MAIN FOUND NO LEAKAGE
24 |  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  | 1975-12-29 | 1975-12-09 | Other |  | Steel/Wrought Iron |  | HAYWARD | CHECKED 4" MAIN FOR 301 FOUND NO LEAKAGE
24 | 72-30067-1 |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1972-02-10 |  | Other |  | Steel/Wrought Iron |  |  | COULD FIND NO LEAKAGE
24 |  |  |  | 2 | Other | [6 empty] | 1975-12-08 |  |  |  | Other Plastic |  | HAYWARD | NOTE: COMPLETED STUB SERVICE FROM PT. 2LT FROM 2" PL. MAIN. FOUND MAIN 6 FT. ...FROM CURB CAN'T DETERMIN ...AT THIS PT.
24 | 72-20398-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1972-02-29 |  | Other |  | Other |  |  | DUG BELL HOLES FOR LEAK AND CHECKED 2' GAS MAIN NO PITS. ...
24 | 72-20397-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1972-02-29 |  | Other |  | Other |  |  | ...NO LEAKAGE PER...
24 | 72-00040-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1972-04-18 |  | Other |  | Other
| 71-20287- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 09/20/0197 | 1971-09-24 | Patch Welded |  | Steel/Wrought Iron |  | HAYWARD | THIS MAIN IS IN POOR CONDITION AND IS 40 YRS OLD. SHOULD BE REPLACED. NO PAVING
24 | 71-20342-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1971-12-06 |  |  |  | Other
| 71-40253- |  |  | 0.5 | Service |  | Body of Pipe |  |  | Other |  | 1971-08-18 | 1971-08-18 | Replace Pipe and/or Service |  | Copper |  | HAYWARD | PERMANENT REPAIRS ON 1/2" COPPER SERV. INST. 3 FT OF 1/2" COPPER TUBING A/C LEAKAGE FOUND 1/2" COUPLING PULL APART
24 |  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1975-11-17 |  |  |  | Steel/Wrought Iron |  | HAYWARD | NO LEAK; INST. E.T.S. ONLY
| 02-40044-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 2002-05-17 |  | Other |  | TR 418 |  | HAYWARD | INSTALLED 5' OF NEW PIPE; INSTALLED 5' OF NEW PIPE.
|  |  |  | 6 | [11 empty] | Steel |  |  | WO 44719-E
24 |  |  |  | 3 | Distribution Feeder Main | [6 empty] | 1979-10-16 | 1979-10-16 | Other |  | Steel/Wrought Iron |  |  | WO40466.
24 | 76-30718-1 |  |  | 0 | Other |  | Meter |  |  | Material Failure |  | 1976-05-20 | 1977-04-20 | Other |  | Steel/Wrought Iron |  | HAYWARD | FOUND (2) TWO 1A CURB METER LEAKING... METER 31149 + 31153 MISSION BLVD. ALSO INSTALLED BYPASS VALVE TO REPAIR LEAK.
| 71-20289- |  |  | 0.75 | Service |  | Other |  |  | Corrosion |  | 1971-09-21 | 1971-09-23 | Patch Welded |  | Steel/Wrought Iron |  | HAYWARD | ROCKS WERE USE FOR SUB BASE AN ARE TOUCHING 3/4" SERVICE ANARE INSTALLED ON WRAP
| 09-22940-1 |  |  | 0.75 | Gathering |  | Riser |  | THREADS | Construction Defect |  | 2009-07-17 | 2010-04-27 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | SAN RAMON | SEE COMMENTS; REMOVE 1 1/4" LINE FOR FOUR METER SETS/REPLACED VALVE AT RISER.
|  |  |  | 12 | Other | [6 empty] | 1979-07-02 |  |  |  | Steel/Wrought Iron |  | SAN RAMON
24 | 74-1 |  |  | 2 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | SAN RAMON | S.O.#652087
24 |  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | SAN RAMON | CUT OFF 3/4" SERV. AT MAIN.
|  |  |  | 8 | [7 empty] | 2003-11-10 |  |  |  | Steel/Wrought Iron |  | DUBLIN
24 |  |  |  | 2 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
|  |  |  | 6 | Distribution Feeder Main | [6 empty] | 1985-01-31 |  |  |  | Steel/Wrought Iron |  | SAN RAMON | CAD WELD TRACER WIRE TO MAIN.
|  |  |  | 3 | Distribution Feeder Main | [6 empty] | 1985-01-31 |  |  |  | Plastic |  | SAN RAMON | PLT. FLEXALE T. IN FOOD CONDITION
|  |  |  | 12 | Transmission |  |  |  |  | Other |  | 2000-03-10 | 00/10/2000 | Other | NONE | Steel/Wrought Iron |  | DUBLIN | INSTALL E.T.S.
|  |  |  | 12 | Transmission | [6 empty] | 2000-03-08 |  |  |  | Steel/Wrought Iron |  | SAN RAMON | ISNTALLED E.T.S. STATION
24 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | DUBLIN | INSTALLED 3/4" STEEL SERV.
24 | 85-00017-1 |  |  | 8 | Distribution Main |  | Girth Weld |  |  | Corrosion |  | 1985-06-10 | 1985-06-12 | Other |  | Steel/Wrought Iron |  | DUBLIN | ARC WELDED OVER LEAK ON WELD. ALSO INSTALLED 9LBS ANODE AT THIS LOCATION
24 | 85-62076-1 |  |  | 8 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1985-06-11 | 1985-06-26 | Patch Welded |  | Steel/Wrought Iron |  | DUBLIN | ; INSTALLED 1 -7" X 5" PATCH OVER LEAK, INSTALLED 1 -3"X 5" PATCH OVER PIT. WASHED OVER SURFAVE PIT INSTALLED 1 -9# ANODE.
24 | 85-40084-1 |  |  | 8 | Distribution Main |  | Body of Pipe |  |  | Other |  | 1985-06-05 | 1985-06-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | DUBLIN | ; 24" X 10" HALF SOLE, 6" X 6" PATCH WELDED OVER 301 UNDERSIDE OF MAIN BY P.C.F.; DURING UPGRADE PROCES-CORROSION PITS BLEW OUT- HALF SOLE WELDED OVER 301'S
24 | 89-62028-1 |  |  | 8 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1989-07-05 | 1989-07-05 | Patch Welded |  | Steel/Wrought Iron |  | DUBLIN | A; PTACHED MAIN (WELDED)
|  |  |  | 8 | [7 empty] | 2003-10-27 |  |  |  | Steel/Wrought Iron |  | DUBLIN
24 |  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | DUBLIN | INSTALLED A NEW 1" PLASTIC SERVICE.
24 |  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | DUBLINE
24 |  |  |  | 8 | Transmission | [7 empty] | 1975-06-11 |  |  | Steel/Wrought Iron |  |  | PROSPECTING GAS MAIN FOR DEPTH IN A/C IMPROVEMENT OF DUBLIN BLVD.
24 |  |  |  | 8 | Distribution Feeder Main | [7 empty] | 1975-07-16 |  |  | Steel/Wrought Iron |  | DUBLIN | PROSPECTION MAIN FOR DEPTH
24 |  |  |  | 12 | Distribution Feeder Main | [7 empty] | 1975-06-11 |  |  | Steel/Wrought Iron |  |  | PROSPECTING GAS MAIN FOR DEPTH
| 08-62709-1 |  |  | 6 | Distribution Main |  | Valves |  |  | Other | VALVE NEEDED GREASING | 2008-04-10 | 2009-09-24 | Other | GREASED VALVE | Steel/Wrought Iron |  | PLEASANTON | GREASED VALVE; SOAP & TESTED VALVE D-06
24 | 87-62029-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-03-24 | 1987-03-30 | Patch Welded |  | Steel/Wrought Iron |  | DUBLIN | PATCH WELDED OVER 301 ON MAIN LEAK ON BOTTOM 10" X 10" PATCH
|  |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1980-11-14 | 1981-08-05 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | DUBLIN | INSTALLED (1) 12" X 30" STAINLESS STEEL LEAK CLAMP & ENCLOSED IT WITH (1) 16" STEEL CAN 4' LONG. -SEE DETAIL SKETCH-
| 85-00016-1 |  |  | 12 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1985-05-06 | 1985-05-14 | Patch Welded |  | Steel/Wrought Iron |  | DUBLIN | ON 12" D.F.M. INST. 1-15" X 8" PATCH OVER LEAK, 1 - 3" DIAMETER PATCH OVER PITS, 1 -2" DIAMITER PATCH OVER PITS; SOME OF WRAP LOOSE AND SOME OK. ALSO WRAP DAMAGED WHEN SEWER LINE WAS INSTALLED. LEAK NOT AT POINT OF SEWER CROSSING.
24 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | DUBLIN | INSTALLED TEST LEAD FO SPANNING
24 | 80-00007-1 |  |  | 6 | Distribution Main |  | Valves |  |  | Other |  | 1980-03-04 | 1980-03-17 | Other |  | Steel/Wrought Iron |  | DUBLIN | GREASED VALVE- CHECK AREA AT LATER DATE. CHECKED ON 4-3-80 FOUND 70PPM IN V.F.C.
|  |  |  | 12 | Distribution Feeder Main | [6 empty] | 1977-08-15 |  |  |  | Steel/Wrought Iron |  | DUBLIN
24 |  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
24 |  |  |  | 12 | [7 empty] | 1990-06-26 | 1990-06-26 |  |  | Steel/Wrought Iron |  |  | INSTALLED 32LB ANODE
24 |  |  |  | 8 | Distribution Feeder Main | [7 empty] | 1975-10-14 |  |  | Steel/Wrought Iron |  | DUBLIN | INSTALLED BAND AND TEST LEAK ...INSULATED 8" VALVE.
24 |  |  |  | 8 | Distribution Feeder Main | [7 empty] | 1975-10-13 |  |  | Steel/Wrought Iron |  | DUBLIN | USED PLASTIC WEDGE TO CLEAN. CONTACT WITH 4"...ELECT. ...CONDUIT.
|  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1979-07-19 |  |  |  | Steel/Wrought Iron
|  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1979-07-19 |  |  |  | Steel/Wrought Iron | ;
24 | 73-1 |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
24 | 87-40108-1 |  |  | 12 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1987-09-15 | 1987-10-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PLEASANTON | REPLACED 12" D.F.M. MAIN FROM 6015 SCRLET CT. TO 1000' EAST OF CUL-D-SACK
24 | 80-00008-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1980-03-04 | 1980-06-27 | Patch Welded |  | Steel/Wrought Iron |  | DUBLIN | INSTALLED 12" X 12" PATCH AT 4 O'CLOCK PASITION ON MAIN TO REP. LEAK
24 | 80-62541-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1980-11-14 | 1980-11-25 | Patch Welded |  | Steel/Wrought Iron |  | DUBLIN | INST. 12" HALF SOLE PATCH ON 12" MAIN.; THIS SECTION OF MAIN PITTED ONLY AT POINT OF LEAKAGE.
24 |  |  |  | 12 | [11 empty] | Steel/Wrought Iron |  | DUBLIN
24 |  |  |  | 12 | [8 empty] | 1990-06-26 |  |  | Steel/Wrought Iron |  | DUBLINE | INSPECTION ONLY; PROSPECTED 12" T.P. GAS MAIN OF 49' IN DEPTH
|  |  |  | 12 | [11 empty] | Steel/Wrought Iron |  | DUBLIN | POINT OF POT HOLE IS 15' BEHIND CURB
24 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | PLEASANTON | RERUN SERVICE TO 3534 OLD SANATA RITA RD. AND TRANSFERES TO NEW 2" PLASTIC MAIN
24 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | PLEASANTON | RERUN SERVICE TO 3622 OLD SANTA RITA RD. AND TRANSFERS TO NEW 2" PLASTIC MAIN
24 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | PLEASANTON | REPLACED SERVICE TO 3610 OLD SANTA RITA RD. AND TRANSFERED TO NEW 2" PLASTIC MAIN 4' OUT.
24 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
24 |  |  |  | 8 | Distribution Feeder Main | [7 empty] | 1974-11-20 |  |  | Steel/Wrought Iron
24 |  |  |  | 8 | Distribution Feeder Main | [7 empty] | 1975-06-25 |  |  | Steel/Wrought Iron |  | PLASANTON
24 | 74- |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | PLEASANTON | CUT AND TESTED SER. SER. OK. INS. 1-9LB ANODE
24 | 92-62533-1 |  |  | 2 | M |  | Tap Connection |  |  | Material Failure |  | 1992-06-04 | 1992-06-04 | Replace Pipe |  | TR 418 |  | PLEASANTON | BROKE TEE OFF MAIN WHILE CUTTING OFF SERVICE. REPLACED 2' OF 2" MAIN. ; REPLACED 2' OF 2" TR 418 WITH SAME. INSTALLED 1" X 2" SERVICE TEE FOR BYPASS FOR MAIN REPAIR
| 73- |  |  | 2 | Distribution Feeder Main | [10 empty] | Other Plastic |  | LIVERMORE
24 |  |  |  | 3 | Distribution Main | [6 empty] | 1983-07-28 |  |  |  | Steel/Wrought Iron |  | PLEASANTON | CONTRACTOR INSTALLING STORM DRAIN AND CROSSED THE 3" HP STL GAS LINE
24 |  |  |  | 3 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | PLEASANTON | C/O 92' OF 3" MAIN & ALTERED SERVICE TO CLEAR STORM DRAIN
24 | 80-62543-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1980-11-14 | 1981-09-16 | Patch Welded |  | Steel/Wrought Iron |  | PLEASANTON | DIG IN 2 PATCHES ARE 18" A PART
24 | 82-65113-2 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1982-11-18 | 1982-12-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SUNOL | REPLACED LEAKING 1 1/4" SERV. WITH 3/4" STL SERVICE. ;
24 | 10-00200-1 | 131 |  | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Weld Failure |  | 2010-11-16 | 2010-11-19 | Fill Weld - Weld |  |  |  | LIVERMORE | REWELDED 45 DEGREE SOCKET WELD FITTING
24 |  |  |  | 2 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  |  | GM 479484-74
24 | 72-60210-1 |  |  | 2 | Distribution Main |  | Tap Connection |  |  | Construction Defect |  | 1972-02-03 | 1972-02-04 | Other |  | Steel/Wrought Iron |  | ; LIVERMORE
24 |  |  |  | 3 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  |  | GM 479484-74
| 71-40305- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-09-20 | 1971-09-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | LIVERMORE | LEAKS WERE CAUSED BY 1" COPPER UNION SERVICE RESTING ON OUR 2" MAIN ELECT WELDED 3 PATCHES OVER BAD SPOTS
24 |  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  |  | GM 479484-74
24 | 73-40013-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-01-03 | 1973-01-12 | Patch Welded |  | Steel/Wrought Iron |  | LIVERMORE. | ANODE M-29-8
24 | 74- |  |  | 3 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | LIVERMORE
1 |  |  |  | 16 | Distribution Feeder Main |  | Other |  |  | Other |  | 1986-08-13 |  | Other |  | Steel/Wrought Iron |  | LIVERMORE
| 71-40311- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Construction Defect |  | 1971-09-24 | 1971-10-07 | Other |  | Steel/Wrought Iron |  | LIVERMORE | ELECT. T.V. & TELEPHONE DUCTS WERE RESTING ON TOP OF 2" MAIN AND CAUSED THE LEAKAGE. INST. 24" X 6" CAN OVER 2 LEAK CLAMPS
24 | 80-62549-1 |  |  | 8 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1980-05-22 | 1981-06-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | LIVERMORE
24 | 72- |  |  | 2 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
24 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | LIVERMORE | INSTALLED -2-8" P.C.F. SPLIT TYPE STOPPED OFF GAS AND INSTALLED AN 6" VALVE AND A 6" KERD TEST
| 73- |  |  | 2 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | LIVERMORE
| 05-11000-1 | 105 |  |  | Transmission |  | Other |  | RELIEVER | Other | WEAR & TEAR | 2005-05-12 | 2005-07-30 | Other |  |  |  | FREMONT | WRONG HIGH TO HIGH NO LEAK FOUND; REBUILT LEAKING RELIEVER RELIANCE HPR-20
24 | 72-20492-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-07-27 | 1973-02-16 | Patch Welded |  | Steel/Wrought Iron |  | HAYWARD | INST. 5# ZINK ANODE; LEAKS FOUND IN OVERHEAD TO ALL C/O ST. TEE. ELECT WELD 3 PATCHES TO MAKE PERMANENT REPAIRS. INST. 5#ANODE. CORROSION CAUSED BY DAMAGE WRAP FROM BACKHOE IN PAST WHEN C/O WAS MADE. NO ATTENTION HAS MADE TO REWRAP MAIN AT THIS TIME.
| 71-60042- |  |  | 1 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1971-02-03 | 1971-02-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | FREMONT | REPAIRED 1" SERVICE INSTAL OF... DUE TO BUILDING TO BE TORN DOWN WITH IN THEY...
24 | 72-20476-1 |  |  | 0.75 | Service |  | Tap Connection |  |  | Construction Defect |  | 1972-07-25 | 1973-02-12 | Other | WELD OVER ELECT. | Steel/Wrought Iron |  | HAYWARD | INST. 5# ANODE, TEMP REPAIR; E;ECT WELD OVER LEAKING WELD POOR WELD. CHECK AREA 50; EACH SIDE NO LEAKAGE.
24 | 71-30069-1 |  |  |  | Other |  | Physical/Mechanical Joint |  |  | Other |  | 1971-12-13 | 1971-12-16 | Other |  |  |  |  | FOUND LEAK WITH ... REPAIRED BY GAS SERVICEMAND, USED BAG TO REPAIR LEAK ON METER SWIVAL.
24 | 72-20519-1 |  |  | 2 | Distribution Main |  | Tap Connection |  |  | Corrosion |  | 1972-08-02 | 1972-11-30 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | ANODE M.20.3; NOTE: STEEL PIN INSERTED INTO MAIN 112' W/O ABINTON FOR SERVICE TO 35180 BLACKBORN DR. NEW TEE INSTALLED. INST. 10" 1/2 SOLE BY ELECT. WELDER TO CONTROLL LEAKAGE ON MAIN. COULD HAVE BEEN CAUSED BY ELECTYOLISIS FROM 3/4" COPPER WATER PIPE.
24 | 72-20521-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-08-02 | 1972-11-09 | Patch Welded |  | Steel/Wrought Iron |  |  | ANODE M.20.3; LEAK ON LEFT SIDE OF MAIN. DUE TO DAMAGED WRAP BY ROCK IMBEDDED INTO PIPE AT TIME OF INSTALLATION. INSTALLED 2" HALF SOLE BY ELECT. WELDER. 5# ANODE INSTALLED
24 | 72-60262-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-11-30 | 1972-12-01 | Patch Welded |  | Steel/Wrought Iron |  | FREMONT | THIS LEAK IS FROM CORROSION DUE TO WRAP BEING CRACKED WHEN PIPE WAS BENT AND NOT REWRAPPED.
24 |  |  |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron
24 | 72-20514-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  |  | 1973-01-22 | Patch Welded | SEE OTHER SIDE | Steel/Wrought Iron |  | HAYWARD | ANODE M.20.3; SERVICE CURB CONDITION AND NO LEAKAGE. SER LEIS THEN 1" FROM DEING ON TOP OF 2" MAIN. CUT IN STREET TURNED IN A' 10" X 3' 2" ...DEPTHOF MAIN.
24 | 72-20514-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-08-01 | 1973-01-22 | Patch Welded | SEE OTHER SIDE | Steel/Wrought Iron |  | HAYWARD | SERVICE GOV. & CONDITION & NO LEAKAGE. SER LESS THAN 1" FROM BEING ON TOP OF 2" MAIN. SER. TEE VERY GOOD CONDITION. MAIN WRAP VERY GOOD FROM THIS POINT BACK; CORROSION LEAKS CAUSED BY POOR WRAP CENTER ONE BLOW DOWN FROM TWO HOLES THRU MAIN. ... CUT IN STREET TURN ... 5'10" X 3' 2" OM DEPTH OFMAIN 38"
24 | 72-20494-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-07-27 | 1973-02-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | HAYARD | CUT TEST AT 90 PSI. 15M. INST. NEW ...PLASTIC INSET OF 1/2" ALYDL PLASTIC AND COPPER ...WIRE AT SAME TIME...SERVICE PIPE & WRAP IN PERFECT CONDITION ...
24 | 81-21003-1 |  |  | 2 | Other |  | Body of Pipe |  |  | Corrosion |  | 1981-01-28 | 1982-01-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | REPLACED 6 M/M REVAMPED IRONS
24 | 73-60048-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-02-09 | 1973-02-12 | Patch Welded |  | Steel/Wrought Iron |  | FREMONT | REST OF PIPE IN PERFECT CONDITION. 3#ANODE. POOR WRAP IS CAUSE OF CORROSION LEAK. WLECT WELD 3" X 3" PATCH OVER CORRODED AREA
24 | 72-20539-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion | SEE OTHER SIDE | 1972-08-03 | 1972-12-28 | Clamp |  | Steel/Wrought Iron |  | HAYWARD | ANODE M.20.7; INST. 2" 2 BOLT SKINNER CLAMP PAVEMENT REPAIR. 5# ANOD INST. 2" BELOW MAIN AND 3' OUT. LEAK CAUSED BY ELECTROLYSIS DUE TO BAD WRAP, WHEN SER. WAS INST. CHECK 50' EACH SIDE OF LEAK NO OTHER LEAK READINGS
24 | 72-20536-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-08-03 | 1972-12-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | HAYWARD | ANODE M.20.17; FOUND READINS OF 5/10 ON J.W.. LEAK DETECTION UNDER SIDEWALK. CUT AND TEST SERVICE WOULD NOT HOLE. CUT OFF OLD 3/4" SEV. AND INSERTED 1/2" ALDLY PLASTIC AND TIED INTO NEW RISER W./...COCK INST. 1 # ZINK ANODE AT RISER- TESTED ALL CORROSION... GREASER - CHECKED ALL AREAS AROUND NO OTHER LEAKAGES FOUND.
24 | 77-61189-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1977-04-27 | 1977-04-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | NEWARK
24 | 77-61130-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1977-04-27 | 1977-04-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | NEWARK
24 | 73-60242-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-08-09 | 1973-08-17 | Other | CAN | Steel/Wrought Iron |  | HAYWARD | NONE OF PITS LEAKING BUT AT LEASE 2/3 IN DEPTH. 3 1/2" X 2 1/4" BLOWING FUTT BORE FROM MAIN. WRAP WAS DAMAGED WHEN SEWER WAS INST. IN PAST WHICH CAUSED CORROSION LEAKING TO BLOW OUT. 3 5/2" C 1 7/2" ALSO FULL BORE & BLOWING. TEMP REPAIRS BY CLEANING ON ... iNST. 10 X 24" CAN OVER CLAMP FOR PERM REPAIRS 8/17/73 1-5# ANODE INSTALLED. 3 5/10 X 11 3/10 PAVING TURNED IN 8-17-73
|  |  |  | 20 | [11 empty] | Steel/Wrought Iron |  | NEWARK | INSTALLED E.T.S. STATION ON 20" T.P. MAIN 200' & 400' EAST OF LEAK
24 | 11-10059-B | 105 | 10.55 | 6 | Transmission >= 20% SMYS |  | Line Valve |  |  | External Corrosion |  | 2011-05-26 | 2011-05-27 | Replace Main Valve >= 2-inch |  | Steel-Other |  | NEWARK | REPLACE 6" VALVE; HYDRO TEST AT 850 PSIG. X-RAY WELDS REPLACE VALVE E69 IN SAME LOCATION. 105' FROM VALVE TO THORNTON.; REPLACE VALVE ON LINE 105 GOING TO REG PIT.; ENTRY INTO METALLIC INP. PIT DEPTH WAS ENTERED AS .001. BECAUSE OF IGIS REQ DEV5 6/2/11
|  |  |  | 30 | Transmission | [10 empty] | Steel-Other |  | FREMONT
24 |  |  |  | 30 | [11 empty] | Steel-Other |  | NEWARL
24 |  |  |  | 2 | [11 empty] | Steel-Other |  |  | HI TO HI ...INST. IN 17 X 30 BOX USED EXISTING STEEL SER. INTO BOX.
24 |  |  |  | 8 | Distribution Feeder Main | [7 empty] | 1977-02-09 |  |  | Steel/Wrought Iron |  | NEWARK
24 |  |  |  | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  | NEWARK | PROSPECT 20" T.P. MAIN 35' OUT FOR DEPTH. CEDAR 10' E/O W/PL CENTRAL AVE.; NONE
24 | 74-10658-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-01-29 | 1974-01-29 | Other |  | Steel/Wrought Iron |  | FREMONT | INST. 1 1/4" M-2 FITTING AND CUT OF 4' OF SERV. PT. END OF PIPE INST. 1 1/4" WELD CAP ON END.; LEAKING UNDER 1 1/4" SERV. AND ON WELD FOR CAP
| 06-61009-1 |  |  | 0.5 | Service |  | Riser |  |  | Damage by 3rd Party |  | 2006-03-29 | 2006-03-29 | Deactivated Partial Service |  | Aldyl A (Tan or Gray) |  | NEWARL | REPLACED RISER DUE TO LEAKAGE.; REPLACED RISER DUE TO LEAKAGE.
| 07-41009-1 |  |  | 0.5 | Service |  | Plastic Tee Cap |  |  | Plastic Crack Failure |  | 2007-03-26 | 2007-03-26 | Other | PLASTIC REPAIR CAP | Aldyl A (Tan or Gray) |  | NEWARK | INSTALLED PLASTIC REPAIR CAP; ISNTALLED PLASTIC REPAIR CAP
24 | 73-60106-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Corrosion |  | 1973-03-07 | 1973-03-08 | Other |  | Copper |  | FREMONT | 1/8" HOLE IN SER. STOP OFF WITH STL. PIN AND WELDED. CUT & TESTED AT 90 PSIG; LEAK CAUSED BY COPPER TO STEEL LINSULATION. ISNT. 5# ANODE ON MAIN SER. TEE. SEE S.O.#217974;
24 | 72-60249-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-12-22 | 1972-12-26 | Other |  | Steel/Wrought Iron |  | FREMONT | CUT SRV AT MAIN AND MADE STAND UP TEST OF 80# FOR 15 MIN-SER IS OK AND PIPE AND WRAP LIKE NEW CONDITION SO DUST WELDED SMALL LEAK IN SERVICE AND RETESTED OK. TEMP CLAMP 12-22-72/12-26-72 REPAIRD. REINSTALL BARRACED POST 8" FROM SER. AND DOUBLE WRAP SER. IN THAT AREA. DEPTH OF MAIN 33"
24 | 72-40383-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-09-27 | 1972-09-28 | Replace Pipe and/or Service | 1/2 PLASTIC INSERT | Steel/Wrought Iron
24 | 72-40384-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-09-26 | 1972-09-27 | Patch Welded |  | Steel/Wrought Iron |  |  | 5# ANODE INSTALLED; PATCH WELD OVER AREA. PIPE IN VERY GOOD CONDITION EXCEPT IN AREA WHERE WRAP WAS KNOCKED OFF. SOMETIME IN PAST AS THERE IS A ...SERVICE HERE.
24 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | DUBLIN;
24 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | DUBLIN | C/O SERVICE...
24 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | DUBLIN
24 |  |  |  | 2 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | NEWARK
24 | 72-60072-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-05-15 | 1972-05-16 | Other |  | Steel/Wrought Iron |  | ;
24 | 72-60072-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-05-15 | 1972-05-16 | Other |  | Steel/Wrought Iron |  | ;
24 |  |  |  | 4 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | NEWARK | PROSPECT ...
24 | 71-30146-1 |  |  | 3 | Transmission |  | Valves |  |  | Construction Defect |  | 1971-12-20 |  | Other |  | Steel/Wrought Iron |  | ; | FOUND 3" T.P. VALVE LEAKING. FREASED THIS VALVE AND TIGHTENED THE NUTS ON THE HEAD TO CORRECT THIS LEAKAGE.
| 71-60111- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-04-22 | 1971-04-23 | Patch Welded |  | Steel/Wrought Iron |  | FREMONT | THIS LEAK WAS DIRECTLY CAUSED OF ROCK BACK FILLED ON TOP OF WRAP- BREAKING WRAP- ROCK REFERD TO WAS BLACK TOP WAS PROSPECTING DEPTH OF MAIN ON SURVEY WHEN LEAK WAS FOUND.
| 07-61122-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2007-07-31 | 2007-07-31 | Other | CUT & THREAD | Steel/Wrought Iron |  | FREMONT | CUT & THREAD RISER DUE TO LEAKAGE.; CUT & THREAD RISER DUE TO LEAKAGE.
24 |  |  |  | 0.75 | Service |  | Other |  |  | Damage by outside Forces |  | 1979-03-24 | 1979-03-24 | Other |  | Steel/Wrought Iron |  | HAYWARD | SERVICE WAS NOT DAMAGED BUT METER & REGULATOR WAS ELECTROYED WHEN IT CAUGHT ON FIRE
24 | 76-64843-1 |  |  | 0.75 | Other | HOUSE LINE | Body of Pipe |  |  | Corrosion |  | 1976-12-03 | 1977-09-23 |  | %9 ISOLATE | Steel/Wrought Iron |  |  | FOUND LEAK IN 3/4" HOUSE LINE TO CLEANERS (ADDRESS BELOW) 300...C/O 3/4" HOUSELINE PER CUSTOMER REQUEST AS IT ...WHICH WAS NOT IN USE. LINE...DRIVEWAY. MAIN NOT INVOLVED AND NOT EXPOSED. NO LEAK FOUND.
| 71-00111- |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-06-25 | 1971-07-29 | Patch Welded |  | Steel/Wrought Iron |  | ; FREMONT | FOUND SMALL PIN HOLE ON 3/4" MEULLER SERVICE TEE. CUT & TESTED SERVICE. WELDED UP SMALL PIN HOLE ON TEE AND RESPORED SERVICE. 2" MAIN IS IN VERY GOOD CONDITION.
24 |  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  |  | INST. 32LB ANODE AT THIS LOCATION
24 |  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | FREMONT | INST. (1) 32LB ANODE AT THIS LOCATION
24 |  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | FREMONT | ISNT. (1) 32LB. ANODE AT THIS LOCATION
|  |  |  | 2 | Transmission | [7 empty] | 2000-01-10 |  |  | Steel/Wrought Iron |  | NEWARK
24 | 72-60119-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-09-28 | 1972-09-29 | Patch Welded |  | Steel/Wrought Iron |  |  | WRAP IN VERY BAD CONDITION. WELDED (2) 6" PATCHES AND WELDED PITS. INSTALLED 9LB. ANODE.
24 | 72-60121-1 |  |  | 6 | Distribution Main |  | Fitting |  |  | Material Failure |  | 1972-07-10 | 1972-09-27 | Other |  | Steel/Wrought Iron |  |  | LEAK ON (8) BOLT FLANGE TO DEAD END. REPAIRED BY REPLACING (2) BOLTS ON FLANGE
24 | 72-60116-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-10-02 | 1972-10-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | USED (1) 6" CLAMP
| 70-60011 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1970-12-31 | 1971-01-04 | Patch Welded |  | Steel/Wrought Iron |  | NEWARK | INST. (2) PATCHES AND (1) HALF SOLE ON 6" T.P. MAIN ON W/S WILLOW ST. AT 588'-592-+624- S/O ENTERPRISE DR. TO CORRECT LEAKAGE.
|  |  |  | 6 | [11 empty] | Steel-Other |  | NEWARK | LOWERED 6" GAS MAIN R.C.F. BT TO CLEAR STORM DRAIN.
24 |  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | NEWARK | LOWERED 6" GAS MAIN R.C.F. B.T. TO CLEAR STORM DRAIN.
24 |  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | NEWARK | LOWERED 6" GAS MAIN P.C.F. BT. TO CLEAR STORM DRAIN.
24 | 72-60141-1 |  |  | 0.75 | Branch Service |  | Body of Pipe |  |  | Corrosion |  | 1972-11-08 | 1972-11-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | FREMONT | BRANCH SERVICE TO 5716 LEMPKE PL. OFF SER. TO 5700 LEMPKE PL. AND 175' W/O FARWELL DR. FREMONT.; AFTER STAND UP TEST IT WAS NECESSARY TO PLASTIC INSERT THIS BRANCH SERVICE ...MORE THAN ONE LEAK 29' OF 1/2" PLASTIC USED.
24 | 72-60142-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-11-08 | 1972-11-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | A; FREMONT | SERVICE TO 5700 LEMPKE PL. 175' W/O FARWELL DR. FREMONT.; AFTER STAND UP TEST I DEEM IT NECESSARY TO PLASTIC INSTERT THIS SERVICE, DUE TO THE FACT THAT THERE WERE MORE THAN ONE LEAK ON SAID SERVICE. 59" OF 1/2" PLASTIC USED.
|  |  |  | 30 | [7 empty] | 1995-11-09 |  |  |  | Steel/Wrought Iron |  | FREMONT | NOTE: LOCATION 1) AND 2) WERE EXISTING LOCATIONS 3) AND 4) WERE INSTALLED ON 11/9/95; EXCAVATED ON LINE 152 ON...TO INSTALL E.T.S. FOUND...FACE TO FACE...
|  |  |  | 0.75 | Other |  | Fitting |  |  | Construction Defect |  |  |  | Other |  | Steel/Wrought Iron |  |  | ....1 1/4 ELBOW LEAKING BELOW GROUND ON CUST. HOUSE LINE TO SWIMMING POOL. INFORMED CUT OF CONDITION... TURNED OFF HOUSE LINE AT VALVE 1-1972. LEDT FOR TAG#62-3010
| 71-00166- |  |  | 8 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-10-08 | 1971-10-11 | Patch Welded |  | Steel/Wrought Iron |  | SAN LEANDRO | ISNT. (3)...PATCHES PIT...
24 |  |  |  | 8 | Distribution Feeder Main | [6 empty] | 1975-04-22 |  |  |  | Steel/Wrought Iron |  | SAN LEANDRO | ISNTALLED WIRE ON 8" MAIN
|  |  |  | 30 | Transmission | [7 empty] | 1983-09-29 |  |  | Steel/Wrought Iron |  | SAN LEANDRO | CONTROL DIGING OVER LINE...
|  |  |  | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN LEANDRO | MAIN INSPECTION ONLY!; PROSPECT MAIN FOR DEPTH.
24 |  |  |  | 0.75 | Service |  | Other |  |  | Other |  |  | 1975-11-20 | Other |  | Steel/Wrought Iron |  | SAN LEANDRO
24 | 00-00000- |  |  | 0.75 | Service |  | Other |  |  | Other |  |  | 1975-04-07 | Other |  | Steel/Wrought Iron |  | SAN LEANDRO | C/O OLD 3/4 GRIS SEL A/ C NOT IN USE
1 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
[5 empty] | Distribution Feeder Main | [6 empty] | 1991-05-07 |  |  |  | Steel/Wrought Iron |  | SAN LEANDRO
24 | 73-20016-1 |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1973-04-18 | 1974-09-10 | Other |  | Steel/Wrought Iron |  |  | REMADE IRONS DUE TO LEAKAGE.
1 | 71-60064- |  |  | 63 | Distribution Main |  | Body of Pipe |  |  | Other |  | 1971-03-02 | 1971-03-02 | Patch Welded |  | Steel/Wrought Iron |  |  | MAIN LEAKING PIT ON USED BY POUR FIELD WRAP
1 | 71-40155- |  |  | 2 |  |  | Other |  |  | Corrosion |  | 1971-04-19 | 1971-04-20 | Patch Welded |  | Steel/Wrought Iron |  | SAN LEANDRO | THERE WILL BE MORE LEAKS IN ARE IN DUP TO ROCK & WOOD BACKFILL OVER MAIN BIG ENOUGH
1 |  |  |  | 62 | Distribution Main |  | Body of Pipe |  |  | Other |  | 1971-02-08 | 02/00/1971 | Patch Welded |  | Steel/Wrought Iron |  |  | INST WELD PATCH ON 2'" PIT LEAK DUE TO POUR FIELD WHEN ON MAIN
1 |  |  |  | 2 | [14 empty] | NO LINKS SK MAIN
1 |  |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  |  |  | Patch Welded |  | Steel/Wrought Iron |  | ; | INST. 3 WELD PATCH ON PIT ON 3" MAIN PITS NOT LEAKING A SD OUT & TEST
24 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1975-07-01 | Other |  | Steel/Wrought Iron |  | SAN LEANDRO | CUT SER OFF AT MAIN
24 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1975-11-17 |  | Other |  | Steel/Wrought Iron |  |  | INST. 3" P.S.P. BT. TO MAKE
24 | [6 empty] | Other |  |  | Other | ; | [6 empty] | CASTRO VALLEY
24 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron
24 | 72-20107-1 |  |  | 0 | Distribution Main |  | Other |  |  | Other |  | 1972-01-10 |  | Other |  | Other
24 | 72-20105-1 |  |  |  | Distribution Main |  | Other |  |  | Other |  | 1972-01-10 |  | Other |  | Other
| 08-24117-1 | [16 empty] | SAN LEANDRO
24 |  |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron |  | SAN LEANDRO | ALTER LEAKAGE
24 |  |  |  | 3 | Distribution Feeder Main | [6 empty] | 1977-02-07 |  |  |  | Steel/Wrought Iron
24 |  |  |  | 3 | Transmission | [7 empty] | 1977-06-17 |  |  | Steel/Wrought Iron |  |  | TURNED OFF 2" VALVE + CUT OFF EXISTING 3" STL MAIN. INST BLANK FLANGE ON VALVE.
24 | 73-20021-1 |  |  | 06.00` | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-04-19 | 1973-05-01 | Other | WELDED CAN AROUND MAIN | Steel/Wrought Iron |  |  | DUG DOWN TO MAIN. FOUND NO LEAKS ON MAIN.
| 02-40000-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | External Corrosion |  | 2002-01-08 | 2002-01-08 | Service Entirely Replaced |  | Steel/Wrought Iron |  | SAN LORENZO | REPLACE 3/4" SLL WITH 1/2 PL
24 |  |  |  | 3 | Distribution Main |  | Other |  |  |  |  | 1976-02-22 |  |  |  | Steel/Wrought Iron |  | HAY | REVIEW 1" SERVICE A/C OOLD SERVICE UNDER BLDG AS PER ENGINEERING. NO LEAKAGE, MOVED METER LOCATION OUTSIDE
24 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1972-04-21 |  | Other |  | Steel/Wrought Iron
24 |  |  |  | 1.25 | [6 empty] | NONE |  | 1983-05-13 |  |  | Plastic |  | HAYWARD | CUT TEST & TRANSFERED 1 1/4" PL MAIN FROM 3" RP STL MAIN ON S/S MEDFORD AVE. 16' OUT TO 4" PL MAIN S/S MEDFORD AVE 9'
24 | 72-60085- |  |  | 0.75 | Service |  | Girth Weld |  |  | Construction Defect |  | 1972-03-30 | 1972-05-15 | Other |  | Steel/Wrought Iron
815 | 71-40335- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1971-10-18 | 1971-10-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | RERAN SER. WITH 1/2 PLASTIC PAVING CUT 2 1/2 X 7'
815 | 71-60113- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-05-24 | 1971-05-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | HAYWARD | 2" MAIN NEEDS TO BE REPLACED POOR CONDITION
24 | 77-20108-1 |  |  |  | Other |  | Other |  |  | Material Failure |  | 1977-02-17 | 1978-01-27 | Other |  | Other |  | HAYWARD | FOUND LEAKAGE AND GLASS PLATE TO METER SEAL PLATE TO CORRECT LEAKAGE ACCT 1957. CHANGE CURB METER COVER A/C BROKEN
24 | 78-63034-1 |  |  | 0.75 | Service |  | Fitting |  | CAP | Other |  | 1978-04-27 | 1978-12-28 | Other |  | Steel/Wrought Iron |  |  | FOUND SERVICE CAP LEAKING. LEAKAGE WAS CORRECTED BY REDOPING AND TIGHTENING.
24 | 77-20113-1 |  |  |  | Other |  | Fitting |  |  | Construction Defect |  | 1977-02-17 | 1978-02-10 | Other |  | Other |  | HAYWARD | BOR TESTED SERVICE FOUND OKAY SOAP TESTED METER SETIOUN CORE ON 3/4" 1100 COCK LEAKING TIGHTEN CORE TO CORRECT LEAKAGE
| 00-00000-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Unknown |  | 2000-10-24 | 2008-09-23 | Other | RESEALED CAP | Steel/Wrought Iron |  | HAYWARD; | LEAK AT SPLIT CONTROL FITTING CAP.
24 |  |  |  | 0.5 | Distribution Main |  | Other |  |  | Other |  |  | 1975-01-13 | Other |  | Steel/Wrought Iron |  | SAN LORENZO | CUT TEST 1/2" PLASTIC INSERT. TEST-OK
1 | 71-20162- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-05-25 | 1971-05-27 | Patch Welded |  | Steel/Wrought Iron |  | SAN LORENZO | FOUND LEAK ON 2" H.P.M. 12' OUT 110' W/OF BOCKMAN RD. ON VIP HORNITOS. HAD ARC WELDER INSTALL A 2" PATCH TO MAKE PERMANENT REPAIRS PAVING CUT 4 1/2' X 3 1/2' X 3"
24 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1972-08-23 |  | Other |  | Steel/Wrought Iron |  | SAN LORENZO | H.T. HOLE 4'X6' X36" DEEP EXPOSED SEPERATED 17268 VIA CUT & TESTED 3/4" SERVICE NO LEAK. CHECKED 4' OF 2 . NO LEAK APPARNELY LEAK IN SERVICE TO 17260 VIA CORMEN WAS THE ONLY ONE IN THE VACCINITY
| 71-20188-1 |  |  |  | Other |  | Other |  |  | Other |  | 1971-06-30 |  | Other |  | Other
|  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | HAYWARD
|  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | HAYWARD
|  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel-Other |  | HAYWARD
|  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | HAYWARD
|  |  |  | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | HAYWARD | LOCATED 12" D.F.M. FOR DEPTH.
|  |  |  | 4 | Distribution Feeder Main | [6 empty] | 1981-06-01 |  |  |  | Steel/Wrought Iron |  | HAYWARD
24 |  |  |  | 4 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | HAYWARD | REMOVE 4' VALVE AND SERV. CLOSED VALVE E10 AND OPEN VALVE E11
24 |  |  |  | 0.75 | Service |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron |  | HAYWARD | CHECK SERVICES 20674 & 20673 AND MAIN FOUND NO LEAKAGE
24 | 10-20869-1 | 1 |  | 0.75 | Single Service |  | Riser |  |  | Other |  | 2010-10-20 | 2011-01-05 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | HAYWARD | TIGHTEN FITTING & SAP TESTED-OK
24 | 10-20880-1 | 1 |  | 0.75 |  |  | Fitting |  |  | Other |  | 2010-10-20 | 2010-01-05 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | HAYWARD | TIGHTEN FITTING SOAP TESTED OK
|  |  |  | 0.75 | Other |  | Other |  |  | Other |  |  | 1972-05-22 | Other |  | Other |  | HAYWARD | REPAIRS TO IRON CORRECTION IN METER BOX
1 | 71-40282- |  |  | 0.75 | Single Service |  | Body of Pipe |  |  | Corrosion |  |  |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | REMOVE 1/2" ...C/O ...WELDED ONE PATCH AND...PITS ON 5
| 93-20261-1 |  |  |  | Other |  | Other |  |  | Other |  |  |  | Other |  | Other |  |  | NO INDICATION OF GAS IN AREA 822-93.
24 | 93-20257-1 |  |  |  | Other |  | Other |  |  | Other |  | 1993-05-24 |  |  |  | Steel-Other |  |  | NO INDICATION OF GAS IN AREA.
| 77-60001-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Corrosion |  | 1977-01-03 | 1977-01-07 | Other |  | Steel/Wrought Iron |  |  | CUSTOMER NOTIFIED TO MAKE OWN REPAIRS.
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1977-09-09 |  | Other |  | Steel/Wrought Iron
24 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1975-09-09 |  | Other |  | Steel/Wrought Iron
|  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1975-02-19 | Other |  | Steel/Wrought Iron |  | CASTRO VALLEY
|  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  |  | 1975-06-27 | Other |  | Steel/Wrought Iron |  | CASTRO VALLEY
24 |  |  |  | 4 | Distribution Feeder Main |  | Other |  |  | Corrosion |  | 1977-05-24 |  | Other |  | Steel/Wrought Iron |  | CASTRO VALLEY | HOLD WAS OPEN TO CLEAN CONTROL ON 4" GAS MAIN
|  |  |  | 6 | Distribution Main |  | Other |  |  | Other |  | 1972-05-12 |  | Other |  | Steel/Wrought Iron
24 | 00-00000-0 |  |  | 6 | Distribution Main |  | Other |  |  | Other |  | 1972-05-10 |  | Other |  | Steel/Wrought Iron
24 | 00-00000-0 |  |  | 6 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron
24 | 76-64583-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1976-09-13 | 1977-02-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | MAIN REPL.
| 71-40222- |  |  | 2 |  |  | Other |  |  | Corrosion |  | 1971-07-01 | 1971-07-01 | Patch Welded |  | Steel/Wrought Iron |  |  | THIS LEAKAGE WAS CAUSED BY PROBE BAR CAUSING ELECTROLYSIS
| 96-60262-1 |  |  |  | Gathering |  | Other |  |  | Corrosion |  | 1996-07-19 | 1996-07-19 | Patch Welded |  | Steel/Wrought Iron |  |  | WELDED 2" PATCH ON 2" MAIN.
| 95-20150-1 |  |  | 2 | Gathering |  | Other |  |  | Damage by Natural Forces |  | 1996-06-25 | 1996-07-28 |  |  | Steel/Wrought Iron |  |  | THIS SHOULD BE GRADED A GRADE 3
| 88-20922-1 |  |  |  | Other |  | Other |  |  | Other |  | 1988-05-31 |  | Other |  | Copper |  |  | OLD METER REPLACED WITH NEW ONE AND ALL WORKED. PUT IN FOR RECHECK
| 88-20941-1 |  |  |  | Other |  | Other |  |  | Other |  | 1988-05-23 |  |  |  | Other |  |  | NO READINGS FOUND AT THIS LOCATION.
| 87-60038-1 |  |  |  | Other |  | Other |  |  | Other |  | 1987-05-04 |  | Other |  | Other |  | HAYWARD | FOUND NO INDICATION OF LEAKAGE 1/26/1988
| 86-63070-1 |  |  |  | Other |  | Other |  |  | Other |  | 1986-05-12 |  | Other |  | Other |  | CASTRO VALLEY | THIS LEAK WAS FOUND 2 MONTHS AGO. NO NEW LEAK IN THE AREA;
| 85-21014-1 | [10 empty] | 1985-04-10 | [5 empty] | FREMONT
815 | 71-30029- |  |  | 0.75 | Service |  | Tap Connection |  |  | Other |  | 1971-08-11 | 1971-10-13 | Other | TIGHTEN PLUG & CAP ON 3/4" SERV TEE | Steel/Wrought Iron |  |  | LIGHTEN PLUG AND CAP ON 3/4" SERV TEE AND CHECK FOR THE
24 | 76-30330-1 |  |  | 0.5 | Other |  | Fitting |  |  | Other |  | 1976-04-07 | 1977-03-24 | Patch Welded |  | Steel/Wrought Iron |  | HAYWARD
24 | 80-20554-1 |  |  | 0.75 |  |  | Body of Pipe |  |  | Corrosion |  | 1980-06-10 | 1981-04-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | HAY
24 | 76-30290-1 | [5 empty] | Other |  |  | Other |  | 1976-04-05 |  | Other |  | Other |  | HAYWARD
24 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  | 1977-03-17 | Other |  | Steel/Wrought Iron |  | HAYWARD
| 99-40025- |  |  | 0.25 | Service |  | Body of Pipe |  |  | Digin |  | 1999-03-24 | 1999-03-24 | Mechanical Repair Fitting - Fitting |  | Aldyl A (Tan or Gray) |  | HAYWARD | REPLACED 3' ET 1 1/4' PLASTIC
|  |  |  | 4 | Distribution Main |  | Other |  |  | Other |  | 1972-06-20 |  | Other |  | Steel/Wrought Iron
24 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1975-09-22 |  | Other |  | Steel/Wrought Iron |  | HAYWARD
815 | 71-40134- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1971-04-02 | 1971-04-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | CUT ONE 3/4" SPLIT PART TO REPLACE 12 INCHES OF 3/4" STEEL PIPE
| 24 | 76-30423-1 |  |  | Other |  | Meter |  |  | Other |  | 1976-04-20 | 1977-03-30 | Replace Pipe and/or Service |  | Other
[18 empty] | HAYWARD | REPLACED 4 S.B METER USE A 175 ROCKWELL
|  |  |  | 0.03 | Distribution Feeder Main
|  |  |  | 0.03 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
|  |  |  | 2 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
815 | 71-30045- |  |  |  | Service |  | Fitting |  |  | Other |  | 1971-08-20 | 1971-09-24 | Other |  | Steel/Wrought Iron
24 | 72-20405-1 |  |  | OT | Other |  | Other |  |  | Other |  |  |  | Other |  | Plastic
24 | 79-20219-1 |  |  |  | Other |  | Other |  |  | Other |  | 1979-10-12 | 1980-10-13 |  |  | Other |  | SL.
24 |  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron
| 72-80110-1 |  |  |  | Other |  | Other |  |  | Other |  |  |  | Other |  | Other |  |  | CHECKED COMPLETE BLACK, ALL WATER-BOXES CURB-VALVE, ALL PLUGS OVER SCHOOL SERVICE, ALSO MANBOLES& CULVERTS COULD NOT DETECT ANY INDICATION OF GAS LEAKAGE
24 | 76-30575-1 | [7 empty] | CUSTOMER HOUSELINE | Other |  | 1976-05-04 | 1977-02-24 | Other |  | Wrought Iron
[5 empty] | Service |  | Other |  |  | Material Failure |  |  | 1972-06-01 | Other |  | Steel/Wrought Iron
815 | 71-40207- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1971-06-17 | 1971-06-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | HAYWARD | REPLACED 2 OF SER A/C TO HIGH
|  |  |  | 2 | Distribution Main | [10 empty] | Steel/Wrought Iron
24 |  |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-12-28 | 1974-01-03 | Clamp |  | Steel/Wrought Iron
24 | [6 empty] | Other |  |  | Other |  | 1975-02-28 |  | Other |  | Steel/Wrought Iron
;
815 | 71-30050- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1971-08-20 | 1971-09-22 | Other |  | Steel/Wrought Iron |  | HAYWARD | ...WELDED OVER PIT
| 71-20285- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1971-09-10 | 1971-09-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | HAYWARD | REPLACE 3/4". 5 WAS WELDS ON 2" MAIN ALSO BLINDLY PITTED
|  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | HAYWARD
24 | 74-21693-1 |  |  |  | Other |  |  |  |  | Other |  | 1974-07-02 |  |  |  | Other |  | HAYWARD | HOUSE LINE LEAK REFERED JOB TO SERVICE DEPT. AT 3 PM TO MAKE TEST
24 |  |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 1974-09-13 |  | Other |  | Steel/Wrought Iron
24 |  |  |  | 30 | Transmission | [6 empty] | 1975-11-14 |  |  |  | Steel/Wrought Iron |  |  | E.T.S. ON FINE 153 OPPOSITE W/P/L @ ANDREW RD. E.T.S. INSTRUCTED APP 6 FT FROM MAIN
| 76-30641-1 |  |  |  | Other |  | Fitting |  |  | Material Failure |  | 1976-05-12 | 1977-04-14 | Other |  | Other |  |  | NO MAIN INSP. LINK AT METER. FOUND NIPPIC BETWEEN RAY.& STOP CORK LEAKING. RESPOND NIPPIC STOPPING
815 |  |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1971-07-03 | 1971-09-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | FOUND BRANCH SERV LEAKING REPLACE SERV WITH 1/2" PLASTIC, USING DO SERV AS A CASEING
24 | 76-00020-1 |  |  | 0.5 | Service |  | Other |  |  | Construction Defect |  | 1976-04-20 | 1977-03-25 | Replace Pipe and/or Service |  | Plastic |  |  | A/C ON POWELL WAS LEAKING
| 02-00000-1 |  |  | 0.75 | Service |  | Other |  | UNION | Other | THREADS | 2002-10-28 | 2002-11-10 | Other | TIGHTEN FITTINGS | Steel/Wrought Iron |  | SAN FRANCISCO | ALSO REPLACE BOX OVER HI-TO-SET
HAYWARD
| 97-40013-1 |  |  |  | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1997-05-26 | 1997-05-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | HAYWARD
HAYWARD
| 06-60020-1 | [16 empty] | HAYWARD
24 |  |  |  |  | Transmission | [10 empty] | Steel/Wrought Iron
24 | 71-1 |  |  | 8 | Distribution Feeder Main | [6 empty] | 1974-03-20 |  |  |  | Steel/Wrought Iron |  | LIVERMORE
| 73-40106-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-02-14 | 1973-02-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron
| 81-62021-1 |  |  |  | Service |  | Body of Pipe |  |  | Corrosion |  | 1981-03-31 | 1981-04-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PLEASONTON | RERUN SERVICE DUE TO LEAKAGE
24 | 72-40546-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-10-08 | 1972-12-11 | Patch Welded |  | Steel/Wrought Iron |  | PLEASONTON
|  |  |  | 6 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron | ; |  | INSTALLED NEW 1/2" PLASTIC SERVICE
| 72- |  |  | 2 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
| 73- |  |  | 8 | Distribution Feeder Main
| 08-42447-1 |  |  | 0.5 | Single Service |  | Riser |  |  | Atmospheric Corrosion |  | 2008-12-09 | 2008-12-09 | Other | REPLACED RISER | Other | RISER CORRODED | PLEASONTON | RISER REPLACED
72-
24 |  |  |  | 8 | Distribution Feeder Main | [7 empty] | 1977-05-06 | [5 empty] | LOWERED D.F.M. MAIN INSTALLED 2-8" BOTTOM TAPS TO LOWER MAIN TO A DEPTH OF "1" FROM EXISITING GRAUE TO TON OF 8" MAIN
24 |  |  |  | 0.75 | Other | C/O HIMADE TEE A/C LEAKAGE | Body of Pipe |  |  | Corrosion |  | 1979-12-13 | 1979-12-17 | Replace Pipe and/or Service | CAN OVER | Steel/Wrought Iron
27 | 73- |  |  | 2 | Other | [10 empty] | Steel/Wrought Iron
24 |  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | PLEASONTON
|  |  |  | 4 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
24 |  |  |  | 8 | Distribution Feeder Main
24 | 72- |  |  | 2 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron
24 | 72-40558-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-09-27 | 1972-12-20 | Patch Welded |  | Steel/Wrought Iron |  | PLEASONTON | LOFT 2"
24 | 73-40081-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-02-02 | 1973-02-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PLEASONTON | 3/4 SERV WITH 1/2" PLASTIC
| 71-40304- |  |  | 2 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 1971-09-21 | 1971-09-22 | Other |  | Steel/Wrought Iron |  | LIVERMORE | FOUND THREADS ON 2" P.C.E. CAP LEAKING REDOPED THREADS & CAP AND REPLACES ARE NO OTHER LEAKAGE.
24 |  |  |  | 6 | Distribution Feeder Main | [12 empty] | LIVERMORE
24 |  |  |  | 4 | Distribution Main | [12 empty] | FILMORE
| 71- |  |  |  | Distribution Main |  | Body of Pipe |  |  | Material Failure |  | 1971-09-08 | 1971-09-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | SERVICE LEAKING AT MAIN AND ... COULD NOT USE OLD SERVICES FOR AN SEEING IS STEEL
1 | 00-00000- |  |  | 2 | Distribution Main |  | Other |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron |  | LIVERMORE
24 | 75-62108-1 |  |  | 4 | Transmission |  | Fitting |  |  | Other |  | 1975-04-28 | 1975-04-29 | Other |  | Steel/Wrought Iron |  | FREMONT
24 | 74-60584-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1974-12-06 | 1974-12-26 | Patch Welded |  | Steel/Wrought Iron |  | PLEASANTON
| 98-60107- |  |  | 12 | Transmission |  | Valves |  |  | Other | VALVS | 1998-11-13 | 1998-12-05 | Other |  | Steel/Wrought Iron |  | HAYWARD | INSTALLED GREASE FIG TO REPAIR LEAK.
|  |  |  | 4 | Transmission |  | Valves |  |  | Material Failure |  | 1998-08-02 | 1998-09-04 | Other | REPLACE VALVE | Steel/Wrought Iron |  | HAYWARD
1 | 71-60094- |  |  | 8 | Transmission |  | Fitting |  |  | Construction Defect |  | 1971-02-10 | 1971-02-01 | Other | TIGHTENED BOLTS ON FLANGES | Steel/Wrought Iron |  | FREMONT
4 | 72-60071-1 |  |  | 3 | Transmission |  | Body of Pipe |  |  | Construction Defect |  | 1972-05-11 | 1972-05-11 | Other |  | Steel/Wrought Iron |  | HAYWARD
| 99-42423-1 |  |  | 4 | Transmission |  | Fitting | Valves |  | Damage by 3rd Party |  | 1999-06-07 | 1999-06-07 |  |  | Steel/Wrought Iron |  | LIVERMORE | WELDED OVER BLEED OFF 4" GATE VALVE. INSTALLED 24 X 36 CONCRETE BOX OVER VALVE STEM
| 75-42006-1 |  |  | 20 | Transmission |  | Girth Weld |  |  | Material Failure |  | 1975-01-30 | 1975-01-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | NEWARK
24 | 71-30144-1 |  |  | 3 | Transmission |  | Valves |  |  | Construction Defect |  | 1971-12-20 | 1972-01-13 | Other |  | Steel/Wrought Iron |  |  | FOUND 3" T.P. VALVE LEAKING GREASED THIS VALVE AND TIGHT THE NUTS ON THE HEAD TO CORRECT THIS
| 93-21037-1 |  |  | 2 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1993-08-02 | 1993-12-03 | Patch Welded |  | Steel/Wrought Iron |  |  | FOUND LEAKAGE ON 2" STEEL, INSTALLED 2X6 HALF SOLE
| 97-20017-1 |  |  | 0.75 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1997-02-14 | 1998-01-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron
24 | 74-20358-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-01-29 | 1974-09-24 | Other |  | Steel/Wrought Iron |  |  | NOTE STUB LEAKING CUT OFF STUB TO MAKE PERM.
24 | 76-64424-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1976-06-15 | 1976-06-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | REPLACED SERVICE IN ORDER TO ELIMINATE LEAKAGE
24 | 75-62460-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1975-12-22 | 1976-11-19 | Other |  | Steel/Wrought Iron |  | LIVERMORE
24 | 71-20294-1 |  |  | 1.25 | Other |  | Fitting |  |  | Corrosion |  |  | 1971-11-22 | Other |  | Steel/Wrought Iron |  |  | HAYWARD
24 | 80-65085-1 |  |  | 0.75 | Other |  | Tap Connection |  |  | Damage by outside Forces |  | 1980-09-09 | 1980-09-09 | Other |  | Steel/Wrought Iron |  | PLEASANTON
24 | 78-63097-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-08-18 | 1978-08-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | HAYWARD | INST. 3/4 M. FITTING TO SHUT OFF GA TO REPAIRS BROKEN 3/4 STEEL STATICK LINE WITCH WAS UNDER GROUND.
24 | 72-20564-1 |  |  | 3 | Other |  | Valves |  |  | Other |  | 1972-08-22 | 1972-08-22 | Other |  | Steel/Wrought Iron |  | FREMONT | .301 CALLED IN BY FOOT SURVEY NEAR DRINKING FOUNTAIN AT GOMES ELEMENTARY SCHOOL. FOUND BONNET ON CUSTOMER OWNED 3" VALVE LEAKING. TIGHTEN BOLTS & GREASE VALVE TO CREAM LEAK, BAR TESTED-FOUND CUSTOMER & HOUSE LINE OK.
24 | 72-60104-1 |  |  | 0.5 | Other |  | Meter |  |  | Material Failure |  | 1972-07-26 | 1972-08-01 | Other |  | Other |  |  | 3/4 PLUG ON HOUSELINE TEA LEAKING DOPED & TIGHTEN PLUG. METER CRACKED ON OUTLET SIDE REFERED TO SERVICE DEPT. METER WILL BE REPLACED 8-1-1972 METER & PLUG TESTED
24 | 77-40042-1 |  |  | 2 | Other |  | Fitting |  |  | Material Failure |  | 1977-03-03 | 1977-03-04 | Other |  | Steel/Wrought Iron |  | HAYWARD | ;
24 | 76-64658-1 |  |  | 0.75 | Other |  | Other |  |  | Other |  | 1976-10-13 | 1977-04-13 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | UNION CITY | FOUND 301 ON 2"-5 METER MANIFOLD (CURB BOX) REPLACED MANIFOLD.
24 | 76-30124-1 |  |  | 0.75 | Other |  | Fitting |  |  | Corrosion |  | 1976-03-15 | 1976-11-18 | Other |  | Steel/Wrought Iron |  | HAYWARD
24 | 73-20062-1 |  |  | 0.75 | Other |  | Fitting |  |  | Material Failure |  | 1973-04-25 | 1974-05-07 | Other |  | Other |  | HAYWARD
24 | 73-20445-1 |  |  | 0.75 | Other |  | Fitting |  |  | Construction Defect |  | 1973-12-06 | 1973-12-13 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | REPAIR LEAKAGE FITTING ON NEG SET
24 | 76-30470-1 |  |  | 0.75 | Other |  | Tap Connection |  |  | Corrosion |  |  | 1977-03-10 | Other |  | Steel/Wrought Iron |  |  | FAUREL CAP ON OLD 3/4 SERVICE THE & LEAKING + UPLOAD CAP. THIS TEE WAS SERVICE CUT OFF
24 | 73-40249-1 |  |  | 2 | Other |  | Body of Pipe |  |  | Corrosion |  | 1973-03-20 | 1973-03-25 | Patch Welded |  | Steel/Wrought Iron |  |  | WRAP WHEN THEY INSTALLED WITH INSTALL TWO 3"X4" PATCHES
24 | 76-64735-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1976-10-27 | 1976-10-27 | Other |  | Steel/Wrought Iron |  | LIVERMORE | CUT OFF UNUSED 3/4" STEEL STUB SERVICE DUE TO LEAKAGE
24 | 73-40522-1 |  |  | 1.25 | Other |  | Longitudinal Weld |  |  | Corrosion |  | 1973-10-02 | 1973-11-06 | Patch Welded |  | Steel/Wrought Iron |  | LIVERMORE | DEF E-4
24 | 76-64731-1 |  |  | 0.25 | Other | NONE USE | Body of Pipe |  |  | Corrosion |  | 1976-11-02 | 1977-05-12 | Other |  | Steel/Wrought Iron |  | LIVERMORE | FOUND NONE USE NUR SERVICE LEAKING REPAIRS BY C/O
24 | 73-00154-1 |  |  | 3 | Other |  | Body of Pipe |  |  | Other |  | 1973-07-31 | 1973-09-19 | Other |  | Plastic
24 | 79-60053-1 |  |  | 0.5 | Other | STUB | Other |  | DEAD END | Damage by outside Forces |  | 1979-06-20 | 1979-06-20 | Other |  | Plastic |  | HAYWARD | STUB WAS DEAD END INSTEAD 5/8'
24 | 72-20134-1 |  |  | 0.75 | Other |  | Other |  |  | Other |  | 1972-01-12 | 1972-05-22 | Other |  | Other |  |  | REPAIRS TO IRON CONNECTION IN METER BOX
24 | 74-21195-1 |  |  | 0.75 | Other |  | Other |  |  | Material Failure |  | 1974-06-04 | 1974-06-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron
24 | 73-20002-1 |  |  | 0.75 | Other | SEN. IRON. CON. | Fitting |  |  | Other | LOOSE FITTING ON IRONS CON. | 1973-04-16 | 1973-04-18 | Other | DOPED & TIGHTEN FITTING | Steel/Wrought Iron |  |  | MAIN NOT EXPOSED
24 | 73-20453-1 |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1973-12-06 | 1973-12-13 | Other | TIGHTER FITTINGS | Steel/Wrought Iron |  |  | TIGHTEN FITTING
|  |  |  | 0.75 | Other |  | Fitting |  |  | Material Failure |  |  | 1972-05-22 | Other |  | Other |  |  | FOUND LEAKAGE ON METER CORRECTION ALL REPHINS WERE PERMANENT
24 | 76-64064-1 |  |  | 0.75 | Other |  | Physical/Mechanical Joint |  |  | Other |  | 1976-01-21 | 1976-11-01 | Other |  | Steel/Wrought Iron |  |  | CAP LEAKING ON SAV. A. VALVE REDOPED CAP AND TIGHTENED
24 | 74-21537-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-06-25 | 1974-06-27 | Other |  | Steel/Wrought Iron |  | SAN LEANDRO
24 | 83-40121-1 | 105 |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1983-10-15 | 1983-10-15 | Other |  | Steel/Wrought Iron |  | HAYWARD | REPAIRING LEAKING VALVE IN BLOCK VALVE AT 18.45 LINE 105; GREASED AND WORKED VALVE TO STOP LEAKAGE
24 | 80-62554-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1980-11-14 | 1981-08-05 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | DUBLIN | INSTALLED (1) 12" X 30" STAINLESS STEEL LEAK CLAMP & ENCLOSED IT WITH (1) 16" STEEL CAN 4' LONG - SEE DETAIL SKETCH-
24 | 93-00001-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1993-11-22 | 1993-12-22 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | HAYWARD | WELD PATCH ON MAIN.; CORROSION LEAK ON 8" STL D.F.M. MAIN
24 | 93-00001-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1993-11-22 | 1993-12-22 | Patch Welded |  | Steel-Other |  | HAYWARD | WELD PATCH ON MAIN.; CORROSION LEAK ON 8" STL D.F.M. MAIN
24 | 98-00002-1 |  |  | 8 | Distribution Feeder Main |  | Tap Connection |  |  | Construction Defect |  | 1998-10-14 | 1999-03-31 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | HAYWARD | ON MAIN 466' S/O SAN LEANDRO BLVD. CANNED NEARING SCREED FITTINGS
24 | 77-61010-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1977-02-09 | 1977-02-09 | Clamp |  | Steel/Wrought Iron |  | NEWARK
24 | 77-00017-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1977-03-29 | 1978-02-22 | Clamp |  | Steel/Wrought Iron |  | NEWARK | PERMANENT REPAIR BY 8" SKINNER CLAMP. FULL RUBBER NO LEAKAGE AFTER CLAMP INSTALLED
24 | 76-64905-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-12-20 | 1976-12-20 | Clamp |  | Steel/Wrought Iron |  | NEWARK | REPAIRED WITH SKIMMER CLAMP
24 | 79-00006-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1979-02-28 | 1979-08-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | NEWARK
24 | 79-00007-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1979-02-28 | 1979-08-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | NEWARK | COMPLETED ON GM 189891
1 | 74-41004-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-12-03 | 1974-12-03 | Patch Welded |  | Steel/Wrought Iron
24 | 74-40934-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-10-01 | 1974-10-02 | Patch Welded |  | Steel/Wrought Iron |  | NEWARK | INST. (1) 3" PATCH ON T.P. 8" MAIN ALSO HALF SOLE AND (1) 9LB ADNODE.
24 | 81-61056-1 |  |  | 2 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1981-10-12 | 1982-03-22 | Other |  | Steel/Wrought Iron |  | FREMONT | GREASED VALVE...
24 | 78-63137-1 |  |  | 12 | Distribution Feeder Main |  | Physical/Mechanical Joint |  |  | Other |  | 1978-11-15 | 1978-11-16 | Other |  | Steel/Wrought Iron |  | HAYWARD | CUT OFF 1/4" METER VALVES OFF... 2" CROSS TIE MAIN ALL CLEAR.
24 | 73-40326-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-06-04 | 1973-06-05 | Patch Welded |  | Steel/Wrought Iron |  | FRENONT | WELDED 3 PATCHES OVER THREE PITS ON THE... INSTALLED #1-5ANODE
24 | 95-00001-1 |  |  | 8 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1995-10-16 | 1995-11-27 | Tighten Cap or Bolt |  |  |  | HAYWARD | LEAK ON CAN TO SAV-A-VALVE FITTINGS DOPED AND REINSTALLED PLUG TIGHTENED CAP.
24 | 76-64810-1 |  |  | 8 | Distribution Feeder Main |  | Other Welds |  |  | Construction Defect |  | 1976-11-22 | 1976-11-22 | Other |  | Steel/Wrought Iron |  | SAN LEANDRO
24 | 77-60263-1 |  |  | 10 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1977-11-30 | 1978-06-16 | Other |  | Steel/Wrought Iron |  | HAYWARD | 2" ZONE VALVE WAS LEAKING PACK IT WITH GREASE.
24 | 76-64212-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-03-30 | 1977-02-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | NEWARK | MAIN REPLACEMENT G.M.185642
24 | 76-64210-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-03-30 | 1977-02-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | NEWARK | MAIN REPLACEMENT G.M. 185642
24 | 76-64213-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-03-30 | 1977-02-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | NEWARK | MAIN REPLACEMENT G.M. 185642
24 | 76-64204-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-03-30 | 1977-02-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | NEWARK | MAIN REPLACEMENT G.M. 185642;
24 | 76-64205-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-03-30 | 1977-02-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | NEWARK | MAIN REPLACEMENT G.M. 185642
24 | 76-64206-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-03-30 | 1977-02-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | NEWARK | MAIN REPLACEMENT G.M. 185642;
24 | 76-64207-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-03-30 | 1977-02-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | NEWARK; | MAIN REPLACEMENT G.M. 185642
24 | 76-64208-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-03-30 | 1977-02-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | NEWARK | MAIN REPLACEMENT G.M.185642
24 | 82-64055-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1982-09-16 | 1983-08-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | NEWARK
24 | 83-00001-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1983-02-03 | 1983-03-14 | Other |  | Steel/Wrought Iron |  | HAYWRD | GREASED ...
24 | 88-00001-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1988-11-21 | 1989-02-10 | Other |  | Steel/Wrought Iron |  | HAYWARD | GREASED VALVE TO REPAIR LEAKAGE.
24 | 78-43076-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-03-17 | 1978-03-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN LEANDRO | ARC WELDER INST. 2-M FITTINS ON 2" MAIN TO REPAIR 4' LEAKING. ALSO 1 1/4" SERVICE LEAKING REPAIR 1/2 ...INSIDE...
24 | 77-61016-1 |  |  | 8 | Distribution Feeder Main |  | Other |  |  | Other |  | 1977-03-07 | 1978-03-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | NILES
24 | 80-64087-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1980-11-03 | 1980-11-04 | Patch Welded |  | Steel/Wrought Iron |  | FREMONT
24 | 77-60066-1 |  |  | 1.25 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1977-03-10 | 1978-03-30 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN LEANDRO | ... 1 1/4" M FITTING ONMAIN TO WELD PATCH
24 | 76-64209-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-03-30 | 1977-02-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | NEWARK | MAIN REPLACEMENT G.M. 185642
24 | 73-40299-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-05-10 | 1973-05-15 | Clamp | SKINNER CLAMP | Steel/Wrought Iron
24 | 77-40055-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1977-02-28 | 1977-03-25 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | DUBLIN
24 | 77-62153-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1977-08-25 | 1977-08-29 | Patch Welded |  | Steel/Wrought Iron |  | LIVERMORE | INST. 5 X 5" PATCH ON 8" MAIN 58' OUT (?) ON SOUTHSIDE...; THIS MAIN IS COVERED WITH SHALLOW PITS, THERE WAS NO VISABLE PIT WHERE IT WAS LEAKING. THERE WAS A POROUS AREA ABOUT 1/2 IN DIAMETER THAT THE GAS WAS SEEPING THOUGH
24 | 77-62190-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  |  | 1977-12-15 | Patch Welded |  | Steel/Wrought Iron
24 | 74-21039-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-05-21 | 1974-05-22 | Patch Welded |  | Steel/Wrought Iron |  | LIVERMORE
24 | 72-40276-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-09-13 | 1972-09-14 | Patch Welded |  | Steel/Wrought Iron |  | LIVERMORE
24 | 81-00009-1 |  |  | 8 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1981-02-19 | 1981-08-13 | Other |  | Steel/Wrought Iron |  | FREMONT | GREASED LEAKING VALVE. STOPPED LEAK VALVE IS LOCATED BEHIND 6' B&N...390' W/O MISSION CITY PRODUCTS OLD CANYON RD.
24 | 89-62557-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1989-12-11 | 1990-01-17 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | PLEASANTON | WELDED 3" X 3" PATCH
24 | 78-64020-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-02-15 | 1978-02-17 | Clamp |  | Steel/Wrought Iron |  | FREMONT | 6" T.P. MAIN IS IN POOR CONDITION SHOULD BE REPLACED
| 79-00005- | [10 empty] | 1979-02-27 | 1979-05-08 |  |  |  |  | NEWARK
24 | 79-00005-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1979-02-27 | 1979-05-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron
24 | 71-00120-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1971-06-29 | 1971-11-18 | Weld Over Sleeve or Can |  | Steel/Wrought Iron
24 | 72-20612- |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1972-09-28 | 1972-10-02 | Other |  | Steel/Wrought Iron |  |  | LEAK IN PACKING, TIGHTENED GLAND BOLTS
| 73-40260-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-01-19 | 1973-01-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | RETER 10 W.O. 4365-H...PLASTIC TO REPAIR LEAKAGE TEE...
24 | 80-00009-1 |  |  | 0.75 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1980-03-05 | 1980-09-18 | Other |  | Steel/Wrought Iron |  | PLEASANTON | RIP LEAKS ON ...VLAVES ON REG PIT.
24 | 79-00111-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1979-03-06 | 1980-03-18 | Patch Welded |  | Steel/Wrought Iron |  | PLEASANTON
24 | 83-62117-1 |  |  | 0.75 | Distribution Feeder Main |  | Physical/Mechanical Joint |  |  | Other |  | 1983-12-19 | 1983-12-19 | Other |  | Steel/Wrought Iron
24 | 80-00004-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1980-02-26 | 1980-03-07 | Clamp |  | Steel/Wrought Iron |  | NEWARK
24 | 82-00005-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1982-02-17 | 1982-07-28 | Clamp |  | Steel/Wrought Iron |  | NEWARK | INSTALLED ONE SKINNER LEAK CLAMP ON 6" D.F.M TO CORRECT LEAKAGE
24 | 82-64000-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1982-01-06 | 1982-02-25 | Patch Welded |  | Steel/Wrought Iron |  | ; FREMONT | ISNT (3) 4' X 5" PATCH ...(4) 2" X 3" PATCHES ...OVER PITTS
24 | 73-40285-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-04-25 | 1973-05-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | LIVERMORE
24 | 73-40286-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-04-25 | 1973-05-10 | Clamp |  | Steel/Wrought Iron |  | LIVERMORE. | ... 1 SKINNER LEAK CLAMP & 1-5# ANODE TO MAKE PERMANENT REPAIRS.
24 | 82-65112-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1982-12-06 | 1982-12-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SUNOL | REPLACED 8 OF 3" STL. ...
24 | 76-00075-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-05-28 | 1977-06-22 | Patch Welded |  | Steel/Wrought Iron |  | DUBLIN | WRAP DAMAGED INSTALLED (1) 4 1/4" X 4 1'4 " PATCH ON MAIN.
24 | 89-00015-1 |  |  | 8 | Distribution Feeder Main |  | Other Welds |  |  | Construction Defect |  | 1989-11-22 | 1990-05-10 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | UNION CITY | INSTALL 16 X 22 WELD CAN FOR REPAIRS.
24 | 78-22076-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-07-24 | 1979-08-01 | Patch Welded |  | Steel/Wrought Iron |  | PLEASANTON | INSTALLED A 8" X 10" PATCH ON A 6" HP MAIN GAS MAIN TO STOP LEAKAGE; WRAP DAMAGED BY OUTSIDE FORCES. P.T.X.T. CROSSING UNDER OUT 6" HP MAIN
24 | 79-00008-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1979-03-05 | 1980-03-31 | Patch Welded |  | Steel/Wrought Iron |  | SUNOL | WELD PATCH OVER LEAKING PIT ON MAIN
24 | 73-40165-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-03-27 | 1973-03-30 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | LIVERMORE
24 | 74-40603-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-01-04 | 1974-01-08 | Patch Welded |  | Steel/Wrought Iron
24 | 95-21615-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1995-11-01 | 1997-03-11 | Replace Pipe |  | Steel/Wrought Iron |  | FREMONT | INSTALLED 2-8" BT. AND REMOVED SECTION OF MAIN THAT HAD HOME MADE BRAZE... ON IT.
24 | 82-00003-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1982-02-11 | 1982-03-23 | Other |  | Steel/Wrought Iron |  | FREMONT | INST. LINE FITTINGS TO CUT OUT OLD SERVICE TEE CUT OFF THAT WAS LEAKING
24 | 73-60292-1 |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-11-28 | 1973-12-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | A; LIVERMORE
|  |  |  | 2 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1996-11-03 | 1996-11-13 | Other |  | Steel/Wrought Iron |  |  | FOUND 2" DRIP OUT OF THAT D.F.M. MAIN WITH A DRESSOR COUPLING CAKING REPAIRED BY SHUTTING 2" VALVE AND CAPING WITH PLUG 2" VALVE BURIED
24 | 73-20406-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-12-05 | 1974-04-09 | Patch Welded |  | Steel/Wrought Iron
24 | 75-42299-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1975-04-01 | 1975-10-29 | Patch Welded |  | Steel/Wrought Iron |  | DUBLIN
24 | 80-62539-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1980-11-14 | 1981-01-16 | Other |  | Steel/Wrought Iron |  | DUBLIN | ... 1- 12"X 12" LEAK CLAMP... 1-12" X 12" HOLD...
24 | 95-62503-1 |  |  | 12 | Distribution Feeder Main |  | Fitting |  |  | Corrosion |  | 1995-03-06 | 1995-03-06 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | CUT OF 3/4" SERV OFF DFM MAIN. REMOVED HI TO HI SET 6" CAN WELDED OVER TEE; LEAKAGE FOUND AND REPAIRED ON 3/4" SERVICE AND TEE. CUT OFF SERVICE TO 6085 SCARLETT CT. AND WELDED 6" CAN OVER TEE
24 | 91-61010-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1991-05-09 | 1991-05-09 | Patch Welded |  | Steel/Wrought Iron |  | FREMONT | WELL 6" X 12" HALD SOUL PATCH
24 | 95-21620-1 |  |  | 12 | Distribution Feeder Main |  | Fitting |  |  | Material Failure |  | 1995-11-03 | 1996-07-26 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | NEWARK | RETYPE 1" PINOFF TEE PLUG & CAP, THAT IS USED FOR GAUGE TAP.
24 | 72-00185-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-07-21 | 1972-08-01 | Patch Welded |  | Steel/Wrought Iron |  | SUNOL | ANODE- M.25.1; 3" GAS MAIN CORROSION AREA ARC WELDED 4 PATCHES...TO REPAIR...INST. 1-9LB ANODE
24 | 75-62302-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1975-08-08 | 1975-08-12 | Patch Welded |  | Steel/Wrought Iron |  | DUBLIN | INSTALLED (2) TWO PATCHES ON 8" T.P. GAS MAIN 5" X 7" & 7" X 10"; WRAP DAMAGED
24 | 88-65016-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1988-03-09 | 1988-08-23 | Patch Welded |  | Steel/Wrought Iron |  | PLEASANTON | INSTALLED 6 X 3 PATCH ON 3" STEEL PIPE 10: C/O E. P.L.
24 | 82-43 3-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1982-02-19 | 1982-02-19 | Other |  | Steel/Wrought Iron |  | UNION CITY | CUT OFF 2" BLOW OFF FROM 8" MAIN BY SHUTTING OFF 2" VLAVE ON BOTTOM OF 8" MAIN.
24 | 73-40507-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-10-05 | 1973-10-10 | Patch Welded |  | Steel/Wrought Iron |  | DUBLIN | ARC WELDED PATCH...4" MAIN TO REPAIR LEAKAGE...1-9#ANODE
| 94-6502-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1994-05-10 | 1994-05-10 | Patch Welded |  | Steel/Wrought Iron |  | PLEASANTON | ISNTALLED 6" CLAMP; LEAK APP 4' SOUTH OF P/L AT HIGH WAY 580. THIS MAIN IS BEING REPLACED ON GM
|  |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1999-10-13 | 1999-10-13 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | PLEASANTON | PATCHED 10" GAS MAIN 6" X 8" PATCH
24 | 97-62707-1 |  |  | 2 | Gathering |  | Tap Connection |  |  | Corrosion |  | 1997-06-05 | 1997-06-06 | Replace Pipe |  | Steel/Wrought Iron |  |  | INSTALLED 2 - IT 2 FITTINGS TO CUT OFF LEAKING HOME MADE TEE. INSTALLED NEW TEE
| 10-99511-1 | 105 |  | 0.75 | Transmission |  | Valves |  |  | Other | O-RINGS | 2010-03-15 | 2010-05-03 | Other | REPLACED O-RINGS | Steel/Wrought Iron |  | SAN LEANDRO | REPLACED O-RINGS; SOAP TESTED ON JOB SITE
| 10-20101-1 |  |  | 1.25 | Gathering |  | Body of Pipe |  |  | Unknown |  | 2010-04-09 | 2010-06-24 | Other | TIGHTEN VALVE & COLAR | Steel/Wrought Iron |  | FREMONT | RETIGHTEN VALVE & COLAR
| 10-20881- | 105 | 23.03 | 8 | Transmission |  | Regulator |  |  | Other | SENSING LINE NEEDLE VALVE | 2010-10-22 | 2010-10-22 | Other | REPAIRS LEAKING NEEDLE VALVE ON D/S SERVICE LINE. | Steel/Wrought Iron |  | SAN LORENZO
| 05-40013-1 |  |  | 0.75 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2005-03-28 | 2005-03-31 | Other | DFM | Steel/Wrought Iron |  | HAYWARD | CUT OFF GAUGE TAP; SOAP TESTED REPAIR WELDED
| 10-20072-1 |  |  | 1.25 | Gathering |  | Fitting |  |  | Other |  | 2010-04-22 | 2010-06-25 | Other | FITTINGS | PE2406 (Yellow or Orange) |  | HAYWARD | REDID METER SET
| 06-60020-1 | 0 | 0 | 0.75 | Transmission |  | Fitting |  |  | Other | NO DOPE IN/ON CAP | 2006-06-12 | 2007-12-10 | Tighten Cap or Bolt | DOPE CAP & TEE | Steel/Wrought Iron |  | HAYWARD | DOPE CAP AND TEE; DOPE CAP AND TEE
| 06-42478-1 | 2408-05 | 8.63 | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2006-11-20 | 2006-11-21 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | DUBLINE
24 | 10-11002-1 |  |  | 6 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Other |  | 2010-11-02 | 2011-01-21 | Other |  | Other |  | UNION CITY | FUZZ LEAKS ON S.ST. FITTINGS TIGHTENED; TIGHTENED FITTINGS
| 09-91353- |  |  | 0.75 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2009-12-03 | 2009-12-03 | Replace Entire Service |  | Steel/Wrought Iron |  | FREMONT | REPLACED; REPLACED BOLT SERVICE MOTHERS AND BRANCH
| 05-11001-1 | 105 |  | 30 | Transmission |  | Valves |  |  | Unknown |  | 2005-05-24 | 2005-07-26 | Other | GREASED FITTING | Steel/Wrought Iron |  | FREMONT | GREASED VALVE STOPPED LEAK; GREASED VALVE
| 01-42441-1 | BLKHAWK | 7.59 | 6 | Transmission |  | Body of Pipe |  |  | Digin |  | 2001-07-09 | 2001-07-09 | Deactivate #TP Main |  | Steel/Wrought Iron |  | SAN RAMON | ISOLATE SECTIONOF MAIN/ BLOW DOWN.
| 05-42453-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  |  |  | 2005-11-10 | 2005-11-11 | Replace TP Main |  | Steel/Wrought Iron |  | SAN RAMON | REPLACE FIVE FEET OF STEEL DFM.
| 00-42468-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2000-10-10 | 2000-10-10 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | DUBLIN | WELDED SLEEVE OVER CORROSION PIT
| 07-62717-1 | 2408-05 | 10.06 | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2007-04-26 | 2007-04-26 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | PLEASANTON | PLIDCO MECHANICAL CLAMP WAS INSTALLED TO MAKE REPAIR
| 03-42413-1 | 0 |  | 4 | Transmission |  | Body of Pipe |  |  | Digin |  | 2003-05-29 | 2003-05-29 | Replace TP Main |  | Steel/Wrought Iron |  | PLEASANTON | REPLCE 9' OF 4" STEEL
| 09-91523-1 |  |  | 0.75 | Gathering |  | Body of Pipe |  |  | Damage by 3rd Party |  | 2009-10-28 | 2009-12-18 | Replace Entire Service |  | Steel/Wrought Iron |  |  | PIPE HIT WITH HEAVY EQUIPMENT COULD NOT CLAMP REPLACED SERVICE... #30749617 CALLED DISPATCH TO RESORE 9 UNITS
| 05-62705-1 | 131 | 43.28 | 4 | Service |  | Fusion Joint |  |  | Damage by Natural Forces |  | 2005-09-13 | 2005-09-14 | Replace Dist Main < 100 ft |  | Aldyl A (Tan or Gray) |  | SUNOL | REPLACED 3' OF 4" GAS PIPE AND 1-4" ...ELBOW; SOAP TESTED DUSIONS. LEAK ON 4" FUSION ELBOW IN 12" CASING 290' E/O HIGH TO HIGH SET.
| 06-11000-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2006-05-09 | 2006-05-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | FREMONT | WELDED SLEEVE ON 4" MAIN; WELDED SLEEVE ON 4" STL MAIN
| 10-00200-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Weld Failure |  | 2010-11-16 | 2010-11-19 | Fill Weld - Weld |  | Steel/Wrought Iron |  | LIVERMORE | REWELDED 45"SOCKET WELD FITTING; NOTIFIED PIPE ENGINEER. SOAP TESTED ENTIRE AREA, NO LEAKS
| 07-42458-1 |  |  | 6 | Transmission |  | Valves |  |  | Unknown |  | 2007-08-22 | 2008-04-16 | Other | GREASE AND TIGHTEN L2" VALVE | Steel/Wrought Iron |  | LIVERMORE | GREASED VALVE - TIGHTENE BOLT; SOAP TESTED VALVE AFTER GREASE AND TIGHTENED
| 05-00000-1 | 105 |  | 1 | Transmission |  | Tap Connection |  |  | Unknown |  | 2005-10-17 | 2007-03-19 | Other | TIGHTEN PLUG | Steel/Wrought Iron |  | SAN LEANDRO | REDOPED THREADS ON PLUG AND TIGHTENED
96 | 10-81348-2 | [5 empty] | Fitting |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | GS2 GAS RACK/FITTING/YELLOW TAPE
96 | 10-81348-1 | [5 empty] | Fitting |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | GS2 GAS RACK/FITTING/YELLOW TAPE
96 | 10-81347-9 | [5 empty] | Fitting |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | GS2 GAS RACK/FITTING/YELLOW TAPE
96 | 10-81347-8 | [5 empty] | Fitting | [10 empty] | PITTSBURG | GS2 GAS RACK/FITTING/YELLOW TAPE
96 | 10-81347-7 | [5 empty] | Fitting | [10 empty] | PITTSBURG | GS2 GAS RACK/FITTING/YELLOW TAPE
96 | 10-81347-6 | [5 empty] | Fitting |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | GS2 GAS RACK/FITTING/YELLOW TAPE
96 | 10-81347-5 | [5 empty] | Fitting |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | GS2 GAS RACK/FITTING/YELLOW TAPE
96 | 10-81347-4 | [5 empty] | Fitting |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | GS2 GAS RACK/FITTING/YELLOW TAPE
96 | 10-81347-3 | [5 empty] | Fitting |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | GS2 GAS RACK/FITTING/YELLOW TAPE
96 | 10-81347-2 | [5 empty] | Fitting |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | GS2 GAS RACK/FITTING/YELLOW TAPE
96 | 10-81347-1 | [5 empty] | Fitting |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | GS1 GAS RACK/FITTING/YELLOW TAPE
96 | 10-81346-9 | [5 empty] | Fitting |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | GS1 GAS RACK/FITTING/YELLOW TAPE
96 | 10-81346-8 | [5 empty] | Fitting |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | GS1 GAS RACK/FITTING/YELLOW TAPE
96 | 10-81346-7 | [5 empty] | Fitting |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | GS1 GAS RACK/FITTING/YELLOW TAPE
96 | 10-81346-6 | [5 empty] | Fitting |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | GS1 GAS RACK/FITTING/YELLOW TAPE
96 | 10-81346-5 | [5 empty] | Fitting |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | GS1 GAS RACK/FITTING/YELLOW TAPE
96 | 10-81346-4 | [5 empty] | Unknown |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | NOT ON PRINT/MARKED YELLOW PAINT V-AA ON COVER
96 | 10-81346-3 | [5 empty] | Unknown |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | NOT ON PRINT/MARKED YELLOW PAINT V-N ON COVER
96 | 10-81346-2 | [5 empty] | Unknown |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | NOT ON PRINT/MARKED YELLOW PAINT V-R ON COVER
96 | 10-81346-1 | [5 empty] | Unknown |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | NOT ON PRINT/MARKED YELLOW PAINT V-A (FIRE VALVE?) ON COVER
96 | 10-81345-9 | [5 empty] | Unknown |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | NOT ON PRINT/MARKED YELLOW PAINT V-T (FIRE VALVE?) ON COVER
96 | 10-81345-8 | [5 empty] | Fitting |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | STRAINER DRAIN LINE D/S V-18
96 | 10-81345-7 | [5 empty] | Unknown |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | V-32 VAULT @ VENT STACK
96 | 10-81345-6 | [5 empty] | Unknown |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | M-1 VENT @ VENT STACK
96 | 10-81345-5 | [5 empty] | Unknown |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | V-34 VAULT AT VENT STACK
96 | 10-81345-4 | [5 empty] | Unknown |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | V-14R VAULT VENT STACK
96 | 10-81345-3 | [5 empty] | Unknown |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | V-13R VAULT VENT STACK
96 | 10-81345-2 | [5 empty] | Unknown |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | V-33 VAULT AT VENT STACK
96 | 10-81345-1 | [5 empty] | Valves |  |  |  |  | 2010-10-01 | [5 empty] | PITTSBURG | V-F BODY BLEED
96 | 11-24001-1 | ST.PIPING | [9 empty] | 2011-06-07 | [5 empty] | OAKLEY | PT-174 @ COVER/EAST SIDE - FRONT YARD
96 | 11-24002-1 | ST.PIPING | [9 empty] | 2011-06-07 | [5 empty] | OAKLEY | MV-175 @ COVER / EAST SIDE - FRONT YARD
96 | 11-24006-1 | ST.PIPING | [15 empty] | OAKLEY | V-62 @ COVER PLATE OF EXCAVATED VALVE BODY BONNET/STATION PIPING; IN EXCAVATION INSIDE FENCE LINE
96 | 10-81344-1 | [5 empty] | Valves |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY
96 | 11-24007-1 | ST.PIPING | [9 empty] | 2011-06-07 | [5 empty] | OAKLEY | ANTIOCH HEADER GS10 @ VALVE COVER / SOUTH SIDE OF FRONT YARD; STATION PIPING
96 | 10-81340-3 | [5 empty] | Unknown |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | ANTIOCH HDV. GS10 @ VALVE COVER / SOUTH SIDE FRONT YARD; SOUTH SIDE FRONT YARD
96 | 10-81339-1 | [5 empty] | Unknown |  |  | Unknown |  | 2010-10-02 | [5 empty] | OAKLEY | PT- S P5 @ COVER / NORTHWEST CORNER OF YARD / YELLOW PAINT
96 | 10-81339-4 | [5 empty] | Unknown |  |  | Unknown |  | 2010-10-02 | [5 empty] | OAKLEY | CCPP CHR___GRAPH TAP @ LOWER/ N/W CORNER OF YARD
96 | 10-81339-6 | [5 empty] | Unknown |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | MV - 158 @ COVER N/E CORNER OF FRONT YARD; N/E CORNER FRONT YARD
96 | 10-81339-7 | [5 empty] | Unknown |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | PT-160 @ COVER / NE CORNER OF FRONT YARD; NE CORNER FRONT YARD
96 | 10-81339-9 | [5 empty] | Unknown |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | M-6 @ VENT STACK / SOUTH SIDE FRONT YARD; SOUTH SIDE FRONT YARD
96 | 10-81340-1 | [5 empty] | Unknown |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | M-7 @ VENT STACK / EAST SIDE OF FRONT YARD; EAST SIDE FRONT YARD
96 | 10-81340-3 | [5 empty] | Unknown |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | ANTIOCH HDV. GS10 @ VALVE COVER / SOUTH SIDE FRONT YARD; SOUTH SIDE FRONT YARD
96 | 10-81340-4 | [5 empty] | Unknown |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | FIRE VALVE @ COVER / SOUTH SIDE FRONT YARD; SOUTH SIDE FRONT YARD
96 | 10-81340-6 | [5 empty] | Unknown |  |  |  |  | 2010-10-03 | [5 empty] | OAKLEY | M-10@ VENT STACK / WEST SIDE - BACKYARD; WEST SIDE BACKYARD
96 | 10-81340-7 | [5 empty] | Unknown |  |  |  |  | 2010-10-03 | [5 empty] | OAKLEY | M-11 @ VENT STACK / WEST SIDE - BACKYARD; WEST SIDE BACKYARD
96 | 10-81340-8 | [5 empty] | Unknown |  |  |  |  | 2010-10-03 | [5 empty] | OAKLEY | M-12 @ VENT STACK / WEST SIDE - BACKYARD; WEST SIDE BACKYARD
96 | 10-81340-9 | [5 empty] | Unknown |  |  |  |  | 2010-10-03 | [5 empty] | OAKLEY | M-13 @ VENT STACK / WEST SIDE - BACKYARD; WEST SIDE BACK YARD
96 | 10-81341-3 | [5 empty] | Unknown |  |  |  |  | 2010-10-03 | [5 empty] | OAKLEY | V-AA @ COVER / WEST SIDE - BACK YARD; WEST SIDE BACK-YARD
96 | 10-81341-4 | [5 empty] | Unknown |  |  |  |  | 2010-10-03 | [5 empty] | OAKLEY | M-14 @ VAULT VENT STACK / WEST SIDE - BACKYARD; WEST SIDE BACK YARD
96 | 10-81341-5 | [5 empty] | Unknown |  |  |  |  | 2010-10-03 | [5 empty] | OAKLEY | M-15 @ VAULT STACK VENT / WEST SIDE - BACK YARD; WEST SIDE BACKYARD
96 | 10-81341-6 | [5 empty] | Unknown |  |  |  |  | 2010-10-03 | [5 empty] | OAKLEY | M-16 @ VAULT VENT STACK / MIDDLE OF BACKYARD; MID BACK YARD
96 | 10-81341-7 | [5 empty] | Unknown |  |  |  |  | 2010-10-03 | [5 empty] | OAKLEY | M-17 @ VAULT STACK / MID-BACK YARD; MID-BACK YARD
96 | 10-81341-8 | [5 empty] | Unknown |  |  |  |  | 2010-10-03 | [5 empty] | OAKLEY | M-18@VAULT VENT STACK / MID-BACK YARD; MID BACK YARD
96 | 10-81341-9 | [5 empty] | Unknown |  |  |  |  | 2010-10-03 | [5 empty] | OAKLEY | MV-97 @ VALVE COVER / SW - BACK YARD; SW- BACK YARD
96 | 10-81342-1 | [5 empty] | Unknown |  |  |  |  | 2010-10-03 | [5 empty] | OAKLEY | V-103R @ VAULT VENT STACK / SW - BACK YARD; SW - BACK YARD
96 | 10-81342-3 | [5 empty] | Unknown |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | M-22 @ VAULT VENT STACK / SE CORNER OF BACK YARD; SE CORNER BACKYARD
96 | 10-81342-4 | [5 empty] | Unknown |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | MV-149 @ COVER / EAST SIDE - BACK YARD; EAST SIDE BACK YARD
96 | 10-81342-5 | [5 empty] | Unknown |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | PT-154D @ COVER / EAST SIDE - BACK YARD; EAST SIDE BACK YARD
96 | 10-81342-7 | [5 empty] | Unknown |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | V - AV @ VALVE COVER / NE CORNER - FRONT YARD; NE CORNER FRONT YARD
96 | 10-81342-8 | [5 empty] | Unknown |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | PT - 114 N @ VALVE COVER / NE CORNER - FRONT YARD; NE CORNER FRONT YARD
96 | 10-81342-9 | [5 empty] | Unknown |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | PT-SP4 TO CHROMATOGRAPH RACK / NW CORNER - FRONT YARD/COVER; NW CORNER FRONT YARD
96 | 10-81344-1 | [5 empty] | Valves |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | V-62 VALVE POSITION INDICATOR TOP COVER / NORTH SIDE - BACK YARD; NORTH SIDE BACK YARD
96 | 10-81344-4 | [10 empty] | 2010-10-02 | [5 empty] | OAKLEY | V-AW @ GROWBOX VENT / NE CORNER - FRONT YARD; NE CORNER FRONT YARD
96 | 11-24005-1 | ST.PIPING | [9 empty] | 2011-06-09 | [5 empty] | OAKLEY | L-303 PIG LAUNCHER - PULL PORT @ THREADS (FENCED FACILITY) STATION PIPING; AT PULL PORT; CONVERTED ON 7-18-11 TO WP#177173
96 | 11-24004-1 | ST.PIPING | [9 empty] | 2011-06-09 | [5 empty] | OAKLEY | V-104 GAGE TAPE/NORTH SIDE/ W/S THREADS (FENCED FACILITY) STATION PIPING; OVER GAGE TAP; CONVERTED ON 7-18-11 TO WR#177185
96 | 11-24003-1 | ST.PIPING | [9 empty] | 2011-06-07 | [5 empty] | OAKLEY | V-58 D/S GAGE TAP @ U/S THREADS (FENCED FACILITY) STATION PIPING; OVER GAGE TAP; CONVERTED ON 7-18-11 TO WR#177187
96 | 10-81344-2 | [5 empty] | Valves |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | CONVERTED ON 7-18-11 TO WR# 177188; GS-1 SUPPLY ROCK FIRST CUT ISOLATION VALVE / WEST SIDE - BACK YARD; WEST SIDE BACK YARD
96 | 10-81339-2 | [10 empty] | 2010-10-02 | [5 empty] | OAKLEY | CHROMATOGRAPH TAP SP4 N/W CORNER OF YARD/ RACK SUPPLY VALVE; N/W CORNER OF YARD
96 | 10-81339-3 | [5 empty] | Valves |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | OLD DRIP / THE VALVE. N/W CORNER OF YARD; N/W CORNER OF YARD
96 | 10-81341-1 | [5 empty] | Fitting |  |  |  |  | 2010-10-03 | [5 empty] | OAKLEY | GAS SUPPLY - 1 @ TEE ON FINAL CUT/ WEST SIDE - BACK YARD; WEST SIDE BACKYARD
96 | 10-81341-2 | [5 empty] | Fitting |  |  |  |  | 2010-10-03 | [5 empty] | OAKLEY | GAS SUPPLLY - 2 TEE O/S OF FILTER ISOLATION VAVLE/ WEST SIDE - BACK YARD; WEST SIDE BACK YARD
96 | 10-81342-6 | [5 empty] | Fitting |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | GAS SUPPLY TO OLD (REMOVED) GS-7/ NB CORNER - BACK YARD; NE CORNER BACKYARD
96 | 10-81343-4 | [5 empty] | Fitting |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | M-24 DP LINE/ EAST SIDE - BACK YARD YELLOW TAPE; EAST SIDE BACK YARD
96 | 10-81343-5 | [5 empty] | Fitting |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | M-24 DP LINE/ EAST SIDE - BACK YARD; EAST SIDE BACK YARD
96 | 10-81343-6 | [5 empty] | Fitting |  |  |  |  | 10/02/0201 | [5 empty] | OAKLEY | M-24 DP LINE / EAST SIDE - BACK YARD; EAST SIDE BACK YARD
96 | 10-81343-7 | [5 empty] | Fitting |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | M-24 DP LINE / EAST SIDE- BACK YARD; EAST SIDE BACK YARD
96 | 10-81343-8 | [5 empty] | Fitting |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | GS6 SUPPLY RACK/ NE CORNER - BACK YARD - YELLOW TAPE; NE CORNER BACK YARD
96 | 10-81343-9 | [5 empty] | Fitting |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | GS6 SUPPLY RACK / NE CORNER-BACK YARD/; NE CORNER BACK YARD
96 | 10-81339-5 | [5 empty] | Unknown |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | OUT OF SERVICE (OS) COVER ADJACENT TO MV-85; ADJACENT TO MV-85
96 | 10-81339-8 | [5 empty] | Fitting |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | GAS SUPPLY 9 / UNION BETWEEN PCV9A & PCV9B; EAS SIDE FRONT YARD
96 | 10-81340-2 | [5 empty] | Unknown |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | ANTIOCH HDV. GS9 @ VALVE COVER / SOUTH SIDE FRONT YARD; SOUTH SIDE FRONT YARD
96 | 10-81340-5 | [5 empty] | Unknown |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | 89R VAULT LID VENT/ NW CORNER BACKYARD; NW CORNER BACKYARD
96 | 10-81342-2 | [5 empty] | Unknown |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | V-181 @ COVER / SE CORNER - BACK YARD; SE CORNER BACKYARD
96 | 10-81343-1 | [5 empty] | Unknown |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | PT - 1034 @ COVER / NE CORNER - FRONT YARD; NE CORNER FRONT YARD
96 | 10-81343-2 | [5 empty] | Valves |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | V-111@ D/S GAGE TAP/ SOUTH SIDE - BACK YARD; SOUTH SIDE BACK YARD
96 | 10-81343-3 | [10 empty] | 2010-10-02 | [5 empty] | OAKLEY | V-185 BODY BLEED/ SE CORNER - BACK YARD; SE CORNER BACK YARD
96 | 10-81344-3 | [5 empty] | Unknown |  |  |  |  | 2010-10-02 | [5 empty] | OAKLEY | C-191 @ COVER / NE CORNER/ FRONT YARD; NE CORNER FRONT YARD
96 | 10-81344-5 | [5 empty] | Unknown |  |  |  |  | 2010-10-03 | [5 empty] | OAKLEY | V-V @ COVER / NW CORNER - BACK YARD; NW CORNER BACK YARD
| 09-60001-1 | [5 empty] | Other |  | 54 TOTAL LEAKS ARE EITHER MECHANICAL JOINTS OR VALVE PACKINGS |  |  | 2009-06-29 | [5 empty] | OAKLEY | VARIOUS LEAKS INSIDE ANTIOCH TERMINAL FENCELINE; 54 TOTAL LEAKS ARE EITHER MECHANICAL JOINTS OR VALVE PACKING
96 | 10-81315-1 | [10 empty] | 2010-10-03 | [5 empty] | OAKLEY | VARIOUS LEAKS INSIDE ANTIOCH TERMINAL FENCELINE; V-AW WORST LEAK; 46 TOTAL LEAKS ALL SEEM TO BE ASSOCIATED W/ MECHANICAL FITTINGS;
96 | 09-60001-1 | [5 empty] | Unknown |  |  | Unknown |  | 2009-06-29 | [5 empty] | OAKLEY | VARIOUS LEAKS INSIDE ANTIOCH TERMINAL FENCELINE; VALVE - AW WORST LEAK; 53 TOTAL LEAKS; ALL SEEM TO BE ASSOCIATED W/ MECHANICAL FITTING
96 | 09-06501-1 | [5 empty] | Valves | Mechanical Joint | 8 ABOVE GRADE |  |  | 2010-06-10 | [5 empty] | CONCORD | COMPRESSOR YARD (FENCED) CLASS LOCATION (SEE PIPLINE PATROL REPORT); 8 ABOVE GRADE
| 09-06502-1 | [5 empty] | Valves | Mechanical Joint | 4 ABOVE GRADE |  |  | 2009-06-04 | [5 empty] | CONCORD | A PAD (FENCED) CLASS 1 LOCATION (SEE PIPELINE PATROL REPORT) 4 ABOVE GRADE
| 09-06503-1 | [5 empty] | Valves |  | 7 ABOVE GRADE |  |  | 2009-06-04 | [5 empty] | CONCORD | B PAD (FENCED) CLASS 1 LOCATION (SEE PIPELINE PATROL REPORT); 1 ABOVE GRADE
| 09-06504-1 | [5 empty] | Mechanical Joint | Valves | 7 ABOVE GRADE |  |  | 2009-06-05 | [5 empty] | CONCORD | C PAD (FENCED) CLASS 1 LOCATION (SEE PIPELINE REPORT); 7 ABOVE
| 09-06505-1 | [5 empty] | Valves | Other | 4 ABOVE GRADE |  |  | 2009-06-05 | [5 empty] | CONCORD | D PAD (FENCED) CLASS 1 LOCATION (SEE PIPELINE PATROL REPORT); 4 ABOVE GRADE
| 09-06501-1 | [5 empty] | Mechanical Joint | Valves |  |  |  | 2009-06-10 | [5 empty] | CONCORD | COMPRESSOR YARD(FENCED) CLASS 1 LOCATION (SEE PIPELINE PATROL REPORT); RMLD; 8 ABOVE GRADE
| 09-06502-1 | [5 empty] | Mechanical Joint | Valves |  |  |  | 2009-06-04 | [5 empty] | CONCORD | A PAD (FENCED). CLASS 1 LOCATION (SEE PIPELINE PATROL REPORT); RMLD; 4 ABOVE GRADE
| 09-06503-1 | [5 empty] | Valves |  | 1 ABOVE GRADE |  |  | 2009-06-04 | [5 empty] | CONCORD | B PAD (FENCED) CLASS 1 LOCATION (SEE PIPELINE PATROL REPORT); 1 ABOVE GRADE
| 09-06504-1 | [5 empty] | Mechanical Joint | Valves |  |  |  | 2009-06-05 | [5 empty] | CONCORD | C PAD (FENCED) CLASS 1 LOCATIONN (SEE PIPELINE PATROL REPORT); 7 ABOVE GRADE
| 09-06505-1 | [5 empty] | Valves |  |  |  |  | 2009-06-05 | [5 empty] | CONCORD | D PAD ( FENCED) CLASS 1 LOCATION (SEE PIPELINE PATROL REPORT
| 09-06501-1 | [17 empty] | CORRECTION
| 09-06502-1 | [17 empty] | CORRECTION
| 09-06504-1 | [17 empty] | CORRECTION
| 09-06505-1 | [17 empty] | CORRECTION
96 | 10-88498-1 | [10 empty] | 2010-11-02 | [5 empty] | WINTERS | 56B-3; WELL Y-Z VALVE 4
96 | 10-88500-1 | [10 empty] | 2010-11-02 | [6 empty] | 56 C; STATION 3-2
96 | 10-88499-1 | [10 empty] | 2010-11-02 | [6 empty] | 56B; STATION 3-1, NEAR VALVE 4
96 | 10-88500-1 | [10 empty] | 2010-11-02 | [6 empty] | 56C; STATION 3-2
96 | 10-88499-1 | [10 empty] | 2010-11-02 | [6 empty] | 56B; STATION 3-1, NEAR VALVE 4
| 09-05606-1 | [5 empty] | Mechanical Joint | Valves | 2 ABOVE GROUND |  |  | 2009-06-15 | 2010-04-22 | Deactivated Partial Service | REPLACE ENTIRE SERVICE; REPLACE VALVE>OR=2-INCH |  |  | WINTERS | WELL 3-4 (FENCED) CLASS 1 LOCATION (SEE PIPELINE PATROL REPORT); 2 ABOVE GROUND
| 09-05603-1 | [5 empty] | Mechanical Joint | Valves |  |  |  | 2009-06-16 | [5 empty] | WINTERS | COMPRESSION YARD (FENCED) CLASS 1 LOCATION (SEE PIPELINE PATROL REPORT); 6 ABOVE GROUND
| 09-05604-1 | [5 empty] | Mechanical Joint | Valves |  |  |  | 2009-06-16 | [5 empty] | WINTERS | WELL 3-1 (FENCED) CLASS 1 LOCATION (SEE PIPELINE PATROL REPORT); 2 ABOVE GRADE
| 09-05605-1 | [5 empty] | Mechanical Joint | Valves |  |  |  | 2009-06-16 | [5 empty] | WINTERS | WELL 3-2 (FENCED) CLLASS 1 LOCATION (SEE PIPELINE PATROL REPORT); 2 ABOVE GRADE
| 10-05601-1 |  |  |  | Gathering | TRANSMISSION STORAGE | Mechanical Joint | Other | 2 ABOVE GRADE |  |  | 2010-04-21 |  |  |  | Steel/Wrought Iron |  | WINTERS | WELL 3-3 FENCED CLASS 1 LOCATION (SEE PIPELINE PATROL REPORT; ABOVE GRADE LEAKS; 2 ABOVE GRADE; SEE PIPELINE PATROL REPORT FOR DETAILS ABOUT LEAKS. READINGS ABOVE INDICATE THE LEAK OF HIGHEST CONCENTRATION.; STORAGE
| 09-05607-1 | [5 empty] | Mechanical Joint | Valves |  |  |  | 2009-06-17 | [5 empty] | WINTERS | WELL 4-1 (FENCED) CLASS 1 LOCATION (SEE PIPELINE PATROL REPORT); 4 ABOVE GRADE
| 09-05608-1 | [5 empty] | Mechanical Joint | Valves |  |  |  | 2009-06-17 | [5 empty] | WINTERS | WELL 4-2 (FENCED) CLASS 1 LOCATION (SEE PIPELINE PATROL REPORT); 2 ABOVE GRADE
|  | 56 | [16 empty] | PLEASANT CK 4" COLLECTION LINE APPROX. 300FT EAST OF WELL 3-2
|  | 56 | [16 empty] | PLEASANT CK. 4" COLLECTION LINE EXPOSED 200' AND 800' WEST OF COMP STA. K-8. INSPECTION SAME AT BOTH LOCATONS.
| 09-05601-1 | 056A |  |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-04-30 |  |  |  | Steel/Wrought Iron |  |  | WELL PAD 4-1 ABOVE GROUND; VALVE; VALV;E VALVE; GAGE GLASS
| 09-05601-1 | 056A |  |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-04-30 |  |  |  | Steel/Wrought Iron |  |  | WELL PAD 4-1 ABOVE GROUND; VALVE
| 09-05602-1 | 056A |  |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-04-30 | [6 empty] | WELL PAD 4-2 ABOVE GROUND; VALVE; VALVE; CONTROLLER; CLOSURE
| 10-81338-1 | SP5 | 4.28 | 30 | Transmission |  | Valves |  |  | Unknown |  | 2010-09-20 |  |  |  | Steel/Wrought Iron |  | ANTIOCH | ORIGINAL #0900501-1; HOLLY LANE TAP VALVE / C-191
| 09-19101-1 | L191 | 5.43 | [8 empty] | 2009-05-29 | 2009-10-23 | Other | REPLACED BLOWDOWN STACK "O" RING |  |  | ANTIOCH | BLOW DOWN STACK IN PARKING LOT N)38°00.283' W)121°50.146'; REPLACED BLOWDOWN STACK "O" RING
| 08-19101-1 | L191 | 8.7 | 24 | Transmission |  | Unknown |  |  | Unknown |  | 2008-11-24 | 2008-12-23 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | PITTSBURG | L-191 ROW, NORTH OF HIGHWAY 4, M.P. -8.70; TIGHTENED FLANGED FITTING
| 08-19101-1 | L191 | 8.7 | 24 | Transmission |  | Unknown |  |  | Unknown |  | 2008-11-24 |  |  |  | Steel/Wrought Iron |  | PITTSBURG
|  | 191 | 7.47 | 0.24 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  |  | 24 | [11 empty] | Steel/Wrought Iron |  |  | APPROX M.P. 5.49 W/S OF SUMERVILLE RD ANTIOCH, CA
|  |  |  | 24 | [14 empty] | APPROX. M.P. 5.48 W/S OF SOMERSVILLE RD. ANTIOCH, CA
|  |  |  | 24 | [14 empty] | APPROX M.P. 5.47 W/S OF SUMERSVILLE RD. ANTIOCH, CA
|  |  |  | 24 | [11 empty] | Steel/Wrought Iron |  |  | LINES WERE NOT EXPOSED.
|  |  |  | 34 | [11 empty] | Steel/Wrought Iron |  |  | LINES NOT EXPOSED.
|  |  |  | 20 | [11 empty] | Steel/Wrought Iron |  |  | INSTALL CP E.T.S. 20'L-191 S/S HWY 4
|  |  |  | 24 | [11 empty] | Steel/Wrought Iron |  |  | LINE 191 APPROX. M.P. 5.3 INSTALL C.P E.T.S.
|  |  |  | 24 | [11 empty] | Steel/Wrought Iron |  |  | LINE 191 APPROX M.P.6.4 INSTALL C.P. E.T.S.
|  |  |  | 20 | [11 empty] | Steel/Wrought Iron |  |  | INSTALL CP E.T.S. N/S W. LELAND RD.
|  |  |  | 24 | [11 empty] | Steel/Wrought Iron |  |  | INSTALL C.P. E.T.S., M.P. 7.38 L-191
|  | 191 | 9.4 | 24 | [11 empty] | Steel/Wrought Iron |  |  | LINE 191 S/O N. PANKSTOI DR. PITTSBURG APPROX. M.P.4; INSTALL C.P. E.T.S.
LINE 191 100' WEST OF CENTER LINE OF CENTURY BLVD. 435 FT NORTH OF DELTA FAIR BLVD CITY OF PITTSBURG. INSTALLED ETS LEAD, RISER FOR LEAD INSTALLED NEXT TO FIRST POWER TOWER WEST OF CENTURY
|  | 191 | 8.46 | [15 empty] | LINE 191 EXPOSED TO INSTALL ETS LEAD 30 FT EAST OF RAILROAD AVE ON CALIFORNIA ST. RISTER FOR LEAD INSTALLED NEXT TO BASE OF POWER TOWER ON EAST SIDE OF RAILROAD.
|  | 191 | 5.4 | [15 empty] | l191 EXPOSED TO INSTALL ETS LEADS NEXT K< 3RD POWER TOWER WEST OF L STREET
|  | 191 | 5.11 | [15 empty] | L 191 EXPOSED TO INSTALL ETS LEADS. APP 75 WEST OF CENTERLINE OF L STREET RISER FOR LEAD TIED TO CANAL FENCE APP 85° WEST OF CENTERLINE OF LOT.
|  |  |  | 24 | [11 empty] | Steel/Wrought Iron |  |  | TOOK WALL THICKNESS OF PIPE AND 45° ELBOWS; WRAP IN GOOD SHAPE ACCEPT AT THE ELBOWS WRAP WAS REMOVED.
L-191 COVERED WITH SAND WHEN IT WAS BACKFILLED.
L-191 COVERED WITH SAND WHEN IT WAS BACKFILLED
[16 empty] | Steel/Wrought Iron |  |  | INSTALLED ARTICULATING GROUT MATTRESS. THERE SOME LIGHT SCRATCHES ON PIPE WHEN EXPOSED .010" OR LESS, PROCEEDED WITH JOB. SOME WRAP WAS LOOSE ON TOP OF PIPE ALL LOOSE WRAP WAS REMOVED, PIPE WS WRAPPED.
|  |  |  | 24 | [11 empty] | Steel/Wrought Iron |  |  | L-191 M.P. 7.50
|  |  |  | 24 | [11 empty] | Steel/Wrought Iron |  |  | COVER ON DRIP LINE 9' O"; COVER OVER MAIN 50"
|  |  |  | 24 | [11 empty] | Steel/Wrought Iron |  |  | TEST LEADS; L-191 APPROX M.P. 10.4; VALLEY ENGINNERS INSTALLED REFERENCE CELL AND TEST LEADS TO WATER LINE, J. MILLER INSTALLED TEST LEADS TO L-191. (WILLOW PASS RD.)
| 09-11402-1 | [5 empty] | Other |  | THREADED CAP |  |  | 2009-07-08 | 2009-11-03 | Tighten Cap or Bolt |  |  |  | OAKLEY | VAULT LID N)38°01.070' W)121°44.928'; THREADED CAP
| 09-11401-1 | 3009-01 | 0.08 | 20 | [7 empty] | 2009-01-13 | 2009-02-20 | Other | INJECTED SEALANT & LUBRICANT |  |  | OAKLEY | SURVEYED ON 1-13-09 REWROTE REPORT W/ NEW GUIDELINES 1-16-09; .02% @ DRIP VALVE ABOVE GRADE/ E. OF BRIDGEHEAD RD. 20'/N. OF ATS DRIVEWAY 300; LUBRICATED & EXERCISED VALVE TO STP LEAK (ABOVE GRADE); INJECTED SEALANT & LUBRICANT
| 09-11401-1 | 3009-01 | 0.08 | [8 empty] | 2009-01-13 | [5 empty] | OAKLEY | .O2% AT DRIP VALVE ABOVE GRADE/ EAST OF BRIDGEHEAD APPROX. 20', NORTH OF ATS DRIVEWAY APPROX 300'
| 09-13101-1 | 131 | [9 empty] | 2009-01-27 | 2009-02-19 |  |  |  |  | OAKLEY
|  |  |  | 12 | [11 empty] | Steel/Wrought Iron |  |  | MEARS PIPE RECOAT PIPE CHECKED BY TES. PIPE WRAPPED WTIH STAC WRAP.
|  |  |  | 20 | [11 empty] | Steel/Wrought Iron |  |  | 20" CCPP; 20" RUNS PARALLEL WITH L-400 POTHOLE WAS ON EAST SIDE OF L-400 MLU 297.87
|  |  |  | 20 | [11 empty] | Steel/Wrought Iron |  |  | 20"CCPP; N/O LINE 400 ON EAST 20" RUNS PARALLEL WITH LINE 400. SHALLOW PIPE.
|  |  |  | 24 | [11 empty] | Steel/Wrought Iron |  |  | NEW CIRCUIT CITY IN PITTSBURG JOB SITE. L-191 WAS NOT EXPOSED, DEPTH CHECKED BY PROBING. COVER OVER PIPE IN FUTURE WILL BE ASPHALT.
|  |  |  | 24 | [11 empty] | Steel/Wrought Iron |  |  | THIS WORK IS FOR NEW AUTO ROW AT CENTURY BLVD. PITTSBURG. WINTER CHEVROLET HONDA. M.P. APPROX 6.3; APPROX M.P. 6.2 W/S OF SPAN
|  |  |  | 24 | [11 empty] | Steel/Wrought Iron |  |  | TELEPHONE CROSSING L-191 AT M.P. 8.44; JUST EAST OF RAIILROAD AVE. PITTSBURG, CA
|  |  |  | 20 | [11 empty] | Steel/Wrought Iron |  | PITTSBURG | +/- 110 FT. WEST OF DOVER WAY CONTRA COSTA COUNTY; S.O. 704 9288
|  |  |  | 20 | [11 empty] | Steel/Wrought Iron |  | PITTSBURG | +/- 110 FT. WEST OF DOVER WAY. CONTRA COSTA COUNTY; S.O. 704 9288
|  | 191 | 5.48 | 24 | [11 empty] | Steel/Wrought Iron
|  | 191 | 5.48 | 24 | [11 empty] | Steel/Wrought Iron
|  |  |  | 24 | [11 empty] | Steel/Wrought Iron |  |  | #15 ON MAP L-191, KINDER CARE PARKING LOT.
|  |  |  | 24 | [11 empty] | Steel/Wrought Iron |  |  | #14 ON MAP EMPTY LOT W/O KINDER CARE. L-191
|  |  |  | 24 | [14 empty] | #13 ON MAP IN FRONT OF RAMADA INN. L-191
[16 empty] | Steel/Wrought Iron |  |  | #12 ON MAP BURGER KING PARKING LOT APPROX 30'FT EAST OF MLV 5.43 L-191.
|  |  |  | 24 | [11 empty] | Steel/Wrought Iron |  |  | MEARS JO O. 8075984, IN FRONT OF RAMADA INN ANTIOCH; L-191 APPROX M.P. 5.40. INSPECT PIPE & DUE TO CLOSE INTERVAL SURVEY.
|  | 303 | 0.03 | 36 | [11 empty] | Steel/Wrought Iron |  | OAKLEY
| 10-81318-1 | 400 | 297.86 |  |  |  | Valves | Other | PACKING & VALVE BONNET | Equipment Malfunction | UNKNOWN | 2010-10-04 |  |  |  | Steel/Wrought Iron |  | ANTIOCH | 4 NORTH OF MLV 297.86 ON LINE 400 / EAST SIDE / 2" TAP VALVE; 4' W/S OF MLV 297.86 EAST SIDE; PACKING & VALVE BONNET
| 10-81317-1 | 400 | 297.86 |  |  |  | Valves | Other | PACKING | Equipment Malfunction | UKNOWN | 2010-10-02 |  |  |  | Steel/Wrought Iron |  | ANTIOCH | 4' NORTH OF MLV 297.86 ON LINE 400 / WEST SIDE / 2" TAP VALVE; 4' W/S/ MLV 297.86 WEST SIDE; PACKING
| 10-81316-1 | [5 empty] | Valves | Unknown |  | Unknown |  | 2010-10-01 | [5 empty] | PITTSBURG | VALVE COVER FIRE VALVE? WORST LEAK. VARIOUS VALVES AT THIS LOCATION INSIDE FENCED YARD (LONG -121.906739 LAT 38.013443); ITEM #11 ON STATION SURVEY REPORT/ WORST LEAK FOOT; VALVE COVER FIRE VALUE? WORST LEAK; 15 LEAKS AT THIS VALVE YARD DETAILED LIST ON STATION LEAK SURVEY REPORT @ LOS MEDANOS
| 10-81314-1 | 400 | 297.87 |  |  |  | Valves |  |  | Unknown | [5 empty] | Steel/Wrought Iron |  |  | 4' NORTH OF MLV 297.87ON LINE / EAST SIDE / 2" TAP VALVE; 4' W/S MLV 297.87
| 10-81313-1 | 400 | 297.87 |  |  |  | Valves |  |  | Unknown |  | 2010-10-02 |  |  |  | Steel/Wrought Iron |  | ANTIOCH | 4' NORTH OF MLV 297.87 ON LINE 400 / WEST SIDE / 2"TAP VALVE; 4' W/S MLV 297.87
| 09-40006-1 | 400 | 297.86 |  |  |  | Valves |  | PACKING | Equipment Malfunction | UNKNOWN |  |  |  |  | Steel/Wrought Iron |  | ANTIOCH | 4' NORTH OF MLV 297.86 ON LINE 400 / WEST SIDE / 2" TAP VALVE; 4' U/S MCV 297.86; PACKING
| 09-40006-1 | [5 empty] | Valves |  | PACKING |  |  | 2009-07-27 | [5 empty] | ANTIOCH | 2" TAP VALVE 4' U/S OF MLV 297.86; PACKING
| 09-40001-1 |  |  | 1 | Single Service |  | Fitting |  |  | Unknown |  | 2009-01-30 | 2009-02-11 | Other | TIGHTEN FITTING | Steel/Wrought Iron |  | ANTIOCH | -297.86 (V-1) @ GAGE TAP THREADED ELBOW --YELLOW PAINT; TIGHTEN FITTINGS; TIGHTENED SEALANT FITTING TO STOP LEAK.
| 09-40002-1 | 400 | T298.29 | 0.5 | Single Service |  | Fitting |  |  | Unknown |  | 2009-01-30 | 2009-02-11 | Other | TIGHTEN FITTING | Steel/Wrought Iron |  | ANTIOCH | T-298.29 (V-1) @ UPSTREAM SEALANT FITTING -- YELLOW PAINT; TIGHTEN FITTING; TIGHTENED FITTING TO STOP LEAK
|  | 400 | 298.16 | [15 empty] | 42" CASING EXPOSED; EXTERNAL INSPECTION ONLY TO CASING
|  | 400 | 298.87 | 0.3 | [11 empty] | Steel/Wrought Iron |  | OAKLEY
|  |  |  | 36 | [11 empty] | Steel/Wrought Iron |  |  | MEARS/CPG INC. TO RECOAT PIPE WITH PROTAL 7200. APPROX M.P. 298.86. LIGHT RUST UPSTREAM OF FLANGE
|  |  |  | 36 | [14 empty] | MEARS/ CPG INC. TO RECOAT PIPE WITH PROTAL 7200. APPROX M.P. 298.82.
|  |  |  | 36 | [11 empty] | Steel/Wrought Iron |  |  | M.P. 298.0 L-400 INSTALLING NEW TAP FOR MIRANT POWER PLT.
|  |  |  | 36 | [11 empty] | Steel/Wrought Iron | OTHER |  | CASING; CASING 42"; CASING EXPOSED (STEEL) 42", LINE 400 NOT EXPOSED. M.P. 298.18 WILBUR AVE.
96 | 10-81337-1 | SP3 | 176.16 |  |  |  | Fitting | Valves |  | Unknown |  | 2010-10-05 | 2010-10-13 | Other | LEAKING THREADS REPAIRED |  |  | CONCORD | VENT VALVE D/S THREADS BETWEEN V-702 & V-704 YELLOW TAPE; LEAKING THREADS REPAIRED
| 10-81336-1 | SP3 | 176.16 |  |  |  | Fitting | Valves |  | Unknown |  | 2010-10-05 | [5 empty] | CONCORD | GAS SUPPLY #1 FITTER ISOLATION VALVE - YELLOW TAPE; GS #1 FILTER VALVE
| 10-81335-1 | SP3 | 176.16 |  |  |  | Fitting |  |  | Unknown |  | 2010-10-05 | [5 empty] | CONCORD | GAS SUPPLY #2 D/S 2ND CUT - YELLOW TAPE; GAS SUPPLY #2 VALVE
| 10-81334-1 | SP3 | 176.16 |  |  |  | Regulator |  |  | Unknown |  | 2010-10-05 | [5 empty] | CONCORD | V-705 POSITIONER SUPPLY REGULATOR - YELLOW TAPE; V705 POSITIONER REG.
| 10-81332-1 | SP3 | 176.16 |  |  |  | Fitting |  |  | Unknown |  | 2010-10-05 | [5 empty] | CONCORD | V-706 CONTROL CABINET SUPPLY VALVE FITTING - YELLOW TAPE; V-706 CABINET FITTING
| 10-81330-1 | SP5 | 5.78 |  | Transmission |  | Other |  | STACK CLOSURE | Unknown |  | 2010-10-05 | [5 empty] | ANTIOCH | YARD BLOWDOWN STACK CLOSURE - YELLOW TAPE; BLOW DOWN STACK CLOSURE; STACK CLOSURE
| 10-81333-1 | SP3 | 176.16 |  |  |  | Regulator |  |  | Unknown |  | 2010-10-05 | 2010-10-13 | Other | REGULATOR BODY BOLTS |  |  | CONCORD | V-706 POSITIONER SUPPLY REGULATOR - YELLOW TAPE; V-706 POSITIONER REG.; REGULATOR BODY BOLTS
| 10-81331-1 | SP3 | 167.32 |  | Transmission |  | Fitting |  |  | Unknown |  | 2010-10-05 | 2010-10-07 | Other | NIPPLE THREADS |  |  | ANTIOCH | PIG LAUNCHER PURGE GAS LINE BLIND FLANGE VENT NIPPLE; LAUNCHER PURGE LINE; DELTA FAIR STATION; PIG LAUNCHER PURGE GAS FLANGE VENT NIPPLE; MECHANICAL REPAIR FITTING; NIPPLE THREADS
| 09-00302-1 |  |  |  | Transmission |  | Valves | Unknown |  | Unknown | [5 empty] | Steel/Wrought Iron |  |  | SP3/ L-191 X-TIE (VARIOUS VALVES AT THIS LOCATION); ITEM #11 ON SERVE REPORT; REFERENCE G.T. STATION LEAK SURVEY REPORT, @ LOS MEADOWS 15 LEAKS @ THIS LOCATION. ITEMIZED LIST.
| 09-00302-1 |  |  |  | Transmission |  | Valves | Unknown |  |  |  | 2009-06-03 | [5 empty] | PITTSBURG | SP3/ L-191 X-TIE (VARIOUS VALVES AT THIS LOCATION ); ITEM #11ON SURVEY REPORT; REFERENCE G.T. STATION LEAK SURVEY REPORT, @ LOS MEADOWS 15 LEAKS @ THIS LOCATION. ITEMIZED LIST.
| 09-00301-1 | SP3 | 176.16 |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-05-28 |  |  |  | Steel/Wrought Iron |  | CONCORD | SP-3 PRESSURE LIMITING STATION; INSERTION PET; PRESSURE TAP; PRESSURE TP; V-702
| 09-00301-1 | SP3 | 176.16 |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-05-28 |  |  |  | Steel/Wrought Iron |  | CONCORD | SP-3 PRESSURE LIMITING STATION; V-701; V-703; V-705; V-706; V-701 PRESSURE TAP & BODY BLEED; V-702 - PRESSURE TAP; V-703 - PRESSURE TAP & BODY BLEED; V-705 - PRESSURE TAP & BODY BLEED; V-706-PRESSURE TAP; UNDER GROUND PRESSURE TAP BY VLV "A"; UNDERGROUND PRESSURE TAP BY V-711; ALL LEAKS MARKED WITH YELLOW PAINT
|  | SP3 | 167.31 |  |  |  | Other |  | FIRE VALVE PACKING | Other | PACKING LOOSE | 2005-04-25 | 2005-05-18 | Mechanical Repair Fitting - Fitting |  |  |  | PITTSBURG | SP-3, L-191 CROSS TIE PITTSBURG; FIRE VALVE PACKING; PACKING LOOSE; SP-3, L-191 X-TIE; TIGHTENED PACKING
|  |  |  | 26 | [11 empty] | Steel/Wrought Iron |  |  | #1 A FORM PER GPS POINTS STANPAC 3. APPROX M.P. 172.0
|  |  |  | 26 | Transmission | [13 empty] | #2 A FORM PER GPS POINTS STANPAC 3
|  |  |  | 26 | Transmission | [13 empty] | #3 A FORM PER GPS POINTS STANPAC 3
|  |  |  | 26 | Transmission | [13 empty] | #4 A FORM PER GPS POINTS STANPAC 3
|  |  |  | 26 | Transmission | [13 empty] | #5 A FORM PER GPS POINTS STANPAC 3
|  |  |  | 26 | Transmission | [13 empty] | #6 A FORM PER GPS POINTS STANPAC 3
|  |  |  | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | REWRAPPED ABOUT 6' OF SP3 WITH STAC WRAP OVER EXISTING WRAP. INSTALLED TEST LEADS, REFERENCE CELL AND BONDING CABLE ON SP3. M.P. 173.9 APPROX. THIS CROSSING IS ON THE CONTRA COSTA CANAL RD. ON THE NORTH SIDE OF CANAL, WE HAVE A SPAN ON SP3 AT THE CANAL AT THAT LOCATION.
| 09-00401-1 | SP4Z | 8.18 | [8 empty] | 2009-01-13 | 2009-02-10 | Mechanical Repair Fitting - Fitting |  |  |  | OAKLEY | READING AT VAULT LID; SP4Z, MP8.18 TIGHTENED 2" THREADED CAP.;
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | APPROX M.P. 8.78
N 3521894472 LONG 1220044.74473.; EXCAVATED PIPE ON 11.5.05; DID NOT REMOVE WRAP ON THIS DATE; COMMENT FOR PGE BY MEAR ON WO 8068322
|  |  |  | 12 | Transmission | [13 empty] | LAT 380044.62127 LONG W1214503.29948
| 10-81330-1 | SP5 | 5.78 |  | Transmission |  | Other |  | STACK CLOSURE | Unknown |  | 2010-10-05 | [5 empty] | ANTIOCH | YARD BLOWDOWN STACK CLOSURE - YELLOW TAPE; BLOWDOWN STACK CLOSURE; STACK CLOSURE
96 | 10-81330-1 | SP5 | 5.76 | [8 empty] | 2010-10-05 | [5 empty] | ANTIOCH | DELTAFAIR STA; YARD BLOWDWN STACK CLOSURE-YELLOW TP
| 10-81320-1 | SP5 | 5.78 |  | Transmission |  | Valves |  |  | Unknown |  | 2010-10-05 | 2010-10-07 | Mechanical Repair Fitting - Fitting | TIGHTENED 1/2" VALVE | Steel/Wrought Iron |  | ANTIOCH | DELTA FAIR STATION; V-5.78 (SP5) BODY BLEED VALVE THREAD YELLOW TAPE; V-5.78 SP5 BODY BLEED VALVE THREADS; TIGHTENED 1/2" VALVE
| 10-81319-1 | SP5 | 5.78 |  | Transmission |  | Valves |  |  | Unknown |  | 2010-10-05 | 2010-10-07 | Mechanical Repair Fitting - Fitting | TIGHTENED 1/2" VALVE | Steel/Wrought Iron |  | ANTIOCH | DELTA FAIR STATION V-5.78 (SP5) GAGE TAP YELLOW TAPE; V-5.78; TIGHTENED 1/2" VALVE
| 10-00501-1 | SP5 |  |  |  |  | Other |  | BLOWDOWN STACK CLOSURE |  |  | 2010-05-05 | [5 empty] | ANTIOCH | DELTA FAIR JUNCTION STATION SEE PIPELINE PATROL REPORT DATED 5-5-10; BLOWNDOWN STACK CLOSURE; BLOWDOWN STACK CLOSURE
| 10-00501-1 | SP5 |  |  |  |  | Other |  | BLOWDOWN STACK CLOSURE |  |  | 2010-05-05 | [5 empty] | ANTIOCH | DELTA FAIR JUNCTION STATION SEE PIPELINE PATROL REPORT DATED 5-5-10; BLOWDOWN STACK CLOSURE
| 09-00501-1 | SP5 | 4.28 | 30 | Distribution Main | TRANSMISSION | Valves |  |  | Equipment Malfunction |  | 2009-05-12 |  |  |  | Steel/Wrought Iron |  | ANTIOCH | HOLLY LN. TAP VALVE CAN
| 09-00503-1 |  |  |  | Transmission |  | Fitting | Valves |  | Equipment Malfunction |  | 2009-05-18 |  |  |  | Steel/Wrought Iron |  | ANTIOCH | PIG LAUNCHER, V 5.78, BLOWDOWN STACK; PIG LAUNCHER; PIG LAUNCHER; V.5.78 TAPS; BLOWDOWN STACK
| 09-00502-1 |  |  |  | Transmission |  | Fitting | Valves |  | Equipment Malfunction |  | 2009-05-18 | 2009-08-13 | Tighten Cap or Bolt | SOAP AND/OR TAPE | Steel/Wrought Iron |  | ANTIOCH | 2" TAP VALVEOFF BLOWDOWN & STALK ; VALVE
| 09-00502-1 |  |  | 2 | Transmission |  | Fitting | Valves |  | Equipment Malfunction |  | 2009-05-18 | 2009-08-13 | Tighten Cap or Bolt | SOAP AND/OR TAPE | Steel/Wrought Iron |  | ANTIOCH | 2" TAP VALVE OFF BLOWDOWN STALK; VALVE
|  |  |  | 2 | [11 empty] | Steel/Wrought Iron |  |  | ABOVE GRADE
| 09-00501-1 | SP5 | 4.28 | 30 | Distribution Main | TRANSMISSION | Valves |  |  | Equipment Malfunction |  | 2009-05-12 |  |  |  | Steel/Wrought Iron |  | ANTIOCH | HOLLY LN. TAP VALVE CAN
| 08-00501-1 | STANPAC5 | 3.17 | 24 | Transmission |  | Unknown | Other | NOT PIPELINE GAS, TESTED AND CONFIRMED NOT TO BE PIPELINE GAS RESULTS 9-22-08 | Unknown |  | 2008-05-30 |  | Other | CASING VENT MODIFICATION | Steel/Wrought Iron |  | ANTIOCH | SP5 HIGHWAY 4 CASING VENT; NOT PIPELINE GAS, TESTED AND CONFIRMED NOT TO BE PIPELINE GAS, RESULTS 9-22-08; NO REPAIR NEEDED TO PIPELINE 9/22/08; CASING VENTS MODIFICATION
|  | SP-5 | 1.13 | 0.24 | [11 empty] | Steel/Wrought Iron |  |  | WR117108
|  | SP3 SP5 | 5.78 | 8 | Transmission | BLOW OFF | Physical/Mechanical Joint | Other | BURIED FLANGE |  |  | 2003-04-10 | 2003-05-09 | Welded Sleeve/Can - Weld |  | Other | GRADE B PIPE | ANTIOCH | NEAR VALVE 5.77 SP5; WR#49223; BURIED FLANGE; BLOW-OFF; GRADE B PIPE; REMOVED EXISTING BURIED FLANGE - WELDED IN STRAIGHT PIPE CAN.; REMOVED LEAKING FLANGE - INSTALLED CAN
|  |  |  | 26 | Transmission | [13 empty] | M.P. APPROX. 297.80 N/O MLV 297.86 SHALLOW PIPE
|  |  |  | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | M.P. APPROX 297380 N/O MLV 297.87 SHALLOW PIPE
|  |  |  | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | M.P. APPROX 297.9 N/O MLV 297.87
|  | SP4 | [16 empty] | LAT 380047.30240 LONG 121 4503.31994
5 | 71-20022-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-07-22 | 1971-07-27 | Patch Welded |  | Steel/Wrought Iron |  | SALINAS | 7-23-71; 7-27-71 ... WELDED PATCH OVER ELECTROLYSIS HOLE
5 | 71-20026 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-09-21 | 1971-12-23 | Patch Welded |  | Steel/Wrought Iron |  | SALINAS
5 | 71-30009-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-12-05 | 1971-12-05 | Patch Welded |  | Steel/Wrought Iron |  | SALINAS | 12-5-71 2:00PM REPLACED LEAKING GAS SERV. PRESSURE TESTED AND FOUND OK
5 | 71-40005 |  |  | 2 | Distribution Main |  | Other |  |  | Corrosion |  | 1971-02-17 | 1971-02-17 | Patch Welded |  | Steel/Wrought Iron |  | SALINAS | PATCH WELD. 2" MAIN; ARC WELDED PATCH OVER LEAK WHICH WAS ON BOTTEM OF MAIN; REPAIRED SERVICE LEADER ON 2" GAS MAIN BY ARC WELDING AND PATCH. THE LEADER WAS 6" S/O SERVICE TEE FOR 1241 MONROE ST. 2-17-71
5 | 71-4000 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-02-12 | 1971-02-12 | Patch Welded |  | Steel/Wrought Iron |  | SAL. | WELDING PATCH ON SEAM AND REWRAPED
5 | 71-40010 |  |  | 4 | Distribution Main |  | Tap Connection |  |  | Corrosion |  | 1971-02-09 | 1971-02-09 | Other |  | Steel/Wrought Iron |  | SALINAS | INSTALLED LEAK CLAMP WELDED CAN OVER LEAK CLAMP; LEAK WAS AT OLD SADDLE ON 4" MAIN TO 1' GAS ... ELECTROLYSIS HAD .. TO MAIN. ELECTROLYSIS JUTS FULL 6' OF MAIN ... 8" IN DEPTH. REMOVED SERVICE AND WELDED LEAK CLAMP. WELDED (ON 8" X 26') OVER LEAK CLAMP, REPLACED GAS SERVICE.
120 | 71-40024 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-09-16 | 1971-09-16 | Patch Welded |  | Steel/Wrought Iron |  | SALINAS | WELDED PATCH ON PIT. WELDED AROUND SERVICE COUPLING.
5 | 72-40092-1 |  |  | 0.5 | Other | ABANDONED CU. | Body of Pipe |  |  | Corrosion |  | 1972-11-12 | 1972-11-15 | Replace Pipe and/or Service |  | Copper |  | SALINAS | PL SERVICE DIRECT BURIAL; FIVE ELECTROLYSIS LEAKS ON COPPER SERVICE LINE WITH LEAK ... REPLACE ARC VICE, ARC WELD LEAK IN WELD. TWO VERY ... PITS ON 2" MAIN. REPLACED MAIN AND ... IN GOOD CONDITION.; PL SERVICE DIRECT BURIAL
5 | 73-00106-1 |  |  | 0.75 |  |  | Body of Pipe |  |  | Corrosion |  | 1973-06-07 | 1973-06-07 | Bell Joint Clamp Replacement |  | Steel/Wrought Iron |  | SALINAS | LEAKING BELOW STOP COCK USED STOP COCK CHANGER, CUT AND RETHREADED SERVICES RISER AND INSTALLED NEW STOP COCK OLN. 6-8-73. LINE USE "C"
5 | 73-00303-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1973-05-09 | 1973-05-09 | Other |  | Steel/Wrought Iron |  | SALINAS | COMMENT ILLEGIBLE DUE TO FADING
5 | 73-00421-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-12-20 | 1974-07-23 | Patch Welded |  | Steel/Wrought Iron
76 | 72-20122-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1972-05-31 | 1972-06-05 | Other |  | Steel/Wrought Iron |  | SANTA CRUZ | CUT RISER TO ... LEAK, REINSTALLED PIPE
72-30000-1
76 | 72-30000-1 |  |  | 6 | Distribution Feeder Main | [6 empty] | 1972-06-05 |  |  |  | Steel/Wrought Iron |  | WATSONVILLE | CHECKED AREA WITH J.W. FOUND NO INDICATION OF GAS. STREET NEWLY REPAVED
[18 empty] | WATSONVILLE | INDICATIONS OF GAS NEAR THE HOLE. 6/7/7; CHECKED AREA WITH J.W. FOUND NO INDICATION OF GAS. STREET NEWLY REPAVED.
76 | 73-40013-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-01-26 | 1973-01-26 | Patch Welded |  | Steel/Wrought Iron |  | SANTA CRUZ | (1) FOUND 1" X 1/2 CO. PIT IN BOTTOM OF 12" TERM MAIN; REPAIR (1) INSTALLED 8" X 10" HALF SOLE PATCH NOTIFIED SAN JOSE LOAD CENTER / 2:00 P.M.
76 | 73-60002-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-12-28 | 1973-01-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | APTOS | REPLACED 18" 3/4" STEEL PIPE
5 | 74-00214-1 |  |  | 0.75 | Other |  | Physical/Mechanical Joint |  |  | Other |  | 1974-03-12 | 1974-03-12 | Other | REPAIR INSULATING UNION | Steel/Wrought Iron |  | SALINAS | REPAIRED LEAK AT INSULATING UNION.
5 | 74-00215-F |  |  | 0.75 | Other | [6 empty] | 1974-03-12 |  |  |  | Other |  | SALINAS | NONE; NONE; NO LEAK FOUND; SCOPED METER CASE - REGULATOR MANIFOLD + ALL FILLINGS IN METER BOX NO LEAKS. CHECKED GROUND AT SIGN WITH LEAK INDICATOR. ABOUT OFF PILOTS + CHECKED HOUSELINE NO LEAKS.
5 | 74-00216-1 |  |  | 0.75 | Other |  | Physical/Mechanical Joint |  |  | Other |  | 1974-03-12 | 1974-03-12 | Other | REPAIR LEAK AT STOP COCK | Steel/Wrought Iron |  | SALINAS | REPAIR LEAK AT STOP COCK
5 | 74-00267-1 |  |  | 24 | Transmission | [6 empty] | 1974-10-11 |  |  |  | Steel/Wrought Iron |  |  | NO LEAK FOUND; SOAP TESTED NIC FITTINGS & VALVES REGULATOR & DIAPHRAM FOUND NO LEAK
5 | 74-00402-1 |  |  | 8 | Transmission |  | Fitting |  |  | Other |  | 1974-01-09 | 1974-01-09 | Other |  | Steel/Wrought Iron |  |  | LEAK FOUND ON 1" CAPOVER SERVICE TEE WHILE ...
76 | 75-20316-1 |  |  | 4 | Other |  | Valves |  |  | Material Failure |  | 1975-04-01 | 1975-04-02 | Other |  | Steel/Wrought Iron |  | SC
76 | 75-60009-1 |  |  | 0.75 | Other | STUB SERVICE | Body of Pipe |  |  | Damage by outside Forces | BROKEN | 1975-02-25 | 1975-02-25 | Other | CUT & CAPPED | Steel-Other |  | SC | CUT & CAPPED GAS STUB IN STREET
76 | 76-20254-1 |  |  | 2 | Service |  | Body of Pipe |  |  | Corrosion |  | 1976-08-17 | 1976-12-28 | Clamp |  | Steel/Wrought Iron |  | SANTA CRUZ | INSTALLED 2" SKINNER LEAK CLAMP ON LEAKING 2" STEEL SERVICE
76 | 76-30098-1 |  |  | 10 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1976-12-28 | 1977-12-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | APTOS | REPLACED LEAKING VALVE IN DIST. REG. PIT
76 | 78-20091-1 |  |  | 2 | Other |  | Fitting |  |  | Construction Defect |  | 1978-11-16 | 1979-06-13 | Other |  | Steel/Wrought Iron |  | S.C. | CAP ON SPLIT CONTROL LEAKING REMOVED DOPED + REINSTALLED SERVICE GAS DEEP PITS CLOSE TO TEE NOT LEAKING AT THIS TIME.
76 | 78-20059-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-07-13 | 1978-12-12 | Other | CAN | Steel/Wrought Iron |  | S.C. | WRAP SCRAPED WHEN INSTALLING LARGE WATER LINE OVER MAIN. CORROSION PITS RESULTED. JOHNSON INSTALLED 4' OF CAN
76 | 78-70014-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-06-20 | 1978-06-20 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | PAJARO
76 | 79-20263-1 |  |  | 0.5 | Distribution Feeder Main |  | Other |  |  | Other |  | 1979-07-31 | 1980-11-26 | Other |  | Steel/Wrought Iron |  | APTOS | TIGHTENED FITTING ON THE SENSING LINE
76 | 79-20198-1 |  |  | 10 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1979-06-22 | 1979-10-22 | Other |  | Steel/Wrought Iron |  | S.C.
76 | 79-20156-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1979-06-21 | 1979-10-22 | Other |  | Steel/Wrought Iron |  | S.C. | GREASED + OPERATED 6" VALVRE, SOAPED VALVE TOP, NO VISIBLE LEAKAGE
76 | 79-40038-1 |  |  | 8 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1979-10-18 | 1979-10-19 | Other |  | Steel/Wrought Iron |  | SCOTT'S VALLEY | EXTENDED SECTION CORE, GROUND VALVE, STOPPED LEAK.
76 | 79-70015-1 |  |  | 10.75 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-09-13 | 1979-09-13 | Patch Welded |  | Steel/Wrought Iron |  |  | COMMENT ILLEGIBLE DUE TO FADING
76 | 80-20393-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 1980-09-02 | 1981-06-03 | Other |  | Steel/Wrought Iron |  | S.C. | REPAIRED BY GREASING VALVE; FOUND 3/4" VALVE LEAKING. REPAIRED BY GREASING VALVE
76 | 80-30136-1 |  |  | 2 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1980-09-16 | 1980-12-29 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | WAT. | IN VALVE PIT; LEAKING 2" BLOW-OFF VALVE GREASED CORE - TIGHTENED GLAND NUT - TIGHTENED COVER BOLTS
76 | 80-70001-1 |  |  | 10 | Transmission |  | Girth Weld |  |  | Other | BAD WELD | 1980-01-23 | 1980-01-23 | Other |  | Steel/Wrought Iron |  | WATSONVILLE | FUZZ LEAK ON WELD, REPAIR DONE BY WELDING A PASS OVER EXISTING WELD. BLEW OUT DURING REPAIR. (IE MEANING ... WELD BAD).
76 | 81-20247-1 |  |  | 4 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1981-04-24 | 1982-04-27 | Other |  | Steel/Wrought Iron |  | CAPITOLA | BOTH REG. PITS IN FRONT; FOLLOW UNION IN REG PIT LEAKING REDOPED UNION FOR REPAIR
76 | 81-20436-1 |  |  | 0.75 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1981-09-03 | 1981-09-08 | Other |  | Steel/Wrought Iron |  | S.C. | GROUND VALVE; ... ; NO LEAKS.
76 | 81-30065-1 |  |  | 10 | Transmission |  | Valves |  |  | Material Failure |  | 1981-10-01 | 1984-04-26 | Other |  | Steel/Wrought Iron |  | WAT. | IN VALVE PIT; TIGHTENED LEAKING METRIC GAUGING VALVE. THIS ENTIRE 10" VALVE IS TO BE REMOVED IN THE FUTURE.
76 | 82-60022-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1982-06-11 | 1982-06-11 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SANTA CRUZ | PLASTIC INSERT SEE 82618; STRUCK SERVICE 6' FROM MAIN, SERVICE THEN INSERTED
76 | 82-70013-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 1982-06-09 |  | Other |  | Steel/Wrought Iron
76 | 83-20093-1 |  |  | 12 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1983-07-05 | 1983-09-01 | Other |  | Steel/Wrought Iron |  | S.C. | N/ SIDE OF BRIDGE ABUTTMENT NEAR MAIN MARKER
76 | 83-20072-1 |  |  | 8 | Distribution Feeder Main |  | Other |  |  | Material Failure |  | 1983-06-24 | 1983-09-08 | Patch Welded |  | Steel/Wrought Iron |  | FELTON | OUTLET ELBOW; FOUND SEAM ON 8" PIPE LEAKING IN OUTLET RISER OF REG PIT. REPAIRED BY ARC WELDING OVER SEAM
76 | 83-20069-1 |  |  | 12 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1983-06-29 | 1984-03-22 | Other |  | Steel/Wrought Iron |  | S.C. | VALVE MARKED B-34; TIGHTENED LEAKING 1/4" METRIC VALVE
76 | 83-20015-1 |  |  | 12 | Distribution Feeder Main |  | Valves |  |  | Construction Defect |  | 1983-06-03 | 1983-07-08 | Other |  | Steel/Wrought Iron |  | S.C. | FOUND 3/4" VALVE AND C" CAP LEAKING REPAIRED BY GREASING VALVE + REDOPING CAP
76 | 83-70005-1 |  |  | 16 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 1983-08-11 | 1983-08-11 | Other |  | Steel/Wrought Iron
76 | 84-70003-1 |  |  | 4 | Transmission |  | Valves |  |  | Material Failure |  | 1984-06-11 | 1984-06-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | REPLACED ... PIPE ...
76 | 85-20065-1 |  |  | 3 | M |  | Body of Pipe |  |  | Corrosion |  | 1985-04-18 | 1990-07-31 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SANTA CRUZ | VENTING OUT OF STREET LIGHT BOX. FAIRLY LARGE SPREAD 5-8... IN STREET LIGHT BOX
76 | 86-30107-1 |  |  | 10 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1986-07-11 | 1987-04-10 | Other |  | Steel/Wrought Iron |  | APTOS
76 | 86-30082-1 | [10 empty] | 1986-07-21 | [5 empty] | WATSONVILLE | GIANT HOLE OPEN WITH TEMP. CLAMP ON MAIN HOLE OVER 6' DEEP
76 | 86-30081-1 | [10 empty] | 1986-07-21 | [5 empty] | WATSONVILLE
76 | 86-30080-1 |  |  | 4 | Service |  | Fitting |  |  | Other |  | 1986-07-18 | 1986-07-18 | Other |  | Steel/Wrought Iron
76 | 87-20044-1 |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1987-06-25 |  | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | CAPITOLA | FOUND ... FLAME PACKED - OK
76 | 81-60100-1 |  |  | 6 | Distribution Feeder Main |  | Girth Weld |  |  | Construction Defect |  | 1981-09-16 | 1981-09-16 | Other |  | Steel/Wrought Iron |  | SANTA CRUZ | ARC WELDED A SMALL ON UNDERSIDE OF WELD
76 | 87-30008-1 | [10 empty] | 1987-02-05 | [5 empty] | WATSONVILLE | FLAME PACK FOUND SNOPER READING AT HSE FOUNDATION NEAR TRANSMISSION MAIN. LEAK INVESTIGATION DETERMINED PROBABLE ... LEAK ONLY. DOWNGRADED TO #3.
76 | 87-50004-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1987-02-03 | 1987-02-03 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | WATSONVILLE
76 | 87-70022-1 |  |  | 4 | Distribution Main |  | Valves |  |  | Other |  | 1987-09-09 | 1988-01-11 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  |  | FOUND LEAK ON FLANGE OF 4" VALVE (#A-02) _ TIGHTENED BOLTS ON FLANGE FOR PERMANENT REPAIR. ALSO FOUND ANOTHER VALVE N/E OF A-02 THAT WAS PAVED-OVER DUG-OUT AND INSTALLED FRAME & COVER.
76 | 87-70014-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1987-06-30 | 1987-07-03 | Other |  | Steel/Wrought Iron |  | WAT. | G.C. ELECTRIC CREW STRUCK & PUT A HOLE IN A MISMARKED 4" STL. TRANSMISSION CAN WALL ANGERING A BEE HIVE. TEMPORARY REPAIRS WITH 4" CLAMP ON 6/30/87. PERMANENT WELDED REPAIR ON 7/3/87 INCLUDING 2 P.G.F.S ON WELD ABOVE.
76 | 88-20065-1 |  |  | 12 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1988-05-18 | 1988-10-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SANTA CRUZ | DUG AROUND VALVE PERM REPAIRS DONE BY M. + C. DEPT.
76 | 88-20063-1 |  |  | 3 | Gathering |  | Valves |  |  | Other |  | 1988-05-12 | 1988-06-02 | Other |  | Steel/Wrought Iron |  | SANTA CRUZ | GREASE VALVE
5 | 89-00178-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1989-07-11 | 1990-10-29 | Other |  | Steel/Wrought Iron |  | SALINAS | GREASE VALVE READING
5 | 89-00203-1 |  |  | 6 | Distribution Main |  | Physical/Mechanical Joint |  |  | Other |  | 1989-10-25 | 1987-10-25 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SALINAS | TIGHTEN BOLTS WITH BOTH SIDES OF VALVE LEAK STOPPED.
5 | 89-00223-1 |  |  | 20 | Transmission |  | Tap Connection |  |  | Other |  | 1989-09-25 | 1990-10-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | PRUNDALE | FOUND CAP OF THE SERVICE TEE LEAKING, TIGHTENED CAP.
5 | 89-223-1 |  |  | 0.75 | Distribution Main |  | Tap Connection |  |  | Other |  | 1990-09-14 | 1990-10-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | CASTROVILLE | FOUND THE CAP ON THE SERVICE TEE LEAKING, TIGHTENED CAP.
5 | 89-00224-1 | [10 empty] | 1989-10-20 | 1990-10-04 |  |  |  |  | SALINAS | BAR TESTED BUT COULD FIND ANY LEAK
5 | 89-00225-1 |  |  | 12 | Transmission |  | Tap Connection |  |  | Other |  | 1989-09-25 | 1990-10-04 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MOSS LANDING | TIGHTEN & REDOPE SERVICE TEE CAP AT VALVE #6. COULD NOT LOCATE THE LEAK NEAR VALVE #7. GRADE 3 LEAK.
| 90-00127-1 |  |  | 12 | Transmission |  | Fitting |  |  | Other |  | 1990-09-12 | 1990-10-04 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | CASTROVILLE | LEAKING CAP NEAR V6. TIGHTENED CAP. COULD NOT LOCATE THE LEAK NEAR V7. GRADE 3 LEAK.
8 | 89-00646-1 |  |  | 0.25 | Transmission |  | Fitting |  |  | Material Failure |  | 1989-10-25 | 1989-10-25 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | HOLLISTER | REPAIRED LEAK ON METRIC VALVE
76 | 88-30078-1 |  |  | 8 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1988-07-26 | 1989-05-03 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | WATS | NO GAS IN GROUND AROUND VALVE FREITAS 12-30-88 TIGHTENED BOLTS
76 | 88-30076-1 |  |  | 16 | Transmission |  | Longitudinal Weld |  |  | Construction Defect |  | 1988-06-02 | 1989-05-19 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | AROMAS | INSTALL WEDDING BAND AS PERMANENT REPAIR.
76 | 88-30076-1 | [10 empty] | 1988-06-21 | [5 empty] | AROMAS
76 | 88-30075-1 |  |  | 0.75 | Distribution Feeder Main |  | Other Welds |  |  | Construction Defect |  | 1988-06-20 | 1989-04-05 | Other |  | Steel/Wrought Iron |  | AROMAS | WELDED OVER LEAK+ TIGHTENED CAP
76 | 88-30069-1 |  |  | 0.75 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1988-06-16 | 1989-03-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | WATS | DOPED + TIGHTENED CAP ON 3/4" TEE USED AS UPSTREAM TEST GAUGE LOCATION FOR VALVE
76 | 88-70029-1 |  |  | 0.75 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1988-11-12 | 1989-03-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | WATS | TIGHTEN CAP ON GAUGES
76 | 88-70027-1 |  |  | 0.75 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1988-11-04 | 1989-03-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | WATS | TIGHTEN CAP ON GAUGE TREE
7 | 89-00025-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1989-04-17 | 1989-07-03 | Clamp |  | Steel/Wrought Iron |  | PAC GROVE | INSTALLED (1) 2" X 6" PERMANENT CLAMP
76 | 89-60036-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1989-10-07 | 1989-10-18 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SANTA CRUZ | SLEEVED MAIN DAMAGED DURING EARTH QUAKE
76 | 89-60025-1 |  |  | 1.25 | Service |  | Fitting |  |  | Other |  | 1989-06-07 | 1989-11-19 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SANTA CRUZ | REDOPE & TIGHTEN CAP ON ABANDON SERVICE TEE
76 | 89-70021-1 |  |  | 0.75 | Transmission | [6 empty] | 1989-10-24 | 00/24/1989 |  |  | Steel/Wrought Iron |  | WATSONVILLE | COMMENTS ILLEGIBLE DUE TO FADING
76 | 89-70011-1 |  |  | 2 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1989-05-08 | 1989-05-08 | Other |  | Steel/Wrought Iron |  | WATSONVILLE | GREASED & TIGHTEN PACKING GLAND
76 | 90-70090-1 |  |  | 12 | Transmission |  | Fitting |  |  | Other |  | 1990-01-26 | 1990-04-10 | Other |  | Steel/Wrought Iron |  | WATS | GREASED VALVES
7 | 91-00039-1 |  |  | 2 | Distribution Feeder Main |  | Valves |  |  |  |  | 1991-11-01 | 1992-04-30 | Other |  | Steel/Wrought Iron |  | MONTEREY | GREASED VALVE AND REPAIRED COVER
76 | 91-70017-1 |  |  | 3 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1991-06-26 | 1991-10-10 | Other |  | Steel/Wrought Iron |  | WATSONVILLE | GRASE VALVE
76 | 90-20006-1 |  |  | 10 | Distribution Feeder Main |  | Girth Weld |  |  | Corrosion |  | 1990-06-20 | 1990-10-14 | Other |  | Steel/Wrought Iron |  | SANTA CRUZ | G.C. REPLACED SECTION OF 10" MAIN (20')
76 | 92-30067-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1992-06-11 | 1992-08-06 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | WATS | WELD
| 93-20011-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1993-05-05 | 1993-05-05 | Clamp |  | Steel/Wrought Iron |  | S. C. | INST. 12" FULL CIRCLE CLAMP
76 |  |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1993-07-02 | 1993-08-13 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SANTA CRUZ | WELDED SLEEVE ON 12" T.P. MAIN
76 | 88-20074-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1988-06-08 | 1996-08-13 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SANTA CRUZ | WELDED SLEEVE ON 12" T.P. MAIN
| 93-30024-1 |  |  | 10 | Transmission |  | Girth Weld |  |  | Corrosion |  | 1993-04-20 | 1993-04-28 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | WATSONVILLE | WELD ON REPAIR SLEEVE
| 93-70024-1 |  |  | 0.75 | Distribution Main |  | Regulator |  |  | Material Failure |  | 1993-05-19 | 1993-05-25 |  |  | Steel/Wrought Iron |  | APTOS | J-14 REPLACED FISHER FOR RELIEF; J-44 LEAK ON PILOT REG.; TWO PIPES ON SINGLE A-FORM.
4 | 95-40001-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Digin |  | 1995-04-25 | 1995-04-25 | Replace Pipe |  | Steel/Wrought Iron |  | GREENFIELD | REPLACED DAMAGED SECTION OF 8" MAIN. 26'.
7 | 95-00052-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1995-09-27 | 1997-09-11 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | PACIFIC GROVE | WELD PATCH
5 | 96-00046-1 |  |  | 12 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 1996-07-15 | 1997-05-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SPRECKELS | REPLACE BOLTS AND TIGHTEN CAP
7 | 97-00064-1 |  |  | 10 | Transmission |  | Fitting |  |  | Other |  | 1997-04-08 | 1998-10-22 | Replace Pipe |  | Steel/Wrought Iron |  | FORT ORD | ELIMINATED VALVE 4.42 BY REPLACING APPROX. 15 FT. OF PIPE AROUND VALVE VAULT
| 97-00064-1 | [10 empty] | 1997-04-08 | [5 empty] | FORT ORD | LEAK ON UP STREAM AND DOWN STREAM FLANGES OF VALVE #4.42 ON MONTEREY #2
5 | 97-00042-1 |  |  | 12.75 | Transmission |  | Body of Pipe |  |  | Digin |  | 1997-06-19 | 1997-06-20 | Replace Pipe |  | Steel/Wrought Iron |  | CASTROVILLE | REPLACED 60' SECTION OF TRANSMISSION MAIN.
| 97-00119-1 |  |  | 1.25 | Transmission |  | Fitting |  |  | Corrosion |  | 1997-11-05 | 1997-11-05 | Clamp |  | Steel/Wrought Iron |  | SALINAS | INST. 2" PERMANENT CLAMP
| 02-50086 | 301B | 6.94 | 12 | Transmission |  | Body of Pipe |  |  | Digin |  | 2002-06-03 | 2002-06-04 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | REPLACED 15FT. OF PIPE W/ PRE-TESTED .375" GR. B SMLS
| 02-50098-1 |  |  | 0.75 | Distribution Main | TRANSMISSION | Fitting | Regulator |  | Damage by 3rd Party | Vehicle | 2002-07-20 | 2002-07-22 | Mechanical Repair Fitting - Fitting | Replace Dist. Main < 100 ft. |  |  | SALINAS | NIPPLE THREADED + INSULATED UNION REPLACED
| 02-20039-1 |  |  | 0.75 | Service | TRANSMISSION | Fitting |  |  | Vehicle |  | 2002-11-11 | 2002-11-11 | Other | RE-BUILT HPR SET | Steel/Wrought Iron |  | WATSONVILLE | RE-BUILT HPR SET, INSPECTED & RE-WRAPPED 3/4" TRANSMISSION SERVICE; HPR SET WAS RE-BUILT AND THE 3/4" TRANSMISSION-PRESSURE RISER WAS STRAIGHTENED. THE 3/4" SERVICE FROM THE HPR TO THE METER SET WAS AIR-TESTED @ 110 PSIG FOR 5 MINUTES.
| 03-50027-1 | 12-301B |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2003-05-02 | 2003-05-28 | Other | GREASED VALVE | Steel/Wrought Iron |  | CASTROVILLE | GREASED INLET 3/4" R/W VALVE TO STOP PACKING LEAK; LEAK WAS ON VOLVE PACKING, GREASED VALVE AND LEAK STOPPED
| 03-50031-1 |  |  | 2 | Distribution Main |  | Valves |  |  | Other |  | 2003-05-08 | 2004-06-22 | Other | GREASED VALVE | Steel/Wrought Iron |  | SALINAS | GREASED A 2" BYPASS VALVE
| 03-50037-1 |  | 0.51 | 0.75 | Service |  | Valves |  |  | Other | LEAKY VALVE | 2003-05-19 | 2003-11-26 | Other | GREASED VALVE | Steel/Wrought Iron |  | SALINAS | GREASED 3/4" TAP VALVE TO HPR SET
| 03-50038-1 | [10 empty] | 2003-05-19 | [5 empty] | SALINAS | NO LEAK FOUND
| 03-50055-1 | [16 empty] | SALINAS | OVER MAIN OR SERVICE TEE; NEXT MILE M/P = 8:90; ABBR. 755
| 03-50066-1 |  |  | 0.75 | Distribution Main | TRANSMISSION | Fitting |  |  | Other |  | 2003-07-22 | 2003-07-22 | Mechanical Repair Fitting - Fitting | TIGHTEN CAP/BOLT | Steel/Wrought Iron |  | SALINAS | IN VALVE PIT; CAP ON FITTING NEEDED TO BE TIGHTEN
| 03-50075-1 | 301C | 17.26 | 8 | Transmission |  | Valves |  |  | Other | BROKEN POSITIONER COVER | 2003-09-02 | 2003-11-26 | Other | REPLACED BROKEN POSITIONER COVER | Steel/Wrought Iron |  | SALINAS | LEAK IN BOX MARKED WITH YELLOW PAINT; REPLACED BROKEN POSITIONER COVERS INSIDE REG POINTS
| 03-50076-1 | MTYDFM#2 | 2.9 | 0.75 | Transmission |  | Valves |  |  | Other | LEAKY VALVE | 2003-09-02 | 2003-11-26 | Other | GREASED VALVE | Steel/Wrought Iron |  | SALINAS | VALVE STRONG GAS ODOR; GREASED VALVES IN REG STATION, INCLUDING VALVE #1
| 03-90004-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | VALVE LEAKING | 2002-07-30 | 2003-08-07 | Other | GREASED VALVE | Steel/Wrought Iron |  | SOLEDAD | ON HP SET LOOK AT MAP; GREASED VALVE RESET RELIEF
| 03-10060-1 | DFM3 | 2.11 | 4 | Transmission |  | Valves |  |  | Other | VALVE STEM LEAK | 2003-10-27 | 2003-11-10 | Other | TIGHTEN STEM | Steel/Wrought Iron |  | SANTA CRUZ | ODOR IN AIR - CALL IN VALVE LEAKING AT STEM; TIGHTEN
| 03-20024-1 | [10 empty] | 2003-05-27 | [5 empty] | WATSONVILLE
| 04-40004-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | LACK OF GREASE | 2004-02-24 | 2004-03-23 | Other | SERVICED VALVES | Steel/Wrought Iron |  | GREENFIELD | HI LOW SET, 2 IN GROUND; 3 VLVS LEAKING FLAME-OUT; 1.0 .3 .5; PAINTED IN YELLOW; REPAIRED LEAK ON INLET (BYPASS VALVES, ALSO RELIEF)
| 04-50060-1 | 103 |  | 6 | Service |  | Riser |  |  | Damage by 3rd Party |  | 2004-04-26 | 2004-04-26 | Deactivate #TP Main | DFM | Steel/Wrought Iron |  | SALINAS | AT RISER; 407 OLD STAGE RD.; CLOSED FIRE VALVE. SERVICE LINE TO BE REMOVED.
| 04-50087-1 | 301-B | 6.6 | 12 | Transmission | [6 empty] | 2004-06-30 |  | Other | RE-WRAP PIPE CONFIRMED OK. | Steel/Wrought Iron |  | SALINAS | APPROX 1/2 MILE N.W. OF SAN JON ROAD CROSSING; X RAY TESTED, OK. ONLY PIPE - REWRAP NECESSARY.
| 04-50118-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | External Corrosion |  | 2004-09-10 | 2004-11-19 | Service Partially Replaced |  | Steel/Wrought Iron |  | SALINAS | INSTALL LEAK CLAMP, STEAL LEAKING
| 05-80025-1 | 103 | 9.37 | 0.75 | Transmission |  | Valves |  |  | Construction Defect |  | 2004-08-31 | 2005-08-31 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | SAN JUAN BAUTISTA | GAS MAIN; REPLACE 3/4 VALVE BETWEEN T.P. LINE 103 AND H.P.R. HR H0S
| 05-50031-1 | 301B |  | 6 | Transmission |  | Valves |  |  | Other | NEEDED GREASE | 2005-04-21 | 2006-05-26 |  |  | Steel/Wrought Iron |  | SALINAS | GREASE VALVE
| 05-50031-1 | 301B | [9 empty] | 2005-04-21 | [5 empty] | SALINAS
| 05-50059-1 |  |  | 0.75 | Transmission |  | Valves |  |  |  |  | 2006-07-01 | 2006-12-20 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | SALINAS | 10' CIRCLE AROUND VALVE; DOWNGRADE TO #2; REPLACED LEAKING VALVE
| 05-50080-1 | [10 empty] | 2005-11-04 | [5 empty] | SALINAS | LEAK TESTED WITH CHROMATEGRAPH BY GAS DISTRIBUTION. NO GAS FOUND.
| 05-50089-1 | 103 |  | 12 | Transmission |  | Body of Pipe |  |  |  |  | 2005-11-19 | 2005-11-20 | Replaced TP Main |  | Steel/Wrought Iron |  | SALINAS | REPLACED 9' OF TP MAIN 12" SMIS
| 06-50004-1 | MTY #1 | 7.95 | 0.75 | Transmission |  | Other Welds |  |  | Construction Defect |  | 2006-02-01 | 2006-02-01 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | ON SOCKET WELD 3/4" - 18' N/W OF H.P.R.; CUT-OUT 3/4" 90 DEGREE SOCKET + REPLACED. PIPE + FITTING PRE-TEST -OK; THIS LEAK WAS FOUND DURING EXCAVATION TO INSTALL A FIRE VALVE. ALL PIPE AND FITTINGS WERE PRE-TESTED ON 1-31-06.
| 06-50044-1 | 301C | 1.1 | 0.75 | Single Service |  | Body of Pipe |  |  |  |  | 2006-04-27 | 2006-04-27 | Deactivated Entire Service |  | Steel/Wrought Iron |  | SALINAS | SHUT DOWN SERVICE AT PIN-OFF TEE, CUT + RETHREADED. SOAP TEST OK.
| 06-10016-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other | TREE | 2006-01-27 | 2006-01-27 | Replace Partial Service |  | Steel/Wrought Iron |  | SANTA CRUZ | HIGH TO HIGH REG STATION AT PK; REBUILD HIGH TO HIGH REG ALSO MOVE 1' OVER ABV GRD.; USING ELBOWS MOVED REG SET AWAY FROM TREE.
| 06-10127-1 | 10181601 |  | 0.75 | Service | TRANSMISSION | Other |  | BLOW OFF | Other | DIRT IN SEAT | 2006-11-18 | 2006-11-20 | Tighten Cap/Bolt - Fitting | BLEW OUT BLOW OFF | Steel/Wrought Iron |  | CAPITOLA | BLOW OFF ON HIGH 2 HIGH; BOX NEEDS TO BE INLARGED. TEE TOO SMALL TO OPERATE PIN OFF TEE. FIXED BLOW OFF.
| 06-10127-2 |  |  | 0.75 | Service | TRANSMISSION | Other |  | BLOW OFF | Other | DIRT IN SEAT | 2006-11-18 | 2006-11-20 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | CAPITOLA | BLOW OFF ON HIGH 2 HIGH; BOX NEEDS TO BE INLARGED. TOO SMALL TO OPERATE PIN OFF TEE. FIXED BLOW OFF.; BLEW OUT BLEW OFF.
| 06-20044-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Construction Defect |  | 2006-08-31 | 2006-09-05 | Other | GREASED VALVE | Steel/Wrought Iron |  | WATSONVILLE | REPAIRED LEAK; GREASED VALVE
| 06-20044-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Construction Defect |  | 2006-08-31 | 2006-09-05 | Other | GREASED VALVE | Steel/Wrought Iron |  | WATSONVILLE | REPAIRED LEAK; GREASED VALVE
| 06-20044-1 | [10 empty] | 2006-08-31 | [5 empty] | WATSONVILLE
| 07-20014-1 |  |  | 0.75 | Service |  | Riser |  |  | Atmospheric Corrosion | EXTERNAL CORROSION | 2007-06-04 | 2007-06-05 | Replace Partial Service |  | Steel/Wrought Iron |  | WATSONVILLE | REPLACED A PORTION OF RISER
| 07-20038-1 | [10 empty] | 2007-10-08 | [6 empty] | DELETED
| 07-20039-1 | [10 empty] | 2007-10-08 | [5 empty] | WATSONVILLE | DELETED
| 08-80020-1 |  |  | 1.25 | Transmission |  | Body of Pipe |  |  |  |  | 2008-10-07 | 2008-10-07 | Replace TP Main |  | Steel/Wrought Iron |  | HOLLISTER | REPLACED 4' SECTION OF 1 1/4" STEEL PIPE (NOT LEAKING); REPLACED 4' SECTION OF 1 1/4" STEEL PIPE.
| 08-70016-1 |  |  | 1.25 | Gathering |  | Other |  | MANIFOLD | Atmospheric Corrosion |  | 2008-02-08 | 2008-02-12 | Other | REPLACE MANIFOLD | Steel/Wrought Iron |  | MONTEREY | HOT CHANGED 4 SERVICES & CHANGED OUT 4MM MANIFOLD & REBUILT REGULATOR SET
| 08-70110-1 | MONTEREY #1 | 18.78 | 0.75 | Single Service |  | Fitting |  |  | Construction Defect |  | 2008-07-17 | 2008-07-17 | Other | REPAIR REGULATOR | Steel/Wrought Iron |  | MONTEREY
| 08-10104-1 | [10 empty] | 2008-08-14 | [5 empty] | FELTON | BASE ROCK + DEBRIS ON HIGH 2 HIGH
| 08-10006-1 | 8-1816-15 |  | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2008-02-11 | 2008-04-16 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | SANTA CRUZ | ON 8" GAS MAIN 55' S/O LYLE WY; INSTALLED SPECIAL 6 BOLT TRANSMISSION MAIN CLAMP
| 08-50067-1 | 301G | 22.6 | [8 empty] | 2008-10-10 | [5 empty] | MOSS LANDING
| 08-50068-1 | 187 | 64.2 | [8 empty] | 2008-10-13 | [5 empty] | SALINAS | DELETED
| 08-50068-1 | 187 | 64.2 | [8 empty] | 2008-10-13 | [5 empty] | SALINAS
| 08-50076-1 | 301C | MP16.15 | 0.75 | Distribution Main |  | Regulator |  |  | Atmospheric Corrosion |  | 2008-11-21 | 2009-06-22 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | SAL | LEAKS ON HI TO HI SET, REPLACED DOWN STREAM STOP COCK; LEAKS ON HI TO HI SET, REPLACED DOWN STREAM STOP COCK.
| 08-50076-1 | 301C | MP 2.41 | [8 empty] | 2008-11-21 | [5 empty] | SALINAS | VINCE TO REPAIR IN JUNE
| 08-50092-1 | 301C |  | 0.75 | Distribution Main |  | Other |  | RELIEF & VALVE | Unknown |  | 2008-11-21 | 2009-07-03 | Other | GREASED VALVE & REPLACED RELIEF | Steel/Wrought Iron |  | SAL | REPLACED RELIEF. GREASED VALVES 3 AND 6.
| 08-50092-1 | 301C | 14.41 | 0.75 | Distribution Main |  | Other |  |  | Unknown |  | 2008-11-21 | 2009-07-03 | Other |  | Steel/Wrought Iron |  | SALINAS | GREASED VALVE AND REPLACED RELIEF
| 08-50092-1 | 301C | [9 empty] | 2008-11-21 | [5 empty] | SALINAS | REPAIRED 7/3/09 ; REPAIR 5/21/10
| 08-50094-1 | 301C | 2.3 | 0.75 | Transmission |  |  |  | RELIEF VALVE | Equipment Malfunction |  | 2008-11-21 | 2009-02-20 | Other | RELIEF VALVE | Steel/Wrought Iron |  | SALINAS | REPLACED RELIEF VALVE H-202, OLD RELIEF WAS LEAKING - BY. 2/20/09; RELIEF VALVE NEEDS TO BE REPLACED, WITH NEW VALVE.
| 08-50094-1 | 301C | 2.3 | [8 empty] | 2008-11-21 | [5 empty] | SALINAS
| 08-50095-1 | 103 | MP 1.70 | 0.75 | Branch Service |  | Valves |  |  | Material Failure |  | 2008-11-21 | 2010-02-26 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | SALINAS | REPLACED SERVICE VALVE; REPLACED DEFECTIVE STOP COCK WITH A NEW STOP COCK.
| 08-50095-1 | 103 | 1.7 | [8 empty] | 2008-11-21 | [5 empty] | SALINAS
| 08-50095-1 | 103 | MP 1.70 | [8 empty] | 2008-11-21 | [5 empty] | SALINAS | RECHECK BY 7/31/2010 SHOWS GRADE 0
| 08-50096-1 | 103 | 22.21 | [8 empty] | 2008-11-20 | [5 empty] | SALINAS
| 09-80008-1 | 300B | 423.92 | 1 | Transmission |  | Valves |  |  | Material Failure | UNKNOWN | 2009-03-05 | 2010-09-01 | Other | REPLACED O-RINGS ON VALVE STEM | Steel/Wrought Iron |  | HOLLISTER | REPLACED O-RINGS ON T.P. INLET VALVE STEM, CLEARED STEM, SOAP TEST OK; SEE DIAGRAM FOR HRH-80 HOLLISTER REGS.
| 09-80012-1 | 300A |  | 2 | Transmission |  | Valves |  |  | Unknown | OTHER | 2009-04-23 | 2009-08-17 | Other | GREASED VALVE | Steel/Wrought Iron |  | HOLLISTER
| 09-80012-1 | 300A | [9 empty] | 2009-04-23 | [5 empty] | HOLLISTER
| 09-80013-1 | 300B | 459.43 | 0.75 | Distribution Main |  | Fitting | Regulator |  | Other | LOOSE FITTING | 2009-04-23 | 2009-07-11 | Replace Partial Service |  | Steel/Wrought Iron |  | HOLLISTER | REPAIRED LEAKS
| 09-80014-1 | 300A |  | 0.75 | Transmission |  | Mechanical Joint | Valves |  | Other | LOOSE FITTING | 2009-04-23 | 2009-06-24 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | HOLLISTER | MARK, YELLOW; HPR. LEAK ON CAP 1STAG.
| 09-80014-1 | 300A | [9 empty] | 2009-04-23 | [5 empty] | HOLLISTER
| 09-80015-1 | 300A |  | 2 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2009-04-23 | 2009-07-02 | Other | 2" UNION | Steel/Wrought Iron |  | HOLLISTER | REPAIRED LEAK ON 2" UNION, REDOPED 2" FITTING, TIGHTEN UP FITTING.
| 09-80015-1 | 300A | [9 empty] | 2009-04-23 | [5 empty] | HOLLISTER
| 09-80018-1 | 300A |  | 0.75 | Transmission |  | Valves |  |  | Other | INACTIVITY | 2009-04-23 | 2009-06-24 | Other | OPERATE | Steel/Wrought Iron |  | HOLLISTER | INLET FIRE VALVE.
| 09-80018-1 | 300A | [9 empty] | 2009-04-23 | [5 empty] | HOLLISTER
| 09-80019-1 | 300B | [9 empty] | 2009-04-23 | [5 empty] | HOLLISTER
| 09-80019-1 | 300B | [9 empty] | 2009-04-23 | [5 empty] | HOLLISTER
| 09-80019-1 | 300B | [9 empty] | 2009-04-23 | [5 empty] | HOLLISTER | DELETED
| 09-80020-1 | 301A |  | 0.5 | Transmission |  | Other |  | PLUG & GREASE STEM |  |  | 2009-04-25 | 2009-09-15 | Soap and/or Tape - Other | GREASED VALVES RE TAPED PLUGS | Steel/Wrought Iron |  | SAN JUAN BAT. | TAG WAS LATE GETTING BACK TO MAPPING; BACK TO MAPPING, LATE, IN IGIS REPAIRED T. WRIGHT 9-24-09; GREASED VALVES, RETAPED PLUG
| 09-80020-1 | 301A | [9 empty] | 2009-04-25 | [5 empty] | SAN JUAN BAT.
| 09-80021-1 | 300A | [9 empty] | 2009-04-25 | [5 empty] | TRES PINOS | DELETED
| 09-80021-1 | 300A | [9 empty] | 2009-04-25 | [5 empty] | TRES PINOS
| 09-80022-1 | 300B |  | 0.75 | Transmission |  | Valves |  |  | Other | NO LEAK FOUND | 2009-04-25 | 2010-10-22 |  |  | Steel/Wrought Iron |  | TRES PINOS | DELETED; NO LEAK FOUND; SOAP & USED GAS TECT SNIFFER, I COULD NOT FIND A LEAK.
| 09-80022-1 | 300B | [9 empty] | 2009-04-25 | [5 empty] | TRES PINOS
| 09-80023-1 | 300A | [9 empty] | 2009-04-25 | [5 empty] | TRES PINOS | REPAIRED ON 00-80025-1
| 00-80022-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | DRY O-RINGS | 2000-10-16 | 2010-06-15 | Other | LUBED O-RINGS | Steel/Wrought Iron |  | HOLLISTER | AT ZONE VALVE INLET VALVE FOR H-85; AT GAS ZONE VALVE, SOME LOCATION, SAME AREA; RESEALED O-RINGS; RELUBED O-RINGS ON MULLER INLET VALVE
| 09-80023-1 | 300A | [9 empty] | 2009-04-25 | [5 empty] | TRES PINOS | T&R REPAIRED
| 09-80023-1 | 300A | [9 empty] | 2009-04-25 | [5 empty] | TRES PINOS
| 09-80025-1 |  |  | 0.5 | Transmission |  | Valves | Other | PLUGS LEAKING | Other | NO TAPE | 2009-04-27 | 2009-08-19 | Tighten Cap/Bolt - Fitting | OTHER-TAPPED PLUGS | Steel/Wrought Iron |  | HOLLISTER | PRESS. TEST LINES ON VALVE - NO TAPE ON THREADS
| 09-80025-1 | [10 empty] | 2009-04-27 | [5 empty] | HOLLISTER
| 09-80032-1 | 103 | 9.66 | 2 | Distribution Main |  | Regulator | Other | VARIOUS FITTINGS | Other | O-RING | 2009-08-14 | 2009-10-30 | Other | NEW O-RING REDOPED. FITTINGS | Steel/Wrought Iron |  | HOLLISTER | DIST. REG LEAK; YELLOW PAINT;
| 09-80040-1 | [10 empty] | 2009-08-22 | [5 empty] | HOLLISTER | SAME AREA, V.9 IN #2 BOX S/E CORNER OF SALLY C/S 6T, LEAK WAS REPAIRED ( DELETED )
| 09-80040-1 | [10 empty] | 2009-08-22 | [5 empty] | HOLLISTER | DELETED; V-9 IN # 2 BOX S/E CORNER OF SALLY C/S 6TH, LEAK ON VALVE HAS BEEN REPAIRED
| 09-80046-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2009-10-20 | 2010-11-11 | Other |  | Steel/Wrought Iron |  | HOLLISTER | LEAK ON VALVE NO #2; NO REPAIR MADE; SOAP TESTED OK
| 09-80046-1 | 300 | [9 empty] | 2009-10-20 |  |  | ; ; |  |  | HOLLISTER
8 | 09-80047-1 | [10 empty] | 2009-10-21 | [5 empty] | HOLLISTER | DELETED; AT VALVE M.P 1.87, MARKED YELLOW, NO LEAK FOUND
| 09-80047-1 | 301 | 31.87 | [8 empty] | 2009-10-21 | [5 empty] | HOLLISTER | 6" VALVE LEAKING; MARK YELLOW
| 09-80047-1 | [10 empty] | 2009-10-21 | [5 empty] | HOLLISTER | AT VALVE M.P 1.87
| 09-80048-1 | 300B | 423.92 | [8 empty] | 2009-10-16 | [5 empty] | HOLLISTER | AT #5 #7 #10; PAINT YELLOW
| 09-40010-1 | 310 |  | 2 | Single Service |  | Fitting | Regulator | VALVE | Unknown |  | 2009-02-24 | 2009-11-21 | Other |  | Steel/Wrought Iron |  | KING CITY | GUAGE LEAK AND BY VALVE ON METER SET; PAINTED RED, PAINTED RED VALVES, SAME AREA; BYPASSED THE METER SET & MADE REPAIRS; THE VALVE THAT IS LEAKING IS A CUSTOMER VALVE.
| 09-40010-1 | 310 |  | 2 | Single Service |  | Fitting |  |  | Unknown |  | 2009-02-24 | 2009-11-21 | Other |  | Steel/Wrought Iron |  | KING CITY | GUAGE LEAK AND BY VALVE; PAINTED RED, PAINTED RED VALVES, SAME AREA; BYPASSED THE METER SET AND MADE REPAIRS; VALVE IS LEAKING - CUSTOMER VALVE
| 09-40010-1 | 310 | [9 empty] | 2009-02-24 | [5 empty] | KING CITY | GUAGE LEAK AND BY VALVE; PAINTED RED
| 09-40012-1 | 310 |  | 8 | Transmission |  | Valves |  |  | Other | VALVE NEEDED GREASE | 2009-02-24 | 2009-03-27 | Other | GREASED VALVES | Steel/Wrought Iron |  | KING CITY | VALVE AND OTHER FITTINGS; PAINT YELLOW; GREASED VALVES, INLET VALVES TO FITTERS. SEE DRAWING 183721 CHANGE 6.
| 09-40013-1 | 310 |  | 0.75 | Single Service |  | Other |  | SCREWED FITTING | Other | REDOPPED FITTING | 2009-02-24 | 2009-10-22 | Other | REDOPE & TIGHTEN FITTINGS | Steel/Wrought Iron |  | KING CITY
| 09-40013-1 | 310 | [9 empty] | 2009-02-24 | [5 empty] | KING CITY | FIRE VALVE & HH SET LEAKING - REG 5PB SET 1%; PAINTED YELLOW, SAME AREA
| 09-40015-1 | 187 |  | 4 | Transmission |  | Valves |  |  | Other | NEEDED GREASE | 2009-02-27 | 2009-12-24 | Other | GREASED VALVE | Steel/Wrought Iron |  | KING CITY | BY PASS VALVE & VALVE #1 - ALL PAINT YELLOW, SAME AREA; GREASED BYPASS VALVE; GREASED VALVE, SOAP TEST, OKAY
| 09-40015-1 | 187 | [9 empty] | 2009-02-27 | [5 empty] | KING CITY | BY PASS VALVE & VALVE ALL PAINT YELLOW; MARK YELLOW
| 09-40015-1 | 187 |  | 5 | Transmission |  | Valves |  |  | Other |  | 2009-02-27 | 2009-12-24 | Other |  | Steel/Wrought Iron |  | KING CITY | GREASED BYPASS VALVE; GREASED VALVE - SOAP TEST OK
| 09-40015-1 | 187 |  | 4 | [7 empty] | 2009-02-27 | 2009-12-24 | Other | GREASED VALVE | Steel/Wrought Iron |  | KING CITY | BY PASS VALVE & VALVE & ALL PAINT YELLOW; MARK YELLOW; REPAIR DATE 12-29-2009; GREASED VALVE
| 09-40015-1 | 187 |  | 4 | Transmission |  | Valves |  |  | Other | NEEDED GREASE | 2009-02-27 |  |  |  | Steel/Wrought Iron |  | KING CITY | BY PASS VALVE & VALVE #1 - ALL PAINT YELL; SAME AREA; NEEDED GREASE; GREASED VALVES SOAP TEST OKAY
| 09-40021-1 | DFM-25 |  | 6 | Transmission |  | Valves |  |  | Unknown |  | 2009-03-26 | 2009-06-19 | Other | GREASED VALVES | Steel/Wrought Iron |  | KING CITY | 2 VALVES BELOW GROUND MARKED W/PAINT/ NO. 8 STATIC LINE BUSHING WALL MOUNT RECORDER; YELLOW PAINT; GREASED VALVES; GREASED V-2. STOPPED LEAK - NO LEAKS VISUALLY, V-1 WAS SOAP TESTED ALSO NO LEAKS VISUALLY - NO GREASE STEM. NO GAS LEAK AT PRESSURE RECORDER SENSING LINES.
| 09-40025-1 | 310 |  | 0.75 | Single Service |  | Valves |  |  | Other | GREASE STEM | 2009-03-26 | 2010-08-23 | Other | GREASED VALVE | Steel/Wrought Iron |  | C. KING | 3 OP ELEC. BOX H & H SET IN BOX; MARK YELLOW RAN RECHECK; GREASE STEM; GREASED VALVE; FOUND GAS LEAK AT SINGLE SERVICE HPR INLET VALVE LEAKING OUT GREASE STEAM BUTTON HEAD GREASED & LEAK STOPPED
| 09-40034-1 | 187 |  | 0.25 | Transmission |  | Valves |  |  | Other | DRY DOPE | 2009-05-01 | 2010-10-27 | Other | RESEAL PLUGS | Steel/Wrought Iron |  | SOLEDAD | VALVE BOX .2% V-40 .01; YELLOW PAINT; DRY DOPE; 1/4" METRIC NEEDLE VALVE PRESSURE TAPS ON EACH SIDE OF PCAPS; V-40.01 RESEALED; RESEALED PLUGS; FOUND PLUGS LEAKING ON 1/4" NEEDLE VALVES ON EACH SIDE OF VALVE 40.01 - RESEALED PLUGS
| 09-40034-1 | 187 |  | 0.25 | Transmission |  | Valves |  |  | Other |  | 2009-05-01 | 2010-10-27 | Other |  | Steel/Wrought Iron |  | SOLEDAD | HWY 101 WEST AFTER SOLEDAD VALVE BOX 40.01 2%; SAME AREA (YELLOW PAINT); SAME AREA; RESEAL PLUGS; RESCALLED PLUGS AND VALVE
| 09-40035-1 | 187 |  | 0.75 | Single Service | TRANSMISSION | Body of Pipe |  |  | Atmospheric Corrosion |  | 2009-05-01 | 2010-08-12 | Replace Partial Service |  | Steel/Wrought Iron |  | SOLEDAD | HWY 101./ MARK RED; RED PAINT; 1" BELOW SVC VALVE ON SERVICE OFF OF TRANS. MAIN; REPLACED 7" SECTION OF 3/4" STEEL PIPE. 3/4"SERVICE IS TRANS. PRESSURE
| 09-40036-1 | 187 |  | 0.75 | Single Service |  | Fitting |  |  | Other |  | 2009-05-01 | 2010-05-25 | Other |  | Steel/Wrought Iron |  | SOLEDAD | 2% H&H SET# 2596153X; DRY SEALANT; REPAIRED LEAKING FITTINGS
| 09-40036-1 | 187 | [9 empty] | 2009-05-01 | [5 empty] | SOLEDAD | 2% H&H SET #2596153X; MARK YELLOW
| 09-40036-1 | 187 |  | 0.75 | Transmission | SERVICE | Fitting |  |  | Other | DRY SEALANT | 2009-05-01 | 2010-05-25 | Other |  | Steel/Wrought Iron |  | SOLEDAD | 2% H&H SET#2596153X; SAME AREA (YELLOW PAINT); HPR SET; REPAIRED LEAKING FITTINGS.
| 09-40037-1 | 187 |  | 2 | Transmission |  | Other |  | UNION | Unknown |  | 2009-05-01 | 2010-10-27 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SOLEDAD | .3 IN BOX K 55; P. REG. STATION KRM -55 LEFT RUN UNION; TIGHTENED FITTING MOLE; FOUND LEAK ON UNION ON LEFT RUN, TIGHTENED UNIW UP MOLE LEAK STOPPED @ MRK - 55
| 09-40037-1 | 187 |  | 2 | Transmission |  | Other |  |  | Unknown |  | 2009-05-01 | 2010-10-27 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SOLEDAD | FRONT STREET REG PIT - 1.3 IN BOX; SAME AREA; THINGTEN FITTING
| 09-40038-1 | 187 | [9 empty] | 2009-05-01 | [5 empty] | SOLEDAD | DELETED
| 09-40038-1 | 187 | [9 empty] | 2009-05-01 | [5 empty] | SOLEDAD | DELETED; 3% ON VALVE; PAINT YELLOW NO LEAK!
| 09-40042-1 | 187 |  | 0.75 |  |  | Other |  | FITTINGS | Other | DRY DOPE | 2010-10-27 | 2010-10-27 | Other | RESEAL FITTINGS | Steel/Wrought Iron |  | KING CITY | FISHER BLOW OFF LEAKING & UNION ATOH SET; MARK YELLOW; RESEALED FITTINGS; PUT STATION ON BYPASS WITH A TANK & REPAIRED LEAKS ON FITTINGS & REPLACED FISHER H-202 RELIEF N~36.24958, W-121.19534
| 09-40042-1 | 187 |  | 0.75 | Transmission |  | Other |  |  | Other |  | 2009-05-04 | 2010-10-27 | Other |  | Steel/Wrought Iron |  | KING CITY | HAS M/LINE TAG - FISHER BLOW-OFF LEAKING AT UNION; MARK YELLOW SAME AREA; REPAIRED LEAK ON FITTING
| 09-40042-1 | 187 | [9 empty] | 2009-05-04 | [5 empty] | KING CITY | HAS M/LINE TAG - FISHER BLOW-OFF LEAKING AT UNION
| 09-40044-1 | 187 |  | 0.75 | Single Service |  | Other |  | UNION | Other | DRY DOPE | 2009-05-04 | 2010-11-03 | Other | RESEALED FITTINGS | Steel/Wrought Iron |  | GREENFIELD | MP 30.19 H&H ST UNION & 3/8CAP#60233840; MARK YELLOW; UNION; RESEALED FITTINGS & REPLACED REGULATOR & RELIEF, & REPLACED OLD VALVES, OLD EQUIP. & NO MAINT. STATION IN GOOD SHAPE NOW, SOAP TEST OK N-36.28651°, W-121.23882
| 09-40044-1 | 187 | [9 empty] | 2009-05-04 | [5 empty] | GREENFIELD | MP 30.19 H&H ST UNION & 3/8 CAP; MARK YELLOW
| 09-40044-1 | 187 | [9 empty] | 2009-05-04 | [5 empty] | GREENFIELD | MP30.19 HTOH SET UNION AND 3/8 CAP
| 09-40045-1 | 187 |  | 0.25 |  |  | Other |  | SENSE LINE FITTINGS | Other | LOOSE FITTING | 2009-05-04 | 2010-10-27 | Other | RESEAL FITTINGS | Steel/Wrought Iron |  | GREENFIELD | REG PIT 1 & 2 11%; MARK YELLOW; RT. RUN SENSE LINES; FOUND FITTINGS LEAKING RT. RUN SENSE LINES TIGHTENED UP & RESEALED FITTINGS
| 09-40045-1 | 187 |  | 0.25 | Transmission |  | Other |  |  | Other |  | 2009-05-04 | 2010-10-27 | Other |  | Steel/Wrought Iron |  | GREENFIELD | GREENLEAF LOOP & OAK - REG PIT 1 AND 2; RESEALL PLUG; RESEALLED PLUG
| 09-40045-1 | 187 | [9 empty] | 2009-05-04 | [5 empty] | GREENFIELD | GREENLEAF LOOP & OAK - REG PIT 1 AND 2
| 09-40045-1 | 187 | [9 empty] | 2009-05-04 | [5 empty] | GREENFIELD | GREENLEAF LOOP & OAK - REG PIT 1 AND 2; LEAK AT REG PIT GREENFIELD LOOP 1&2
| 09-40046-1 | 187 | [9 empty] | 2009-05-04 | [5 empty] | GREENFIELD | DELETED; 12TH STREET - SINGER FILTER LEAK; NOT FOUND
| 09-40047-1 | 187 |  | 0.75 | Single Service |  | Valves | Other | RELIEF & FITTINGS | Other | OLD EQUIP.; | 2009-05-04 | 2010-10-05 | Other | REPLACED REGULATOR, RELIEF, & D.S. VALVE & REDOPED FITTINGS | Steel/Wrought Iron |  | KING CITY | FISHER OFF 11 & BY PASS VALVE; YELLOW PAINT; REPLACED REG, & RELIEF, P.S. VALVE, REDOPED; FOUND GAS LEAKS ON BYPASS VALVE, INLET TO REG & ON H-ZOR RELIEF ON D.S. VALVE, SO REPLACED __REGULATOR N/FISHER 627, REPLACE H-ZOR. RELIEF & D.S. VALVE & REDOPED & TIGHTENED FITTINGS, INSTALLED LUBE FITTINGS ON INLET & BYPASS VALVES.
| 09-40047-1 | 187 |  | 0.75 | Single Service |  | Other |  |  | Other |  | 2009-05-04 | 2010-10-05 | Other |  | Steel/Wrought Iron |  | KING CITY | FISHER; SAME AREA; YELLOW PAINT; REPLACED REG AND RELIEF - REDOPPED; FOUND LEAK ON BYPASS VALVE, INLET TO REG AND H2 RELIEF ON D.S. VALVE, REPLACED HPR REG WITH FISHER 627, REPLACED H20R RELIEF AND D.S. VALVE
| 09-40047-1 | 187 | [9 empty] | 2009-05-04 | [5 empty] | KING CITY | DATE 9-14-10 NAME JAMES MORRIS
| 09-40047-1 | 187 |  | 0.75 | Single Service |  | Other |  |  | Other |  | 2009-05-04 | 2010-10-05 | Other |  | Steel/Wrought Iron |  | KING CITY | REPAIRED; FISHER; SAME AREA; YELLOW PAINT; REPLACED REG AND RELIEF - REDOPPED
| 09-40047-1 | 187 | [9 empty] | 2009-05-04 | [5 empty] | KING CITY
| 09-40048-1 | 187 |  | 0.75 | Transmission |  | Valves |  |  | Unknown |  | 2009-05-06 | 2010-10-05 | Other | LUBE & OPERATE VALVES | Steel/Wrought Iron |  | KING CITY | 2ND HOLD ST LEAK; MARK YELLOW; LUB & OPERATE VALVES; FOUND VALVES #6, 7, LEAKING TODAY, LUBED & OPERATED VALVES MOST OF LEAKS REPAIRED BACK ON 9-20-10 WHEN ROUTINE MAINT. WAS PERFORMED, MADE CORR TAG TO HAVE STATION UPDATED & REBUILT
| 09-40051-1 | 187 |  | 0.75 | Transmission |  | Valves |  |  | Other | DRY LUBE | 2009-05-08 | 2010-11-05 | Other | LUBED VALVES | Steel/Wrought Iron |  | KING CITY | .1 IN H&H BOX ONLY ONE (IN FIELD); PAINTED; INSTALLED LUBE FITTINGS - LUBED; INSTALLED LUBE FITTINGS & LUBED VALVES. REPLACED D.S. VALVE & RESEALED FITTINGS, PAINTED HPR SET, SOAP TEST OK, FOUND HPR OFF & LEFT IT OFF
| 09-40082-1 | 187 | 11.7 | [8 empty] | 2009-05-16 | [5 empty] | KING CITY | DELETED; H&H SET FISHER BLOW OFF #819615C
| 09-40082-1 | 187 | 11.77 | [8 empty] | 2009-05-15 | [5 empty] | KING CITY | H2H SET, FISHER BLOWOFF #819615C; NO LEAK FOUND (DELETED THIS LEAK)
| 09-40082-1 | 187 | 11.77 | [8 empty] | 2009-05-16 | [5 empty] | KING CITY | DELETED; H2H SET, FISHER BLOWOFF #819615C; NO LEAK FOUND (DELETED THIS LEAK)
| 09-40082-1 | 187 | 11.7 | [8 empty] | 2009-05-16 | [5 empty] | KING CITY | DELETED; H & H SET, FISHER BLOWOFF #819615C
| 09-40083-1 | 187 | 28.16 | 0.75 | Single Service |  | Valves |  |  | Other | DRY LUBE | 2009-05-18 | 2010-11-09 | Other | LUBE VALVES | Steel/Wrought Iron |  | KING CITY | H2 VALVE FISHER BLOW OFF & UNION; MARK YELLOW; DRY LUBE; INLET VALVE & BYPASS VALVE LUBED; INSTALLED LUBE FITTINGS ON INLET & BYPASS VALVES, RESEALED THREAD TO INLET OF REGULATOR, REPLACED D.S. VALVE, SINGLE SERVICE HPR OFF - SO LEFT IT OFF, SOAP TEST OK, PAINTED HPR. .3 TENTHS OF A MILE N/O TEAGE, N-36.25737º, W-121.20425º
| 09-40083-1 | 187 | 28.16 | [8 empty] | 2009-05-18 | [5 empty] | KING CITY | NORTH OF THORPE RD. H2H SET FISHER BLOWOFF UNION
| 09-40092-1 | [10 empty] | 2009-08-28 | [5 empty] | KING CITY | DELETED; ON FLANGE PAINTED IN YELLOW; "SEE ABOVE", FOUND REPAIRED
| 09-40092-1 | [10 empty] | 2009-08-28 | [5 empty] | KING CITY | BY PASS VALE IN CCAGED AREA; "SEE ABOVE" FOUND REPAIRED
| 09-40092-1 | 187 | [9 empty] | 2009-08-28 | [5 empty] | KING CITY | BY PASS VALVE; VALVE
| 09-40092-1 | 187 | [9 empty] | 2009-06-28 | [5 empty] | KING CITY | FOUND REPAIR, DELETED; JOLON RD - REG PIT V-22.82; AT REG PIT, NO LEAK IT WAS REPAIRED ALREADY (DELETED)
| 09-40095-1 | 187 | 46.65 | 8 | Transmission |  | Valves |  |  | Unknown | OTHER | 2009-10-08 | 2009-11-19 | Other |  | Steel/Wrought Iron |  | SOLEDAD | HWY 101 - OP MURPHY & SON ACROSS FROM PRISON; O.P. VALVE 46.63; GREASED ALL VALVES IN THE VAULT; GREASED ALL VALVES IN THE VAULT
| 09-40095-1 | 187 | [9 empty] | 2009-10-08 | [5 empty] | SOLEDAD | VALVE V 46.63
| 09-40095-1 | 187 | 46.65 | 8 | Transmission |  | Valves |  |  | Unknown |  | 2009-10-06 | 2009-11-19 | Other |  | Steel/Wrought Iron |  | SOLEDAD | HWY 101; O.P. VALVE 46.63; GREASED ALL VALVES IN THE VAULT
| 09-40096-1 | 187 | 45.13 | 0.75 | Branch Service | TRANSMISSION | Fitting | Mechanical Joint | RISER | Damage by Earth Movement | DRY PIPE SEALANT | 2009-10-08 | 2010-05-24 | Other |  | Steel/Wrought Iron |  | SOLEDAD | SILLMAN RD.; READING AT H TO H SET VALVE M.P. 45.13; SAME AREA; REPAIRED ALL LEAKING FITTINGS
| 09-40096-1 | 187 | 45.13 | 0.75 | Branch Service |  | Fitting |  |  | Damage by Earth Movement |  | 2009-10-08 | 2010-05-24 | Other |  | Steel/Wrought Iron |  | SOLEDAD | SILLMAN RD.; READING AT H TO H SET VALUE M.P. 45.13
| 09-40096-1 | 187 | [9 empty] | 2009-10-08 | [5 empty] | SOLEDAD | H2H SET HIGH SIDE VALVE LEAK; YELLOW PAINT
| 09-40097-1 | 187 | 45.39 | 0.75 | Transmission |  | Fitting |  |  | Other | LOOSE FTG. | 2009-10-09 | 2009-11-24 | Other | REMOVED & RESEALED | Steel/Wrought Iron |  | SOLEDAD | DUPLICATE 09-40096-1 ALREADY COMPL.; H 2 H SET IN BOX 2%; CLEANED LEAKING FITTINGS & RE SEALED, SOAP TEST OK; REMOVED LEAKING FITTINGS, RESEALED & REINSTALLED, SOAP TEST OK
| 09-40097-1 | 187 |  | 0.75 | Single Service |  | Valves |  |  | Other | DRY CORE | 2009-10-09 | 2010-05-24 | Other | GREASED THE VALVE | Steel/Wrought Iron |  | SOLEDAD | H2H SET IN BOX 2%; DRY CORE; H 2 H SET
| 09-40097-1 | 187 |  | 0.75 | Transmission |  | Fitting |  |  | Other |  | 2009-10-09 | 2009-11-24 | Other |  | Steel/Wrought Iron |  | SOLEDAD | H2H SET IN BOX 2%; REPLACED LEAKING FITTING
| 09-40104-1 | 187 | [9 empty] | 2009-10-12 | [5 empty] | SOLEDAD | DELETED; 41.06 1/2 TABS; MARK YELLOW; NO LEAK FOUND
| 09-40138-1 | 187 | [9 empty] | 2009-11-14 | [5 empty] | KING CITY | DELETED 5-20-10; V-8; NO LEAK
| 09-40139-1 | 187 |  | 2 | Single Service | TRANSMISSION | Valves |  |  | Other | NEEDS GREASE | 2009-11-20 |  |  |  | Steel/Wrought Iron |  | KING CITY | OFF AIRSTRIP & OASIS SAN BERNDA WINEY; LEAK AT GAS VALVE
| 09-40139-1 | 187 |  | 2 | Transmission |  | Valves |  |  | Other | NEEDS GREASE | 2009-11-20 | 2011-05-10 | Other | GREASE & OPERATE | Steel/Wrought Iron |  | SAN LUCAS | OFF AIRSTRIP & OASIS SAN BERNABE PURCHASING SHOP; LEAK AT VALVE LEAKS ON SET & BY PASS; GREASED & OPERATED, SOAP TEST OK;
| 09-40139-1 | 187 |  | 2 | Transmission |  | Valves |  |  | Other | NEEDS GREASE | 2009-11-20 | 2011-05-10 | Other | GREASE & OPERATE | Steel/Wrought Iron |  | SAN LUCAS | OFF AIRSTRIP & OASIS SAN BERNABE PURCHASING SHOP; LEAK AT VALVE LEAKS ON SET & BY PASS; GREASED & OPERATED, SOAP TEST OK; GREASED & OPERATED VALVES, SOAP TEST OK
| 10-40015-1 | 187 | [9 empty] | 2009-11-20 | [5 empty] | KING CITY | H2H SET IN 24X36" BOX; YELLOW PAINT
| 09-40140-1 | 187 | [9 empty] | 2009-11-23 | [5 empty] | KING CITY | SAN BENABA WINLY (OFF OAIS); IN GROUND NEXT TO HIGH TO HIGH SET
| 09-40140-1 | 187 |  | 2 | Transmission |  | Valves |  |  | Other | NO GREASE | 2009-11-24 | 2011-05-10 | Other | GREASE & OPERATE | Steel/Wrought Iron |  | KING CITY | SAN BENABA WINLY (OFF OAIS); NO LEAK FOUND; GREASED & OPERATED VALVES, SOAP TEST OK
| 09-40143-1 | 187 |  | 0.75 | Single Service |  | Mechanical Joint |  |  | Other | LOOSE FITTING | 2009-11-23 | 2011-05-10 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN ARDO | 62879 CATTLEMAN ROAD; GREASE VALVE; RESEALED & TIGHTENED FITTING, SOAP TEST OK; RESEAL & TIGHTENED LOOSE FITTING ON HI TO HI, SOAP TEST OK
| 09-10018- |  |  | 0.75 |  |  | Valves |  |  | Other | SEALS NEED GREASE | 2009-02-03 | 2009-02-09 | Tighten Cap or Bolt | GREASED VALVE | Steel/Wrought Iron |  | SANTA CRUZ | REG J11 VALVES CAPS; REPAIRED LEAKS BY TIGHTENING UP PIPE FITINGS AND GREASING INLET VALVE TO LEFT RUN OF STATION
| 09-10018 |  |  | 0.75 | Distribution Main |  | Valves |  |  | Other | SEALS NEED GREASE | 2009-02-03 | 2009-02-09 | Tighten Cap or Bolt | GREASED VALVE | Steel/Wrought Iron |  | SANTA CRUZ | REG J11 VALVES CAPS; REPAIRED LEAKS BY TIGHTENING UP PIPE FITTINGS AND GREASING INLET VALVE TO LEFT RUN OF STATION
| 09-10019-1 |  |  | 3 | Transmission |  | Other |  | FILTER | Construction Defect |  | 2009-02-03 | 2009-12-22 | Other | REPLACE FILTER | Steel/Wrought Iron |  | SCOTTS VALLEY | LOCKWOOD LANE, SCOTTS VALLEY, REG KO1 IN BOX; REPLACED FILTER; REPLACED LEAKING FILTER, SOAP TEST OK
| 09-10021 |  |  | 0.75 | Transmission |  | Other |  | STEEL TEE CAP | Other | DRY PIPE DOPE | 2009-02-04 | 2009-02-11 |  |  | Steel/Wrought Iron |  | SANTA CRUZ | HPR SET; J-08 HPR STATION @ GRAHAM HILL RD & HIDDEN CREEK; INLET MULLER CAP WAS LEAKING, SO PULLED IT OFF CLEANED THREADS WITH WIRE BRUSH REDOPED THREADS AND TIGHTED CAP BACCK UP TO REPAIR LEAK.
| 09-10021 |  |  | 0.75 | Transmission |  | Other |  | STEEL TEE CAP | Other | DRY PIPE DOPE | 2009-02-11 | 2009-02-11 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SANTA CRUZ | HPR SET; J-08 HPR STATION @ GRAHAM HILL RD & HIDDEN CREEK; INLET MULLER CAP WAS LEAKING, SO PULLED IT OFF CLEANED THREADS WITH WIRE BRUSH RE DOPED THREADS AND TIGHTED CAP BACK UP TO REPAIR LEAK
| 09-10024 |  |  | 0.75 | Transmission |  | Unknown |  |  | Unknown |  | 2009-02-04 |  | Other | NO LEAK FOUND | Steel/Wrought Iron |  | SANTA CRUZ | J07 REG STATION; SOAP TEST, NO LEAKS; NO LEAKS FOUND DURING SOAP TEST
| 09-10024 |  |  | 0.75 | Transmission |  | Unknown |  |  | Unknown |  | 2009-02-04 |  | Other | NO LEAK FOUND | Steel/Wrought Iron |  | SANTA CRUZ | J07 REG STATION; SOAP TEST, NO LEAKS; NO LEAKS FOUND DURING SOAP TEST
| 09-10036-1 |  |  | 0.75 | Single Service |  | Fitting |  |  | Other | PIPE DOPE | 2009-08-05 | 2009-08-20 | Other | TIGHTENED FITTINGS | Steel/Wrought Iron |  | SANTA CRUZ | HPR SET SOUTH OF DEER PATH; HPR SCT.; RE-DOPED & TIGHTENED FITTINGS; RON RMMD MORRIS SHUT DOWN SERVICE TEE, AND EDDY MERCADO AND HIS CREW DISASSEMBLED, RE-DOPED AND RE-ASSEMBLED HPR SET.
| 09-10036-1 | [10 empty] | 2009-03-05 | [5 empty] | SANTA CRUZ | HPR SET SOUTH OF DEER PATH; DOWN GRADE TO 2
| 09-10036-1 |  |  | 0.75 | Single Service |  | Fitting |  |  | Other | PIPE DOPE | 2009-03-05 | 2009-08-20 | Other | TIGHTENED FITTINGS | Steel/Wrought Iron |  | SANTA CRUZ | HPR SET SOUTH OF DEER PATH; HPR SCT.; RE-DOPED & TIGHTENED FITTINGS.; RON MORRIS SHUT DOWN SERVICE TEE, AND EDDY MERCADO AND HIS CREW DISASSEMBLED, RE-DOPED AND RE-ASSEMBLED HPR SET.
| 09-10036-1 | [10 empty] | 2009-03-05 | [5 empty] | SANTA CRUZ
| 09-20011-1 | 181B |  | 0.75 | Distribution Main | TRANSMISSION | Other |  | RELIEF | Equipment Malfunction |  | 2009-03-26 | 2009-03-26 | Other | REBUILT RE | Steel/Wrought Iron |  | WATSONVILLE | #2 BOX; HPR STATION @ AROMAS RD. & QUARRY RD.; REBUILT REGULATOR AT STATION & PAINTED STATION AND SET PRESS @ 30 PSIG.
| 09-20011 |  |  | 0.75 | Distribution Main | Transmission | Other |  | RELIEF | Equipment Malfunction |  | 2009-03-26 | 2009-03-26 | Other | REBUILT REG. | Steel/Wrought Iron |  | WATSONVILLE | THIS HAS BEEN FIXED; #2 BOX; HPR STATION @ AROMAS RD & QUARRY RD.; REBUILT REGULATOR AT STATION & PAINTED STATION AND SET PRESS @ 30 PSIG.
| 09-20013-1 |  |  | 6 | Transmission |  | Other |  | BLOW OFF | Unknown |  | 2009-03-27 | 2009-05-14 | Tighten Cap/Bolt - Fitting | OTHER-CLEAN "O" RING | Steel/Wrought Iron |  | PAJARO | AT FENCE; AT END OF MATIESVICH LANE @ FENCE
| 09-20013-1 | [10 empty] | 2009-03-27 | [5 empty] | PAJARO | AT FENCE
| 09-20015-1 | 181.B |  | 0.75 | Transmission |  |  |  |  | Other | GREASED VALVE | 2009-03-26 | 2009-06-15 | Other | GREASED | Steel/Wrought Iron |  | AROMAS | K14 REG STATION CUSTOMER SMELLS GAS;; END OF ANTON PLACE - AROMAS; SMALL LEAKS ON FIRE VALVE & STA. BYPASS VALVE. GREASED - STOPPED LEAK FOR NOW.
| 09-20015-1 | [10 empty] | 2009-03-26 | [5 empty] | AROMAS | K14 REG STATION CUSTOMER SMELLS GAS
| 09-20016-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | GREASE | 2009-03-26 | 2010-08-20 | Other | GREASED | Steel/Wrought Iron |  | AROMAS; | COLE ROAD AT ANZAR, VALVE MARKED V2.10; V2.10; GREASED VALVES & FLUSHED G. BUTTONS
| 09-20016 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | GREASE | 2009-03-26 | 2010-08-20 |  |  |  |  | AROMAS | VALVE MARKED V-2.10; 2(A) FORMS FOR THIS LEAK
| 09-20017-1 | 181-A |  | 0.25 | Transmission |  | Fitting |  |  | Other | DRY DOPE | 2009-03-28 | 2009-11-10 | Tighten Cap or Bolt | SOAP AND/OR TAPE | Steel-Other |  | PAJARO | SAN JUAN& RXR TRACKS K15 & K16 - YELLOW ZIPTIES; REDOPE & TIGHTEN; DOPED FITTING - SOAP TEST; REPAIRED LEAKS
| 09-20017-1 |  |  | 0.25 | Transmission | Gathering | Valves |  |  | Other | DRY DOPE | 2010-03-26 | 2009-11-10 | Soap and/or Tape - Other |  | Steel/Wrought Iron |  | PAJARO | K-15 SAN JUAN RD. REG STA. WATSONVILLE; 3 NEEDLE VALVES LEAKING. REDOPED & TIGHTENED
| 09-20020-1 | 181605 |  | 0.75 | Transmission |  | Valves |  |  | Other | VALVE | 2009-04-21 | 2009-06-16 | Other | GREASE VALVE | Steel/Wrought Iron |  | WATSONVILLE | VALVE TO J45; MEFIVERS WAY; J-45 @ 916A LARKIN VALLEY RD; GREASED & OPERATED
| 09-20043-1 | [10 empty] | 2009-06-03 | [5 empty] | WATSONVILLE | MC CAHAN FLORAL #5 BOX REG PIT J-20; NO GAS
| 09-20046-1 |  |  | 1.25 | Transmission |  | Other |  | GREASE FITTING | Unknown |  | 2009-06-03 | 2009-07-17 | Other | GREASE FITTING | Steel/Wrought Iron |  | WATSONVILLE | VALVE Z 13 AT DFM CROSSING; INLET & FIRE VALVE TO J-35
| 09-20048-1 | [10 empty] | 2009-08-03 | [5 empty] | AROMAS | AT GAS METER BOX OF ADDRESS
| 09-20049-1 |  |  | 0.75 | Service |  | Valves |  |  | Other | GREASE | 2009-06-03 | 2009-11-19 | Other | GREASE | Steel/Wrought Iron |  | AROMAS | INTERSECTION OF SAN JUAN RD& QUAIL HILL LN.; AT VALVE B-77 WEST SIDE OF SAN JUAN RD AT RISER; GREASED VALVE & REPLACED GREASE STEM; REPLACED GREASE STEM & GREASED VALVE B-77
| 09-20049-1 | [10 empty] | 2009-06-03 | [5 empty] | AROMAS | INTERSECTION OF SAN JUAN RD & QUAIL HILL LN; AT VALVE B??
| 09-20049-1 | [10 empty] | 2009-06-03 | [5 empty] | AROMAS | INTERSECTION OF SAN JUAN RD. & QUAIL HILL LN.; AVLVE B-77 WEST SIDE OF SAN JUAN RD. AT RISER;
| 09-50001-1 | MTY 1 | [9 empty] | 2009-01-02 | [5 empty] | SALINAS | T&R DELETED; MAIN LINE VALVE V-6.90; NO LEAK FOUND
| 09-50003-1 | MTY 1 |  | 2 | Distribution Main |  | Valves |  |  | Other | NO GREASE | 2009-01-07 | 2009-07-01 | Other | GREASED VALVE | Steel/Wrought Iron |  | SALINAS | 1% VALVE SR 5 88; VALVE; CORRAL DE TERRA RD. AND HWY. 68 REG STA SRS-88; GREASED VALVE; GREASED VALVE TO STOP LEAK. V.1
| 09-50005-1 | 3017 | 0.03 | 06.00 - 11.00 | Transmission |  | Valves |  |  | Unknown |  | 2009-03-13 | 2009-03-18 | Other | WHEEL VALVE | Steel/Wrought Iron |  | SALINAS | 301 7; YELLOW PAINT; ESPINOSA RD. SALINAS; WHEEL VALVE WAS LEAKING, GRESED BY HAND PUMP STOPPED LEAKING. SKINNER CLAM ON GREASE FITTING EXTENSION WAS LOOSE AND LEAKING BY, TIGHTEN CLAMP, STOPPED LEAKING.
| 09-50006-1 | 6 D7M | 2.3 | 0.75 | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-01-13 | 2009-03-18 | Other | H-202 RELIEF VALVE. | Steel/Wrought Iron |  | SALINAS | FISHER BLOW OFF; FOXWOOD LN & ESPINOSA RD., SALINAS; RELIEF VALVE WAS WEEPING GAS, RE-ADJUSTED PRESS TO STOP GAS FROM LEAKING DYE.
| 09-50008-1 | 6 D7M | 1.63 | 0.75 | Distribution Main |  | Other |  | RELIEF H-202 | Equipment Malfunction |  | 2009-01-13 | 2009-06-24 | Other | RELIEF VALVE | Steel/Wrought Iron |  | SALINAS | FISHER BLOW OFF; NO FIRE VALVE; FISHER; LEAK WAS REPAIRED RE-ADJUSTED 6/24/09 CLEANED.
| 09-50009-1 | 6 D7M |  | 2 | Single Service |  | Body of Pipe | Regulator | VALVE | Atmospheric Corrosion | EXTERNAL CORROSION, STRESS CORROSION CRACKING | 2009-01-13 | 2009-04-10 | Other | PILOTS ON REGULATORS | Steel/Wrought Iron |  | SALINAS | SET HAS LEAKS ALL OVER/ NO FIRE VALVE; MARK YELLOW; REPAIRED LEAKS ON SET (REG) SINGLE SERVICE, REPLACED PILOTS, REPAIRED SEVERAL LEAKS ON PIPELINE.
| 09-50009-1 | 6 D7M |  | 2 | Single Service |  | Body of Pipe | Regulator | VALVE | Atmospheric Corrosion | EXTERNAL CORROSION, STRESS CORROSION CRACKING | 2009-01-13 | 2009-04-10 | Other | PILOTS ON REGULATORS | Steel/Wrought Iron |  | SALINAS | SET HAS LEAKS ALL OVER/ NO FIRE VALVE; MARK YELLOW; REPAIRED LEAKS ON SET (REG) SINGLE SERVICE, REPLACED PILOTS, REPAIRED SEVERAL LEAKS ON PIPELINE.
| 09-50010-1 | 6 D7M | 3.36 | 2 | Single Service |  | Other |  | LEAK ON THREADED FITTING | Other | DOPE DRYOUT | 2009-01-13 | 2009-09-03 | Other | REDOPE FITTING & TIGHTEN | Steel/Wrought Iron |  | SALINAS | 2" UNION & FISHER BLOW OFF 1%; LEAK ON THREADED FITTING; 2" UNION ON BYPASS, VARIOUS OTHER THREADED FITTINGS REDOPED LOOSE FITTINGS.; REDOPE & TIGHTEN LOOSE FITTINGS, INSTALL PLUGS. SOAP TEST OK.
| 09-50072-1 | 187 | 62 | 8 | Transmission |  | Body of Pipe |  |  |  |  | 2009-04-04 | 2009-04-04 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | SHUT VALVES AT TWO LOCATIONS. CUT OUT DAMAGED PIPE & REPLACED; 21' OF PIPE REPLACED. WELDS XRAY TESTED OK & SOAP TEST OK
| 09-50077-1 | 187 | 63.44 | 0.75 | Distribution Main |  | Regulator |  |  | Other | OLD | 2009-04-10 | 2009-06-25 | Other | REG. TO REPLACE HI TO HI | Steel/Wrought Iron |  | SALINAS | LEAKING AT REGULATOR ON HI TO HI SET; HI TO HI SET
| 08-50091-1 | 301C | 13.85 | 4 | Transmission |  | Other |  | BLOW OFF FLANGE | Other | GASKET | 2008-11-21 | 2009-11-19 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | SALINAS | 201 MONTERY-SALINAS HIGHWAY (68) - VALVE 16.63; REPLACED GASKET ON BLOW OFF FLANGE; REPLACED LEAKING GASKET, SOAP TEST OK
| 09-50107-1 | 301A | [9 empty] | 2009-04-25 | [5 empty] | MOSS LANDING | MOSS LANDING TAPS, V1 AND V2 LEAKING .5; IN V-1, V-2 FRAME & COVER
| 09-50107-1 | 301A | [9 empty] | 2009-04-25 | [5 empty] | MOSS LANDING | V1 & V2 LEAKING .5; NO GAS FOUND
| 09-50108-1 | 301A |  | 0.75 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 2009-04-27 | 2009-07-23 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | PRUNDALE | V-1 3%/ P/U OFF TEE SUPPLYING FIRE VALVE V-1; DOPE AND TIGHTEN CAP; CLEAN, DOPE, & TIGHTEN CAP ON P/U-OFF TEE SUPPLYING FIRE VALVE V-1
| 09-50110-1 | 301B | 390 | 0.75 | Distribution Main |  | Valves |  |  | Construction Defect |  | 2009-04-27 | 2010-09-29 | Other | GREASED VALVE ALL OK | Steel/Wrought Iron |  | PRUNDALE | VALVE; GREASED VALVE; GREASED VALVE. SOAP TEST OK.
| 09-50110-1 | DFM | 20.36 | 0.75 | Transmission |  | Valves |  |  | Construction Defect |  | 2009-04-27 | 2010-09-29 | Other |  | Steel/Wrought Iron |  | SALINAS | VALVE; SAME AREA; GREASED GAS VALVE
| 09-50111-1 |  |  | 1.25 | Transmission |  | Valves |  |  | Other |  | 2009-04-27 | 2009-06-23 | Other |  | Steel/Wrought Iron |  | PRUNDALE | VALVES MARKING YELLOW 5%; GREASED VALVE; INLET VALVE LEAKING - GREASED VALVE
| 09-50114-1 | 187 |  | 0.75 | Transmission |  | Valves |  |  | Other | BAD O-RINGS | 2009-04-28 | 2010-09-01 | Other | REPLACE & LUBE ORINGS | Steel/Wrought Iron |  | SALINAS | 3% AT VALVE NEW PLANT 2 VALVE; IN X84T 7 IN VALVE FRAME & COVER; 2 - G-5 BOXES S/O MARKINGS RD STATIONS; REPAIRED GAS LEAKING ON VALVE TEES FOR SCADA LINES REPLACED OLD DRY O-RINGS. IN MULLER TEES
| 09-50115-1 | 187 |  | 0.75 | Transmission |  | Other |  | LUBE FITTING | Other | DRY DOPE | 2009-04-30 | 2010-09-17 | Other | LUBE FITTING | Steel/Wrought Iron |  | SALINAS | POTTER RD. VALVES ST_____ LEAKING; IN 3 X 2 BOX'S SAME AREA; LUBE FITTING LEAKING ON VALVE 2; LUBE VALVE #2 & REDOPPED LUBE FITTING @ VALVE STATION
| 09-50115-1 | 187 | [9 empty] | 2009-04-30 | [5 empty] | SALINAS | ST 187 60.03 ALL VALVE LEAKING; IN 3' X 2' BOX'S;
| 09-50118-1 | 187 |  |  | Single Service |  | Valves |  |  | Other | NO GREASE; ; | 2009-05-01 | 2010-09-09 | Other | GREASE & OPERATED | Steel/Wrought Iron |  | SOLEDAD | BY PASS VALVE LEAKING 2%; (MILL TRAILER PARK); MARK YELLOW; TWO BYPASS VALVES LEAKING; GREASED VALVES.; GREASED & OPERATED, SOAP TEST OK
| 09-50119-1 | 187 | 60 | 4 | Transmission |  | Valves |  |  | Unknown |  | 2009-04-01 | 2010-10-05 | Other | LUBE & OPERATE VALVE | Steel/Wrought Iron |  | SOLEDAD | VALVE 2% @ BYPASS VALVE @ SRT-18; RED COVER; LUBED & OPERATED BYPASS VALVE @ DIST. REG. STATION SRT-18, VALVE BURIED & IN G-5 BOX, PAINTED RED
| 09-40040-1 | 187 | [9 empty] | 2009-04-01 | [5 empty] | SOLEDAD | VALVE 2%; RED COVER
| 09-50120-1 | 187 | [9 empty] | 2009-05-01 | [5 empty] | SOLEDAD
| 09-50120-1 | 187 | 46.73 | 0.75 | Single Service |  | Fitting | Other | BLOW OFF | Other | LOOSE FITTING | 2009-06-01 | 2009-11-24 | Other | TIGHTEN FITTINGS | Steel/Wrought Iron |  | SOLEDAD | OFF HIGHWAY 101 - H&H SET FISHER BLOW OFF; CLEANED FITTING RESEALED & INSTALLED SOAP TEST OK; CLEANED FITTING, RESEALED & INSTALLED. SOAP TEST OK.
| 09-50121-1 | 301B |  | 2 | Distribution Main |  | Regulator |  |  | Equipment Malfunction |  | 2009-05-07 | 2009-05-07 | Other | REG. | Steel/Wrought Iron |  | SALINAS | 10% AT REG BLOW OFF; WE FOUND GAS LEAKING THROUGH THE REG. VENT. REBUIT THE REGULATOR.
| 09-50122-1 |  |  | 0.5 | Single Service |  | Body of Pipe |  |  |  |  | 2009-05-07 | 2009-05-07 | Replace Partial Service |  | Aldyl A (Tan or Gray) |  | PRUMEDALE | REPLACED 12" OF 1/2" PLASTIC PIPE WITH 2 MET- FIT COUPLINGS.; INSTALLED TWO METFIT COUPLINGS/ REPLACED 12" OF 1/2" PIPE 12' FROM RISER SOAP TEST OK.
| 09-50123-1 | 301B |  | 0.75 | Single Service |  | Valves |  |  | Construction Defect |  | 2009-05-07 | 2010-11-05 | Other | RESEALED BY PASS VALVE | Steel/Wrought Iron |  | SALINAS | HTOH SET 1/2 SHUT OFF LEAKING .1; 1/2" SHUT OFF; REPAIRED GAS LEAKS; NEED CREW TO DIG UP PEN OFF TEE @ MAIN TO REPAIR BYPASS, ALL LEAKS REPAIRED ON 11-5-10, SOAP TEST OK, CUT OUT BYPASS & INSTALLED A DOWNSTREAM BYPASS
| 09-50124-1 | 301B | [9 empty] | 2009-05-07 | [5 empty] | SALINAS | H TO H ST LEAK; YELLOW PAINT LEAK ON FITTING NO LEAKS FOUND BEEN REPAIRED
| 09-50125-1 | 301B |  | 0.75 | Single Service |  | Valves |  |  | Other | OLD - NO MAINT. | 2009-05-07 | 2010-11-01 | Other | LUBED VALVES | Steel/Wrought Iron |  | SALINAS | HTOH SET 2%; YELLOW PAINT; LEAKS ON FITTINGS; LUBED INLET & BYPASS VALVES; FOUND LEAKS @ 437 HITCHOCK HPR SET. IN LET & BY PASS LEAKING, INSTALLED LUBE FITTING ON INLET VALVE LUBED & OPERATED BOTH VALVES RESETED THREADS ON INLET TO REG & REPLACED RELIEF
| 09-50126-1 | 301B |  | 0.75 | Single Service |  | Valves |  |  | Other |  | 2009-05-07 | 2009-07-01 | Other | STOPCOCK VALVE | Steel/Wrought Iron |  | SALINAS | .1 AT S/COCK BELOW 4476870; YELLOW PM; LEAKING BELOW STOP COCK, REPAIRED.
| 09-50127-1 | 301B | [9 empty] | 2009-05-07 | [5 empty] | SALINAS | HTOH SET LEAKING MARK YELLOW; MARK YELLOW VALVE CASING NO LEAK FOUND; NO LEAKS FOUND - HPR WAS REPAIRED DURING T.P. DIG-IN, SOAP TEST OK.
| 09-50128-1 | 187 |  | 0.75 | Transmission |  | Valves |  |  | Other | DRY LUBE | 2009-05-08 | 2010-11-05 | Other | LUBED VALVE; | Steel/Wrought Iron |  | CHURLAN | H2H SET BY PASS LEAKING; YELLOW PAINT; INSTALLED LUBE FITTING - LUBED; INSTALLED LUBE FITTINGS IN INLET VALVE & BYPASS VALVE AND LUBED VALVES, PAINTED HPR SOAP TEST OK
| 09-50129-1 |  |  | 1 | Single Service |  | Riser |  |  | Construction Defect |  | 2009-05-19 | 2009-08-07 | Replace Valve < 2 inch |  | PE2406 (Yellow or Orange) |  | CASTROVILLE | BELOW STOPCOCK - ISLAMIC CENTER OF CASTROVILLE; RISER; REPLACE VALVE - 1/4"; EXCAVATE PLASTIC SERVICE SQUEEZE PIPE, REPLACE SERVICE VALVE. REMOVE SQUEEZER. PURGE. SOAP TEST OK.
| 09-50132-1 | 103 | [9 empty] | 2009-05-23 | [5 empty] | SALINAS | .01 VALVE FRESH EXPRESS;
| 09-50132-1 | 103 | [9 empty] | 2009-05-23 | [5 empty] | SALINAS | FRESH EXPRESS - .01 VALVE; NO GAS FOUND
| 09-50133-1 | 103 | [9 empty] | 2009-05-23 | [5 empty] | SALINAS | H2H SET LEAK .5%; MARK YELLOW; NO LEAKS
| 09-50134-1 | 103 | [9 empty] | 2009-05-23 | [5 empty] | SALINAS | H2H SET UNION S/COCK HILLSIDE NUR; MARK YELLOW NO LEAK FOUND; FIRE VALVE BURNED
| 09-50135-1 | 103 | [9 empty] | 2009-05-23 | [5 empty] | SALINAS | DELETED; CREEKSIDE NURSERY, H2H SET .5; SAME AREA NO LEAK FOUND
| 09-50135-1 | 103 | [9 empty] | 2009-05-23 | [5 empty] | SALINAS | H2H SET .5 VALVE BURNED; MARK YELLOW
| 09-50135-1 | 103 | [9 empty] | 2009-05-23 | [5 empty] | SALINAS | CREEKSIDE NURSERY, H2H SET .5; NO LEAK FOUND
| 09-50136-1 | 103 | [9 empty] | 2009-05-23 | [5 empty] | SALINAS | DIST REG. ST; MARK YELLOW SAME AREA
| 09-50136-1 | 103 | [9 empty] | 2009-05-23 | [5 empty] | SALINAS | DIST REG ST. 2 VALVES; MARK YELLOW NO LEAKS FOUND @ SRS-44; NO LEAKS FOUND @ SRS-44, SOAP TEST OK
| 09-50137-1 | 103 |  | 12 | Transmission |  | Valves |  |  | Other | VALVE SOC | 2009-05-23 | 2009-11-20 | Other | GREASED VALVES | Steel/Wrought Iron |  | SALINAS | VAULT ISSUED V-25.47/SVQ-33
| 09-50138-1 | 103 | [9 empty] | 2009-05-23 | [5 empty] | SALINAS | H2H LEAKING FISHER BLOW OFF; NO LEAK FOUND
| 09-50138-1 | 103 | [9 empty] | 2009-05-23 | [5 empty] | SALINAS | FRESH EXPRESS, H2H LEAKING FISHER BLOWOFF; NO LEAK FOUND
| 09-50139-1 | 103 | 0 | 6 | Transmission |  | Fitting |  |  | Construction Defect |  | 2009-05-23 | 2009-07-17 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SALINAS | FIRE VALVE MP 0.+00; TIGHTEN LOOSE FITTING; CLEAN & RE-TIGHTEN COMPLETION CAP. SOAP TEST OK.
| 09-50140-1 | 103 | [9 empty] | 2009-05-23 | [5 empty] | SALINAS | .5 IN VAULT; MARK YELLOW
| 09-50140-1 | 103 |  | 0.375 | Distribution Main |  | Fitting |  |  | Unknown |  | 2009-05-23 | 2009-07-02 | Other | SENSEING TUBING | Steel/Wrought Iron |  | SALINAS | .5 IN VAULT; MARK YELLOW; LOADING LINE REPAIRED-TIGHTEN UP FITTING
| 09-50141-1 | 103 |  | 8 | Transmission |  | Valves |  |  | Other | VALVE SEAL | 2009-05-23 | 2009-11-20 | Other | GREASED VALVE | Steel/Wrought Iron | GREASED VALVE | SALINAS | NATIVDAD & E. LAUREL 2% VAULT - VALVE V22.21; READING AT VALVE- SAME AREA; FOUND V.-1 LEAKING SO GRASED; GREASED & LUBED VALVES IN PIT
| 09-50142-1 | 103 | 23.55 | 0.75 | Transmission |  | Valves |  |  | Other | LOOSE FITTING | 2009-05-23 | 2009-07-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SALINAS | BOTH REG BANKS LEAKING .6 VALVE; MARK YELLOW; REPAIRED LEAKS AT POWER GAS BANKS.
| 09-50145-1 | 103 |  | 2 | Distribution Main |  | Valves |  |  | Other | NO GREASE | 2009-05-30 | 2009-08-28 | Replace Valve >= 2 inch |  | Steel/Wrought Iron |  | SALINAS | MONTERYE FISH - H2H SET 5X8 LEAKING; YELLOW PAINT; SERVICE TAP ON TRANSMISSION LINE; CHANGED VALVES
| 09-50145-1 | 103 |  | 2 | Distribution Main |  | Valves |  |  | Other | NO GREASE | 2009-05-30 | 2009-08-28 | Other | GREASED VALVE | Steel/Wrought Iron |  | SALINAS | H2H SET 5 & 8 LEAKING; YELLLOW PAINT; GREASED VALVES & OPERATED, SOAP TEST OK
| 09-50146-1 | 103 | [9 empty] | 2009-05-30 | [5 empty] | SA | H2H SET BY PASS VALVE 2%; MARK YELLOW
| 09-50146-1 | 103 |  | 0.75 | Distribution Main |  | Valves |  |  | Unknown |  | 2009-05-30 | 2009-12-01 | Other | GREASED BYPASS VALVE | Steel/Wrought Iron |  | SALINAS | H2H SET BYPASS VALVE 2%; MARK YELLOW; GREASED BYPASS VALVE; GREASED BYPASS VALVE @ SINGLE SERVICE HPR, INSTALLED LOCK
| 09-50165-1 | 103 | 23.55 | 6 | Transmission |  | Valves |  |  | Other | PACKING LEAK | 2009-07-06 | 2009-10-02 | Other | REPLACED PACKING | Steel/Wrought Iron |  | SALINAS | OPERATING REGULATOR (CONTROL VALVE); VALVE 3 STEM; LEAKING OUT OF PACKING ON VALVE 3
| 09-50165-1 | 103 | 23.55 | [8 empty] | 2009-07-06 | [5 empty] | SALINAS | CALIFORNIA REG. STATION - OPERATING REGULATOR; GREASED & WORKED VALVE
| 09-50165-1 | 103 | 23.55 | [8 empty] | 2009-07-06 | [5 empty] | SALINAS | REPAIRED; CALIFORNIA REG. STTAION - OPERATING REGULATOR; NO GAS FOUND
| 09-70032-1 |  |  | 0.5 | Transmission |  | Valves |  |  | Other | LOOSE NUT | 2009-02-10 | 2009-11-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MONTEREY | FIGUEROA AND FRANKLIN STS INSIDE PIT MARKED YELLOW; INSIDE BIG FRANK AT PIT MARKED YELLOW; SAME AREA; IN VAULT; TIGHTENED PACKING NUT
| 09-70033-1 | 1815-02 | 7.96 | 0.75 | Single Service |  | Valves |  |  | Other | LACK OF GREASE | 2009-02-10 | 2009-03-09 | Other | GREASED VALVE | Steel/Wrought Iron |  | MARINA | HIGHT TO HIGH SET, NW CORNER IN OPEN FIELD; IMJIN & 8TH - NW; HPR SET GREASED BY-PASS VALVE; GREASED BY-PASS VALVE (3/4") SOAP TEST FOR LEAKS
| 09-70033-1 | [10 empty] | 2009-02-10 | [5 empty] | MARINA | HIGHT TO HIGH SET; NW CORNER IN OPEN FIELD; IMGIN & ITH - NW
| 09-70034-1 | 301 |  | 0.25 | Transmission |  | Fitting |  |  | Other | DRY DOPE | 2009-02-10 | 2009-11-30 | Other | DOPE THREADS | Steel/Wrought Iron |  | MARINA | RESERVATION RD. AT DEL MONTE - MARKED IN YELLOW; AREA MARKED WITH YELLOW X PAINT; SAME AREA; DRY DOPE ON PIPE THREADS
| 09-70036-1 | [10 empty] | 2009-02-10 | [5 empty] | SEASIDE | DELETED NO LEAK; GIGLING PIT AT NOMEAU ROAD, SEASIDE, NEAREST 1; NO LEAK FOUND
| 09-70036-1 | [10 empty] | 2009-02-10 | [5 empty] | SEASIDE | GIGLING PIT AT NOMEAU ROAD, SEASIDE, NEAREST 1; GIGLING PIT NEAREST HWY 1, MARKED YELLOW; NO LEAK FOUND (DELETED THIS)
| 09-70036-1 |  |  |  | Transmission |  | Valves |  |  | Unknown |  | 2009-02-10 | 2009-09-17 | Other | LUBED & OPERATED VALVES | Steel/Wrought Iron |  | SEASIDE | PIT NEAREST HWY 1, AREA MARKED IN YELLOW PAINT X; GIGLING PIT NOUMEA RD.
| 09-70037-1 |  |  | 4 | Transmission |  | Valves |  |  | Other | NEEDS GREASE | 2009-02-10 | 2009-11-30 | Other | GREASED VALVE | Steel/Wrought Iron |  | SEASIDE | LA SALLE ST. AND FREMONT AVE. MARKED YELLOW; LA SALLE AND FREMONT - VALVE ON LA SALLE; SAME AREA; GREASED VALVE
| 09-70038-1 |  |  | 0.5 | Distribution Main |  | Fitting |  |  | Other | VARIOUS FITTINGS | 2009-02-10 | 2009-09-17 | Other | REDOPED & TIGHTEN VARIOUS FITTINGS | Steel/Wrought Iron |  | CARMEL | AQUIJITO ROAD AND HIGHWAY 1, IN YELLOW AT PIT; AREAS MARKED IN YELLOW PAINT AT PITS; REDOPED & TIGHTEN VARIOUS FITTINGS
| 09-70038-1 |  |  | 0.75 | Distribution Main |  | Other |  | PLUG ON FILTER | Other | OLD SEALANT | 2009-02-10 | 2009-12-11 | Other | REDOPED PLUG | Steel/Wrought Iron |  | CARMEL | AQUAJITO ROAD AND HIGHWAY 1, IN YELLOW AT PIT; AREAS MARKED IN YELLOW PAINT AT PAINTS; REDOPED PLUG & TIGHTENED FITTINGS; REPAIRED LEAKS DURING CLASS "A" INSPECTION
| 09-70038-1 |  | 2.13 | [8 empty] | 2009-02-10 | [5 empty] | CARMEL | READING MARKED IN YELLOW PAIN X C PITS; AREAS MARKED IN YELLOW PAINT @ PIPES
| 09-70038-1 |  |  | 0.75 | Distribution Main |  | Other |  | PLUG ON FILTER | Other | OLD SEALANT | 2009-02-10 | 2009-12-11 | Other | REDOPED PLUG | Steel/Wrought Iron |  | CARMEL | AQUAJITO ROAD AND HIGHWAY 1, IN YELLOW @ PIT; AREAS MARKED IN YELLOW PAINT AT PITS; REDOPED PLUG & TIGHTENED FITTINGS; REPAIRED LEAKS DURING CLASS "A" INSPECTION
| 09-70041-1 | 1813-02 | 15.7 | 1 | Distribution Main |  | Regulator |  |  | Construction Defect |  | 2009-02-13 | 2009-03-06 | Other | REPAIR REGULATOR | Steel/Wrought Iron |  | MONTEREY | HPR SET 200 WEST OF HWY 68 MARKED WITH YELLOW PAINT; SEE ABOVE INFO; REPLACED ORING ON H.P. FISHER REGULATOR. SOAP TEST FOR LEAKS
| 09-70041-1 | [10 empty] | 2009-02-13 | [5 empty] | MONTEREY | HPR SET 200 WEST OF HWY 68 MARKED WITH YELLOW PAINT; SEE ABOVE INFO
| 09-70042-1 | 1813-02 | 17.5 | 0.75 | Single Service |  | Regulator |  |  | Construction Defect |  | 2009-02-13 | 2009-03-09 | Other | REMOVE & RE-INSTALL DOPED NIPPLE INTO REGULATOR | Steel/Wrought Iron |  | MONTEREY | HPR SET DOWN IN RAVINE, PAINTED YELLOW ON HWY 68; SEE ABOVE INFO; LEAK ON HPR SET REMOVE & REDOPED & RE-INSTALL; REMOVE, REDOPE & RE-INSTALL NIPPLE INTO UP STREAM SIDE OF REGULATOR
| 09-70043-1 | 1813-02 | 15.62 | 0.75 | Single Service |  | Valves |  |  | Other | GREASED VALVE | 2009-02-13 | 2009-03-06 | Other | GREASED VALVE | Steel/Wrought Iron |  | MONTEREY | APPROX 250' S/W OF 2901 HWY 68 ENTRANCE PAINTED YELLOW W/STAK - HPR SET; SEE ABOVE INFO; HPR SET GREASED VALVE; GREASED VALVE; GREASED VALVE TO CORRECT 301. SOAP TEST FOR LEAKS
| 09-70044-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 2009-02-13 | 2009-04-02 | Other | GREASED VALVE | Steel/Wrought Iron |  | MONTEREY | NEAR HWY 68 WEST OF ENTRANCE (BLOCK VALVE); MARKED YELLOW PAINT; GREASED ALL VALVES, NO VISUAL LEAKS.
| 09-70045-1 | 1813-02 | 14.65 | 0.375 | Distribution Main |  | Regulator |  |  | Construction Defect |  | 2009-02-13 | 2009-03-06 | Other | TIGHTENED FITTING | Steel/Wrought Iron |  | MONTEREY | ABOVE GROUND REG. PIT FURTHEST BACK ON HWY 68 MARKED WITH YELLOW PAINT SUB-SURFACE PIT MARKED TOO; SEE ABOVE INFO.; TIGHTENED STAINLESS STEEL FITTING; TIGHTENED FITTING; TIGHTENED STAINLESS STL. FITTINGS. SOAP TEST FOR LEAKS
| 09-70045-1 | [10 empty] | 2009-02-13 | [5 empty] | MONTEREY | ABOVE GROUND REG. PIT FURTHEST BACK ON HWY 68 MARKED WITH YELLOW PAINT SUB-SURFACE PIT MARKED TOO; SEE ABOVE INFO
| 09-70046-1 | 181-02 | 13.27 | 0.75 | Single Service |  | Regulator |  |  | Construction Defect |  | 2009-02-13 | 2009-03-06 | Other | TIGHTENED UNION | Steel/Wrought Iron |  | MONTEREY | HPR SET NEAR FENCE NEAR HWY 68 MARKED W/ STALE & YELLOW PAINT; SEE ABOVE INFO'; TIGHTENED UNION & SOAP TEST FOR LEAKS
| 09-70046-1 | [10 empty] | 2009-02-13 | [5 empty] | MONTEREY | HPR SET NEAR FENCE NEAR HWY 68 MARKED W/STAKE & YELLOW PAINT; SEE ABOVE INFO
| 09-70047-1 | 1813-02 | 13.35 | 0.75 | Single Service |  | Regulator |  |  | Construction Defect |  | 2009-02-13 | 2009-03-06 | Other | TIGHTENED UNION | Steel/Wrought Iron |  | MONTEREY | LEAK @ HPR SET LOW IN RAVINE, OFF HWY 68 MARKED IN YELLOW PAINT; SEE ABOVE INFO; TIGHTENED UNION, SOAP TEST FOR LEAKS
| 09-70047-1 |  |  | 1.25 | Distribution Main |  | Fitting |  |  | Other | NEEDS TIGHTENING | 2009-02-13 | 2009-03-10 | Other | RE-DOPED AND TIGHTENED FITTING | Steel/Wrought Iron |  | MONTEREY | LEAK @ HPR SET LOW IN RAVINE OFF HWY 68 MARKED IN YELLOW PAINT; SEE ABOVE INFO; TOOK OUT ONE RUN AT A TIME, AND REMOVED FITTINGS. REDOPED AND PUT BACK TOGETHER.
| 09-70049-1 | [10 empty] | 2009-02-13 | [5 empty] | MONTEREY | N/E CORNER OF RAGSDALE AND HYW 68 INTERSECTION UNIONS LEAKING MARKED IN YELLOW PAINT; SEE ABOVE INFO
| 09-70078-1 | 1813- |  | 4.11 | Transmission |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2009-03-24 | 2009-03-24 | Replace TP Main | SOAP AND/OR TAPE, WELDED SLEEVE/CAN | Steel/Wrought Iron |  | SEASIDE | LEAK ON WELD; REPLACED A 20" SECTION OF 4" PIPE BETWEEN THE 10" MAIN & THE #2 BRIDLE VALVE AT V. 12.95
| 09-70087-1 |  |  | 2 | Distribution Main | TRANSMISSION | Valves |  |  | Other |  | 2009-03-26 | 2009-04-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MONTEREY | READING @ PIT NEAREST HWY 68; REMOVE @ PIT; REPAIRED THREE LEAKS, TWO ON THE INLET MUELLER VALVES, CAPS WERE LOOSE, DOPED BOTH. REPLACED 289 RELIEF VALVE, 1" NIPPLE WS CROSS-THREADED INSIDE AND LEAKING , REPLACED BOTH.
| 09-70087-1 | [10 empty] | 2009-03-26 | [5 empty] | MONTEREY | READING @ PIT NEAREST HWY 68; READING @ PIT
| 09-70088-1 |  |  | 2 | Transmission |  | Valves | Other | RELIEF | Other | LOOSE FITTING | 2009-03-26 | 2009-04-01 | Other | TIGHTEN RELIEF VALVE | Steel/Wrought Iron |  | MONTEREY | TRANSMISSION PIT VALVE BOX; HYW. 68 IN BOX 152; LOOSE FITTING; TIGHTEN UP RELIEF VALVE H-202 LEAK REPAIRED.
| 09-70088-1 | [10 empty] | 2009-03-26 | [5 empty] | MONTEREY | TRANSMISSION PIT VALVE BOX; HWY 68 IN BOX ADD 1528
| 09-70089-1 |  |  | 0.75 | Transmission |  | Regulator |  |  | Other |  | 2009-03-26 | 2009-04-01 | Other | REGULATOR | Steel/Wrought Iron |  | MONTEREY | HPR SET @ DRIVEWAY OF 1531 HWY 68; DRIVEWAY OF 1531 HWY 68; REGULATOR WS LEAKING ON FITTING (3/4") BYPASSED SERVICE AND REPAIRED FITTING ON TRANSMISSION SIDE (INLET).
| 09-70089-1 | [10 empty] | 2009-03-26 | [5 empty] | MONTEREY | HPR SET @ DRIVEWAY OF 1531 HWY 68; DRIVEWAYY OF 1531 HWY 68
| 09-70103-1 |  | 2.13 | 0.375 | Transmission |  | Other |  | STAINLESS FITTINGS | Construction Defect |  | 2009-03-30 | 2009-04-30 | Other | TIGHTEN FITTINGS | Other | STATIC LINES | CARMEL | ABOVE GROUND #3 VALVE (MARKED YELLOW) PITS MARKED IN YELLOW PAINT- 4 OF THEM X; 4 PITS & 3 VALVE; TIGHTENED VARIOUS FITTINGS & PLUGS. GREASED 2 VALVES, SOAP TEST FOR LEAKS
| 09-10209-1 | [10 empty] | 2009-05-27 | [5 empty] | SANTA CRUZ | 84' NORTH OF HOLDER BUNKER FRAME & COVER; NO GAS FOUND
| 09-10209-1 | [10 empty] | 2009-05-27 | [5 empty] | SANTA CRUZ | 84' NORTH OF HOLDER BUNKER FRAME AND COVER; NO LEAK FOUND (DELETED), NO LEAK FOUND
| 09-10209-1 | [10 empty] | 2009-05-27 | [5 empty] | SANTA CRUZ | 84' NORTH OF HOLDER BUNKER FRAME AND COVER; NO LEAK FOUND (DELETED)
| 09-10209-1 | [10 empty] | 2009-05-27 | [5 empty] | SANTA CRUZ | 84' NORTH OF HOLDER BUNKER FRAME AND COVER
| 09-10210-1 | 1818-01 | 5.6 | 12 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2009-05-27 | 2010-06-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SANTA CRUZ | WILDER RANCH OVER TP MAIN; SAME AREA OVER TP GAS MAIN, LATE RECHECK COULDN'T LOCATE EXACT LEAK
| 09-10210-1 | 1818-01 | [9 empty] | 2009-05-27 | [5 empty] | SANTA CRUZ | OVER TP MAIN; LATE RECHECK COULD NOT LOCATE EXACT LEAK LOCATION
| 09-10210-1 | 181801 | 5.6 | 12 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2009-05-27 | 2010-06-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SANTA CRUZ | WILDER RANCH OVER TP MAIN; JOB H REPAIR ON 41097513
| 09-10210-1 | 181801 | 5.6 | 12 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2009-05-27 | 2010-06-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SANTA CRUZ | WILDER RANCH OVER TP MAIN; JOB H REPAIR ON 41097513
| 09-10216-1 | [10 empty] | 2009-06-04 | [5 empty] | SANTA CRUZ | OCEAN AND E. CLIFF - SEWER MAN HOLE IN INTERSECTION; NO LEAK FOUND
| 10-88001-1 | 1 |  |  | Single Service |  | Fitting |  |  | Atmospheric Corrosion |  | 2010-10-18 | 2011-03-15 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | KING CITY | RISER OF FARMTAP 50' S/E OF MTR819615C.MP11.70; NONE
| 10-88003-1 | 1 |  | 0.5 | Transmission |  | Valves |  |  | Other | LOOSE FITTING | 2010-10-18 | 2011-03-22 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | HOLLISTER | LEAK 50' WEST OF 901 NEAR TRANS. LINE MARKER (TAP); SAME; CHANGE VALVE. SOAP TEST OK; REPLACE BYPASS VALVE SOAP TEST OK
8 | 10-88005-1 | 300A | 45359 | [8 empty] | 2010-10-19 | [5 empty] | HOLLISTER | BELOW GRND IN BOX S/OFF V/V; SOAP TEST OK. GAS TRACK, NO LEAK FOUND
| 10-81016-1 | 1111111 | [9 empty] | 2010-10-02 | [5 empty] | SANTA CRUZ | REG BOX BTWN D/WYS 10' RD/WY; NO LEAK FOUND
5 | 10-88026-1 | 187 | 65.69 | 6 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Other |  | 2010-11-09 | 2011-01-24 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SALINAS | BASE OF V-6 I/SI HARKIN REG STA; NONE; TIGHTENED FITTINGS; FOUND FEW FITTINGS ON VALVE #6 & ITS GAS SAVER CURCUIT LEAKING SO TIGHTENED THEM UP SOAP TEST OK
| 10-88045-1 | 300B | 46076 | 0.75 | Transmission |  | Regulator |  |  | Unknown |  | 2010-10-22 | 2011-01-10 | Other | REPLACE REGULATOR & RESEAL FITTINGS | Steel/Wrought Iron |  | HOLLISTER | 6100 PACHECO PASS; LEAK AT TAP T-460.77; REPLACED 1ST. STAGE REG & RESEALED FITTINGS; REPAIRED GAS LEAKS, REPLACED 1ST STAGE REG. & RESEALED FITTINGS, SOAP TEST OK
76 | 10-81031-1 | 1816-01 | 8.44 | 8 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other |  | 2010-10-13 | 2011-02-08 | Greased - Other |  | Steel-Other |  | WATSONVILLE | REGPIT I/S FENC IFO GATE, MIDDLEPIT 2ARDS BK; SHADOWMERE WAY; GREASED V.5 STA. V. SOAP TEST OK
| 10-88376-1 | 301-A |  |  |  |  | Valves |  |  | Other | DRY GREASE | 2010-10-20 | 2011-02-07 | Other | GREASED VALVE | Steel/Wrought Iron |  | HOLLISTER | FALLCON RD & SCAGLIOTTI 450 YDS SW FROM SW CORNER; @ REG STATION; DRY GREASE; GREASED 2ND & 3RD STAGE BYPASS VALVES; HRH40 REG STATION
| 10-88377-1 |  |  | 0.75 | Service |  | Mechanical Joint |  |  | Atmospheric Corrosion |  | 2010-10-20 | 2011-03-17 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | HOLLISTER | ABOVE GROUND, REG STATION BEHIND HOUSE, FIRST STAGE HP REG 650/350 SET 627; ABOVE GROUND REG STATION BEHIND HOUSE; REPLACE 1DT CUT HP REG; REPAIR LEAKS, REPLACE HP REG
| 10-88378-1 | 300A | 454.76 | 0.75 | Transmission |  | Valves |  |  | Internal Corrosion |  | 2010-10-20 | 2011-03-14 | Other | REPLACE "O" RINGS | Steel/Wrought Iron |  | HOLLISTER | BELOW GOURND IN VENT, NEXT TO MARKER & REG STATION; BELOW GROUND IN VENT NEXT TO MARKER & RE; REPLACE WORN O RINGS IN VALVE T CAP
| 10-88379-1 | 300A | 452.71 | 0.75 |  |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2010-10-20 | 2011-03-11 | Replace Partial Service |  | Steel/Wrought Iron |  | HOLLISTER | LEAK ON TAP 30 YARDS WEST OF HOUSE; LEAK ON TA 30 YARDS WEST OF THE HOUSE; REPLACED 18" IF 3/4" PIPE; REPLACED 18" OF 3/4" PIPE AT RISER
5 | 10-88485-1 | DREG5408 | 0.02 | [8 empty] | 2010-10-26 | [5 empty] | SALINAS | DOLAN RD./RUSSO RD. @ EXHAUST STACKS, - DOLAN STATION; THIS IS A GAS VENT;
5 | 10-88486-1 | STA PIPE | [9 empty] | 2010-11-09 | [5 empty] | MOSS LANDING | BOC 3016 N. BLOW OFF VALVE S END OF MAIN METERING; THIS IS A GAS VENT
5 | 10-88528-1 | DREG5408 | 0.02 | [8 empty] | 2010-10-26 | [5 empty] | SALINAS | DOLAN RD. REG STATION AT BLOW STACKS, - THIS COULD BE THE POSITIONER RELIEFS; THIS IS A GAS VENT
76 | 10-81951-1 | 1870-01 | 2.26 | [8 empty] | 2010-10-15 | [5 empty] | SANTA CRUZ | NEXT TO VALVE V-B77, ACROSS FROM QUAIL HILL LANE; SOAP TEST OK, NO LEAK ON VALVE
| 10-81952-1 | DF3433 | 0.01 | 0.75 | Transmission |  | Valves |  |  | Other | O RINGS | 2010-10-11 | 2011-01-07 | Other | REPLACED "O" RING | Steel/Wrought Iron |  | AROMAS | COLE REGSTA; V/V BX FURTHEST N@REGSTA; REPLACED TWO "O" RINGS ON PIN OFF CAP; SOAP TEST OK
| 10-81952-1 | DF3433 | 0.01 | 0.75 | Transmission |  | Valves |  |  | Other | O RINGS | 2010-10-11 | 2011-01-07 | Other | REPLACED "O" RING | Steel/Wrought Iron |  | AROMAS | COLE REGSTA; V/V BX FURTHEST N@REGSTA; REPLACED TWO "O" RINGS ON PIN OFF CAP; SOAP TEST OK
| 10-81953-1 | DF3426 | 8.46 | 1 | Transmission |  | Tap Connection | Valves |  | Other | O RING | 2010-10-20 | 2011-01-13 | Other | O RING | Steel/Wrought Iron |  | WATSONVILLE | REG STATION ROUND VALVE @ 2 CLOCK FROM GATE OPENIN; WHITE PAINT; REPLACED CAP "O" RINGS"; SOAP TEST OK
| 10-81954-1 | X6472 | 8.45 | 1 | Transmission |  | Tap Connection | Valves |  | Other | O RING | 2010-10-20 | 2011-01-13 | Other | O RING | Steel/Wrought Iron |  | WATSONVILLE | REG STATION THIRD ROUND VALVE FROM GATE OPENING 15A; REPLACED CAP "O" RINGS; SOAP TEST OK
| 10-81955-1 | 1816-01 | 3.44 | 0.5 | Transmission |  | Fitting |  |  | Other | NO DOPE | 2010-10-14 | 2011-01-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | WATSONVILLE | XTIE REGSTA; 1817-01/X1851; RE-DOPED & TIGHTENED NIPPLE; SOAP TEST OK
| 10-50200-1 | 103 | 0.66 | 0.75 | Transmission |  | Other |  | RELIEF | Unknown |  | 2010-10-08 | 2011-01-03 | Other | RELIEF | Steel/Wrought Iron |  | SALINAS | RELIEF VALVE LEAKING; SOCIAL SECURITY BLDG; REPLACE RELIEF; REPLACED H202 RELIEF. CHECK LOCK UP, SET PRESS E 4O#, SOAP TEST OK.
| 10-50203-1 | 103 |  | 0.75 | Single Service |  | Valves |  |  | Unknown |  | 2010-10-19 | 2011-01-05 | Other | LUBE VALVES RESEAL FITTINGS | Steel/Wrought Iron |  | SALINAS | INLET VALVE NEEDS GREASE; HPR SET; INLET VALVE & BYPASS & FITTINGS; INSTALLED LUBE FITTINGS IN INLET & BYPASS VALVES LUBED VALVES & RESEALED FITTINGS, REPLACED D.S. VALVE & H-202, SOAP TEST OK, PAINTED SET
| 10-50204-1 | 301E | 0.89 | 12 | Transmission |  | Valves |  |  | Other | DRY STEAM PACKING | 2010-10-13 | 2010-10-21 | Other | ADDED 909 STEAM PACKING, LUBED & OPERATE VALVE | Steel/Wrought Iron |  | SALINAS | VALVE #1 OUT OF STEAM D.S. VALVE @ SRS-18; ADDED 909 STEAM PACKING - GOOD NOW; FOUND VALVE #1 LEAKING OUT STEAM - WITH CAMBELL VALVE COMPANY WE PACKED STEAM WITH 909 STEAM MATERIAL PACK LUBED & OPERATED VALVE FEW TIMES & ADJUSTED BONNET WORKS GOOD MOW & NO LEAKS
5 | 09-50212-1 | [10 empty] | 2009-08-01 | [5 empty] | SALINAS | S/COCK TRANS, FISHER NIPPLE ON HIGH SIDE OF A; SAME AREA, SAME AREA, NO LEAK FOUND
| 09-50212-1 | [10 empty] | 2009-08-01 | [5 empty] | SALINAS | S/COCK TRANS, FISHER, NIPPLE ON HIGH SIDE OF RE,; YELLOW PAINT SEE ABOVE;
5 | 10-50302-1 | 187 |  | 4 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-09 | 2010-10-09 | Other |  |  |  | GONZALES | VALVE BOX, 4' FROM FENCE, N/W COR OF INTERSECTION; VALVE BOX, 4' FROM FENCE, N/W COR OF INT; GREASED VALVE
| 10-50305-1 | 301 |  | 0.75 | Single Service |  | Mechanical Joint |  |  | Atmospheric Corrosion |  | 2010-11-15 | 2011-02-09 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | SALINAS | HV BOX H2H SET; BOX PAINTED; REPAIR GAS LEAK @ REG UPSTREAM & DOWNSTREAM UNIONS. CHECK FOR LOCK-UP GOOD. REPLACE RELIEF H202 LE PLACE RELIEF METRIC VALVE. AF/L PRESS SET AT 25 PSIG. SET RELIEF AT 40 PSIG.
5 | 10-50338-1 |  |  | 12 | [7 empty] | 2010-12-23 | [5 empty] | SALINAS | N SIDE OF 808 DOLAN RD MOSS LANDING; NO LEAK FOUND. SOAP TEST OK
| 10-80307-1 | 300B |  | 0.75 | Transmission |  | Other |  | UNION & FITTINGS | Unknown |  | 2010-10-07 | 2010-10-08 | Other | REPLACED & REDOPPED. FITTINGS | Steel/Wrought Iron |  | HOLLISTER | LEAK ON HIGHT TO HIGH UNION & ELBOW; LEAK @ HIGHT TO HIGH UNION & ELBOW TIGHTEN UNION UP SOME TO SLOW DOWN LEAK; UNION & VARIOUS OTHER FITTINGS ON 1ST; WENT & CHECKED OUT LEAK ON 10-7-10 & TIGHTENED UNION SLOWED LEAK DOWN THEN CAME OUT & MADE REPAIRS ON 10-8-10 & HOT TANKED CUSTOMERS - 3MM @ 1 PSIG.
| 10-80307-1 | 300B |  | 0.75 | Transmission |  | Other |  | UNION & FITTINGS | Unknown |  | 2010-10-07 | 2010-10-08 | Other | REPLACED & REDOPPED FITTINGS | Steel/Wrought Iron |  | HOLLISTER | LEAK ON HIGH TO HIGH UNION & ELBOW; LEAK @HIGH TO HIGH UNION & ELBOW; UNION & VARIOUS OTHER FITTINGS ON 1ST STAGE; WENT & CHECKED OUT LEAK ON 10-7-10 & TIGHTENED UNION SLOWED LEAK DOWN THEN CAME OUT & MADE REPAIRS ON & HOT TANKED CASTOMERS. 3MM @ 1PSIG.
| 10-80324-1 | 300B | 435-80 | 0.75 | Transmission |  | Mechanical Joint |  |  | Other | LOOSE FITTINGS / DRIED PIPE DOPE | 2010-10-12 | 2011-06-06 | Other | RE-SEAL & TIGHTEN | Steel/Wrought Iron |  | PAICINES | 2355 COTTONWOOD RD.; LEAK AT HIGH TO HIGH SET T-435.80; RE SEALED & TIGHTENED VARIOUS FITTINGS, SOAP TEST OK; RE-SEALED & TIGHTENED VARIOUS LOOSE FITTINGS, SOAP TEST OK
| 10-80333-1 | 300B | 439.47 | 0.75 | Transmission |  | Valves |  |  | Unknown |  | 2010-10-21 | 2011-01-10 | Other | RESEALED FITTINGS & GREASED VALVES | Steel/Wrought Iron |  | HOLLISTER | LEAK AT METER #997315-E, NOTIF 104909189; REPAIRED LEAKS; RESEALED ALL FITTINGS, REPLACED 1ST STAGE REG., SOAP TEST OK
| 10-80334-1 | 103 |  | 0.75 | Single Service |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2010-10-18 | 2010-10-21 | Replace TP Main |  | Steel/Wrought Iron |  | SAN JUAN BAUTISTA | HPR SET, INLET & BYPASS CORRODED; HPR SET; REPLACED 16" OR 3/4" PIPE ON THE INLET SIDE OF H2H.
8 | 10-80338-1 | 103 | 966 | 0.25 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-10-25 | 2010-10-25 | Tighten Cap/Bolt - Fitting |  |  |  | SAN JUAN BAUTISTA | I/F/O ADDRESS @ REG ST HRH08; SENSING LINES
8 | 10-80343-1 | 103 | [9 empty] | 2010-11-24 | [5 empty] | SAN JUAN BAUTISTA | LEAK ON HIGH SIDE & LOW SIDE; NO LEAK FOUND
8 | 10-80346-A | 300B | 455.11B | 0.75 | Transmission >= 20% SMYS |  | Regulator |  |  | Other | LOOSE BOLTS | 2010-12-24 | 2010-12-24 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | HOLLISTER | LEAK ON FIRST STAGE REG @ HRH-42; TIGHTENED BOLTS AROUND REG DIAFRAM HOUSING, SOAP TEST OK; TIGHTENED BOLTS AROUND REG. DIAFRAM HOUSING, SOAP TEST OK
| 09-91652-1 | 103 | 9.37 | 0.75 | Transmission |  | Valves |  |  | Construction Defect |  | 2009-11-07 | 2009-11-07 | Other | REPLACED GREASE FITTING | Steel/Wrought Iron |  | SAN JUAN BATISTA | REPLACED BAD GREASE FITTING, SOAP TEST OK
18 | 92-00171-1 |  |  | 1.25 | Service |  | Fitting |  |  | Other |  | 1992-10-19 | 1992-10-20 | Replace Pipe |  | TR 418 |  | SALINAS | REMOVED S/ TEE + 4' OF PIPE. INST. 54" OF 1 1/4" +S/TEE + TESTED 33" OF G/M + G/S TO 6/6 ANDINA FOR 1/2 HR, GM + GS OK. INST. (2) SOCKET COUPLINGS + SOAP TESTED WITH GAS. LEAK SURVEY 76' 40 S/S + 33' S/O G/S - OK.
11 | 92-00171-1 |  |  | 0.5 | Service |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1992-10-19 | 1992-10-20 | Replace Pipe |  | TR 418 |  | SALINAS | @ PROP LINE 616 ADINA BY SEC. SPLICE BOX ON PL. SVC TEE; CROSS CAP THREADED; SEE ... FORM A #9800171
| 94-00124-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Digin |  | 1994-10-14 | 1994-10-14 | Replace Pipe |  | Steel/Wrought Iron |  | CASTROVILLE | REPLACED 32' PF 12" STEEL PIPELINE
4 | 94-00702-1 | 187 | 44.82 | 8 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1994-10-24 | 1994-10-25 | Replace Pipe |  | Steel/Wrought Iron |  | SOLEDAD | REPLACE 30' SECTION OF 8" PIPE (M.P. 44.82)
8 | 73-00602-1 |  |  | 30 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-03-21 | 1973-03-21 | Patch Welded |  | Steel/Wrought Iron |  |  | 30" LINE 301; ORIGINAL IN LINE FOLDERS
8 | 76-00619-1 |  |  | 12 | Transmission |  | Longitudinal Weld |  |  | Other | MANUFACTURE DEFECT | 1976-06-30 | 1976-07-12 | Patch Welded |  | Steel/Wrought Iron |  | HOLLISTER | TL 103; MP 2.49; ORIGINAL IN LINE FOLDER
8 | 76-00621-1 |  |  | 3 | Distribution Main |  | Fitting |  |  | Material Failure |  | 1976-06-30 | 1977-03-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | HOLLISTER | COUPLING LEAKING. INSTALLED 3' TOP TAP. PLUGED ... IN, CUT OUT THE COUPLING AND WELDED A NEW SECTION INTO THE MAIN.; PARTIAL.
8 | 78-00615-1 |  |  | 20 | Transmission | [6 empty] | 1978-09-25 |  |  |  | Steel/Wrought Iron |  | HOLLISTER | M.P. 2.10
8 | 78-00616-1 |  |  | 30 | Transmission | [6 empty] | 1978-09-25 |  |  |  | Steel/Wrought Iron |  | HOLLISTER | PICKED UP READING ON SAMPLE IN VENT; M.P. 2.10
5 | 72-10302-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-10-30 | 1972-10-30 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | ORIGINAL IN LINE FOLDERS
4 | 75-00725-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1975-07-30 | 1975-07-30 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | ORIGINAL IN LINE FOLDERS
4 | 81-00706-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1981-03-19 | 1981-03-19 | Patch Welded |  | Steel/Wrought Iron |  |  | ORIGINAL IN LINE FOLDER
76 | 96-00026-1 |  |  | 12.75 | Distribution Feeder Main |  | Body of Pipe |  |  | Material Failure |  | 1996-06-24 | 1996-06-28 | Replace Pipe |  | Steel/Wrought Iron |  | SANTA CRUZ | DISCOVERED SEVERAL PINHOLE LEAKS. DOWNGRADED TO GR 2. X-RAYED PIPE WALL TO DETERMINE EXTENT OF REPAIR REQ'D.
76 | 96-20004-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1996-02-19 | 1996-03-01 | Replace Pipe |  | Steel/Wrought Iron |  | WATSONVILLE | REPLACED SERV, INSERT 1/2" PI IN STL SERV
76 | 97-20034-1 |  |  | 4 | Transmission |  | Fitting |  |  | Other |  | 1997-12-23 | 1997-12-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN BENITO CO. | FLANGED VALVE WAS EXCAVATED 12/30/7. BOLTS ON FLANGES WERE TIGHTENED, ELIMINATING THE LEAK.
| 98-00068- |  |  | 0.5 | Service |  | Body of Pipe | Fitting |  | Construction Defect |  | 1998-10-14 | 1998-10-15 | Mechanical Repair Fitting - Fitting |  | TR 418 |  | SALINAS | REPLACED TEE
| 98-00037-1 |  |  | 8 | Transmission |  | Valves |  |  | Other |  | 1998-05-11 | 1998-06-25 | Other |  | Other |  | CAPITOLA | BAR HOLES OVER MAIN VALVE B-41-1LEAKED AND FILLED APROX AREA W GAS VENT OUT --
76 | 98-00054-1 |  |  | 8 | Distribution Feeder Main |  | Tap Connection |  |  | Material Failure |  | 1998-05-11 | 1998-05-11 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SCRUZ | TEFLON TAPE & TIGHTEN CAP
76 | 98-00102-1 |  |  | 0.5 | Transmission |  | Fitting |  |  | Construction Defect |  | 1998-07-20 | 2000-01-14 | Replace Pipe |  | TR 418 |  | SANTA CRUZ | SERVICE LEAKING @ PI-STL ADAPTER - INSTALLED NEW ADAPTER TO FIX LEAK.
| 99-00013 | 187 | 45.39 | 0.75 | Transmission |  | Body of Pipe |  |  | Digin |  | 1999-02-24 | 1999-02-24 | Replace Pipe |  | Steel/Wrought Iron |  | SOLEDAD | REPLACED 5' OF 3/4" PIPE
| 99-00210-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Digin |  | 1999-07-30 | 1999-07-30 | Mechanical Repair Fitting - Fitting |  | TR 418 |  | MARINA | INST 2- 1"X1" M... FIT COUPLING
| 99-00022-1 |  |  | 0.75 | Service |  | Body of Pipe | Riser |  | Atmospheric Corrosion |  | 1999-06-23 | 1999-06-23 | Other | RETREAD PIPE | Steel/Wrought Iron |  | SALINAS | RETREAD RISER
| 99-00037-1 |  |  |  | Transmission |  | Fitting | Valves |  | Material Failure |  | 1999-05-05 | 2000-11-08 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | SALINAS | REPLACED 1" NIPPLE AND GREASE VALVE
| 99-00041-1 | [16 empty] | SALINAS | NEXT TO WATER BOX; READS TOO LOW DELETE
| 99-00048 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin | Plastic Crack Failure | 1999-09-19 | 1999-09-19 | Mechanical Repair Fitting - Fitting |  | TR 418 |  | SALINAS | REPLACE 24" OF 1/2" PLASTIC PIPE AND 2-1/2 X 1/2 PERFECTION COUPLING
| 99-00051-1 |  |  | 0.5 | Service |  | Fitting | Riser | VALVES | Construction Defect |  |  | 2000-01-31 | Other | SEE REMARKS. | Other | PRE-FAB RISER | SALINAS | RE-DOPED.; LEAKING BELOW STOP COCK TURN IN TO SERVICED DEPT.
| 99-00052-1 |  |  | 0.5 | Service |  | Fitting | Riser | VALVES |  |  |  | 2000-01-31 | Other | SEE REMARKS. |  |  | SALINAS | REDOPED.; 301 STOPCOCK (BELOW)
| 99-00053-1 |  |  | 0.75 | Service |  | Body of Pipe | Fitting | GIRTH WELD | Construction Defect |  |  | 2001-01-10 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | N. SALINAS | RE WELDON 3/4" SERVICE TEE
| 99-00062-1 |  |  | 0.5 | Service |  | Body of Pipe | Fitting |  | Construction Defect |  |  | 2000-12-20 | Mechanical Repair Fitting - Fitting |  | TR 418 |  | SALINAS | INSTALL 1/2" X 1/2" PLASTIC TEE
| 99-00061-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | External Corrosion |  | 1999-07-16 | 2000-12-20 | Mechanical Repair Fitting - Fitting | SKINNER CLAMP | Steel/Wrought Iron |  | SALINAS | INSTALL SKINNER CLAMP.
| 99-00046-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Damage by Natural Forces |  | 1999-07-06 | 1999-07-06 | Other |  | TR 418 |  | SANTA CRUZ | REPLACE 4' OF 1 1/4 PLASTIC
| 99-00047-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Damage by 3rd Party | DIGIN | 1999-07-07 | 1999-07-07 | Patch Welded |  | Steel/Wrought Iron |  | SANTA CRUZ | WELD SERVICE TEES
| 00-80022-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | DRY O-RINGS | 2000-10-16 | 2010-06-15 | Other | LUBED O-RINGS | Steel/Wrought Iron |  | HOLLISTER | RESEALED O-RINGS; RELUBED O-RINGS ON MULLEN INLET VALVE
| 00-80022 | [10 empty] | 2000-10-16 | [5 empty] | PANOCHE | ZONE VALVE IN GROUND; CAN BE GREASED WITH INSPECTION
| 00-80023 | 300A |  | 0.75 | Transmission |  | Valves |  |  | Other | VALVE NEEDED GREASE | 2000-10-17 | 2005-04-26 | Other | GREASED VALVE | Steel/Wrought Iron |  | PANOCHE | GREASED GAS VALVE
| 00-80024 |  |  | 0.75 | Service |  | Valves |  |  | Construction Defect |  | 2000-10-17 | 2002-01-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | PANOCHE | TIGHTEN CAP ON VALVE
| 00-40006 | 187 | 3.74 | 6 | Transmission |  | Body of Pipe |  |  | Digin |  | 2000-09-24 | 2000-09-25 | Replace Pipe |  | Steel/Wrought Iron |  | SAN ARDO | 10FT SECTION OF 6" (6.625"OD) INSTALLED ON ORDER #8038976 (SEE ORDER FOR STRENGTH TEST); NEW PIPE: 6.625" OD 0.188" WT X42 ERW
| 00-10085 | DFM03 | 13.61 | 12 | Transmission |  | Body of Pipe |  |  | Unknown |  | 2000-11-17 | 2000-12-14 | ABANDON |  | Steel/Wrought Iron |  | DAVENPORT | REROUTE & REPLACE 12" W/ 3" STEEL
| 01-80003-1 |  |  | 2 | Gathering | Service | Body of Pipe | Unknown |  | Digin |  | 2001-03-01 | 2001-03-22 | Mechanical Repair Fitting - Fitting |  |  |  | HOLLISTER | REPLACE 18" ... GAS PIPE
| 01-70135-1 | MTY DFM 2 | 12.95 | 4 | Transmission |  | Valves |  |  | Construction Defect |  | 2001-12-21 | 2001-12-21 | Other | FLUSH & GREASE INLET VALVE | TR 418 |  | SEASIDE | ON INLET TIP PRESSURE VALVE TO REG STATION; GREASED & FLUSHED VALVE READING MINIMAL 1% LEAK
| 01-50005-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Construction Defect |  | 2001-03-09 | 2001-03-19 | Patch Weld - Weld |  | Steel/Wrought Iron |  | SALINAS | PIPE WAS UNDER STRESS CAUSING LEAK. CLOSED VALVE, CUT PIPE, RELIEVED STRESS + REWELDED.
| 01-50006-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by 3rd Party | DIGIN | 2001-02-09 | 2001-02-09 | Mechanical Repair Fitting - Fitting |  | TR 418 |  | CASTROVILLE | REPLACED SECTION OF PIPE
| 01-50090- |  |  | 12 | Transmission |  | Valves |  |  | Other | LACK OF PACKING MATERIAL IN VALVE | 2001-07-10 | 2001-07-24 | Other | ADDED PACKING MATERIAL - REBUILT PACKING EXTENSION | Steel/Wrought Iron |  | MOSS LANDING | LEAK ON 12" VALVE - 22 WAS STOPPED BY ADDING PACKING MATERIAL; REPAIRED GREASE STEM - GREASED VALVE; SOAP TEST VALVE OK.
| 01-50109-1 | 187 | 61.35 | 8 | Transmission |  | Body of Pipe |  |  | Digin |  | 2001-08-30 | 2001-08-31 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | INSTALLED 3 FT OF 8" GR B SEAMLESS .322" WT; PRE-TESTED PIPE, MAPPING RETAINS RECORDS
| 01-50110-1 | 187 | 61.25 | 8 | Transmission |  | Body of Pipe |  |  | Digin |  | 2001-08-31 | 2001-08-31 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | WHILE REPAIRING DIGIN @ MP 61.35, GC GAS DAMAGED PIPE @ MP 61.25; PRE-TESTED PIPE, SEE ATTACHED
| 10-80160-1 | 103 |  | 0.75 | Single Service |  | Mechanical Joint |  |  | Other | DRIED PIPE DOPE | 2010-09-10 | 2011-07-07 | Other | RE-SEAL & TIGHTEN | Steel/Wrought Iron |  | SAN JUAN BAUTISTA | LEAK 3/4 UNION & ABOVE & BELOW S/COCK YELLOW PAINT; UNION & S/COCK, (SHUT OFF VALVE) ROTARY MTR FR ANY CEL MEASURED LEAKS TOO BEHIND RED BARN; LEAKS ON RE & THREADS; REPAIRED LEAKS @ THREAD JOINTS BEFORE & AFTER REG ON HI TO HI SET, SOAP TEST OK
| 10-80162-1 | 301D |  | 0.75 | Transmission |  | Mechanical Joint |  |  | Other | DRIED PIPE DOPE | 2010-09-10 | 2011-07-07 | Other | RE-SEAL & TIGHTEN | Steel/Wrought Iron |  | SAN JUAN BAUTISTA | H2H SET REG BOTH SIDE; YELLOW PAINT, H2H SET; REPAIRED LEAKS ON HI TO HI BEFORE & AFTER REG @ THREADS SOAP TEST OK
| 10-80185-1 | 300B | 435.8 | 0.75 | Transmission |  | Fitting |  |  | Other |  | 2004-09-13 | 2010-12-10 | Other | REBUILT SET | Steel/Wrought Iron |  | PAICINES | LEAK HIGH SIDE VALVE; YELLOW PAINT; REBUILT SET; REBUILT THE HPR SET. SOAP TESTED O.K.
| 10-80186-1 | 300B | 418.36 | 0.75 | Transmission |  | Fitting |  |  | Other |  | 2010-09-13 | 2010-12-07 | Soap and/or Tape - Other |  | Steel/Wrought Iron |  | PAICINES | FIRST STAGE 3/4 CAP LEAKING 1%; YELLOW PAINT; REPAIRED THE LEAKING PIN OFF TEE
| 10-80187-1 | 300B |  | 0.75 | Transmission |  | Fitting |  |  | Other | DRY SEALANT | 2010-09-13 | 2010-12-07 | Soap and/or Tape - Other |  | Steel/Wrought Iron |  | PAICINES | 2 STAGE ON TAP; YELLOW TAP; REMOVED THE PIN-OFF CAP; APPLIED THREAD SEALANT; RE INSTALLED THE PIN-OFF CAP; SOAP TESTED O.K.
| 10-50001-1 | 301-F |  | 0.75 | Transmission |  | Mechanical Joint |  |  | Other | LOOSE FITTING | 2010-01-04 | 2011-07-01 | Other | TIGHTENED LOOSE FITTING/UNION | Steel/Wrought Iron |  | SALINAS | ESPINOSA RD (REG SET) VALVE; LEAK AT HIGH TO HIGH SET (YELLOW PAINT), VALVE; TIGHTENED LOOSE FITTINGS, SOAP TEST OK; TIGHTENED LOSE FITTINGS SOAP TEST OK;
| 10-50001-1 | 301-F |  | 0.75 | Transmission |  | Mechanical Joint |  |  | Other | LOOSE FITTING | 2010-01-04 | 2011-07-07 | Other | TIGHTENED LOOSE FITTING/UNION | Steel/Wrought Iron |  | SALINAS | ESPINOSA RD (REG SET) VALVE; VALVE; TIGHTENED LOOSE FITTINGS, SOAP TEST OK; TIGHTENED LOOSE FITTINGS, SOAP TEST OK.
| 10-50002-1 | 301-F | 3.81 | 0.75 | Single Service |  | Valves |  |  | Unknown |  | 2010-01-04 | 2010-08-29 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | SALINAS | 92 ESPINOSA RD. LEAK AT HIGH TO HIGH SET (YELLOW PAINT, LEAK AT HIGH TO HIGH SET - YELLOW PAINT; REPLACED INLET VALVE; REPLACED LEAKING INLET VALVE DURING SHUT DOWN @ DIG-IN 6.301B
| 10-50006-1 | 301-F |  | 2 | Single Service |  | Valves | Other | VARIOUS FITTINGS | Other | DRY SEALS | 2010-01-05 | 2010-04-01 | Other | GREASE VALVES & REDOPED FITTINGS | Steel/Wrought Iron |  | SALINAS | 384 ESPINOSA RD; LEAK AT HIGH TO HIGH SET; INLET BYPASS VALVE & VARIOUS FITTINGS; REPAIRED GAS LEAK @ REG. STATION 4-1-10
| 10-50002-1 | 301-F | [9 empty] | 2010-01-04 | [5 empty] | SALINAS | 92 ESPINOSA RD. HIGH SIDE UNION; LEAK AT HIGH TO HIGH SET (YELLOW PAINT;
| 10-50003-1 | 301-F |  | 0.75 | Single Service |  | Fitting |  |  | Atmospheric Corrosion |  | 2010-01-04 | 2011-01-01 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | SALINAS | 147 ESPINOSA RD.;____;______
| 10-50003-1 | 301-F |  | 0.75 | Single Service |  | Fitting |  |  | Atmospheric Corrosion |  | 2010-01-04 | 2011-07-01 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | SALINAS | 147 ESPINOSA RD., LEAK BELOW BY PASS COCK ON RISER; LEAK ON HIGH TO HIGH SET (YELLOW PAINT; TIGHTEN FITTING BELOW LOW SIDE BY PASS VALVE; TIGHTEN FITTING BELOW DOWNSTREAM BYPASS. SOAP TEST GOOD.
| 10-50003-1 | 301F |  | 0.75 | Single Service |  | Fitting |  |  | Atmospheric Corrosion |  | 2010-01-04 | 2011-07-01 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | SALINAS | TIGHTEN FITTING BELOW LOW SIDE BYPASS VALVE; TIGHTEN FITTING BELOW DOWNSTREAM BYPASS. SOAP TEST GOOD.
| 10-50004-1 | 301-F |  | 3 | Transmission |  | Valves | Other | UNION | Other | LOOSE FITTING | 2010-01-04 | 2011-04-27 | Other | GREASE & OPERATE | Steel/Wrought Iron |  | SALINAS | GREASED + OPERATED VALVE, TIGHTENED UNION, SOAP TEST OK; TIGHTENED LOOSE UNION AND GREASED + OPERATED VALVE, SOAP TEST OK.
| 09-50492-1 | D7M |  | 1.5 | Transmission |  | Bell Joint |  |  | Other | DRIED PIPE DOPE | 2009-11-02 |  |  |  | Steel/Wrought Iron |  | SALINAS
| 10-50004-1 | 301-F |  | 3 | Transmission |  | Valves | Other | UNION | Other | LOOSE FITTING | 2010-01-04 |  | Other | GREASE & OPERATE. | Steel/Wrought Iron |  | SALINAS | GREASED + OPERATED VALVE, TIGHTENED UNION, SOAP TEST OK; TIGHTENED LOOSE UNION AND GREASED + OPERATED VALVE, SOAP TEST OK
| 10-50005-1 | 301-F |  |  | Single Service |  | Fitting |  |  | Atmospheric Corrosion |  | 2010-01-05 | 2011-03-18 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | SALINAS | TIGHTEN FITTINGS; REDOPE & TIGHTEN FITTING ON PILOT SUPPLY LINE
5 | 10-50005-1 | 301-F | [9 empty] | 2010-01-05 | [5 empty] | SALINAS
| 10-50006-1 | 301-F |  | 2 | Single Service |  | Valves | Other | VARIOUS FITTINGS | Other | DRY SEALS | 2010-01-05 | 2010-04-01 | Other | GREASE VALVES & REDOPED FITTINGS | Steel/Wrought Iron |  | SALINAS | REPAIRED GAS LEAK @ REG. STATION 4-1-10 LAJ/MAH
| 10-50055-1 | [10 empty] | 2010-03-05 | [5 empty] | SALINAS
| 10-50070-1 | 1881-01 | 2.74 | 2 | Transmission |  | Valves |  |  | Other | NO GREASE | 2010-03-18 | 2010-03-18 | Other | GREASED VALVE | Steel/Wrought Iron |  | SALINAS | VALVE LEAKING FROM GREASE STEM, GREASED VALVE SOAP TEST OK
| 10-50165-1 | 301-B | 7.5 | 12 | Transmission |  | Body of Pipe |  |  |  |  | 2010-08-28 | 2010-08-30 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SALINAS | REPAIR SLEEVE WELDED OVER HOLE; REPAIR SLEEVE WELDED OVER DAMAGE. WELD WAS X-RAYED + MAGNETIC PARTICLE TESTED. SOAP TEST, OK.
| 10-50166-1 | 187 |  | 0.75 | Transmission |  |  |  |  | Other | PIPE DOPE | 2010-09-02 | 2010-09-02 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SALINAS | REMOVE CAP / CLEAN THREADS / DOPE & INSTALL CAP; REMOVED CAP ON PIN-OFF TEE. CLEANED THREADS AND DOPED AND RE-INSTALLED CAP.
| 10-50167-1 | 301B | 4.71 | 0.75 | Single Service |  | Valves |  |  | Other | LOOSE FTG. | 2010-09-09 | 2010-09-13 | Other | REPLACED GREASE FITTING | Steel/Wrought Iron |  | SAL | REPLACE GREASE STEM; REPLACE GREASE FITTING + TIGHTEN LOOSE FITTINGS. SOAP TEST OK.
| 10-50167-1 | 301-B |  | 0.75 | Single Service |  | Valves |  |  | Other |  | 2010-09-09 | 2010-09-13 | Other |  | Steel/Wrought Iron |  | SALINAS | REPLACED VALVE
| 10-50167-1 | 301-B |  | 0.75 | Single Service |  | Valves |  |  | Other |  | 2010-09-09 |  |  |  | Steel/Wrought Iron |  | SALINAS
| 10-50167-1 | 301-B | 4.71 | 0.75 | Single Service |  | Valves |  |  | Other | LOOSE FTG. | 2010-09-09 | 2010-09-13 | Other | REPLACED GREASE FITTING | Steel/Wrought Iron |  | SAL | REPLACE GREASE STEM; REPLACED GREASE FITTING + TIGHTEN OTHER LOOSE FITTINGS. SOAP TEST OK.
| 10-50173-1 | 301-B | 55 | 0.75 | Transmission |  | Fitting |  |  | Other |  | 2010-09-30 | 2010-12-09 | Soap and/or Tape - Other |  | Steel/Wrought Iron |  | SALINAS | REPAIRED THE LEAKS, SOAP TESTED OK
| 10-50175 |  |  | 0.75 | Transmission |  | Other |  |  | Other |  | 2010-09-30 | 2010-12-24 | Other | JS | Steel/Wrought Iron |  | SALINAS | THIS LOOKS LIKE A NEW HPR SET; SOAP TESTED OK.
| 10-50175-1 |  |  | 0.75 | Single Service |  | Riser |  |  | Construction Defect |  | 2010-09-30 | 2010-12-23 | Other | REAPPLY PIPE SEALANT | Steel/Wrought Iron |  | SALINAS | CLEAN RISER THREADS REAPPLY DOPE; EXCAVATE AND SHUT DOWN PIN OFF TEE ON TRANSMISSION MAIN. REMOVE VALVE, CLEAN RISER THREADS, REAPPLY PIPE SEALANT, SOAP TEST OK. TRAVIS MASSEY OPERATED PINOFF TEES.
| 10-50189-1 | 187 |  | 0.75 | Transmission |  | Fitting | Mechanical Joint | REGULATOR OTHER | Other |  | 2010-10-01 | 2010-12-23 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | SALINAS | REBUILT HPR SET. SOAP TESTED OK
| 10-50194-1 | 301-B | 6 | 12 | Transmission |  | Body of Pipe |  |  |  |  | 2010-10-02 | 2010-10-03 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | CLOSE 2 VALVES, BLOW DOWN PIPE. REPLACE 3' SECTION OF PIPE.; JASON BRUNI TESTED PIPE 10/2/05.;
5 | 10-50197-1 | MTY#1 | 8.19 | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Unknown |  | 2010-10-07 | 2010-12-27 | Other |  | Steel/Wrought Iron |  | SALINAS | INSTALLED NEW FITTING
| 10-50197-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Unknown |  | 2010-10-07 | 2010-12-27 | Other | LUBE & OPERATE | Steel/Wrought Iron |  | SALINAS | INSTALLED LUBE FITTINGS & LUBED VALVES; INSTALLED LUBE FITTINGS ON INLET BYPASS VALVES LUBED & OPERATED VALVES, REPAIRED LEAKS, SOAP TEST OK.
| 10-40002-1 | 187 | 35.78 | 0.75 | Transmission |  | Valves | Other |  | Unknown |  | 2010-01-20 | 2010-01-20 | Other | DISASSEMBLE & RESEALED | Steel/Wrought Iron |  | GREENFIELD | ON HIGH TO HIGH SET FEEDING HOUSE# 38730; MP 35.78; REMOVED LEAKING FITTINGS, CLEANED RESEALED & REINSTALLED, SOAP TEST OK
| 09-50107-1 | 301A | [9 empty] | 2009-04-25 | [5 empty] | MOSS LANDING | MOSS LANDING TAPS, V1 AND V2 LEAKING .5; SAME, NO GAS FOUND
| 10-40007-1 | 187 | [9 empty] | 2009-05-01 | [5 empty] | SOLEDAD | OFF HGHWAY 101 - H&H SET FISHER BLOW OFF;____
| 10-40008-1 | [10 empty] | 2010-03-04 | [5 empty] | KING CITY | GUAGE LEAK AND BY VALVE; NO LEAK FOUND (DELETED)
4 | 10-40015-1 | [10 empty] | 2010-05-28 | [5 empty] | KING CITY | SAN BERNABE VINEYARD H&H SET IN 24X36 BOX; FOUND ON RECHECK OF 90-40140-1, NO LEA FOUND
| 10-40017-1 | 187 | 39.91. | 0.75 | Single Service |  | Other |  | RELIEF BLOWING | Other | REGULATOR POOR U/U | 2010-07-15 | 2010-07-15 | Other | REPLACED REGULATOR | Steel/Wrought Iron |  | SOLEDAD | FISHER B/OFF BLOWING GAS; FISHER / OFF; FOUND RELIEF BLOWING AT A SINGLE SERVICE HPR POOR LOCK UP ON REGULATOR SO REPLACED IT, RELIEF OK JUST DOING #5 JOB
| 10-70054-1 |  |  | 4 | Transmission |  | Fitting |  |  | Construction Defect |  | 2010-02-16 | 2010-02-17 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MARINA | READING FROM VALVE BOX MARKED IN YELLOW PAINT. DIRT AREA; GAS READING FROM VALVE BOX DIRT AREA; REDOPED PLUGS & CAPS ON TWO VALVE; SOAP TEST FOR LEAKS; CREW FOUND LEAKS @ 2 3/4" STL SAVE-A-VALVES ON 4" STL TRANSMISSION. REMOVED, REDOPED, & REPLACED 3/4" STL CAPS & 3/4" BRASS PLUGS, RE-WRAPPED VALVES
| 10-70054-1 |  |  | 4 | Transmission |  | Fitting |  |  | Construction Defect |  | 2010-02-16 | 2010-02-17 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MARINA | READING FROM VALVE BOX MARKED IN YELLOW PAINT DIRT AREA; GAS READING FOR VALVE BOX DIRT AREA; REDOPED PLUGS & CAPS ON TWO VALVE; SOAP TEST FOR LEAKS; CREW FOUND LEAKS @ 2 3/4" STL SAVE-A-VALVES ON 4" STL TRANSMISSION. REMOVED REDOPED & REPLACED 3/4" STL CAPS & 3/4" BRASS PLUGS, RE-WRAPPED VALVES
| 10-70056-1 | 1815-02 |  | 12 | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2010-02-22 | 2010-04-11 | Other | GREASE VALVE | Steel/Wrought Iron |  | MONTEREY | LEAKING BELOW GROUND NEXT 19'49 - 16'40; PUMPED GREASE INTO VALVES; SOAP TEST FOR LEAKS; CREW GREASED LEAKING VALVES WHEN COMPLETED, VALVES NO LONGER LEAKED.
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | SANTA CRUZ | HWY 1 NORTH OF SCARONI RD
|  |  |  | 12 | Transmission | [6 empty] | 2010-09-21 |  |  |  | Steel/Wrought Iron |  | SANTA CRUZ | HWY 1 NORTH OF SCARONI RD
| 10-10004-1 |  | 1.6 | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2010-02-12 | 2010-05-03 | Other | PLIDCO SPLIT & SLEEVE | Steel/Wrought Iron |  | SANTA CRUZ | EDGE OR ROAD WAY BETWEEN DRIVEWAYS; INSTALLED 8" REPAIR CLAMP H.P.PLIDCO SPLIT & SLEEVE SOAP TEST FOR LEAKS TORQUE TO 91 FELBS
| 10-10004-1 |  | 1.6 | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2010-02-12 | 2010-05-03 | Other | PLIDCO SPLIT & SLEEVE | Steel/Wrought Iron |  | SANTA CRUZ | EDGE OF ROADWAY BETWEEN DRIVEWAYS; INSTALLED 8" REPAIR CLAMP H.P.PLIDCO SPLIT & SLEEVE SOAP TESTED FOR LEAKS TORQUE TO 91 FELBS
| 10-10004-1 |  | 1.6 | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2010-02-12 | 2010-05-03 | Other | PLIDCO SPLIT & SLEEVE | Steel/Wrought Iron |  | SANTA CRUZ | EDGE OF ROADWAY BETWEEN DRIVEWAYS; INSTALLED 8" REPAIR CLAMP H.P.PLIDCO SPLIT & SLEEVE SOAP TEST FOR LEAKS TORQUE TO 91 FELBS.
| 10-10007 | DFM-9 |  | 0.75 | Distribution Main <= 60 PSIG |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-02-25 | 2010-12-15 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SANTA CRUZ | 5318 GRAHAM HILL; LEAK ON HIGH TO HIGH SET BY CAR POINT; LEAK ON HIGH TO HIGH END SET BY CAR PORT; LEAK ON HIGH TO HIGH SET BY CAR PORT; FIXED LEAKED; REMOVED - REDOPED - RETIGHTENED; PLACED 2 HOUSES ON BYPASS GAS. REMOVED FITTING, RE-DOPED & REINSTALLED FITTING, SOAP TEST OK
| 10-10007 | DFM-9 |  | 0.75 | Distribution Main |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-02-25 | 2010-12-15 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SANTA CRUZ | 5318 GRAHAM HILL; LEAK ON HIGH TO HIGH SET BY CAR PORT; LEAK ON HIGH TO SET BY CAR PORT; FIXED LEAK ; REMOVED - REDOPED - TIGHTENED; PLACED 2 HOUSES ON BYPASS GAS. REMOVED FITTING; RE-DOPED & REINSTALLED FITTING. SOAP TEST OK
| 10-10009-1 | DFM-9 |  | 0.75 | Single Service |  | Regulator |  |  | Atmospheric Corrosion |  | 2010-02-25 | 2010-12-20 | Other | REPLACED H.P.R. SET | Steel/Wrought Iron |  | SANTA CRUZ | 1950 GRHAM HILL RD.; ATMOSPHERIC CORROSION, PITTED & LEAKING, SOAP TEST - REPLACED H.H.; USED H.P. PRE TESTED SEAMLESS PIPE & NIPPLES TO BE REPAIR. SOAP TEST OK
| 10-20113-1 | [10 empty] | 2010-09-28 | [5 empty] | PAHERO
| 10-20131 | 181-A |  | 0.75 | Single Service |  | Other |  | INLET VALVE | Other | NEEDED GREASE | 2010-10-04 | 2010-12-22 | Greased - Other |  | Steel-Other |  | WATSONVILLE | HPR SET #153, LEAKING FROM GREASE FITTING ON INLET; CUSTOMER CONCERNED - INLET VALVE - GREAT; GREASED VALVE; GREASED VALVE; GREASED INLET VALVE - SOAP TEST OK
76 | 10-20324-1 | 1816-20 |  | 3 | Gathering |  | Fitting |  |  | Other |  | 2010-10-21 | 2010-10-21 | Other |  |  |  | WATSONVILLE | 15' S/O J65 REG ST. IFO 7/11; RLSC DID READING; RLSC NOT IN IGIS
76 | 10-20326-1 | [10 empty] | 2010-10-14 | [5 empty] | WATSONVILLE | WATSONVILLE CROSSTIE REG STA 1817-01/X1851; WATSONVILLE CROSSTIE REG STA, NO LEAK FOUND;
76 | 10-20324-1 | 1816-20 |  | 3 | Gathering |  | Fitting |  |  | Other |  | 2010-10-21 | 2010-10-21 | Other |  |  |  | WATSONVILLE | 15' S/O J65 REG ST. IFO 7/11; RLSC DID READING; RLSC NO IN IGIS
76 | 10-20327-1 | 1 |  | 0.75 | Single Service |  |  |  |  | Unknown |  | 2010-10-19 | 2010-10-19 | Other |  |  |  | WATSONVILLE | XST CAREIN VALLEY -S/OFF VALVE ON METER SET; X ST CAREIN VALLEY - S/OFF VALVE ON METER; INSTALLED A GREASE FITTING
76 | 10-20328-1 | 1 |  | 8 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-19 | 2010-10-19 | Other |  |  |  | WATSONVILLE | B061 B062, VALVE 200' S/O 855; GREASED VALVES & RETAPED PLUG
76 | 10-20333-B |  |  | 0.75 | Distribution Main > 60 PSIG |  | Line Valve |  |  | Other |  | 2010-12-11 | 2010-12-11 | Greased - Other |  | Steel-Other |  | WATSONVILLE | @TAP VALVE UPSTREAM FROM H.P.R.; LEAK ON VALVE IN FRAME/COVER; GREASED VALVE TO CORRECT LEAK; VALVE LEAKING AT STEM, GREASED TO CORRECT
4 | 11-40001-B | 187 | 1.03 | 6 | Transmission |  | Bell Joint |  |  | Digin/Excavation |  | 2011-01-25 | 2011-01-26 | Replace #TP Main < 50 ft |  | Steel/Wrought Iron |  | SAN ARDO | C/O STRUCK PIPE (4') + REPLACED W/ 4' 6" 0.188" W.T. X-42 ERW
4 | 11-40002-1 |  |  | 10 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2011-04-26 | 2011-06-06 | Greased - Other |  | Steel/Wrought Iron |  | KING CITY | GREASE VALVE. WAS LEAKING FROM GREASE FITTING.
4 | 11-40005-1 | 187 | 22.82 | 4 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | Construction Defect |  | 2011-05-26 | 2011-05-26 | Replace #TP Main < 50 ft |  | Steel/Wrought Iron |  | KING CITY | REPLACED 3' OF 4" STEEL ON REG STATION.; SOAP TEST FOR LEAKS. TWESTED 4" STL FOR TRANSMISSION LINE WITH MAOP OF 313 @ 1140 PSI FOR 1-1/2 HRS. CHART IS ATTACHED.
4 | 11-40005-1 | 187 | 22.82 | 4 | Transmission |  | Body of Pipe |  |  | Construction Defect |  | 2011-05-26 | 2011-05-26 | Replace #TP Main < 50 ft |  | Steel/Wrought Iron |  | KING CITY | REPLACED 3' OF 4" STEEL ON REG STATION.; SOAP TEST FOR LEAKS. TESTED 4" STL FOR TRANSMISSION LINE WITH MAOP OF 313 @ 1140 PSI FOR 1 1/2 HRS. CHART IS ATTACHED.
76 | 11-70262 | 301F | 7.17 | 16 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | External Corrosion |  | 2011-06-25 | 2011-06-28 | Type A Sleeve - Weld |  | Steel-Other |  | MARINA | INSTALLED A SLEEVE OVER DAMAGED SECTION; WELDED ON A SLEEVE, SOAP TESTED OK.
76 | 11-70262 | 301F | 7.17 | 16 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | External Corrosion |  | 2011-06-25 | 2011-06-28 | Type A Sleeve - Weld |  | Steel/Wrought Iron |  | MARINA | INSTALLED A SLEEVE OVER DAMAGED SECTION; WELDED ON A SLEEVE, SOAP TESTED OK
7 | 11-70262-1 | 301F | 7.17 | 16 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2011-06-25 | 2011-06-28 | Type A Sleeve - Weld |  | Steel/Wrought Iron |  | MARINA | INSTALLED SLERVE OVER LEAK; WELDED ON A SLEEVE, AND SOAP TEST OK
7 | 11-70059-A | 1813-02 | 12.95 |  |  |  | Body of Pipe |  |  | Other | SAND BLASTING | 2011-04-12 | 2011-04-12 | Welded Sav-A-Valve - Weld |  | Steel-Other |  | SEASIDE | WELDED THREAD-O-LET OVER HOLE + PLUGGED, SOAP TEST OK; SAND BLASTER PUNCTURED HOLE IN 9" BRIDAL PIPING, WELDED THREAD-O-LET/SAVE-A-VALVE OVER HOLE + PLUGGED. SOAP TEST OK.
| 11-50029-1 | 1815-02 | 8.09 | 2 | Distribution Main > 60 PSIG | TRANSMISSION (>= 20% SMYS) | Line Valve |  |  | Other |  | 2011-03-17 | 2011-03-17 | Tighten Cap or Bolt | Greased - Other | Steel/Wrought Iron |  | SALINAS | GREASE THE FIRE VALVE + TIGHTEN THE PACKING ON PIT VALVE
5 | 11-50081-B | 301A | MP51.22 | 0.75 | Transmission >= 20% SMYS |  | Threads |  |  | Other |  | 2011-05-21 | 2011-05-21 | Other | TIGHTEN GREASE STEM | Steel/Wrought Iron |  | PRUDALE | TIGHTEN GREASE STEM; TIGHTEN GREASE STEM
76 | 11-10022-A |  |  | 0.75 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2011-03-31 | 2011-03-31 | Other | REPLACED 3/4" NIPPLE | Steel/Wrought Iron |  | SANTA CLARA | REPLACED LEAKING NIPPLE -- RESEALED THREADS; REPLACED NIPPLE ABOVE REG. RESEALED THREADS, SOAP TEST OK.
76 | 11-10022-A |  |  | 0.75 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2011-03-31 | 2011-03-31 | Other | REPLACED 3/4" NIPPLE | Steel-Other |  | SANTA CRUZ | REPLACED LEAKING NIPPLE - RESEALED THREADS; REPLACED NIPPLE ABOVE REG, RESEALED THREADS, SOAP TEST OK
5 | 95-00006-1 |  |  | 8.62 | Transmission |  | Tap Connection |  |  | Digin |  | 1995-05-20 | 1995-05-20 | Replace Pipe |  | Steel/Wrought Iron |  | SALINAS | TEMPORARY REPAIR OF MUELLER FITTING OVER LEAK. PERMINENT REPAIR BY REPLACING DAMAGED PORTION OF MAIN.
5 | 78-00423-1 |  |  | 12 | Distribution Main | [6 empty] | 1978-06-09 |  |  |  | Steel/Wrought Iron |  | SALINAS | NO LEAK 7/19/1978
| 78-00423-1 |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | SALINAS | NO LEAK; CHECK 12" MAIN AND DRIP LINE FOR LEAK. SOAP TEST TEE AND DRIP LINE. NO ... AND LEAK. ... REPAIRED BY ... OIL. WRAP ON MAIN IS ...
18 | 78-00425-1 |  |  | 8 | Transmission | [6 empty] | 1978-07-10 |  |  |  | Steel/Wrought Iron |  |  | PICKED SMALL READING 4 ON SAMPLE ON MAIN MTY#1 - 8" WHERE MAIN CROSSED HWY. 68. M.P.4.88. ALSO PICKED UP READING ON BOTH SIDES OF HWY. 68 IN THE GROUND ON ANGLE POINTS.
5 | 78-00427-1 |  |  | 8 | Transmission | [6 empty] | 1978-06-27 |  |  |  | Steel/Wrought Iron |  | SALINAS | SEE #7900422; PICKED UP READING ON LEAK INDICATOR S/END OF HARKINS RD. METER STA. NEAR V-65.70.; SEE LEAK #790042 FOR PRE-REPAIR CHECK.
5 | 78-00428-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-06-29 | 1978-09-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | ORIGINAL IN LINE FOLDER
| 94-00013-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1994-05-09 | 1996-08-13 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SANTA CRUZ | WELDED SLEEVE ON 12" T.P. MAIN
76 | 90-60125-1 |  |  | 8 | Distribution Main | TRANSMISSION | Valves |  |  | Other |  | 1998-04-28 | 1998-04-28 | Other |  | Steel/Wrought Iron |  | SANTA CRUZ | GREASED STATION VALVES
76 | 90-60125-1 | [10 empty] | 1990-01-23 | [5 empty] | SANTA CRUZ
| 09-70587-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2009-11-03 | 2011-05-02 | Other | TIGHTEN FITTING | Steel/Wrought Iron |  | CARMEL | CARMEL VALLEY RD/ CARMEL KNOLLS DR.; ON MAIN 200 FT NE FROM INTERS PGE VAULT, MARKED VAULT W/YELLOW X; REDOPED & RETIGHTEN SCADA FITTINGS; REMOVE, REDOPE, RETIGHTEN SCADA TUBING CONNECTIONS; SOAP TEST OK.
| 09-90703-1 |  |  | 0.75 | Gathering |  | Riser |  |  | Other | PIPE DOPE | 2009-09-10 | 2009-12-10 | Other |  | Steel/Wrought Iron |  | MARINA | AT RISER THREADS; INSTALLED SKINNER CLAMP
| 09-90819-1 |  |  | 0.75 | Gathering |  | Fitting | Riser |  | Other | PIPE DOPE | 2009-09-11 | 2009-12-02 | Other | PIPE DOPE | Steel/Wrought Iron |  | MARINA | SPICKET W/ HOT PLUG BELOW RISER; REMOVED, REDOPED & RETIGHTENED COCK
| 09-90819-1 |  |  | 0.75 | Gathering |  | Fitting | Riser |  | Other | PIPE DOPE | 2009-09-11 | 2009-12-02 | Other | PIPE DOPE | Steel/Wrought Iron |  | MARINA | REMOVED, REDOPED, & RETIGHTENED COCK
| 09-91350-1 |  |  | 1.25 | Gathering |  | Riser |  |  | Material Failure |  | 2009-10-06 | 2010-01-05 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | PACIFIC GROVE | BYPASS VALVE ON METERS FOR APT 400 AND ABOVE; TIGHTENED NUT ON BYPASS & GREASED
| 10-70291-1 | 301F | 3.74 | 0.375 | Single Service |  | Regulator |  |  | Construction Defect |  | 2010-10-05 | 2010-12-21 | Other | REPLACE S.S. FITTING | Steel/Wrought Iron |  | SALINAS | CITY: HPR#287; REPLACED STAINLESS STEEL FITTING; FOUND LEAKING STAINLESS STEEL FITTING ON REGULATOR, PILOT. REPLACE STAINLESS FITTING AND SOAP TEST FOR LEAKS.
| 10-70291-1 | 301F | 3.74 | 0.375 | Single Service |  | Regulator |  |  | Construction Defect |  | 2010-10-05 | 2010-12-21 | Other | REPLACE S.S. FITTING | Steel/Wrought Iron |  | SALINAS | CITY: HPR#287; REPLACED STAINLESS STEEL FITTING; FOUND LEAKING STAINLESS STEEL FITTING ON REGULATOR, PILOT, REPLACED STAINLESS FITTING AND SOAP TEST FOR LEAKS.
7 | 10-70364-1 | 1 |  | 0.75 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Other |  | 2010-10-18 | 2010-10-18 | Other |  |  |  | MONTEREY | REBUILT STATION - GREASED BYPASS VALVE
| 09-70238-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 2009-05-04 | 2009-06-24 | Other | BLOW-OFF VALVE-'A' | Steel/Wrought Iron |  | MARINA | VALVE MARKED INSIDE FENCED ENCLOSURE; VALVE MARKED INSIDE FENCED AREA.; NO U.S.A. VALVES IN FRAME & COVER NO DIGGING INVOLVED.; GREASED VALVE NO VISUAL LEAKS
| 09-70239-1 |  |  | 3 | Transmission |  | Valves |  |  | Other |  | 2009-05-04 | 2009-06-23 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MONTEREY | LEAK AT PIT BOX, AND FLEXLINE AT #6 VALVE 40' SOUTH OF PIT BOX; LEAK @ PIT BOX MARKED YELLOW #6 VALVE
| 09-70379-1 |  |  | 1.25 | Transmission |  | Valves |  |  | Other | DRY DOPE | 2009-06-26 | 2010-07-15 | Other | REDOPE THREADS | Steel/Wrought Iron |  | MONTEREY | ACROSS FROM 9841 BLUE LARKSPUR NEAR WHITE FENCE; REG P.T; REDOPPED THREADS & TIGHTENED FITTINGS; REPAIRED GAS LEAKS @ DIST. REG. STATION M-06 BY REDOPING THREADS
| 09-70470-1 |  |  | 4 | Transmission |  | Valves | Other | NEEDLE VALVE | Other | DRY DOPE ON THREADS & GREASE | 2009-07-29 | 2009-07-29 | Other | GREASE, REDOPE THREADS | Steel/Wrought Iron |  | MONTEREY/SEASIDE | IN REG. PITS @ MRM-05 & VALVE #4; REG. STATION
| 09-70471-1 |  |  | 2 | Distribution Main |  | Other |  | FLANGE | Other | FLANGE GASKET | 2009-07-29 | 2010-05-05 | Other | REPLACED FLANGE GASKET & NEW BOLTS | Steel/Wrought Iron |  | MONTEREY | READING @ 4" STACK @ REG PIT M-15; 2" VALVE MARKED YELLOW LEAK INSIDE PIT; 10 MIN SOAP TEST; FOUND INLET FLANGE TO FILTER FOAMING SO REPLACED GASKET & BOLTS AND GREASE ALL VALVES LAJ/MAN 5/5/10
[12 empty] | 1975-12-09 |  |  |  | Steel-Other |  | WATSONVILLE
|  |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1986-12-23 | 1986-12-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | WELDED SLEEVE OVER DAMAGED PIPE FOR REPAIR
| 09-10356-1 |  |  |  | Distribution Main |  | Valves |  |  | Other | GREASE | 2009-08-25 | 2011-02-23 | Other | GREASED | Steel/Wrought Iron |  | BEN LOMOND | GREASED - SOAP TEST OK; GREASED & OPERATED VALVE AFTER VALVE TRUCK REMOVED DIRT, SOAP TEST OK
| 00-10085- | DFM03 | 13.61 | 12 | Transmission |  | Body of Pipe |  |  | Unknown |  | 2000-11-17 | 2000-12-14 | ABANDON |  | Steel/Wrought Iron |  | DAVENPORT | REROUTE & REPLACE 12" W/ 3" STEEL
| 10-10007- | DFM-9 |  | 0.75 | Distribution Main <= 60 PSIG |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-02-25 | 2010-12-15 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SANTA CRUZ | JORGENSEN NEEDS HELP; LEAK ON HIGH TO HIGH SET BY CAR PORT, LEAK ON HIGH TO HIGH SET BY CAR PORT, FIXED LEAK; REMOVED-REDOPED-TIGHTENED; PLACED 2 HOUSES ON BYPASS GAS. REMOVED FITTING, REDOPED & REINSTALLED FITTING. SOAP TEST OK
| 09-10019-1 |  |  | 3 | Transmission |  | Other |  | FILTER | Construction Defect |  | 2009-02-03 | 2009-12-22 | Other | REPLACE FILTER | Steel/Wrought Iron |  | SCOTTS VALLEY | REPLACED FILTER; REPLACED LEAKING FILTER, SOAP TEST OK
| 09-10021- |  |  | 0.75 | Transmission |  | Other |  | STEEL TEE CAP | Other | DRY PIPE DOPE | 2009-02-04 | 2009-02-11 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SANTA CRUZ | INLET MULLER CAP WAS LEAKING, SO PULLED IT OFF CLEANED THREADS WITH WIRE BRUSH REDOPED THREADS AND TIGHTED CAP BACK UP TO REPAIR LEAK
| 09-10210-1 | 181801 | 5.6 | 12 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2009-05-27 | 2010-06-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SANTA CRUZ | WILDER RANCH OVER TP MAIN; JOB H. REPAIR ON 41097513
76 | 93-20011-1 | DFM1 |  | 12 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | External Corrosion |  | 1993-05-05 | 1993-05-05 | Welded Sleeve/Can - Weld |  |  |  | SANTA CRUZ | ON TRANS LINE; INSTALL 12" FULL CIRCLE SLEEVE
| 09-90387-1 |  |  | 0.75 | Gathering |  | Riser | Other | THREADS | Other | PIPE DOPE | 2009-06-12 | 2009-11-04 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | SANTA CRUZ | INLET VALVE THREADS; COMPLETE UPON ARRIVAL
| 10-10483-1 | DFM-3 | 7.82 | 0.75 |  |  | Fitting |  |  | Weld Failure | DRY DOPE | 2010-12-20 | 2011-03-14 | Fill Weld - Weld | REDOPE & TIGHTEN NIPPLE | Steel/Wrought Iron |  | SANTA CRUZ | ABOVE INLET VALVE ON HPR; SEC MARK THOMAS OR CHARLES LAM FOR EXACT LOCATION. IT CAN BE BY-PASSED. HOG SOLID BY PASS; SOAP TEST OK
76 | 10-10478-1 | DFM3 | 3.65 | 0.75 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other |  | 2010-12-10 | 2010-12-10 | Greased - Other |  | Steel-Other |  | SANTA CRUZ | GREASED VALVE
76 | 11-10022-A |  |  | 0.75 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2011-03-31 | 2011-03-31 | Other | REPLACED 3/4" NIPPLE | Steel-Other |  | SANTA CRUZ | LEAK ON HIGH TO HIGH REG. SET.; REPLACED LEAKING NIPPE - RESEALED THREADS; REPLACED NIPPLE ABOVE REG. RESEALED THREADS, SOAP TEST OK;
76 | 10-81026-1 | 1816-15 |  | 8 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-03 | 2010-10-20 | Other |  |  |  | SANTA CRUZ | INSTALLED 8" PLIDCO CLAMP
76 | 10-81027-1 | 1816-15 |  | 0.75 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-03 | 2010-10-09 | Other |  |  |  | SANTA CRUZ | NO GAS FOUND; THREADS ON INLET TO REG.; REPAIRED GAS LEAK ON INLET AND OUTLET OP REG SHUT CUST OFF
76 | 10-81008-1 | 1819-01 |  | 0.75 | Transmission >= 20% SMYS |  | Other Welds |  |  | Unknown |  | 2010-10-01 | 2010-10-09 | Patch Weld - Weld |  |  |  | WATSONVILLE | WELDED LEAKING FTG; REWELDED LEAKING SOCKET WELD DWNSTREAM OP H TO H REG. SOAP TEST OK;
| 10-10004-1 |  | 1.6 | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2010-02-12 | 2010-05-03 | Other | PLIDCO SPLIT & SLEEVE | Steel/Wrought Iron |  | SANTA CRUZ | INSTALLED 8" REPAIR CLAMP H.P. PLIDCO SPLIT & SLEEVE. SOAP FOR LEAKS. TORQUE TO 91 FELBS
| 08-10147-1 |  | 47 | 10 | Transmission |  | Tap Connection |  |  | Equipment Malfunction |  | 2008-11-12 | 2009-06-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SANTA CRUZ | TIGHTENED BOLTS ON CONTROL LINE; SOME TEST FITTINGS.
| 09-10425-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2009-10-05 | 2011-04-01 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | SANTA CRUZ | INSTALLED 2" SKINNER CLAMP AND WRAPPED MAIN
| 09-10433-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Other | PIPE DOPE | 2009-10-06 | 2011-04-01 | Tighten Cap or Bolt | PIPE DOPE | Steel/Wrought Iron |  | SANTA CRUZ | MUELLER BOTTEM TAP ADD PIPE DOPE AND TIGHTEN
| 05-10039-1 | 181601 |  | 3 | Transmission |  | Valves |  |  | Material Failure |  | 2005-05-26 | 2005-05-26 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | SANATA CRUZ | @ VALVE # B181; SEE ATTACHMENT
| 04-10062-B |  |  | 4 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2010-12-10 | 2011-02-07 | SS Clamp w/Anode - Clamp |  | Steel-Other |  | SANTA CRUZ | INSTALLED SS CLAMP FULL CIRCLE AND DRIVEABLE ANODE; 158' FROM 15TH AVE. TO SS CLAMP, 160 TO ABANDON 3/4" TEE EXTREME PITTING AT ABANDON TEE SHOULD REPLACE 30" SECTION OF MAIN.
| 09-10455-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2009-10-09 | 2011-04-07 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | SANTA CRUZ | INSTALLED 2 STAINLESS STEEL CLAMPS FULL CIRCLE, 2 ANODES DRIVEABLE (1 CLAMP FOR LEAK 1 CLAMP FOR PITTING & GAUGE) (MAYBE BECAUSE OF OLD POLE HOLE) 55 FEET FROM ELDORADO AVE ON BROMMER STREET.
76 | 09-10241-1 |  |  | 4 | Distribution Main >60 PSIG and <20% SYMS |  | Fitting |  |  | Equipment Malfunction |  | 2009-06-25 | 2010-12-22 | Other |  |  |  | SANTA CRUZ | PARK STRIP WEST CORNER, SAME AREA, SAME AREA; DOPE FITTINGS & TIGHTENED FITTINGS; SOAP TEST
| 09-10257-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2009-06-26 | 2010-11-17 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | SANTA CRUZ | BARHOLES IN STREET., SAME AREA, SAME AREA; SOAP TEST
| 03-10060-1 | DFM3 | 2.11 | 4 | Transmission |  | Valves |  |  | Other | VALVE STEM LEAK | 2003-10-27 | 2003-11-10 | Other | TIGHTEN STEM | Steel/Wrought Iron |  | SANTA CRUZ | ODOR IN AIR - CALL IN, VALVE LEAKING AT STEM; TIGHTEN; VALVE MAINTANICE
| 09-10281-1 |  |  | 2 | Distribution Main |  | Fitting |  | BOTTOM TAP CAP | Other | THREADS | 2009-07-13 | 2011-01-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SANTA CRUZ | DOPED CAP ON BOTTOM TAP; SOAP TEST FINAL JOINT
| 09-10274-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2009-07-07 | 2011-01-06 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | SANTA CRUZ | SOAP TEST
| 06-10127-2 |  |  | 0.75 | Transmission |  | Other |  | BLOW OFF | Material Failure | DIRT IN SEAT | 2006-11-18 | 2006-11-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | CAPITOLA | BOX NEEDS TO BE INLARGED. ... TO OPERATE PIN OFF TEE. FIXED BLOW OFF; SOAP TEST
76 | 10-10335-1 |  |  | 2 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2010-07-02 | 2011-04-21 | Skinner Clamp - Clamp |  | Steel-Other |  | CAPITOLA | INSTALLED 3 CLAMPS; INSTALLED 3 CLAMPS 4 PITTED AREAS ON 2" MAIN
76 | 11-10014-B |  |  | 1 | Distribution Main <= 60 PSIG |  | Fitting |  |  | Stress Corrosion Cracking |  | 2011-03-26 | 2011-03-26 | Replace #TP Main >= 50 ft | REPLACE DIST MAIN < 100 FT. | Other | AM FIT TEE | CAPITOLA | 1' METER TEE AND BRANCHED 100 SAN JOSE, 120 ESPLANDE; 1" MET FIT TEE, 1/2" PERMANENT TEE FOR BRANCH
| 09-10333-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Equipment Malfunction |  | 2009-08-05 | 2011-02-03 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SANTA CRUZ | SERVICE T AND WATER VALVE COVER; AT FIRE SERVICE VALVE; REMOVE CAP DOP & TIGHTEN; SOAP TEST
76 | 10-81031-1 | 1816-01 | 8.44 | 8 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other |  | 2010-10-13 | 2011-02-02 | Greased - Other |  |  |  | WATSONVILLE | GREASED VALVE; SOAP TEST WAS OK V-5 GREASSED
76 | 10-81953-1 | DF3426 | 8.46 | 1 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-20 | 2011-01-13 | Other |  | Steel-Other |  | WATSONVILLE | REPLACED CAP "O" RINGS; SOAP TEST OK
76 | 10-81954-1 | X6472 | 8.45 | 1 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-20 | 2011-01-13 | Other |  | Steel-Other |  | WATSONVILLE | REPLACED CAP O RINGS; SOAP TEST OK
| 09-20020-1 | 181605 |  | 0.75 | Transmission |  | Valves |  |  | Other | VALVE | 2009-04-21 | 2009-06-16 | Other | GREASE VALVE | Steel/Wrought Iron |  | WATSONVILLE | GREASED & OPERATED
76 | 10-20328-1 | 1 |  | 8 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-19 | 2010-10-19 | Other |  |  |  | WATSONVILLE | GREASED VALVES & RETAPED PLUG; GREASED VALVES - RESEALED PLUGS
76 | 10-81033-1 | 1816-05 | 0 | 8 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-14 | 2010-10-19 | Other |  | Steel-Other |  | WATSONVILLE | GREASED VALVE & RETAPED PLUG
76 | 10-20333-B |  |  | 0.75 | Distribution Main > 60 PSIG |  | Line Valve |  |  | Other |  | 2010-12-11 | 2010-12-11 | Greased - Other |  | Steel-Other |  | WATSONVILLE | LEAK ON VALVE IN FRAME/COVER; GREASED VALVE TO CORRECT LEAK; VALVE LEAKING AT STEM, GREASED TO CORRECT.
76 | 10-81020-1 | 1816-05 |  | 0.75 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-02 | 2010-10-10 | Other |  |  |  | WATSONVILLE | SAME
| 09-20046-1 |  |  | 1.25 | Transmission |  | Other |  | GREASE FITTING | Unknown |  | 2009-06-03 | 2009-07-17 | Other | GREASE FITTING | Steel/Wrought Iron |  | WATSONVILLE
| 05-20061-1 | GM174439 |  | 1.25 | Transmission |  | Body of Pipe |  |  | Other | UNKNOWN | 2005-11-10 |  | Other |  | Steel/Wrought Iron |  | WATSONVILLE
76 | 10-20324-1 | 1816-20 |  | 3 | Gathering |  | Fitting |  |  | Other |  | 2010-10-21 | 2010-10-21 | Other |  |  |  | WATSONVILLE | RLSC DID READING; RLSC NOT IN IGIS
76 | 10-81014-1 | X8151 | 1 | 0.25 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-02 | 2010-10-10 | Tighten Cap/Bolt - Fitting |  |  |  | WATSONVILLE | NO LEAK FOUND; TIGHTEN 1/4" NIPPLE BELOW SERIES 20 MO
76 | 10-81021-1 | 1816-20 |  | 3 | Gathering |  | Fitting |  |  | Other |  | 2010-10-02 | 2010-10-21 | Other |  |  |  | WATSONVILLE | REPLACE GASKET ON FILTER FLANGE; SOAP TEST
76 | 10-81955-1 | 1816-01 | 3.44 | 5 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-10-14 | 2011-01-14 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | WATSONVILLE | REDOPED AND TIGHTENED NIPPLE; SOAP TEST
| 94-50004-1 |  |  | 3 | Transmission |  | Longitudinal Weld |  |  | Material Failure |  | 1994-06-21 | 1994-06-21 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | WATSONVILLE
76 | 10-81008-1 | 1819-01 |  | 0.75 | Transmission >= 20% SMYS |  | Other Welds |  |  | Unknown |  | 2010-10-01 | 2010-10-09 | Patch Weld - Weld |  |  |  | WATSONVILLE | WELDED LEAKING FTG; REWELDED LEAKING SOCKET WELD DWNSTREAM OP H TO H REG. SOAP TEST OK
76 | 10-81005-1 | 181A |  | 0.25 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-09-30 | 2010-10-07 | Other |  |  |  | WATSONVILLE | SUPPLLY LINE & SERVICE LINE FTG; REPR GAS LEAK ON SUPPLY LINE & SENCE LINE ON MTR. J-73
76 | 10-81950-1 | 181B | 10.12 | 6 | Transmission >= 20% SMYS |  | Clamp |  |  | Unknown |  | 2010-10-01 | 2010-10-18 | Tighten Cap/Bolt - Fitting |  |  |  | WATSONVILLE | RESEALED BLOW OFF CAP
76 | 90-70090-1 |  |  | 12 | Transmission |  | Fitting |  |  | Other |  | 1990-01-26 | 1990-04-10 | Other |  | Steel/Wrought Iron |  | WATSONVILLE | GREASED VALVE
| 05-20065-1 |  |  | 16 | Transmission |  | Valves |  |  | Other | VALVE CORE LEAK | 2005-11-22 | 2006-02-17 | Other | GREASED VALVE | Steel/Wrought Iron |  |  | GREASED VALVE
| 09-20013-1 |  |  | 6 | Transmission |  | Other |  | BLOW OFF | Unknown |  | 2009-03-27 | 2009-05-14 | Other | CLEAN O-RINGS | Steel/Wrought Iron |  | PAJARO
76 | 10-81002-1 | 181B |  | 2 | Transmission >= 20% SMYS |  |  |  |  | Unknown |  | 2010-09-30 | 2010-10-07 | Other |  |  |  | WATSONVILLE | GREASED VALVE 2 & REPAIRED GEAR CHATION; GREASED VLV#2 BYPASS STATE LINE TO CHART BOX LEAKING FTG
76 | 89-30016-1 | [10 empty] | 1989-06-29 | 1993-08-13 | Weld Over Sleeve or Can |  |  |  | WATSONVILLE | M & C DEPT. MADE REPAIRS NO GAS IN REG. PIT
| 09-20017-1 | 181A |  | 0.25 | Transmission |  | Fitting |  |  | Other | DRY DOPE | 2009-03-26 | 2009-11-10 | Tighten Cap or Bolt | Soap and/or Tape | Steel/Wrought Iron |  | PAJARO | REDOPE & TIGHTEN; DOPED FITTING - SOAP TEST; REPAIRED LEAKS
| 09-20015-1 | 181B |  | 0.75 | Transmission |  |  |  |  | Other | GREASED VALVE | 2009-03-26 | 2009-06-15 | Other | GREASED | Steel/Wrought Iron |  | AROMAS | SMALL LEAKS ON FIRE VALVE & STA. BYPASS VALVE. GREASED - STOPPED LEAK FOR NOW.
76 | 10-20337-1 | 1870-01 |  | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Unknown |  | 2010-10-15 | [5 empty] | SANTA CRUZ
76 | 10-81001-1 | 1870-01 |  | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Unknown |  | 2010-09-30 | 2010-10-09 | Other |  |  |  | SANTA CRUZ | NEXT TO VALVE V-B77; GREASED VALVE; GREASED INLET FIREWALL TO DIST. REG K-12
| 09-90620-1 |  |  | 0.75 | Gathering |  | Fitting |  |  | Other | NO DOPE | 2009-08-31 | 2009-11-19 | Other |  | Steel/Wrought Iron |  | WATSONVILLE | REPLUMBED & REDOPED FITTINGS; REPLUMBED & REPLACED FITTINGS SOAP TESTED.
76 | 10-81004-1 | 181B |  | 0.25 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-09-30 | 2010-10-06 | Other |  |  |  | AROMAS | NO GAS FOUND; TIGHTENED LOOSE SENSE LINE FITTING; REG SENSE LINE FITTING LOOSE;TIGHTENED FITTING
| 09-20011-1 |  |  | 0.75 | Transmission | Distribution Main | Other |  | RELIEF | Equipment Malfunction |  | 2009-03-26 | 2009-03-26 | Other | REBUILT REG. | Steel/Wrought Iron |  | WATSONVILLE | REBUILT REGULATOR AT STATION & PAINTED STATION AND SET PRESSURE @30 PSIG
| 09-20016-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | GREASE | 2009-03-26 | 2010-08-20 | Other | GREASED | Steel/Wrought Iron |  | AROMAS | GREASED VALVES & FLASHED G. BUTTONS
76 | 10-81007-1 | 181B |  | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-09-30 | 2010-10-06 | Other |  |  |  | AROMAS | PLUG LKING REDOPED-GREASED VALVE; RESEALED PLUG&FITTINGS;GREASED VALVE ON SENSE LINE
76 | 10-81952-1 | DF3433 | 0.01 | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-11 | 2011-01-07 | Other |  | Steel-Other |  | AROMAS | REPLACED 2 "O" RINGS ON PINOFF CAP; SOAP TEST OK
76 | 10-81003-1 | 1870-01 | 3.31 | 0.75 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-09-30 | 2010-10-09 | Other |  |  |  | SANTA CRUZ | TIGHTENED UP UNION; TIGHTEN LOOSE UNION@HPR REGSTA J76 OR J29
76 | 97-20034-1 |  |  | 4 | Transmission |  | Fitting |  |  | Other |  | 1997-12-23 | 1997-12-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN BERNITO CO. | FLANGED VALVE WAS EXCAVATED 12/30/97 BOLTS ON FLANGE WERE TIGHTENED, ELIMINATING THE LEAK
76 | 92-30067-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1992-06-11 | 1992-08-06 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | WATSONVILLE | WELD
8 | 10-88045-1 | 300B | 460.76 | 0.75 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Unknown |  | 2010-10-22 | 2011-01-10 | Other |  | Steel-Other |  | HOLLISTER | REPLACED 1ST STAGE REG. AND RESEALED FITT; REPAIRED GAS LEAKS, REPLACED 1ST STAGE REG AND RESEALED FITTINGS - SOAP TEST OK
8 | 10-88003-1 | 301 |  | 0.5 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-18 | 2011-03-22 | Replace Service Valve <2-inch |  | Steel-Other |  | HOLLISTER | CHANGED VALVE- SOAP TEST OK; REPLACE BYPASS VALVE - SOAP TEST OK
| 09-80020-1 |  |  | 0.5 | Transmission |  | Other |  | PLUG & GREASE STEM |  |  | 2009-04-25 | 2009-09-15 | Other | GREASED VALVES. RE-TAPED PLUG | Steel/Wrought Iron |  | SAN JUAN BAT. | TAG WAS LATE GETTING BACK TO MAPPING; BACK TO MAPPING LATE IN IGIS REPAIRED T. WRIGHT 9-24-09; VALVES 1 & 2 GREASED VALVES, RETAPED PLUG
8 | 10-88382-1 | DREG5362 | 0.01 | 12 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-21 | 2011-03-23 | Other |  | Steel-Other |  | HOLLISTER | 500" SE FROM ADDRESS, REG STATION IN FIELD, VALVE 130' S. OF SHORE ROAD, NO LEAK DETECTED; LEAK DETECTED
| 09-80014-1 | 300A |  | 0.75 | Transmission |  | Mechanical Joint | Valves |  | Other | LOOSE FITTING | 2009-04-23 | 2009-06-24 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | HOLLISTER | LEAK ON CAP 1ST STAG
| 09-80018-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | INACTIVITY | 2009-04-23 | 2009-06-24 | Other | OPERATE | Steel/Wrought Iron |  | HOLLISTER | INLET FIRE VALVE
| 10-80307-1 | 300B |  | 0.75 | Transmission |  | Other |  | UNION & FITTINGS | Unknown |  | 2010-10-07 | 2010-10-08 | Other | REPLACED & REDOPPED FITTINGS | Steel/Wrought Iron |  | HOLLISTER | UNION & VARIOUS OTHER FITTINGS; WENT & CHECKED OUT LEAK ON 10-7-10 & TIGHTENED UNION SHOWED LEAK DOWN THEN CAME OUT & MADE REPAIRS ON 10-8-10 & HOT ...CUSTOMERS 3MM @1PSI
8 | 11-80006-A | 300B |  | 0.75 | Distribution Main <= 60 PSIG |  |  |  |  | Vehicle | TRACTOR | 2011-05-06 | 2011-05-06 | Mechanical Repair Fitting - Fitting |  | Steel-Other |  | HOLLISTER | SHUT VALVE, REBUILD HPR SET
8 | 10-88008-1 | 300B | 455.11 | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Unknown |  | 2010-10-19 | 2011-01-04 | Other |  | Steel-Other |  | HOLLISTER | LUBED VALVES & TIGHTENED FITTINGS; TIGHTENED FITTING & LUBED VLVS SOAP OK
8 | 10-80346-A | 300B | 455.11 | 0.75 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Other | LOOSE BOLTS | 2010-12-24 | 2010-12-24 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | HOLLISTER | TIGHTENED BOLTS AROUND REG. DIAFRAM HOUSING, SOAP TEST OK; TIGHTENED BOLTS AROUND REG. DIAFRAM HOUSING, SOAP TEST OK. SEE HRH-42
| 10-88378-1 | 300A | 454.76 | 0.75 | Transmission |  | Valves |  |  | Internal Corrosion |  | 2010-10-20 | 2011-03-14 | Other | REPLACE "O" RINGS | Steel/Wrought Iron |  | HOLLISTER | REPLACED UNION O RINGS IN VALVE T CAP
| 09-80012-1 | 300A |  | 2 | Transmission |  | Valves |  |  | Unknown | OTHER | 2009-04-23 | 2009-08-17 | Other | GREASED VALVE | Steel/Wrought Iron |  | HOLLISTER
| 09-80046-1 | 300 | [9 empty] | 2009-10-20 | [5 empty] | HOLLISTER
8 | 10-88002-1 | 103 |  | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Unknown |  | 2010-10-18 | 2010-12-30 | Other |  | Steel-Other |  | HOLLISTER | FIXED LKS AND REPLACED PS. VALVE; RESEALED FITTINGS & RPLCD DS VLV
8 | 10-88004-1 | 103 | 7.73 | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-18 | 2010-10-25 | Other |  |  |  | HOLLISTER | LUBED AND OPERATED INLET VALVE @ HRH-14
8 | 10-80338-1 | 103 | 966 | 0.25 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-10-25 | 2010-10-25 | Tighten Cap/Bolt - Fitting |  |  |  | SAN JUAN BAUTISTA | TIGHTENED FITTINGS ON MONITOR SENSING LINES
8 | 10-88001-1 | 903 | 9.65 | 0.25 | Gathering |  | Fitting |  |  | Other |  | 2010-10-18 | 2010-10-25 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SAN JUAN BAUTISTA | TIGHTENED FTGS ON MONITOR SENSE LINES
| 05-80025-1 | 103 | 9.37 | 0.75 | Transmission |  | Valves |  |  | Construction Defect |  | 2005-08-31 | 2005-08-31 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | SAN JUAN BAUTISTA
| 09-91652-1 | 103 | 9.37 | 0.75 | Transmission |  | Valves |  |  | Construction Defect |  | 2009-11-07 | 2009-11-07 | Other | REPLACED GREASED FITTING | Steel/Wrought Iron |  | SAN JUAN BAUTISTA | REPLACED BAD GREASE FITTING, SOAP TEST OK
8 | 87-00628-1 |  |  | 12 | Transmission >= 20% SMYS |  | Fitting |  |  | Material Failure |  | 1987-08-31 | 1987-09-01 | Replace TP Main |  |  |  | HOLLISTER
8 | 82-00606-1 |  |  | 12 | Transmission >= 20% SMYS |  | Tap Connection |  |  | Other |  | 1982-04-28 | 1982-05-13 | Other |  |  |  | HOLLISTER
| 09-80025-1 |  |  | 0.5 | Transmission |  | Valves | Other | PLUGS LEAKING | Other | NO TAPE | 2009-04-27 | 2009-08-19 | Tighten Cap or Bolt | TAPPED PLUGS | Steel/Wrought Iron |  | HOLLISTER | PRESS. TEST LINES ON VALVE - NO TAPE ON THREADS
8 | 10-88007-1 | 300A | 448.37 | 1 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Other |  | 2010-10-19 | 2010-10-22 | Other |  |  |  | HOLLISTER | REMOVED AND REPLACED LOOSE FITTINGS; REPLACED LOOSE FITTING, SOAP TEST OK
| 09-80015-1 | 300A |  | 2 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2009-04-23 | 2009-07-02 | Other | 2" UNION | Steel/Wrought Iron |  | HOLLISTER | REPAIRED LEAK ON 2" UNION, REDOPED 2" FITTING, TIGHTEN UP FITTING
8 | 10-88006-1 | 300B | 445.32 | 12 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-19 | 2010-12-22 | Other |  | Steel-Other |  | HOLLISTER | TIGHTENED LOOSE PLUG, SOAP; TIGHTENED LOOSE PLUGS, SOAP TEST OK
| 00-80023- | 300A |  | 0.75 | Transmission |  | Valves |  |  | Other | VALVE NEEDED GREASE | 2000-10-17 | 2005-04-26 | Other | GREASED VALVE | Steel/Wrought Iron |  | PANOCHE | GREASED GAS VALVE
| 10-80333-1 | 300B | 439.47 | 0.75 | Transmission |  | Valves |  |  | Unknown |  | 2010-10-21 | 2011-01-10 | Other | RESEALED FITTINGS & GREASED VALVES | Steel/Wrought Iron |  | HOLLISTER | HIGH TO HIGH SET T-439(B); REPAIRED LEAKS; RESEALED ALL FITTINGS, REPLACED 1ST STAG REG. SOAP TEST OK.
| 10-80185-1 | 300B | 435.8 | 0.75 | Transmission |  | Fitting |  |  | Other |  | 2004-09-13 | 2010-12-10 | Other | REBUILT SET | Steel/Wrought Iron |  | PAICINES | REBUILT THE HPR SET. SOAP TESTED OK.
| 10-80186-1 | 300B | 418.36 | 0.75 | Transmission |  | Fitting |  |  | Other |  | 2010-09-13 | 2010-12-07 | Soap and/or Tape - Other |  | Steel/Wrought Iron |  | PAICINES | REPAIRED THE LEAKING PIN OFF TEE
| 09-80023-1 | 300A | [9 empty] | 2009-04-25 | [5 empty] | TRES PINOS | REPAIRED ON 00-80025-1
| 00-80022-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | DRY O-RINGS | 2000-10-16 | 2010-06-15 | Other | LUBED O-RINGS | Steel/Wrought Iron |  | HOLLISTER | AT ZONE VALVE INLET VALVE FOR H-85; AT GAS ZONE VALVE, SOME LOCATION, SAME AREA; RESEALED O-RINGS; RELUBED O-RINGS ON MULLER INLET VALVE
| 10-80187-1 | 300B |  | 0.75 | Transmission |  | Fitting |  |  | Other | DRY SEALANT | 2010-09-13 | 2010-12-19 | Soap and/or Tape - Other |  | Steel/Wrought Iron |  | PAICINES | REMOVED THE PIN-OFF CAP; APPLIED THREAD SEALANT; REINSTALLED THIS PIN-OFF CAP; SOAP TESTED OK
| 09-40095-1 | 187 | 46.65 | 8 | Transmission |  | Valves |  |  | Unknown | OTHER | 2009-10-08 | 2009-11-19 | Other |  | Steel/Wrought Iron |  | SOLEDAD | O.P. VALVE 46.63; GREASED ALL VALVES IN THE VAULT; GREASED ALL VALVES IN THE VAULT
| 09-40094-1 | 187 |  | 3 | Distribution Main |  | Valves |  |  | Other |  | 2009-10-08 | 2011-03-31 | Other |  | Steel/Wrought Iron |  | SOLEDAD | GREASED LEAKING VALVE (V.9) ON REG. SET, SOAP TESTED OK
| 09-40097-1 | 187 | 45.39 | 0.75 | Transmission |  | Fitting |  |  | Other | LOOSE FTG | 2009-10-09 | 2009-11-24 | Other | REMOVED & RESEALED | Steel/Wrought Iron |  | SOLEDAD | DUPLICATE 09-40096-1 ALREADY COMPL.; CLEANED LEAKNG FITTINGS AND RESEALED. SOAP TEST OK; REMOVED LEAKING FITTINGS, RESEALED & REINSTALLED. SOAP TEST OK
4 | 94-00702-1 | 187 | 44.82 | 8 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1994-10-24 | 1994-10-25 | Replace Pipe |  | Steel/Wrought Iron |  | SOLEDAD | REPAIRED 30' SETTING OF 8" PIPE (MP44.82)
| 09-40037-1 | 187 |  | 2 | Transmission |  | Other |  | UNION | Unknown |  | 2009-05-01 | 2010-10-27 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SOLEDAD | TIGHTENED FITTING MORE; FOUND LEAK ON UNION ON LEFT RUN, TIGHTENED UNION UP UP MORE LEAK STOPPED @HRH-55
| 09-40034-1 | 187 |  | 0.25 | Transmission |  | Valves |  |  | Other | DRY DOPE | 2009-05-01 | 2010-10-27 | Other | RESEAL PLUGS | Steel/Wrought Iron |  | SOLEDAD | RESEALED PLUGS; FOUND PLUGS LEAKING ON 1/4" NEEDLE VALVES ON EACH SIDE OF VALVE 40.01- RESEALED PLUGS
| 10-40002-1 | 187 | 35.78 | 0.75 | Transmission |  | Valves | Other |  | Unknown |  | 2010-01-20 | 2010-01-20 | Other | DISSASEMBLE & RESEALED | Steel/Wrought Iron |  | GREENFIELD | REMOVED LEAKING FITTINGS, CLEANED RESEALED & REINSTALLED. SOAP TEST OK
| 09-40045-1 | 187 |  | 0.25 |  |  | Other |  | SENSE LINE FITTINGS | Other | LOOSE FITTING | 2009-05-04 | 2010-10-27 | Other | RESEAL FITTINGS | Steel/Wrought Iron |  | GREENFIELD | RT. RUN SENSE LINES; FOUND FITTINGS LEAKING RERUN SENSE LINES TIGHTENED UP & RESEALED FITTINGS
4 | 95-40001-1 | 187 |  | 8 | Transmission |  | Body of Pipe |  |  | Digin |  | 1995-04-25 | 1995-04-25 | Replace Pipe |  | Steel/Wrought Iron |  | GREENFIELD | REPLACED DAMAGED SECTION OF 8" MAIN 36'
| 09-40042-1 | 187 |  | 0.75 | Transmission |  | Other |  | FITTINGS | Other | DRY DOPE | 2009-05-04 | 2010-10-27 | Other | RESEAL FITTINGS | Steel/Wrought Iron |  | KING CITY | RESEALED FITTINGS; PUT STATION ON BYPASS WITH A TANK & REPAIRED LEAKS ON FITTINGS & REPLACED FISHER H-202 RELIEF. N63.24958, W-121.19534
4 | 10-88002-1 | 310 | 35.88 | 0.75 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Other |  | 2010-10-19 | 2010-10-19 | Mechanical Repair Fitting - Fitting |  |  |  | KING CITY | REPLACED REGULATOR; HPR REG WAS REPLACED
| 09-40012-1 | 310 |  | 8 | Transmission |  | Valves |  |  | Other | VALVE NEEDED GREASE | 2009-02-24 | 2009-03-27 | Other | GREASED VALVES | Steel/Wrought Iron |  | KING CITY | GREASED VALVES. INLET VALVES TO FILTERS. SEE DRAWING 183721 CHANGE 6
| 97-40003-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1997-01-31 | 1997-02-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | KING CITY | REPLACED VALVE STEM & GREASED VALVE
| 09-40021-1 | DFM-25 |  | 6 | Transmission |  | Valves |  |  | Unknown |  | 2009-03-26 | 2009-06-19 | Other | GREASED VALVES | Steel/Wrought Iron |  | KING CITY | GREASED V-2, STOPPED LEAK - NO LEAKS VISUALLY, V-1 WAS SOAP TESTED ALSO NO LEAKS VISUALLY- NO GREASE STEM NO GAS LEAK AT PRESSURE RECORDER SENSING LINES
4 | 11-40005-1 | 187 | 22.82 | 4 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | Construction Defect |  | 2011-05-24 | 2011-05-26 | Replace #TP Main < 50 ft |  | Steel-Other |  | KING CITY | REPLACED 3' OF 4" STEEL ON REG. STATION; SOAP TEST FOR LEAKS. TESTED 4" STL FOR TRANSMISSION LINE WITH MAOP OF 313 @ 1140PSI FOR 1 1/2 HOURS. CHART IS ATTACHED.
| 09-40015-1 | 187 |  | 4 | Transmission |  | Valves |  |  | Other | NEEDED GREASE | 2009-02-27 | 2009-12-04 | Other | GREASED VALVE | Steel/Wrought Iron |  | KING CITY | GREASED BYPASS VALVE; GREASED VALVE, SOAP TEST OKAY
| 09-40048-1 | 187 |  | 0.75 | Transmission |  | Valves |  |  | Unknown |  | 2009-08-06 | 2010-10-05 | Other | LUBE & OPERATE VALVES | Steel/Wrought Iron |  | KING CITY | FOUND VALVES #6,7 LEAKING TODAY, LUBED & OPERATED VALVES MOST OF LEAKS REPAIRED BACK ON 9-20-10 WHEN ROUTINE MAINT. WAS PERFORMED, MADE CORR. TAG TO HAVE STATION UPDATED AND REBUILT.
| 09-40051-1 | 187 |  | 0.75 | Transmission |  | Valves |  |  | Other | DRY LUBE | 2009-05-08 | 2010-11-05 | Other | LUBED VALVES | Steel/Wrought Iron |  | KING CITY | INSTALLED LUBE FITTINGS - LUBED; INSTALLED LUBE FITTINGS & LUBED VALVES. REPLACED D.S. VALVE AND RESEALED FITTING, PAINTED HPR SET, SOAP TEST OK, FOUND HPR SET AND LEFT IT OFF
4 | 97-40006-1 |  |  | 6 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | Digin/Excavation |  | 1997-06-13 | 1997-06-14 | Replace TP Main |  |  |  | KING CITY | REPLACED 28' SECTION OF TRANSMISSION MAIN.
| 09-40139-1 | 187 |  | 2 | Transmission |  | Valves |  |  | Other | NEEDS GREASE | 2009-11-20 | 2011-05-10 | Other | GREASE & OPERATE | Steel/Wrought Iron |  | SAN LUCAS | GREASED & OPERATED, SOAP TEST OK.; GREASED & OPERATED VALVES, SOAP TEST OK
| 00-40006- | 187 | 3.74 | 6 | Transmission |  | Body of Pipe |  |  | Digin |  | 2000-09-24 | 2000-09-25 |  |  | Steel/Wrought Iron |  | SAN ARDO | 10 FT SECTION OF 6" ORDER #8038976 (SEE ORDER FOR STRENGTH TEST) NEW PIPE 6.625" OD 0.188WT X42 ERW
| 09-40141-1 | 187 |  | 2 | Transmission |  | Valves |  |  | Other | NO GREASE | 2009-11-24 | 2011-05-10 | Other | GREASE & OPERATE | Steel/Wrought Iron |  | SAN ARDO | GREASED AND OPERATED, SOAP TEST OK; GREASED AND OPERATED VALVES, SOAP TEST OK
4 | 11-40001-B | 187 | 1.03 | 6 | Transmission >= 20% SMYS |  | Bell Joint |  |  | Digin/Excavation |  | 2011-01-25 | 2011-01-26 | Replace #TP Main < 50 ft |  | Steel-Other |  | SAN ARDO | C/O STRUCK PIPE (4') AND REPLACED W/4' 6" 0.188" W.T. X-42 ERW
7 | 10-81008-1 | 301F | 6.21 | 16 | Transmission >= 20% SMYS | [6 empty] | 2010-10-03 | [5 empty] | MONTEREY
| 09-70034-1 | 301 |  | 0.25 | Transmission |  | Fitting |  |  | Other | DRY DOPE | 2009-02-10 | 2009-11-30 | Other | DOPE THREADS | Steel/Wrought Iron |  | MARINA | AREA MARKED WITH YELLOW X PAINT, SAME AREA; DRY DOPE ON PIPE THREADS; DRY DOPE ON PIPE THREADS
7 | 10-81005-1 | 301F | 5.84 | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-03 | 2010-10-14 | Other |  |  |  | MONTEREY | SS FITTING ON RIGHT RUN REG. PILOT; REPAIRED LK ON RT RAN REG PILOT FITTINGS
7 | 10-81009-1 | BD631 |  | 2 | Transmission >= 20% SMYS |  |  |  |  | Atmospheric Corrosion |  | 2010-10-13 | 2010-10-20 | Other |  |  |  | MONTEREY | RPLCD VLV&TIGHTEND BOLTS; RPLCD RUSTY VLV, TIGHTEN LOOSE BOLTS ON DS VLV
| 09-70492-1 |  |  | 3 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2009-08-21 | 2011-02-02 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | PACIFIC GROVE | TIGHTEN CAP; SOAP TEST FOR LEAK; CREW FOUND FUZZ LEAK ON THREADS @ 3" MUELLER TOP TAP. CREW TIGHTENED CAP. SOIL IN AREA CONTAMINATED BY PREVIOUS GAS STATION. CREW REPLACED SOIL IN BELL HOLE. CREW PLACED REMOVED SOIL IN HAZ-MAT BARRELS
| 09-91203-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2009-10-01 | 2011-03-25 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | PEBBLE BEACH | INSTALLED SS CLAMP W/ ANODE; SOAP TEST FOR LEAKS; CREW FOUND LEAK ON 2" STEEL MAIN. CREW INSTALLED SS CLAMP W/ 5# ANODE. REWRAPPED 2" STEEL MAIN. CLAMP INSTALLED 22' WEST OF 3/4" STL SRVC TO 4149.
| 09-70032-1 |  |  | 0.5 | Transmission |  | Valves |  |  | Other | LOOSE NUT | 2000-02-10 | 2009-11-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MONTEREY | TIGHTENED PACKING NUT; TIGHTENED PACKING NUT
| 10-70056-1 | 1815-02 |  | 12 | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2010-02-22 | 2010-04-11 | Other | GREASE VALVE | Steel/Wrought Iron |  | MONTEREY | PUMPED GREASE INTO VALVES; SOAP TEST FOR LEAKS; CREW GREASED LEAKING VALVES. WHEN COMPLETED, VALVES NO LONGER LEAKED
| 10-70322-1 |  |  | 2 | Distribution Main |  | Valves |  |  | Other | NO GREASE | 2010-10-28 | 2011-12-03 | Other | GREASE & OPERATE VALVE | Steel/Wrought Iron |  | MONTEREY | GREASED AND OPERATED VALVE; GREASED AND OPERATED VALVE. SOAP TEST FOR LEAKS
| 10-70323-1 |  |  | 2 | Distribution Main |  | Plastic Tee Cap |  |  | Construction Defect |  | 2010-10-28 | 2011-01-10 | Replace Plastic Tee Cap - Plastic |  | PE2406 (Yellow or Orange) |  | MONTEREY | REPLACED CAP & RUBBER; SOAP TEST FOR LEAKS; CREW FOUND LEAK ON 2" X 1 1/4" E.F. TEE CAP. CAP HAD NO RUBBER INSIDE CAP. CREW REPLACED CAP W/ NEW RUBBER
| 09-70544-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2009-10-08 | 2011-04-06 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | MONTEREY | INSTALLED SS CLAMP; SOAP TEST FOR LEAKS; CREW FOUND LEAK @ PIT ON 2" STEEL MAIN. INSTALLED CLAMP OVER LEAK. REWRAPPED MAIN. CLAMP INSTALLED 30' S/O SERVICE TEE TO 922 DOVE ST.
7 | 10-81012-1 | DREG5092 | 12 | 2 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-01 | 2010-10-14 | Tighten Cap or Bolt |  |  |  | MONTEREY | REG INLET FRANGE LOOSE??; TIGHTENED LOOSE FLANGE BOLTS ON INLET TO REG & SSFITTINGS ON MONITOR
7 | 10-81013-1 | 1815-02 | 18.47 | 6 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-01 | 2010-10-14 | Other |  |  |  | MONTEREY | NO GAS FOUND; SSFITTINGSS ON RT. RUN REG PILOT FILTER; REPAIRED LK ON T RUN REG ILOT FILTER W/ TAPE AND DOPE; SOAP TEST OK
| 08-70016-1 |  |  | 1.25 | Gathering |  | Other |  | MANIFOLD | Atmospheric Corrosion |  | 2008-02-08 | 2008-02-12 | Other | REPLACE MANIFOLD | Steel/Wrought Iron |  | MONTEREY | HOT CHANGE 4 SERVICES AND CHANGED OUT 4 MM MANIFOLD AND REBUILT REGULATOR SET.
7 | 10-81015-1 | DREG5088 | 0.01 | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-01 | 2010-10-14 | Other |  |  |  | MONTEREY | VARIOUS FITTING ON BOTH RUNS; REPLACED AND TIGHTENED VARIOUS FITTINGS ON BOTH RUNS @ M-10; SOAP TEST OK
7 | 10-81029-1 | 1815-02 |  | 1.25 | Transmission >= 20% SMYS |  |  |  |  | Unknown |  | 2010-10-02 | 2010-10-18 | Other |  |  |  | MONTEREY | GREASED AND OPERATED INLET VALVE#1
| 09-70044-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 2009-02-13 | 2009-04-02 | Other | GREASED VALVE | Steel/Wrought Iron |  | MONTEREY | GREASED ALL VALVES. NO VISUAL LEAKS.
| 09-70089-1 |  |  | 0.75 | Transmission |  | Regulator |  |  | Other |  | 2009-03-26 | 2009-04-01 | Other | REGULATOR | Steel/Wrought Iron |  | MONTEREY | REGULATOR WAS LEAKING ON FITTINGS (3/4") BYPASSED SERVICE AND REPAIRED FITTINGS ON TRANSMISSION SIDE (INLET)
| 09-70087-1 |  |  | 2 | Transmission | DISTRIBUTION MAIN | Valves |  |  | Other |  | 2009-03-26 | 2009-04-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MONTEREY | REPAIRED THREE LEAKS, TWO ON THE INLET MUELLER VALVES, CAPS WERE LOOSE, DOPED BOTH. REPLACED 289 RELIEF VALVE, 1" NIPPLE WAS CROSS-THREADED INSIDE AND LEAKING, REPLACED BOTH
| 09-70087-1 |  |  | 2 | Transmission | DISTRIBUTION MAIN | Valves |  |  | Other |  | 2009-03-26 | 2009-04-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MONTEREY | REPAIRED THREE LEAKS, TWO ON THE INLET MUELLER VALVES, CAPS WERE LOOSE, DOPED BOTH. REPLACED 289 RELIEF VALVE, 1" NIPPLE WAS CROSS-THREADED INSIDE AND LEAKING, REPLACED BOTH
| 09-70088-1 |  |  | 2 | Transmission |  | Valves |  | RELIEF | Other | LOOSE FITTING | 2009-03-26 | 2009-04-01 | Other | TIGHTEN RELIEF VALVE | Steel/Wrought Iron |  | MONTEREY | TIGHTEN UP RELIEF VALVE H-202 LEAK REPAIRED
7 | 10-81006-1 | 301F | 7.32 | 16 | Transmission >= 20% SMYS | [6 empty] | 2010-10-03 | [5 empty] | MONTEREY
7 | 10-81002-1 | 1813-02 | 9.24 | 10 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-03 | 2010-10-09 | Other |  |  |  | MARINA | ON FILTER TO PILOT- TIGHTENED LOOSE FITTING; REPAIRED LEAK ON FILTER TO REG. PILOT SOAP TESTED OK
7 | 10-81004-1 | 301F | 7.94 | 10 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-03 | 2010-10-09 | Tighten Cap/Bolt - Fitting |  |  |  | MONTEREY | LK ON STATIC LINE FOR PILOT; FIXED LK STATIC LINE FOR PILOT, SOAP TEST OK
7 | 10-81007-1 | 1813-02 | 9.42 |  | Transmission >= 20% SMYS | [6 empty] | 2010-10-03 |  |  |  | Steel-Other |  | MONTEREY | BELOW GROUND 3X3 AREA 120 FT FROM NW CO.., LEAK FOUND LOCATED & BAR HOLED
| 09-70033-1 | 1815-02 | 7.96 | 0.75 |  |  | Valves |  |  | Other | LACK OF GREASE | 2009-02-10 | 2009-03-09 | Other | GREASED VALVE | Steel/Wrought Iron |  | MARINA | GREASED BY-PASS VALVE (3/4") SOAP TEST FOR LEAKS
| 01-70135-1 | DFM2 | 12.95 | 4 | Transmission |  | Valves |  |  | Construction Defect |  | 2001-12-21 | 2001-12-21 | Other | FLUSH & GREASE INLET VALVE | TR 418 |  | SEASIDE | ON INLET TIP PRESSURE VALVE TO REG. STATION; GREASED VALVE NO INSPECTION REQUIRED; GREASED AND FLUSHED VALVE READING MINIMAL 1% L.E.L.
| 09-70078-1 | 1813 |  | 4 | Transmission |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2009-03-24 | 2009-03-24 | Replace TP Main | SOAP AND/OR TAPE; WELDED SLEEVE/CAN | Steel/Wrought Iron |  | SEASIDE | REPLACED A 20" SECTION OF 4" PIPE BETWEEN THE 10" MAIN AND THE #2 BRIDLE VALVE AT V 12.95
| 09-70037-1 |  |  | 4 | Transmission |  | Valves |  |  | Other | NEEDS GREASE | 2009-02-10 | 2009-11-30 | Other | GREASED VALVE | Steel/Wrought Iron |  | SEASIDE | GREASED VALVE; GREASED VALVE
7 | 11-70059-A | 1813-02 | 12.95 | 4 |  |  | Body of Pipe |  |  | Other | SAND BLASTING | 2011-04-12 | 2011-04-12 | Welded Sav-A-Valve - Weld |  | Steel-Other |  | SEASIDE | WELDED THREAD-O-LOT OVER HOLE & PLUGGED, SOAP TEST OK; SAND BLASTED POINT... HOLE IN 4" BRIDAL PIPING, WELDED THREAD-O-LOT/SAV-A-VALVE ... HOLE & PLUGGED. SOAP TEST OK
7 | 10-70364-1 | 1 |  | 0.75 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Other |  | 2010-10-18 | 2010-10-18 | Other |  |  |  | MONTEREY | REBUILT STATION-GREASED BYPASS VALVE; REBUILT REG. STATION- GREASED BYPASS VALVE
7 | 10-81031-1 | 1815-02 | 15.83 | 0.75 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Other |  | 2010-10-02 | 2010-10-18 | Other |  |  |  | MONTEREY | REBUILT STA & GREASED BYPASS VALVE; REBUILT REG. STATION AND GREASED AND OPERATED BYPASS VALVE, SOPA TEST OK
| 09-70238-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 2009-05-04 | 2009-06-24 | Other | BLOW-OFF VALVE 'A' | Steel/Wrought Iron |  | MARINA | NO USA VALVES IN FRAME AND COUCV. NO DIGGING INVOLVED..
7 | 10-81036-1 | 1813-06 | 0.02 | 4 | Transmission >= 20% SMYS |  |  |  |  | Unknown |  | 2010-10-13 | 2010-12-21 | Other |  | Steel-Other |  |  | GREASED AND OPERATED VALVE; LUBED VALVES
| 10-70054-1 |  |  | 4 | Transmission |  | Fitting |  |  | Construction Defect |  | 2010-02-16 | 2010-02-17 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MARINA | REDOPED PLUGS AND CAPS ON TWO VALVES; SOAP TEST FOR LEAKS; CREW FOUND LEAKS @ 2 3/4" STL SAVE-A-VALVES ON 4" STL. TRANSMISSION. REMOVED, REDOPED, AND REPLACED 3/4" STL CAPS AND 3/4" BRASS PLUGS. REWRAPPED VALVES
| 09-70064-1 | [10 empty] | 2009-03-11 | [5 empty] | PACIFIC GROVE
| 09-70103-1 |  | 2.13 | 0.375 | Transmission |  | Other |  | STAINLESS FITTINGS | Construction Defect |  | 2009-03-30 | 2009-04-30 | Other | TIGHTEN FITTINGS | Other | STATIC LINES | CARMEL | TIGHTEN VARIOUS S.S. FITTINGS; TIGHTENED VARIOUS FITTINGS AND PLUGS. GREASED 2 VALVES, SOPA TEST FOR LEAKS.
7 | 10-81023-1 | 1815-02 |  | 3 | Transmission >= 20% SMYS |  |  |  |  | Unknown |  | 2010-10-02 | 2010-10-16 | Other |  |  |  | MONTEREY | GREASED VALVE; LUBED V-10 AT REG. STA. MRM29 B/P VALVE
| 09-70239-1 |  |  | 3 | Transmission |  | Valves |  |  | Other |  | 2009-05-04 | 2009-06-23 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MONTEREY
7 | 10-81025-1 | 1815-02 | 14.26 | 2 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-10-02 | 2010-10-16 | Other |  |  |  | MONTEREY | VARIOUS UNIONS & FITTINGS ON RT. RUN; REPAIRED LEAKS ON FITTINGS ON MRM-19 RIGHT RUN
| 01-50090- |  |  | 12 | Transmission |  | Valves |  |  | Other | LACK OF PACKING MATERIAL IN VALVE | 2001-07-10 | 2001-07-24 | Other | ADDED PACKING MATERIAL - REBUILT PACKING EXTENSION | Steel/Wrought Iron |  | MOSS LANDING | LEAK ON 12" VALVE- 22 WAS STOPPED BY ADDING PACKING MATERIAL; REPAIRED GREASE STEM- GREASED VALVE. SOAP TEST VALVE OK
5 | 10-88487-1 | STA PIPE |  | 12 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other |  | 2010-11-09 | 2011-02-10 | Greased - Other |  | Steel-Other |  | MOSS LANDING | GREASED VALVE; GREASED VALVE THAT STOPPED THE LEAK
5 | 10-88488-1 | STA PIPE |  | 12 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other |  | 2010-11-09 | 2011-02-10 | Greased - Other |  | Steel-Other |  | MOSS LANDING | GREASED LEAKING GAS VALVE
5 | 10-50340-1 |  |  | 12 | Transmission >= 20% SMYS |  | Line Valve | Unknown |  | Other |  | 2010-12-28 | 2011-02-10 | Greased - Other |  | Steel-Other |  | CASTROVILLE | GREASED V-22; WE GREASED V-22; SOAP TESTED OK
5 | 10-88529-1 | DREG5408 | 0 | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Unknown |  | 2010-10-26 | 2010-12-15 | Other |  | Steel-Other |  | SALINAS | LUBED AND OPERATED B/P VALVE; LUBED AND OPERATED B/P VALVE#2 @SRS61; SOAP OK
| 94-00124-1 | 301B | 0.73 | 12 | Transmission |  | Body of Pipe |  |  | Digin |  | 1994-10-13 | 1994-10-14 | Replace Pipe |  | Steel/Wrought Iron |  | CASTROVILLE | REPLACED 32' OF 12" STEEL PIPELINE
| 03-50027-1 | 12-301B |  | 0.75 | Transmission >= 20% SMYS |  | Valves |  |  | Other |  | 2003-05-02 | 2003-05-28 | Other | GREASED VALVE | Steel/Wrought Iron |  | CASTROVILLE | GREASED VALVE TO STOP LEAK
| 09-91855-1 |  |  | 0.75 | Single Service |  | Fitting |  |  | Material Failure |  | 2009-11-09 | 2009-12-10 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | CASTROVILLE | CAP LEAK; FOUND CAP LEAK; RE-EXCAVATED COLD MIX PATCH TO MAKE REPAIR OF LEAKING CAP. RECENTLY EXCAVATED BY P.G. & E. CREW
5 | 10-81007-1 | 301B |  | 4 | Transmission >= 20% SMYS |  |  |  |  | Unknown |  | 2010-09-29 | 2010-10-08 | Other |  |  |  | CASTROVILLE | GREASED VALVE "A" @ SVC 12 VALVE STAT
| 09-50108-1 | 301A |  | 0.75 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 2009-04-27 | 2009-07-23 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | PRUNDALE | DOPED AND TIGHTEN CAP; CLEAN, DOPE AND TIGHTENED CAP ON PIN-OFF TEE SUPPLYING FIRE VALVE V-1
5 | 89-00223-1 |  |  | 20 | Transmission |  | Tap Connection |  |  | Other |  | 1989-09-25 | 1990-10-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | PRUNDALE | FOUND CAP OF THE SERVICE TEE LEAKING. TIGHTENED CAP
|  | 301A |  | 0.75 | Distribution Main |  | Tap Connection |  |  | Other |  | 1990-09-14 | 1990-10-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | CASTROVILLE | FOUND THE CAP ON SERVICE TEE LEAKING. TIGHTENED CAP
5 | 89-00225-1 |  |  | 12 | Transmission |  | Tap Connection |  |  | Other |  | 1989-09-25 | 1990-10-04 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MOSS LANDING | TIGHTENED & REDOPED SERVICE TEE CAP AT VALVE # 6 COULD NOT LOCATE THE LEAK NEAR VALVE #7. GREASE LEAK
| 90-00127-1 |  |  | 2 | Transmission |  | Fitting |  |  | Other |  | 1990-09-12 | 1990-10-04 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | CASTROVILLE | LEAKING CAP NEAR V6 TIGHTENED CAP. COULD NOT LOCATE THE LEAK NEWAR V7/ GRADE 3 LEAK
| 09-50110-1 | 301B | 390 | 0.75 | Distribution Main |  | Valves |  |  | Construction Defect |  | 2009-04-27 | 2010-09-29 | Other | GREASED VALVE ALL OK | Steel/Wrought Iron |  | PRUNDALE | GREASED VALVE; GREASED VALVE. SOAP TEST OK
| 09-50111-1 |  |  | 1.25 | Transmission |  | Valves |  |  | Other |  | 2009-04-27 | 2009-06-23 | Other | GREASED VALVE | Steel/Wrought Iron |  | PRUNDALE | INLET VALVE LEAKING GREASED VALVE
5 | 11-50081-B | 301A | 51.22 | 0.75 | Transmission >= 20% SMYS |  | Threads |  |  | Other |  | 2011-05-21 | 2011-05-21 | Other | TIGHTEN GREASE STEM | Steel-Other |  | PRUNDALE | TIGHTEN GREASE STEM
| 09-50432-1 |  |  | 2 | Distribution Main |  | Plastic Tee Cap |  |  | Construction Defect |  | 2009-10-22 | 2011-04-21 | Replace Plastic Tee Cap - Plastic |  | Aldyl A (Tan or Gray) |  | PRUNEDALE | INSTALLED PLASTIC TEE CAP REPAIR KIT; INSTALLED PLASTIC TEE CAP REPAIR KIT. SOAP TEST OK
| 09-50213-1 |  |  | 0.5 | Transmission |  | Clamp |  |  | Unknown |  | 2009-08-01 | 2009-10-23 | Other | CUT & RETHREAD | Steel/Wrought Iron |  | SALINAS | PIPE CUT AND RETHREADED, SOAP TEST OK
| 09-50005-1 | 3017 | 0.03 | 06.00-11.00 | Transmission |  | Valves |  |  | Unknown |  | 2009-01-13 | 2009-03-18 | Other | WHEEL VALVE | Steel/Wrought Iron |  | SALINAS | WHEEL VALVE; WHEEL VALVE WAS LEAKING, GREASED BY HAND PUMP STOPPED LEAKING. SKINNER CLAMP ON GREASE FITTING EXTENSION WAS LOOSE AND LEAKING BY, TIGHTEN CLAMP, STOPPED LEAK
5 | 87-00189-1 |  |  | 12 | Transmission >= 20% SMYS |  |  |  |  | Construction Defect |  | 1987-09-29 | 1988-04-15 | Tighten Cap/Bolt - Fitting |  |  |  | SALINAS
| 10-50004-1 | 301F |  | 3 | Transmission |  | Valves | Other | UNION | Other | LOOSE FITTING | 2010-01-04 | 2011-04-27 | Other | GREASE & OPERATE | Steel/Wrought Iron |  | SALINAS | GREASED AND OPERATED VALVES, TIGHTENED UNIONS SOAP TEST. ; TIGHTENED LOOSE UNION AND GREASED OPERATED VALVE. SOAP TEST OK. SRS-73
| 09-50006-1 | 6 D7M | 2.3 | 0.75 | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-01-13 | 2009-03-18 | Other | H-202 RELIEF VALVE. | Steel/Wrought Iron |  | SAL | RELIEF VALVE WAS WEEPING GAS, RE-ADJUSTED PRESS. TO STOP GAS FROM LEAKING DYE
5 | 97-00042-1 | 301B | 5.14 | 12.75 | Transmission |  | Body of Pipe |  |  | Digin |  | 1997-06-19 | 1997-06-20 | Replace Pipe |  | Steel/Wrought Iron |  | CASTROVILLE | REPLACED 60" SECTION OF TRANSMISSION MAIN.
| 10-50194-1 | 301B | 6 | 12 | Transmission |  | Body of Pipe |  |  |  |  | 2010-10-02 | 2010-10-03 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | CLOSE 2 VALVES BLOW DOWN PIPE. REPLACE 3/ SECTION OF PIPE.; JASON BRUN. TESTED PIPE 10/2/05; FARMER WAS RIPPING FIELD AND STRUCK A 12" TRANSMISSION LINE. OPERATOR WWAS TOLD NOT TO RIP ...GAS LINE AND DID NOT ...RIPPER ON LEAST PASS.
| 09-50425-1 | 301B |  | 12 | Transmission |  | Body of Pipe |  |  |  |  | 2009-10-23 | 2009-10-23 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | FARMER WAS RIPPING FIELD AND STRUCK A 12" STEEL TRANSMISSION LINE, CAUSING A HOLE 2" X 2/12"
| 02-50086- | 301B | 6.94 | 12 | Transmission |  | Body of Pipe |  |  | Digin |  | 2002-06-03 | 2002-06-04 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | REPLACED 15FT OF PIPE W/ PRETESTED .375" GR. B. SMLS;
| 10-50165-1 | 301B | 7.5 | 12 | Transmission |  | Body of Pipe |  |  |  |  | 2010-08-28 | 2010-08-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SALINAS | REPAIR SLEEVE WELDED OVER HOLE; REPAIR SLEEVE WELDED OVER DAMAGE. WELD WAS X-RAYED AND MAGNETIC PARTICLE TESTED SOAP TEST OK
| 10-50198-1 | 301B | 7.9 | 0.75 | Transmission |  | Valves |  |  | Unknown |  | 2010-10-08 | 2011-01-03 | Other | GREASED VALVE | Steel/Wrought Iron |  | SALINAS | LUBE AND OPERATE; GREASED AND OPERATED VALVE. SOAP TEST OK.
| 02-50026-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Construction Defect |  | 2002-03-05 | 2010-12-17 | Patch Welded |  | Steel/Wrought Iron |  | SALINAS | WELD OVER PINHOLE ON MAIN.; WELD OVER PIN HOLE BELOW BASE OF MUELLER TEE. SOAP TEST OK.
5 | 10-88001-1 | 103 |  |  | Transmission >= 20% SMYS |  |  |  |  | Construction Defect |  | 2010-10-15 | 2010-11-04 | Other |  |  |  | SALINAS | REPLACED TAP VALVE AND D/S VALVE; REPAIRED LEAKS ON HPR SET. SOAP TEST OK
| 05-50089-1 | 103 |  |  | Transmission |  | Body of Pipe |  |  |  |  | 2005-11-19 | 2005-11-20 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | SEE ATTACHED TEST DATA
5 | 90-00105-1 |  |  | 12 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 1990-05-08 | 1990-05-10 | Other |  |  |  | SALINAS | TIGHTEN BOLTS ON BLOW OFF STACK
| 99-00037-1 |  |  | 0 | Transmission |  | Fitting | Valves |  | Material Failure |  | 1999-05-05 | 2000-11-08 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | SALINAS | REPLACE 1" NIPPLE AND GREASE VALVE.
| 09-50141-1 | 103 |  | 8 | Transmission |  | Valves |  |  | Other | VALVE SEAL | 2009-05-23 | 2009-11-20 | Other | GREASED VALVE | Steel/Wrought Iron |  | SALINAS | FOUND V-1 TIGHTENS ... GREEN; GREASED AND LUBED VALVES IN PIT. SEE ATTACHED MAP
| 09-50142-1 | 103 | 23.55 | 0.75 | Transmission |  | Valves |  |  | Other | LOOSE FITTING | 2009-05-23 | 2009-07-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAL | REPAIRED LEAKS AT POWER GAS BANKS
| 10-50070-1 | 1881-01 | 2.74 | 2 | Transmission |  | Valves |  |  | Other | NO GREASE | 2010-03-18 | 2010-03-18 | Other | GREASED VALVE | Steel/Wrought Iron |  | SALINAS | VALVE LEAKING FROM GREASED STEM, GREASED VALVE SOAP TEST OK
| 09-50165-1 | 103 | 23.55 | 6 | Transmission |  | Valves |  |  | Other | PACKING LEAK | 2009-07-06 | 2009-10-02 | Other | REPLACED PACKING | Steel/Wrought Iron |  | SALINAS | LEAKING OUT OF PACKING, ON VALVE 3
| 04-50007-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 2004-01-29 | 2004-01-29 | Service Partially Replaced |  | Aldyl A (Tan or Gray) |  | SALINAS | SQUEEZED PIPE REPLACED DAMAGED SECTION, SOAP TEST OK.; LEAK NO 04-50007-1
| 09-50536- | DFM18 | 2.74 | 4 | Transmission |  |  |  |  | Other |  | 2009-11-19 | 2009-11-19 | Fill Weld - Weld |  | Steel/Wrought Iron |  | SALINAS | REWELDED LAKING GAUGE NIPPLE ON 4" TP MAIN SOAP TEST OK.
| 10-50173-1 | 301B | 55 | 0.75 | Transmission |  | Fitting |  |  | Other |  | 2010-09-30 | 2010-12-09 | Soap and/or Tape - Other |  | Steel/Wrought Iron |  | SALINAS | REPAIRED THE LEAKS, SOAP TESTED OK
| 09-92027-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2009-10-27 | 2011-04-25 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | SALINAS | INSTALLED SKINNER LEAK REPAIR CLAMP OVER PITT; INSTALLED SKINNER CLAMP OVER PIT IN 4" MAIN/ SOAP TEST OK
5 | 09-91994-1 |  |  | 2 | Distribution Main >60 PSIG and <20% SYMS |  |  |  |  | Other |  | 2009-10-27 | 2011-03-17 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SALINAS | REMOVED CAP/CLEANED AND REDOPED CAP, CLEANED CAP/DOPE AND TIGHTEN CAP- INSTALLED VALVE ON SERVICE TO 930, INSTALLED NEW PLASTIC TO INSTALL EFV, SERVICE TO 930 SIERRA MADRE
| 05-50031-1 | 301B |  | 6 | Transmission |  | Valves |  |  | Other | NEEDED GREASE | 2005-04-21 | 2006-05-26 |  |  | Steel/Wrought Iron |  | SALINAS | GREASE VALVE; SOAP TESTED VALVE
| 10-50204-1 | 301E | 0.89 | 12 | Transmission |  | Valves |  |  | Other | DRY STEAM PACKING | 2010-10-13 | 2010-10-21 | Other | ADDED 909 STEAM PACKING, LUBED & OPERATE VALVE | Steel/Wrought Iron |  | SALINAS | ADDED 909 STEM PACKING- GOOD.; FOUND VALVE #1 LEAKING OUT STEM- WITH CAMBELL VALVE COMPANY WE PACKED STEM WITH 909 STEM PACK MATERIAL LUBED AND OPERATED VALVE FEW TIMES AND ADJUSTED BONNET WORKS. GOOD NOW NO LEAKS
5 | 10-81026-1 | 301E |  | 3 | Transmission >= 20% SMYS |  |  |  |  | Unknown |  | 2010-10-02 | 2010-10-09 | Other |  |  |  | SALINAS | GREASED VALVE
| 09-50557-1 | MTY-1 | 57 | 12 | Transmission |  | Unknown |  |  | Unknown |  | 2009-12-16 | 2010-01-13 | Other | GREASED VALVE | Steel/Wrought Iron |  | SALINAS | GREASED VALVE 4.08;
| 09-50137-1 | 103 |  | 12 | Transmission |  | Valves |  |  | Other | VALVE SOC | 2009-05-23 | 2009-11-20 | Other | GREASED VALVES | Steel/Wrought Iron |  | SALINAS
| 10-50200-1 | 103 | 0.66 | 0.75 | Transmission |  | Other |  | RELIEF | Unknown |  | 2010-10-08 | 2011-01-03 | Other | RELIEF | Steel/Wrought Iron |  | SALINAS | REPLACE RELIEF; REPLACED H-202 RELIEF. CHECK LOCK UP, SET PRESS @ 40#, SOAP TEST OK
5 | 10-50301-1 | 1 |  | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Unknown |  | 2010-10-19 | 2010-10-19 | Other |  |  |  | SALINAS | GREASED AND OPERATED VALVE; LUBE AND OPERATED INLET FV TO SRS-13
5 | 10-88004-1 | DREG5416 |  | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Unknown |  | 2010-10-15 | 2010-10-19 | Greased - Other |  | Steel-Other |  | SALINAS | GREASED AND OPERATED VALVE
| 08-50094-1 | 301C | 2.3 | 0.75 | Transmission |  | Other |  | RELIEF VALVE | Equipment Malfunction |  | 2008-11-21 | 2009-02-20 | Other | RELIEF VALVE | Steel/Wrought Iron |  | SALINAS | REPLACED RELIEF VALVE H-202. OLD RELIEF WAS LEAKING
| 10-50166-1 | 187 |  | 0.75 | Transmission |  |  |  |  | Other | PIPE DOPE | 2010-09-02 | 2010-09-02 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SALINAS | REMOVE CAP/ CLEAN THREADS/ DOPE AND INSTALLED; REMOVED CAP ON PIN-OFF TEE. CLEANED THREADS AND DOPED AND RE-INSTALLED CAP.
5 | 10-81034-1 | 103 | 27.72 | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-10-13 | 2010-10-20 | Mechanical Repair Fitting - Fitting |  |  |  | SALINAS | CLEANED THE LINE AND REPAIRED THE LEAKS; REPAIRED LEAK & SOAP TEST
5 | 10-81037-1 | 301C | 17.26 | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-13 | 2010-10-18 | Mechanical Repair Fitting - Fitting |  |  |  | SALINAS | REPAIRED MULTIPLE LEAKS; B/P THE POWER GAS SUPPLY & REPAIRED LEAKS
5 | 10-88026-1 | 187 | 65.69 | 6 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Other |  | 2010-11-09 | 2011-01-24 | Other |  | Steel-Other |  | SALINAS | TIGHTENED FITTING
| 03-50075-1 | 301C | 17.26 | 8 | Transmission |  | Valves |  |  | Other | BROKEN POSITIONER COVER | 2003-09-02 | 2003-11-26 | Other | REPLACED BROKEN POSITIONER COVER | Steel/Wrought Iron |  | SALINAS | ...POSTION COVER INSIDE REG. PITS.
| 09-50114-1 | 187 |  | 0.75 | Transmission |  | Valves |  |  | Other | BAD O-RINGS | 2009-04-28 | 2010-09-01 | Other | REPLACE & LUBE ORINGS | Steel/Wrought Iron |  | SALINAS | REPAIRED GAS LEAKS ON VALVE TES FOR SCADA LINES. REPLACED OLD DRY ORINGS IN MULLER TEES
| 09-50139-1 | 103 | 0 | 6 | Transmission |  | Fitting |  |  | Construction Defect |  | 2009-05-23 | 2009-07-17 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SALINAS | TIGHTEN LOOSE FITTING; CLEAN AND RE-TIGHTEN COMPLETION CAP, SOAP TEST OK
5 | 96-00046-1 |  |  | 12 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 1996-07-15 | 1997-05-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SPRECKELS | REPLACE BOLTS AND TIGHTEN CAP
| 09-50072-1 | 187 | 62 | 8 | Transmission |  | Body of Pipe |  |  |  |  | 2009-04-03 | 2009-04-04 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | SHUT VALVE AT TWP LOCATIONS. CUT OUT DAMAGED PIPE AND REPLACED; TEST DATA ATTCHED 21' OF PIPE REPLACED. WELDS XRAY TESTED OK AND SOAP TEST OK
| 10-50189-1 | 187 |  | 0.75 | Transmission |  | Fitting | Mechanical Joint | REGULATOR, OTHER | Other |  | 2010-10-01 | 2010-12-23 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | SALINAS | REBUILT THE HPR SET. SOAP TEST OK
| 09-50115-1 | 187 |  | 0.75 | Transmission |  | Other |  | LUBE FITTING | Other | DRY DOPE | 2009-04-30 | 2010-09-17 | Other | LUBE FITTING | Steel/Wrought Iron |  | SALINAS | LUBE FITTING GETTING ON VALVE 2; LUBE VALVE #2 AND REDOPPED LUBE FITTING @ VALVE STATION
5 | 95-00006-1 | 187 | 61.91 | 8.62 | Transmission |  | Tap Connection |  |  | Digin |  | 1995-05-20 | 1995-05-20 | Replace Pipe |  | Steel/Wrought Iron |  | SALINAS | TEMPORARY REPAIR OF MUELLER FITTING OVER LEAK. PERMANENT REPAIR BY REPLACING DAMAGED PORTION OF MAIN
| 01-50109-1 | 187 | 61.35 | 8 | Transmission |  | Body of Pipe |  |  | Digin |  | 2001-08-30 | 2001-08-31 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | INSTALLED 3FT OF 8" GR. B. SEAMLESS .322" W.T.
| 01-50110-1 | 187 | 61.25 | 8 | Transmission |  | Body of Pipe |  |  | Digin |  | 2001-08-31 | 2001-08-31 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | WHILE REPAIRING DIGIN @ MP61.35 GC GAS DAMAGED PIPE @ 61.25; PRETESTED PIPE SEE ATTACHED
| 09-50333-1 | 187 | 60.17 | 0.75 | Transmission |  | Valves |  |  | Other | LUBE FITTING | 2009-10-09 | 2010-01-06 | Other | GREASED VALVES | Steel/Wrought Iron |  | SALINAS | FOUND FEW SMALL LEAKS AT VALVE SITE SVQ-12. GREASED VALVES
| 98-00059- | 187 | 58.48 | 8 | Transmission |  | Body of Pipe |  |  | Digin |  | 1998-09-05 | 1998-09-06 | Replace Pipe |  | Steel/Wrought Iron |  | CHUALAR | REPLACE 80FT OF 8" MAIN
| 09-50492-1 | DFM |  | 1.5 | Transmission |  | Bell Joint |  |  | Other | DRIED PIPE DOPE | 2009-11-02 | 2011-04-27 | Other | RE-DOPE & TIGHTEN. | Steel/Wrought Iron |  | SALINAS | REMOVED NIPPLE, RE-DOPED AND TIGHTENED. SOAP TEST OK
| 09-50493-1 | DFM |  | 0.75 | Transmission |  | Mechanical Joint |  |  | Other | LOOSE UNION | 2009-11-02 | 2011-04-27 | Other | TIGHTEN LOOSE UNION | Steel/Wrought Iron |  | SAL | TIGHTENED LOOSE UNION FITTINGS, SOAP TEST OK
5 | 10-81030-1 | 1815-02 |  | 0.75 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-02 | 2010-10-09 | Other |  |  |  | SALINAS | TIGHTENED UNION
5 | 10-81015-1 | DREG5078 | 0.01 | 4 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-09-30 | 2010-11-15 | Other |  |  |  | SALINAS | DRY O RINGS ON FILTER RESEALED
5 | 10-81011-1 | DREG8583 |  | 2 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-01 | 2010-10-09 | Other |  |  |  | SALINAS | GREASED VALVE
| 10-50197-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Unknown |  | 2010-10-02 | 2010-12-27 | Other | LUBE & OPERATE | Steel/Wrought Iron |  | SALINAS | INSTALLED LUBE FITTINGS AND OPERATED.; INSTALLED LUBE FITTINGS ON INLET & BYPASS VALVES LUBED AND OPERATED VALVES, REPAIRED LEAKS SOAP TEST OK
| 11-50035-1 |  |  | 0.75 |  |  | Line Valve |  |  | Other |  | 2011-03-18 | 2011-03-18 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SALINAS | REPAIRED THE LEAK ON A PIN-OFF TEE; REPAIRED LEAK ON PIN-OFF TEE AT A SINGLE CUSTOMER HPR SET. SOAP TEST OK.
| 11-50035-8 |  |  | 0.75 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other |  | 2011-03-18 | 2011-03-18 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SALINAS | REPAIRED THE LEAK ON A PIN-OFF TEE; REPAIRED LEAK ON PIN OFF TEE AT A SINGLE CUSTOMER HPR SET. SOAP TEST OK
| 11-50029-1 | 1815-02 | 8.09 | 2 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other |  | 2011-03-17 | 2011-03-17 | Tighten Cap/Bolt - Fitting | GREASED - OTHER | Steel-Other |  | SALINAS | GREASE THE FIRE VALVE AND TIGHTEN THE PACKING ON PIT VALVE
| 06-50004-1 | MTY #2 | 7.95 | 0.75 | Transmission |  | Other Welds |  |  | Construction Defect |  | 2006-02-01 | 2006-02-01 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | CUT-OUT 3/4" 90" SOCKET AND REPLACED. PIPE AND FITTINGS PRETEST OK.; THIS LEAK WAS FOUND DURING EXCAVATION TO INSPECT A FIRE VALVE. ALL PIPE AND FITTINGS WERE PRE-TESTED ON 1-31-06
| 09-50128-1 | 187 |  | 0.75 | Transmission |  | Valves |  |  | Other | DRY LUBE | 2009-05-08 | 2010-11-05 | Other | LUBED VALVE | Steel/Wrought Iron |  | CHUALAR | INSTALLED LUBE FITTING- LUBED; INSTALLED LUBE FITTINGS IN INLET VALVE AND BYPASS VALVE AND LUBED VALVES, PRINTED HPR, SOAP TEST OK
5 | 10-50302-1 | 187 |  | 4 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-09 | 2010-10-09 | Other |  |  |  | GONZALES | GREASED VALVE; GREASED VALVE-SOAP TEST
5 | 10-81005-1 | 187 |  | 4 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-09-29 | 2010-10-09 | Greased - Other |  |  |  | GONZALES | GREASED VALVE
5 | 10-81006-1 | 187 |  | 4 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-09-29 | 2010-10-09 | Other |  |  |  | GONZALES | GREASED VALVE, ON VALVES
5 | 10-81035-1 | DREG5180 | 0.15 | 0.75 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-13 | 2010-10-20 | Other |  |  |  | GONZALES | REPLACED REG AND RELIEF FITTINGS; REPLACED REG & RELIEF FITTINGS ON 2 SVC HPR
| 09-50119-1 | 187 | 60 | 4 | Transmission |  | Valves |  |  | Unknown |  | 2009-04-01 | 2010-10-05 | Other | LUBE & OPERATE VALVE | Steel/Wrought Iron |  | SOLEDAD | LUBED AND OPERATED BYPASS VALVE @ DIST. REG. STATION SRT-18, VALVE BURIED AND IN G-5 BOX, PAINTED RED
5 | 10-81001-1 | 187 |  | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-09-29 | 2010-10-12 | Other |  |  |  | SOLEDAD | INSTALLED LUBE FITTINGS ON INLET AND B/P VALVE; INSTALL LUBE FITTINGS ON INLET AND B/P. LUBED AND OPERATED
| 09-50425-1 | 301B |  | 12 | Transmission |  | Body of Pipe |  |  |  |  | 2009-10-23 | 2009-10-23 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | SHUT DOWN APPROX 8 MILE SECTION OF PIPE W/VALVES.; FARMER WAS RIPPING FIELD AND STRUCK A 12" STEEL TRANSMISSION LINE, CAUSING A HOLE 2 X 2 1/2".
| 09-50426-1 | 301-G | 16.82 | 0.75 | Distribution Main |  | Valves |  |  | Other | THREADS | 2009-10-27 | 2010-01-14 | Other | REPLACED VALVE & TIGHTENED UNION | Steel/Wrought Iron |  | PRUNEDALE | SRS-76 HIGH TO HIGH SET; LEAK AT HIGH TO HIGH SET SRS (76); REPLACED BYPASS VALVE & TIGHTEN UNION; HOT TANKED MAIN & REPLACED BYPASS VALVE & REPAIRED UNION
| 09-50427-1 | 301-A | 19.47 | 0.75 | Distribution Main |  | Other |  | UNION | Other | LOOSE FITTING | 2009-10-27 | 2010-01-08 | Other | UNION | Steel/Wrought Iron |  | PRUNEDALE | SRS-57; LEAK ON UNION HI TO HI SET; TIGHTENED UNION FITTING; LEAK ON UNION REPAIRED BY TIGHTEN
| 09-50491-1 | D7M | [9 empty] | 2009-11-02 | [5 empty] | SALINAS | LEAK ON FILTER & PLAN REF; MARK YELLOW, NO LEAK FOUND;
| 09-50492-1 | D7M |  | 1.5 | Transmission |  | Bell Joint |  |  | Other | DRIED PIPE DOPE | 2009-11-02 | 2011-04-27 | Other | RE-DOPE & TIGHTEN | Steel/Wrought Iron |  | SALINAS | H2H SET 2%; YELLOW PAINT ON REG; REMOVED NIPPLE, RE-DOPED & TIGHTENED. SOAP TEST OK
| 09-50493-1 | D7M |  | 0.75 | Transmission |  | Mechanical Joint |  |  | Other | LOOSE UNION | 2009-11-02 | 2011-04-27 | Other | TIGHTEN LOOSE UNION | Steel/Wrought Iron |  | SALINAS | H2H SET 2%; YELLOW PAINT ON ELBOW; TIGHTENED LOOSE UNION FITTING, SOAP TEST OK
5 | 09-50528-1 | 301A |  | 0.75 | Single Service |  | Fitting |  |  | Other |  | 2009-11-17 | 2011-05-18 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | PRUNDALE | 90-B DESMOND RD.; LEAK AT HIGH TO HIGH SET; YELLOW PAINT; TIGHTEN FITTINGS, REDOPE THREADS
| 09-50536 | DFM18 | 2.74 | 4 | Transmission |  | Other Welds |  |  | Other |  | 2009-11-19 | 2009-11-19 | Fill Weld - Weld |  | Steel/Wrought Iron |  | SALINAS | BLOW BOX NIPPLE OFF MAIN (WELD); RE-WELD LEAKING GAUGE NIPPLE ON Y" TP MAIN SOAP TEST OK
| 09-50557-1 | MTY-1 | 57 | 12 | Transmission |  | Unknown |  |  | Unknown |  | 2009-12-16 | 2010-01-13 | Other | GREASED VALVE | Steel/Wrought Iron |  | SALINAS | 4.08 VALVE PIT SVQ-53; LEAK AT VALVE 4.08 PIT; GREASED VALVE 4.08
| 09-50557-1 | MTY 1 | [9 empty] | 2009-12-16 | [5 empty] | SALINAS | J - 4.08; PIT VALVE
| 09-50558-1 | MTY 1 | [9 empty] | 2009-12-16 | [5 empty] | SALINAS | S-83; PITI NO NO LEAK
| 09-50558-1 | MTY-1 | [9 empty] | 2009-12-16 | [5 empty] | SALINAS | PIT SRS-83; LEAK AT PIT SR-83
5 | 84-00121-1 |  |  | 12 | Transmission |  | Longitudinal Weld |  |  | Construction Defect |  | 1984-05-15 | 1985-04-12 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SALINAS | LEAK FOUND IN WELD. SEE W044750 COMPL'D 4/12/85
5 | 85-00132-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1985-06-17 | 1985-06-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | 3/4" SERVICE ON ... BY CAT-PLOW
5 | 85-00133-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1985-06-18 | 1985-06-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | MONTEREY | 3/4" STL SERV OF 8" TERM IS CUT ON BACK RIGHT SIDE
| 09-50209-1 |  |  | 0.75 | Single Service |  | Tap Connection |  |  | Construction Defect |  | 2009-08-01 | 2009-09-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SALINAS | 5% OVER MAIN; YELLOW PAINT; DOPE & TIGHTEN CAP; DOPE & TIGHTEN CAP ON SERVICE TEE TO 413 ESPINOZA RD SOAP TEST, OK.
| 09-50212-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Other | NO LEAK FOUND | 2009-08-01 | 2010-12-01 | Other |  | Steel/Wrought Iron |  | SALINAS | S/COCK TRANS, FISHER NIPPLE ON HIGH SIDE OF AL; SAME AREA, NO LEAK FOUND; NO LEAK FOUND; 1 SOAP TESTED O.K.
| 09-50213-1 |  |  | 0.5 | Transmission |  | Clamp |  |  | Unknown |  | 2009-08-01 | 2009-10-23 | Other | CUT & RETHREAD | Steel/Wrought Iron |  | SALINAS | 5% 3017 & OTHER VALVE, 4-05 VALVE STATION; PIPE CUT & RETHREADED, SOAP TEST OK.
| 09-50214-1 | 103 | [9 empty] | 2009-08-01 | [5 empty] | SALINAS | H2H SET LEAK UNION & S/COCK (VALVE); MARK YELLOW, SEE ABOVE NO LEAKS FOUND @ HPR SET
| 09-10428-1 | [10 empty] | 2009-10-05 | [5 empty] | SANTA CRUZ | J10 HPR SET
| 09-10431-1 |  |  | 1.25 | Single Service |  | Other |  | CRACKED CAP | Construction Defect |  | 2009-10-05 | 2010-08-11 | Other | REPLACED STEEL CAP | Steel/Wrought Iron |  | SANTA CRUZ | SERVICE TEE AT TP MAIN; LEAK MIGRATING; REPLACED CAP TO PIN OFF TEE; REPLACED 1.25 CAP TO PIN OFF TEE SOAP TEST AND WRAPPED
| 09-10431-1 |  |  | 1.25 | Single Service |  | Other |  | CRACKED CAP | Construction Defect |  | 2009-10-05 | 2010-08-11 | Other | REPLACED STEEL CAP | Steel/Wrought Iron |  | SANTA CRUZ | SERVICE TEE AT TP MAIN; LEAK MIGRATING; REPLACED CAP TO PIN OFF TEE; REPLACED 1.25 CAP TO PIN OFF TEE SOAP TEST AND WRAPPED
| 09-10432-1 | [10 empty] | 2009-10-05 | [5 empty] | SANTA CRUZ | BUS STOP IN PATCH
| 09-50332-1 | 187 | [9 empty] | 2009-10-09 | [5 empty] | SALINAS | 1% ON VALVE IN BACK OF FENCE; READ ABORT, SOAP TEST NO LEAK
| 09-50333-1 | 187 | 0.17 | 0.75 | Transmission |  | Valves |  |  | Other | LUBE FITTING | 2009-10-09 | 2010-01-06 | Other | GREASED VALVES | Steel/Wrought Iron |  | SALINAS | ALL VALVE LEAKING VALVE WITH X YELLOW 10%; FOUND FEW SMALL LEAKS AT VALVE SITE SVQ-12 GREASER VALVES
| 09-50367-1 | 6 D7M | 16.95 | 0.75 | Distribution Main |  | Other |  | UNION | Other | THREADS LEAK | 2009-10-21 | 2010-01-13 | Other | REPLACED D.S. UNION | Steel/Wrought Iron |  | PRUNDALE | VALVE IN STREET & H2H SET; PAINTED YELLOW; REPLACED UNION; REPLACED D.S. UNION, SHUT DOWN MAIN & BAGGED 2 - CUST, SHUT OFF ONE - DOG & GATE
5 | 81-00111-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1981-03-25 | 1981-03-25 | Other |  | Plastic |  |  | ILLEGIBLE DUE TO FADING
5 | 79-00422-1 |  |  | 8 | Transmission | [6 empty] | 1979-07-16 |  |  |  | Steel/Wrought Iron |  | SALINAS | SEE #8100128
| 79-422 | [16 empty] | SALINAS | PICKED UP READING ON LEAK INDICATOR S/END OF HARKINS RD. METER STA. NEAR V-65.70; FOR REF ONLY
76 | 10-10478-1 | DFM3 | 3.65 | 0.75 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other |  | 2010-12-10 | 2010-12-10 | Greased - Other |  | Steel-Other |  | SANTA CRUZ | FAIR & INGAUS; ON GAS - GREASE VALVE (GREASED LEAKING); GREASED VALVE
| 10-10483-1 | DFM-3 | 7.82 | 0.75 |  |  | Fitting |  |  | Weld Failure | DRY DOPE | 2010-12-20 | 2011-03-14 | Fill Weld - Weld | OTHER-REDOPE & TIGHTEN NIPPLE | Steel/Wrought Iron |  | SANTA CRUZ | ABOUT INLET VALVE ON HPR.; SOAP TEST OK
| 10-10228-1 | [10 empty] | 2010-04-22 | [5 empty] | DAVENPORT | HIGH TO HIGH SET ON RISER; REPAIRED 6/07/2010; LEAK ARE?
76 | 10-10478-1 | DFM3 | 3.65 | 0.75 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other |  | 2010-12-10 | 2010-12-10 | Greased - Other |  | Steel-Other |  | SANTA CRUZ | FAIR & INGAUS; ON GAS - GREASE VALVE (GREASED LEAKING); GREASED VALVE
1 | 10-10478-A | DFM3 | 3.65 | 0.75 |  |  | Line Valve |  |  | Other |  | 2010-12-10 | 2010-12-10 | Greased - Other |  | Steel-Other |  | SANTA CRUZ | LEAK ON GREASE STEM ON VALVE; GREASE STEM; GREASED & OPERATED VALVE, SOAP TEST OK; GREASED & OPERATED LEAKING VALVE, SOAP TEST OK
| 09-90387-1 |  |  | 0.75 | Gathering |  | Riser | Threads |  | Other | PIPE DOPE | 2009-08-12 | 2009-11-04 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | SANTA CRUZ | COMPLETE UPON ARRIVAL
| 09-90620-1 |  |  | 0.75 | Gathering |  | Fitting |  |  | Other | NO DOPE | 2009-08-31 | 2009-11-19 | Other |  | Steel/Wrought Iron |  | WATSONVILLE | REPLUMBED & REDOPED FITTINGS; REPLUMBED & REDOPED FITTINGS SOAP TESTED;
| 09-10367-1 |  |  | 3 | Distribution Main |  | Valves |  |  | Equipment Malfunction |  | 2009-08-27 | 2009-08-31 | Other |  | Steel/Wrought Iron |  | SCOTTS VALLEY | 902 LOCKWOOD LN.; AT GAS VALVE REG PIT; SAME AREA; GREASED VALVE;
| 09-90161-1 | [10 empty] | 2009-08-05 | [5 empty] | SCOTTS VALLEY | RISER THREADS; RISER THREADS
| 09-10367-1 |  |  | 3 | Distribution Main |  | Valves |  |  | Other | GREASE FITTING PLUGGED | 2009-08-27 | 2009-08-31 | Other | GREASED VALVE | Steel/Wrought Iron |  | SCOTTSVALLEY | VALVE NEAR REG PIT; AT VALVE; ON MAIN VALVE GREASED; NOTHING WAS REPLACED
| 09-10367-1 |  |  | 3 | Distribution Main |  | Valves |  |  | Equipment Malfunction |  | 2009-08-27 | 2009-08-31 | Other | GREASED VALVE | Steel/Wrought Iron |  | SCOTTSVALLEY | VALVE NEAR REG PIT.; AT VALVE
76 | 72-40003-1 |  |  | 1 | Service |  | Fitting |  |  | Construction Defect |  | 1972-01-24 | 1972-01-25 | Other |  | Plastic |  | SANTA CRUZ | INSTALLED NEW RUBBER + STEEL O-RING IN COMPR. FITTING
76 | 71-04008-6 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-09-03 | 1971-09-07 | Patch Welded |  | Steel/Wrought Iron |  | SANTA CRUZ | 2" X 3" PATCH ARC WELDED
76 | 71-40069 |  |  | 3 | Other |  | Body of Pipe |  |  | Corrosion |  | 1971-06-18 | 1971-06-24 | Patch Welded |  | Steel/Wrought Iron |  | SANTA CRUZ | INSTALLED 3" X 3" PATCH
71-20081-1
76 | 71-20081-1 |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1971-10-19 | 1972-03-13 | Other |  | Steel/Wrought Iron |  | WATSONVILLE
71200811 | [17 empty] | WATSONVILLE
76 | 71-20011-2 |  |  |  | Other |  | Fitting |  |  | Other |  | 1971-04-02 | 1971-12-23 |  |  | Other |  | SANTA CRUZ
76 | 71-20011-1 |  |  |  | Other |  | Fitting |  |  | Other |  | 1971-04-02 | [6 empty] | NO LEAK FOUND!
60 | 71-00012- |  |  | 12 | Distribution Main |  | Other |  | OB | Other |  | 1971-08-16 | 1971-08-16 | Bell Joint Clamp |  | Cast/Ductile Iron |  | SAN FRANCISCO | 1 - 12" CLAMP. 25' S/N/L 22ND ST, 58' W/W/L ILLINOIS. F COLLISON 8/16/71
60 | 71-00161- |  |  | 2 | Distribution Main |  | Other |  | OP | Corrosion |  | 1971-09-10 | 1971-10-05 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | SERVICE TAP - IN FRONT OF BUILDING. 100% GAS OVER MAIN, 40% GAS NEAR BUILDING. WELD ON 2" X 20" PATCH N/S ...
60 | 71-00193- |  |  | 3 | Distribution Main |  | Other |  | OP | Corrosion |  | 1971-09-15 | 1971-09-30 | Other |  | Cast/Ductile Iron |  | SAN FRANCISCO | MIDDLE OF INTERSECTION. EAST SIDE 15' FROM EAST CURB. WEST SIDE OF INTERSECTION - 35% GAS. WELDED 3" X 24" CAN OVER PIN HOLES. 9-30-71 DAPP.
60 | 71-00194- |  |  | 0.75 | Service |  | Other |  | OP | Corrosion |  | 1971-09-15 | 1971-09-24 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | 2' E/W/L 3RD ST. 115' S/S/L ARTHUR ST. REPACKED 3/4" VALVE SHP IN S.W.M.B. AND REDOPED TWO 3/4" STL ... SERVICE IS OLD AND PITTED. TO BE REPLACED. (PG&E SIDEWALK AREA ELEC U.D.).
1 | 71-21134- |  |  | 0 | Other |  | Other |  | OP | Corrosion |  | 1971-04-30 | 1971-08-03 | Replace Pipe |  | Other |  | SAN FRANCISCO | REPL. 1 1/2" SERVICE W. 1" PLASTIC. 8-3-71 GERNLER.
1 | 71-21913- |  |  | 0 | Other | [6 empty] | 1971-06-22 | 1971-08-09 |  |  | Other |  | SAN FRANCISCO
1 | 71-21914- |  |  | 0 | Other | [6 empty] | 1971-06-22 | 1971-08-09 |  |  | Other |  | SAN FRANCISCO
60 | 73-40091-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1973-02-05 |  | Other |  | Other |  | SAN FRANCISCO
60 | 73-40177-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1973-03-22 |  | Other |  | Other |  | SAN FRANCISCO
1 | 71-40049- |  |  | 0 | Service |  | Other |  |  | Other |  | 1971-01-11 |  | Other |  | Other |  | SAN FRANCISCO
1 | 71-40240- |  |  | 8 | Distribution Main |  | Other |  | OP | Corrosion |  | 1971-04-17 | 1971-04-20 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO
1 | 71-40250- |  |  | 0 | Other |  | Other |  |  | Other |  | 1971-04-19 | 1971-04-20 | Other |  | Other |  | SAN FRANCISCO
1 | 71-40307- |  |  | 20 | Distribution Main |  | Other |  | OP | Corrosion |  | 1971-05-05 | 1971-05-07 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELDED PATCH 3' E/E/C BAYSHORE. 31' S/N/C FAITH.
1 | 71-40349- |  |  | 0.75 | Service |  | Other |  | OP | Corrosion |  | 1971-05-24 | 1971-05-24 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO
1 | 71-40358- |  |  | 0.75 | Service |  | Other |  | OP | Damage by outside Forces |  | 1971-05-25 | 1971-05-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPAIR SERVICE 1015 BROTHERHOOD WAY. S/S BROTHERHOOD WAY 1540 E/O LAKE MERCED BLVD.
1 | 71-40366- |  |  | 2 | Service |  | Other |  | OF | Damage by outside Forces |  | 1971-06-02 | 1971-06-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPAIRED SERVICE (BROKEN ELBOW AT METER SITE)
1 | 71-40372- |  |  | 0 | Service |  | Other |  | OP | Corrosion |  | 1971-06-02 | 1971-06-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACED SERVICE. 25TH AVE 260' S/O TARAVAL
| 71-40373- |  |  | 1.25 | Service |  | Other |  | OP | Corrosion |  | 1971-06-07 | 1971-06-07 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPAIR 1 1/4 SHP SERVICE. INST. 1" COCK...
1 | 71-40376- |  |  | 0.75 | Service |  | Other |  | OP | Corrosion |  | 1971-06-01 | 1971-06-02 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | ... CLAMP. REPLACED VALVE BOX. GRAHAM 6-2-71.
1 | 71-40413- |  |  | 4 | Distribution Main |  | Other |  | OP | Corrosion |  | 1971-06-05 | 1971-06-08 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELDED 2 - 4"X6" PATCHES 5' E/W/CURB MCARTHUR BLVD. 244' & 257' N/A/C EL POLIN LOOP. PRESIDIO.
1 | 71-40462- |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1971-06-11 | 1971-07-13 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | TIGHTEN GREASE NUT ON 3/4" NORDSTROM S.W. VALVE. HAD SLIGHT LEAK.
1 | 71-40463- |  |  | 0.75 | Service |  | Other |  | OP | Corrosion |  | 1971-06-11 | 1971-07-12 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | FOUND 3/4" NIBCO S.W. VALVE LEAKING AT THREADS. REPL. VALVE... 7/13/71. N/S HARKNER 12'E/O SPARTA.
1 | 71-40466- |  |  | 2 | Distribution Main |  | Other |  | OV | Material Failure |  | 1971-06-11 | 1971-07-14 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACED AND TIGHTENED GREASE NUT ON 3/4" HP VALVE.
1 | 71-40467- |  |  | 0.75 | Service |  | Other |  | OP | Corrosion |  | 1971-06-11 | 1971-07-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | ... 3/4" HP SIDEWALK VALVE - REMOLDED VALVE AND INSTALLED 17' 3/4" PIPE AND NEW VALVE. 7/14/71.
1 | 71-40469- |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1971-06-11 | 1971-07-14 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | FOUND NO GAS READING... CHECKING SERVICE NEAR VALVE IN SIDEWALK. 7/14/71.
1 | 71-40470- |  |  | 1.25 | Service |  | Other |  | OV | Material Failure |  | 1971-06-11 | 1971-07-16 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPACK PACKING NUTS 7-19-71. REPACKED VALVE.
1 | 71-40471- |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1971-06-11 | 1971-07-16 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | GAS % FROM OTHER SOURCE 7-19-71. T-CAIN. NO GAS AT THIS LOCATION.
1 | 71-40472- |  |  | 0.5 | Service |  | Other |  | OP | Corrosion |  | 1971-06-11 | 1971-07-30 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | INST (1) 1" ... P/L SOAP AND TAP'D THREADS ON OFFSET BEHIND ... IN YARD. REPL. 1" SERV. WITH 1/2" PLASTIC 7/30/71 W. BECKMILL.
1 | 71-40473- |  |  | 1.25 | Service | [6 empty] | 1971-06-11 | 1971-07-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO
1 | 71-40474- |  |  | 0.5 | Service |  | Other |  |  | Other |  | 1971-06-11 | 1971-07-14 | Other |  | Plastic |  | SAN FRANCISCO | NO LEAK AT THIS LOCATION.
1 | 71-40475- |  |  | 0.75 | Service |  | Other |  | OP | Corrosion |  | 1971-06-11 | 1971-07-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | INST. 3 - 3/4 ADAMS CLAMP. SERVICE PITTED AND RUSTED OUT. REPLACED 3/4" SER. WITH 1/2" PL BRACE.
1 | 71-40476- |  |  | 0.5 | Service |  | Other |  |  | Other |  | 1971-06-11 | 1971-07-14 | Other |  | Copper |  | SAN FRANCISCO | NO LEAK AT THIS LOCATION.
1 | 71-40477- |  |  | 0.5 | Service |  | Other |  |  | Other |  | 1971-06-11 | 1971-07-14 | Other |  | Copper |  | SAN FRANCISCO | NO LEAK AT THIS LOCATION.
1 | 71-40478- |  |  | 0.75 | Service |  | Other |  | OP | Corrosion |  | 1971-06-11 | 1971-07-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACED 3/4" SERV. WITH 1/5" PL. BRUCE.
1 | 71-40480- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-06-14 | 1972-03-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACED MAINS AND SERVICES. G.C. 3/28/72; 0 12-27-72.
1 | 71-40482 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-06-14 | 1972-03-28 | Replace Pipe and/or Service |  |  |  | SAN FRANCISCO | REPLACED MAINS AND SERVICES 3/38/72.
1 | 71-40483- |  |  | 1.25 | Service |  | Other |  | OP | Corrosion |  | 1971-06-08 | 1971-06-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACE SERVICE 68-70 GLOVER. 12' N/S/L GLOVER 130' E/O LEAVENWORTH.
1 | 71-40485- |  |  | 1.25 | Service |  | Other |  | OP | Corrosion |  | 1971-06-14 | 1971-06-14 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | K&A SERVICE
1 | 71-40491- |  |  | 6 | Distribution Main |  | Other |  | OP | Corrosion |  | 1971-06-16 | 1971-06-18 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELDED 4' ... ON BOTTOM OF PIPE. 18'E/Q/L BRYANT 167' N/O 15TH ST.
1 | 71-40495- |  |  | 6 | Distribution Main |  | Other |  | OP | Corrosion |  | 1971-06-01 | 1971-07-08 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | WEL D"1 1' PATCH ON 6" HP ST. MAIN, JOB COMPLETED 7-8-11 J. ZIRKLE. 5'6" M/S/L ... 28'6" W/E/L BRODERICK.
1 | 71-40497- |  |  | 6 | Distribution Main |  | Other |  | OP | Corrosion |  | 1971-06-21 | 1971-06-23 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELDED PATCH ON MAIN S/S CALIF. 32' W/O PARKER/ WM GRAHAM 6/23/71.
1 | 71-40510- |  |  | 4 | Distribution Main |  | Other |  | OT | Corrosion |  | 1971-06-17 | 1971-06-21 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | LEAK @ 4" MUELLER CONTROL FITTING 6' S/N/L INNER 6' E/W/L DONAHUE.
1 | 71-40511- |  |  | 16 | Distribution Main |  | Other |  | OP | Corrosion |  | 1971-06-22 | 1971-06-28 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELDED 7'1 - 2' X 2' & 1' X 1' PATCHES ON MAIN. 17' W/E/LBATTERY 76' S/O BROADWAY.
1 | 71-40520- |  |  | 8 | Distribution Main |  | Other |  | OP | Corrosion |  | 1971-06-29 | 1971-07-01 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | 18' E/W/L VIENNA 18' N/N/L RUSSIA. WELDED PATCH ON 8" MAIN.
1 | 71-40522- |  |  | 0.5 | Service |  | Other |  | OP | Construction Defect |  | 1971-07-06 | 1971-07-13 | Other |  | Plastic |  | SAN FRANCISCO | REPAIRED WELD.
1 | 71-40530- |  |  | 2 | Distribution Main |  | Other |  | OP | Corrosion |  | 1971-06-15 | 1971-07-09 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELDED 6" X 2" PATCH ON MAIN. 4' E/W/L LAPHAM WAY N/O RABINSON (FROM CURB).
1 | 71-40537- |  |  | 1.25 | Service |  | Other |  | OV | Material Failure |  | 1971-07-12 | 1971-07-12 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPAIRED 1 1/4" SERVICE VALVE.
1 | 71-40541- |  |  | 0.75 | Service |  | Other |  | OP | Corrosion |  | 1971-07-15 | 1972-02-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACED 3/4" SHP SERVICE WITH 1/2" PLASTIC, JOB COMPLETE 2-8-72, M. MCGOVERN.
1 | 71-40543- |  |  | 2 | Distribution Main |  | Other |  | OP | Damage by outside Forces |  | 1971-07-14 | 1971-07-14 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | CUT AND CAPPED 2' HP MAIN.
1 | 71-40546- |  |  | 0.75 | Service |  | Other |  | OP | Corrosion |  | 1971-06-20 | 1971-07-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACED SERVICE WITH 1" PLASTIC.
1 | 71-40551- |  |  | 16 | Distribution Main |  | Other |  | OP | Corrosion |  | 1971-07-16 | 1971-07-20 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELDED PATCH 5' N/S/L RUSSIA 25' E/O EDINBURGH.
1 | 71-40554- |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-07-20 | 1972-02-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACED 6" MAIN BY G.C.
1 | 71-40560- |  |  | 4 | Distribution Main |  | Other |  | OP | Corrosion |  | 1971-07-22 | 1971-07-22 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | K&A 1" STREET LIGHT SERVICE. 9' E/W/L RANDALL 94' S/O 16TH ST.
1 | 71-40561- |  |  | 0.75 | Service |  | Other |  | OP | Corrosion |  | 1971-07-23 | 1971-11-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | TEMP REP 3/4" SHP SERV. INST. AOAM CLAMP AT TEOO AT MAIN, 7-28-71. REPLACED SERVICE WITH 1/2 PLASTIC, M. MCGOVERN. 11-16-71. MAIN IN POOR CONDITION.
| 71-40562- |  |  | 0.75 | Service |  | Other |  | OP | Corrosion |  | 1971-07-23 | 1971-11-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | TEMP REP. 3/4 " SHP SERVICE. INST. AOAM CLAMP AT TEE AT MAIN, 7-28-11 MEYER. REPL. 3/4" SERVICE W. 1/2" PL, 11-16-71. MAIN IN POOR CONDITION.
1 | 71-40588- |  |  | 0 | Other |  | Other |  |  | Other |  | 1971-07-27 |  | Other |  | Other |  | SAN FRANCISCO | NO READINGS AT THIS TIME.
60 | 71-40697- |  |  | 4 | Distribution Main |  | Other |  | OP | Construction Defect |  | 1971-09-10 | 1971-09-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACED 1 1/4" BLOW OFF ON END OF H.P. MAIN. 47' W/O FACE FERRY BUILDING (EMBARCADERO). 5' N/N/END FERRY BUILDING. CORRIGAN, 9-10-71
60 | 71-40856-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1971-11-11 |  | Other |  | Other |  | SAN FRANCISCO | 0 READINGS ON MSA SLOPE AT 1207-1209. 6-12-72, T. CAIN.
60 | 72-23202-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1972-06-29 | 1972-07-18 | Other |  | Other |  | SAN FRANCISCO | REFER TO 72-23205. COMING FROM SERVICE 1661.
60 | 72-23204-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1972-06-29 | 1972-07-18 | Other |  | Other |  | SAN FRANCISCO | REFER TO 72-23205; COMING FROM SERV. AT #1661.
60 | 72-40688-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  | 1972-10-05 | 1972-10-05 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | FORM B CODE 2 1-13-73 RECHECK.
60 | 72-40825-1 |  |  |  | Other |  | Body of Pipe |  |  | Corrosion |  | 1972-11-24 | 1972-11-24 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | FORM B CODE 2 1-15-73 RECHECK; REPAIRED 3/4" DRIP RISER.
60 | 72-40890-1 |  |  | 16 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-12-15 | 1972-12-15 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | REAPRIED 20" TP MAIN. WLD BROKE. 278' B/O HRWY.
60 | 73-23058-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1973-07-16 | 1973-08-08 | Other |  | Other |  | SAN FRANCISCO | DELETE FORM C, PG3 LINE 6 - 10-10-73.
60 | 73-23274-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1973-07-24 |  | Other |  | Other |  | SAN FRANCISCO | DELETED FORM C, PG3 LINE D - 10-10-73.
60 | 93-21201-1 |  |  | 08.00 & 04.00 | Gathering |  | Bell Joint |  |  | Other |  | 1993-04-26 | 1993-06-11 | Bell Joint Seal |  | TR 418 |  | SAN FRANCISCO | PEROBOND 4 BY 8 INCH CROSS IN STREET.
| 97-80388-1 |  |  | 15 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1992-01-10 |  | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELD PATCH.
60 | 74-01670-1 |  |  | 24 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1974-08-01 | 1974-11-27 | Bell Joint Clamp |  | Cast/Ductile Iron |  | SAN FRANCISCO | BELL JOINT WAS ALREADY CLAMPED WITH NEW 24" LEAK CLAMP. 24" BELL JOINT ON PROPERTY LINE. INSTD 1 - 24" LEAK CLAMP AT E/PL FAIR ONLY. 22' S/N/PL 25TH ST.
60 | 82-23466-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  | 1982-04-12 | 1983-02-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACED 2' OF 1" BLOW OFF & TWO VALVES AT LOC. BELOW. 6" STL SHP - GOOD CONDITION.
60 | 82-23854-1 |  |  | 0.75 | Other |  | Tap Connection |  |  | Corrosion |  | 1982-06-23 | 1983-06-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACED DRIP RISER.
60 | 74-20678-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1974-04-19 |  | Other |  | Other |  | SAN FRANCISCO | NO READ PER M.S.A. SCOPE; 35 DORMAN SER OFF INDUSTRIAL 0 ... 4-30-74.
60 | 74-21612-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1974-01-29 |  | Other |  | Other |  | SAN FRANCISCO | SEWER BAS ...
60 | 74-21790-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1974-03-18 |  | Other |  | Other |  | SAN FRANCISCO | FORM C DEL. 4-34 (5-31-74); E/S 4TH & JESSIE PTT M.H. NO READING. CLEARED ON LEAK # 74270081
60 | 74-21880-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1974-03-28 |  | Other |  | Other |  | SAN FRANCISCO | 20 LEL MAIN SEWER.
| 82-24316- |  |  | 6 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1982-07-21 | 1983-05-19 | Bell Joint Seal |  | Cast/Ductile Iron |  | SAN FRANCISCO | INST. 6" OVER SEAL.
60 | 74-22008-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1974-01-24 |  | Other |  | Other |  | SAN FRANCISCO | NO READINGS PER M.S.A SCALE; NO READINGS AS OF 1-31-74.
60 | 74-22121-1 |  |  |  | Service |  | Valves |  |  | Material Failure |  | 1974-01-30 | 1974-01-31 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | GREASED VALVE ON 3/4" SERVICE.
60 | 74-27001-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1974-03-06 |  | Other |  | Other |  | SAN FRANCISCO | LEAK CLEARED. SERVICE HAS BEEN REPLACED. 4-3-74.
60 | 74-40796-1 |  |  | 2 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-09-13 | 1974-09-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACED 6" OF 2" PIPE AND HP VALVE ON BLOW OFF AT 20' S/N/L CALIFORNIA AND 12' E/W/L KEARNY. MAIN ENCASED IN THE CONCRETE OF SEWER MANHOLE.
60 | 74-40846-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-10-04 | 1974-10-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | 22 W/S/L DE HARD. 146' S/S/L 16TH ST. REMOVED AND REPLACED 1" DRIP RISER THAT WAS FITTED AND LEAKING.
60 | 75-20177-1 |  |  | 4 | Other |  | Bell Joint |  |  | Material Failure |  | 1975-02-13 | 1975-03-03 | Bell Joint Clamp |  | Cast/Ductile Iron |  | SAN FRANCISCO | 3' IN CURB W/S LAKE. 57' S/S/L EL CAMINO DEL MAR, RIGHT UNDER BRICK STAIRS. INST. 4" L. CLAMP.
60 | 75-22213-1 |  |  | 4 | Other |  | Bell Joint |  |  | Material Failure |  | 1975-09-12 | 1976-05-19 | Bell Joint Clamp |  | Cast/Ductile Iron |  | SAN FRANCISCO | INST. 1 - 4" BELL JOINT CLAMP IN 4" ci MAIN AT 20' S/N/L SANTA YNEZ. 169' E/E/L ALELANO.
| 76-24860- |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1976-09-21 | 1976-09-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | TEMP REPAIRED 1 1/4" SERVICE WITH LEAK CLAMP UNDER FOUNDATION.
60 | 76-40082-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1976-01-23 | 1976-01-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | 142 BEULAH ST. REPLACED 1 FOOT OF 1 1/4" PIPE FROM RISER TO MANIFOLD 64' N/N/L BELUAH ST. 229' E/E/L STANYAN ST.
60 | 76-40417-1 |  |  | 0.75 | Other |  | Drip |  |  | Corrosion |  | 1976-06-17 | 1976-06-17 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO
60 | 76-40482-1 |  |  | 12 | Distribution Main |  | Fitting |  |  | Corrosion |  | 1976-08-07 | 1976-08-05 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | CAN 1 1/2" SEWER VALVE ON 12" H.P. MAIN S/S DEWEY SHP. ELOYACHECO ST.
60 | 77-00037-1 |  |  | 1 | Other |  | Drip |  |  | Material Failure |  | 1977-07-19 | 1979-05-17 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | 25% IN DRIP BOX OVER MAIN, 11-16-77. 40%, 7-24-78 FITZGERALD. 70%, 3-8-79 MICHAEL DE JESUS. 20' N/S/L CLAY. 148' E/O JONES. TIGHTEN 1" CAP ON DRIP, 5-17-79.
60 | 77-21477- |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1977-05-03 | 1977-08-10 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPAIRED LEAKING 3/4" DRIP ON 4" STL MAIN. 14' N/S/L PARAMOUNT. 270 W/W/L STANYAN.
60 | 77-22804-1 |  |  | 1 | Service |  | Fitting |  |  | Material Failure |  | 1977-01-31 | 1978-04-19 | Other |  | Plastic |  | SAN FRANCISCO | REPLACED O-RING ON SERVICE HEAD ADP OF 1" P.L. SERVICE. JOB COMPLETE.
60 | 77-22916-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Material Failure |  | 1977-03-04 | 1979-04-25 | Replace Pipe and/or Service |  | Cast/Ductile Iron |  | SAN FRANCISCO | 35% WB. 20 LEL SEVER VENT CALLED CREW. REPLACED 1" CU THAT WAS LEAKING AT SLEEVE WITH 1" CU FROM MAIN TO SWV BOX.
60 | 77-23014- |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1977-04-18 | 1977-04-18 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | TIGHTEN PLUG ON DRIP RISER.
60 | 77-23052- |  |  | 4 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1977-04-28 | 1978-04-17 | Bell Joint Clamp |  | Cast/Ductile Iron |  | SAN FRANCISCO | 30% 10-21-77 FITZGERALD. 40% AT CURB. 75% OVER MAIN. INST. 1 - 4" LC 12' S/S/L JARBOE...
60 | 77-23057- |  |  | 4 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1977-04-29 | 1978-05-30 | Bell Joint Clamp |  | Cast/Ductile Iron |  | SAN FRANCISCO | 40% 10-21-77, FITZGERALD. 15' W/E/L - FOLSOM. 161' S/S/L - RUGENIA. INSTALLED 1 - 4" LEAK CLAMP.
60 | 77-23059- |  |  | 0.04 | Distribution Main |  | Body of Pipe |  |  | Material Failure |  | 1977-04-29 | 1978-04-04 | Other |  | Cast/Ductile Iron |  | SAN FRANCISCO | 10%, 10-21-77, FITZGERALD. 12' W/E/L GATES. 5' S/S/L EUGENIA. INSTALLED 1 - 4" LEAK CLAMP.
60 | 77-23403-1 |  |  | 2 | Service |  | Body of Pipe |  |  | Corrosion |  | 1977-01-11 | 1978-03-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | 30% 0-0-77 FITZGERALD. SOAKED AND TAPED 3' OF 2" SERVICE IN ST. TO BE REPLACED. MCGOVERN, 3-28-78.
60 | 77-23766-1 |  |  | 16 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1977-04-05 | 1979-03-30 | Bell Joint Clamp Replacement |  | Cast/Ductile Iron |  | SAN FRANCISCO | 5% 10-18-77 FITZGERALD. 5% 3-3-79 MICHAEL DE JEAN. INSTALL 16" B.J. CLAMPS AT 16', 40', AND 52' E/O COLUMBUS OUT 13' ON N/S JACKSON.
60 | 72-23838- |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1977-04-22 | 1978-04-17 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | 30% 10-28-77 FITZGERALD. REPLACED 1 1/2" SERVICE FROM MAIN TO METER. JOB COMPLETE.
60 | 77-23848- |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1977-04-26 | 1978-04-23 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | 10% 1-26-77 FITZGERALD. 1" PLASTIC FROM MAIN TO METER. JOB COMPLETE.
60 | 77-25015-1 |  |  | 24 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1977-08-24 | 1980-03-11 | Bell Joint Clamp |  | Cast/Ductile Iron |  | SAN FRANCISCO | 80% 3-13-79 FITZGERALD... INSTALL 24" LEAK CLAMP ON 24" B.J.
60 | 77-40467-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-10-07 | 1977-10-07 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | 22' N/S/L OCEAN. 14' D" E/W/L HOWTH. REPAIRED 3/4" DRIP WITH 1 - TRAFFIC BOX.
60 | 77-40477-1 |  |  | 0.75 | Service |  | Valves |  |  | Material Failure |  | 1977-10-13 | 1977-10-13 | Other |  | Other |  | SAN FRANCISCO | REPLACED 3/4" NIBCO VALVE. 20' S/S/L DAWNVIEW. 5' W/E/L BURNETT.
60 | 78-00002-1 |  |  | 8 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1978-01-31 | 1979-05-11 | Bell Joint Clamp |  | Cast/Ductile Iron |  | SAN FRANCISCO | 80 LEL 4/30/79 MICHAEL DEJEAN. 18' E/W/L - BATTERY. 8'9 AMD 9' S/S/L CALIFORNIA. REMOVED AND INSTALLED 1 - 8" LEAK CLAMPS ON SLIEVE. JOB COMPLETE. M. MCGOVERN.
60 | 78-21260- |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  | 1978-05-02 | 1978-05-02 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | FOUND LEAK ON 1" HOUSELINE UNDERGROUND AT METER. TEMP REPAIR AND NOTIFIED DISPATCH T O SEND SERVICEMAN. 5-2-78 REGAN.
60 | 78-21344- |  |  | 2 | Other |  | Body of Pipe |  |  | Corrosion |  | 1978-05-23 | 1978-05-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO
60 | 78-21363-1 |  |  | 1.25 | Service |  | Valves |  |  | Material Failure |  | 1978-02-21 | 1978-08-29 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | #1639 POLK. TIGHTEN 1 1/4" BONNET ON VALVE. 8-29-78 BURKE.
60 | 78-21451-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Other |  | 1978-03-13 | 1980-07-02 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | 50 LEL, GCB. 5-6-80 FITZGERALD. NOT ROOM VALUE READING IN W.B. 5-13-80 BURKE. 22' S/N/L - VALLEJO, 60' E/S/L - BUCHANAN. REPAIRED LEAK ON 4" T.S. LEAKING AT BOLTS. JOB COMPLETE.
60 | 78-21456- |  |  | 8 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1979-03-09 | 1979-04-05 | Bell Joint Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | INSTALLED 8" B.J. CLAMP 19' E/W/L STEINER OUT 31' ON SOUTH SIDE OF CALIF. D RUIZ 4/5/79.
60 | 78-23096- |  |  | 1.5 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-02-12 | 1979-05-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | INSTALL 1 1/2 ... CLAMP ON SL SIDE OF VALVE TERMINAL IN FOR REPLACEMENT. SERVICE REPL. G.L. GAS 5-23-86.
60 | 78-24207-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Material Failure |  | 1978-04-27 | 1980-07-22 | Replace Pipe and/or Service |  | Cast/Ductile Iron |  | SAN FRANCISCO | REMOVED AND REPLACED 13' SECTION OF 4" CI AND REPLACED WITH 4" ST. 124' W/W/L STOCKTON TO 137' W/W/L STOCKTON ON N/ SIDE PINE.
60 | 78-24207-1 |  |  |  | Distribution Main | [6 empty] | 1978-04-27 | [5 empty] | SAN FRANCISCO | 80% 5-6-80, FITZGERALD.
60 | 70-24546-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1978-08-25 | 1978-08-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | TEMP REPAIRED 1 1/4" AND 3/4" SERVICE IN LAWN AREA. SERVICE TO BE REPLACED. M. MCGOVERN.
60 | 78-24923- |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1978-07-20 | 1980-02-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | 8-8-79, 10% AT PROPERTY LINE. REP. 1 1/4 STL WITH 1/2" PLASTIC W/S 2G AVE... S/S/L SANTIAGO.
60 | 78-25063- |  |  | 0.75 | Other |  | Drip |  |  | Material Failure |  | 1978-08-29 | 1980-03-04 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | 30% NEAR DRIP OVER MAIN IN SIDEWALK IN FRONT OF P.T.&T. BLDG. ON WEST PORTAL. 3-7-79. DOPE 3/4" PLUG ON DRIP.
60 | 78-27909-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1978-12-11 | 1978-12-11 | Other |  | Cast/Ductile Iron |  | SAN FRANCISCO | 11' W/E/L JUNIPER. 390' S/S/L FOLSOM. INST. 3/4" DRIP ON MAIN - 4" CILP MAIN IS DEAD UNDER THERE. 12-11-73.
60 | 78-40003-1 |  |  | 1 | Other |  | Drip |  |  | Corrosion |  | 1978-01-02 | 1978-01-04 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | 30% GAS AT CURB. 1-2-78 P REGAN. REPLACED 1" DRIP. PIPE, PIPE = CORRODED 31' E/W/L SANCHEZ, N/S/L 25TH ST.
60 | 78-40073-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1978-02-17 |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | FOUND 3/4" ...
60 | 78-40513- |  |  | 0.75 | Other |  | Physical/Mechanical Joint |  |  | Damage by outside Forces |  | 1978-08-21 | 1978-08-21 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | CUT & THREAD AND EXTEND 3/4" DRIP PIPE. 372' W/W/L 6TH ST. COMPLETE 8-21-78.
60 | 78-40520-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1978-08-25 | 1978-08-25 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACED 28' OF 3/4" PIPE WITH S8' OF 1/2" PL. JOB COMPLETE.
60 | 78-40527-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1978-08-29 | 1978-08-29 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | 7' N/S/L - 18TH ST. 3' W/E/L - HARRISON. INSTALLED 2 - 4" PERM REPAIR CLAMPS ON 4" STEEL MAIN. JOB COMPLETE. MAIN BADLY PITTED AT THIS POINT. BAD, ROCKY BACKFILL.
60 | 78-40537-1 |  |  | 14 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1978-08-10 | 1978-08-10 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | 4' N/S/L - MANSELH. 2' E/W/L - GOETTINGEN. INSTALLED 4" X 12" CAN ON 4" MAIN. JOB COMPLETE.
60 | 78-40621-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  | 1978-09-26 | 1978-09-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | NEW 1" STL HP DRIP RISER.
60 | 78-40625-1 |  |  | 0.75 | Other |  | Drip |  |  | Corrosion |  | 1978-09-28 | 1980-07-10 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | SLEL; 6-20-79. 11' W/E/L - JESSIE. 109' W/W/L MCGOPPIN. INSTALLED 3/4' DRIP RISER.
60 | 78-40655-1 |  |  | 4 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1978-10-04 | 1978-10-04 | Replace Pipe and/or Service |  | Cast/Ductile Iron |  | SAN FRANCISCO | CLEAR 1ST TIME; 3RD AVE. 242' S/O CORNWALL. 25' W/E/ LINE 3RD AVE. INSTALL 4" B.J. CLAMP. 10/4/78.
60 | 78-40733-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-11-10 | 1978-11-10 | Other |  | Plastic |  | SAN FRANCISCO | ... 74' W/W/; - ARTHUR. REPAIRED 1/2" PL SERVICE IN ST AREA...
60 | 78-40750-1 |  |  | 4 | Other |  | Bell Joint |  |  | Material Failure |  | 1978-11-12 | 1978-11-27 | Bell Joint Clamp |  | Cast/Ductile Iron |  | SAN FRANCISCO | INSTALL 4 4" BELL JOINT CLAMP ON 4" CROSS. D RUN, 11-27-78.
60 | 78-40757-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1978-11-22 | 1978-11-29 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | ... 3/4 HP SERV BLOWING...
60 | 78-40776-1 |  |  | 20 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-12-12 | 1978-12-12 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELDED 6" X 6" STEEL PATCH OVER LEAK.
60 | 78-40789-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1978-12-01 | 1978-12-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | GOOSE NECK LEAKING. INSTALLED NEW FITTINGS INTO METER LOCATION. 12/1/78.
60 | 78-40811-1 |  |  | 4 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1978-12-19 | 1978-12-19 | Bell Joint Clamp |  | Cast/Ductile Iron |  | SAN FRANCISCO | 29' S/N/L - REVERE, 453' W/W/L - 3RD ST. INSTALLED 1 - 4" LEAK CLAMP.
60 | 78-40814-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1978-12-19 | 1978-12-19 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | 20' N/S/L - ARMSTRONG. 1' E/E/L - KEITH. INSTALLED 3/4" DRIP RISER ON 4" CI MAIN THAT WAS FITTED AND LEAKING.
60 | 78-40888-1 |  |  | 1.5 | Service |  | Body of Pipe |  |  | Corrosion |  | 1978-11-06 | 1978-11-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | SERV. IS OFF VILLA 133' W/O SNAGSTONE ON S/SIDE OF VILLA. SOP & TAPED SERV. ON HOUSE SIDE OF VALVE. D RUN 11/6/78,
| 79-20192- |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1979-03-02 | 1979-03-02 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | FOUND 30-90% GAS OVER HOUSE LINE. NOTIFIED SFHA PLUMBING FOREMAN AND SHUT OFF LINE.
| 79-20277- |  |  | 4 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1979-04-04 | 1979-05-18 | Bell Joint Clamp |  | Cast/Ductile Iron |  | SAN FRANCISCO | CALLED ON 4-4-79. FOUND READING OF 60% OVER MAIN. DRILLED AND VENTED, MC GOVERN 4-4-79. RECHECK. INSTALL 4" B.J. CLAMP 12' N'N'L CALIF. OUT 38' ON E/ CHERRY. D. RIES 5-18-79. INSTALLED 1 - 4" SHRINK SLEEVE 24' N/N/L CALIFORNIA 23' OUT E/S CHERRY. 4" SHRINK SLEEVE (1).
60 | 79-20279- |  |  | 4 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1979-04-04 | 1979-04-11 | Bell Joint Clamp |  | Cast/Ductile Iron |  | SAN FRANCISCO | DRILLED HOLES OVER MAIN AND VENTED. 4-4-79. RECHECK IN COUPLE DAYS. INSTALLED 4" B.J. CLAMP 82' E/O BEAUMONT OUT 21' ON N/S ANYA, D. RIES 9/11/79.
60 | 79-20641-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1979-06-20 | 1979-11-02 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | 80%, 10-19-79 FITZGERALD. INSTALLED 1 1/4" ADAMS CLAMP ON HOUSE SIDE OF S.W. VALVE. SERVICE FOR REPLACEMENT. D. RIES 11/2/79.
60 | 79-21907-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1979-06-28 | 1979-08-13 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | GREASED VALVE.
60 | 79-22318- |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-03-30 | 1979-03-30 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | TEMP. REP 1 1/4" SET AT CURB. SOAP + TAPED SLR TO BE REPLACED. 5-30-79...
60 | 79-22339-1 |  |  | 4 | Other |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1979-05-01 | 1980-08-07 | Bell Joint Seal |  | Cast/Ductile Iron |  | SAN FRANCISCO | 50%, 10-22 79 FITZGERALD. 22' N/S/L JEFFERSON. 142' E/O BRODERICK. INST. 4" AVON SEAL ON SPLIT - SLU JEFFERSON. TO #1961, 8-7-80 BOSSIER.
60 | 79-22338-1 |  |  | 4 | Other |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1980-08-07 | 1980-08-07 | Bell Joint Seal |  | Cast/Ductile Iron |  | SAN FRANCISCO | 22' N/S/L JEFFERSON. 143' E/O BRODERICK. INST/ 4" AVON SEAL ON SPLIT SLU TO 196' JEFFERSON, 8-7-80 BOSSIER.
60 | 79-22448-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-02-07 | 1979-06-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | STREET RESURFACE. SOAP + TAPED SERV OF MAIN. TUNED SERV IN FOR REPLACEMENT. (X.P.D STREET RESURFACING) 136' N?O GEARY OUT 19' W/30TH AVE. D. RIES 6/18/1979.
60 | 79-22710-1 |  |  | 2 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-06-19 | 1979-06-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | SOP + TAPED SERV, TUNED IN FOR REPLACEMENT. X.P.D. SERV RUNNING UNDER BLDG. TURNED INTO ENGINEERING FOR X.P.D. REPLACEMENT, D. RIES 6/19/79.
60 | 79-22745- |  |  | 1.5 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-03-05 | 1979-03-05 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | 5% SEWER VENT. INSTALL 1 1/2 SKINNER PERMANENT REPAIR CLAMP OUT 6' FROM P.L. D. RIES 3/5/79.
60 | 79-28027-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Material Failure |  | 1979-09-21 | 1979-09-21 | Clamp |  | Cast/Ductile Iron |  | SAN FRANCISCO | 20' E/W/L - CAYUGA, 27' S/N/L - ROUSSEAU. INSTALLED 1 - 4" SKINNER SPLIT SEAL CLAMP ON BROKEN 4" CI MAIN.
60 | 79-28260- |  |  | 1.5 | Other |  | Body of Pipe |  |  | Corrosion |  | 1979-12-28 | 1980-01-10 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | ... 27' N/S/L BROADWAY W45' E/O SCOTT...
60 | 79-28461- |  |  | 1 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-11-29 | 1979-11-30 | Replace Pipe and/or Service |  | Copper |  | SAN FRANCISCO | REAPAIRED LEAK ON 1 1/4" RISER AT METER LOCATION. JOB COMPLETE. REPAIRED 1' OF 1 1/4" PIPE AT RISER.
1 | 79-23704- |  |  | 8 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1979-10-09 | 1979-10-10 | Bell Joint Clamp |  | Cast/Ductile Iron |  | SAN FRANCISCO | 24' W/E/L - GRANT AVE. 33' S/S/L - MAIDEN LANE. INSTALLED 1 - 8" LEAK CLAMP. OLD AGE.
60 | 79-28982- |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-11-29 | 1980-04-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACED 1 1/4" STEEL SERVICE FROM MAIN TO SWV BOX WITH 1" P.L. INST. #9 MAG ANODE AT VALVE BOX. JOB COMPLETE.
60 | 79-40001-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1979-01-02 | 1979-01-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO
60 | 79-40087-1 |  |  | 6 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1979-01-22 | 1979-02-02 | Bell Joint Clamp |  | Cast/Ductile Iron |  | SAN FRANCISCO | 362 NOE CALLED IN AS ODOR IN AIR. DRILLED OVER 4" CI W/S NOE AND 6" CO E/S NOE READING 10% TO 50% OVER MAIN. NO READING IN SW AREA, INSTALL 6" B.S. CLAMP 145' N/N/L 17TH ST. OUT 25' ON E/S NOE. D. RIES 2/2/79.
60 | 79-40112-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-02-12 | 1979-02-12 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | INSTALLED 10' OF 1/2" P.L. FROM SWV TO METER. JOB COMPLETE.
60 | 79-40246-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-03-21 | 1979-03-23 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | 20' W/E/L STOCKTON. 72' S/S/L UNION. ... % 1 1/4" SERVICE IN USE AT MAIN 3-23-79 BOSSIER.
60 | 79-40250-1 |  |  | 16 | Other |  | Valves |  |  | Other |  | 13/13/1979 | 1979-03-21 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | EVACUATED AND GREASED TWO 6" HP MAIN VALVES STUB OFF 16" HP MAIN, 4' N/S/L PINE,7' E/W/L TAYLOR. INST. TWO SWVB.
60 | 79-40255-1 |  |  | 1.25 | Other |  | Fitting |  |  | Other |  | 1970-03-23 | 1979-03-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | INST. (1) NEW SERVICE COCK...
60 | 79-40313-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1979-04-04 | 1979-04-04 | Weld Over Sleeve or Can |  | Cast/Ductile Iron |  | SAN FRANCISCO | ARC WELDED 6" HP WELD ON 6" HP STUB AND VALVE.
60 | 79-40314-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Material Failure |  | 1979-04-16 | 1979-04-16 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPAIRED LEAK ON BONNET OF 1 1/4" POWELL GATE VALVE. JOB COMPLETE. M MCGOVERN 4-16-79.
60 | 79-40316-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Material Failure |  | 1979-04-13 | 1979-04-13 | Clamp |  | Cast/Ductile Iron |  | SAN FRANCISCO | 27' N/S/L - HOWARD. 91' E/E/; - RAUSCH. INSTALLED 6" SPLIT SKINNER REPAIR CLAMP ON BROKEN MAIN. JOB COMPLETE. UNKNOWN.
60 | 79-40383-1 |  |  | 4 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-05-01 | 1979-05-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | INSTALLED 4" ... CIRCLE CLAMP, 1 SKINNER PERM. REPAIR CLAMP + SOAP AND TAPED WELD ALL IN VALVE BOX AREA ...
60 | 79-40419-1 |  |  | 1 | Service |  | Body of Pipe |  |  | Material Failure |  | 1979-05-07 | 1979-05-07 | Other |  | Copper |  | SAN FRANCISCO | REPAIRED LEAK ON 1" CU SLEEVE AT VALVE BOX. INST. NEW 1" NIBCO GATE VALVE, JOB COMPLETE.
60 | 79-40674-1 |  |  | 0.5 | Other |  | Drip |  |  | Other |  | 1979-06-27 | 1979-06-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | 3/4" DRIP WAS BROKEN BOTTOM OF DRIP. REMOVED AND INST. NEW 3/4" D.W. PIPE.
2 | 79-40698-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1979-07-10 | 1979-07-10 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | K&A ST LIST AT MAIN. 12' E/E/L JULIAN. 19' N/S/L 14TH ST.
60 | 79-40840-1 |  |  | 6 | Other | I | Tap Connection |  |  | Material Failure |  | 1979-08-20 | 1979-08-20 | Other |  | Copper |  | SAN FRANCISCO | MADE PERM REPAIR - TIGHTENED SET SCREWS ON STYLE 80 SERVICE SADDLE, 8-20-79 P REGAN.
1 | 80-20417- |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1980-01-25 | 1980-01-25 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPAIRED PIT HOLE ON 3/4" STATIC LINE TO REGULATOR PIT WITH PERM. REPAIR CLAMP INSTALLED 9# ANODE.
60 | 80-40608-1 |  |  | 4 | Other |  | Bell Joint |  |  | Material Failure |  | 1980-09-16 | 1980-09-16 | Bell Joint Seal |  | Cast/Ductile Iron |  | SAN FRANCISCO | INSTALLED 4" AVON SEAL ON BELL JOINT DRIP.
60 | 80-40646-1 |  |  | 0.75 | Other |  | Fitting |  |  | Material Failure |  | 1980-09-18 | 1980-09-18 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | 3/8" ELBOW WAS CRACKED. REMOVED 3/8" ELBOW AND NIPPLE AND INST. 3/8" PLUG IN 3/4" X 3/8" BUSHING. 9-18-1980.
| 80-22296- |  |  | 0.75 | Other |  | Fitting |  |  | Corrosion |  | 1980-11-26 | 1980-11-26 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACE FITTINGS (2) ON STATIC LINE. 11-26-80.
| 80-22425- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1980-01-23 | 1980-01-23 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | STREET RESURFACING; INSTALLED (3) 3/4 PERM REPAIR CLAMPS IN STREET SERVICE WAS ON TOP OF ROCK ABOUT 1 SERVICE.
1 | 80-22466- |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1980-02-06 | 1980-02-06 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | #4919 MISSION. 100% OVER ... VENTED. INSTALL 7 1/2" PATCH ON 8" I.D. H/P MAIN BY ARC WELDING.
60 | 81-20217-1 |  |  | 24 | Distribution Main |  | Girth Weld |  |  | Corrosion |  | 1981-02-04 | 1981-12-04 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SAN FRANCISCO | CALL COLE.
| 81-20217-1 |  |  | 24 | Distribution Feeder Main |  | Girth Weld |  |  | Corrosion |  |  | 1981-12-04 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SAN FRANCISCO
60 | 80-21762- |  |  | 2 | Other |  | Fitting |  |  | Material Failure |  | 1980-03-28 | 1980-03-28 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | FOUND LEAK ON METER REPAIRED BY SERV. DEPT. 3-28-80.
| 80-28620- |  |  | 1 | Other |  | Valves |  |  | Other |  | 1980-11-19 | 1980-11-20 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | ... REPAIRED LEAK AT 2 - 1" GAUGE TAP VALVES. 11-20-80...
60 | 80-40017-1 |  |  | 1.5 | Service |  | Body of Pipe |  |  | Material Failure |  | 1979-01-01 | 1979-01-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | 23' N/E/L ... 233 N/CLEMENT, REPLACED 1 1/2" SERVICE WITH 1" P.L. FROM MAIN TO SWV BOX. TO BE COMPLETED.
60 | 80-40022-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1980-01-04 | 1980-01-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACE SERV. W/ 1" PL INSERT.
60 | 80-40050-1 |  |  | 4 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  |  | 1980-01-18 | Other |  | Cast/Ductile Iron |  | SAN FRANCISCO | 23' S/N/L NORTH POST. 19' W/E/L MASON. A. APPROX 10' OF 4" CL MAIN... CUT AND CAP. SEE SKETCH.
60 | 80-40123-1 |  |  | 6 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1980-01-25 | 1980-01-25 | Bell Joint Seal |  | Cast/Ductile Iron |  | SAN FRANCISCO | 22' N/S/L - BAY. 22' W/E/L - FRANKLIN. INSTALLED 1 - 6" AVON SEAL.
60 | 80-40139-1 |  |  | 2 | Service |  | Body of Pipe |  |  | Corrosion |  | 1980-02-26 | 1980-02-26 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | INSTALLED 2" PERM REPAIR CLAMP ON SERVICE IN SW. ALSO #9 MAG ANODE.
60 | 80-40161-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1980-03-05 | 1980-03-05 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | CUT-OFF 1 1/4" SERVICE AT MAIN. SERVICE NOT IN USE. JOB COMPLETE.
60 | 81-21429-1 |  |  | 0.75 | Distribution Main |  | Valves |  |  | Material Failure |  |  | 1981-04-10 | Other | REPAIR 3/4" VALVE | Steel/Wrought Iron |  |  | REPAIR 3/4" SHP VALVE INSIDE VALVE BOX. TURNED IN FOR REPLACEMENT, POSSIBILITY OF MORE LEAKAGE. UNDER NOW EXPOSED PACK SURFACE. 4-10-8, S. SPROINI.
60 | 81-21597-1 |  |  | 16 | Distribution Feeder Main |  | Other Welds |  |  | Corrosion |  | 1981-05-01 | 1981-06-29 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | INSTALL 8" PATCH, 4" & 3" PATCH 37' W/O LEAVENWORTH. MAIN OUT 18'.
60 | 81-23150-1 |  |  | 4 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1981-08-10 | 1981-10-05 | Bell Joint Seal |  | Cast/Ductile Iron |  | SAN FRANCISCO | INSTALLED 14" ... PINPOINTED.
| 81-23329- |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1981-09-03 | 1981-09-03 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | INSTALLED 2 - 1 1/4" ADAMS CLAMP ON SERVICE BOTTOM OF RISER.
60 | 81-23871- |  |  | 0.5 | Service |  | Fitting |  |  | Material Failure |  | 1981-11-03 | 1981-11-04 | Other |  | Copper |  | SAN FRANCISCO
60 | 81-24643- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1981-10-06 | 1982-10-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO
60 | 81-24643-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1981-10-06 | 1982-10-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | 9/5/90 E VULCAN; INST. ADAMS CLAMP ON 3/4" SERVICE, 10-1-82.
1 | 81-25344- |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1981-11-02 | 1981-11-03 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | VENTED OVER SERV. IN REAR OF BLDG. 11-2-81. TIGHTENED SERVICE TEE AT MAIN, 11-3-81.
60 | 81-40685-1 |  |  | 1.25 | Other |  | Valves |  |  | Construction Defect |  | 1981-10-02 | 1981-10-02 | Other | REPLACED GUTS | Steel/Wrought Iron |  | SAN FRANCISCO | CUSTOMER COMPLAINT; REPLACED GUTS TO UNION COCK, 10-2-1981 S. SPROINI. NO EXPOSED.
60 | 81-40725- |  |  | 0.75 | Other |  | Fitting |  |  | Corrosion |  | 1981-10-28 | 1981-10-28 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | C/O 6" OF 3/4" DRIP PIPE. 10-28-81... 32' W/E/L DAVIS. 28' N/S/L BROADWAY.
60 | 81-40805-1 |  |  | 3 | Other |  | Bell Joint |  |  | Material Failure |  | 1981-10-15 | 1981-10-16 | Bell Joint Seal |  | Cast/Ductile Iron |  | SAN FRANCISCO | INST. ONE 3" AVON SEAL ON 4X4X3 CI TEE (SERV. TAP FOR 1299 CALIF.) NEED LEAK # - FOUND IN FIELD.
60 | 81-22616-1 |  |  | 0.75 | Other |  | Drip |  |  | Corrosion |  | 1981-06-18 | 1982-07-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACED 3/4" DRIP THAT WAS LEAKING WITH NEW PIPE + INSTALLED 3 RT BOX/ 7-18-82 VALLOT.
1 | 81-20736- |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1981-02-10 | 1981-02-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | TAPED SECTION 2' FROM VALVE. SERV. BADLY PITTED & SEAMS SPLIT. TAPED... SHOULD BE REPLACED ASAP.
2 | 81-20795- |  |  | 3 | Service |  | Valves |  |  | Material Failure |  | 1981-02-24 | 1981-02-24 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO
60 | 81-20795-1 | [10 empty] | 1981-02-23 | [5 empty] | SAN FRANCISCO
2 | 81-20802- |  |  | 2 | Service |  | Body of Pipe |  |  | Corrosion |  | 1981-02-25 | 1981-02-26 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | ...
60 | 81-21723-1 |  |  | 1 | Other |  | Drip |  |  | Corrosion |  | 1981-04-07 | 1982-03-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | 40% AT DRIP ... 1" DRIP LEAKING REPLACED 24" OF 1" PIPE WITH 3/4".
60 | 81-21967-1 |  |  | 8 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1981-05-05 | 1981-11-05 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO
1 | 81-22415- |  |  | 6 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1981-05-14 | 1981-05-20 | Bell Joint Seal |  | Cast/Ductile Iron |  | SAN FRANCISCO | DRILLED AND VENTED OVER MAIN. MARKED IN RED APPROX 26' S/N/L BUSH 29 W/E/L LYON. 5-14-81 BURKE. INST. (1) 6" AVON SEAL ON BELL JOINT. 5-20-81.
1 | 81-22386- |  |  | 1.5 | Service |  | Body of Pipe |  |  | Corrosion |  | 1981-04-30 | 1981-04-30 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | INSTALLED 1 1/2" ADAMS CLAMP UNDER FOUNDATION TUNNEL SERV IN FOR REPLACEMET. REPL. SERV. 4/30/81.
60 | 82-20683-1 |  |  | 1.25 | Other |  | Fitting |  |  | Material Failure |  | 1982-01-11 | 1982-11-24 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | TIGHTENED CAPO ON 1 1/4" LINE STOPPER MUELLER FITTING.
60 | 82-21300-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1982-03-09 | 1982-10-21 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | GREASED HP VALVE TO ... 10-21-81.
| 82-21678- | [5 empty] | Body of Pipe |  |  | Corrosion |  |  | 1984-01-09 | Replace Pipe and/or Service |  |  |  | SAN FRANCISCO | REPAIRED MAIN...
60 | 82-21678-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1982-12-08 | 1984-01-03 | Replace Pipe and/or Service | SOAP TAPE | Steel/Wrought Iron |  | SAN FRANCISCO | SOAP TAPE; SOAP & TAPE 1 1/2' SECTION OF 2" STL MAIN (SEAM SPLIT). MAIN WILL HAVE TO BE REPL OR SECTION CUT-OUT. 1-3-84 ALVAREZ.
| 82-24316- |  |  | 6 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1982-07-26 | 1983-05-19 | Bell Joint Seal |  | Cast/Ductile Iron |  | SAN FRANCISCO | CALL CREW. INST. 6" AVON SEAL.
60 | 82-25033-1 |  |  | 1.25 | Other | STATIC LINE | Body of Pipe |  |  | Corrosion |  | 1982-10-28 | 1983-08-22 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | MADE PERMANENT REPAIRS TO 1 1/4" X 4" SKINNER.
60 | 82-25284-1 |  |  | 2 | Service |  | Valves |  |  | Material Failure |  | 1982-11-01 | 1983-10-08 | Other |  |  |  | SAN FRANCISCO | STREET RESURFACING.
60 | 82-25299-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1982-11-04 | 1983-08-16 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | SERV. REPL 7-25-94 NIELSEN.
60 | 82-25302-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1982-11-05 | 1983-08-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO
60 | 82-25310-1 |  |  | 0.75 | Service |  | Valves |  |  | Material Failure |  | 1982-11-12 | 1983-08-23 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | TIGHTENED 3/4" MAIN VALVE AT SUB.
| 82-25316- |  |  | 4 | Service |  | Body of Pipe |  |  | Corrosion |  | 1982-11-15 | 1983-09-21 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | VENTED O/S AT MAIN. INSTALLED...
60 | 82-25318-1 |  |  | 4 | Distribution Main |  | Girth Weld |  |  | Construction Defect |  | 1982-11-15 | 1983-09-07 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SAN FRANCISCO
60 | 82-25376- |  |  | 0.35 | Service |  | Body of Pipe |  |  | Corrosion |  | 1982-12-10 | 1984-01-24 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | VENTED O/M. INST 3/4" ADAMS CLAMP ON SERV 1-24-84. SVC REPLACED. 7-9-94. BLOXHAM DC.
60 | 82-25395-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Corrosion |  | 1982-12-14 | 1984-01-30 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | VULCAN - 3-28-90; SOAPED & TAPED SERV. TEE, #20 REDONDO ST. 01-30-84. J. VITORELO. VULCAN REPL SVC - 3-28-90.
60 | 82-25387-1 |  |  | 4 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1982-12-03 | 1984-01-23 | Bell Joint Seal |  | Cast/Ductile Iron |  | SAN FRANCISCO | INST. 4 AVON SEAL, IN 4" CRAGS ...
60 | 82-25423-1 |  |  | 1 | Other |  | Valves |  |  | Other |  | 1982-11-12 | 1983-09-12 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | GREASED AND REDOPED 1" SHP VALVE... THREAD OUT COULD NOT DETERMINE WHERE IT TIES IN OR TO.
60 | 82-25424-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1982-11-12 | 1983-09-15 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO
60 | 82-40093-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1982-01-26 | 1982-01-26 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | INSTALLED 3/4" PERMANENT REPAIR CLAMP ON 3/4" NIPPLE...
60 | 82-40273-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1982-03-22 | 1982-03-22 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | CUT-OFF OLD ST. LIGHT 1' 15' E/W/L MINNA. 189' N/N/L 8TH ST. 3-22-82...
60 | 82-40300-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1982-03-09 | 1982-03-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | FOUND 3/4" DRIP NIPPLE LEAKING ALL OVER. REMOVED 3/4" FPR DRIP AND REPLACE WITH SAME. NIPPLE IS 34" LONG.
60 | 82-40942-1 |  |  | 8 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1982-10-07 | 1982-10-07 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | FOUND H.P. VALVE #162 LEAKING VERY BAD AT GREASE FITTING. REPACK FITTING AND TIGHTEN TOP. JOB COMPLETED. NO PAVING. 10-6-82 VALLOT.
60 | 82-40943-1 |  |  | 8 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1982-10-07 | 1982-10-07 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | FOUND H/P. VALVE #967 LEAKING VERY BAD AT GREASE FITTING. REPACK FITTING JOB COMPLETED. NO PAVING. 10-6-82 VALLOT.
60 | 82-41046-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1982-11-23 | 1982-11-23 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | CUT-OFF 10' OF ABANDONED LEAKING 3/4" GAS STREET LIGHT PIPE. 31' N/N/L JOHN ST. 23' N/S/L MASON.
60 | 83-21269- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1983-05-12 | 1984-05-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | DRILL & VENT OVER STREET & SIDEWALK AREA OVER MAIN & SERVICE. G. JEW 5-12-83. INST 2...
60 | 83-29080-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1983-10-28 | 1984-03-01 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACED 3/4" LEAKING DRIP WITH 3/4" DOUBLE WRAPPED NIPPLE. PAVING ORDER 3-2-84 VOLLET.
60 | 83-29247-1 |  |  | 0.75 | Other | DRIP | Fitting |  |  | Other |  | 1983-11-07 | 1984-04-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | STREET RESURFACING; REPLACED LEAK ON 3/" DRIP ON 8" STL MAIN. 4-16-84 LUCCHESE.
60 | 83-29595-1 |  |  | 1.25 | Other |  | Valves |  |  | Material Failure |  | 1983-12-21 | 1984-04-10 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO
60 | 83-29953- |  |  | 2 | Service |  | Tap Connection |  |  | Corrosion |  | 1983-12-10 | 1984-02-29 | Replace Pipe and/or Service | SOAP & TAPE | Steel/Wrought Iron |  | SAN FRANCISCO | SOAP & TAPE; VENTED. SEND CREW NEXT WEEK. VERY OLD SERVICE... READINGS OVER SERV AT MAIN, 12-16-83... SPECIAL SURVEY.
60 | 83-20331-1 |  |  | 3 | Other | DRIP | Valves |  |  | Other | GREASE PACKING | 1978-06-17 | 1983-07-05 | Other | GREASED | Steel/Wrought Iron |  | SAN FRANCISCO | CABLE CAR. GREASED VALVE AND REPLACED GREASE FITTING. 24' S/N CALIF. 6' E/W/L LIEDSDORFF.
60 | 83-21269- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1983-05-12 | 1984-05-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | DRILL & VENT OVER STREET & SIDEWALK AREA OVER MAIN & SERVICE. G. JEW 5-12-83. INST...
60 | 83-21418-1 |  |  | 4 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1983-01-12 | 1984-02-24 | Bell Joint Seal |  | Cast/Ductile Iron |  | SAN FRANCISCO
60 | 83-21858-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  | 1983-04-04 | 1984-04-10 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | STREET RESURFACING; FOUND ABANDONED 1" STREET LIGHT WITH A LEAKING CAP ON A NIPPLE. REMOVED MIPPLE AND REPLACED IT WITH A 1" PLUG, 261' S/O 22ND ST., 21' E/W/L YORK ST.
60 | 83-22128-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1983-01-11 | 1984-02-23 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | D+L O/SERV S/W AREA. 6-3-83 LIEBER... D+V P/S - OFF MAP 1-23-84 BOSSIER. INST. 3" PERM REPAIR CLAMP...
60 | 83-22364-1 |  |  | 2 | Distribution Main |  | Valves |  |  | Material Failure |  | 1983-02-17 | 1983-03-01 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | STREET RESURFACING; GREASED 2" HP NORD MAIN VALVE #732.
60 | 83-23688-1 |  |  | 0.75 | Other | STATIC LINE | Other |  | TEE | Other |  | 1983-06-28 | 1984-06-14 | Other | REDOPED CAP | Steel/Wrought Iron |  | SAN FRANCISCO | VENTED 6-28-83 BOSSIER. 50% OVER 6" HP MAIN IN SIDEWALK AREA NEAR PG&E M.H. TIGHTENED CAP ON 34" TEE FEEDING STATIC LINE.
60 | 83-23758- |  |  | 1.25 | Service |  | Fitting |  |  | Corrosion |  | 1983-06-06 | 1984-06-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | SERVICE TURNED... AFTER REPLACEMENT. DRILL & VENT AT SERVICE & MAIN ON LOWER GREAT HIWA. 40%-60% NEAR TEE @ MAIN. RED. SERV.
60 | 83-23977-1 |  |  | 1 | Other |  | Other |  |  | Material Failure |  | 1983-09-08 | 1984-07-14 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | TIGHTENED PLUG ON DRIP RISER 1" NO LEAK NOW. 7-14-84 BURTON.
60 | 83-27158-1 |  |  | 16 | Transmission |  | Girth Weld |  |  | Corrosion |  | 1983-11-03 | 1983-11-28 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SAN FRANCISCO | CABLE CAR PROJECT. REPAIR HEAVY PITTED 16z" OXY & ACT WELD WITH 16" WRINKLE BELLY, ARC WELD OVER LEAK. CORROSION HAD ATE AWAY 4" OF OLD WELD. PAVING UNDER 11-24-92 VALLOT.
60 | 83-40009-1 |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Material Failure |  | 1983-01-05 | 1983-01-05 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELD BROKE; NOTE: FOUND 16" HP OCT & ACT WELDS BROKEN ABOUT 10" ACROSS THE TOP. MADE REPAIRS WITH ONE 6" X 16" WRANKLE BELLU. COMPLETE REPAIRS BY ARC WELDING. PAVING ORDER XPD 1-5-82 VALLOT.
60 | 83-40080-1 |  |  | 2 | Other |  | Fitting |  |  | Other |  | 1983-02-01 | 1983-02-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPAIRED LEAK ON HP DRIP. REPLACED 2" PLUG ON NORD VALVE.
60 | 83-40122-1 |  |  | 4 | Other |  | Valves |  |  | Other |  | 1983-02-21 | 1983-02-21 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO
60 | 83-40213-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Corrosion |  | 1983-03-01 | 1983-03-18 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO
60 | 83-40230-1 |  |  | 0.75 | Other |  | Fitting |  |  | Other |  | 1983-03-23 | 1983-03-23 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | RETIGHTENED 3/4" FITTINGS & NIPPLES OUTSIDE OF METER ROOM ON 3/4" HP SERVICE.
60 | 83-40238-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1983-03-26 | 1983-03-26 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | ... LEAKING. 23' E/W/L TAYLOR. 12' N/S/L WATER.
60 | 83-40299-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Other |  | 1983-04-19 | 1983-04-19 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | CUT-OFF 1" STREET LIGHT AT MAIN HATCH 4-19-83.
60 | 83-40311-1 |  |  | 1.25 | Other |  | Fitting |  |  | Corrosion |  | 1983-04-11 | 1983-04-11 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | REMOVED LEAKING 1 1/4" X 3" NIPPLE AT 3/4" TAP HOLE ON 8" CILP MAIN. (NEED LEAK #).
60 | 83-40393-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1983-05-03 | 1983-05-03 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACED 3/4" RISER DRIP/
60 | 83-40453-1 |  |  | 1.25 | Other |  | Tap Connection |  |  | Material Failure |  | 1983-05-20 | 1983-05-20 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | 1 1/4" PLUG; READJUSTED 1 1/4" PLUG TO STOP LEAK. PAVING ORDER 5-20-83 VALLOT.;
60 | 74-00017-1 |  |  | 16 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-01-04 | 1974-01-25 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | MOBILE SURVEY; 70% GCB TO PARK & REC BLDG. WELDED PATCH ON 16" T.P. MAIN 4' S/N/L OF FELTON ST., 24' E/W/L OF HOLYOKE ST.
60 | 74-00025-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-01-04 | 1974-03-12 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | MOBILE SURVEY; ... 70% W.B. PERMIT APPLIED FOR EXPIRES ON JUL 30 1974.
60 | 74-00062-1 |  |  | 26 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-01-08 | 1974-01-11 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | 73$ MAIN LINE S/E CORNER OF INTERSECTION. 60% GAS 5' FROM BLDG. WELDED 2 PATCHED ON THE MAIN 20' W/E/L OF THIRD ST/ 26" HP MAIN 7' N/S/L OF 22ND ST.
60 | 74-00095-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-01-10 | 1974-01-18 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | 10' E/W/L QUINT. 10' S/N/L FAIRFAX. 100% BAR HOLES WEST SIDE OF ST. 250' S/O EVANS ST. INST. 2 - 2" PER. REPAIR CLAMPS.
60 | 83-40508-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1983-05-31 | 1983-05-31 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPAIRED BY VULCAN #1. INSTALLED 3/4" ADAMS CLAMP BELOW RISER INSIDE GARAGE.
60 | 83-40545-1 |  |  | 1 | Other |  | Fitting |  |  | Damage by outside Forces |  | 1983-06-02 | 1983-06-02 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | CUT & PLUGGED 1" STREET LIGHT SERVICE, PULLED BY CONTRACTOR. NEED CUT-OFF IN AM...
60 | 83-40572-1 |  |  | 1.25 | Other |  | Other |  |  | Material Failure |  | 1983-06-16 | 1983-06-16 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACED 1 1/4" ST. RISER WITH 1' OF 1 1/4" STEEL. 6-16-83, D. KERN.
60 | 83-40716-1 |  |  | 1 | Other |  | Fitting |  |  | Damage by outside Forces |  | 1983-07-20 | 1983-07-20 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | CUT OFF 1" ST LIGHT SERVICE @ MAIN (4" CILP OUT 14' N/S OF VALPARAISO) SCAFANI 7-20-83.
60 | 83-40720-1 |  |  | 4 | Other |  | COMPRESSOR COMPONENTS |  | DRESSER SLEEVE | Construction Defect |  | 1983-07-19 | 1983-07-19 | Other |  | Steel/Wrought Iron | STYLE 39-62 | SAN FRANCISCO | NOTE: FOUND 4" CI TO STH TRANSITION SLEEVE (39-62) LEAKING. READJUSTED ALL BOLTS TO STOP LEAKGAGE. PAVING ORDER. 7-19-83 VALLOT.
60 | 83-40723-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  | 1983-07-21 | 1983-07-21 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO
60 | 83-40945-1 |  |  | 0.72 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1983-09-13 | 1983-09-13 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | CUTT-OFF ABANDONED 3/4" STATIC LINE OFF FROM 16" CILP 20'N/S/L 16TH ST. 98' W/W/L ...
60 | 83-40965-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1983-08-18 | 1983-08-18 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | ... LEAKING & BURIED 3/4" DRIP TILL CONTRACTOR COMPLETES BLDG. DEMOLITION.
60 | 84-40200-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1984-02-10 | 1984-02-14 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO
60 | 84-40301-1 |  |  | 1 | Other |  | Body of Pipe |  |  | Corrosion |  | 1984-03-19 | 1984-03-19 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | CUT OFF OLD 1" SERVICE @ 4' CILD MAIN.
60 | 84-41233-1 |  |  | 1.25 | Other |  | Fitting |  |  | Damage by outside Forces |  | 1984-09-20 | 1984-09-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | INSTALLED 1 1/4" ...
60 | 84-21375-1 |  |  | 0.75 | Other | STATIC | Body of Pipe |  |  | Corrosion |  | 1984-01-04 | 1985-02-16 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | STREET RESURFACING; INSTALLED 3/4" PERMANENT REPAIR CLAMP ON STATIC LINE 22' S/N/L OF GEARY; LINE ON E/S 30TH OUT 24'. 2-16-85 ALVAREZ.
60 | 84-21648-1 |  |  | 2 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-03-02 | 1985-03-04 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | INST. 2" ADAMS... AND ENCAPSULATED CLAMP... MAIN IN BAD SHAPE. UNABLE TO CAP MAIN - LEAKING GASOLINE TANK CLOSE BY.
60 | 84-21693-1 |  |  | 1.25 | Other |  | Fitting |  |  | Other |  | 1984-01-13 | 1984-12-24 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | CALLED IN. INST. 1 1/4" THREAD CLAMP ON 1 1/4" BLOW OFF ON 16" HP MAIN. D+V O/M IN ST. + S/W 11-21-84 MACCAULAY.
60 | 84-22118- |  |  | 1.25 | Other |  | Body of Pipe |  |  | Corrosion |  | 1984-01-16 | 1984-01-16 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO
60 | 84-23747-1 |  |  | 2 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-03-05 | 1985-02-28 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | INST. 2" SKINNER PERM. REP. MAIN IN BAD SHAPE... 2/28/85.
60 | 84-28557-1 |  |  | 2 | Transmission |  | Fitting |  |  | Other |  | 1984-09-17 | 1985-11-05 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN FRANCISCO | STREET RESURFACING. TIGHTENED PLUG & CAP ON 2" MUELLER TEE. 11-5-85.
60 | 85-29424- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1985-09-05 | 1985-09-05 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | VULCAN; INST. 3/4" ADAMS CLAMP ON RISER 9-5-85.
60 | 86-20323-1 |  |  |  | Other |  | Other |  |  | Other |  | 1986-08-14 | 1986-08-14 | Other |  | Other |  | SAN FRANCISCO | SERVICE DEPT FIXED METER. SERVICE DEPT REMOVED LEAKING METER.
60 | 86-22404-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1986-04-03 | 1986-10-28 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | INSTALLED 1 - 4" PERM REPAIR CLAMP ON 4" TP MAIN 10-28-86.
60 | 86-26493-1 | [10 empty] | 1986-09-29 | [5 empty] | SAN FRANCISCO
60 | 86-26493-1 |  |  | 36 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1986-09-29 | 1987-10-22 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELDED 8 - PATCHES ON 36" LP MAIN.
60 | 87-23479-1 |  |  | 6 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1987-05-29 | 1988-02-22 | Bell Joint Seal |  | Cast/Ductile Iron |  | SAN FRANCISCO | INSTALLED 1 - 6" AII
60 | 87-23759-1 |  |  | 4 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1987-07-31 | 1988-03-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN FRANCISCO | TIGHTENED BOLTS ON 4" D.E. FLANGE W MANHOLE.
60 | 85-25262-1 |  |  | 6 | Distribution Main |  | Bell Joint |  |  | Material Failure |  | 1985-05-14 | 1986-04-11 | Bell Joint Seal |  | Cast/Ductile Iron |  | SAN FRANCISCO | INSTALL 1 - 6" AVON SEAL.
60 | 87-24990-1 |  |  | 0.75 | Service |  | Valves |  |  | Construction Defect |  | 1987-09-04 | 1987-09-08 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN FRANCISCO
60 | 88-80636-1 |  |  | 20 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1988-04-06 | 1988-04-06 | Bell Joint Seal |  | Cast/Ductile Iron |  | SAN FRANCISCO | INSTALLED 1 - 20" SIV AVON SEAL.
60 | 88-81598-1 |  |  | 4 | Distribution Main |  | Valves |  |  | Other |  | 1988-12-20 | 1988-12-20 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPACKED 4" H.P. VALVE #850.
60 | 89-80825-1 |  |  | 1.25 | Service |  | Other Welds |  |  | Digin |  | 1989-10-11 | 1989-10-11 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | REOVE ABANDONED 1 1/4" TEE DIE TO DIGIN & WELD PATCH ON 4" H.P. MAIN
60 | 89-80879-1 |  |  | 0.75 | Service |  | Valves |  |  | Digin |  | 1989-11-03 | 1989-11-03 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | CUT-OFF 10' OF 3/4" STL DUE TO HIT.
60 | 89-25055-1 |  |  | 4 | Distribution Main |  | Valves |  |  | Other |  | 1989-10-27 | 1989-12-14 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | GREASE VALVE IN GUB
60 | 76-22322-1 |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-05-04 | 1976-07-19 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SAN FRANCISCO | 70% OVER MAIN LEAKING AT...
60 | 90-40015-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1990-09-18 | 1990-09-18 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | SPECIAL SURVEY. LVE W CURB.
60 | 91-20868-1 | [16 empty] | SAN FRANCISCO | 0 READINGS 6-8-91.
60 | 92-21378-1 |  |  | 16 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1992-04-06 | 1992-10-09 | Tighten Cap or Bolt | REPLACE PIPE | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACE BOLTS ON 16" LP FLANGE VALVE (#1-7)
60 | 92-21379-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1992-04-06 | 1992-10-07 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELD 9" X 8" PATCH ON SIDE OF 12" HP MAIN AT CROSSWALK IN ST.
60 | 92-21380-1 |  |  | 12 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1992-04-06 | 1992-10-22 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN FRANCISCO | REDOPE & RETIGHTEN CAP ON 2" SAVE-A-VALVE ON TOP OF 12" HP MAIN.
60 | 92-21381-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1992-04-06 | 1992-10-21 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELD 7" X 7" PATCH ON TOP OF 12" HP STL MAIN.
60 | 90-23677-1 |  |  | 12 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1990-08-28 | 1990-08-28 | Tighten Cap or Bolt |  |  |  | SAN FRANCISCO | TIGHTEN FITTING 3/4" COCK IN REG PIT ON 3/4" LOAD LINE.
6 | 76-00016-1 |  |  | 1.25 | Other |  | Other |  |  | Other |  | 1972-01-10 | 1972-01-10 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | CUT + CAPPED 1 1/4" SERVICE TIED TO DEAD MAIN W/ LEL RENDING + ODOR.
60 | 72-25009-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1972-10-17 |  | Other |  | Other |  | SAN FRANCISCO
60 | 72-25059-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1972-11-02 | 1972-12-01 | Other |  | Other |  | SAN FRANCISCO | NO READINGS M.S.A...
60 | 72-25156-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1972-11-16 | 1973-02-15 | Other |  | Other |  | SAN FRANCISCO | REF. LEAK 72-25157; NO READINGS. STREET RESURFACING.
60 | 72-25304-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1972-11-12 |  | Other |  | Other |  | SAN FRANCISCO | FOUND NO READINGS 11-30-72. STREET RESURFACING.
60 | 71-30104-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1971-11-30 |  | Other |  | Other |  | SAN FRANCISCO
60 | 71-30107-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1971-12-01 |  | Other |  | Other
60 | 71-30211-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1971-12-15 |  | Other |  | Other |  | SAN FRANCISCO | NO READING IN AREA.
60 | 84-22733-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Other |  | 1984-01-06 | 1985-01-23 | Other |  | Other |  | SAN FRANCISCO | 1-23-85 REPLACED PLASTIC TO SLT TRANSITION (1/2 TO 3/4) ON 1/2 PLASTIC SERVICE 91' N/O SUNNYDALE AT G.V.B.
60 | 84-22736-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1984-01-06 | 1985-01-29 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | INSTALLED 6" PERM-REPAIR CLAMP TO 6" HP STL MAIN 1-29-85.
60 | 84-22775-1 |  |  | 0.75 | Service |  | Tap Connection |  |  | Material Failure |  | 1984-08-13 | 1985-01-30 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | CALLED CREW. 24 RECHECK VENTED O/M IN PLANTER AREA 1-29-85 BOSSIER. CREW AM. REDOPED & TIGHTENED COMPLETION PLUG ON SERVICE TEE.
60 | 84-22781-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1984-08-21 | 1985-10-29 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | INST. 1 - 2' X 3" PERM REPAIR CLAMP ON 2" MAIN 10/29/85 ...
60 | 92-22062-1 |  |  | 6 | Distribution Main |  | Fitting |  |  | Other |  | 1992-08-31 | 1993-04-26 | Tighten Cap or Bolt |  | Cast/Ductile Iron |  | S.F. | TIGHTEN 1 1/4" PLUG ON 6" CILP GAS MAIN.
60 | 92-22112-1 |  |  | 1.25 | Service |  | Valves |  |  | Other |  | 1992-10-15 | 1993-07-15 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | SERVICED 1 1/4" NIBCO VALVE IN SIDEWALK.
| 93-22689-1 |  |  | 16 | Distribution Feeder Main |  | Body of Pipe |  |  | External Corrosion |  | 1993-10-26 | 1994-03-04 | Replace Pipe |  | Steel/Wrought Iron |  | S.F. | WELD 8" X 10" PATCH ON 16" HP
| 93-80222-1 |  |  | 4 | Gathering |  | Bell Joint |  |  | Other |  | 1993-06-11 | 1993-06-11 | Bell Joint Seal |  | Cast/Ductile Iron |  | S.F. | PERMABOND 4" BELL JOINT IN STREET
| 94-21173-1 |  |  | 16 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1994-03-23 | 1994-03-24 | Other |  | Steel/Wrought Iron |  | SAN FRANCISOC | LINE SIZE NOT CLEAR.; VENTED VALVE PIT. SVC V#253, STOP GAS LEAK. (REMARK NOT LEGIBLE)
60 | 94-21783-1 |  |  | 4 | Distribution Feeder Main |  | Bell Joint |  |  | Material Failure |  | 1994-08-18 | 1995-09-30 | Bell Joint Seal |  | Cast/Ductile Iron |  | SAN FRANCISCO | 4" CI BELL (REMARK NOT LEGIBLE)
60 | 94-21949-1 |  |  | 6 | Distribution Main |  | Other |  |  | Other |  | 1994-12-23 | 1996-02-13 | Other |  | Cast/Ductile Iron |  | SAN FRANCISCO | P/B (1) 6" BJ
60 | 94-21949-1 |  |  | 6 | Distribution Main |  | Other |  |  | Other |  | 1994-12-23 | 1996-02-13 | Other |  | Cast/Ductile Iron |  | SAN FRANCISCO | P/B (1) 6" BJ
60 | 94-80467-1 |  |  | 16 | Distribution Feeder Main |  | Girth Weld |  |  | Construction Defect |  | 1994-09-29 | 1994-10-05 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELDED PASS OVER LEAKING WELD ON 16" HP
60 | 94-80501-1 |  |  | 0.75 | Gathering |  | Drip |  |  | External Corrosion |  |  | 1994-11-08 | Replace Pipe |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACED 3/4 DRIP PIPE (BURRIED)
60 | 95-21035-1 |  |  | 8 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1995-05-23 | 1995-12-08 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | REGREASE LEAKING FLANGE VALVE IN GVB
60 | 95-21055-1 |  |  | 8 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1995-06-22 | 1996-05-17 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | GREASED 8" NORD VALVE.; FOUND TWO INDIVIDUAL A-FORMs WITH DIFFERENT LEAK NUMBER STICK TOGETHER, PLEASE SEPERATE IT.
| 97-21355-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | External Corrosion |  | 1997-08-14 | 1997-08-14 | Replace Pipe |  | Steel/Wrought Iron |  | SAN FRANCISCO | UNABLE TO READ LEAK CAUSE.; REPLACED 2' OF 3/4" DRIP PIPE INSIDE G.J.B. TO #1 NEWBURY ST. (REMARK NOT LEGIBLE)
| 97-80145-1 |  |  | 0.5 | Transmission |  | Body of Pipe |  |  | Digin |  | 1997-04-21 | 1997-04-21 | Other |  | TR 418 |  | SF | REPAIRED 4" X 1/2" PL TEE (BLOW OFF)
| 97-80388-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1997-11-10 |  | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELD PATCH
60 | 97-80399-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1997-11-14 | 1997-11-14 | Replace Pipe |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACED 24" OF 3/4" DRIP PIPE.
| 99-21378-1 |  |  | 0.5 | Transmission |  | Plastic Tee Cap |  |  | Other |  | 1999-09-01 | 2000-11-14 | Tighten Cap or Bolt |  | TR 418 |  | SAN FRANCISCO | TIGHTEN CAP ON TEE; NO PROTECTION
60 | 92-21380-1 |  |  | 12 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1992-04-06 | 1992-10-22 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN FRANCISCO | REDOPED & RETIGHTEN CAP ON 2" SAVE-A-VALVE ON TOP OF 12" HP MAIN
60 | 92-21379-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1992-04-06 | 1992-10-07 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELD 9"X8" PATCH ON SIDE OF 12" HP MIAN AT CROSSWALK IN ST
60 | 91-22001-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1991-04-29 | 1992-02-12 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | REGREASE LEAKING 4" HP VALVE #255 IN GVB IN ST.
|  |  |  | 2 | Gathering | [10 empty] | TR 418 |  | SAN FRANCISCO
|  |  |  | 2 | Gathering | [10 empty] | Steel/Wrought Iron |  | SAN FRANCISCO
|  |  |  | 2 | Gathering | [10 empty] | PE 100
| 05-20525-1 |  |  | 1 | Service |  | Riser |  |  | Construction Defect |  |  | 2006-01-17 | Replace Partial Service |  | Copper |  | SAN FRANCISCO | INSTALL STYLE 88 TEE & 6" SADDLE ONTO CI MAIN; REPLACE SERVICE MAIN TO VALVE
[13 empty] | 1996-11-13 |  |  |  |  | SAN FRANCISCO | INST REMOTE ETX STATION ON #109 TIP MAIN
| 04-21662-1 |  |  | 1.5 | Service |  | Body of Pipe |  |  | External Corrosion |  |  | 2006-02-03 | Replace Entire Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | INSTALL STYLE 88 TEE & 4" SADDLE ONTO CI MAIN; REPLACE SERVICE: MAIN TO RISER
60 | 92-22058-1 |  |  | 26 | Transmission |  | Valves |  |  | Other |  | 1992-08-27 | 1993-04-22 | Other |  | Steel/Wrought Iron |  | S.F. | GREASED BURIED -- VALVE ON TRANSMISSION MAIN
60 | 91-21099-1 |  |  | 0.75 | Other |  | Other |  |  | Other |  | 1991-06-25 | 1992-02-18 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | SHUT OFF OLD 3/4" STATIC LINE IN REG. PIT #209 A. FEEDING OLD 6" C.I. MAIN
| 93-80308-1 |  |  | 24 | Transmission |  | Tap Connection |  |  | Digin |  | 1993-07-27 | 1993-07-27 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | INST. 1 - 10" X 10" PATCH ON MAIN HIT BY CONTRACTOR #132
|  |  |  | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN FRANCISCO | RECONDITIONED A.O. SMITH PIPE.
60 |  |  |  | 2 | [7 empty] | 1990-01-31 | 1990-01-31 |  |  |  |  | SAN FRANCISCO | CUT OFF 2" TP SER. WELD CAPON MUELLER TEE AT 2" TP MAIN
[18 empty] | SAN FRANCISCO | INST. 9 1/2" NEW 3/4" STL. SER.
60 | 87-80073-1 |  |  | 2 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-04-21 | 1987-04-21 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | INSTALLED 1 - 2" SKINNER PERM. REPAIR CLAMP
56 | 79-40382-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-09-05 | 1979-09-06 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SO SF | WELDED PATCH OVER PIT HOLE TO STOP LEAK ON TRANSMISSION MAIN
60 | 78-27094-1 |  |  | 2 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-11-08 | 1979-01-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO
|  |  |  | 2 | Gathering | [10 empty] | Steel/Wrought Iron |  | SAN FRANCISCO
|  |  |  | 24 | [7 empty] | 2001-05-18 |  |  |  | Steel/Wrought Iron |  | SAN FRANCISCO | REWRAPPED 2' OF 24" TP MAIN
|  |  |  | 24 | [7 empty] | 2001-05-18 |  |  |  | Steel/Wrought Iron |  | SAN FRANCISCO | REWRAPPED 2' OF 24" TP MAIN
|  |  |  | 2 | Gathering | [10 empty] | Steel/Wrought Iron |  | SAN FRANCISCO
56 | 79-40382-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-09-05 | 1979-09-06 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SO SF | WELDED PATCH OVER PIT HOLE TO STOP LEAK ON TRANSMISSION MAIN
6 | 72-00018-1 |  |  | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-01-10 | 1972-01-13 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO
60 | 72-40101-1 |  |  | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-01-31 | 1972-01-31 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELDED 4 PATCHES - 1 WELD REINFORCEMENT BAND
60 | 72-40663-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-09-25 | 1972-09-25 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPAIRED BY WELDING PATCH 1'X1'
60 | 73-23468-1 |  |  | 26 | Transmission |  | Other |  |  | Material Failure |  | 1973-08-08 | 1973-08-29 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | 1 1/4; PLUG LEAKING IN STEEL MAIN TIGHTEN CAMP
60 | 77-40459-1 |  |  | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1977-09-29 | 1977-10-04 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | 9/30/77 - TEMP. REPAIRED WITH PATCH & CHAIN CLAMP
60 | 75-60306-1 |  |  | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-01-09 | 1975-03-06 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | INST 2 - 12" X 12" WELD PATCHES ON 26" HP MAIN ALSO 8" X 6" PATCH.
60 | 77-00090-1 |  |  | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1977-11-14 | 1977-11-14 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPAIRED PIT HOLE ON 26" WITH WELDED PATCH - PIT HOLE NEAR TOP OF MAIN
60 | 78-20550-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-05-11 | 1980-03-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | LEAK ON BOTTOM SIDE OF 16" PENN MAIN WITHIN CASING, CASING LAYING ON CONCRETE BOX SEWER. REPAIR CAN'T BE MADE. SECTION WITHIN CASING SHOULD BE REPLACED.
60 | 78-25652- |  |  | 20 | Transmission |  | Valves |  |  | Other |  | 1978-10-25 | 1978-10-25 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | T&R LUBE VALVE NO READING
60 | 78-27094-1 |  |  | 2 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-11-08 | 1979-01-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | PIPE FOR BLOW OFF REMOVED OLD RISER.
| 79-22172- |  |  | 2 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-02-06 | 02/00/1979 | Other |  | Steel/Wrought Iron
60 | 79-40114-1 |  |  | 6 | Transmission |  | Fitting |  |  | Material Failure |  | 1979-02-14 | 1979-02-14 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | INSTALL (2) 4" CANS ON 6" T.P. MAINS 4" IN CURB ON SHAFTER & IN CURB ON INDUSTRIAL; FOUND 2 - 2" PLUGS LEAKING THIS MAIN WAS CONVERTED TO T.P.
60 | 79-40251-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-03-13 | 1979-03-21 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | INST. TWO 12" X 12", ONE 6" X 6" & ONE 4" X 4" PATCH 16" HP MAIN
60 | 79-40252-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-03-13 | 1979-03-21 | Patch Welded |  | Steel-Other |  | SAN FRANCISCO | INST. (1) 4" X 4" PATCH ON 16" HP MAIN.
60 | 79-40253-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-03-13 | 1979-03-21 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | INST (1) 4" X 4" PATCH ON 16" HP MAIN
60 | 80-40746-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1980-10-21 | 1980-10-29 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | INST. ONE 7"X6" PATCH. ALSO INST. ONE 9LB. ANODE.
60 | 80-20432-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1980-01-28 | 1981-04-17 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | INST 1-PATCH ON 16" TP MAIN
| 81-21271- |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1981-04-16 | 1981-04-27 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPAIR CLAMP; REPLACED 10' 6" T.P. MAIN
60 | 83-41248-1 |  |  | 16 | Transmission |  | Girth Weld |  |  | Corrosion |  | 1983-11-29 | 1983-11-29 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPAIR HEAVY PITTED 16" OXY & ACT. WELD WITH 16" WRINKLE BELLY ARC WELDED OVER CORROSION LEAKS THAT HAVE ATE AWAY 6" OR SO AT THE OLD WELD.
60 | 83-41247-1 |  |  | 6 | Transmission |  | Valves |  |  | Corrosion |  | 1983-11-29 | 1983-11-29 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | FOUND 6" HP VALVE, BOLTS HAD COMPLETELY CORROD TO THE EFFECT THEIR WAS NO LONGER EFFECTIVE IN HOLDING THE FLANGES TOGETHER. REPAIRED WITH EIGHT NEW FLANGE BOLTS
1 | 83-21161- |  |  | 16 | Other |  | Body of Pipe |  |  | Corrosion |  | 1983-03-11 | 1984-02-06 | Patch Welded |  | Steel/Wrought Iron |  |  | INST. ONE 8" X 10 " PATCH ON 16" T.P. MAIN
60 | 85-22323-1 |  |  | 2 | Transmission |  | Fitting |  |  | Other |  | 1985-04-19 | 1985-10-22 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN FRANCISCO | TIGHTEN PLUG AND CAP ON 2" PCF.
60 | 85-22322-1 |  |  | 2 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1985-04-19 | 1985-10-23 | Clamp |  | Steel/Wrought Iron |  | SF | INSTALLED 2" PERM REPAIR CLAMP ON MAIN.
60 | 85-22321-1 |  |  | 2 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1985-04-19 | 1985-10-24 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | INSTALLED 2" PERM REPAIR CLAMP ON TP MAIN.
60 | 86-22096-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1986-02-08 | 1986-08-27 | Patch Welded |  | Steel/Wrought Iron |  | SF | WELD PATCH ON 16" STL T.P. MAIN
60 | 86-23243-1 |  |  | 4 | Transmission |  | Other Welds |  |  | Construction Defect |  | 1986-05-30 | 1987-01-05 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELD ON 4" T.P. MAIN. HAD WELDER RUN A COUPLE OF PASSER OVER
60 | 86-25644-1 | [10 empty] | 1986-09-19 | [5 empty] | SAN FRANCISCO
60 | 86-25644-1 |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1986-09-19 | 1987-09-24 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | GREASED VALVES #881 # #882
60 | 86-25834-1 | [10 empty] | 1986-08-19 | [5 empty] | SAN FRANCISCO
60 | 86-25834-1 |  |  | 26 | Transmission |  | Valves |  |  | Other |  | 1986-08-19 | 1987-07-13 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | GREASE VALVE #862 ON TP MAIN
60 | 86-26487- |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-01-22 | 1987-01-22 | Patch Welded |  | Steel/Wrought Iron |  |  | WELDED 12" X 12" PATCH ON 20" TP MAIN
60 | 84-21232- |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-04-26 | 1984-04-26 | Patch Welded |  | Steel/Wrought Iron |  |  | WELD PATCH ON 20' MAIN; 6" X 6" PATCH;
60 |  |  |  | 20 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1984-10-10 | 1984-10-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | MADE PERM REPAIR ON 20" TRANS. MAIN; WELDED 3 PATCHES ON MAIN
60 | 84-40332-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-03-12 | 1984-03-12 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELDED 6"X
60 | 87-21328-1 |  |  | 4 | Transmission |  | Fitting |  |  | Other |  | 1987-02-26 | 2008-01-06 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | INSTL 2" THREAD CLAMP ON 2" THREADED COUPLING WITH NIPPLE OFF 4" TP MAIN
60 | 87-21328-1 |  |  | 4 | Transmission |  | Fitting |  |  | Other |  | 1987-02-26 | 2008-01-06 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | INSTL 2" THREAD CLAMP ON 2" THREADED COUPLING WITH NIPPLE OFF 4" TP MAIN
60 | 87-21338-1 |  |  | 2 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-02-27 | 1988-01-14 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | INSTL 1 - 2" PERM REPAIR CLAMP ON STL MAIN
60 | 87-80073-1 |  |  | 2 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-04-21 | 1987-04-21 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | INSTALLED 1 - 2" SKINNER PERM. REPAIR CLAMP
60 | 87-21587-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-03-04 | 1987-04-06 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELDED PATCH ON 16" TP MAIN
60 | 87-21807-1 |  |  | 2 | Transmission |  | Valves |  |  | Material Failure |  | 1987-03-25 | 1988-01-07 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN FRANCISCO | TIGHTENED PACKING ON 2" BLOW-OFF VALVE
60 | 87-22939-1 |  |  | 8 | Transmission |  | Valves |  |  | Other |  | 1987-05-06 |  | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | SERVICED VALVE #967 GREASED
60 | 87-23529-1 |  |  | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-09-23 | 1987-10-15 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELD PATCH ON 26" MAIN
60 | 87-25313-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-09-19 | 1987-09-21 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELD PATCH ON 16" HP MAIN LEAKING AT PINHOLE
60 | 88-21830-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1988-04-26 | 1988-06-30 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELDED PATCH ON 20" TP MAIN #101
60 | 90-23704-1 |  |  | 26 | Transmission |  | Valves |  |  | Other |  | 1990-08-21 | 1990-08-29 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | GREASE 26" TP VALVE
60 | 90-40022-1 |  |  | 20 | Transmission |  | Other Welds |  |  | Other |  | 1990-09-18 | 1990-09-18 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELD PATCH OVER LEAKING WELD ON 20" TP MAIN
60 | 91-23888-1 |  |  | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1991-11-07 | 1992-06-10 | Patch Weld - Weld |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELDED 8"X9" PATCH ON TP MAIN IN STREET
| 91-208-1 |  |  | 3 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1991-02-06 | 1991-02-09 | Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | T & MS. REPAIR CLAMP PITT ON 3" STL TP MAIN
60 | 92-22058-1 |  |  | 26 | Transmission |  | Valves |  |  | Other |  | 1992-08-27 | 1993-04-22 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | GREASED & BURIED VALVE ON TRANSMISSION MAIN
60 | 92-22100-1 |  |  | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1992-09-30 | 1993-06-18 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELDED 6"X6" PATCH ON 26" T.P. MAIN
60 | 93-22460-1 |  |  | 26 | Transmission |  | Valves |  |  | Other |  | 1993-09-22 | 1994-09-09 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | HAD 26" VALVE OFF MAIN #109 GREASED
| 93-80308-1 |  |  |  | Transmission |  | Tap Connection |  |  | Digin |  | 1993-07-27 | 1993-01-27 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | INST 1 - 10" X 10" PATCH ON MAIN NOT BY
60 | 95-22119-1 |  |  | 20 | Transmission |  | Valves |  |  | Material Failure |  | 1995-10-23 | 1997-03-19 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | REPLACED FAIRCHILD 24 SNAP ACTING REBYS
60 | 97-21747-1 |  |  | 2 | Transmission |  | Valves |  |  | Other |  | 1997-10-13 | 1999-04-07 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | GREASED 2" T.P. MAIN VALVE #109
| 97-21912-1 |  |  | 20 | Transmission |  | Girth Weld |  |  | Corrosion |  | 1997-10-04 | 1997-11-01 | Replace Pipe |  | Steel/Wrought Iron |  | SAN FRANCISCO | CUT IN SECTION 20" STEEL SERVICE
| 97-21912-1 | [10 empty] | 1997-10-04 | [5 empty] | SAN FRANCISCO
| 99-80327-1 |  |  | 24 | Transmission |  | Valves |  |  | Unknown |  | 1999-11-12 | 1999-11-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN FRANCISCO | GUB; TIGHTEN BONNETT TO CHART BOX #109
| 99-80333-1 |  |  | 24 | Transmission |  | Other |  | PIEDO TUBE | Other | FITTING | 1999-11-12 | 1999-11-18 | ABANDON |  | Steel/Wrought Iron |  | SAN FRANCISCO | ELIMINATED PLEDO TUBE ASSEMBLY INSTALLED PLUG & CAP ON 1 1/4" MUELLER FITTING
| 00-20856-1 |  |  | 1.5 | Gathering |  | Fitting |  |  | Other |  | 2000-04-13 | 2001-06-13 | Soap and/or Tape - Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | SOAP & TAPE 1' OF 1 1/2" LP STL GAS SVC AT MAIN
| 01-20641-1 |  |  | 6 | Transmission |  | Other |  | FLANGES | Other | BAD GASKET | 2001-04-03 | 2002-01-11 | Other | SEE COMMENTS | Steel/Wrought Iron |  | SAN FRANCISCO | VALVE #851 BY-PASSING CAUSING LEAK @ 6" BLOW OFF FLANGE AND ___ REPLACE GASKET AND
| 03-20491- |  |  | 6 | Transmission |  | Valves |  |  | Other | DRY GREASE | 2003-03-26 | 2003-03-27 | Other | GREASE VALVE | Steel/Wrought Iron |  | SAN FRANCISCO | GREASED 6" TP MAIN VALVE #851
| 05-20577-1 |  |  | 24 | Transmission |  | Valves |  |  | Other | DRY GREASE | 2005-09-07 | 2005-09-07 | Other | GREASED VALVE | Steel/Wrought Iron |  | SAN FRANCISCO | GREASED VALVE
| 07-20576-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2007-10-16 | 2011-01-14 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | INST 4" FULLER CL.
| 07-20576- | [16 empty] | SAN FRANCISCO
| 07-20576-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2007-10-16 | 2011-01-14 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | INST 4" FULLER CL.; UNPROTECTED AREA (1957 MAIN) BC 1/20/11
| 07-80162-1 |  |  | 1.5 | Service |  | Body of Pipe |  |  | External Corrosion |  | 2007-08-02 | 2007-08-02 | Soap and/or Tape - Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | SOAP & TAPE 2' OF 1 1/2" LP STL GAS SVC
| 08-20001-1 |  |  | 1 | Single Service |  | Valves |  |  | Unknown |  | 2008-01-02 | 2008-06-05 | Soap and/or Tape - Other |  | Copper |  | SAN FRANCISCO | SOAP & TAPE SIDEWALK VALVE
| 08-20288-1 |  |  | 0.5 | Single Service |  | Valves |  |  | Construction Defect |  | 2008-05-15 | 2008-05-15 | Replace Valve < 2 inch |  | PE2406 (Yellow or Orange) |  | SAN FRANCISCO | REPLACE CURB VALVE
| 08-21289-1 |  |  | 0.75 | Transmission |  | Other |  | THREADS | Construction Defect |  | 2008-10-01 | 2008-11-14 | Replace Partial Service |  | Steel/Wrought Iron |  | SAN FRANCISCO | CUT - OUT 3/4 CURB VALVE
| 09-80335-1 | L101 | 42.35 | 20 | Transmission |  | Body of Pipe |  |  |  |  | 2009-11-11 | 2009-11-13 | Other | .375 FULL CIRCLE SLEEVE 50K SMYS | Steel/Wrought Iron |  | SAN FRANCISCO | WELDED SLEEVE OVER BACK IN T 20" MAIN (TRANSMISSION MAIN; FULL CIRCLE SLEEVE REPAIR BY GC OQ WELDERS; REPAIR OVER INWARD PROTRUDING DENT 1" AND HOLE X-RAY'D LONG SEAM MAG PRACTICAL CIRC WELD 20" PIPE UNDER FIBER OPTICS DUCT BANK
60 | 09-80335-1 | 101 | 42.35 | 20 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | Digin/Excavation |  | 2009-11-11 | 2009-11-13 | Welded Sleeve/Can - Weld |  |  |  | SAN FRANCISCO | \WELDED SLEEVE OVER HOLE IN T-20" MAIN
60 | 09-80335-1
| 09-20958-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2009-07-02 | 2010-12-10 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | SS CLAMP
| 09-20958-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2009-07-02 | 2010-12-10 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | SS CLAMP; UNPROTECTED MAIN (1936) BC 12/22/10
| 09-20979-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Material Failure |  | 2009-07-28 | 2011-01-19 | Other | REPLACED 2 - 2" METIFITS WITH 4 - 2" ELECTROFUSION COUPPLINGS | PE2406/2708 (Yellow) |  | SAN FRANCISCO | REPLACED 2 -2 " MET FIT COUPLING; R/R 2 -2" METFITS WITH 4 - 2" ELECTRICFUSION COUPLINGS
| 09-21001-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2009-07-13 | 2011-01-12 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | INSTALL LEAK CLAMP
| 09-21008-1 |  |  | 8 | Distribution Main |  | Other Welds |  |  | Weld Failure |  | 2009-07-20 | 2011-01-14 | Direct Deposition Weld - Weld |  | Steel/Wrought Iron |  | SAN FRANCISCO | DIRECT DEP WELD
| 09-21050- |  |  | 4 | Distribution Main <= 60 PSIG |  | Bell Joint |  |  | Construction Defect |  | 2009-08-17 | 2011-01-27 | Bell Joint Permabond - Cast Iron |  | Cast Iron |  | SAN FRANCISCO | PERMABOND
| 10-20643-1 |  |  | 6 | Distribution Main |  | Bell Joint |  |  | Construction Defect |  | 2010-08-27 | 2010-11-19 | Bell Joint Permabond - Cast Iron |  | Cast/Ductile Iron |  | SAN FRANCISCO | PERMA BOND 1 - 6" CILP - BJ
| 10-21130-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-11 | 2010-11-17 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | INST 6" FULL CIRCLE CLAMP
60 | 11-20309-B | 132 |  | 6 | Transmission >= 20% SMYS |  | Line Valve |  |  | Construction Defect |  | 2011-04-17 | 2011-04-20 | Greased - Other |  | Steel-Other |  | SAN FRANCISCO | GREASED VALVE
| 10-21130-1 | [10 empty] | 2010-10-11 | [5 empty] | SAN FRANCISCO
| 10-21130-1 |  |  | 6 | Distribution Main |  |  |  |  | External Corrosion |  | 2010-10-11 | 2010-11-17 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | SAN FRANCISCO | INST 6" FULL CIR CLAMP
| 10-21296-1 |  |  | 4 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2010-10-13 | 2011-01-06 | Tighten Cap or Bolt |  | Cast/Ductile Iron |  | SAN FRANCISCO | TIGHTEN SADDLE
| 10-21399-1 |  |  |  | Distribution Main |  | Fitting |  |  | Incorrect Operation |  | 2010-10-18 | 2011-01-10 | Tighten Cap or Bolt |  | Cast/Ductile Iron |  | SAN FRANCISCO | TIGHTEN 6" END CAP
| 10-21542-1 |  |  | 4 | Distribution Main |  | Bell Joint |  |  | Damage by Earth Movement |  | 2010-10-25 | 2011-01-18 | Bell Joint Permabond - Cast Iron |  | Cast/Ductile Iron |  | PRESIDIO | PERMABOND BELL JOINT
| 10-80257-1 |  |  | 0.5 | Single Service |  | Valves |  |  | Construction Defect |  | 2010-10-22 | 2010-10-22 | Replace Valve < 2 inch |  | Aldyl A (Tan or Gray) |  | SAN FRANCISCO | R/R 1 - 1/8" PLASTIC CURB VALVE
| 02-80381-1 |  |  | 1.25 | Gathering |  | Valves |  |  | Other | LOOSE BONNETT | 2002-09-17 | 2002-09-17 | Other | TIGHTEN BONNETT | Steel/Wrought Iron |  | SAN FRANCISCO | TIGHTEN BONNETT ON SVC VALVE IN SIDEWALK
| 03-21198-1 | 101 |  | 0.75 | Single Service |  | Valves |  |  | Construction Defect |  | 2003-09-19 | 2008-04-21 | Other | GREASED 3/4 PLUG VALVE | Steel/Wrought Iron |  | SAN FRANCISCO | GREASED 3*4 PLUG VALVE
| 03-21450- | [10 empty] | 2003-09-22 | [5 empty] | SAN FRANCISCO | 40 LEL AT BLDG 20% O/MAIN NOT OUR GAS
| 03-21451-1 |  |  | 200 | Service |  | Valves |  |  | Construction Defect |  | 2003-09-22 | 2005-03-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN FRANCISCO | TIGHTEN BONNETT ON 2" GAS VALVE
| 06-20014-1 |  |  | 0.75 | Service |  | Valves |  |  | Construction Defect |  | 2006-03-02 | 2006-03-02 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | GREASED 3/4 PLUG VALVE
| 06-20116-1 | 132 |  | 1 |  |  | Unknown |  |  | Unknown |  | 2006-03-08 |  |  |  | Steel/Wrought Iron |  | SAN FRANCISCO
| 08-20042-1 | 132 |  | 0.75 | Single Service |  | Valves |  |  | Construction Defect |  | 2008-03-07 | 2008-03-07 | Other | TIGHTEN VALVE | Steel/Wrought Iron |  | SAN FRANCISCO | TIGHTEN 3/4 BYPASS
| 09-90330-1 | [10 empty] | 2009-07-14 | [5 empty] | SAN FRANCISCO | 0 OUT ZERO OUT LEAK
| 91-22001-1 |  |  | 4 |  |  | Valves |  |  | Material Failure |  |  | 1992-02-12 | Other |  | Steel/Wrought Iron |  |  | REGREASE LEAKING 4" HP VALVE #255 IN GVB IN ST.
60 | 11-20022-B | 101 |  |  | Single Service |  | Curb Valve |  |  | Construction Defect |  | 2011-04-09 | 2011-04-09 | Greased - Other |  | Steel-Other |  | SAN FRANCISCO | GREASED 3/4" CURB VALVE
60 | 11-20306-A | 132 |  | 0.75 | Single Service |  | Riser Valve Threads |  |  | Construction Defect |  | 2011-04-17 | 2011-04-20 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SAN FRANCISCO | TIGHTENED RISER VALVE
60 | 11-20308-B | 132 |  | 0.75 | Single Service |  | Curb Valve |  |  | Construction Defect |  | 2011-04-17 | 2011-04-20 | Greased - Other |  | Steel-Other |  | SAN FRANCISCO | GREASED VALVE
| 06-80001-1 |  |  | 0.75 | Single Service |  | Body of Pipe |  |  |  |  | 2006-01-05 | 2006-01-05 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | SF | CONTRACTOR INSTALLING ELECT FOR PG&E HIT 3/4 HPSTL SERVICE
| 06-80002-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | External Corrosion |  | 2006-01-05 | 2006-01-05 | Deactivated Entire Service |  | PE 100 |  | SAN FRANCISCO | C/O ABANDONED 1# STL AT MAIN
| 06-21024-1 | 108 | [9 empty] | 2006-06-01 | [5 empty] | SACRAMENTO | LINE 108- REG PIT ELK GROVE BI; DELETE LEAK
52 | 94-20211-1 | 108T |  | 3 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1994-03-01 | 1994-06-02 | Other |  | Steel/Wrought Iron |  | SACTO | ABANDONED MAIN
52 | 94-20211-1 | 108T |  | 3 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1991-03-04 | 1994-06-02 | Other |  | Steel/Wrought Iron |  | SACTO. | ABANDONED MAIN
52 | 93-20465-1 | 108T |  | 3 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1993-04-28 | 1994-06-02 | Other |  | Steel/Wrought Iron |  | SAC COUNTY | ABANDONED MAIN
52 | 93-20469-1 | 108T |  | 3 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1993-04-30 | 1993-06-02 | Other |  | Steel/Wrought Iron |  | SAC COUNTY | ABANDONED MAIN
52 | 93-20468-1 | 108T |  | 3 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1993-04-30 | 1994-06-02 | Other |  | Steel/Wrought Iron |  | SAC COUNTY | ABANDONED MAIN
52 | 94-20212-1 | 108T |  | 3 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1994-03-01 | 1994-06-02 | Other |  | Steel/Wrought Iron |  | SACTO. | ABANDONED MAIN
52 | 94-20215-1 | 108T |  | 3 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1994-03-01 | 1994-06-02 | Other |  | Steel/Wrought Iron |  | SACTO. | ABANDONED MAIN
52 | 93-20463-1 | 108T |  | 3 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1993-04-28 | 1994-06-02 | Other |  | Steel/Wrought Iron |  | SAC COUNTY | ABANDONED MAIN
53 | 94-20215-1 | 108 | [9 empty] | 1994-03-01 | [5 empty] | SACTO. | MAIN ABANDONED 5 - 94
52 | 93-20469-1 | 108T | [9 empty] | 1993-04-30 | [5 empty] | SAC COUNTY
53 | 94-20212-1 | 108 |  | 3 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1994-03-01 |  | Other |  | Steel/Wrought Iron |  | SACTO. | MAIN ABANDONED 5 - 94
52 | 93-20468-1 | 108T | [9 empty] | 1993-04-30 | [5 empty] | SAC COUNTY
52 | 94-20209-1 | 108T | [9 empty] | 1994-03-01 | [5 empty] | SACTO. | MAIN ABANDONED 5 - 94
52 | 93-20463-1 | 108T | [9 empty] | 1993-04-28 | [5 empty] | SAC COUNTY
48 | 94-33106-1 | [10 empty] | 1994-05-04 | [5 empty] | DIXON
48 | 94-33107-1 | [10 empty] | 1994-05-04 | [5 empty] | DIXON
48 | 94-33108-1 | [10 empty] | 1994-05-04 | [5 empty] | DIXON
48 | 94-33109-1 | [10 empty] | 1994-05-05 | [5 empty] | DIXON
48 | 94-33110-1 | [10 empty] | 1994-05-05 | [5 empty] | DIXON
48 | 94-33111-1 | [10 empty] | 1994-05-05 | [5 empty] | DIXON
48 | 94-33112-1 | [10 empty] | 1994-05-05 | [5 empty] | DIXON
48 | 94-33134-1 | [10 empty] | 1994-06-02 | [5 empty] | VACAVILLE
48 | 94-33148-1 | [10 empty] | 1994-05-04 | [5 empty] | DIXON
48 | 91-33029-1 |  |  | 0.75 | Service |  | Regulator |  |  | Material Failure |  | 1991-06-07 | 1992-03-26 | Other |  | Steel/Wrought Iron |  | DIXON | REPAIRED REGULATOR
48 | 91-53029-1 |  |  | 0.75 | Service |  | Regulator |  |  | Other |  | 1991-08-06 | 1991-08-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | DIXON | TIGHTEN 3/4" NIPPLE ON RELIEF
48 | 92-33000-1 | [10 empty] | 1992-05-06 | [5 empty] | DIXON
36 | 87-30260-1 | [10 empty] | 1987-07-23 | [5 empty] | EUREKA
36 | 87-30380-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1987-12-14 | 1988-03-11 | Replace Pipe |  | Steel/Wrought Iron |  | EUREKA
| 10-30021-1 | 300A | 145.69 | 12 | Transmission |  | Valves |  |  | Material Failure | OTHER - VALVE SEAT | 2010-11-07 |  |  |  | Steel/Wrought Iron |  | BARSTOW | 1/2" METRIC VALVE STEM PACKING
98 | 11-54001-B | 300B | 161.44 | 34 |  |  | Line Valve |  |  | Other | UNKNOWN | 2011-04-11 |  |  |  | Steel-Other |  | HINKLEY | VALVE HOLE COVER; FIRE VALVE LEAKING
| 10-88388-1 | 300B | 108.25 | 12 | Transmission |  | Other |  | UNI-CAP | Other | GASKET | 2010-10-31 |  |  |  | Steel/Wrought Iron |  | HINKLEY | BLOW OFF UNI-CAP
98 | 10-88389-1 | 300B | 112.74 | 12 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-31 | 2011-04-27 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | HINKLEY | BLOW OFF UNICAP; TIGHTENED UNI-BOLT CAP
| 10-88387-1 | 300B | 125.24 | 12 | Transmission |  | Other |  | UNIBOLT CAP | Other | LOOSE CAP | 2010-11-01 |  |  |  | Steel/Wrought Iron |  | HINKLEY DISTRICT PIPELINE | UNIBOLT CAP
98 | 10-88388-1 | 300B | 108.25 | 12 | Transmission >= 20% SMYS |  | Clamp | Other |  | Other |  | 2010-10-31 | 2011-04-27 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | HINKLEY | TIGHTENED UNI-BOLT CAP
[18 empty] | TURLOCK AREA | DIABLO TELECOM STAND BY
[18 empty] | KEYES | TIE-IN LOCATION UPSTREAM TRANSMISSION PSI
| 01-40094 |  |  | 0.75 | Transmission |  | Regulator |  |  | Damage by 3rd Party |  | 2001-10-28 | 2001-10-28 | Other |  | Steel-Other |  | BRENTWOOD | ABOVE GROUND HIGH TO HIGH REGULATOR SET. HIT BY CAR INVOLVES IN ACCIDENT SEE CHP. REPORT.
30 | 09-90872-1 |  |  | 0.75 | Single Service |  | Riser Valve Threads |  |  | No/Deteriorated Pipe Dope |  | 2009-12-03 | 2011-02-26 | Other |  | Steel-Other |  | BRENTWOOD | TIGHTEN VALVE
| 09-90899-1 |  |  | 0.5 | Gathering |  | Valves |  |  | Equipment Malfunction |  | 2009-12-02 | 2009-12-02 | Tighten Cap or Bolt | TIGHTENED CONE/NUT ON VALVE | Steel/Wrought Iron |  | BRENTWOOD | SOAP TEST & SCREWED VALVE FOR FIRE VALVE FOR TRAILER PARK. TIGHTENED TAG. NEED TO MAKE JOB FOR NEW WELDED VALVE.
| 09-98453-1 |  |  | 1.25 | Gathering |  | Riser |  |  | Construction Defect |  | 2009-11-19 | 2010-02-16 | Replace Main Valve < 2-inch |  | Steel/Wrought Iron |  | DANVILLE | INSTALLED NEW 1 1/4" SVC VALE; SOAP TEST
| 09-26886-1 |  |  | 1.25 | Gathering |  | Body of Pipe |  |  | Construction Defect |  | 2009-12-09 | 2010-03-04 | Other |  | Steel/Wrought Iron |  | DANVILLE | RE-DOPED RISER VALVE & TIGHTENED
| 09-26884-1 |  |  | 1.25 | Gathering |  | Body of Pipe |  |  | Construction Defect |  | 2010-03-08 | 2010-03-08 | Replace Valve < 2 inch | ; ; ; ; REPLACED 1.25 SVC VALVE | Steel/Wrought Iron |  | DANVILLE | 1 1/4" SVC VALVE; 5 M.M.; REPLACED 1.25 SVC VALVE; SEE REPAIR REMARKS
| 08-40088-1 |  |  | 0.75 | Gathering |  | Other Welds |  |  | External Corrosion |  | 2008-08-14 | 2008-09-10 | Replace Entire Service |  | Steel/Wrought Iron |  |  | PM# 30651943; INSERTED ENTIRE SUC. WITH 1/2" PL. GAS PIPE; INSERTED ENTIRE SEC. WITH 1/2" PL. GAS PIPE.
| 04-26135-1 |  |  | 8 | Transmission |  | Fitting |  |  | Construction Defect |  | 2004-09-28 | 2006-03-23 | Tighten Cap or Bolt | NEW GASKET | Steel/Wrought Iron |  | ALAMO | INSTALLED NEW GASKET IN PCV & TIGHTENED BOLTS; TIGHTENED PCV CAP & INSTALLED NEW GASKET
| 03-26125-1 | 3017-01 | 5.64 | 8 | Transmission |  | Body of Pipe |  |  | Other | MANUFACTURING FLAW | 2003-08-06 | 2008-12-13 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | DANVILLE | USED A WELDED HIGH PRESSURE CLAMP, PLIDCO CLAMP, OVER ~ 1/2 APPARENT MANUFACTURE FLAW CRACK. TAX WRAP SAMPLE SENT IN TO tes FOR ASBESTOS TEST.
30 | 97-26184-1 | [10 empty] | 1997-09-19 | [5 empty] | W.C
30 | 98-36003-1 |  |  | 8 | Transmission |  | Fitting |  |  | Other |  | 1998-02-04 | 1999-05-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  |  | RE-DOPE COMP. PLUG
30 | 97-26185-1 |  |  | 8 | Transmission |  | Fitting |  |  | Corrosion |  | 1997-09-17 | 1998-11-14 | Replace Pipe |  | Steel/Wrought Iron |  |  | REPLACE BY M&C. VALVE REPLACED
30 | 97-26184-1 |  |  | 8 | Transmission |  | Fitting |  |  | Construction Defect |  | 1997-09-19 | 1999-05-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  |  | RE-DOPE LEAKING SAV-A-NIPPLE PLUG.
| 97-23316-1 |  |  | 8 | Transmission |  | Fitting |  |  | Other |  | 1997-11-03 | 1999-05-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  |  | RE-DOPED CAP & RETIGHTENED
| 09-43163-1 | 191 |  | 4 | Transmission |  | Fitting |  |  | Other | MISSING CAP | 2009-09-16 | 2009-04-16 | Other | INSTALLED CAP ON GREASE FITTING | Steel/Wrought Iron |  | WALNUT CREEK
| 95-93058-1 | 191 |  | 0.75 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1995-03-09 | 1995-03-09 | Other |  | Steel/Wrought Iron |  | WALNUT CRK | TOOK 3/4" GAUGE OUT OF SERVICE PER M&C PEOPLE
| 09-23059-1 | 191 | 15.78 | 4 | Transmission |  | Valves |  |  | Other |  | 2009-04-13 | 2009-04-13 | Other | GREASED VALVE | Steel/Wrought Iron |  | CLAYTON | GREASED VLV.- LEAK STOPPED
| 08-43495 |  |  | 1.25 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2008-12-27 | 2008-12-27 | Replace Dist Main >= 100 ft |  | Aldyl A (Tan or Gray) |  | CONCORD | INSTALLED 1' OF 1'/4" PLASTIC GAS MAIN, WITH (2) 1'/4" MET-FIT COUPLINGS 226 N/O WEST ST 12' OUT FROM P/C N/SIDE OF WESLEY CT
| 98-43227-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1998-09-17 | 1998-09-17 | Patch Welded |  | Steel/Wrought Iron |  | MORAGA | DAMAGED TP MAIN BY DIRECTIONAL BORE MACHINE - 378' N/W ST MARYS RD.; WELDED ON PATCH
| 02-23043-1 |  |  |  | Transmission |  | Fitting |  |  | Unknown |  | 2002-04-25 | 2003-08-28 | Other | REPAIRED LEAKING TUBE FTS. | Other |  | CONCORD
| 05-26097-1 | 191 |  | 8 | Transmission |  | Fitting |  |  | Other | LOOSE FTG. | 2005-10-25 | 2010-11-15 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | LAFAYETTE | SOAP TESTED
| 09-23047-1 | 191 |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2009-04-27 | 2009-04-27 | Other | GREASE VLV. | Steel/Wrought Iron |  | MARTINEZ | GREASED VALVES
30 | 92-33010-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Corrosion |  | 1992-05-26 | 1992-12-07 | Other |  | Steel/Wrought Iron
| 09-23045-1 | 191 |  | 6 | Transmission |  | Regulator |  |  | Other |  | 2009-03-31 | 2009-04-14 |  |  | Steel/Wrought Iron |  | MARTINEZ | TIGHTENED SS. TUBE FTS @ REGULATOR
| 09-23046-1 | 191 |  | 6 | Transmission |  | Regulator |  |  | Other |  | 2009-03-31 | 2009-04-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MARTINEZ | TIGHTENED SS. TUBE FTS ON REG.
30 | 98-43013-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Construction Defect |  | 1998-01-14 | 1999-07-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | W.C | SKETCH NOT NECESSARY 4-5 DIFFERENT LOCATIONS
30 | 98-26086-1 | 191 |  | 0.75 | Transmission |  | Fitting |  |  | Construction Defect |  | 1996-05-09 | 1999-10-26 | Tighten Cap or Bolt |  | Steel/Wrought Iron
30 | 98-26086-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Construction Defect |  | 1998-05-09 | 1999-10-26 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  |  | TIGHTENED 3/4" CAP ON TEE!
| 98-23024-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Construction Defect |  | 1998-04-28 | 1998-04-28 | Other |  | Steel/Wrought Iron |  | PLEASANT HILL | C/O STUB
30 | 09-98171-1 |  |  | 0.75 | Transmission |  | Pressure Control Fittings |  |  | Other | LOOSE CAP | 2009-10-30 | 2011-04-08 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | LAFAYETTE | TIGHTEN CAP ON PIN OFF TEE VALVE 2
| 00-26058-1 | 191 |  | 8 | Transmission |  | Fitting |  |  | Construction Defect |  | 2000-04-26 | 2001-05-10 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ORINDA | RE-DOPED CAP AND TIGHTENED. TP HAS TO FILL IN APP. BOXES
| 09-43087-1 |  |  | 1.25 | Gathering |  | Plastic Tee Cap |  |  | Material Failure |  | 2009-02-27 | 2009-02-27 | Other | INST. BLACK CAP REPAIR KIT | Aldyl A (Tan or Gray) |  | WALNUT CREEK | SOAP TESTES BLACK CAP REPAIR KIT AFTER INST.
| 05-43042-1 | 191 |  | 6 | Transmission |  | Fitting |  |  | Other | GREASE | 2005-02-10 | 2005-03-14 | Other | GREASED VALVE STEM | Steel/Wrought Iron |  |  | GREASED FITTING; GREASED FITTING ON ABANDONED BLOW OFF
| 08-40082 |  |  | 0.75 | Gathering |  | Valves |  |  | Construction Defect |  | 2008-07-31 | 2008-07-31 | Replace Main Valve < 2-inch |  | Steel/Wrought Iron |  | PITTSBURGH | FOUND LEAK BELOW VALVE. CHANGE VALVE AND RES. ON TAILENDS
| 09-97755 |  |  | 0.75 | Branch Service |  | Other |  | RISER THRDS | Other | DRY PIPE DOPE | 2009-09-17 | 2009-09-17 | Other | SKINNER PIPE JOINT CLAMP | Steel/Wrought Iron |  | WALNUT CREEK | INSTALL PIPE JOINT CLAMP; SOAP TEST
80 | 93-60008-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1993-01-21 | 1993-01-23 | Other |  | Steel/Wrought Iron |  | MTN VIEW | PUNCH HOLES OVER DIST. MAIN NO GAS FOUND. 10% IN REG. PIT. CONTACT M&C DEPT. TO MAKE REPAIRS.
80 | 93-60008-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1993-01-21 | 1993-01-23 | Other |  | Steel/Wrought Iron |  | MTN VIEW | PUNCH HOLES OVER DIST. MAIN NO GAS FOUND. 10% IN REG. PIT. CONTACT M&C DEPT. TO MAKE REPAIRS.
| 94-30468-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1994-09-15 | 1994-09-15 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | MTN VIEW | WELD 500 WALL WELDING SLEEVE OVER HOLE ON MAIN
| 94-30418-1 |  |  | 0.75 | Distribution Feeder Main |  | Other |  |  | Other |  | 1994-07-20 | 1994-07-21 | Replace Pipe |  | Steel/Wrought Iron |  | MTN VIEW | PLUG OFF TEE AND REPLACE GAUGE TAP AND METER VALVE.
80 | 94-30129-1 |  |  | 2 | Other | M | Tap Connection |  |  | Other |  | 1994-03-07 | 1994-11-28 | Tighten Cap or Bolt |  | TR 418 | PLASTIC | CUPERTINO | REPLACE DAMAGED O-RING AND TIGHTEN CAP ON 2" SERVICE PUNCH TEE.
80 | 94-30048-1 |  |  | 10 | Distribution Feeder Main |  | Other Welds |  |  | Other |  | 1994-01-14 | 1994-02-04 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | CAMPBELL | MADE REPAIRS BY WELDING 10'' X 12'' SLEEVE OVER WELD; MADE REPAIRS BY WELDING 10" X 12" SLEEVE OVER WELD
80 | 71-01492-1 |  |  | 4 | Distribution Feeder Main |  | Girth Weld |  |  | Construction Defect |  | 1971-12-31 | 1973-03-02 | Other |  | Steel/Wrought Iron |  | SUNNYVALE | WELD LEAKING ON 6'' X 6'' X 4'' TEE; REWELD WELD ON 6'' MAIN; INSTALL ANODE; JW 50 OVER MAIN AND SERVICE ALL CLEAR.
| 71-01492-1 | [16 empty] | SUNNYVALE | WELD LEAKING ON 6'' X 6'' X 4'' TEE; REWELD WELD ON 6'' MAIN; INSTALL ANODE; JW 50 OVER MAIN AND SERVICE ALL CLEAR. 10-10-8;; INS. OF GAS AT TEE VALVE 100/470 ... 7-10- 3; WELD LEAKING ON 6'' X 6'' X 4'' TEE; REWELD WELD ON 6'' MAIN; INSTALL ANODE; JW 50 OVER MAIN AND SERVICE ALL CLEAR.
80 | 72-00530-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-07-19 | 1972-11-27 | Patch Welded |  | Steel/Wrought Iron |  | SARATOGA | WELD PATCH ON 3'' MAIN ; INST. 9LB ANODE; JW 50' BOTH SIDES OF LEAK.; ALL CLEAR.
| 72-00530-1 | [16 empty] | SARATOGA | WELD PATCH ON 3'' MAIN ; INST. 9LB ANODE; JW 50' BOTH SIDES OF LEAK.; ALL CLEAR. ; 3473; B2; ALL CLEAR ...;
80 | 72-00389-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-06-14 | 1972-07-31 | Patch Welded |  | Steel/Wrought Iron |  | LOS ALTOS | ARC WELDED 19'' X 15'' PATCH OVER LEAK AND PITTED AREA; INSTALLED 9# ZINC ANODE; 7-31-72; F. STONE; BAR TESTED ... EACH SIDE OF LEAK - NO MORE GAS FOUND.
| 72-00389-1 | [16 empty] | LOS ALTOS | ARC WELDED 19'' X 15'' PATCH OVER LEAK AND PITTED AREA; INSTALLED 9# ZINC ANODE; 7-31-72; F. STONE; BAR TESTED 100 EACH SIDE OF LEAK - NO MORE GAS FOUND.; REG. SOX ...
80 | 72-00177-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-03-23 | 1972-03-24 | Patch Welded |  | Steel/Wrought Iron |  | MT. VIEW | LEAK CAUSED BY WRAP; DAMAGE WHEN SEWER WAS REPAIRED OTHER WRAP EXPOSED IS IN GOOD CONDITION; ACK WELDED 18'' X 2'' PATCH OVER PITTED AREA; 9 LBS MAG. ANODE INSTALLED ON MAIN AT THIS LOCATION; O.W. AREA O.K.
| 72-00177- | [16 empty] | MT. VIEW | LEAK CAUSED BY WRAP; DAMAGE WHEN SEWER WAS REPAIRED OTHER WRAP EXPOSED IS IN GOOD CONDITION; ACK WELDED 18'' X 2'' PATCH OVER PITTED AREA; 9 LBS MAG. ANODE INSTALLED ON MAIN AT THIS LOCATION; O.W. AREA O.K.;
80 | 72-00158-1 |  |  | 10 | Distribution Feeder Main |  | Fitting |  |  | Material Failure |  | 1972-03-20 | 1973-07-10 | Other |  | Steel/Wrought Iron |  | SUNNYVALE | 20 ON 4% SEALE IN P.4; SEE MAP; U.G. SCOTT ; CALLED REGULATION SHOP ON MAY 31, 1993 TO CHECK AND REPAIR LEAK IN REG. PIT. T. ; RECHECKED 7-10-73 ...
80 | 72-00131-1 |  |  | 2 | Distribution Feeder Main |  | Fitting |  |  | Material Failure |  | 1972-03-08 | 1973-02-23 | Other |  | Steel/Wrought Iron |  | MTN. VIEW | CAP ON CONTROL FITTING; LEAKING AND SAVER NIPPLE LEAKING; REDOPED AND TIGHTENED BOTH CAPS; J W 50' BOTH SIDES; ALL CLEAR.
| 72-00131-1 | [16 empty] | MTN. VIEW | CAP ON CONTROL FITTING; LEAKING AND SAVER NIPPLE LEAKING; REDOPED AND TIGHTENED BOTH CAPS; J W 50' BOTH SIDES; ALL CLEAR. ; NO GAS' SSP 6-28-73 ...
80 | 73-01269-1 |  |  |  | Other |  | Fitting |  |  | Material Failure |  | 1973-12-26 | 1974-02-22 | Other |  | Steel/Wrought Iron |  | SUNNYVALE | METER LEAK; REPAIRED LEAK AT INLET UNION ON METER BY REDOPING AND TIGHTEN.; JW OVER MAIN AND SERVICES ON BOTH SIDE OF 1073; FOUND NO READINGS.; CAW
80 | 73-01186-1 |  |  | 4 | Distribution Main |  | Valves |  |  |  |  | 1973-12-17 | 1974-03-20 |  |  | Steel/Wrought Iron |  | SVLE | 4'' VALVE ... ; ; NO PAVEING ORDER WORK DONE IN VALVE BOX.
80 | 73-03038-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-10-11 | 1973-10-11 | Patch Welded |  | Steel/Wrought Iron |  | CUPT. | E8.E9; WELD 8'' X 8'' PATCH ON GAS MAIN AT 2:00; POSITION ON PIPE FACING E/; ONLY 1 LARGE PIT IN THIS EXPOSURE, REST OF PIPE AND WRAP IN GOOD CONDITION; INST. 9LB ANODE.; PAVING TAG TURNED IN ON JOB; AREA STILL HAS 30/100 READINGS DUE TO SATURATION; RECHECK 60 DAYS.
| 73-03038- | [16 empty] | CUPT. | E8.E9; WELD 8'' X 8'' PATCH ON GAS MAIN AT 2:00; POSITION ON PIPE FACING E/; ONLY 1 LARGE PIT IN THIS EXPOSURE, REST OF PIPE AND WRAP IN GOOD CONDITION; INST. 9LB ANODE.; PAVING TAG TURNED IN ON JOB; AREA STILL HAS 30/100 READINGS DUE TO SATURATION; RECHECK 60 DAYS.
80 | 73-30348-1 |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-05-11 | 1973-05-14 | Patch Welded |  | Steel/Wrought Iron |  | SUNNYVALE | SERVICE TO 391 DUAN LEAKING; WELD IN 6'' OF 3/4'' STEEL CUT & TEST ... WITH ...# ... 30 MIN.; TEST OK; INSTALLED 9 ... ANODE AT MAIN; TEST 50' E & W WITH J & W. NO GAS; 5-14-73 D. ...
80 | 73-30348-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-05-14 | 1973-05-14 |  |  | Steel/Wrought Iron |  | SUNNYVALE | SERVICE . . . DUANE AT TEE REPLACE 2' AT 3/4 SERVICE; TEST AT 100 LB.; ... INSTALL 9 ... ANODE; NO PAVEING ... DIRT; TEST AREA WITH J & W ...; 3-25-74 D. ANDREWS
| 73-30709- |  |  |  | Other |  | Meter |  |  | Corrosion |  | 1974-11-11 | 1974-11-11 | Other |  | Other |  | SVLE | NOTIFIED GAS DISPATCH TO REPLACE GAS MHR.; J.W. MAIN & SERVICE, NO INDIE. OF GAS; CHECK MTR. SET AND FOUND LEAKAGE UNDER 5# GAS MTR.; NOTIFIED GAS SERVICE DEPT. TO CHANGE GAS MTR. A.S.A.P.;; SIRALDE... SREVICEMAN;; CHECKED LEAKS ON M...; METER LEAK
80 | 73-30548-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Construction Defect |  | 1973-08-16 | 1973-08-17 | Patch Welded |  | Steel/Wrought Iron |  | LOS ALTOS | WELD 2-3'' X 6'' PATCHES ON 2'' MAIN; INST. 9LB ANODE; JW AREA RECHECK THE SAME AREA IN 30 DAYS; (PIPE HAD A POOR FIELDWRAP)
| 73-30548- | [16 empty] | LOS ALTOS | WELD 2-3'' X 6'' PATCHES ON 2'' MAIN; INST. 9LB ANODE; JW AREA RECHECK THE SAME AREA IN 30 DAYS; (PIPE HAD A POOR FIELDWRAP); NO GAS FOUND 12-18-73
80 | 73-60141-1 |  |  | 0.75 | Distribution Feeder Main |  | Regulator |  |  | Other |  | 1973-03-26 | 1973-03-26 | Other |  | Steel/Wrought Iron |  | SUNNYVALE | BAR PUNCHED AND J.W.ED OVER MAIN FIFTY FEET EACH WAY FROM SERV. NO READING.
| 73-60141-1 | [16 empty] | SUNNYVALE | BAR PUNCHED AND J.W.ED OVER MAIN FIFTH FT. EACH WAY FROM SERV. NO READING.; NO GAS SSP JW 7-23-73. ...; NO GAS SSP. J.W. 7-12-...
80 | 73-60078-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Construction Defect |  | 1973-02-12 | 1973-02-12 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | ... | 30-F-7, 12-12; ...
| 73-60331- |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-07-02 | 1975-04-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SUNNYVALE | TEMP CLAMPED 12-3-73 BY W. CAPPS; INST. 2-2'' M/2S AND 10' OF STEEL PIPE; MAIN UNDER PROTECTION; JW AREA ALL CLEAR; SEE LK # 7530117 FOR PREMANENT REPAIRS; CAUSE OF LEAK WATER & SEWER OVER MAIN
80 | 73-60331-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1973-07-02 | 1973-12-03 | Clamp |  | Steel/Wrought Iron |  | SUNNYVALE | NOTE MAIN SHOULD BE RENEWED VERY BAD CONDITION
| 74-30351-1 | [16 empty] | LOS GATOS | (2'' MAIN); 2'' MAIN LEAKING AS FIELD WRAP. ROCK IN BACK FILL INTO WRAP. INTALLED 10'' X 3'' PATCH ON MAIN. J & W ... TEST SERVICE AT 16226 ENGLEWOOD ... OK. 4-3-74 D. ANDREWS.; ... MAG. ANODE AT MAIN.
80 | 74-30220-X |  |  |  | Other |  | Valves |  |  | Material Failure |  | 1974-03-06 | 1974-03-06 | Replace Pipe and/or Service |  |  |  | SARATOGA | REPLACE STOP COCK; J.W. AREA ALL CLEAR.; 58.A8
| 74-30220-X | [16 empty] | SARATOGA | REPLACE STOP COCK; J.W. AREA ALL CLEAR. ; 58.A8; NO GAS FOUND 4-15-74; RICKSON; SOX; CAW
| 74-30124- |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-02-08 | 1974-02-14 |  |  | Steel/Wrought Iron |  | MT. VIEW | FOUND LEAKS ON 2'' MAIN THAT RUNS E/...W ON LEONG OR CLAMPED ... LEAKS IN A 15' AREA ON THE CORNER OF LEONG DR. & EVANDALE ... FROM P.E.F. TO P.C.F. ON LEONG DR. I FOUND GAS IN BAR HOLE TESTING; THIS MAIN IS IN POOR CONDITION AND SHOULD BE REPLACED FROM 10-20 % ON THE 100% SEALE ON THE J.W. ALONG LEONG DR. ; CAW
| 74-30124- | [17 empty] | FOUND LEAKS ON 2'' MAIN THAT RUNS E/O...W ON LEONG OR CLAMPED ... LEAKS IN A 15' AREA ON THE CORNER OF LEONG DR. & EVANDALE ... FROM P.E.F. TO P.C.F. ON LEONG DR. I FOUND GAS IN BAR HOLE TESTING; THIS MAIN IS IN POOR CONDITION AND SHOULD BE REPLACED FROM 10-20 % ON THE 100% SEALE ON THE J.W. ALONG LEONG DR. ; LEAKAGE FOUND 80% J.W.; 3-28-74 P. RICKSON; CAW ;
80 | 74-60063- |  |  |  | Other |  | Other |  |  | Other |  | 1974-02-13 | 1974-02-13 | Other |  | Other |  | MT. VIEW | NO LEAK; LEAK WAS FOUND ON THE POOL HEATER; J.W. AROUND METER AND FOUND NO READINGS; (OWNER CALLED PLUMMER TO REPAIR POOL HEATER.); HAZARD NOTICE WAS NOT GIVEN TO CUST.; CUST. FOUND HIS OWN LEAK AND CALLED PLUMMER.; CAW
80 | 74-60042-1 |  |  | 0.75 | Service |  | Valves |  |  | Material Failure |  | 1974-02-01 | 1974-02-01 | Other |  | Steel/Wrought Iron |  | SUNNYVALE | CAW.; NO GAS FOUND 3-19-74; P. RICKSON J.W. ; CAW.
8 | 74-60421- |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-10-02 | 1974-10-02 |  |  | Steel/Wrought Iron |  | LOS GATOS | SERVICE LEAKING. INSERT 59' AT 1'' NIPAK P.L. PIPE. ... MAIN ....; INSTALL 1 1/4 ...ULLER TEE. ... ; WELD 3'' CAN OVER ...; ... 10-2-74 ; DON ANDREWS; CEMAN.... TURNED IN 10-2-74.
| 74-60420- |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-09-30 | 1974-09-30 |  |  | Plastic |  | LOS ALTOS HILLS | BACK HOE TREN... WATER SERVICE DITCH CUT 1 1/4'' P.L. MAIN IN TO. ; INSTALLED 1' 1/4'' P.L. PIPE USED TWO 1 1/4'' AMP FIT COUPLING SOAP TEST. PURG AIR AT END OF MAIN TIP IN #8 TRACEING WIRED USED. NIPAK P.L. PIPE 2'' SAND COVER OVER MAIN. J.T. ELECT. OK.; 9-30-74; D. ANDREWS;; URGUHART TRENCHING; OWNER; GENE URGUHART; OPERATOR; 3790 CONCORD AVE. MT. VIEW; PHONE 968 5801.; LA-12.; CUT OUT 1' 1 1/14'' P.L. MAIN TIE IN WITH TWO 1 1/4'' AMP. FIT COUPLING.
| 74-60420- | [16 empty] | LOS ALTOS HILLS | BACK HOE TREN... WATER SERVICE DITCH CUT 1 1/4'' P.L. MAIN IN TO. ; INSTALLED 1' 1/4'' P.L. PIPE USED TWO 1 1/4'' AMP FIT COUPLING SOAP TEST. PURG AIR AT END OF MAIN TIP IN #8 TRACEING WIRED USED. NIPAK P.L. PIPE 2'' SAND COVER OVER MAIN. J.T. ELECT. OK.; 9-30-74; D. ANDREWS;; URGUHART TRENCHING; OWNER; GENE URGUHART; OPERATOR; 3790 CONCORD AVE. MT. VIEW; PHONE 968 5801.; LA-12.; ALL CLEAR; WILLIAMSON; 5-29-75.; CUT OUT 1' 1 1/14'' P.L. MAIN TIE IN WITH TWO 1 1/4'' AMP. FIT COUPLING.;
80 | 74-60359- | [5 empty] | Other |  |  | Other |  | 1974-08-28 | 1974-08-28 | Replace Pipe and/or Service |  | Plastic |  | SUNNYVALE | RAISGH PAVEMENT CO. GRADING FOR NEW STREET STRUCK & BROKE 2'' P.L. MAIN; INST. DEAD END CAP; BAR TEST AREA ALL CLEAR.; INST. DEADEND.; CAW.
| 75-01061-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 1975-05-28 | 1976-04-08 | Other |  | Steel/Wrought Iron |  |  | REPAIRED LEAK ON SERVICE TEE CAP & ON 3/4'' STOP COCK, CUT & TESTED SERVICES AT 100LBS. OK. NO PAVING CUTS REQUIRED.
| 75-01079-1 |  |  | 00/.75 |  |  | Fitting |  |  | Other |  | 1976-05-29 | 1976-04-09 | Other |  | Steel/Wrought Iron |  | SUNNYVALE | J.W. SERVICE & MAIN NO INDIC. OF GAS FOUND; FOUND LEAK ON ELBOW ON GAS; MTR SET TURNED IN TAG TO GAS SERVICE DEPT. TO REPAIR.
| 75-01046-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1975-12-15 | 1975-12-16 |  |  | Steel/Wrought Iron |  | SUNNYVALE | STEEL GAS SERVICE LEAKING; REPLACE SERVICE WITH 1/2'' ORANGE STANDARD PIPE; BAR TESTED & J.W. AREA; NO EVIDENCE OF GAS; ...; FOUND 3/4'' STEEL SERVICE LEAKING; INSERTED 34' OF 1/2'' PL. ORANGE STANDARD; TEST OK; J.W. AREA ALL CLEAR; 12-16-75; D. ANDREWS.
| 75-01028-1 |  |  | 2 | Distribution |  | Body of Pipe |  |  | Corrosion |  | 1975-05-23 | 1975-11-24 | Patch Welded |  | Steel/Wrought Iron |  | SUNNYVALE | BAD FIELD WRAP
80 | 75-00091-1 |  |  | 0.75 | Other |  | Meter |  |  | Material Failure |  | 1975-01-14 | 1975-12-09 | Other |  | Steel/Wrought Iron |  | SARATOGA | BAR TEST OVER GAS SERV. NO READING OF GAS FOUND ON METER SET. TURN OVER TO SERVICE DEPT. ; METER LEAK. ;
80 | 7-266- |  |  |  | Distribution Feeder Main |  | Other |  |  | Corrosion |  | 1975-05-09 | 1975-05-09 |  |  | Steel/Wrought Iron |  | CUPT. | 5/9/75; LEAK IN BAD AREA TO WELD; PATCH INSTEAD 2 BOLT; SKINNER CLAMP; AREA UNDER C.O.; NO PAVEMENT TAG REQUIRED; BAR CHECKED AREA ALL CLEAR.; REFER TO LEAK NO # 74001291.; E-10.
| 75-30179- |  |  |  | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1975-03-31 | 1975-04-01 |  |  | Steel/Wrought Iron |  | MT. VIEW | FOUND 2'' H.P. STEEL MAIN ...; INSTALLED ...SKINNER ...
| 75-30171- |  |  | 0.75 | Service |  | Girth Weld | Fitting |  | Construction Defect |  | 1975-03-03 | 1975-03-26 |  |  | Steel/Wrought Iron |  | PALO ALTO | FOUND 3/4'' SERVICE LEAKING AT WELD AT MAIN & MULLER TEE ALSO CAP ... TEE. REPAIR WELD ON TEE SOAP TEST OK. CUT PUMP & TEST SERVICE OK. REDOPE BRASS PLUG & CAP ON TEE OK.; NO PAVEING ORDER DIRT; SERVICE ORDER IN 3-25-75; 3-26-75; DON ANDREWS.; ORIGINALLY CALLED ...3795 LA ...
| 75-30171- | [16 empty] | PALO ALTO | FOUND 3/4'' SERVICE LEAKING AT WELD AT MAIN & MULLER TEE ALSO CAP ... TEE. REPAIR WELD ON TEE SOAP TEST OK. CUT PUMP & TEST SERVICE OK. REDOPE BRASS PLUG & CAP ON TEE OK.; NO PAVEING ORDER DIRT; SERVICE ORDER IN 3-25-75; 3-26-75; DON ANDREWS.; ORIGINALLY CALLED ... ON 2-28 ...75 3795 LA SELL ...LEAK # 7560082 CUST. ...FOUND OTHER LEAKS.; NO GAS FOUND 9-2-75; RICKSON (CENTURY) CAW;
| 75-30135- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1975-03-13 | 1975-03-14 |  |  | Steel/Wrought Iron |  | LOS ALTOS | FOUND 2'' STEEL MAIN LEAKING DUE TO BAD FIELD WRAP. WELD 6 X 5 PATCH ON MAIN. INSTALL ... ANODE. ; GAS STI... IN AREA; SERVICE 20 24191 HAS LEAK. LEAK ORDER IN 3-14-75. PAVEING ORDER IN 3-14-75.; 3-14-75; DON ANDREWS.; 6-10-A
80 | 75-30117- |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1975-03-10 | 1975-03-10 | Patch Welded |  | Steel/Wrought Iron |  | SUNNYVALE | TEMP CLAMPED BY LARANJO 3-10-75; WELD 3 PATCHES 2'' X 6'' ON 2'' MAIN; MAIN UNDER PROTECTION; JW AREA ALL CLEAR.
| 75-30117- | [16 empty] | SUNNYVALE | LEAKING 2'' H.P. GAS MAIN; DUG MAIN AT TWO LOCATIONS; FOUND TEMP. LEAK CLAMPS LEAKING; RESET CLAMPS AND TIGHTEN BOLTS; MAIN ...PIPE...J.W. AREA ALL CLEAR.; CAUSE OF LEAKS WATER SERVICES ON TOP OF MAIN.
| 75-30117- | [16 empty] | SUNNYVALE | LEAKING 2'' H.P. GAS MAIN; DUG MAIN AT TWO LOCATIONS; FOUND TEMP. LEAK CLAMPS LEAKING; RESET CLAMPS AND TIGHTEN BOLTS; MAIN ...PIPE...J.W. AREA ALL CLEAR...; ALL CLEAR 9-8-75 ... SOX;; CAUSE OF LEAKS WATER SERVICES ON TOP OF MAIN;
| 75-30090- |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1975-02-24 | 1975-02-25 |  |  | Steel/Wrought Iron |  | MT. VIEW | FOUND 2 LEAKS ON 3'' MAIN. LEAKS DUE TO WRAP BEING DAMAGED. WELD TWO PATCHES ON MAIN 7 X 5 + 8 X 5. GAS STILL IN AREA. PAVEING ORDER IN WHEN JOB IS COMPLETE.; 2-25-75 DON ANDREWS.; CAW.; NO GAS FOUND 9-3-25
80 | 75-30505-1 |  |  |  | Distribution Feeder Main |  | Fitting |  |  | Construction Defect |  | 1975-09-15 | 1975-10-10 | Patch Welded |  | Steel/Wrought Iron |  | LOS ALTOS HILLS | 2'' CONTROL LEAKING TIGHTEN PLUG; REDOPE CAP AND TIGHTEN; BAR TEST AREA ALL CLEAR.
80 | 75-30495-1 |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1975-09-18 | 1975-10-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | LOS ALTOS HILLS; | 2'' MAIN LEAKING 6 PLACES; INST 2-2'' M2S AND 8' OF 2'' PIPE; INST. 15LB ANODE; BAR TEST AREA ALL CLEAR.
| 75-30406-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Other |  | 1976-06-29 | 1976-06-30 | Other |  | Steel/Wrought Iron |  | SUNNYVALE | FOUND GAS 3' FROM TAP HOLE TIE IN 800 PPM 12-12-75 ... SOX;; SEE LEAK SHEET MENTIONED ABOVE.
8 | 75-30769- |  |  | 1 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-12-23 | 1975-12-23 |  |  | Steel/Wrought Iron |  | SUNNYVALE | FOUND 1'' SERVICE TO 385 ARBOR LEAKING INSURT 1/2 STANDARD ... INSTALL POWER ... AT RISE. PUMP - TEST ... WITH SAND. ; 12-25-75 NO PAVEING ORDER ... D. ANDREWS.
80 | 75-30745 - |  |  |  | Other |  | Other |  |  | Other |  | 1975-12-16 | 1975-12-16 | Other |  | Other |  | MT. VIEW | BAR TEST OVER SERVICE; MAIN AND AROUND BUILDING; FOUND NO READINGS; BLOWER EFFECTING BURNER FLAME; SERVICEMAN DISCONNECTED FURN.; 12/17/75 M.S.
80 | 75-30744- |  |  |  | Other |  | Other |  |  | Other |  | 1975-12-16 | 1975-12-16 | Other |  | Other |  | SUNNYVALE | BAR TEST OVER MAIN ALL CLEAR; (BUTANE BOTTLE LEAKING); 12-17-75 M.S.
| 75-30709-1 |  |  |  | Other | HOUSELINE | Other |  | HOUSELINE | Corrosion |  |  |  | Other | NO REPAIR MADE |  |  | LOS ALTOS HILLS | SERV. RECENTLY INSERTED WTIH 1/2'' PL. FOUND GAS IN AREA HAD SERVICEMAN CLOCK METER FOUND LEAK OF 9 CU. FT. P/AR. IN HOUSELINE. SERVICEMAN SEALED METER. J.W. OVER SERVICE ALL CLEAR ON 4% SCALE. ; HOUSELINE LEAK.
80 | 75-30662- |  |  |  | Distribution Feeder Main |  | Other Welds |  |  | Other |  | 1975-11-04 | 1975-11-07 | Patch Welded |  | Steel/Wrought Iron |  | SARATOGA | WELD LEAKING ON 2'' STEEL MAIN. REWELD WELD. BAR TEST AREA ALL CLEAR. NO PAVEMENT.
8 | 76-31399- |  |  | 0 | Other |  | Other |  |  | Other |  | 1976-05-07 | 1977-11-10 | Other |  | Other |  | SARATOGA | J.W. OVER SERVICES & MAIN, NO INDIE. OF GAS FOUND. FEGLING CHECKED AREA WITH T.V.L. NO INDIC. FOUND.
| 76-31122- |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-04-13 | 1976-04-14 | Patch Welded |  | Steel/Wrought Iron |  | LOS GATOS | FOUND 10'' MAIN LEAKING WELD 10'' X 8'' PATCH; BAR TEST AREA ALL CLEAR; CUASE OF LEAK ... TOP LAYING ON TOP OF MAIN.; SAND & ROCK ...
| 76-31119- |  |  | 1.25 |  |  | Body of Pipe |  |  | Corrosion |  | 1976-04-12 | 1976-04-29 | Patch Welded |  | Steel/Wrought Iron |  | SAN JOSE | WELDED 12'' LONG PATCH ON BOTTOM OF 1 1/4'' GAS MAIN. 9LB ANODE INST. PAVING CUT MADE FOR 3' X 5' PATCH.
80 | 76-31093- |  |  |  | Other | P | Fitting |  |  | Other |  | 1976-04-12 | 1976-04-12 | Other |  | Steel/Wrought Iron |  | LOS GATOS | FOUND 3/4'' X 1/2'' TRANSITION FITTING LEAKING. FITTING HAND TIGHT. TIGHTEN FITTING. SOAP TEST OK. BAR TEST OK.
8 | 76-31030-1 |  |  | 0 | Other |  | Meter |  |  | Other |  | 1976-04-01 | 1977-08-17 | Other |  | Other |  | CUPERTINO | J.W. OVER GAS SERVICE & MAIN; NO INDIC. OF GAS FOUND. FOUND GAS MTR. LEAKING & TURNED TAG INTO SERVICE DEPT. CALLED THIS TO MATHAS IN GPS DISPATCH 8-17-77 5:10PM CAW
Other
| 76-30920- |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-08-16 | 1976-11-17 | Patch Welded |  | Steel/Wrought Iron |  | LOS GATOS | INSTALLED ...
80 | 76-30820- |  |  |  | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1976-03-23 | 1976-03-26 |  |  | Steel/Wrought Iron |  | SAN JOSE | FOUND 301 ON 2'' CONTROL FITTING. TIGHTEN PLUG AND CAP SOAP TEST OK. BAR TEST AREA ALL CLEAR.
80 | 76-30755- |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-03-22 | 1976-03-25 | Patch Welded |  | Steel/Wrought Iron |  | SAN JOSE | FOUND 2'' HP MAIN LEAKING 3 PLACES; TEMP CLAMP 3-22-76; WELD 3 PATCHES 4'' X 6'' 4'' X 4'' AND 3'' X 5''; BAR TEST AREA AIRING OUT RECHECK.
80 | 76-31934- |  |  |  | Other |  | Body of Pipe |  |  | Corrosion |  | 1976-08-23 | 1976-08-23 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SUNNYVALE | FOUND 301 ON 3/4 HOUSE LINE; INST. 18'' OF HOUSE LINE FOR REPAIRS; SOAP TEST OK; BAR TEST OVER SERVICE AND MAIN OK.
| 76-31621- |  |  | 0.75 | Other |  | Other |  |  | Other |  | 1976-06-01 | 1976-06-01 | Other |  | Steel/Wrought Iron |  | CUPERTINO | ABAN 3/4'' STEEL STUB AT MAIN, DUE TO LEAKAGE. STUB HAD NO FUTURE USE. CONCRETE REPAIR TAG MADE FOR 4' X 8' SECTION OF SIDEWALK.
| 76-32480-1 |  |  |  | Transmission | M | Body of Pipe |  |  | Corrosion |  |  |  | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CUPERTINO | INST. 2 BOLT 2'' SKINNER CLAMP TO REPAIR LEAKAGE. INST. 9LB MAG. ANODE. J.W. AREA ALL CLEAR ON ...
80 | 76-32301- | [5 empty] | Other |  |  | Other |  | 1976-11-01 | 1976-11-01 | Other |  | Other |  | SUNNYVALE | SER. DEPT. FOUND LEAK IN HOUSE LINE OF MINOR NATURE, NOTIFIED CUST. TO HAVE REPAIRED.; BAR TEST OVER BOTH SERVICES AND MAIN FOUND NO READINGS. CALL SERVICEMAN TO CLOCK TEST HOUSE LIKE AT # 279 WAVERLY. YAMASHITA PICKUP SLIGHT READING UNDER HOUSE. FLAME PACK SER. AT #273 ALL CLEAR.
80 | 76-60395- |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-12-03 | 1976-12-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | LOS ALTOS HILLS | 3 ... STORM DRAIN CORSSING OVER 3'' MAIN. 3'' MAIN LEAKING IN 4 PLACES. INST. 2-3'' M2S AND 10' OF ...'' STEEL PIPE.
80 | 76-60391- |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-11-30 | 1976-11-30 | Patch Welded |  | Steel/Wrought Iron |  | MT. VIEW | FOUND 2'' MAIN LEAKING WELD 3'' X 8'' PATCH. INST. 9LB ANODE.
80 | 76-60381- |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-11-22 | 1976-11-24 | Patch Welded |  | Steel/Wrought Iron |  | MT. VIEW | FOUND LEAK ON 2'' STEEL MAIN. CAUSE OF LEAK - SMALL NICK IN THE WRAP WELD 6'' X 2'' PATCH; INST. 9LB. ANODE.
80 | 76-60374- |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-11-18 | 1976-11-18 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CAMPBELL | HOLE DRILLED IN 2'' MAIN BY WNRICK AND ASSOCIATES USED EXISTING 4'' P.C.F. 4'' M2 AND INST. 5' OF 2'' STEEL PIPE FOR REPAIR; SOAP TEST OK.
80 | 76-60348- |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-11-04 | 1976-11-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | LOS ALTOS HILLS | FOUND 2'' MAIN LEAKING CUASE OF LEAK - 30'' STORM DRAIN CROSS OVER 2'' MAIN. CUST. SAID THE STORM DRAIN WAS PUT IN TWO YEARS AGO. INST. 2-2'' SPLIT CONTROL BOTTOM TAPS AND 10' OF 2'' STEEL PIPE. ; ... DID NOT INSTALL ANODE.
76-60228- |  |  |  | 2 | Other | M | Body of Pipe |  |  | Corrosion |  | 1976-07-14 | 1976-07-14 | Clamp |  | Steel/Wrought Iron |  | SULE | REPAIRED GAS MAIN WITH 2-2'' X 10'' SKINNER CLAMPS & I WELDED PATCH. 9LB ANODE INST. IN F. & COU... ; NO PAVING CUTS MADE.; ; PITT AREA SEEM TO UST BE IN VICINITY WHERE WATER SERVICE CROSSED GAS MAIN. 9LB. ANODE INSTALLED IN F. & C. NEXT TO WATER ...
| 76-60149- |  |  | 0.75 | Other |  | Body of Pipe |  |  | Other |  | 1976-05-03 | 1976-05-03 | Other |  | Steel-Other |  | LOS ALTOS | J.W. SERVICE & MTR SET NO INDIC. OF GAS FOUND. NOTIFIED GAST DISP. TO CLOCK HOUSE LINE & REPAIR LEAK ON POOL HEATER NEXT TO MTR SET. FLAME PAK SHOULD ... AREA.;; MAIN NOT EXPOSED; ALL CLEAR; 5-20-76; RICKSON.
| 76-60101- |  |  |  | Other |  | Other |  |  | Other |  | 1976-03-25 | 1976-03-25 | Other |  | Other |  | MT. VIEW | CUST. REPORTED GAS ODOR IN AREA. SERVICEMAN & CREW CHECK AREA NO INDIC. OF GAS FOUND. WE SCOPED AND J.W. SERVICE AND GAS ... & ... AREA CLEAR.
| 76-60003- |  |  | 0 | Other |  | Other |  |  | Other |  | 1976-01-05 | 1976-01-05 | Other |  | Other |  |  | J/W/ SERVICE AND CATCH BASINS IN TENNIS COURT AREA. WE DIDN'T FIND ANY INDIE. OF GAS WITH J.W. AND NO ONE ON THE PERMITER HAS REPORTED...ODOR OR KNEW OF ANYONE WHO ...; MAIN NOT EXPOSED
80 | 92-30369-1 |  |  | 10 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1992-05-11 | 1992-06-04 | Other |  | Steel/Wrought Iron |  | MOUNTAIN VIEW | GREASED 10" VALVE & REPAIRED LEAK ON METRIC VALVE
80 | 92-30368-1 |  |  | 2 | Distribution Main |  | Valves |  |  | Other |  | 1992-05-11 | 1992-06-24 | Other |  | Steel/Wrought Iron |  | MOUNTAIN VIEW | J-W AND FLAMEPAK MAIN NO GAS FOUND. TWO VALVES IN TEMP REG PIT FOUND LEAKING MOV DEPT. GREASED VALVES.
80 | 92-30369-1 |  |  | 10 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1992-05-11 | 1992-06-04 | Other |  | Steel/Wrought Iron |  |  | GREASED 10" VALVE & REPAIRED LEAK ON METRIC VALVE
80 | 92-30645-1 |  |  | 8 | Distribution Feeder Main |  | Valves |  |  | Other |  | 08/20/0199 | 1992-10-30 | Other |  | Steel/Wrought Iron |  | LOS GATOS | MADE REPAIRS BY GREASING VALVE
80 | 92-30644-1 |  |  | 0 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1992-08-20 | 1992-09-08 | Other |  | Steel/Wrought Iron |  | LOS GATOS | REPAIRED 301 ON SAVER NIPPLE, REDOPED AND TIGHTENED
80 | 92-30643-1 |  |  | 0 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1992-08-19 | 1992-10-05 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MOUNTAIN VIEW | CALL M & C CREW OUT TO REPAIR LEAK ON STRIKE LINE; FOUND SMALL LEAK ON 1/4" STATIC LINE INSIDE REG PIT. CALLED OUT M&C CREW TO REPAIR LEAK. THE 2" VALVE COMING OFF 10" FEEDER MAIN OK
80 | 92-30642-1 |  |  | 2 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1992-08-19 | 1992-10-05 | Other |  | Steel/Wrought Iron |  | MOUNTAIN VIEW | CALL M &C OUT TO GREASE THE VALVE FOR PERM. REPAIR; FOUND SMALL LEAK ON 2" VALVE LEADING FROM 10" FEEDER MAIN TO REG PIT. HAD M & c CREW COME OUT ANG GREASE VALVE FOR PERM. REPAIR.
80 | 92-30641-1 |  |  | 24 | Transmission | [6 empty] | 1992-08-20 | 1992-10-05 |  |  | Steel/Wrought Iron |  | MOUNTAIN VIEW | BAR TEST AREA. SOAP VISABLE COMPONENTS OF VALVES INSIDE BOXES & VALVE F& C'S------ NO LEAKS FOUND; J.W. INSIDE ALL GVB'S (5) AT THIS LOCATION AND FOUND NO TRACES OF GAS. SOAP TEST ALL VISIBLE FITTINGS, AND BAR TEST OVER 24" TRANS. MAIN & 4" DISTR. MAIN IN AREA OF GVB'S -----NO TRACES OF GAS FOUND.
| 93-30360-1 |  |  |  | Transmission |  | Valves |  |  | Other |  | 1993-09-03 | 1993-11-03 | Other |  | Steel/Wrought Iron |  | PALO ALTO | REPAIRED LEAKING VALVE
80 | 93-30278-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 1993-09-01 | 1994-03-08 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | MOUNTAIN VIEW | ARC WELD PATCH OVER LEAK AND PITTED AREA
80 | 93-30277-1 | [10 empty] | 1993-09-01 | 1994-04-26 |  |  |  |  | MOUNTAIN VIEW | NO GAS FOUND
| 95-30012-1 |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  | 1995-03-06 | 1995-04-18 | Other |  |  |  | LOS ALTOS HILLS | REPAIRED LEAK ON FILTER
| 95-30012-1 |  |  | 6 | Distribution Feeder Main |  | Other |  |  | Other |  | 1995-03-06 | 1995-04-18 | Other |  | Steel/Wrought Iron |  | LOS ALTOS HILLS | REPAIRED LEAK ON FILTER
| 96-30650-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1996-09-10 | 1996-09-10 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SAN JOSE | WELD GRADE 70 AS16 .375 WALL 10" X 18" BAND OVER GASH IN PIPE.
| 96-30673-1 |  |  | 1.25 | Distribution Feeder Main |  | Other |  |  | Damage by outside Forces |  | 1996-10-15 | 1996-10-15 | Replace Pipe |  | Plastic |  | CAMPBELL | REPLACED 7' OF 1 1/4" PL MAIN WITH 2 1/4 MET FIT REPAIR COUPLING
80 | 71-00807-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-11-22 | 1972-11-22 | Other |  | Steel/Wrought Iron |  | SARATOGA | INST 3-4" LEAK CLAMPS ON 4" PIPE AT 3 DIFFERENT LOCATIONS. ALL 3 LEAKS WERE FOUND ON BOTTOM OF THE MAIN. LEAKS WERE CAUSED BY ROCLEY SOIL 4" MAIN 1' FROM 8' ACTAINEV WALL: THE WALL COULD CAUE IN IF DIGGING TO CLOSE. TOO MUCH WATER TO USE JW GAS INDICATED BY WATER BUBBLING
80 | 71-00825-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1971-08-02 | 1973-03-06 | Patch Welded |  | Steel/Wrought Iron |  | MOUNTIAN VIEW | WELD 2-3X6 PATCH ON 2" P MAIN INST 9 LB AMOUR CAUSE OF LEAK-ROCKS. FOUND MORE R. CODINGS 25/100% STILL WORKING IN AREA RECHECK IN 30 DAYS
80 | 71-00806-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-11-20 | 1972-11-20 | Other |  | Steel/Wrought Iron |  | SARATOGA | INST 2-4" LEAK CLAMPS ON 4" PIPE FOUND BOTH LEAKS ON BOTTOM OF THE PIPE. LEAKS WERE CAUSED BY ROCKEY SOIL. 4" MAIN IS 1' FORM A 8' RETAINER WALL. THE WALL COULD CAVE IN IF DIGGING TO CLOSE. TOO MUCH WATER TO USE JW/ GAS INDICATED BY WATER BUBBLING.
80 | 71-30249-1 |  |  | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1971-05-17 | 1972-06-16 | Patch Welded |  | Steel/Wrought Iron |  | PALO ALTO | ADDED 20" X 16" PATCH OVER PIT HOLES IN LINE #132 ALIGHT BE HERE LEAKS
80 | 71-30313-1 |  |  | 24 | Transmission |  | Body of Pipe |  |  | Material Failure |  | 1971-09-08 | 1971-09-09 | Patch Welded |  | Steel/Wrought Iron |  | SUNNYVALE
80 | 71-030313 |  |  | 24 | Transmission |  | Body of Pipe |  |  | Material Failure |  | 1971-09-08 | 1971-09-09 |  |  | Steel/Wrought Iron |  | SUNNYVALE INC | 2 PIT HOLES IN BOTTOM OF 24" TRANSMISSION LINE # 132 ARC WELDED 18"X18" PATCH
80 | 71-30355-1 |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1971-10-18 | 1975-04-30 | Patch Welded |  | Steel/Wrought Iron |  | SUNNYVALE | ENKAGE FOUND 2% OVER MAIN. WELD PATCHO ON 2" MAIN INST 9 LB ANOOG JW AREA ALL CLEAR. PAVEMENT TAG MADE.
80 | 72-30321-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-09-19 | 1972-10-09 | Patch Welded |  | Steel/Wrought Iron |  | LOS GATOS | WELD 4 PATHES 6" LONG MAIN. INST 1-92B & HODE JW AREA ALL CLEAR
| 72-30321-1 | [16 empty] | LOS SATOS | MAIN UNDER PERMANENT CHECK AREA REG S SP. GIVER TO KERRING NEED LAKE FLAME PAK
80 | 72-30094-1 |  |  |  | Distribution Feeder Main |  | Fitting |  |  | Material Failure |  | 1972-03-03 | 1975-04-28 | Other |  | Steel/Wrought Iron |  |  | RECHECKED 11-20-1974 J.F.F. FOUND 20% GOES IN T.V. BOX NEXT TO SIDEWALK .23% SHORTSIDE OF SIDEWALK 100 PP MIN WATER BOX. REDOPED & TIGHTENED CONTROL CAP
80 | 73-30006-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-12-29 | 1973-01-04 | Patch Welded |  | Steel/Wrought Iron |  | MOUNTAIN VIEW | WELD PATCH ON 2" MAIN AT THE SERVICE FOR #521. INST 2-M2S ABANDON 9' OF 2" PIPE AND INST 9' OF 2" XTR. INSTALLED ANODE JW AREA ALL CLEAR
| 73-30006-1 | [16 empty] | MOUNTAIN VIEW | WELDED PATCH ON 2" MAIN AT THE SERVICE FOR #521. INST 2-M2S ABANDON 9' OF 2" PIPE AND INST 9' OF 2" XTR PIPE. INSTALLED ANODE JW AREA ALL CLEAR.
| 72-30441- |  |  | 8 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  |  | 1974-12-04 |  |  | Steel/Wrought Iron |  | SUNNYVALE | FOUND THREE 3/4" MULLER SERVICE TEAS LEAKING ALSO 8" STEAL MAIN LEAKING ON BOTTOM. WELD 8"X10" ON MAIN. USE 3 3"X2" WELD CANS. 3 2"X4" NIPPLES 3 2" WELD CAPS. INSTALLED 9 LB ANODE ON MAIN. J&W AREA CLEAR RECHECKED BY PINLEL TEES WERE BRAZED ON MAIN REASON FOR COVERING THEM. LEAK ORDER IN 12/6/1974 , 12/14/1974, 12/23/1974. BACKFILL DITCH WITH SAND. WRAP ON 8" GLAT MOISTURE UNCLEAR WRAP. ROCK IN BACKFILL BRAKING INTO WRAP 8" HAS SMALL PITS OVER 100% OF A RAY.
80 | 72-30408-1 |  |  | 2 | Distribution Feeder Main |  | Fitting |  |  | Construction Defect |  | 1972-11-24 | 1972-11-27 |  |  | Steel/Wrought Iron |  | SARATOGA | NO. CAP ON 2" CONTROL FITTING BLOWING TIGHTEN CAP INSTALLED ANODE. JW AREA FOUND MORE GAS WITH IN 4' OF TAP HOLE AIRING OUT RECHECK IN 30 DAYS.
72-34-1
80 | 72-61053-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-12-06 | 1972-12-07 | Other |  | Steel/Wrought Iron |  | MONTA VISTA | WELD 6" X3" PATCH ON 2" MAIN INST 9 LB ANODE. COULDN'T JW AREA TOO MUCH WATER UNDER GROUND BUT FOUND NO BUBBLING.
| 72-61053- | [16 empty] | MONTA VISTA | WELD 6"X3" PATCH ON 2" MAIN. INST 9LB ANODE COULDN'T JW AREA TOO MUCH WATER UNDERGROUND BUT FOUND NO BUBBLING,
80 | 72-61046-1 |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-11-28 | 1972-11-28 | Other |  | Steel/Wrought Iron |  | LOS GATOS | DOUND 1 DIME SIZE PIT WELD PATCH ON 3" MAIN. INST 9 LB ANODE. JW 50' BOTH SIDEWS OF LEAK AREA ALL CLEAR
| 72-61046- | [17 empty] | FOUND ONE DIME SIZE PIT WELD PATCH ON 3" MAIN. INST 9 LB ANODE JW 50" BOTH SIDES OF LEAK AREA ALL CLEAR
80 | 72-60997-1 |  |  | 0.75 | Service |  | Valves |  |  | Material Failure |  | 1972-10-26 | 1972-10-26 | Other |  | Steel/Wrought Iron |  | SUNNYVALE | SOAP TEST LEAKS
72-60477-1
80 | 72-60986-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-10-18 | 1972-10-19 | Patch Welded |  | Steel/Wrought Iron |  | SAN JOSE | WELD PATCH ON 2" HP MAIN INST 9 LB ANODE JW AREA (AIRING OUT) RECHECK IN 30 DAYS
| 72-60986- | [16 empty] | SAN JOSE | WELD PATCH ON 2" HP MAIN. INST 9 LB ANODE. JW AREA (AIRING OUT) RECHECK IN 30 DAYS
80 | 72-60959-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-09-28 | 1972-09-29 | Patch Welded |  | Steel/Wrought Iron |  | CUPERTINO | WELD PATCH ON 2" MAIN. JW AREA (AIRING OUT) RECHECK IN 30 DAYS. INST 1-9 LB ANODE
| 72-60959-X | [16 empty] | CUPERTINO | WELD PATCH ON 2" MAIN. JW AREA (AIRING OUT) RECHECK IN 30 DAYS. INST 1-9 LB ANODE
80 | 73-00148-1 |  |  | 3 | Distribution Feeder Main |  | Fitting |  |  | Material Failure |  | 1973-02-05 | 1973-03-01 | Other |  | Steel/Wrought Iron |  | SUNNYVALE | PLUG ON ABANDON SERVICE TEE LEAKING. TIGHTEN PLUG AND CAP FOUND LEAKAGE IN BOTH REG PITS. REGULATION WILL TAKE CARE OF IT. JW 50' BOTH SIDES OF LEAK AREA OVER MAIN AND SERVICE ALL CLEAN.
| 73-00148-1 | [16 empty] | SUNNYVALE | PLUG ON ABANDON SERVICE TEE LEAKING. TIGHTEN PLUG AND CAP FOUND LEAKAGE IN BOTH REG PITS. REGULATION WILL TAKE CARE OF IT. JW 50' BOTH SIDES OF LEAK AREA OVER MAIN AND SERVICE ALL CLEAN.
80 | 73-00091-1 |  |  | 22 | Transmission | [12 empty] | SAN JOSE | NO LEAK FOUND
80 | 73-60090- |  |  | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | NO LEAKS FOUND
80 | 73-00089- |  |  | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | NO LEAK FOUND
80 | 73-60621- |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-01-23 | 1973-01-23 | Patch Welded |  | Steel/Wrought Iron |  |  | WELD PATCH ON 2" MAIN INST 9 LB ANODE BAR. TEST ALL CLEAR.
80 | 73-60587-1 |  |  |  | Other |  | Other |  |  | Other |  |  | 1973-12-10 | Other |  | Other |  |  | NO LEAK FOUND; THIS WAS NOT A GAS LEAK. IN ABOUT HITTING OUR ELECT DUCT
80 | 74-30424-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-04-13 | 1974-10-30 |  |  | Steel/Wrought Iron |  | SUNNYVALE | SERVICE TEE TO 375 CYRRESS AVE WAS NOT WRAP AT TIME OF INSTALLATION. COMPLEATION CAP HATE GONE DUE TO CORROSION. DOPE BRASS PLAY AND INSTAK NEW SERVICE CAP. WELD PITS ON SERVICE TEE. INSTALL
| 74-30957- |  |  | 2 | Distribution Main |  | Fitting |  |  | Other |  | 1974-12-20 | 1974-12-20 |  |  | Steel/Wrought Iron |  | SUNNYVALE | FOUND 3/4" MULLER TEE CAP LEAKING REMOVE BRASS PLUG RECOAP. REDOAP COMPLATION CAP AREA. SILL HAS GAS
| 74-30957 | [16 empty] | SUNNYVALE | FOND 3/4" MULLER TEE CAP LEAKING. REMOVE BRASS PLUG RECOAP. REDOAP COMPLATION CAP AREA STILL HAS GAS
| 74-30956- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-12-24 | 1974-12-24 |  |  | Steel/Wrought Iron |  | SUNNYVALE | FOUND 2" MAIN LEAKING DUE TO SEWER INSTALLER BREAKING WRAP OFF MAIN. WELD 7"X4" PATCH ON MAIN. J&W AREA CLEAR.
| 74-30956- | [16 empty] | SUNNYVALE | FOUND 2" MAIN LEAKING DUE TO SEWER INSTALLER HACKING WRAP OFF MAIN WELD 7"X4" PATCH ON MAIN J&W AREA CLEAR
| 74-30955- |  |  | 1.25 | Distribution Main |  | Fitting |  |  | Other |  | 1974-12-18 | 1974-12-18 |  |  | Plastic
8 | 74-30951- |  |  | 1.25 | Distribution Main |  | Fitting |  |  | Other |  | 1974-12-17 | 1974-12-18 |  |  | Plastic |  | MOUNTAIN VIEW | LEAKAGE FOUND AT EDGE OF DRIVEWAY NEXT TO TRAINFORMER READING IN TRANSFORMER ALSO. 800 PPM SO.X. 5% JW
| 74-30934- |  |  | 2 | Distribution Main |  | Other Welds |  |  | Other |  | 1974-12-06 | 1974-12-09 |  |  | Steel/Wrought Iron |  |  | 2" P.C.F. LEAKING DUE TO AND FIELD WELD AT TWO PLACES REWELD SAME SOAP TEST OK. AREA NEAR J&W INSTALL 9TH ARADE ON MAIN.
80 | 74-30917- |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-11-06 | 1974-11-08 |  |  | Steel/Wrought Iron |  | LOS ALTOS HILLS | ARE WELDED 4 5"X5" PATCH OVER LEAKS LINE B
8 | 74-30903- |  |  | 0.34 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-10-29 | 1974-10-29 | Other |  | Steel/Wrought Iron |  | SUNNYDALE | CAUSE OF LEAK CORROSION. REPAIRED BY INSERTING 1/2" PLASTING STANDARD POWELL RISER IN. ; NOTE THIS SERVICE WAS TO BE REPLACED BY CREW RENEWING GAS MAIN AND SERVICES AT THIS LOCATION ON DN G92423
| 74-30903- | [16 empty] | SUNNYDALE | CAUSE OF LEAK CORROSION. REPAIRED BY INSERTING 1/2" [;ASTOC STANDARD POWELL RISER IN.; NOTE THIS SERVICE WAS TO BE REPLACED BY CREW RENEWING GAS MAIN AND SERVICES AT THIS LOCATION ON G92423.
| 74-30894- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-11-07 | 1974-11-08 |  |  | Steel/Wrought Iron |  | CAMPBELL | 2" STEEL H.P. MAIN LEAKING DUE TO ROCK IN BACKFILL DAMAGING WRAP. ARC TWO PATCHES ON 7"X3" ONE 6"X3". ARE TO BE RECHECKED IN 30 DAYS. PHONE VOLTS & SEWER MAN HOLES CLEAR. SOAP TEST VALVE ON 5/W CORNER CLEAR INSTALLED 9TH ANODE ON MAIN.
8 | 74-30889- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1974-10-24 | 1974-10-24 | Patch Welded |  | Steel/Wrought Iron |  | SUNNYVALE
80 | 74-30842- |  |  | 0.38 | Other |  | Fitting |  |  | Other |  | 1974-09-12 | 1974-09-12 |  |  | Copper |  | MOUNTAIN VIEW | FOUND 3/8" FITTING LEAKING. REPAIRS MADE BY TIGHTENING FITTING. CALL REGULATION TO COME OUT AND LOOK AT OLD METERING STN. NOTHING ELSE COULD BE DONE BY CREW. REGULATION SAID THEY WOULD TAKE CARE OF METERING STN.
80 | 74-30805- |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-08-22 | 1974-08-22 | Patch Welded |  | Steel/Wrought Iron |  | SUNNYVALE | WELD PATCH ON 2" MAIN INST ALB ANODE JW AREA ALL CLEAR
8 | 75-20429- |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1975-05-16 | 1975-05-16 |  |  | Plastic |  |  | TWO FEET SECTION OF PL PIPE REMOVED AND REBALANCED BY A NEW SECTION OF PL PIPE AND TWO PC 4" COUPLING
| 75-60093- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-03-10 | 1975-03-10 |  |  | Copper |  | LOS ALTOS | FOUND 3/4" STEEL & CAP. SERVICE LEAKING DUE TO LOAD FIELD WRAP. INSRET 42' MAIN TO LP. DIRECT BURY 32' P TO RISE 1/2" P.L STANDARD INSTALL POWER LASER KIT. PUMP & TEST. J & W OVER CLEAR.
75-60082- | [17 empty] | PALO ALTO | FOUND 3/4" STEEL SERVICE LEAKING UNDER CEMENT WALK AT SWIMMING POOL. INSERT 42' 1/2' STANDARD P.L. INSTALL POWELL RISER KIT.PUMP & TEST SERVICE OK. GAS STILL IN ALLEY WELL CLEAR ON R.C. ORDER. NO CAVAING ORDER DIRT.
| 75-60082- |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1975-02-28 | 1975-02-28 |  |  | Steel/Wrought Iron |  | PALO ALTO | FOUND 3/4" STEEL SERVICE LEAKING UNDER CEMENT WALK AT SWIMMING POOL. INSERT 42' 1/2 STANDARD P.L. INSTALL POWELL RISER KIT. PUMP&TEST SERVICE OK. GAS STILL IN ALLEY WELL CLEAR ON R.C. ORDER
80 | 75-60423- |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1975-10-21 | 1975-10-22 | Clamp |  | Steel/Wrought Iron |  | SUNNYVALE | CAUSE OF LEAK 2ND WATCH CROSSINV OVER 2" GAS LINE. WATER TO CLOSE TO WELD A PATCH. INST 2" 2 BOLT SKINNER CLAMP. INST 9 LB ANODE BAR TEST AREA ALL CLEAR NO PAVEMENT.
| 75-60397- |  |  | 1.14 | Other |  | Body of Pipe |  |  | Corrosion |  | 1975-10-08 | 1975-10-08 | Clamp |  | Steel/Wrought Iron |  |  | FOUND GAS LEAK IN HIGH HOUSE LINE FOR SCHOOL. J SANDOVAL CLOCKED GAS INTO HR. LEAK. WE PUT 4 CLAMPS ON HOUSE LINE TO TEMP REPAIR AND. NO LEAKAGE; J. 10 ; HOUSELINE LEAK;
| 75-60349- |  |  | 1.14 | Other |  | Fitting |  |  | Damage by outside Forces |  | 1975-08-23 |  | Other |  | Steel/Wrought Iron |  | SUNNYVALE | UNKNOWN AUTO STRUCK 2 4 MTK HDR ALONG DR. WY TO REAR APTS AT 311 HASTRE TO, NIPPLE ON HEADER WAS BROKEN OFF. 4 UNITS HAD TS BE SHUTOFF. REPAIRS WERE MADE BY WELDING NIPPLE ON HDR AND J.W. SERVICE, NO MICLIC OF GAS FOUND.
| 76-00200- |  |  | 4 | Transmission |  | Valves |  |  | Other |  | 1976-08-23 | 1976-08-24 | Other |  | Steel/Wrought Iron |  | SUNNYVALE | GAS REG. SHOP GREASED LEAKING 4" VALVE FEEDING PITS FROM #132. MAIN NOT EXPOSED.
| 76-00199- |  |  | 0.75 | Other |  | Other |  |  | Corrosion |  | 1976-08-23 | 1976-08-24 | Other |  | Steel/Wrought Iron |  | SUNNYVALE | SERVICE & MAIN NO EXPOSED
| 76-30667- |  |  | 0.34 | Other |  | Other |  |  | Other |  | 1976-03-10 | 1976-03-10 | Other |  | Other |  | SARATOGA | CHECKED OVER SERVICE AND MAIN WITH J.W. NO ... NOTIFIED GAS DISPATCHER AND ...SERVICEMAN TO CHECK ...LINE
80 | 76-30420- |  |  |  | Other |  | Fitting |  |  | Material Failure |  | 1976-02-10 | 1976-02-10 |  |  |  |  | SUNNYVALE | FOUND LEAK ON STOP COCK AND METER SET.REPLACED STEP COCK AND TURNED METER SET OVER TO SERVICE MAN TO REPLACE.
80 | 76-30390- |  |  |  | Other |  | Other |  |  | Other |  | 1976-02-05 | 1976-02-05 | Other |  | Other |  | CUPERTINO | REPAIRED LEAK AT 6211 BALSAMO 301 AT 6219 HAS AIRED OUT REFER TO LEAK #76-30389
| 76-30323- |  |  | 0 | Other |  | Meter |  |  | Other |  | 1976-02-02 | 1976-02-02 | Other |  | Other |  | SUNNYVALE | J.W. OVER SERVICE AND MAIN. NO INDIE OF GAS WITH J.W. FOUND 301 ON GAS ... GAS SERVICE DEPT. MARK REPAIRED; MAIN NOT EXPOSED.
| 76-30280- |  |  | 0.34 | Other |  | Other |  |  | Other |  | 1976-01-29 | 1976-01-29 | Other |  | Steel/Wrought Iron |  | SAN JOSE | J.W. SERVICE NO INDIE. OF GAS FOUND. LEAKAGE WAS FOUND UNDER GAS MTR., UNION 3/4" REG, AND ON FITTING ON U.G. HOUSELINE. ALL REPAIRS MADE BY GAS SERVICE DEPT.; MAIN NOT EXPOSED
80 | 76-30167- |  |  |  | Other |  | Meter |  |  | Other |  | 1976-01-19 | 1976-01-19 | Replace Pipe and/or Service |  | Other |  | SUNNYVALE | FOUND METER LEAKING TURNED IN TO SERVICEMAN TO REPLACE. BAR TEST OVER SERVICE & MAIN FOUND NO READINGS.
| 77-30383- |  |  | 0.75 | Other |  | Other |  |  | Other |  | 1977-04-04 | 1977-04-04 | Other |  | Steel/Wrought Iron |  | MOUNTIAN VIEW | ...SERVICEMAN R. TA...HOUSE LINE AND FOUND 10 1/2" OUTFT. HR. LEAK IN ...
| 77-31379- |  |  | 10 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1977-09-27 | 1977-09-27 | Other |  | Steel/Wrought Iron |  |  | PER BOB..., JOHN...FROM REG. DEPT. WAS SEAT CUT ON THIS LEAK IN REG. PIT. C.A.W.
8 | 77-31282- |  |  | 0 | Other |  | Other |  |  | Other |  | 1977-09-19 | 1977-09-19 | Other |  | Other |  | LOS ALTOS | THIS LEAK WAS REPAIRED ON LK # 7731283 FOR 892 UNIVERSITY
| 77-31581- |  |  |  | Other | MANIFOLD | Fitting |  |  | Construction Defect | [5 empty] | Steel/Wrought Iron |  | SUNNYVALE | STOPPAGE MAKE LEAKING ON 2 METER MANIFOLD. TIGHTENED COKE TO REPAIR LEAKAGE. J.W. AREA ALL CLEAR ON
| 77-31576- |  |  |  | Other | METER | Meter |  |  | Material Failure |  |  |  | Replace Pipe and/or Service |  | Cast Iron |  | SUNNYVALE | FOUND METER LEAKING IN CURB METER BOX. TURNED INTO DISPATCH TO REPLACE METER. J.W. AREA ALL CLEAR ON 4% JOACE.
82 | 77-31513-1 |  |  | 24 | Transmission | [6 empty] | 1977-10-25 |  |  |  | Steel/Wrought Iron |  | STANFORD | 8.000P.P.M. IN VALVE. NO OTHER GAS FOUND
8 | 77-60491- |  |  | 0.75 | Other |  | Regulator |  |  | Other |  | 1977-11-01 | 1977-11-09 | Other |  | Steel/Wrought Iron |  | CAMPBELL | FOUND 3/4" NIPPLE ON TOP OF 3/4"...COCK LEAKING. J.W. RISER NO INDIE. FOUND. SERVICE & MAIN UNDER CONCRETE SLAME PAK. RECHECKED AREA. MADE TAG FOR SERVICE DEPT TO REPAIR 3 MTR H.D.R. GAVE TO BILL SCHRADER.
| 77-60460- |  |  |  | Other |  | Fitting |  |  | Other |  | 1977-10-12 |  |  |  | Steel/Wrought Iron |  | MOUNTAIN VIEW | FLAMEPACKED FOUND FITTING A WATER LEAKING MADE PINK TAG FOR SERVICE ADAPT TO FIX REFOLDS
8 | 77-60267- |  |  | 0.75 | Other |  | Other |  |  | Other |  | 1977-06-17 | 1977-06-17 | Other |  | Steel/Wrought Iron |  | LOS GATOS | PISANO BROS. INC. WAS INSTALLING NEW WATER MAIN ON ROBERTS RD. THEY STRUCK AN UNKNOWN 3/4" STEEL PIPE. IN CHECKING OUT THIS LINE WE FOUND IT TO BE AN ABANDON PIECE OF PIPE. WE CUT IT AND PUT DUCT SEAL IN EACH END. ALL LIVE GAS LINES HAD BEEN MARKED BY LOCATION
80 | 77-60079- |  |  |  | Other |  | Meter |  |  | Other | ; | 1977-02-15 | 1977-02-15 | Replace Pipe and/or Service |  | Other |  |  | BAR TEST OVER MAIN & SER FOUND NO READINGS. ; FOUND LEAKS ON METER SET TURNED INTO SREVICE DEPT.; FLAME PACK AREA BY FEYLINS FOUND NO READINGS
8 | 78-30560- |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  |  | 1978-04-21 |  |  | Plastic |  | LOS GATOS | FOUND 1/2 CU. SERVICE LEAKING AT MAIN AND RISER. INSTALLED 1/2 P.L. SERVICE D.B. INSERT 1 1/4" P.L. MAIN AREA CLEAR
| 78-30519- |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1978-03-07 | 1978-03-10 |  |  | Steel/Wrought Iron |  | LOS ALTOS HILLS | INSERT 2" PL. IN 3" CASEING BACKFILL WITH SAND 2' OVER MAIN. PUMP & TEST 30 MIN OK. INSTALL 17 LB ARODE F&C
| 78-30315- |  |  |  | Other | HOUSELINE | Body of Pipe |  | HOUSELINE | Corrosion |  |  |  | Other | NO REPAIR MADE | Steel/Wrought Iron |  | SUNNYVALE | SEAL METER UNDER REPAIRS MADE ON 4TH OTHER
8 | 78-30107- |  |  |  | Other |  | Fitting |  |  | Other |  | 1978-02-01 | 1978-02-02 | Other |  | Steel/Wrought Iron |  | SUNNYVALE | J.W. OVER SERVICE NO INDIE. OF GAS FOUND. DUG UP 3/4" RISER & 5' GAS SERVICE AND CHECKED SERVICE NO LEAKAGE FOUND. FOUND 2 LEAKS ON AL 425 GAS MTR SET. 1 ON ELBOW TO INLET AND ON 1 1/4 PLUG. NOTIFIED GAS DISPATCH TO REPAIR MTR SET.
80 | 78-31043- |  |  |  | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1978-05-23 | 1978-05-23 | Clamp |  | Steel/Wrought Iron |  | SAN JOSE | FOUND 1 1/4" STL MAIN LEAKING 4" FROM STREET LIGHT POLE. TO CLOSE TO POLE TO WELD PATCH, INST 1 1/4" 2 BOLT SKINNER CLAMP; SAND BACK FILL
| 00-30597- |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 2000-08-05 | 2000-08-05 | Mechanical Repair Fitting - Fitting |  | TR 418 |  | MONTE SERENO | INSTALL 1' OF 1/2" PLASTIC & TWO PERMANENT COUPLINGS
| 98-30685-1 |  |  | 1.25 |  |  | Body of Pipe |  |  |  |  | 1998-09-14 |  | Replace Pipe |  | TR 418 |  | SALINAS | REPLACE 3' OF PIPE
| 08-30002-1 | 132A | 0 | 0.75 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2008-01-16 | 2008-02-14 | Replace TP Main |  | Steel/Wrought Iron |  | MT. VIEW | 5' 3/4" TAP PIPING REPLACED; 5' OF PIPE REPLACED. 3 SMALL EXTERNAL CORROSION LEAKS. NOTE: SCADA TAP FOUND UNPROTECTED ON 11/15/07 AND THEN PLACED UNER FROTECTION BY WAYNE SHIMODA. NOTE: MUCH OF THIS A-FORM WAS FILLED OUT BY DREW KELL WHO HAD PERSONAL KNOWLEDGE OR WITNESSED ALL WORK.
| 08-30571-1 | [10 empty] | 2008-04-30 | [5 empty] | SUNNYVALE
| 07-30085-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2007-07-10 | 2007-10-02 | Replace Dist Main >= 100 ft |  | Steel/Wrought Iron |  | LOS ALTOS | INSERT OF MAIN; WAYNE SHIMODA INVESTIGATED AND FOUND CPA 3349-01 DOWN AND THE RESTORED ON 10/04/07. ...ANODE INSTALLED @2672 BYPASS PACKING...3/4/08
| 06-30616-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2006-08-29 | 2006-08-29 | Replace Entire Service |  | Steel/Wrought Iron |  | SUNNYVALE | INSERTED SERVICE
| 04-30140-1 | [10 empty] | 2004-08-20 | [5 empty] | PALO ALTO | FLAME PACKED ALL OF LINE 109 IN INTERSECTION OF ARASTRADERO & MCKELLAR AND NO GAS WAS FOUND. 14' SOUTH OF TRANS LINE IS PALO ALTO DISTRIBUTION VALVE. ONLY GAS FOUND WAS IN FRAME & COVER. PULLED COVER & VERIFIED LEAK WITH LEAK SOAP. BILL LAKE WILL CONTACT CITY OF PALO ALTO TO MAKE THEM AWARE THAT LEAK IS ON THEIR FACILITY.
| 04-30140-1 | [10 empty] | 2004-08-20 | [5 empty] | PALO ALTO
| 03-30027-1 | [10 empty] | 2003-04-22 | [5 empty] | L.A. HILLS
| 03-30028-1 |  |  | 2 | Distribution Main |  | Valves |  |  | Material Failure |  | 2003-04-21 | 2004-10-12 | Other | GREASED VALVE | Steel/Wrought Iron |  | LOS ALTOS | DUG UP VALVE, REPLACED FRAME, COVER & CASING. GREASED VALVE.; REPLACED FRAME, COVER AND CASING. GREASED VALVE.
| 03-30028-1 | [10 empty] | 2003-04-21 | [5 empty] | LOS ALTOS | GETTING READINGS FROM...WHERE VALVE SHOULD BE, VALVE IS BURRIED
| 03-30028-1 |  |  | 2 | Distribution Main |  | Valves |  |  | Material Failure |  | 2003-04-21 | 2004-10-12 | Other | GREASED VALVE | Steel/Wrought Iron |  | LOS ALTOS | DUG UP VALVE, REPLACED FRAME, COVER & CASING. GREASED VALVE.; REPLACED FRAME, COVER, AND CASING. GREASED VALVE
|  |  |  | 2 | Service |  | Body of Pipe |  |  | Digin |  | 2002-05-07 | 2002-05-07 | Service Partially Replaced |  | Steel/Wrought Iron |  | LOS GATOS | GAS FOUND AT WATER VALVE IN STREET AT WEST PROP. LINE POST REPAIR CHECK NEW LEAK # IS 02-30085- ; USED 3' OF 3/4" STL PIPE
|  |  |  | 2 | Service |  | Body of Pipe |  |  | Digin |  | 2002-05-07 | 2002-05-07 | Service Partially Replaced |  | Steel/Wrought Iron |  | LOS GATOS | GAS FOUND AT WATER VALVE IN STREET IN FRONT OF 175 AT WEST PROP. LINE. BETWEEN 119 & 123 SDWLK. POST REPAIR RECHECK # 15 02-30085
| 09-20152-1 | 0804-01 | [9 empty] | 2009-05-07 | [5 empty] | SANTA CLARA | NLF FOLLOWING REPAIR OF SEPERATE LEAK
| 09-20153-1 | 0804-01 |  | 6 | Distribution Main |  | Valves |  |  | Other | LACK OF GREASE, LOOSE FITTINGS | 2009-05-07 | 2009-07-02 | Other | GREASE & RE DOPE | Steel/Wrought Iron |  | SANTA CLARA | GREASED VALVE #7 & REPAIRED NIPPLE ON PILOT & SOAP TESTED
78 | 09-20874-1 |  |  | 2 | Distribution Main >60 PSIG and <20% SYMS |  | Other |  | STEEL CONTROL CAP 2" | No/Deteriorated Pipe Dope |  | 2009-10-06 | 2011-05-02 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SAN JOSE | TIGHTEN CAP; TIGHTEN 2" STEEL CAP. SOAP TEST OK
| 09-20874-1 | [10 empty] | 2009-10-06 | [5 empty] | SAN JOSE | INFO ONLY
| 10-10151-1 |  |  | 2 | Distribution Main |  | Other |  | BOLT ON TEE | Unknown |  | 2010-04-25 | 2010-04-25 | Replace Dist Main < 100 ft |  | Aldyl A (Tan or Gray) |  | GILROY | INSTALLED 2' DRISCOPLEX 2" MAIN. REPLACED BOLT ON TEE WITH ELEC-FUSION 2 X 1/2 SVC TEE
| 10-10187-1 | 100 |  | 20 | Transmission | TRANSMISSION VALVE | Valves |  |  | Other | NEEDED GREASE | 2010-05-12 | 2010-05-14 | Other | GREASED | Steel/Wrought Iron |  | SAN JOSE | GREASED VALVE0 SOAP TESTED; SEE ATTACHED SHEET
78 | 10-10203-1 | 0814-05 |  | 4 | Transmission >= 20% SMYS |  | Line Valve |  |  | No/Deteriorated Pipe Dope |  | 2010-05-14 | 2010-11-24 | Greased - Other |  | Steel-Other |  | SAN JOSE | GREASED VALVE & REG-SEATED; NOT ABLE TO SEE PIPE, ONLY STEM FOR GREASING. GREASED/SOAP TESTED, OK.; SEE ATTACHED SHEET
| 10-10211-1 |  |  | 8 | Transmission |  | Valves |  |  | Other | VALVE. JUST NEEDED TO BE WORKED |  | 2010-05-20 | Other | WORKED GATE VALVE BACK & FORTH | Steel/Wrought Iron |  | GILROY | WORKED GATE VALVE- SOAP TESTED- NO BUBBLES OR FOAM
| 10-10212-1 | 0833-01 |  | 6 | Transmission |  | Fitting |  |  | Construction Defect |  | 2010-05-18 | 2010-07-21 | Tighten Cap or Bolt | BLEW OUT CONTAMINANT SO THAT VALVE IN PCF SEATED CORRECTLY. | Steel/Wrought Iron |  | GILROY | B;EW OUT CONTAMINANT SO THAT VALVE IN P.C.F. SEATED CORRECTLY
78 | 10-10214-1 |  |  | 1.25 |  |  | Fitting | Threads |  | Damage by 3rd Party |  | 2010-05-18 | 2011-05-26 | Mechanical Repair Fitting - Fitting | SOAP AND/OR TAPE - OTHER | Steel-Other |  | SAN MARTIN | REPAIRED ALL LEAKS; SOAP TEST OK.
| 10-10217-1 |  |  | 6 | Transmission |  | Fitting |  |  | Other | VALVE NEEDED GREASE | 2010-05-19 | 2011-03-04 | Other | GREASED VALVE | Steel/Wrought Iron |  | GILROY | GREASED VALVE; "SOAP TEST OK."; SEE ATTACHED MAP
| 10-10235-1 | 300A |  |  | Transmission |  | Other |  | NONE FOUND | Other | NO LEAK FOUND | 2010-05-28 |  | Other | NO LEAK FOUND | Steel/Wrought Iron |  | GILROY | NONE, NO LEAK FOUND
| 10-10249-1 | 0813-09 |  | 0.75 | Transmission |  | Fitting |  |  | Other | LOOSE CAP | 2010-06-07 | 2010-08-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN JOSE | TIGHTEN & REDOPE CAPS; SOAP TEST PIN OFF TEE CAP LEAK. RETIGHTEN CAP. SOAP TEST LEAK STOPPED #41327885
| 10-11031- |  |  | 0.75 | Transmission |  | Valves |  |  | Other | DRIED OUT PIPE DOPE | 2010-09-18 | 2010-09-29 | Other | CLEANED REDOPED CAPS ON 2 SAV A VALVES 2 GREASE FITTINGS | Steel/Wrought Iron |  | SAN JOSE | SEE BELOW; CLEARANCE SJ 10-09- BROUGHT PRESSURE DOWN FLAT. VALVE 11 TO TALL. EXPOSED- FOUND LEAKS ON 2 SAV-A-VALVE CAPS ON EITHER SIDE OF VALVE. REMOVED CAPS, CLEANED, REDOPED, TIGHTENED- 2 LEAKS ON GREASE FITTING- REMOVED, CLEANED REDOPED, TIGHTENED, SOAP TESTED ALL UNDER PRESSURE- GOOD
| 10-11075-1 | 300A |  | 34 | Transmission |  | Valves |  |  | Other | 3/4 PLUG | 2010-10-05 | 2010-12-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | GILROY | 3/4 PLUG TIGHTEN REDOPE; .../ PLUG REDOPED AND TIGHTEN; IN BOX NEXT TO SONIC METER PLUG LOOSE. VALVE IN SMALL VAULT
| 10-11335-1 | 0833-01 |  | 8 | Transmission |  | Fitting |  |  | Other | LOOSE PLUG | 2010-10-27 | 2011-01-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | GILROTY | REDOPED LOOSE PLUG ON BLEED VALVE @ V-82 A-80 TIGHTENED FITTING (SOAP TEST OK)
78 | 10-11342-1 | 382704 |  | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-11-08 | 2011-03-07 | Deactivated Partial Service | MECHANICAL REPAIR FITTING - FITTING, OTHER | Steel-Other |  | SAN JOSE | TIGHTEN FITTING
| 10-10588-1 | 100 |  | 4 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2010-09-11 | 2010-09-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN JOSE | REDOPED & TIGHTENED PLUG ON A VALVE; TIGHTENED & REDOPED PLUG ON LINE VALVE OF TRANSMISSION WHEEL VALVE: SOAP TEST OK
| 10-10589-1 | [10 empty] | 2010-09-11 | [5 empty] | MORGAN HILL | HOUSE LINE LEAK- EXPOSED LEAK SHUT-OFF ROTORY METER SET. 9-11-10
| 10-10590-1 | 100 |  | 6 | Transmission |  | Fitting |  |  | Unknown |  | 2010-09-11 | 2010-09-12 | Other | REPLACE GREASE BUTTON | Steel/Wrought Iron |  | SAN JOSE | LEAK FROM GREASE BUTTON HAD TO REPLACE IT.; GRASE BUTTON LEAKING @ V-3414-C6B, REPLACED GREASE BUTTON, SOAP TEST GOOD
| 10-10591-1 |  |  | 8 | Distribution Main |  | Valves |  |  | Other | GREASE | 2010-09-11 | 2010-09-12 | Other | GREASE | Steel/Wrought Iron |  | SAN JOSE | GREASE VALVE LEAK STOPPED; GREASE VALVE SOAP TEST OK
| 10-10592-1 | 100 |  | 6 | Transmission |  | Valves |  |  | Incorrect Operation |  | 2010-09-11 | 2010-09-12 | Other | OPERATE VALVE | Steel/Wrought Iron |  | SAN JOSE | RESEAT VALVE; OPERATE VALVE. SOAP TEST OK.
| 10-10593-1 | 101 |  | 36 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2010-09-12 | 2010-09-12 | Other | TIGHTEN FITTING | Steel/Wrought Iron |  | SAN JOSE | TIGHTENED TUBE FITTING; TIGHTENED LOOSE TUBE FITTING; SOAP TESTED OK. GREASED INLET VALVE
| 10-10594-1 | 100 |  | 2 | Transmission |  | Valves |  | A-L100 | Material Failure | GASKET | 2010-09-12 | 2010-09-17 | Other | REPLACE GASKET | Steel/Wrought Iron |  | SAN JOSE | CLEARANCE SJ 10-08- REMOVED BONNET ON 2" KENOTEST (720W09) SERIES 300. BALL VALVE, CLEANED, REPLACED GASKET
| 10-10595-1 | 100 |  | 20 | Transmission |  | Valves |  |  | Other | OPERATE VALVE | 2010-09-12 | 2010-09-12 | Other | OPERATE VALVE | Steel/Wrought Iron |  | SAN JOSE | OPERATE VALVE SOAP & GAS TRACT OK
| 09-10013-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other | NORMAL WEAR & TEAR | 2009-01-11 | 2009-03-18 | Other | TORE APART - RETIGHTEN | Steel/Wrought Iron |  | MORGAN HILL | REPARED LEAKS SOAP TEST OK; SOAP TEST FITTINGS
| 09-10013-1 | [10 empty] | 2009-01-11 | [5 empty] | MORGAN HILL | SOAP TEST FITTINGS; SEE LAST PAGE
| 09-10171-1 | 0809-01 |  | 0.75 | Single Service |  | Riser |  |  | Construction Defect |  | 2009-05-29 | 2009-05-29 | Other | DOPE THREAD ON STOP COCK | Steel/Wrought Iron |  | MORGAN HILL | SOAP TEST
| 09-10275-1 |  |  | 2 | Distribution Main |  | Regulator |  |  | Equipment Malfunction |  | 2009-11-23 | 2010-02-05 | Other | SHUT-IN STATION | Steel/Wrought Iron |  | MORGAN HILL ; | SHUT IN STATION THAT WAS VENTING GAS; INSIDE REG VAULT 11-23-09. SAN JOSE GAS T & R ELIMINATED LEAK BY SHUTTING-IN REG STATION H-13 AT HILL & DIANA. PROBLEM W/2 REGULATOR.; SHUT-IN STATION TO ELIMINATE LEAK GAS ENGINEERING TO REVIEW ABANDON/REBUILD OPTIONS. STATION "SHUT-IN" 2/5/10 BY FRED GARCIA- FBG3. PLEASE GIVE PAPER WORK TO SCOT FANNON.
| 09-10280-1 |  |  | 6 | Transmission |  | Valves |  |  | Other | DRY VALVE | 2009-12-09 | 2009-12-09 | Other | GREASE VALVE | Steel/Wrought Iron |  | SAN JOSE | GREASED/SOAP TEST
| 09-10966- |  |  | 1.25 | Single Service |  | Riser |  |  | Atmospheric Corrosion |  | 2009-11-23 | 2009-11-23 | Replace Partial Service |  | Steel/Wrought Iron |  | MORGAN HILL | WELDED M2, AND CUT & THREADED RISER; CUT & THREAD @ RISER
| 10-20135-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2010-02-08 | 2010-05-06 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | SANTA CLARA | INSTALLED SKINNER CLAMP OVER PIT ON 4" STL. MAIN.
| 10-20135-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2010-02-08 | 2010-05-06 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | SANTA CLARA | INSTALLED SKINNER CLAMP OVER PIT ON 4" STL. MAIN
| 10-20550-1 | [10 empty] | 2010-04-09 | [5 empty] | SAN JOSE | FOUND NO LEAK; GAS SENTRY BOTH VAULTS -0. GAS TRACK BOTH VAULTS - 0. TEST WATER BOX - 0
| 10-20551-1 | 300A |  | 20 | Transmission |  | Valves |  |  | Unknown |  | 2010-04-09 | 2010-06-29 | Other | GREASED | Steel/Wrought Iron |  | SAN JOSE | GREASED & OPERATED VALVE; GREASED VALVE, OPERATED VALVE, SOAP TEST - GOOD
| 10-20601-1 |  |  | 6 | Transmission |  | Fitting | Other |  | Material Failure |  | 2010-04-29 | 2010-05-24 | Other | GREASE VALVE | Steel/Wrought Iron |  | MILPITAS | GREASE VALVE; SOAP TEST. GREASE INTO FITTING (VALVE)
| 10-20601-1 | [10 empty] | 2010-04-29 | [5 empty] | MILPITAS
| 10-21237-1 | [10 empty] | 2010-07-13 | [5 empty] | SAN JOSE
| 10-21702-1 | 300A | 502.12 | 34 | Transmission |  | Other |  | BODY CAVITY PLUG | Other | DRY SEALANT | 2010-09-11 | 2010-09-13 | Other | CLEANED PLUG THREAD AND REPLA | Steel/Wrought Iron |  | MILPITAS | GENERAL INFORMATION: DUG UP MLV 502.12 300A APPROXIMATLY 10' EXPOSED FOUND 2ND BODY CAVITY PLUG LEAKING. CLEANED & REPLACED PLUG LINE STEEL 34"
| 10-21703-1 |  |  | 8 | Distribution Main |  | Fitting |  |  | Other | LOOSE FITTING | 2010-09-11 | 2010-09-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MILPITAS | LOOSE FITTING, TIGHTENED STAINLESS STEEL CONNECTION; TIGHTENED LOOSE SENSE LINE CONNECTION DOWNSTREAM PIT. SOAP TEST GOOD
| 10-21704-1 | 100 |  | 4 | Transmission |  | Valves |  |  | Unknown |  | 2010-09-11 | 2010-09-12 | Other | GREASED VALVE; | Steel/Wrought Iron |  | SAN JOSE | V-1 LEAKING, GREASED VALVE IN ORDER TO STOP LEAK; FOUND V-1 IN UPSTREAM PIT LEAKING, GREASED VLAVE TIGHTENED BOLT. SOAP TEST OK
| 10-21705-1 | 100 |  | 24 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2010-09-11 | 2010-09-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MILPITAS | LOOSE GREASE BUTTON, TIGHTENED DOWN FITTINGS; TIGHTENED LOOSE GREASE BUTTON FITTING: SOAP TEST GOOD
| 10-21707-1 | 132 |  | 24 | Transmission |  | Fitting |  |  | Unknown |  | 2010-09-12 | 2010-09-12 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | SAN JOSE | TIGHTEN SENSING LINE FITTING AND SOAP TESTED OK
| 10-21708-1 | 109 |  | 3.5 | Distribution Main |  | Fitting |  |  | Other | LOOSE FITTING | 2010-09-12 | 2010-09-12 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | SAN JOSE | RESEAL PIPE PLUG & SOAP TESTED OK
| 10-21709-1 | 109 |  | 24 | Transmission |  | Valves |  |  | Unknown |  | 2010-09-10 | 2010-09-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MILPITAS | GREASED BOLT FITTING STEM; GREASED VALVE STEM SOAP TEST OK
78 | 10-21795-1 | 132 |  | 6 | Transmission >= 20% SMYS |  |  |  |  | Incorrect Operation |  | 2010-10-23 | 2010-10-23 | Other |  |  |  | SAN JOSE | IGIS COPY POSS DUPL/W 10-81162. TRANSMISSION LEAK. ORIGINAL COPY IN WALNUT CREEK.; RESEALED GATE VALVE
| 10-21811-1 | 100 | 149.3 | 6 | Transmission |  | Valves |  |  | Incorrect Operation |  | 2010-11-08 | 2010-11-08 | Tighten Cap or Bolt | SOAP AND/OR TAPE | Steel/Wrought Iron |  | MILPITAS | TIGHTENED VALVE....; LEAK FOUND AROUND PLUG. ...AND RETIGHTENED PLUG TO REPAIR LEAK. VALVE BOX V-158 IN DIRT AREA IN VALVE BOX NUMBERED V-158 217 BARBER CT. MILPITAS ABBOTT DFM + L100. LEAK FOUND AROUND VALVE WERE ATTACHED TO NIPPLE. REPAIRED BY TIGHTENING. LEAK FOUND AROUND HANDLE OR VALVE. RETIGHTENED TO REPAIR LEAK.
78 | 11-10111-1 | 300A |  | 0.75 | Transmission >= 20% SMYS |  | Line Valve |  |  | Unknown |  | 2011-04-19 | 2011-04-24 | Replace Service Valve <2-inch | REPLACE SERVICE VALVE <2 INCH - REPLACE, OTHER | Steel-Other |  | GILROY | REPLACED THE BALL VALVE; FOUND 1/4" PLUG VALVE CRACKED @ TANG OLD NORTH STEM VALVE. REPLACED WITH 2000# BALL VALVE. FIXED SMALL FOAMER D/S ON HPR
78 | 11-10114-1 |  |  | 0.75 | Branch Service |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2011-04-19 | 2011-06-21 | Other |  | Steel-Other |  | SAN MARTIN | TIGHTENED THREADS; TIGHTEN THREADS SOAP TEST OK
| 11-10115-B |  |  | 0.75 | Single Service |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2011-04-19 | 2011-04-22 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SAN MARTIN | REDOPED, TIGHTEN FITTING & THD; STAND-BY REMOVED WTR AND MUD. T&R FIXED 3 LEAKS ON PIN-OFF TEE CAP; UNION HP; 1/4" PLUG. 2ND CORRECTION TURNED IN FOR UPGREAD HPR SET.; SEE ATTACHED MAP
78 | 11-10124-B |  |  | 2 | Transmission >= 20% SMYS |  | Pressure Control Fittings |  |  | No/Deteriorated Pipe Dope |  | 2011-04-19 | 2011-07-11 | Other | RE-DOPE AND TIGHTEN CAP | Steel-Other |  | SAN MARTIN | REDOPE CAP, TIGHTEN COMPETION PLUG; REDOPE AND TIGHTEN CAP ... 2" SPLIT CONTROL
78 | 11-10133-B | [10 empty] | 2011-05-03 | [5 empty] | SAN JOSE
78 | 11-10134-B |  |  | 75 | Distribution Main >60 PSIG and <20% SYMS |  | Body of Pipe |  |  | External Corrosion |  | 2011-05-04 | 2011-05-06 | Replace Partial Service |  | Steel-Other |  | SAN JOSE | REPLACED 3 11" OF 3/4" STEEL
78 | 11-10183-B |  |  | 0.75 | Branch Service |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2011-05-24 | 2011-05-24 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SAN MARTIN | REMOVED, REDOPED, AND REPLACED CAP ON 00.75" TEE; REMOVED, REDOPED, AND REPLACED CAP ON 00.75 SERVICE TEE. SOAP TEST OK
78 | 11-10401-B |  |  | 2 | Transmission >= 20% SMYS |  | Pressure Control Fittings |  |  | No/Deteriorated Pipe Dope |  | 2011-07-11 | 2011-07-13 | Other | INSTALL HP CAP RE-DOPE/TIGHTEN CAP | Steel-Other |  | SAN MARTIN | TIGHTEN COMPLETION PLUG- INSTALL HP CAP; TIGHTEN COMPLETION PLUG (2 TURNS) INSTALL HP 1400PSI CAP, REDOPE, TIGHTEN, PRESSURE WAS LOWERED FROM 300PSI TO 50PSI FOR REPAIR. ALSO USED FLUSH SUIT
78 | 11-11510-1 |  |  | 0.75 | Branch Service |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2011-04-20 | 2011-06-21 | Replace Main Valve < 2-inch |  | Steel-Other |  | GILROY | REPLACE VALVE AND CUT & THREAD RISER; REPLACED VALVE CUT & THREAD RISER SOAP TEST OK
78 | 11-20499-1 | [10 empty] | 2011-04-18 | [5 empty] | SAN JOSE
78 | 10-81028-1 | 0809-02 | 0.07 |  | Transmission >= 20% SMYS |  | Line Valve |  | B/D STICK |  |  | 2010-09-28 | 2011-03-02 | Mechanical Repair Fitting - Fitting |  | Steel-Other |  | MORGAN HILL | REMOVED VALVE; CLEANED THREADS & REPLACED VALVE
78 | 10-81028-1 | 0809-02 | 0.07 | [8 empty] | 2010-09-28 | [5 empty] | MORGAN HILL | INFO ONLY
78 | 10-81101-1 | 0813-13 | 0.9 | [8 empty] | 2010-09-25 | [5 empty] | SAN JOSE
78 | 10-81113-1 | 0809-01 | 199 | 4 |  |  | Line Valve |  |  | Other | PIPELINE UNDER WATER | 2010-09-27 | 2011-02-22 | Greased - Other | 3 VALVES | Steel-Other |  | MORGAN HILL | GREASE TWO VALVE IN MAN-HOLE (INLET & OUTLET); GREASED VALVES
78 | 10-81113-1 | 0809-01 | 199 | [8 empty] | 2010-09-27 | [5 empty] | MORGAN HILL | INFO ONLY
| 10-81118-1 | 0829-01 | 0.71 | 0.75 | Single Service |  | Other |  | MUELLER CAP | Unknown |  | 2010-09-27 | 2010-12-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MILPITAS | REDOPE & TIGHTENED MUELLER CAP IN H.P.R. SET SOAP TEST OK ; SEE SKETCH (ATTACHED SHEET)
78 | 10-81119-1 | 0810-01 | 0.1 | 0.75 | Transmission >= 20% SMYS |  | Body of Pipe | Fitting |  | No/Deteriorated Pipe Dope |  | 2010-09-28 | 2011-01-24 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | GILROY | REDOPED, TIGHTEN FITTING ON 3/4" H.P. UNION; TIGHTEN 3/4" H. PRESSURE UNION. PAINT HPR SET. INSTALLED 1/4" VENT. SOAP TESTED OK
78 | 10-81402-1 | 0804-03 | 186 | 2 | Distribution Main >60 PSIG and <20% SYMS |  | Other |  | STEEL TEE CAP | Other | TIGHTEN 2" STEEL CAP. | 2010-09-28 | 2011-03-31 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SANTA CLARA | TIGHTEN 2" STEEL CAP; TIGHTEN 2" STEEL CAP, FOR SIDE TAP CONNECTION
| 10-81511-1 | 0833-04 | 0.17 | 8 | Transmission |  | Fitting |  |  | Other | THREADS | 2010-10-10 | 2010-11-04 | Fill Weld - Weld |  | Steel/Wrought Iron |  | GILROY | WELDED OVER THREADS; SOAP TESTED
| 10-10651-1 |  |  | 8 | Transmission |  | Fitting |  |  | Other | THREADS | 2010-09-15 | 2010-10-04 | Fill Weld - Weld |  | Steel/Wrought Iron |  | GILROY | SOAP TESTED; SEE OTHER DOCUMENT
| 10-81534- | 0817-01 | 0.78 | 4 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-10 | 2011-01-04 | Skinner Clamp - Clamp |  | Steel-Other |  | SAN JOSE | INSTALLED 4" SKINNER CLAMP OVER PIT; INSTALLED 4" SKINNER CLAMP ON MAIN "SOAP TEST OK"
78 | 10-81688-1 | 300B | 47364 | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-11 | 2011-02-28 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | MORGAN HILL | 1ST 2ND STAGE MUPT. LEAKS HPR; FITTINGS REDOPED & TIGHTENED ON 1ST & 2ND STAGE HPR, SOAP TEST & CLOCK TEST GAS SERVICE. GC WELDER REPLACED INLET 3/4" HP PIPE
78 | 10-81688-1 | 300A | 47364 | [8 empty] | 2010-10-11 | [5 empty] | MORGAN HILL | INFO ONLY
78 | 10-81689-1 | 300B | 47397 | 0.75 | Transmission |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-11 | 2011-02-28 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | MORGAN HILL | 1ST & 2ND STAGE MULT. LEAKS; FITTINGS REDPED & TIGHTEN ON 1ST & 2ND STAGE HPR SOAP & CLOCK TEST SERVICE. REPLACED NEW FITTINGS
78 | 10-81689-1 | 300A | 47397 | [8 empty] | 2010-10-11 | [5 empty] | MORGAN HILL | INFO ONLY
| 10-82072-1 |  |  | 6 | Transmission |  | Valves |  |  | Other | DRIED OUT GREASE | 2010-10-14 | 2010-12-06 | Other | GREASED VALVE | Steel/Wrought Iron |  | SANTA CLARA | PER SCOTT FANNING- DUPLICATE WITH 80-10-81105 NO NEED TO ENTER; GREASED VALVE - SOAP TEST OK; SEE ATTACHED MAP
78 | 10-88020-1 | 0810-01 | 20 | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-21 | 2011-01-25 | Mechanical Repair Fitting - Fitting |  | Steel-Other |  | GILROY | REPLACED & TIGHTENED 3/4" FITTING; NEW 3/4" NIPPLE (FITTING) SOAP TEST PASSED
78 | 10-88021-1 | 0810-01Q | 6 | [8 empty] | 2010-10-21 | [5 empty] | GILROY
78 | 10-88023-1 | 0810-01 | [9 empty] | 2010-10-21 | [5 empty] | GILROY | NEED 3/4" PROBE HOT TANK SINGE REG. FISHER S402 SPRAGNE 250-MTR RD. 5176;
78 | 10-88022-1 | 0810-01 | 0.72 | [8 empty] | 2010-10-21 | [5 empty] | GILROY | NO LEAK FOUND
78 | 10-88023-1 | 0810-01 | [9 empty] | 2010-10-21 | [5 empty] | GILROY | NO GAS FOUND
78 | 10-88030-1 | 300A | 46238 | [8 empty] | 2010-10-21 | [5 empty] | GILROY | NO GAS FOUND
78 | 10-88041-1 | 300A |  | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-21 | 2011-02-28 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SAN MARTIN | PIN OFF CAP LEAKING; REDOPED AN TIGHTENED PIN OFF TEE CAP SOAP TEST GOOD
| 10-88043- | 300B | 47044 | 0.75 | Transmission >= 20% SMYS |  | Other |  | CAP | Construction Defect |  | 2010-10-21 | 2011-01-18 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SAN MARTIN | TOOK OFF CAP AND REDOPED CAP ON PIN OFF TEE
78 | 10-88044-1 | 300B | 47044 | 0.75 | Single Service |  | Fitting |  |  | Other | LOOSE FITTINGS | 2010-10-21 | 2011-02-16 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SAN MARTIN | TIGHTENED TWO UNIONS. REMOVED DOPE PIN OFF TEE CAP; FIXED 3 LEAKS IN HIGH TO HIGH BOX. 2 LEAKS ON UNION COLLARS AND 1 LEAK ON PIN OFF TEE, SOAP TEST OK
78 | 10-88044-1 | 300B | 470.44 | [8 empty] | 2010-10-21 | [5 empty] | SAN MARTIN | INFO ONLY
78 | 10-88046-1 | 300A | 46625 | 0.75 |  |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-10-22 | 2011-02-09 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | GILROY | REDOPED & TIGHTENED NIPPLE, SOAP TEST OK
78 | 10-88047-1 | 300B | 46423 | [8 empty] | 2010-10-22 | [5 empty] | GILROY | CALL CUSTOMER TO ARRANGE 857-5431
78 | 10-88047-1 | 300B | 46423 | 0.75 | Distribution Main >60 PSIG and <20% SYMS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-22 | 2011-04-19 | Other |  | Steel-Other |  | GILROY | REMOVED AND REDOPED 3/4" NIPPLE; REMOVED 3/4" NIPPLE ON INLET SIDE OF HIGH TO HIGH SET AND REDOPED.; SEE ATTACHED MAP
78 | 10-88048-1 | 300B | 46422 | 0.75 | Transmission >= 20% SMYS |  | Riser Valve Threads |  |  | Other |  | 2010-10-22 | 2011-03-11 | Replace Valve >= 2 inch | MECHANICAL REPAIR FITTING - FITTING | Steel-Other |  | GILROY | REDOPED & TIGHTENED INLET VALVEREPLACE & 3/4" PIPE HP. ; 2-2-11 REPAIRED TWO LEAKS. 2-3-11 WENT TO MAPPING TO GET AS BUILTS. 03-11-11 REPLACED 1/2" VALVE AND 3/4" FITTING.
78 | 10-88049-1 | 300A | 46747 | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-22 | 2011-02-02 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | GILROY | REDOPED/TIGHTENED FITTING- SOAP TEST OK; REPAIRED LEAK; REPAIRED LEAK, SOAP TEST OK
;
78 | 10-88160-1 | 300A | 46747 | 0.75 |  |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-22 | 2011-02-02 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | GILROY | REPAIRED LEAK; REDOPED/ TIGHTEN FITTING; REPAIRED LEAK SOAP TEST OK
98 | 10-88380-1 | 300A | 47047 | 0.75 | Single Service |  | Threads |  |  | No/Deteriorated Pipe Dope | DRIED OUT PIPE DOPE | 2010-10-21 | 2011-02-24 | Mechanical Repair Fitting - Fitting |  | Steel-Other |  | GILROY | HIGH TO HIGH SHUT IN LEAKS COULD BE REPAIRED- SOAP TEST OK
98 | 10-88384-1 | 0833-01 | 0.61 | 0.75 |  |  | Other |  | NO LEAK FOUNd | Other |  | 2010-10-22 | 2011-02-10 |  |  | Other |  | GILROY | NO LEAK FOUND O SERVICE TAP H-74; 3675 HWY 152 HAS PROPANE OF + OF MAP GIVIN PI#3683-66. THE SERVICE TAP FOUND H-74 HAS NO LEAK & "A" INSP. ALSO DONE AT SAME TIME PERATED GATE VALVE TOO. NO LEAK FOUND.
98 | 10-88421-1 | 300B | 46052 | 0.75 | Transmission >= 20% SMYS |  | Line Valve | Fitting |  | Other |  | 2010-10-22 | 2011-03-18 | Greased - Other | MECHANICAL REPAIR FITTING - FITTING, OTHER | Steel-Other |  | HOLLISTER | REPAIR MULTIPLE LEAKS; HOT TANK
98 | 10-88421-1 | 300B | 46052 | 0.75 | Transmission >= 20% SMYS |  | Line Valve | Fitting |  | Other |  | 2010-10-22 | 2011-03-18 | Greased - Other | MECHANICAL REPAIR FITTING - FITTING, OTHER | Steel-Other |  | HOLLISTER | REPAIR MUPLTIPLE LEAKS; HOT TANK
| 10-31105-1 | [10 empty] | 2010-09-11 | [5 empty] | MT. VIEW
| 10-31110-1 |  |  |  | Distribution Main |  | Valves |  |  | Other | GREASE DRIED OUT | 2010-09-12 | 2010-09-12 | Other | VALVE GREASED | Steel/Wrought Iron |  | MT. VIEW | GREASED VALVE. SOAP TEST OK
| 10-31113-1 |  |  | 6 | Distribution Main |  | Fitting |  |  | Other | LOOSE FITTING | 2010-09-12 | 2010-09-12 | Other | REG STATION | Steel/Wrought Iron |  | MT. VIEW
| 10-31113-1 |  |  | 6 | Distribution Main |  | Fitting |  |  | Other | LOOSE FITTING | 2010-09-12 | 2010-09-12 | Other | REG STATION | Steel/Wrought Iron |  | MT. VIEW | REPAIRED FITTING. SOAP TEST OK
| 10-81105- |  |  | 6 | Transmission |  | Valves |  |  | Other | DRIED OUT GREASE | 2010-09-26 | 2010-12-06 | Other | GREASED VALVE | Steel/Wrought Iron |  | SANTA CLARA | COMPLETED 12/6 ISSD TO DIV 80 BUT SHOULD HAVE BEEN 78 DUPLICATE WITH 78-10-82072-1; GREASED VALVE SOAP TEST OK; SEE ATTACHED MAP
| 09-31017-1 |  |  | 0.75 | Branch Service |  | Riser |  |  | Construction Defect |  | 2009-08-11 | 2009-09-23 | Skinner Clamp - Clamp | SOAP AND/OR TAPE | Steel/Wrought Iron |  | LOS GATOS | INSTALLED 3/4" SKINNER CLAMP; SOAP TESTED!
| 08-30255-1 | 8807-02 | [9 empty] | 2008-08-22 | 2008-12-24 |  |  |  |  | SUNNYVALE | DUPLICATE LK TO REPAIRED LK 08-305661; DUPLICATE LK TO REPAIRED OK 08-30566-1
| 09-30708- |  |  | 0.75 | Single Service |  | Riser |  |  | Construction Defect |  | 2009-10-21 | 2009-10-21 | Other | REPLACE RISER | PE2406 (Yellow or Orange) |  | SARATOGA | INSTALL NEW RISER AND 1' OF 1/2" PL
| 77-20277- |  |  | 1.25 | Other |  | Body of Pipe |  |  | Corrosion |  | 1977-03-24 | 1977-03-24 | Clamp |  | Steel/Wrought Iron |  | ELM | 1 1/4" HOUSE LINE BADLY PITTED AND LEAKING. INST. 4 BOLT LEAK CLAMP TO STOP LEAKAGE. NOTIFIED FATHER COSTA (MAINENANCE FOREMAN) FILLED OUT HAZARD NOTICE AND FATHER COSTA SIGNED. SCHOOL WILL HAVE TO REPAIR OR REPLACE LEAKING HOUSE LINE.; 1 1/4" HOUSE LINE LEAKAGE, BADLY PITTED INST. 4 BOLT TEMP LEAK CLAMPS
| 77-20158- |  |  | 0.25 | Other |  | Body of Pipe |  |  | Corrosion |  | 1977-02-24 | 1977-04-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN JOSE | TEST GAUGE NIPPLE ASSY, LEAKING ON ...ADANDONED EXISTING LINE... INST. NEW TEST GAUGE NIPPLE; 1/4" STL GAUGE NIPPLE LEAKING ON BEND REPLACED GAUGE NIPPLE.
| 77-20668- |  |  | 0.25 | Other |  | Fitting |  |  | Damage by outside Forces |  | 1977-08-24 | 1977-08-24 | Patch Welded |  | Steel/Wrought Iron |  | SAN JOSE | 1/4" GAUGE LINE BROKEN BY G.C. GAS CREW. ARC WELDED STEEL PIN IN PLACE OF GAUGE LINE. G.C. GAS TO RENEW OR REPLACE THIS INTERSECTION.
8 | 77-31778- |  |  | 0 | Other |  | Other |  |  | Other |  | 1977-12-07 | 1977-12-07 | Other |  | Steel/Wrought Iron |  | SANTA CLARA | FOUND 1/4" FT. HR. LEAK IN GAS HOUSE LINE TO 2652 HOMESTEAD RD., RUBINS BARBER SHOP. GAS SERVICEMAN L. FURT...ISSUE HAZARD NOTICE WITH 5 DAY FOLLOW UP SERVICE WAS NOT SHUT OFF AT THIS TIME. GAS MAIN NOT EXPOSED
8 | 77-31642- |  |  | 0 | Other |  | Other |  |  | Other |  | 1977-12-06 | 1977-12-06 | Other |  | Steel/Wrought Iron |  | SANTA CLARA | CHECKED HOSUE LINE TO 2649 & 2648 HOMESTEAD RD. 2644 OK. FOUND 3/4" FT. HR. LEAKAGE TO 2648, FIELDMAN JEWLER, IN THE HOUSE LINE, MTR WAS SEALED BY L. FURTADO, SERVICEMAN. HAZARD NOTICE ISSUED. MAIN NOT EXPOSED.
80 | 77-31417- |  |  |  | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1977-10-04 | 1977-10-27 | Patch Welded |  | Steel/Wrought Iron |  | SANTA CLARA | FOUND 6" DFM LEAKING ON BOTTOM OF PIPE. FOUND HEAVY PITTING IN THE SAME AREA. WELD 6" X 18" HALF SOUL FOR REPAIRS
80 | 77-60031- |  |  |  | Other |  | Other |  |  | Other |  | 1977-01-27 | 1977-01-27 | Other |  |  |  | SANTA CLARA | BAR TEST SERVICE...
| 77-40054- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-04-12 | 1977-04-12 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN JOSE | USED ...3/4"... INST. NEW SELF...SERV TEE
| 77-40055- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1977-04-12 | 1977-04-12 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN JOSE | ISNT. 53' OF SEAMLESS 3/4" STL SERVICE PIPE AND NEW SELF-PIN -OFF SERVICE TEE
| 77-40056- |  |  | 0.75 | Other |  | Drip |  |  | Damage by outside Forces |  | 1977-04-13 | 1977-04-13 | Other |  | Steel/Wrought Iron |  | SAN JOSE | CUT 3/4" DRIP BLOW OFF- ARC WELDED BONNET OVER 3/4" PIPE AND 3/4" DRESSER COUPLING 4-14-77
| 77-40027- |  |  | 0.5 | Other |  | Fitting |  |  | Damage by outside Forces |  | 1977-02-18 | 1977-02-18 | Other |  | Steel/Wrought Iron |  | SAN JOSE | CAR BUMBER STRUCK GAS METER, BREAKING OUTLET METER SPUD. NO DAMAGE TO RISER. BAR TESTED ENTIRE SERVICE USING J.W. ON 4% SEAL NO LEAKAGE. SERVICEMAN REPLACED METER & MADE NEW METER SET. LOW PRESSURE SYSTEM. METER WAS LOCKED BY SERVICEMAN & C.G.I.ED; MAIN WAS NOT EXPOSED
80 | 78-20355- |  |  |  | Other |  | Body of Pipe |  |  | Corrosion |  | 1978-04-11 | 1978-04-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN JOSE | 3/4" DRIP LINE LEAKING IN 4 DIFFERENT PLACES. ABANDON DRIP LINE AT MAIN. INST. NEW 3/4" DRIP LINE OVER THE MAIN. INST. FRAME AND COVER; SAND BACK FILL
80 | 78-20227- |  |  |  | Other |  | Body of Pipe |  |  | Corrosion |  | 1978-03-21 | 1978-03-21 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN JOSE | 2" HOUSE LINE GOING TO DEL MONTE FOODS LEAKING. CUST-MADE REPAIRS BY REPLACING SECTION OF PIPE. BAR TEST AREA ALL CLEAR.
| 79-20652- |  |  | 0.75 | Other |  | Meter |  |  | Construction Defect |  | 1979-10-05 | 1979-10-05 | Other |  | Steel/Wrought Iron |  |  | FOUND ... COULD...OR NEAR RISER UNDER GREASED USING J.W. ON 4% SCALE
8 | 79-30365- |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1979-04-05 | 1979-04-09 | Other |  | Steel/Wrought Iron |  | SAN JOSE | GREASED LEAKING SERVICE VALVE & J.W. SERVICE. NO INDIE FOUND 3/4" NORD VALVE.
8 | 79-30350- |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1979-03-26 | 1979-04-09 | Other |  | Steel/Wrought Iron |  | SAN JOSE | REPAIRED LEAKING FLANGE ON 6" VALVE BY TIGHTENING BOTH AND GREASING VALVE. NO PAVING CUTS
| 79-30000- |  |  |  | Other | HOUSELINE | Other |  | HOUSELINE LEAKING | Corrosion |  |  |  | Other | NO REPAIRS MADE GAVE REG. DEPT. | Steel/Wrought Iron |  | SANTA CLARA | FOUND HOUSELINE FOR POOL HEATER LEAKING TO CAPRI HOTEL. GAVE TO REGULATION DEPT. TO HAVE ...OVER SERV...MADE.
8 |  |  |  | 1.25 | Service |  | Other |  |  | Other |  | 1979-10-13 | 1979-10-13 | Replace Pipe and/or Service |  | Plastic
| 79-40165- |  |  | 0.5 | [7 empty] | 1979-10-13 | 1979-10-13 |  |  | Other Plastic |  | SAN JOSE | CUST. WAS REMOVING SOD FROM YARD WITH BACK HOE AND SNAGGED GAS SERVICE. REPAIRS MADE BY REPLACING 18' AND LOWERING 1/2" PL. AND NEW PIN...RISER
8 | 80-20503-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-04-10 | 1981-05-28 | Other |  | Other |  | SAN JOSE | ...NO METER...CUSTOMER STATED ...P.G.&E. REAPIRED LEAK IN ...80' REPAIRED HUMP IN LOWER SEC. ..ON TAP LEAK IN LOWER...; GAS MAIN NOT EXPOSED
8 | 80-20239-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-04-16 | 1981-05-21 | Other |  | Other |  | SAN JOSE | CHECKED 2K2 WITH J.W. NO INDIE. FOUND. 2 RECENT PATCHES IN STREET IN MAIN AREA. INDICATING THAT THIS WAS REPAIRED; MAIN NOT EXPOSED
| 80-20389- |  |  | 0.25 | Other |  | Fitting |  |  | Construction Defect |  | 1980-04-08 | 1980-06-04 | Other |  | Steel/Wrought Iron |  | SAN JOSE | ...FAMERS ON FITTINGS INSIDE REG. PIT. NEXT TO FIRE HYDRANT. MARKED BOTH IN YELLOW AND TURNED OVER TO REG. DEPT.
8 | 80-40127- |  |  | 0 | Other |  | Other |  |  | Other |  | 1980-08-31 | 1980-08-31 | Other |  | Steel/Wrought Iron |  | SAN JOSE | CST. REPAIRED AS ORDER ... OVER GAS SERVICE...ALSO J.W. RECOMMEDED THAT...; GAS MAIN OR GAS SERVICE NOT EXPOSED. 9-2-80RECHECKED WITH LFLAME PACK NO GAS FOUND.
| 80-40023- |  |  | 0.75 | Other | MANIFOLD | Fitting |  |  | Damage by outside Forces |  | 1980-02-19 | 1980-02-19 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN JOSE
8 | 81-40178- |  |  |  | Other |  | Other Welds |  |  | Damage by outside Forces |  | 1981-09-19 | 1981-09-19 | Patch Welded |  | Steel/Wrought Iron |  | ; SAN JOSE | 14 METER MANIFOLD STRUCK BY CAR. REPAIRED 3/4" STL NIPPLE BY RE-WELDING NEW NIPPLE FORE METER
8 | 80-30297- |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1981-03-13 | 1981-07-02 | Clamp |  | Steel/Wrought Iron |  | SAN JOSEREPAIRED LEAK ON ...STEEL PIPE MAIN WTH 2" X 3 1/2" SKINNER CLAMP. NO PAVING CUTS; MAIN IN EXCELENT CONDITION EXCEPT 1 LARGE PIT, REPAIRED BY SKINNER CLAMP
| 84-40138- |  |  | 2 | [7 empty] | 1984-07-24 |  |  |  | Steel-Other |  |  | MADE SAFE SAME DAY 7-24-84 DOWN GREADED TO 2 7-25-84 PER BERRY 2-10-84
11 | 85-40040- |  |  | 0.75 | Service |  | Valves |  |  | Damage by outside Forces |  | 1985-02-04 | 1985-02-04 | Other |  | Steel/Wrought Iron |  | SAN JOSE | ABANDON 3/4" F.P. ST. GAS ...AT MAIN
11 | 85-20541- |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1986-02-06 | 1986-02-07 | Clamp |  | Steel/Wrought Iron |  | SARATOGA | INSTALL 6" SKINNER REPAIR CLAMP TO REPAIR CORROSION LEAK
| 85-20512- |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1985-09-19 | 1985-12-20 | Clamp |  | Steel/Wrought Iron |  | SAN JOSE
| 83-40018- |  |  | 0.75 | Other | P | Valves |  |  | Construction Defect |  | 1983-02-03 | 1983-02-03 | Other |  | Steel/Wrought Iron |  | MILPITAS | TIGHTENED 3/4" STOPCOCK ON NEW RISER
| 83-20308- |  |  | 6 | Distribution Feeder Main |  |  |  |  | Construction Defect |  | 1983-09-28 |  | Weld Over Sleeve or Can |  | Steel-Other |  | SAN JOSE
78 | 86-20178- |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1986-05-19 | 1986-05-19 | Other |  | Steel/Wrought Iron |  | SANTA CLARA | REGULATION DEPARTMENT GREASED GAS VALVES AT LOCATION FOR REPAIRS
11 | 86-20003- |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1986-01-13 | 1986-01-17 | Patch Welded |  | Steel/Wrought Iron |  | SAN JOSE | WELD 16" LONG HALF SOLE 10" K.P. GAS MAIN TO REPAIR CORROSION LEAK
78 | 86-40252- |  |  | 20 | Transmission |  | Body of Pipe |  |  | Digin |  | 1986-12-03 | 1986-12-03 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SAN JOSE | T-L-100 BELONS TO PIPE LINE OPERATIONS. DIVISION GAS TO RESPOND OVER TO RE...OF STRUCK GAS LINE, BLOWING P.LO. MADE ALL REPAIRS; P.LO. INSTALLED 20" X 18" X.500 SPLIT WEDDING BAND ON MAIN.
78 | 86-40239- |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1980-11-12 | 1986-11-12 | Other |  | Steel/Wrought Iron |  | SAN JOSE | 10/100% IN VALVE F/C. NO ROADS 4% SCALE NEAR BLDGS...M.H. ...BYERS. E.T.C. DOWN...#2
78 | 86-40210- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Digin |  | 1986-10-06 | 1986-10-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | MILPITAS
78 | 86-40197- |  |  | 2 | M |  | Other |  |  | Damage by outside Forces |  | 1986-09-22 | 1986-09-22 | Other |  | Steel/Wrought Iron |  | SAN JOSE
78 | 86-40023- |  |  | 0 | Other |  | Other |  |  | Other |  | 1986-01-31 | 1986-02-03 | Other |  | Other |  |  | NO GAS FOUND BY ...LAME PACK...; NO GAS FOUND 2Y J.W. OR FLAME PACK
| 87-40034- |  |  | 26 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-03-12 | 1987-04-20 | Other |  | Steel/Wrought Iron |  | SANTA CLARA | FLAME PACK BY M. ...VAVLE LEAKING TURNED IN TO REG.
78 | 89-20566-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1989-09-14 | 1989-09-18 | Replace Pipe |  | Steel/Wrought Iron |  | S.C. | INSTALL 16" FULL CIRCLE CLAMP ON WRINKLE BEND
78 | 90-20359-1 |  |  | 3 | M |  | Body of Pipe |  |  | Cast Iron Fracture |  | 1990-04-20 | 1990-08-24 | Clamp |  | Cast/Ductile Iron |  | SAN JSOE | FOUND CRACK ON 3" MAIN. 2/3 CIRCUMFRANCE OF PIPE 5" FROM LEAKING BELL JOINT. INSTALLED ALH BJ REPAIR KIT & FULL CIRCLE LEAK CLAMP
78 | 92-10208-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1992-09-21 | 1992-10-08 | Patch Welded |  | Steel/Wrought Iron |  | SAN JOSE | ARC WELDED AND PATCH OVER... PIT
| 92-10208-1 | [11 empty] | 1992-10-08
8 |  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ABANDONED 3/4" GAS SERVICE
28 |  |  |  | 8 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | SAN JOSE | ABANDON 3/4" GAS SERVICE AT LOCATION
78 | 91-10202-1 |  |  | 16 | Transmission |  | Valves |  |  | Other |  | 1991-09-12 | 1994-06-29 | Other |  | Steel/Wrought Iron |  | SJ | NO VALVE ON 16" FEEDER; HAD REGULATION PACK VALVE
78 | 91-10180-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1991-09-12 | 1991-10-04 | Other |  | Steel/Wrought Iron |  | MH | GREASED VALVE STOPPED LEAK
78 | 91-10180-1 |  |  | 4 | Distribution Feeder Main |  | Valves |  |  | Other |  |  | 1991-10-04 | Other |  | Steel/Wrought Iron |  | MH | GREASED VALVE
78 | 91-10122-1 |  |  | 2 | M |  | Valves |  |  | Other |  | 1991-05-10 | 1991-07-01 | Other |  | Steel/Wrought Iron |  | SJ | GREASE VALVE FOR REPAIRS.
78 | 91-10122-1 |  |  | 2 | Distribution Main |  | Valves |  |  | Other |  |  | 1991-07-31 | Other |  | Steel/Wrought Iron |  | SJ | GREASED VALVE FOR REPAIR
78 | 91-10119-1 |  |  | 0.75 | Service | TRANSMISSION | Regulator |  |  | Other |  | 1991-05-09 | 1991-09-24 | Replace Pipe |  | Steel/Wrought Iron |  | SAN JOSE | TURNED OVER TO GAS REGULATION FOR REPAIRS
78 | 91-10119-1 | [16 empty] | SJ
78 | 91-10118-1 |  |  |  | Transmission |  | Valves |  |  | Other |  | 1991-09-24 | 1991-09-24 | Other |  | Steel/Wrought Iron |  | SAN JOSE | TURNED OVER TO PIPE LINE OPERATION FOR REPAIRS
78 | 91-10118-1 | [16 empty] | SJ
78 | 75-00024-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1975-07-01 | 1975-07-22 | Clamp |  | Steel/Wrought Iron |  | MORGAN HILL | 32% VENTING FROM MANHOLE
78 | 76-15016-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1975-06-03 | 1978-09-11 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | GILROY | 100 PPM IN PATCH IN FRONT OF 7630. 1% IN WATER BOX IN FRONT OF 7600. 1% TO 1% IN PATCHES IN STREET NO GAS OVER SERVICE NEAR HOUSES.
78 | 76-15000-1 |  |  | 20 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1976-03-22 | 1976-03-23 | Patch Welded |  | Steel/Wrought Iron |  | SAN MARTIN
| 77-10242- |  |  | 2 | Other |  | Body of Pipe |  |  | Corrosion |  | 1977-09-26 | 1977-09-26 | Clamp |  | Steel/Wrought Iron |  | SAN JOSE | HOUSELINE; MADE TEMPORARY REPAIRS WITH 2" CLAMP; FOUND LEAK ON 2" HOUSELINE- MADE TEMPORARY REPAIRS AND TOLD IT WAS THEIR RESPONSIBILITY TO REPAIR LINE-
| 78-70017-1 |  |  |  | Service |  | Meter |  |  | Damage by outside Forces |  | 1978-11-09 | 1978-11-09 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | MORGAN HILL | METER WAS STRUCK AT NIGHT APPROX 12:00 AM 11/9/78. SHUT OFF 2:45 BY KLM___
8 | 78-70013-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-08-14 | 1978-08-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | GILROY | REPAIRS MADE BY CUTTING OUT 5FT SECTION REPLACING WITH 250-B SEAMLESS 6" PIPE AND 2-375 BANDS
80 | 78-50181- |  |  |  | Other |  | Fitting |  |  | Damage by outside Forces |  | 1978-11-20 | 1978-11-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN JOSE | STRUCK METER AND MANIFOLD 3/4" NIPPLE BROKE OFF INSIDE STOP COCK. REPLACE STOP COCK FOR REPAIRS. SOAP TEST OK.
80 | 78-50115- |  |  |  | Other |  | Fitting |  |  | Other |  | 1978-07-29 | 1978-07-29 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN JOSE | FOUND PLUG ON OIL DRIP LINE BLOWING IN REG PIT CALLED REGULATION TO MAKE REPAIRS
78 | 78-15031-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-11-14 |  |  |  | Steel/Wrought Iron |  | GILROY | WELDED 6"X4" HALF SOLE & GASKET OVER PIT ON 4"; OVER SERVICE TEE & MAIN
| 78-20051- |  |  | 0.75 | Other | HOUSE LINE | Other |  |  | Other |  | 1978-01-30 | 1978-01-31 | Other |  | Steel/Wrought Iron |  | S.J. | HOUSELINE; ABANDONED 3/4" HOUSELINE CAUSING LEAKAGE. REMOVED BROKEN FITTING & PLUGED & CAPED ENDS OF PIPE; A. SUPPOSEDLY ABANDONED HOUSELINE WAS CAUSING ODOR AT POINT WHERE LINE HAD BEEN BROKEN. CAPED & PLUGED BOTH ENDS OF THIS HOUSE LINE
80 | 78-10181-2 |  |  |  | Other | [6 empty] | 1978-08-01 | 1978-08-02 |  |  | Steel/Wrought Iron |  | SAN JOSE | HOUSE LINE LEAKING, DID NOT STAND UP TO A CLOCK TEST. REGULATION LEFT THE SCHOOL A HAZARD CARD BAR TEST OVER 1 1/4" P SER OK
| 78-10053- |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1978-08-09 | 1978-03-09 | Patch Welded |  | Steel/Wrought Iron |  |  | 10" MAIN HAD BEEN STRUCK BY AUTO WHEN PT&T PALE WAS INSTALLED - REPAIRED LEAK WITH A 4"X8" HALF SALE TYPE PATCH WELD-
80 | 79-20454- |  |  |  | Other |  | Body of Pipe |  |  | Corrosion |  | 1979-06-27 | 1979-06-28 | Other |  | Steel/Wrought Iron |  | SAN JOSE | FOUND 1" HOUSELINE LEAKING CAUSE OF LEAK - CONCRETE INST. TEMP. 2 BOLT LEAK CLAMP. TURN LEAK OVER TO MAINTAINCE CREW AT I.B.M. HOUSE LINE NOT IN USE ABANDON AT REG SET.
78 | 80-70005- |  |  | 0.75 | Other |  | Fitting |  |  | Damage by outside Forces |  | 1980-04-11 | 1980-04-11 | Replace Pipe and/or Service |  | Plastic |  | GILROY | METER LEAK
| 80-40152- |  |  |  | Other |  | Meter |  |  | Material Failure |  | 1980-10-29 | 1980-10-30 | Other |  |  |  | C/S STORY | BAR TESTED OVER SERVICE & MAIN USING J.W. ON 4% SCALE. NO INDICATION OF LEAKAGE SOAP TESTED METER & METER SET REPAIRED FOAMER ON METER 10-30-80; FOAMER ON TOP METER. REPAIRED SAME
8 | 81-50089- |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1981-08-10 | 1981-08-13 | Patch Welded |  | Steel-Other |  | SAN JOSE | MADE PERM REPAIR BY WELDING A 10"X10" PATCH ON 10 MAIN
8 | 81-50071- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1981-07-07 | 1981-07-10 | Patch Welded |  | Steel/Wrought Iron |  | SAN JOSE | ARC WELDED 3" X 4' 2" PATCH ON 2" HP/STL
| 81-50027- |  |  |  | Distribution Feeder Main |  | Fitting |  |  | Material Failure |  | 1981-03-25 | 1981-03-25 |  |  | Steel/Wrought Iron |  | MORGAN HILL | FOUND HI TO HI SET LEAKING ALSO A 3/4" VALVE GAVE LEAK TO REGULATIONS SO THEY CAN MAKE PERM REPAIRS
| 81-10034- |  |  | 4 | Distribution Feeder Main |  | Other Welds |  |  | Material Failure |  | 1981-06-08 |  | Patch Welded |  |  |  | SAN JOSE | LEAK AT BOTH SAVER VALVE NIPPLES WELDED UP EACH ONE
8 | 83-10104- |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1983-05-27 | 1983-05-31 | Other |  |  |  | SAN JOSE
8 | 83-10000- |  |  | 1.25 | Other |  | Body of Pipe |  |  | Construction Defect |  | 1982-01-06 | 1982-01-13 | Other |  | Steel/Wrought Iron |  | SAN JOSE
8 | 82-10132- |  |  | 2 | Other |  | Other |  |  | Other |  | 1982-04-26 | 1982-04-26 |  |  | Steel/Wrought Iron |  | MORGAN HILL | WHILE DIGGING FOR 4" MAIN TO INSTALL A VALVE WE FOUND THE CAP ON THE TEE LEAKING BAD; RE-DOPED & RE-TIGHTENED CAP
78 | 88-10183-1 | [10 empty] | 1988-09-01 | [5 empty] | SAN JOSE
78 | 88-10146-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1988-02-26 | 1989-02-16 | Patch Welded |  | Steel/Wrought Iron |  | SAN JOSE | FOUND LEAK ON 10" FEEDER; ARC WELDED A PATCH OVER THE LEAK.
78 | 88-10146-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1988-02-26 | 1989-02-16 | Patch Welded |  | Steel/Wrought Iron |  | SAN JOSE | FOUND LEAK ON 10" FEEDER MAIN. ARC WELDED A PATCHOVER THE LEAK.
78 | 88-15036-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1988-09-06 | 1988-09-21 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | GILROY | LEAK ON MAIN; WELD 8" HALF SOLE
78 | 88-15035-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1988-09-06 | 1988-09-20 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | GILROY | LEAK ON MAIN; WELD 6" HALF SOLE & 2-2" PATCHS
78 | 89-10316-1 | [10 empty] | 1989-09-21 | [5 empty] | G
78 | 89-10315-1 | [10 empty] | 1989-09-21 | [5 empty] | G
78 | 89-10314-1 | [10 empty] | 1989-09-21 | [5 empty] | G
78 | 89-10313-1 | [10 empty] | 1989-09-21 | [5 empty] | G
78 | 89-10312-1 | [10 empty] | 1989-09-21 | [5 empty] | G
78 | 89-10311-1 | [10 empty] | 1989-09-21 | [5 empty] | G
78 | 89-10310-1 | [10 empty] | 1989-09-21 | [5 empty] | G
78 | 89-10309-1 | [10 empty] | 1989-09-21 | [5 empty] | G
78 | 89-10247-1 |  |  | 0 | Other |  | Other |  |  | Other |  | 1989-06-21 | 1989-06-02 | Other |  | Other |  | SAN JOSE | HOUSE LINE LEAK; HOUSE LINE LEAKING; SHUT OFF VALVE NOTIFIED CUSTOMER & SERVICE DEPT
78 | 90-10129-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1990-10-17 | 1990-11-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SJ | TIGHTEN ALL FLANGE BOLTS 1/2 WERE LOOSE 2 WERE ONLY FINGER TIGHT. OK NOW
78 | 90-10129-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  |  | 1990-11-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SJ | RETIGHTENED ALL FLANGE BOLTS ON THE VALVE
78 | 90-10128-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1990-10-08 | 1990-10-31 | Other |  | Steel/Wrought Iron |  | SJ | LEAK ON 3/8" COPPER LINE TO TELEMETER; TELEMETER NO LONGER IN USE. ABANDONED 3/4" SERVICE AT MAIN
78 | 90-10128-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  |  | 1990-10-31 | Other |  | Steel/Wrought Iron |  | SJ | ABANDONED 3/4" SERVICE (TELEMETER NO LONGER IN USE)
78 | 90-10123-1 |  |  | 0.75 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1990-09-21 | 1990-11-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | G | SENT TO GAS REGULATIONS 11-8-90. OIL CHECK PIPE NEEDS TO BE TIGHTENED OR REPLACED.; TIGHTENED VALVE
78 | 90-10123-1 |  |  | 0.75 | Distribution Feeder Main |  | Valves |  |  | Other |  |  | 1990-11-16 | Tighten Cap or Bolt |  |  |  | G | RETIGHTENED VALVE
78 | 90-10121-1 | [10 empty] | 1990-09-17 | [5 empty] | SJ | 2-11-91 TOOK 4 READS WITH CHROMOGRAPH NO GAS FOUND. DELETE LEAK
78 | 90-10121-1 | [16 empty] | SJ
78 | 89-50120-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1989-08-25 | 1989-08-25 | Other |  | Steel/Wrought Iron |  | GILROY | CUT THREADS & WELD 3" - 1/4" NIPPLE
78 | 91-50119-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 1991-12-23 | 1991-12-30 | Replace Pipe |  | Steel/Wrought Iron |  | GILROY | REPLACE VALVE REGULATION ASST.
78 | 91-50119-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  |  | 1991-12-30 | Replace Pipe |  | Steel/Wrought Iron |  | G | REPLACED THE VALVE ON THE STOPCOCK
78 | 91-50015-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1991-02-19 | 1991-02-19 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | GILROY | BODY OF PIPE; WELDED SLEEVE AROUND MAIN AT LEAK POINT. XRAY & SOAP TESTED WELDS; ARC WELDED 6"X10" FULL CIRCLE SLEEVE; WELDS WERE ALSO XRAY TESTED BY GEN. CONST. XRAY TESTER.
78 | 91-50015-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  |  | 1991-02-19 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | G
78 | 91-50005-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | External Corrosion |  | 1991-01-22 | 1991-01-24 | Replace Pipe |  | Steel/Wrought Iron |  | M.H. | REPLACED 3/4" NIPPLE ON HI TO HI SET. SET TO BE REMOVED WEEK OF 1-28-91
78 | 91-50005-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  |  | 1991-01-24 | Replace Pipe |  | Steel/Wrought Iron |  | G | REPLACED 3/4" NIPPLE ON HI TO HI SET (SET TO BE REMOVED)
78 | 93-10136-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | External Corrosion |  | 1993-04-07 | 1994-06-06 | Patch Welded |  | Steel/Wrought Iron |  | SAN JOSE | LEAK ON BOTTOM OF 10" MAIN; ARC WELDED A PATCH OVER THE LEAK.
78 | 93-10136-1 | [10 empty] | 1993-04-07 | [5 empty] | SAN JOSE
78 | 93-10112-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | External Corrosion |  | 1993-03-12 | 1993-03-29 | Patch Welded |  | Steel/Wrought Iron |  | S.J. | LEAK ON BOTTOM OF 10" FEEDER MAIN. ARC WELDED A PATCH OVER THE LEAK.
78 | 93-10084-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1993-02-24 | 1993-06-22 | Patch Welded |  | Steel/Wrought Iron |  | SAN JOSE | ON SIDE OF 8" FEEDER MAIN. ARC WELDED A PATCH OVER THE LEAK.
78 | 94-50117-1 |  |  | 0.75 | Distribution Feeder Main |  | Riser |  |  | Damage by outside Forces |  | 1994-04-09 | 1994-04-09 | Other |  | Steel/Wrought Iron |  | GILROY | STRUCK HI-HI SET; STRAIGHTEN BOTH DISTRIBUTION RISER AND DISTRIBUTION FEEDER RISER REBUILT SET. INT PROT POST
78 | 94-40290-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1994-09-28 | 1994-09-28 | Other |  | Steel/Wrought Iron |  | S CLARA | FOUND LEAK STEM ON F.P. VALVE # 51F3B. LEAK ELIMINATED BY GREASING OF VALVE BY M&C DEPT
78 | 94-40290-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1994-09-28 | 1994-09-28 | Other |  | Steel/Wrought Iron |  | S CLARA | FOUND LEAKING STEM ON F.P. VALVE #51F3B. LEAK ELIMINATED BY GREASING OF VALVE BY M&c DEPT
78 | 94-40287-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | External Corrosion |  | 1994-09-27 | 1995-10-04 | Patch Welded |  | Steel/Wrought Iron |  | S. CL. | ARC WELDED 12" LONG HALF SOLE PATCH OVER LEAKING CORROSION PIT IN BOTTOM SIDE OF 6" F.P. GAS MAIN
78 | 94-40287-1 | [10 empty] | 1994-09-27 | 1994-09-27 |  |  |  |  | S. CL. | IN AREA UNABLE TO DEFINE LEAK - RECHECK IN 2 MONTHS
78 | 94-40287-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | External Corrosion |  | 1994-09-27 | 1995-10-04 | Patch Welded |  | Steel/Wrought Iron |  | S. CL. | ARC WELDED 12" LONG HALF SOLE PATCH OVER LEAKING CORROSION PIT IN BOTTOM SIDE OF 6" F.P. GAS MAIN
78 | 94-40221-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1994-07-12 |  | Replace Pipe |  | TR 418 |  | SAN JOSE
77 | 94-40213-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1994-06-15 | 1994-06-16 | Patch Welded |  | Steel/Wrought Iron |  | SANTA CLARA | LEAK OVER TRANS MAIN; WELD A 6X6 PATCH ON MAIN.
78 | 95-40173-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | External Corrosion |  | 1995-05-04 | 1995-06-28 | Patch Welded |  | Steel/Wrought Iron |  | S JOSE | 195 F F.P. LOWERED TO 60# ARC WELDED 10" LONG HALF SOLE PATCH .375 WALL THICK OVER CORROSION LEAK ON 8" F.P. MAIN; INSTALLED 10" LONG FULL CIRCLE LEAK CLAMP OVER CORROSION LEAK ON BOTTOM SIDE OF 8" T.P. MAIN FOR TEMP. REPAIRS
78 | 95-40019-1 |  |  | 36 | Transmission |  | Fitting |  |  | Construction Defect |  | 1995-01-20 | 1995-03-06 | Other |  | Steel/Wrought Iron |  | MILPITAS | REMOVED LEAKING UNION ON 1/4" VALVE BLEED LINE ON 3" BELL VALVE
78 | 95-50200-1 |  |  | 3 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1995-12-27 | 1995-12-27 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SAN JOSE | FOUND CAP ON 1" FEEDER PRESURE TEE LEAKING. TEE WELDED ON 4" MAIN OUTSIDE OF PRIMARY PIT.; REDOPE AND TIGHTEN CAP
78 | 95-50194-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | External Corrosion |  | 1995-12-08 | 1995-12-08 | Patch Welded |  | Steel/Wrought Iron |  | SAN JOSE | FOUND LEAK ON BOTTOM OF 10" STEEL MAIN.; WELD 12"12" PATCH.
78 | 11-10127-1 | [10 empty] | 2011-04-19 | [5 empty] | MORGAN HILL
78 | 11-10112-1 | [10 empty] | 2011-04-19 | [5 empty] | GILROY
78 | 11-10113-1 | [10 empty] | 2011-04-19 | [5 empty] | GILROY
78 | 11-10121-1 | [10 empty] | 2011-04-19 | [5 empty] | SAN MARTIN
78 | 11-10123-1 | [10 empty] | 2011-04-19 | [5 empty] | SAN MARTIN
78 | 11-10125-1 | [10 empty] | 2011-04-19 | [5 empty] | SAN MARTIN
| 07-10075-1 |  |  | 2 | Distribution Main |  | Plastic Tee Cap |  |  | Construction Defect |  | 2007-05-23 | 2007-07-13 | Other | REPLACED TEE CAP. | TR 418 |  | SAN JOSE | REPLACED PLASTIC CAP ON TEE. (TEE USED TO BYPASS MG. DURING PREVIOUS REPAIR); REPLACED PLASTIC TEE CAP
| 07-10198-1 |  |  | 6 | Transmission |  | Valves |  |  | Internal Corrosion |  | 2007-10-27 | 2007-11-27 | Replace Valve >= 2 inch |  | Steel/Wrought Iron |  | SAN JOSE | REPLACED VALVE
78 | 10-81101-1 | 0813-13 | 0.9 | [8 empty] | 2010-09-25 | [5 empty] | SAN JOSE
78 | 11-10149-1 | [10 empty] | 2011-05-09 | [5 empty] | GILROY
78 | 11-10160-1 | [10 empty] | 2011-05-10 | [5 empty] | GILROY
78 | 11-10163-1 | [10 empty] | 2011-05-11 | [5 empty] | MORGAN HILLS
78 | 11-10164-1 | [10 empty] | 2011-05-11 | [5 empty] | GILROY
98 | 10-82003-1 | 100 | 13843 | [8 empty] | 2010-09-18 | [5 empty] | SAN JOSE
| 08-20069-1 | LAFAYATTE DFM |  | 6 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2008-02-06 | 2009-07-28 | Replace TP Main |  | Steel/Wrought Iron |  | SANTA CLARA | STEEL 6" DFM BY GC GAS WELDED ON 6" CONTROL, CLOSED VALVE INSTALLED 41" OF NEW 6"
| 08-20203-1 |  |  | 6 | Distribution Main |  | Valves |  |  | Other | OLD GREASE | 2008-06-10 | 2008-06-10 | Other | GREASED VALVE | Steel/Wrought Iron |  | SANTA CLARA | GREASED LEAKING VALVE (FBG3) SOAP TEST
| 08-20158-1 |  |  | 3 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2008-05-10 | 2008-07-11 | Replace Dist Main < 100 ft |  | Steel/Wrought Iron |  | SAN JOSE | C/OUT VALVE & ISOLATING FITTING EAST 837; C/OUT V-17 & ISLATION FITTING. REPLACED ISOLATION FITTING W/NEW, INSTALLED 2-32;B ANODES & A FRAME AND COVER.
| 08-20158-1 | [10 empty] | 2008-05-10 | [5 empty] | SAN JOSE
| 04-30076- |  |  | 2 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2004-05-10 | 2010-12-09 | Skinner Clamp - Clamp |  | Steel-Other |  | CAMPBELL | SMALL PIT ON BOTTOM OF MAIN, USED TWO BOLT SKINNER CLAMP.; SOAP TEST SKINNER CLAMP
| 04-30076-1 | [10 empty] | 2004-05-10 | [5 empty] | CAMPBELL | INFO ONLY
| 06-30653-1 | 8803-01 |  | 0.75 | Transmission |  | Body of Pipe |  |  |  |  | 2006-10-20 | 2006-10-20 | Other | 3/4" STEEL CAP | Steel/Wrought Iron |  | MTN. VIEW | 3/4" VALVE SCREWED ON 3/4" NIPPLE WHICH WAS WELDED TO END OF CAP ON 6" NASA SERVICE LINE. NIPPLE BROKE @ SCREWED CONNECTION TO VALVE
| 07-30054-1 | 8807-01 | 5.06 | 0.25 | Transmission |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2007-05-10 | 2007-05-11 |  |  |  |  | SUNNYVALE | REPLACED 2" NIPPLE WELDED DIRECTLY TO 16" LINE; GAUGE TAP LOCATED ON TOP OF 16" DFM JUST S/O MLV 5.05 WAS ATMOSPHERICALLY CORRODED
| 07-30179-1 | 132A | 0 | 0.75 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2007-11-01 | 2007-11-15 | Replace TP Main |  | Steel/Wrought Iron |  | MTN. VIEW | NOTE: PLACED UNDER CP ON 11/23 BY WAYNE SHINODA. REPLACE 3' PIPE; BOX CONTAINS 4 VALVES 3/4 ONE ON EACH DIFFERENTIAL LINE ONE PRESSURE SENSE ON EACH SIDE OF THE BURIED FLANGED ON LINE. NOTE: THE FLANGED ON LINE IS BURIED UNDER THE BOX. 570 W. PARR CAMPBELL POSSIBLE WATER CONTROL. LID COVER 27 X 39 CONCRETE 32 X 44 ONE 6" EXTESION PRESENT...12"
| 08-30007-1 | TULLY |  | 6 | Transmission |  | Valves |  |  |  |  | 2008-01-28 | 2008-04-01 | Other | GREASED VALVE | Steel/Wrought Iron |  | CAMPBELL | GREASED VALVE; GREASED VALVE. NOTE SOME INFORMATION ABOVE NOR KNOWN AS THE PIPE WAS NOT EXPOSED. "FAKE" VALVES WERE ENTERED TO ALLOW IGIS ENTRY DMK 4/3/2008
| 08-30566-1 | 8807-02 |  | 10 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2008-04-30 | 2008-08-23 | Other | INSTALLED STEEL CAP FROM A PLIDCO 2000# PSIG PINHOLE CLAMP | Steel/Wrought Iron |  | SUNNYVALE | A CAP RATED FOR 2000 PSI FROM A 10" PLIDCO PINHOLE CLAMP WAS WELDED DIRECTLY TO THE PIPE TO COVER TWO LEAKING CORROSION PITS LOCATED 2.5" APART. THE WELD WAS TESTED WITH MAGNETIC PARTICELS
| 09-30201-1 |  |  | 6 | Gathering |  | Valves |  |  | Other | GREASE | 2009-06-09 | 2009-06-10 | Other | GREASED | Steel/Wrought Iron |  | PALO ALTO | FOAMS ON REG. SET.
| 09-30670-1 | BFP-13 |  | 0.25 | Transmission |  | Mechanical Joint |  |  | Unknown |  | 2009-08-19 | 2009-08-19 | Mechanical Repair Fitting - Fitting |  | Other | STAINLESS STEEL | LOS GATOS | THE REPAIR WAS MADE ON MECHANICAL STATIC FITTINGS INSIDE DOWNSTREAM REGULATOR PIT.
| 10-30134- |  |  | 3 | Distribution Main <= 60 PSIG |  | Pressure Control Fittings |  |  | No/Deteriorated Pipe Dope |  | 2010-05-19 | 2011-01-12 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | CUPERTINO | REDOPED & TIGHTEN CAP; SOAP TEST 3" CAP AND THREADS
| 10-30678-1 |  |  | 16 | Transmission |  | Fitting |  |  | Construction Defect |  | 2010-09-11 | 2010-09-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MT. VIEW | REDOPED CAP & TIGHTEN; SOAP TEST
| 10-30737-1 |  |  | 2 | Transmission |  | Valves |  |  | Construction Defect |  | 2010-09-30 | 2010-10-01 | Replace Valve >= 2 inch |  | Steel/Wrought Iron |  | MT. VIEW | P.G.&E CREW DOING VALVE MAINTANCE PER RICH QUIROZ. NEVER SHOULD HAVE BEEN AN 8 SERIES LEAK.; REPLACE VALVE; REPLACE VALVE- SOAP TEST
80 | 10-30750-A |  |  | 0.5 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-12-02 | 2010-12-20 | Replace Main Valve < 2-inch |  | Steel-Other |  | MOUNTAIN VIEW | EXPOSED & SHUT OFF PIN OFF TEE & REPLACED 1/2" GAUGE TAP
| 10-31102-1 |  |  | 4 | Transmission |  | Other |  | PLUG | Other | LOSE FITTING | 2010-09-10 | 2010-09-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MT. VIEW | BLOW DOWN FILTER REDOPE PLUG TIGHTEN
| 10-31103-1 | L-132 |  | 24 | Transmission |  | Drip |  |  | Other | LOOSE FITTING PLUG | 2010-09-10 | 2010-09-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SUNNYVALE | DOPED & TIGHTEN PLUG ON DMP; REDOPED TIGHTENED SOAP TEST OK
| 10-31104-1 | 101 |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2010-09-11 | 2010-09-13 | Other | REPLACED GREASE FITTING | Steel/Wrought Iron |  | MT. VIEW | GREASED VALVE V9.78
| 10-31106-1 | 101 |  | 8 | Transmission |  | Valves |  |  | Construction Defect |  | 2010-09-11 | 2010-09-13 | Other | GREASE VALVE | Steel/Wrought Iron |  | PALO ALTO | GREASE VALVE; SOAP TEST
| 10-31109-1 | 109 |  | 3 | Transmission |  | Valves |  |  | Other | DRY VALVE | 2010-09-12 | 2010-09-12 | Other | GREASED VALVE | Steel/Wrought Iron |  | MT. VIEW | GREASED THE VALVE; GREASED V .49 E4B & SOAP TESTED OK
| 10-31114-1 |  |  | 6 | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2010-09-12 | 2010-09-12 | Other | TIGHTEN FITTING | Steel/Wrought Iron |  | MT. VIEW | GREASE DRY OUT; FIX FITTING SOAP TEST OK
| 10-31114-1 |  |  |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2010-09-12 | 2010-09-12 | Other | TIGHTEN FITTING | Steel/Wrought Iron |  | MT. VIEW | GREASE DRY OUT. FIX FITTING SOAP TEST OK; FIXED FITTING SOAP TEST OK
80 | 10-81204-1 | 8807-01 |  | 18 | Distribution Main >60 PSIG and <20% SYMS |  | Body of Pipe |  |  | External Corrosion |  | 2010-09-24 | 2011-03-16 | Other |  | Steel-Other |  | SAN JOSE | INSTALLED PLIDCO WELD CAP RATED FOR 2000PSIG
80 | 10-88140-1 | 101 | 8.08 | 36 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other |  | 2010-10-20 | 2011-03-10 | Greased - Other |  | Steel-Other |  | MT. VIEW | GREASED VALVE SOAP TEST OK
80 | 10-88141-1 | 101 |  | 1.25 | Transmission >= 20% SMYS |  | Threads |  |  | Other Natural Forces |  | 2010-10-21 | 2011-02-23 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | MT. VIEW | PIPE DOPE AND TIGHTEN FITTINGS
80 | 10-88300-1 | 101 |  | 1.25 | Transmission >= 20% SMYS |  | Threads |  |  | Other Natural Forces |  | 2010-10-21 | 2011-02-23 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | CUPERTINO | PIPE DOPE AND TIGHTEN FITTINGS
80 | 11-30563-B |  |  | 1.25 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | Digin/Excavation |  | 2011-03-29 | 2011-03-29 | Mechanical Repair Fitting - Fitting |  | PE2406/2708 (Yellow) |  | MT. VIEW | USED 1 1/4" METFIT COUPLING; SOAP TEST 1 1/4" METFIT COUPLING
80 | 92-30669-1 |  |  | 2 | Transmission |  | Valves |  |  | Other |  | 1992-08-20 | 1992-11-12 | Other |  | Steel/Wrought Iron |  | PALO ALTO | GREASED 2" VALVE OFF LINE 132
80 | 97-30078-1 |  |  | 3 | Transmission |  | Fitting |  |  | Other |  | 1997-02-15 | 1998-04-18 | Other |  | Steel/Wrought Iron |  | MT. VIEW | GREASED LEAKING VALVES
80 | 11-30558-B |  |  | 16 | Distribution Main >60 PSIG and <20% SYMS |  | Line Valve |  |  | Other | NEEDED GREASE | 2011-03-12 | 2011-03-12 | Greased - Other |  | Steel-Other |  | MOUNTAIN VIEW | REQUIRED GREASE TO STOP LEAK; GREASED VALVE TO STOP LEAK & SOAP TESTED
80 | 11-30559-B |  |  | 4 | Distribution Main >60 PSIG and <20% SYMS |  | Line Valve |  |  | Other | NEEDED GREASE | 2011-03-12 | 2011-03-12 | Greased - Other |  | Steel-Other |  | MOUNTAIN VIEW | REQUIRED GREASE TO STOP LEAK; GRASED VALVE TO STOP LEAK & SOAP TESTED.
| 03-10012-1 |  |  | 16 | Distribution Main |  | Valves |  |  | Other | TIGHTEN ADJ VALVE | 2003-02-07 | 2004-05-27 | Mechanical Repair Fitting - Fitting | TIGHTEN PLUG | Steel/Wrought Iron |  | GILROY | C/S PACHECO PASS HWY VALVE 83-87A; AT VALVE 83-87A OVER VALVE 83 B7B; TIGHTEN PACKING ON BALL VALVE 83-B7B; 83-B7A; 83-B7A WAS NOT LEAKING; REPAIR 3 LEAKS ON VALVES.
| 03-10012-1 | [10 empty] | 2003-02-07 | [5 empty] | GILROY | AT VALVE 83-87A OVER VALVE
| 03-10011-1 |  |  | 8 | Transmission |  | Fitting | Other | VALVE | Material Failure |  | 2003-02-06 | 2004-08-04 | Other | GREASED VALVE | Steel/Wrought Iron |  | GILROY | 232 S OF HOLSCLA RD VALVE 83-AIA; ON VALVE 83-AIA OVER VALVE; M&C MECH. HERNANDEZ & TOM C. GREASED ZERT FITTING; M&C GREASED ZERT FITTING
| 03-10010-1 |  |  | 2 | Distribution Main | [6 empty] | 2003-02-06 | 2004-05-24 |  |  | TR 418 |  | GILROY | RESIDUAL GAS ONLY - ABANDON MAIN & HIGH TO HIGH SET; 50­° E OF NEW AV SOUTH SIDE OF CHURCH, ABANDON MAIN & HIGH TO HIGH SET RESIDUAL GAS ONLY. NO GAS;
| 03-50101-1 |  |  | 0.75 | Service |  | Riser |  |  | Atmospheric Corrosion |  | 2003-09-03 | 2003-09-03 | Replace Valve >= 2 inch |  | Steel/Wrought Iron |  | SAN JOSE | ON RISER; ON RISER; USED STOP COCK CHANGER TO STOP GAS - CUT & RETHREAD RISER - INSTALLED INSULATED STOP COCK
| 03-50061-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2003-06-19 | 2003-06-19 | Service Partially Replaced | ABOVE GROUND 4" 3/4" STL. | Steel/Wrought Iron |  | SJ. | ODOR IN AIR, 4" UNDER STOP COCK ON 3/4" PIPE; RISER NEXT TO HOUSE; CUT OUT BAD PIPE RETHREADED PUT INSULATED STOPCOCK ON; 3/4" STL RISER THREADED PUT NEW STOP COCK
| 03-50055-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2003-10-29 | 2003-10-29 | Other | WELD OVER CORROSION PITTS | Steel/Wrought Iron |  | SAN JOSE | 16" FEEDER MAIN LEAKING IN STREET AREA; FEEDER MAIN LEAKING IN STREET AREA; RAN BEADS OVER EACH PITT FILL THEM JUST OVER FLUSH OF MAIN; (SOAP TEST WELDS); WELDED UP 5 CORROSION PITT HOLE
| 03-50055-1 | [10 empty] | 2003-06-11 | [5 empty] | SAN JOSE | OVER MAIN IN FRONT OF ADDRESS IN W.B. TRANSFORMER #3 BOX; OVER MAIN, PUNCHHOLE OVER MAIN VENTING OUT, LEAK OVER FEEDER MAIN IN STREET, F/O IN STREET NEAR SOUND WALL
[12 empty] | 2003-09-19 |  |  |  | Steel/Wrought Iron |  |  | RELOCATE 16" DFM (WRO)
|  | 0824-02 |  | 12.75 | Transmission | [6 empty] | 2003-09-04 | [5 empty] | SAN JOSE | TIE-IN 12" & REMOVE BYPASS FOR SEVWD PROJECT
|  | 0824-02 |  | 12.75 | Transmission | [6 empty] | 2003-09-04 | [5 empty] | SAN JOSE | TRAIN 12" & REMOVE BY PASS FOR SEVWD PROJECT
|  | 132 |  | 24 | Transmission | [6 empty] | 2003-08-08 |  |  |  | Steel/Wrought Iron |  | SAN JOSE | S/E CORNER HWY 237 @ ZANKER VTA BUS TERMINAL
|  | 101 |  | 36 | Transmission | [6 empty] | 2003-03-12 |  |  |  | Steel/Wrought Iron
| 05-10132-1 |  |  | 8 | [7 empty] | 2005-08-16 | [5 empty] | SAN JOSE | 2% ON FEEDER MAIN; ON FEEDER MAIN, NO GAS FOUND
| 05-10071- |  |  | 1.25 | Service |  | Valves |  |  | Other | NEED GREASE | 2005-04-29 | 2005-05-02 | Other | GREASE VALVE | Steel/Wrought Iron |  | M.H. | STOPCOCK LEAKING; ON CALL SUPV, STOP COCK; GREASED VALVE
| 05-10071-1 |  |  |  | Transmission | [6 empty] | 2005-04-29 | 2005-05-02 |  |  |  |  | MORGAN HILL | STOPCOCK LEAKING; STOPCOCK; 04-29-05 GSR CHECKED FOR THE LEAK
| 05-10071-1 | [10 empty] | 2005-04-29 | [5 empty] | MORGAN HILL | STOPCOCK LEAKING; STOPCOCK; 04-29-05 GSR CHECK FOR THE LEAK
| 05-10053-1 |  |  | 4 | Distribution Main |  | Valves |  |  | Unknown |  | 2005-04-04 | 2005-04-04 |  |  | Steel/Wrought Iron |  | SAN JOSE | REG PIT LEAK; REG PIT; GREASE VALVES IN REPAIR
| 05-20059-1 |  |  | 12 | Transmission |  | Valves |  |  | Construction Defect |  | 2005-02-08 | 2005-08-25 | Other | SEE REPORT DATA | Steel/Wrought Iron |  | SAN JOSE | F/O OVER VALVES IN DR. WAY NEXT TO -RR CROSSING; F/O O/VALVES, IN VALVE F/O; GREASED LEAKING FEEDER PRESSURE VALVE #20
78 | 96-40226-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | External Corrosion |  | 1996-08-10 | 1996-08-10 | Replace Pipe |  | Steel/Wrought Iron |  | SANTA CLARA | CATH PROTECTION CONTACT ON SERVICE INSERTED BRANCH SERVICES
[5 empty] | Transmission | [6 empty] | 2001-05-17 |  |  |  | Steel/Wrought Iron |  | SAN JOSE
|  |  |  | 16 | Transmission | [6 empty] | 2001-05-10 |  |  |  | Steel/Wrought Iron |  | SAN JOSE
|  | 132 | [9 empty] | 2001-04-26 | [5 empty] | SANTA CLARA
|  |  |  | 24 | Transmission | [6 empty] | 2001-04-19 |  |  |  | Steel/Wrought Iron |  | SANTA CLARA
[12 empty] | 2001-03-28 |  |  |  | Steel/Wrought Iron |  | SAN JOSE
|  |  |  | 8 | [7 empty] | 2001-03-27 |  |  |  | Steel/Wrought Iron |  | SAN JOSE
|  | TL109 |  | 22 | Transmission | [6 empty] | 2001-03-27 | [5 empty] | SANTA CLARA
|  |  |  | 12 | Transmission | [6 empty] | 2001-08-09 |  |  |  | Steel/Wrought Iron |  | S.J | -
|  |  |  | 8 | Transmission | [6 empty] | 2001-03-27 | 2001-03-27 | Soap and/or Tape - Other |  | Steel/Wrought Iron |  | SAN JOSE | BODY OF PIPE - WRAP WAS RIDED OFF BY SHOWED PRIMER & WRAP
[12 empty] | 2001-02-18 | [5 empty] | SAN JOSE
| 99-40235- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by 3rd Party | DIGIN | 1999-08-03 | 1999-08-03 | Mechanical Repair Fitting - Fitting | DEAD END | Steel/Wrought Iron |  | MILPITAS | BLOWING 3/4 STEEL SERVICE; SERVICE WAS CUT IN HALF.; M&C'S LEAK PROBLEM; STRUCK 3/4" FEEDER ABANDON SERVICE.; WELD ON 3/4" M/Z AND DEAD END SERVICE. SERVICE WAS NOT MARKED
| 01-40202-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Digin |  | 2001-10-05 | 2001-10-05 | Other | ABAND. | Steel/Wrought Iron |  | SAN JOSE | STRUCK GAS STEEL - BLOWING SJFD ON SITE; EDEN VALE REPAIR CREW, RESPONDED 1120 HRS. HED SQUEEZED BLOWING 3/4" F.P. GAS SV. 1140 HRS.; GAS SRV. WAS STRUCK BY CONTRACTOR WITH BLADE TRACTOR BREAKING ROCKWELL VALVE AT RISER. ABAND SRV. AT 8" FP. STL MAIN; ABAND.; 3/4" F.P. GAS RISER WAS BURIED (NOT VISIBLE) UNABLE TO LOCATE 8-7, 8-01 ASSISTED BY T&D & M&c LOCATORS, SRV. NOT MAPPED
| 02-40006-1 |  |  | 4 | Gathering |  | Fusion Joint |  |  | Construction Defect |  | 2002-01-12 | 2002-01-12 | Other |  | TR 418 |  | SAN JOSE | 20 S/N R TRIMBLE 7' E/W R ZANKER; HISSING; (2) 4" INNOGAZ COUPLINGS (1) FUSION 45° .4 - 22 OF "4" TR418
| 99-50080- |  |  | 6 | Transmission |  | Fitting |  |  | Construction Defect |  |  | 1999-04-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | GILROY | O/MAIN; NEAR VALVE; 83-C36; TIGHTENED BOLTS ON TOP OF 6"
| 99-50051- |  |  | 0.5 | Service |  | Fitting |  |  | Construction Defect |  | 1999-03-10 | 1999-03-10 | Other | RE MELTED | TR 418 |  | SAN JOSE | FOAMING AT SERVICE TEE; FOAMING AT SERV TEE; SQUEEZED TEE, REMELTED 1/2 PL ONTO TEE; SOAP TESTED
| 00-50174- |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 2000-11-18 | 2000-11-18 | Other | PERFECTION CO-P | TR 418 |  | GILROY | STRUCK SERVICE
| 00-50090- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Digin |  | 2000-06-08 | 2000-06-08 | Mechanical Repair Fitting - Fitting |  | TR 418 |  | GILROY | (BLOWING); (BLOWING 2" MAIN); INSTALL 30" OF 2" PLASTIC & TWO MID-FIT COUPLING'; INSTALL 30" OF 1/2 PL & TWO MID-FIT COUPLING
| 02-10022-1 | 300A |  | 6 | Transmission |  | Valves |  |  | Material Failure |  | 2002-05-08 | 2002-10-27 | Other |  | Steel/Wrought Iron |  | MORGAN HILL | OVER VALVE; GREASE VALVE; SOAP TEST
| 12-0402- |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | GILROY
|  |  |  | 8 | Transmission | [6 empty] | 2002-12-03 |  |  |  | Steel/Wrought Iron |  | GILROY
|  | TAYLOR12" |  | 12 | Transmission | [6 empty] | 2002-10-07 | [5 empty] | SAN JOSE
|  |  |  | 8 | Transmission | [6 empty] | 2002-09-13 |  |  |  | Steel/Wrought Iron |  | GILROY
|  |  |  | 8 | Transmission | [6 empty] | 2002-09-13 |  |  |  | Steel/Wrought Iron |  | GILROY
|  |  |  | 8 | [7 empty] | 2002-09-10 |  |  |  | Steel/Wrought Iron |  | GILROY
|  |  |  | 4 | Distribution Main | [6 empty] | 2002-03-19 |  |  |  | Steel/Wrought Iron |  | S.C.C. | INSPECTION ONLY; NB GAS SERVICE
|  |  |  | 24 | Transmission | [6 empty] | 2002-03-05 |  |  |  | Steel/Wrought Iron |  | S.C. | S/O HWY 237.
|  |  |  | 2 | Distribution Main | [6 empty] | 2002-02-26 |  |  |  | Steel/Wrought Iron |  | S.J.
|  | 300B | 496.45
|  | 300A | 482.85
98 | 10-20601-1 | 101 | 0.12 | 6 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-04-29 | 2010-05-24 | Mechanical Repair Fitting - Fitting |  | Other
| 10-20601-1 | 101 | 0.12 | 6 | Transmission |  | Fitting | Other | GREASE FITTING | Material Failure |  | 2010-04-29 | 2010-05-24 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | MILPITAS | PUMPED GREASE FITTING WITH GREASE & THIS WAS A GREASE FITTING ISSUE; SEE ATTACHED OPERATING DIAGRAM #383510
98 | 10-82004-1 | 300B | 47910 | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-09-17 | 2010-09-20 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | MORGAN HILL | GAUGE TAP ON BLOW OFF VALVE
| 10-- | 300B | 479.1 |  |  |  | Fitting |  |  |  |  | 2010-09-17 | [5 empty] | MORGAN HILL
98 | 10-82003-1 | 100 | 13843 | [8 empty] | 2010-09-18 | [5 empty] | SAN JOSE | OPEN OLD FILTER LINE 100; V-12
| 10-- | [10 empty] | 2010-09-18 | [5 empty] | SAN JOSE | V-12
96 | 10-82022-1 | 303 | 4383 | 36 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-09-27 | 2010-09-28 | Other |  |  |  | FREMONT
96 | 10-82022-1 | 303 | 4383 | 36 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-09-27 | 2010-09-28 | Other |  |  |  | FREMONT
|  | 303 | 42.83 |  | Transmission |  | Fitting |  |  | Other | PIPE DOPE | 2010-09-27 | 2010-09-28 | Other | CLEAN & REPLACE PLUG |  |  | FREMONT
96 | 10-82023-1 | 131 | 50.57 | 2 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-09-27 | 2010-09-28 | Other |  |  |  | FREMONT
96 | 10-82023-1 | 131 | 50.57 | 2 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-09-27 | 2010-09-28 | Other |  |  |  | FREMONT
|  | 131 | 50.57 | 2 |  |  | Fitting |  |  | Other | PIPE DOPE | 2010-09-27 |  | Other | CLEAN & REPLACE NIPPLE |  |  | FREMONT
96 | 10-82021-1 | 303 | 4283 | 2 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-09-27 | 2010-09-28 | Other |  |  |  | FREMONT | CLEAN REPLACE PLUG ON PRESSURE TAP
96 | 10-82021-1 | 303 | 42.83 | 2 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-09-27 | 2010-09-28 | Other |  |  |  | FREMONT | CLEAN REPLACE PLUG ON PRESSURE TAP
|  | 303 | 42.83 |  | Transmission |  | Fitting |  |  | Other | PIPE DOPE | 2010-09-27 | 2010-09-28 | Other | CLEAN & REPLACE PLUG ON PRESSURE TA | Steel/Wrought Iron |  | FREMONT
96 | 10-82071-1 | 0804-12 | 0.06 | [8 empty] | 2010-10-14 | [5 empty] | FREMONT
98 | 10-82072-1 | 0804-03 | 1.97 | 6 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-10-14 | 2010-12-06 | Greased - Other |  | Steel-Other |  | SANTA CLARA | CLOSED BY DIVISION; GREASED VLV
96 | 10-82072-1 | 0804-03 | 1.97 | [8 empty] | 2010-10-14 | [5 empty] | FREMONT
96 | 10-88653-1 | 1 | [9 empty] | 2010-11-01 | [5 empty] | SUNOL
98 | 10-88671-1 | [10 empty] | 2010-11-02 | [5 empty] | MILPITAS
96 | 10-88654-1 | DREG4716 | 0 | [8 empty] | 2010-11-02 | [5 empty] | SUNOL
98 | 10-88682-1 | 107 | 28.11 |  | Transmission >= 20% SMYS | [6 empty] | 2010-11-04 | [5 empty] | FREMONT
96 | 10-88681-1 | 107 | 28.25 | [8 empty] | 2010-11-04 |  |  |  | Other |  | FREMONT | SHUT OFF VALVE AT BASE OF REG STATION
96 | 10-88681-1 | 107 | 28.25 | [8 empty] | 2010-11-04 | [5 empty] | FREMONT
|  | 303 | 41.11 | [12 empty] | Steel/Wrought Iron
|  | 300B | 500.46 | 34 | [7 empty] | 2010-09-03 | [5 empty] | MILPITAS
98 | 11-52001-1 | 109 |  | 1 | Transmission >= 20% SMYS |  | Other |  |  | Material Failure |  | 2011-01-15 | 2011-01-15 | Other |  | Steel-Other |  | COLMA | REPAIRED & REBUILT VOLUME BOOSTER, SOAP TE
|  | 107 | 30.8 | [14 empty] | FREMONT | STANDBY IN FREMONT ON LINE 107 TRANSMISSION LINE. WORKING W/ MEARS AND UNDERGROUND CONSTRUCTION TO INSPECT PIPE ON WEST SIDE OF SPAN AT THE LOWER ELBOW AREA. PIPE SIZE IS 24" AND SECTION EXESTED WAS SEAMLESS.
24 | 10-88401-1 | X6427 | 0 | 22 | Transmission >= 20% SMYS |  | Other Mechanical Joint |  |  | Inspection Only |  | 2010-11-02 | 2011-06-28 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | FREMONT | LEAK REPAIR ON VI BLIND FLANGE, DISCOVERED A COUPLE LOOSE NUTS/ BOLTS WHICH WERE TIGHTENED.; PUT TIE IN TAPE AROUND BLIND FLANGE AND SOAP TESTED AND THERE WERE NO BUBBLES FOUND. TIGHTENED LOOSE NUTS/BOLTS.
24 | 10-88400-1 | X6427 | 0 00 | 22 | Transmission >= 20% SMYS |  | Line Valve |  |  | Inspection Only |  | 2010-11-02 | 2011-06-28 | Soap and/or Tape - Other |  |  |  | FREMONT | LEAK REPAIR ON MLV, SOAP TESTED AREA OF LEAK INDICATED BY YELLOW ZIPT TIE, BUT DID NOT GET ANY BUBBLES.; SOAP TESTED AREA OF LEAK INDICATED BY YELLOW ZIP TIE, BUT DID NOT GET ANY BUBBLES.
78 | 10-11031-1 | 100 |  | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-09-18 | 2010-09-29 | Other |  |  |  | SAN JOSE | CLEANED REA CAPS ON 2 SAN A VALVE 2 GREA
78 | 10-11031-1 |  |  | 0.75 |  |  | Valves |  |  |  |  | 2010-09-18 | [5 empty] | SAN JOSE
78 | 10-81208-1 | 300B |  | 34 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-09-29 | 2010-10-12 | Tighten Cap/Bolt - Fitting |  |  |  | SAN JOSE | CANT READ
| 10-81208-1 | 300B |  | 34 | Transmission |  | Valves |  |  | Other | NO LEAK FOUND | 2010-09-29 | 2010-10-12 | Tighten Cap or Bolt | SOAP AND/OR TAPE | Steel/Wrought Iron |  | SAN JOSE | FOUND NO LEAKS USING CG-IT SOAP TEST. TIGHTENED FITTINGS ELT.; DID SOAP TEST
| 10-81208-1 | 300B |  | 34 | Transmission |  | Valves |  |  |  |  | 2010-09-29 | 2010-10-12 | Tighten Cap or Bolt | SOAP AND/OR TAPE |  |  | SAN JOSE | FOUND NO LEAKS UNSING CG IT SOAP TEST. TIGHTENED FITTINGS EDT
24 | 10-81148-1 | L107 | [9 empty] | 2010-09-29 | [5 empty] | FREMONT | NO LEAK FOUND
| 10-81148-1 | L107 | [9 empty] | 2010-09-29 | [5 empty] | FREMONT | NO LEAKS FOUND
24 | 10-81701-1 | DFDS8559 | 1 | [8 empty] | 2010-10-06 | [5 empty] | FREMONT
| 10-81701-1 | DFDS8559 | 1 | 36 | [7 empty] | 2010-10-06 | [5 empty] | FREMONT | LEAK LOCATION WAS MISS-IDENTIFIED SEE ATTACHED A-FORM FOR CORRECT LOCATION; NO LEAKS FOUND
56 | 10-81003-1 | 109 | 4347 | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-10-07 | 2010-10-12 | Mechanical Repair Fitting - Fitting |  |  |  | DALY CITY | NO LEAK FOUND; REPAIR FITTING
| 10-81003-1 | 109 | 4347 |  |  |  | Fitting |  |  |  |  | 2010-10-10 | 2010-10-12 | Mechanical Repair Fitting - Fitting |  |  |  | DALY CITY
| 10-81003-1 | 109 | 4347 |  |  |  | Fitting |  |  |  |  | 2010-10-07 | 2010-10-12 | Mechanical Repair Fitting - Fitting |  |  |  | DALY CITY
| 10-81003-1 | 109 | 4347 | [8 empty] | 2010-10-07 | [5 empty] | DALY CITY
56 | 10-81003-3 | 109 | 43.47 | [8 empty] | 2010-10-07 | [5 empty] | DALY CITY
56 | 10-81003-2 | 109 | 43.47 | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-10-07 | 2010-10-12 | Other |  |  |  | DALY CITY
| 10-81003-2 | 109 | 4347 | 0.75 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2010-10-07 | 2010-10-12 | Other | TIGHTENED FITTING | Steel/Wrought Iron |  | DALY CITY
56 | 10-81003-4 | 109 | 43.42 | 0.75 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-10-07 | 2010-12-07 | Other |  | Steel-Other |  | DALY CITY
56 | 10-81003-4 | 109 | 4347 |  |  |  | Other |  | 746 POSITIONER ON MV-13 |  |  | 2010-10-07 | [5 empty] | DALY CITY
| 10-81003-3 | 109 | 43.47 | [8 empty] | 2010-10-07 | [5 empty] | DALY CITY
| 10-81003-4 | 109 | 4347 |  |  |  | Other |  | 746 POSITIONER ON MV-13 |  |  | 2010-10-07 | 2010-12-07 | Other | REPLACED VALVE POSITION ON V-13, SOA TEST ALL FITTING. ON VALVE (NO LEAKS) |  |  | DALY CITY | THIS IS NOT HCA POSITIONER ON MV-13,. CONTROL GAS, PARTS ORDERED
56 | 10-81003-5 | 109 | 43.47 | [8 empty] | 2010-10-07 | [5 empty] | DALY CITY
| 10-81003-5 | 109 | 4347 | 1 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2010-10-07 |  |  |  | Steel/Wrought Iron |  | DALY CITY | THIS IS NOT HCA FUZZ LEAK ON THE FUEL RACK
78 | 10-81058-1 | X6511 |  | 24 | Transmission >= 20% SMYS |  | Fitting |  |  | Equipment Malfunction |  | 2010-09-28 | 2010-10-14 | Tighten Cap/Bolt - Fitting |  |  |  | MILPITAS
| 10-81058-1 | 6511 |  | 24 | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2010-09-28 | 2010-10-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MILPITAS | FIXED LEAKING GREASE FITTING
24 | 10-81901-1 | 2406-01 | 0 | 36 | Transmission >= 20% SMYS |  | Fitting |  |  | Incorrect Operation |  | 2010-10-21 | 2010-10-21 | Tighten Cap/Bolt - Fitting |  |  |  | FREMONT
|  | 107 | 33.6 | 0.36 | Transmission |  | Fitting |  |  | Incorrect Operation |  | 2010-10-21 | 2010-10-21 | Tighten Cap or Bolt | SOAP AND/OR TAPE | Steel/Wrought Iron |  | FREMONT | REPAIRED LEAK ON __BLEED VALVE & PING & TIGHTENED REPAIRED LEAK ON GREASE FITTING BY GREASING VALVE & TIGHTENED.
98 | 10-88672-1 | 0824-01 | 0.27 | [8 empty] | 2010-11-05 | [5 empty] | SAN JOSE | NO LEAK FOUND
| 10-88672- | 0824-01 | 0.27 | [8 empty] | 2010-11-05 | [5 empty] | SAN JOSE | NO LEAKS FOUND; PROBED AROUND VALVES & UP & DOWN L. 100. NO LEAKS
98 | 10-88835-1 | 300B | 49730 | [8 empty] | 2010-11-05 | [5 empty] | SAN JOSE | NO LEAKS FOUND
| 10-88635- | 300B | 49730 | [8 empty] | 2010-11-06 | [5 empty] | SAN JOSE | NO LEAKS FOUND
78 | 10-21811-1 | 100 | 1493 | 6 | Distribution Main >60 PSIG and <20% SYMS |  |  |  |  | Incorrect Operation |  | 2010-11-08 | 2010-11-08 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | MILPITAS | TIGHTENED VALVE
| 10-21811-1 | 100 | 149.3 | 0.06 | Distribution Main |  | Valves |  |  | Incorrect Operation |  | 2010-11-08 | 2010-11-08 | Tighten Cap/Bolt - Fitting | SOAP AND/OR TAPE | Steel/Wrought Iron |  | MILPITAS | REPAIRED LEAK; TIGHTENED VALVE ONTO NIPPLE. TIGHTENED VALVE HANDLE. TIGHTENED PLUG.; LEAK FOUND AROUND PING. RECONSEALED PLUG & RETIGHTENED PLUG TO REPAIR LEAK.; LEAK FOUND AROUND VALVE WHERE ATTACHED TO NIPPLE. REPAIRED BY TIGHTENING.; LEAK FOUND AROUND HANDLE OF VALVE. RETIGHTENED TO REPAIR LEAK.
98 | 10-88681-1 | STA PIPE |  |  | Transmission >= 20% SMYS | [6 empty] | 2010-11-05 | [5 empty] | FREMONT | NO LEAK FOUND
| 10-88681- | STA PIPE | [9 empty] | 2010-11-05 | [5 empty] | FREMONT | NO LEAKS FOUND; FOUND NO INDICATION OF LEAKS INSIDE STATION IF AT REG SET, THIS IS DIVISION OUTSIDE OF STATION ON ALBRAE
| 03-13101-1 | 131 | 45.5 | 24 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2003-01-21 | 2003-03-05 | Patch Weld - Weld |  |  |  | FREMONT/ ALAMEDA CO. | 8 X 10 WELD PATCH
|  | 300-B | 450.9 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | EXPOSED PIPE TO INSTALL UNDERGROUND UTILITY
|  | 300-A | 472.65 | 34 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 107 | 30.6 | 36 | Transmission | [6 empty] | 1998-10-15 |  |  |  | Steel/Wrought Iron |  | FREMONT | POTHOLE L-107 FOR DEPTH VERIFICATION
| 87-00001-1 | 300B | 415.1 | 0.75 | Service |  | Valves |  |  | Material Failure |  | 1987-03-09 | 1988-04-18 | Other |  | Steel-Other |  | HOLLISTER | REPLACE "O" RING ON FIRE VALVE STEM. INSTALLED JUMPER & MAINTAINED SERVICE TO CUSTOMER
| 87-00001-1 | 300B | 415.1 | 0.75 | Service |  | Valves |  |  | Material Failure |  | 1987-03-09 | 1988-04-18 | Other |  | Steel-Other |  | HOLLISTER | REPLACE "O" RING ON FIRE VALVE STEM. INSTALLED JUMPER & MAINTAINED SERVICE TO CUSTOMER
|  | 300-A | 472.65 | 34 | Transmission | [7 empty] | 1998-09-02 |  |  | Steel/Wrought Iron |  |  | REMOVES SEWER LINE CROSSING LINE 300-A WITH NO SEPARATION ALSO ATTACH WIRES FOR E.T.S.
|  |  |  | 34 | Transmission | [6 empty] | 1998-11-14 | 1998-11-18 |  |  | Steel/Wrought Iron |  | HOLLISTER | BACKFILL EXCAVATION HOLE & CLEAN UP
|  | L-103 | MP 0.2 | 20 | [13 empty] | HOLLISTER
|  | 300-A | 467.18 | 34 | Transmission | [6 empty] | 1998-12-14 |  |  |  | Steel/Wrought Iron |  | GILROY | 14" SEPARATION FROM MAIN & CONDUIT & WATER MAIN & 11/2"
|  | 300-A | 467.18 | 34 | Transmission | [6 empty] | 1998-12-11 | 1998-12-15 | Other |  | Steel/Wrought Iron |  | GILROY | FEATHER ROUGH EDGES ON DENT DUE FROM MECHANICAL MEAN DENT WAS 0.110 MISSING METAL WAS 0.020 REPAIRS
|  |  |  | 34 | Transmission | [6 empty] | 1998-11-14 | 1998-11-18 |  |  | Steel/Wrought Iron |  | HOLLISTER | BACKFILL EXCAVATION HOLE & CLEAN UP
|  | 300-B | 450.9 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | EXPOSED PIPE TO INSTALL UNDER GROUND UTILITY
|  | 300-A | 467.18 | 34 | Transmission | [6 empty] | 1998-12-14 |  |  |  | Steel/Wrought Iron |  | GILROY | 14" SEPARATION FROM MAIN & CONDUIT & 4" WATER MAIN AND 11/2 CONDUIT
|  | 300-A | 467.18 | 34 | Transmission | [6 empty] | 1998-12-11 | 1998-12-15 | Other |  | Steel/Wrought Iron |  | GILROY | FEATHER OUT ROUGH EDGES ON DENT DUE FROM MECHANICL MEAN DENT WAS 0.110 MISSING METAL WAS 0.020 REPAIRS
|  | L-103 | MP 0.2 | 20 | [13 empty] | HOLLISTER
| 09-80047 |  |  | 6 | [7 empty] | 2009-10-21 | 2010-12-20 |  |  | Steel-Other |  | HOLLISTER | AT VALVE M.P 1.87; NO LEAKS FOUND
| 09-80047 |  |  | 6 | [7 empty] | 2009-10-21 | 2010-12-20 |  |  | Steel-Other |  | HOLLISTER | NO LEAK FOUND; AT VALVE M.P 1.87; NO LEAKS FOUND
8 | 09-80047-1 |  | 1.87 | [8 empty] | 2009-10-21 | [5 empty] | HOLLISTER | AT VALVE M.P 1.87; YELLOW
|  | 300A | 453.56 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  | HOLLISTER | SNIFF HOLE W/ SAV-A-VALVE INSTALLED
|  | 300A | 454.42 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  | HOLLISTER | SNIFF HOLE AND SAV A VALVE INSTALLED NEXT TO TOP
98 | 10-82004-1 | 300B | 47910 | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-09-20 | 2010-09-20 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | MORGAN HILL | REPAIRS WERE MADE ON SITE; GAUGE TAP ON BLOW OFF VALVE
98 | 10-82004-1 | 300B | 47910 |  |  |  | Fitting |  |  |  |  | 2010-09-17 | [5 empty] | MORGAN HILL | REPAIRS WERE MADE ON SITE
78 | 10-81028-1 | 0809-02 | 0.07 |  | Transmission >= 20% SMYS |  | Line Valve |  | B/D STACK |  |  | 2010-09-28 | 2011-03-02 | Mechanical Repair Fitting - Fitting |  | Steel-Other |  | MORGAN HILL | FITTING IN FIELD; PIPE DOPE REPLACE; L-300B MP 476.27 REMOVED VALVE; CLEANED THREADS & REPLACE VALVE
| 10-82094-1 | 301A |  | 6 | Transmission |  | Other |  | PACKING LEAK |  |  | 2010-10-09 | 2010-10-21 | Other | REPLACED PACKING | Steel/Wrought Iron |  | HOLLISTER
98 | 10-82094-1 | 301A |  | 6 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Unknown |  | 2010-10-09 | 2010-10-21 | Other |  |  |  | HOLLISTER | REPLACED PACKING
| 10-88451-1 |  |  | 12.75 |  |  | Fitting |  |  | Other | PIPE DOPE | 2010-10-20 | 2010-10-20 | Other | CLEANED & REAPPLIED DO REPLACED EXIS VALVE |  |  | HOLLISTER | ABOVE GROUND VALVE
98 | 10-88381-1 | 300A | 45834 | [8 empty] | 2010-10-21 | [5 empty] | HOLLISTER | NO INDICATION OF LEAK FOUND AT LOCATION
| 10-88381-1 | 300A | 458.33 | [8 empty] | 2010-10-21 | [5 empty] | HOLLISTER | NO INDICATION OF LEAK FOUND AT LOCATION
8 | 10-88382-1 | DREG5362 | 0.01 | 12 | Transmission >= 20% SMYS |  | Other |  | NO LEAK DETECTED BLOWDOWN STACK W/UNIBOLT | Other | NO LEAK DETECTED | 2010-10-21 | 2011-03-23 | Other | NO LEAK DETECTED | Steel-Other |  | HOLLISTER | NO LEAK DETECTED
8 | 10-88382-1 | DREG5362 | 0.01 | [8 empty] | 2010-10-21 | [5 empty] | HOLLISTER | 500" SE ADDRESS, REG STATION IN FIE; VALVE 130'S. OF SHORE ROAD;
|  | 300A | 458.32 | 34 | Transmission |  | Tap Connection |  |  | Material Failure |  | 2010-09-23 |  |  |  | Steel/Wrought Iron |  | HOLLISTER
98 | 10-88380-1 | 300A | 47047 | 0.75 | Single Service |  | Other |  |  | No/Deteriorated Pipe Dope |  | 2010-10-21 | 2011-02-24 | Mechanical Repair Fitting - Fitting |  | Steel-Other |  | GILROY | RAPIRED BY DIVISION 2/24/2011; N HIGH TO HIGH SHUT IN SO LEAKS COULD BE
98 | 10-88421-1 | 300B | 46052 | [8 empty] | 2010-10-22 | [5 empty] | HOLLISTER | PLAT 3646-G06
98 | 10-88383-1 | 300A | 46240 | [8 empty] | 2010-10-22 | [5 empty] | HOLLISTER | WM IS 3683-B07; SEWER GAS
| 10-88383-1 | 0000300A | 462.4 | [8 empty] | 2010-10-22 | [5 empty] | HOLLISTER | BELOW GROUND IN SEWER MAN HOLE 60FT SET OF REG. STATION
98 | 10-88384-1 | 0833-01 | 0.61 | [8 empty] | 2010-10-22 | [5 empty] | GILROY | WM IS 3683-C05; NO LEAK FOUND; CLOSED BY...
98 | 10-88384-1 | 0833-01 | 0.61 | [8 empty] | 2010-10-22 | [5 empty] | GILROY | WM IS 3683-C05
98 | 10-88385-1 | 300A | 46241 | [8 empty] | 2010-10-22 | [5 empty] | HOLLISTER | WM IS 3683-B07
98 | 10-88527-1 | BD621 | 0 | [8 empty] | 2010-10-23 | [5 empty] | HOLLISTER | WM IS 3683-B07
98 | 10-88526-1 | 301G | 4.36 | 0.75 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other | LEAK FROM GREASE FITTING | 2010-10-23 | 2011-03-08 | Other |  | Steel-Other |  | HOLLISTER | EXCAVATED, GREASED VALVE; NO LEAKAGE
98 | 10-88526-1 | 301G | 4.36 |  | Transmission >= 20% SMYS |  | Line Valve |  |  |  |  | 2010-10-23 |  |  |  | Steel-Other |  | HOLLISTER
98 | 10-88527-1 | BD621 | 0 | [8 empty] | 2010-10-23 | [5 empty] | HOLLISTER
98 | 10-88481-1 | 301A | 4.39 | [8 empty] | 2010-10-23 | [5 empty] | HOLLISTER
98 | 10-88482-1 | 301A | 439 | 0.75 | Transmission >= 20% SMYS |  | Line Valve |  | GAUGE TAP | Other |  | 2010-10-23 | 2011-02-08 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | HOLLISTER | CAP WAS LOOSE AND VALVE WAS SLIGHTLY OPEN
98 | 10-88483-1 | 301A | 3.65 | 0.25 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-23 | 2011-03-08 | Mechanical Repair Fitting - Fitting |  | Steel-Other |  | HOLLISTER | 2 REPAIRS NEXT TO FILTER LINE HAD TO BLOW DOWN FITTINGS REMOVED AND SEALANT APPLIED TO THREADS; ALL LEAKS WERE IN TUBBING & ON PIPE FITTINGS
| 10-88485-1 | DREG5408 | 0.02 | [8 empty] | 2010-10-26 | [5 empty] | SALINAS
| 10-88528-1 | DREG5408 | 0.02 | 1 | Transmission |  | Valves |  |  | Unknown |  | 2010-10-26 | 2011-01-19 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | SALINAS | REPLACED 1" VALVE ON SIDE OF B/O STACK
|  | 103 | 12.9 | 12 | Transmission | [6 empty] | 2010-01-29 |  |  |  | Steel/Wrought Iron |  | SALINAS | PIPE EXPOSED BY EROSION. ADDITIONAL PIPE WITH BARE COVER
|  | 103 | 15.3 | 12 | Transmission | [6 empty] | 2010-09-08 |  |  |  | Steel/Wrought Iron |  | SALINAS
98 | 11-53001-1 | 300A | 462.19 | 1 | Transmission >= 20% SMYS |  | Other |  | VALVES | Inspection Only |  | 2011-01-13 |  |  |  | Steel-Other |  | GILROY
98 | 11-53001-1 | 300A | 462.19 | 1 | Transmission >= 20% SMYS |  | Other |  | VALVES | Inspection Only |  | 2011-01-13 |  |  |  | Steel-Other |  | GILROY
|  | 300A | 443.8 | [14 empty] | TRES PINOS | NO DRIP FOUND
|  | DREG5419 | 0.75 | 4 | Distribution Main >60 PSIG and <20% SYMS | [6 empty] | 2011-01-12 |  |  |  | Steel-Other |  | HOLLISTER
87 | 11-80003-b | 402/DFM | 16.09 | 6 | Transmission >= 20% SMYS |  | Other |  |  | Other | FAILED THERMAL CHECK VALVE | 2011-01-20 | 2011-02-08 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | ANDERSON | REMOVED THERMAL EXPANSION PLUG & REPLACED WITH A SOLID PLUG ISOLATED & BLEW DOWN VALVE. PLUG WAS ON BODY OF VALVE
87 | 73-38- |  |  | 1.25 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1973-08-29 | 1973-08-29 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | SOAP TEST OK. STAND UP PRESSURE TEST. OK
87 | 74-00025-1 |  |  | 10 | Transmission |  | Fitting |  |  | Material Failure |  | 1974-05-29 | 1974-08-16 | Other |  | Steel/Wrought Iron |  |  | FOUND... AROUND CAP ...REPAIRING...AND TIGHTENING CAP
87 | 74-00062-1 |  |  | 0.75 | Other |  | Other |  |  | Other |  | 1974-06-24 | 1974-07-01 | Replace Pipe and/or Service |  | Steel/Wrought Iron
87 | 74-00063-1 |  |  | 8 | Transmission |  | Valves |  |  | Other |  | 1974-06-24 | 1974-07-01 | Other |  | Steel/Wrought Iron
87 | 75-00015-1 |  |  | 2 | Distribution Feeder Main |  | Longitudinal Weld |  |  | Construction Defect |  |  | 1975-01-24 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | REPAIRED WELD 16" OF PIPE AND 2 - 45 DEGREE WELDING ELLS; INST. 2-2" P.C.F. WITH 3/4" BYPASS & REPLACE LEAKING WELD WITH 2' OF PIPE AND 2-45' WELDING
87 | 77-00007-1 |  |  | 2 | Other | M | Fitting |  |  | Construction Defect |  | 1977-01-17 |  | Other |  | Wrought Iron |  | REDDING | FOUND LEAKAGE AROUN P.C.F. CAP. REPAIRED BY REDOPING AND TIGHTENING CAP
87 | 77-00078-1 |  |  | 10 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 1977-07-28 | 1977-07-28 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | ANDERSON | 10" TP MAIN LINE FEED TO REDDING. WESTSIDE OF HWY 213 CROSSING 6' INSIDE 16" CASEING 500TH SOUTH OF ANDERSON FAIRGROUNDS. ALOT OF MOISTURE UNDER CASEING INSTALLED ...
87 | 83-00028-1 |  |  | 10 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 1983-03-16 | 1984-06-07 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | REDDING | FOUND A SMALL LEAK ON A GIRTH WELD ON 10" PIPE. LEFT OFF FOR NOW. SUPERVISORS WILL DECIDE ON COURSE OF PERMANENT REPAIRS AT LATER LIFE.; REPAIRED WITH...
83 | 79-00050-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1979-03-06 | 1979-03-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | BURNEY
87 | 79-00040-1 |  |  | 1.25 | Other |  | Meter |  |  | Other |  | 1979-02-16 | 1979-03-20 | Other |  | Steel/Wrought Iron |  | REDDING | FOUND LEAK AT SWIVAL CONNECTION ON OUT LET SIDE OF METER REPAIRED BY TIGHENING SWIVAL
13 | 81-00050-1 |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1981-11-24 | 1981-11-24 | Other |  | Steel/Wrought Iron |  | REDDING | REPAIRED; REPLACED BY ....
13 | 82-00038-1 |  |  | 0.5 | Distribution Main |  | Other |  |  | Material Failure |  | 1982-11-05 | 1982-11-08 | Replace Pipe and/or Service |  | Plastic |  | REDDING | REPAIRED; INSERTED RISER LEAKING INTERNALLY
87 | 82-00023-1 |  |  | 0.75 | Transmission |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 1982-04-29 | 1982-07-22 | Other |  | Steel/Wrought Iron |  | MOUNTAIN GATE | REPAIRED; FOUND CAP ON PRESSURE GAUGE-TAP LEAKING. REPAIRED SAME. RESET VALVE FRAME MOVER.
87 | 83-00008-1 |  |  | 3 | Distribution Feeder Main |  | Girth Weld |  |  | Construction Defect |  | 1983-04-10 | 1984-06-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | PARKVIEW | REPAIRED & ...; LARGE AMOUNT OF SCALE FOUND INSIDE MAIN
87 | 83-00012-1 |  |  | 10 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-02-17 | 1984-05-24 | Other |  | Steel/Wrought Iron |  | PINE GROVE | REPAIRED
87 | 83-00019-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Material Failure |  | 1983-04-22 | 1983-05-03 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | RED BLUFF | REPAIRED; WELD FULL WEDDING BAND 24"
87 | 83-00020-1 |  |  | 12 | Transmission | [6 empty] | 1983-04-22 |  |  |  | Steel/Wrought Iron |  | RED BLUFF | DELETED
13 | 83-00025-1 |  |  | 0.75 | Other |  | Fitting |  |  | Construction Defect |  | 1983-05-10 | 1983-05-13 | Other |  | Steel/Wrought Iron |  | ANDERSON | REPAIRED; REPAIRED LEAK BY TIGHENING CAP S/O SERV. LINE
87 | 83-00050-1 |  |  | 1 | Distribution Main |  | Tap Connection |  |  | Construction Defect |  | 1983-11-22 | 1983-11-22 | Other |  | Plastic |  | REDDING | REPAIRED; LEAK AT THP CONNECTION
| 10-70010 | 177A | 48.85 | [8 empty] | 2010-03-27 | [5 empty] | RED BLUFF | AT 3RD STAGE REG STA. 119; NO LEAKAGE FOUND DELETE
85 | 10-70017-1 | 177A | 85.73 | [8 empty] | 2010-04-23 | [5 empty] | PLATINA | 1ST STAGE BOX AT GUAGE TAP; NO LEAK FOUND
| 10-70017-1 | 177 | 85.73 | 0.75 |  |  | Fitting |  |  | Other | LOOSE | 2010-04-23 |  |  |  | Steel/Wrought Iron |  | PLATINA
| 10-70018-1 | 177 | 85.73 | 0.75 |  |  | Fitting |  |  | Other | LOOSE | 2010-04-23 |  |  |  | Steel/Wrought Iron |  | PLATINA | 1. SOURCE OF LEAK AT REG.; 2. DATE SOURCE WAS DETERMINED 4/23/2010; 3. NO PROMT REPAIRS REQUIRED
| 10-70019-1 | 177 | 85.73 | 0.75 |  |  | Fitting |  |  | Other | LOOSE | 2010-04-23 |  |  |  | Steel/Wrought Iron |  | PLATINA
| 10-70020-1 | 177 | 78.21 | 0.75 |  |  | Fitting |  |  | Other | LOOSE | 2010-04-23 |  |  |  | Steel/Wrought Iron |  | PLATINA | 1. SOURCE OF LEAK BYPASS CAP; 2. DATE SOURCE WAS DETERMINED 4/23/2010; 3. NO PROMT REPAIRS REQUIRED
| 10-70021-1 | 177 | 78.21 | 0.75 |  |  | Fitting |  |  | Other | LOOSE | 2010-04-23 |  |  |  | Steel/Wrought Iron |  | PLATINA | 1. SOURCE OF LEAK BYPASS CAP; 2. DATE SOURCE WAS DETERMINED 4/23/2010; 3. NO PROMPT REPAIRS NEEDED
85 | 10-81078-1 | DREG5030 | 30.25 | [8 empty] | 2010-10-16 | [5 empty] | COMING
| 09-70026-1 | 177 | 88.8 | 0.75 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2009-05-13 | 2009-05-14 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | HARRISON GULCH | SOAP TEST
| 09-70027-1 | 177 | 88.8 | 0.75 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2009-05-13 | 2009-05-14 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | HARRISON GULTH | SOAP TEST
| 09-70028-1 | 177 | 88.8 | 0.75 | Transmission |  | Fitting |  |  | Other | LOOSE CAP | 2009-05-13 | 2009-05-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | HARRISON GULCH | SOAP TEST
| 09-70029-1 | 177 | 88.8 | 0.75 | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-05-13 | 2009-05-14 | Other | OPERATE VALVE | Steel/Wrought Iron |  | HARRISON GULCH | SOAP TEST
| 09-70030-1 | 177 | 85.73 | 0.75 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2009-05-13 | 2009-05-14 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | PLATINA | SOAP TEST
| 09-70031-1 | 177 | 85.73 | 0.75 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2009-05-13 | 2009-05-14 | Other | TIGHTENED FITTINGS | Steel/Wrought Iron |  | PLATINA | SOAPTEST
| 09-70032-1 | 177 | 78.21 | 0.75 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2009-05-13 | 2009-05-15 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | PLATINA | SOAP TEST
| 05-70009-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 2005-04-28 | 2005-04-28 | Mechanical Repair Fitting - Fitting |  | Aldyl A (Tan or Gray) |  | RED BLUFF | PM 40507119; INSTALLED DEAD END 28" INCH. BELOW GROUND
| 03-70018-1 | [10 empty] | 2003-08-23 | [5 empty] | RED BLUFF
| 03-70019-1 | 177 | 38.89 | 0.75 | Transmission |  | Fitting |  |  | Other | LOOSE PLUG | 2003-08-23 | 2004-02-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | RED BLUFF | TIGHTEN VALVE PLUG; EAST END OF OHMAN AVE.
| 03-70020-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other | LOOSE FITTING | 2003-08-23 | 2003-10-22 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | RED BLUFF | TIGHTENED FITTING
| 02-70022-1 |  |  | A | Transmission |  | Other |  | FLANGE IN PIT | Construction Defect |  | 2002-10-28 | 2003-06-04 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | RED BLUFF | REPAIRED FLANGE IN MONITOR PIT
| 01-70004-1 | [10 empty] | 2001-07-12 | [5 empty] | RED BLUFF | IN REG BOX; IN REG BOX; IN REG BOX; NO LEAK FOUND
| 01-70008-1 |  |  | 4 | Transmission |  | Valves |  |  | Other | GREASE & BONNET | 2001-08-07 | 2002-10-02 | Other | TIGHTEN BONNETT & GREASED | Steel/Wrought Iron |  | RED BLUFF
| 01-70008-1 |  |  | 4 | Transmission |  | Valves |  |  | Other | GREASE & BONNET | 2001-08-07 | 2002-10-02 | Other | TIGHTEN BONNETT & GREASED | Steel/Wrought Iron |  | REDBLUFF | DUG UP TIGHTENED BONNET & GREASED; SOAP
85 | 74-00016-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-04-18 | 1974-04-18 | Other |  | Steel/Wrought Iron |  |  | DRIP CUT OFF ON WORK ORDER
85 | 74-00056-1 |  |  | 2 | Distribution Feeder Main |  | Physical/Mechanical Joint |  |  | Other |  | 1974-11-20 |  | Other |  | Steel/Wrought Iron |  |  | DELETED; RECHECKED BY R. LINDERMANH, NO LEAKAGE COULD BE FOUND 12-11-74; FIRST STAGE REG.
85 | 72-00002-1 |  |  | 12 | Transmission |  | Valves |  |  | Other |  | 1972-03-31 | 1972-04-07 | Other |  | Steel/Wrought Iron |  |  | VALVE STEM LEAKING REPAIR. BY PACKING WITH PLASTIC PACKING.
85 | 72-00031-1 |  |  | 0.75 | Other |  | Drip |  |  | Corrosion |  | 1972-11-02 | 1972-11-06 | Other |  | Steel/Wrought Iron |  |  | WELDED TO MAIN LEFT IN PLACE
85 | 71-60003- | 177 | 57.08 | 12 | Transmission |  | Fitting |  |  | Other |  | 1971-03-17 | 1971-06-23 | Other |  | Steel/Wrought Iron |  | RED BLUFF | FOUND CAP ON 1" VALVE TEE LEAKING, MADE REPAIRS BY TIGHTENING CAP.
| 71-60003-1 | [5 empty] | Fitting |  |  | Other
85 | 71-60003- | 177 | 57.08 | 12 | Transmission |  | Fitting |  |  | Other |  | 1971-03-17 | 1971-06-23 | Other |  | Steel/Wrought Iron |  | RED BLUFF | FOUND CAP ON 1" VALVE TEE LEAKING, MADE REPAIRS BY TIGHTENING CAP
10 | 93-00002-1 |  |  | 2 | Other | M | Tap Connection |  |  | Material Failure |  | 1993-01-12 | 1992-01-27 | Other |  | Aldyl A (Tan or Gray) |  | RED BLUFF | REPAIRED SERVICE TEE CAP BY USING REPAIR FITTING FOR ALDYLA SERVICE TEES; REPAIRED; LEAK AT SERVICE TEE
85 | 91-10001-1 |  |  | 1 | Distribution Feeder Main |  | Physical/Mechanical Joint |  |  | Damage by outside Forces |  | 1991-10-21 | 1991-10-21 | Other |  | Steel/Wrought Iron |  | PROBERTA | REPAIRED NIPPLE AND PLACED REG. BACK IN SERVICE; ENTERED
85 | 86-00007-1 |  |  | 4 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1986-05-06 | 1986-05-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | RED BLUFF | REPAIRED; FOUND COMPOSITION CAP LEAK ON OLD T.P TAP HAD BEEN C/O OFF-REDOPED CAP AND TIGHTEN
85 | 82-00004-1 |  |  | 0.5 | Service |  | Fitting |  |  | Construction Defect |  | 1982-02-18 | 1982-03-31 | Other |  | Plastic |  | RED BLUFF | REPAIRED
85 | 82-00012-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1982-12-09 | 1982-12-10 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | CORNING | INST. 6"X12" FULL CIR. PATCH INTERNAL COLLISION
85 | 81-00004-1 |  |  | 12 | Transmission | [6 empty] | 1991-04-30 |  |  |  | Steel/Wrought Iron |  |  | DELETED
85 | 81-00025-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1981-11-30 | 1981-12-01 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | REPAIRED; INTERNAL COORUSION-NOT INSPCD. GATHERING LINE # 193 NORTH PARALELL LINE # 177. CLASS 1 LOC.
85 |  | 193 |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1981-11-30 | 1981-12-01 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | INTERNAL COORUSION-NOT INSPCD. GATHERING LINE # 193 NORTH PARALELL LINE # 177. CLASS 1 LOC.
85 | 80-00026-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1980-11-25 | 1980-11-26 | Replace Pipe and/or Service |  | Wrought Iron |  |  | REPAIRED; 3/8" +/- HOLE IN PIPE. REPLACED 53 1/4" OF 6" GATHERING LINE (6.625" DIA .188W.T. 5L. CRD. B, 35,000); CLASS I LOCATION UNORIZED GAS.;
85 | 79-00002-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Corrosion |  | 1979-01-31 | 1979-02-08 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | REPAIRED; LINE 193-GATHERING LINE BETWEEN PEND #2 & COMPENSION ON HALL ROAD-KIRKWOOD. CAL. WELDED ON PATCH & REPAIR.
85 | 79-00007-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1979-04-30 | 1980-04-08 | Other |  | Steel/Wrought Iron |  | RED BLUFF | LEAKING 3/4" DRIP C/O DRIP RISER BELOW GROUND.
85 | 76-00002-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-03-22 | 1976-03-22 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | REPAIRED
85 | 75-00001-1 |  |  | 1.25 | Other |  | Body of Pipe |  |  | Corrosion |  | 1975-01-23 | 1975-01-24 | Patch Welded |  | Steel/Wrought Iron |  | RED BLUFF | GAS IN PT&T MANHOLE WALNUT E/O JACKSON LINCOLN ALLEY.; FOUND 1 1/4 STUB (OLD CUT OFF) CORRODED & LEAKING. WALNUT ST 108 W/O MONROE
85 | 75-00021-1 |  |  | 0.75 | Other |  | Drip |  |  | Corrosion |  | 1975-04-30 | 1975-04-30 | Other |  | Steel/Wrought Iron |  |  | REPAIRED 4-30-75
85 | 75-00036-1 |  |  | 2 | Distribution Feeder Main | [6 empty] | 1975-07-07 |  |  |  | Steel/Wrought Iron |  |  | NO LEAK FOUND
| 07-80003-1 |  |  | 1.25 | Service |  | Fitting | Plastic Tee Cap |  | Construction Defect |  | 2007-01-22 | 2007-01-22 | Tee Fused Over Defect - Plastic |  | Aldyl A (Tan or Gray) |  | REDDING | INSTALLED TEE REPAIR CAP TO. SRVICE TO .2779 RESERVIOR APT #86.; INSTALLED TEE REPAIR CAP TO SERVICE TO 2779 RESERVOR, APT #86
| 07-80027-1 | 402 |  | 2 | Transmission |  | Valves |  |  | Other | GREASE | 2007-03-15 | 2007-03-15 | Other | GREASED VALVE | Steel/Wrought Iron |  |  | GREASED VLAVE
| 07-80039-1 | 402 | 36.23 | 3 | Transmission |  | Valves |  |  | Other | BUTTON HEAD | 2007-05-01 | 2007-05-01 | Other | REPLACED GREASE FITTING | Steel/Wrought Iron |  | MOUNTAIN GATE | REPLACED GREASE FITTING
| 04-80005-1 | 402 | 17.89 | 0.75 | Transmission |  | Fitting |  |  | Construction Defect |  | 2004-01-09 | 2004-01-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ANDERSON | CAPS ON BOTH PIN OFF TEES LEAKING. USED TEFLON TAPE. RETIGHTEN; TEFLON TAPE LEAKING CAPS, TIGHTEN.
| 04-80005-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Construction Defect |  | 2004-01-09 | 2004-01-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ANDERSON | COPY FOR RECHECK; CAPS ON BOTH PIN OFF TEES LEAKING. USED TEFLON TAP, RETIGHTENED
| 04-80007-1 | 402 | 17.39 | T | Transmission |  | Regulator |  |  | Material Failure |  | 2004-01-09 | 2004-01-13 | Other | REBUILT REGULATOR | Steel/Wrought Iron |  | ANDERSON | REG. BLOWING OUT OF VENT, REBUILT REG.; FIX DIAPHRAM ON REG
| 04-80009-1 | [10 empty] | 2004-01-26 | [5 empty] | MCARTHUR | AT SECOND STAGE; H-202 LEAKING; 41139 BROWN RD-REG. STA 73-2ND STAGE; NO LEAKAGE FOUND
| 04-80024-1 | 402 | 17.39 | 0.75 | Transmission |  | Regulator |  |  | Other | DIAPHRAGM FROZE | 2004-03-03 | 2004-03-10 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ANDERSON | TIGHTEN BOLTS ON DIAPHRAM HOUSEING; SOAP TEST
| 04-80122-1 | 402 | 19.31 | 0.75 | Transmission |  | Regulator |  |  | Equipment Malfunction |  | 2004-10-08 | 2010-04-27 | Other | NEW REG | Steel/Wrought Iron |  | ANDERSON | REPLACED REG; SOAP TEST RAN, LEFT + DAY RECORDER
| 03-80050-1 | DFM |  | 0.75 | Transmission |  | Valves |  |  | Other | DRIED OUT GREASE | 2003-06-18 | 2004-02-11 | Other | GREASE VALVE | Steel/Wrought Iron |  | MCARTHUR | ABOVE GROUND VALVE ON 3/4" PIPE LEAKING, GREASED VALVE; GREASED LEAKING VALVE.
| 03-80049-1 | FALL RIVER FEEDER |  | 0.75 | Transmission |  | Fitting | Valves |  | Other | THREADS | 2003-06-18 | 2003-09-24 | Deactivate #TP Main | REPLACE TP MAIN; REPLACE VALVE < 2 INCH | Steel/Wrought Iron | MCARTHUR |  | TIGHTENED PLUG & REPLACED 3/4" V-51 & 8" OF 3/4" T.P. PIPE
| 03-80058-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2003-06-24 | 2003-09-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MCARTHUR | CAP ON 3/4" PIN OFF TEE, REDOPED AND TIGHTENED
| 03-80059-1 | DFM |  | 0.75 | Transmission |  | Valves |  |  | Other | GREASE | 2003-06-24 | 2004-07-15 | Other | GREASE VALVE | Steel/Wrought Iron |  | MCARTHUR | GREASED & OPERATED VALVE. REPLACED BUTTON HEAD
| 03-80061-1 | DFM |  | 0.75 | Transmission |  | Other |  | RELIEF VALVE | Other | REG FAILURE | 2003-06-24 | 2004-07-22 | Other | REBUILT REG | Steel/Wrought Iron |  | MCARTHUR | REBUILT 141 REG @ FIRST STAGE
| 03-80074-1 | [10 empty] | 2003-07-14 | [5 empty] | BURNEY | REG STA. 93-1ST & 2ND STAGES
| 03-80081-1 | [10 empty] | 2003-07-23 | [5 empty] | BURNEY | REG STA. 64-SECOND STAGE BOX; NO LEAKAGE
[12 empty] | 2002-06-13 |  |  |  | Steel/Wrought Iron |  | REDDING | NO LEAK SCARRED PIPE; G.C. TO DO REPAIRS ON 6-17-02
| 02-80016-1 |  |  | 3 | Transmission |  | Valves |  |  | Other | GREASE FITTING | 2002-03-13 | 2002-03-14 | Other | GREASE FITTING | Steel/Wrought Iron |  | REDDING | GREASED VALVE
| 02-80068-1 |  |  | 0.5 | Gathering |  | Body of Pipe |  |  | Other | RODENT | 2002-09-24 | 2002-09-30 | Mechanical Repair Fitting - Fitting |  | Aldyl A (Tan or Gray) |  | ANDERSON | RODENT CHEWED ALDYLA SVC. INSTALL REPAIR COUPLING
| 02-80068-1 |  |  | 0.5 | Gathering |  | Body of Pipe |  |  | Other | RODENT | 2002-09-24 | 2002-09-30 | Mechanical Repair Fitting - Fitting |  | Aldyl A (Tan or Gray) |  | ANDERSON | RODENT CHEWED ALDYL 'A' SVC. INSTALL REPAIR COUPLING
| 02-80106-1 | SIGNAL DFM |  | 3 | Transmission |  | Body of Pipe |  |  | Atmospheric Corrosion | EXTERNAL CORROSION | 2002-12-16 | 2002-12-16 | Deactivate #TP Main |  | Steel/Wrought Iron |  | ANDERSON | SHUT V-201 (TAP VALVE) ISOLATED LEAKING LINE
| 00-80017-1 |  |  | 4 | Distribution Main |  | Fusion Joint |  |  | Construction Defect |  | 2000-03-28 | 2001-05-09 | Other | INNOGAS COUPLING | Aldyl A (Tan or Gray) |  | ANDERSON | BUTT FUSION WAS BAD. INSTALL INNOGAS REPAIR COUPLING.
| 00-80017-1 |  |  | 4 | Distribution Main |  | Fusion Joint |  |  | Construction Defect |  | 2000-03-28 | 2001-05-09 | Other | INNOGAS COUPLING | Aldyl A (Tan or Gray) |  | ANDERSON | BUTT FUSION WAS BAD, INSTALL INNOGAS REPAIR COUPLING; INSTALL BYPASS TEST GAUGES, PINT, 4" COUPLING (SEE ATTACHED SKETCH) TO REPAIR FAILED BUTT FUSION JOINT.
| 00-80017-1 | [10 empty] | 2000-03-28 | [5 empty] | ANDERSON | 150' W/O NORTH ST. ON SIDE; SAME
| 99-80006 |  |  | 2 | Transmission |  | Fitting |  |  | Damage by Natural Forces | MATERIAL FAILURE | 1999-02-24 | 1999-02-27 | Other | REPLACED 2"-45º ELL | Steel/Wrought Iron |  | MCARTHUR | BEGAN REPAIR # 0600 ON 3/26/99, REPAIR COMPLETED # 0630 ON 3/27/99
87 | 99-80007-1 |  |  | 12.75 | Transmission |  | Longitudinal Weld |  |  | Material Failure |  | 1999-03-25 |  | Replace Pipe |  | Steel/Wrought Iron |  | COTTON WOOD | SEE JOB 6022344-55
| 99-80013-1 |  |  | 0 | Transmission |  | Body of Pipe | Fitting |  | Construction Defect |  | 1999-03-30 | 2000-11-15 | Other | REPLACED MAIN JOB# 7035612 | Steel/Wrought Iron |  | REDDING | REPLACED MAIN 117' IN STREET AT 150' E/O HWY 273
| 99-80013-1 |  |  | 10 | Transmission |  | Body of Pipe | Fitting |  | Construction Defect |  | 1999-03-30 | 2000-11-15 | Other | REPLACED MAIN JOB# 7035612 | Steel/Wrought Iron |  | REDDING | REPLACED MAIN 117' IN STREET AT 150' E/O HWY 273
| 99-80013-1 |  |  | 0 | [7 empty] | 1999-03-30 | [5 empty] | REDDING | N/S OF BONNY VIEW OVER MAIN AT R/R CROSSING; N/S OF BONNY VIEW OVER MAIN AT R/R CROSSING; FOUND LEAK ON WELD ON 10" TP.; DOWN GRADE TO III READING DOWN. HOB DRAWN UP TO REPAIR RECHECKD ON 6 MONTH RECHECK.
87 | 97-80010-1 |  |  | 0.5 | Service |  | Fitting |  |  | Material Failure |  | 1997-03-18 | 1998-03-19 | Other |  | Aldyl A (Tan or Gray) |  | REDDING | E/S EAST SIDE RD. 760 N/O WAVERLY DR. ALDYLA SOUCE TEE INSTALL REPAIR CAP
87 | 96-80025-1 | [10 empty] | 1996-04-09 | 1996-04-22 |  |  |  |  | S. REDDING | DOWNGRADED TO 3
87 | 96-80030-1 |  |  | 10 | Transmission |  | Fitting |  |  | Other |  | 1996-04-11 | 1996-05-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ANDERSON | TIGHTEN FLANGE
87 | 95-80041-1 |  |  | 2 |  |  | Body of Pipe |  |  | Corrosion |  | 1995-05-03 | 1996-04-10 | Clamp |  | Steel/Wrought Iron |  | REDDING | REPAIR CLAMP 51' NORTH OF ...AVE.
87 | 95-80149-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1995-10-07 | 1995-10-07 | Replace Pipe |  | TR 418 |  | FALL RIVER | OVER 2" MAIN AND 1" SER OFF OF MAIN BETWEEN HOSPITAL AND DOCTORS OFFICES. INSTALLED 2" ELBOW AND 6' OF 2" TR-418 PLASTIC PIPE 2" COUPLING 2 X 1" SERVICE TEE 4' OF TR 418 PLASTIC PIPE 2" SUPPORT CLAMP; SKETCH ATTACHED
87 | 94-80014-1 |  |  | 2 | M |  | Tap Connection |  |  | Construction Defect |  | 1994-11-12 | 1994-11-12 | Replace Pipe |  | Aldyl A (Tan or Gray) |  | REDDING | OFF SET MAIN-INSTALLED NEW SER. TEE!; SERVICE TEE SIDE TAP PULLED OFF 2" ALDYL MAIN SQUEEZE OFF MAIN-CUT OUT DAMAGED SECTION MADE MAIN OFFSET OF 2" MAIN 3'X1' OFFSET INSTALLED NEW SERVICE TEE
13 | 91-90125-1 |  |  | 1.25 | M |  | Body of Pipe |  |  | External Corrosion |  | 1991-07-21 | 1991-07-23 | Patch Welded |  | Steel/Wrought Iron |  | REDDING | FOUND PIT ON 2" MAIN WHERE SEWER LATERAL CROSSED GAS MAIN APPRX 2' S/OF SERVICE TIE-IN...WELDED PATCH ON LEAK C/OFF 1 1/4" FOR NON USE PER CUSTOMER REQUEST 7-23-91 GIM; REPAIRED; ; WELDED PATCH 3' S/OF SERVICE TIE-IN LEAKAGE CAUSED BY BACK HILL MATERIAL AS THEY CROSSED GAS FACILITIES! C/OFF 1 1/4 SERVICE 1' W/OF BRANCH CONNECTION PER CUSTOMER REQUEST.
10 | 91-00021-1 |  |  | 1 | Transmission |  | Fitting |  |  | Other |  | 1991-04-08 | 1991-04-25 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | REDDING | FOUND SAVOR CAP NOT TIGHTENED RE-DOPED AND TIGHTENED
87 | 91-00022-1 |  |  | 0.75 | Transmission |  | Other Welds |  |  | Construction Defect |  | 1991-05-09 | 1991-05-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | REDDING | REPAIRED LEAK ON 3/4" COUPLING WITH 3/4 STL. PLUG WELDED IN WAS LEAKING WELDED 3" NIPPLE WITH SAVER VALVE.
87 | 88-10001-1 | [10 empty] | 1988-04-12 | [5 empty] | REDDING
| 08-80076-1 | DFM |  | 0.75 | Transmission |  | Valves |  |  | Other | GREASE | 2008-06-23 | 2009-07-20 | Other | GREASE VALVE | Steel/Wrought Iron |  | GLENBURN | SOAP TEST GREASED VALVE
| 08-80088-1 | [10 empty] | 2008-07-10 | [5 empty] | JOHNSON PARK | 30' W/O FRAME AND COVER; NO LEAK
| 09-80041-1 | DFM |  | 0.75 | Transmission |  | Other |  | CAP ON PIN OFF TEE | Other | LOOSE CAP | 2009-05-07 | 2009-05-07 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MCARTHUR | SOAP TEST
| 09-80042-1 | 400 | 84.19 | [8 empty] | 2009-05-07 | [5 empty] | BURNEY
| 09-80044-1 | 401/400 | 80.94 | 2 | Transmission |  | Fitting |  |  | Other | LOOSE | 2009-05-14 | 2009-05-15 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | JOHNSON PARK | REDOPED & RETIGHTENED 2" BTTM TAP CAP. BOTTOM TAP FEED JOHNSON PARK DRS.
| 09-80044-1 | 401 | 80.94 | [8 empty] | 2009-05-07 | [5 empty] | JOHNSON PARK
| 09-80105-1 | DFM | 32.8 | 6 | Transmission |  | Valves |  |  | Unknown |  | 2009-05-23 | 2010-06-14 | Other | OPERATION | Steel/Wrought Iron |  | SHASTA LAKE CITY | SOAP TEST
| 09-80105-1 | DFM | 32.8 | [8 empty] | 2009-05-23 | 2009-05-23 |  |  |  |  | SHASTA LAKE CITY
| 09-80105-1 | DFM |  | 3 | [7 empty] | 2009-05-23 | [5 empty] | SHASTA LAKE | V-LONG AT FLANGE N/....LEAK AT FITTING
| 09-80106-1 | 402 | 36.23 | [8 empty] | 2009-05-23 | 2009-05-23 |  |  |  |  | MOUNTAIN GATE | NORTH AND SOUTH BOXES; SOUTH BOX; SOUTH BOX
| 09-80106-1 | 402 | 36.23 | 2 | [7 empty] | 2009-05-23 | 2009-05-23 |  |  |  |  | MOUNTAIN GATE
| 09-80107 | 402 | 30.68 | 4 | Transmission >= 20% SMYS |  | Line Valve |  |  | Equipment Malfunction |  | 2009-05-26 | 2010-11-18 | Replace Valve >= 2 inch | REPLACE DIST MAIN <100FT - REPLACE | Steel-Other |  | REDDING | REPLACE VALVE 250 N/W VALVE; REPLACED 118"4" STL VALVE 250 INSTALLED INSOLATOR & 8'4" 10" STL MAIN
| 09-80107-1 | 402 | 30.68 | [8 empty] | 2009-05-26 | [5 empty] | REDDING | VALVE 250-N.W VALVE; VALVE 250; VALVE 250; VALVE 250; VALVE 250
| 09-80107-1 | 402 | 30.68 | [8 empty] | 2009-05-26 | [5 empty] | REDDING | VALVE 250-N/W VALVE; VALVE 250; VALVE 250; VALVE 250
| 09-80107-1 | 402 | 30.68 | 4 | [7 empty] | 2009-05-26 | [5 empty] | REDDING | 5/26 LEAK ON V-FLANGES
| 09-80108-1 | 402 | 31.72 | [8 empty] | 2009-05-23 | [5 empty] | REDDING | EAST BOX; EAST BOX; EAST BOX
| 09-80108-1 | 402 | 31.72 | 0.75 | [7 empty] | 2009-05-23 | [5 empty] | REDDING | 5/23 LEAK AT FITTING
87 | 09-80109-1 | 1015-06 | 32.87 | [8 empty] | 2009-05-23 | [5 empty] | SHASTA LAKE CITY | NORTH AND SOUTH BOXES; NO LEAKS
| 09-80110-1 | 402/DFM | 16.73 | 0.25 | Transmission |  | Valves |  |  | Other | LOOSE METRIC | 2009-05-03 | 2009-11-19 | Other | TIGHTEN FITTING | Steel/Wrought Iron |  | REDDING | TIGHTENED METRIC VALVE CORE; SOAP TESTED OK CXCP
| 09-80110-1 | DFM | 16.73 | [8 empty] | 2009-06-03 | [5 empty] | REDDING
| 09-80111-1 | 402/DFM | 21.41 | 6 | Transmission |  | Valves |  |  | Other | GREASE | 2009-06-03 | 2010-01-14 | Other | GREASE | Steel/Wrought Iron |  | REDDING
| 09-80111-1 | DFM | [9 empty] | 2009-06-03 | [5 empty] | REDDING | VALVE 218 AND SOUTH BOX; VALVE218 AND SOUTH BOX; NO LEAK
| 09-80112-1 | DFM | [9 empty] | 2009-06-03 | [5 empty] | REDDING
| 09-80116-1 | 402/DFM | 23.99 | 3 | Transmission |  | Valves |  |  | Other |  | 2009-06-03 | 2010-06-10 | Other | GREASED; | Steel/Wrought Iron |  | REDDING | SOAP TEST
| 09-80116-1 | 402/DFM | 23.99 | [8 empty] | 2009-06-03 | [5 empty] | REDDING | VALVE 225 & 331; CHECK 225
87 | 09-80117-1 | 1015-03 | 23.99 | [8 empty] | 2009-06-03 | [5 empty] | REDDING | ALL 3 REG BOXES; 1ST STAGE; NO LEAK FOUND
| 09-80117-1 | 402/DFM | 23.99 | [8 empty] | 2009-06-03 | [5 empty] | REDDING | ALL 3 REG BOXES; 1ST STAGE
| 09-80196-1 | 402 | 35.83 | [8 empty] | 2009-09-24 | [5 empty] | MOUNTAIN GATE | SOUTH BOX; NO LEAK
| 09-80196-1 | 402 | 35.83 | [8 empty] | 2009-09-24 | [5 empty] | MOUNTAIN GATE
| 09-80199-1 | 402 | 29.36 | [8 empty] | 2009-09-29 | [5 empty] | REDDING | NO LEAK
| 09-80199-1 | 402 | 29.36 | [8 empty] | 2009-09-29 | [5 empty] | REDDING
87 | 09-80200-1 | 402 | 28.78 | [8 empty] | 2009-09-29 | [5 empty] | REDDING | SOUTH BOX; SOUTH BOX; SOUTH BOX; SOUTH BOX
| 09-80200-1 | 402 | 28.78 | [8 empty] | 2009-09-29 | [5 empty] | REDDING | SOUTH BOX; SOUTH BOX
| 09-80200-1 | 402 | 28.78 | [8 empty] | 2009-09-29 | [5 empty] | REDDING
| 09-80201-1 | 402 | 27.98 | [8 empty] | 2009-09-29 | [5 empty] | REDDING | VLAVE27.98; NO LEAK FOUND
| 09-80201-1 | 402 | 27.98 | [8 empty] | 2009-09-29 | [5 empty] | REDDING
87 | 09-80202-1 | 1015-07 | 30.68 | [8 empty] | 2009-09-24 | [5 empty] | REDDING | SOUTH BOX; SOUTH BOX
| 09-80202-1 | 402 | 30.68 | [8 empty] | 2009-09-24 | [5 empty] | REDDING
| 09-80203-1 | 402 | 30.68 | [8 empty] | 2009-09-24 | [5 empty] | REDDING | S/E VALVE; NO LEAK FOUND
| 09-80203-1 | 402 | 30.68 | [8 empty] | 2009-09-24 | [5 empty] | REDDING
| 10-80186-1 | 402/SVC | 38.15 | 8 | Transmission |  | Valves |  |  | Unknown | OTHER | 2010-05-20 | 2010-06-10 | Other | GREASED | Steel/Wrought Iron |  | MOUNTAIN GATE | SOAP TEST
| 10-80186-1 | 402/SVC | 38.15 | [8 empty] | 2010-05-20 | [5 empty] | MOUNTAIN GATE
| 10-80187-1 | 402 | 27.58 | 10 | Transmission |  | Valves |  |  | Other | NEEDED GREASE | 2010-05-25 | 2010-05-26 | Other | GREASE | Steel/Wrought Iron |  | REDDING | BRIDGE VALVES AT HILLTOP AND DEPPERTRUE, SOAP TEST
| 10-80188-1 | 402 | 27.98 | 10 | Transmission |  | Valves |  |  | Other | NEEDED GREASE | 2010-05-25 | 2010-05-26 | Other | GREASE | Wrought Iron |  | REDDING | BRIDGE VALVE CLUSTER FOR HILLTOP TAP. SOAP TEST
| 10-80189-1 | 402 | 27.98 | 10 | Transmission |  | Valves |  |  | Other | NEEDED GREASE | 2010-05-25 | 2010-05-26 | Other | GREASE | Steel/Wrought Iron |  | REDDING | BRIDLE VALVE CLUSTER FOR HILLTOP AND PEPPER TREE, SOAP PEST
87 | 10-80190-1 | 402 | 28.78 | [8 empty] | 2010-05-25 | [5 empty] | REDDING | NORTH BOX; NORTH BOX; NORTH BOX
| 10-80190-1 | 402 | 28.78 | [8 empty] | 2010-05-25 | [5 empty] | REDDING
87 | 10-80191-1 | 1015-02 | 22.12 | [8 empty] | 2010-05-25 | [5 empty] | REDDING | VENT; NO LEAK FOUND
| 10-80191-1 | 402 | 22.12 | [8 empty] | 2010-05-25 | [5 empty] | REDDING
87 | 10-80192-1 | 1015-02 | 22.12 | [8 empty] | 2009-05-25 | [5 empty] | REDDING | NORTH BOX; NO LEAK FOUND
| 10-80192-1 | 402 | 22.12 | [8 empty] | 2010-05-25 | [5 empty] | REDDING
| 10-80193-1 | 402 | 18.42 | [8 empty] | 2010-05-25 | [5 empty] | ANDERSON
| 10-80194-1 | 402 | 16.73 | [8 empty] | 2010-05-25 | [5 empty] | ANDERSON
87 | 10-80195-1 | 1035-02 | 16.73 | [8 empty] | 2010-05-25 | [5 empty] | ANDERSON | WEST BOX; NO LEAK FOUND
| 10-80195-1 | 402 | 16.73 | [8 empty] | 2010-05-25 | [5 empty] | ANDERSON
87 | 10-80196-1 | 402 | 14.76 | [8 empty] | 2010-05-25 | [5 empty] | ANDERSON | MIDDLE BOX; NO GAS FOUND
| 10-80196-1 | 402 | 14.76 | [8 empty] | 2010-05-25 | [5 empty] | ANDERSON
| 10-80197-1 | DFM | [9 empty] | 2010-05-25 |  |  |  | Wrought Iron |  | SHASTA LAKE
87 | 10-80198-1 | 402/DFM | [9 empty] | 2010-05-25 | [5 empty] | SHASTA LAKE CITY | NORTH BOX; NO GAS FOUND
| 10-80198-1 | DFM | [9 empty] | 2010-05-25 | [5 empty] | SHASTA LAKE
87 | 10-80200-1 | 1015-03 | 23.99 | [8 empty] | 2010-05-25 | [5 empty] | REDDING | SECOND STAGE; SECOND STAGE
| 10-80200-1 | 402/DFM | 23.99 | [8 empty] | 2010-05-25 | [5 empty] | REDDING
| 10-80203-1 | 402/SVC | 38.15 | 8 | Transmission |  | Valves |  |  | Other | NEED GREASE | 2010-05-20 | 2010-06-15 | Other | GREASE VALVE | Steel/Wrought Iron |  | MOUNTAIN GATE | GREASE VALVE; SOAP TEST AFTER VALVE GREASING
| 10-80203-1 | 402/SVC | 38.15 | [8 empty] | 2010-05-20 | [5 empty] | MOUNTAIN GATE
| 10-80210-1 | DFM/402 | 21.41 | 4 | Transmission |  | Valves |  |  | Unknown |  | 2010-06-01 | 2010-06-17 | Other | GREASE OPERATE | Steel/Wrought Iron |  | REDDING | SOAP TESTED, OPERATED, GREASED, PAINTED; SEE MAP ON BACK
| 10-80223-1 | 402 | 31.72 | [8 empty] | 2010-06-17 | [5 empty] | REDDING
87 | 10-80496-1 | 402/DFM | 16.09 | 6 | Transmission >= 20% SMYS |  | Line Valve | Fitting |  | Other Natural Forces | OTHER | 2010-12-16 | 2010-12-17 | Greased - Other |  | Steel-Other |  | ANDERSON | GREASED AND OPERATED VALVE; I AM NOT A CREW LEADER
87 | 10-80497-1 | DREG5485 | 0.53 | [8 empty] | 2010-12-14 | [5 empty] | SHASTA LAKE CITY | NORTH REG BOX; NO LEAK
87 | 10-81201-1 | DREG5485 | 0.51 | 6 | Transmission >= 20% SMYS |  | Other |  | GREASE FITTING | Other | LACK OF GREASE | 2010-10-13 | 2011-01-07 | Greased - Other |  | Steel-Other |  | SHASTA LAKE CITY | GREASE FITTING W.A. LEAING CREW GREASED VALVE; GREASE FITTING IN VALVE #253 WAS LEAKING. VALVED WAS GREASED, SOAP TEST APPLIED
| 10-88001-1 | 1042-01 | 0.01 | 0.75 | Transmission |  | Valves |  |  | Other | LOOSE GAUGE TAP | 2010-10-14 | 2011-01-25 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | FALL RIVER | SOAP TEST OK...
87 | 10-88039-1 | 402 | 34.47 | 0.75 | Distribution Main >60 PSIG and <20% SYMS |  | Other Mechanical Joint |  |  | No/Deteriorated Pipe Dope |  | 2010-10-18 | 2011-02-28 | Other | WELDED CAPS | Steel-Other |  | REDDING | C/O BYPASS TO ELIMINATE LEAK ON HIGHT TO HIGH SET; WELDED 3/4" AND 1" CAPS ON HIGH TO HIGH SET (ABOVE GROUND SET) TO ELIMINATE LEAK
| #NAME? | DFM |  | 6 | Transmission >= 20% SMYS |  | Threads |  |  | Other | TIGHTEN LOOSE THREADS |  | 2011-02-08 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | BURLINGAME | TIGHTEN THREADS ON FITTING
| 08-20287-1 | L101 | 30.41 | 6 | Transmission |  | Other |  | VALVE | Other | GREASED VALVE | 2005-05-10 | 2008-07-18 | Other | GREASE VALVE. | Other |  | BURLINGAME
| 10-60217- |  |  | 2 | Distribution Main |  | Longitudinal Weld |  |  | External Corrosion |  | 2010-10-19 | 2010-11-16 | Replace Dist Main < 100 ft |  | Steel/Wrought Iron |  | SAN MATEO | REPLACE 1' OF 2'" STEEL MAIN WITH SAME
| 08-25018-1 | 132 | 0 | 30 | Transmission |  | Valves |  |  | Other | GREASE NIPPLE | 2008-09-17 | 2010-02-17 | Other | GREASE VALVE | Steel-Other |  | HILLSBOROUGH | GREASE VALVE TO STOP LEAK; GREASE VALVE#177
| 09-20287-1 | T 132 | 32.32 | 2 | Transmission |  | Valves |  |  | Other |  | 2009-10-01 | 2009-10-14 | Other | GREASE VALVE | Steel/Wrought Iron |  | HILLSBOROUGH | GREASE 2" TRANSMISSION VALVE; GREASED VALVE, SOAP TESTED
| 10-60281-A | 132 |  | 2 | Distribution Main > 60 PSIG |  | Line Valve |  |  | Construction Defect |  | 2010-11-23 | 2010-11-24 | Greased - Other |  | Steel-Other |  | HILLSBOROUGH | GREASE VALVE
| 08-20299-1 | 0210-01 |  | 2 | Single Service | TRANSMISSION | Valves |  |  | Other | GREASE VALVE | 2008-05-14 | 2009-02-04 | Other | GREASED VALVE | Steel-Other |  | HALF MOON BAY | GREASE VALVE
| 08-20300-1 | 0210-01 |  | 2 | Transmission |  | Fitting |  |  | Other |  | 2008-05-14 | 2009-02-20 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | HALF MOON BAY | REPAIRED LEAKS ON H TO H SET
| 07-20411-1 | 0209-01 |  | 2 | Transmission |  | Valves |  |  | Other | GREASED | 2007-12-15 | 2008-12-29 | Other | GREASED VALVE | Steel-Other |  | SAN MATEO | GREASE VALVE
| 07-20411- | [10 empty] | 2007-12-15 | [5 empty] | BELMONT
| 08-25019-1 | 109 | 30.55 | 3 | Transmission |  | Valves |  |  | Other | GREASE NIPPLE | 2008-09-17 | 2010-02-15 | Other | GREASED VALVE | Steel-Other |  | SAN MATEO | GREASE VALVE TO STOP LEAK
| 08-20579- | 109 |  | 1.5 | Transmission |  | Tap Connection |  |  | Other |  | 2007-10-09 | 2008-10-02 | Other | TIGHTENED CAP | Steel/Wrought Iron |  | BELMONT | TIGHTEN METER CAP
| 10-20051-1 | 101 |  | 0.75 | Transmission |  | Drip | Valves |  | Other | VALVE | 2010-03-10 | 2010-03-12 | Other | GREASE VALVE & TIGHTEN PLUG | Steel-Other |  | BELMONT | GREASE VALVE & TIGHTEN PLUG
| 09-20060- |  |  | 8 | Transmission |  | Other |  | 3/4" PLUG | Unknown |  | 2009-03-17 | 2009-06-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | REDWOOD CITY | TIGHTEN 3/4" PLUG; 3/4" OPLUG ON 8" LEAKING AT THREADS. BACKEDOFF AND REDOPE
|  | 0214-01 |  | 0.08 |  |  | Other |  | 3/4" PLUG ON 8" MUELLER TOP FLANGE |  |  |  | 2009-06-01 | Tighten Cap or Bolt | 3/4" PLUG |  |  |  | FOUND LEAK AT 3/4" PLUG ON TOP OF 8" MUELLER FLANGE
| 09-20072-1 | 147 |  | 6 | Transmission |  | Valves |  |  | Other | VALVE STEM | 2009-03-27 | 2009-05-07 | Other | GREASE VALVE. | Steel/Wrought Iron |  | SAN CARLOS | GREASE VALVE 285 LEAK STOPPED
| 09-20071-1 | 147 | 2.35 | 25 | Transmission |  | Body of Pipe | Other | 1/4 WELDED PIPE | External Corrosion |  | 2009-03-27 | 2009-06-13 | Welded Sav-A-Valve - Weld |  | Steel/Wrought Iron |  | SAN CARLOS | ABANDONED GAUGE TAP; INSTALLED NEW SAV-A VALVE GAUGE TAP
| 09-20076-1 | L109 |  | 2 | Transmission |  | Valves |  |  | Other | GREASE VALVE | 2009-03-30 | 2009-04-02 | Other | GREASE VALVE 245 | Steel/Wrought Iron |  | MENLO PARK | GREASE VALVE 245
2 | 96-60145- | 109-132-&147 |  | 10 | Transmission |  | Valves |  |  | Material Failure |  | 1996-07-13 | 1996-07-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | WOODSIDE | TIGHTEN BOLTS ON 10" VALVE AND PACK VALVE WITH GREASE
| 05-60415- | 101 | 19.43 | 0.75 | Transmission |  | Fitting |  |  | Construction Defect |  | 2005-12-10 | 2005-12-13 | Other | INSTALLED PLUG | Steel/Wrought Iron |  | REDWOOD CITY | REMOVED GAUGE & INSTALLED PLUG
| 10-20045- | DFM |  | 0.5 | Transmission |  | Valves |  |  | Other | 1/2" PLUG | 2010-03-04 | 2010-03-19 | Other | TIGHTEN PLUG | Steel-Other |  | MENLO PARK | TIGHTEN 1/2" PLUG ON TAP
| 08-20668- | 132 |  | 02.00" | Transmission | REG STATION | Fitting | Other | S/S FITTING | Other |  | 2008-09-29 | 2008-12-03 | Other | TIGHTEND S/S FITTING GREASED VALVE | Steel/Wrought Iron |  | ATHERTON | LEAK ON S/S FITTING; LEAK ON FILTER; GREASE VALVE; TIGHTEN S/S FITTING GREASE VALVE
| 08-20668-1 | 132 |  | 2 | Transmission |  | Fitting |  |  | Other |  | 2008-12-03 | 2008-12-03 | Other |  | Steel/Wrought Iron |  | ATHERTON | K ON S/S FITTING LEAK ON FILTER GR
| 08-20638-1 | 132 |  | 2 | Transmission |  | Fitting |  |  | Other |  | 2008-09-29 |  |  |  | Steel/Wrought Iron |  | ATHERTON | LEAK ON BOTH REG. PITS AND VALVE BOX OMIT NO LEAK FOUND. REG PIT LEAK REPAIRED LEAK
| 08-20306-1 | WALSH DFM |  | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2008-05-21 | 2010-09-30 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | ATHERTON | INSTALLED 1-4" PLIDCO CLAMP
| 03-60335- | 109 | 16 | 22 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2003-12-16 | 2003-12-17 | Patch Weld - Weld |  | Steel/Wrought Iron |  | PALO ALTO | WELDED IN POSITION
|  | 109 | 16 | [12 empty] | Steel/Wrought Iron |  | PALO ALTO | 1ST INSPECTION AREA ON A FORM; 2ND INSPECTION AREA COVERS; DIFFERENT COATING TYPE 18' S E OF REPAIR
| 10-60185- | 132 |  | 2 | Transmission |  | Valves |  |  | Construction Defect |  | 2010-09-23 | 2010-09-24 | Other | GREASED VALVE | Steel/Wrought Iron |  | STANFORD | GREASE PLUG VALVE
| 10-20010-1 | 132 | 0.19 | 0.5 |  |  | Other |  | SENCE LINE | Unknown |  | 2010-01-25 | 2010-03-05 | Other | TIGHTEN FITTING | Other | STAINLESS STEEL | STANFORD | TIGHTEN 1/2" SENCE LINE IN DOWNSTREAM PIT
| 11-60093-B |  |  | 1 | Distribution Main <= 60 PSIG |  | Tap Connection |  |  | Damage by Earth Movement |  | 2011-03-08 | 2011-04-07 | Replace Partial Service |  | PE2406 (Yellow or Orange) |  | PORTOLA VALLEY | REPLACE 11/2 OF 1" PLASTIC GAS SERVICE TESTED. REMOVED BROKEN STRESS BENT 1" PL FROM TRANSITION FITTING AT TEE TIED IN AND RESTORED SERVICE
| 09-20079- |  |  | 24 | Transmission |  | Other |  | FLANGE | Other |  | 2009-03-31 | 2009-04-07 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | STANFORD | TIGHTENED PLUG
| 10-60186- | 109 |  | 0.25 | Transmission |  | Fitting |  |  | Construction Defect |  | 2010-09-23 | 2010-09-27 | Other | REDOPE 1/4" PLUG | Steel/Wrought Iron |  | STANFORD | REDOPE 1/4" PLUG ON GAUGE TAP
| 09-20083- | L132 |  | 24 | Transmission |  | Other |  | VALVE | Other | GREASE WAS DRY | 2009-03-31 | 2009-04-03 | Other | GREASE VALVE | Steel/Wrought Iron |  | STANFORD | REPAIR WITH VALVE GREASE
| 09-20082- | L109 |  | 0.25 | Transmission |  | Other |  | METRIC VALVE | Other |  | 2009-03-31 | 2009-04-08 | Replace Main Valve < 2-inch |  | Other |  | STANFORD | REPLACED A LEAKING A 1/4" METRIC VALVE WITH A 1/4" BALL VALVE. ITS FUNCTION IS ONLY FOR GAUGING
| 09-10003-1 | 132 |  | 2 | Transmission |  | Valves |  |  | Construction Defect |  | 2009-03-31 | 2009-04-02 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | BRISBANE | TIGHTEN 2" PLUG
| 09-20058- | LINE 101 |  | 8 | Transmission |  | Fitting |  |  | Construction Defect |  | 2009-03-17 | 2009-04-06 | Tighten Cap or Bolt | PLUG | Steel/Wrought Iron |  | BRISBANE | TIGHTEN 3/4" PLUG ON 8" FLANG
| 09-10002-1 | 147 |  | 24 | Transmission |  | Valves |  |  | Other | GREASED VALVE | 2009-03-27 | 2009-04-01 | Other | GREASED VALVE | Steel/Wrought Iron |  | DALY CITY | GREASED VALVE IN REG PIT
| 98-30157- |  |  | 20 | Transmission |  | Body of Pipe |  |  | Digin |  | 1998-09-11 | 1998-09-11 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | DALY CITY | WORKED 20" BAND
| 05-30097- | 109 |  | 12 | Transmission |  | Fitting |  |  | Construction Defect |  | 2005-05-06 | 2005-05-19 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | DALY CITY | WELDED 6" CAN OVER LEAKING 3" HOMEMADE CAN
| 05-30108-1 | 109 |  | 12 | Transmission |  | Fitting |  |  | Construction Defect |  | 2005-05-19 | 2005-05-19 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | DALY CITY | WELDED 6" CAN OVER LEAKING 3" HOMEMADE CAN
| 10-30137- | 132 |  | 0.375 | Transmission |  | Mechanical Joint |  |  | Construction Defect |  | 2010-10-06 | 2010-10-06 | Other | TIGHTEN STAINLESS STEEL FITTING | Other | SSTL | DALY CITY | TIGHTEN STAINLESS STEEL FITTING
| 09-30255-1 | 132 | 42.99 | 30 | Transmission |  | Girth Weld |  |  | Weld Failure |  | 2009-11-16 |  | Welded Sleeve/Can - Weld | Type B Sleeve | Steel/Wrought Iron |  | SOUTH SAN FRANCISCO | INSTALLED 30" .625 WT X 60 SLEEVE CODE 02-1111 FULL ENCIRCLEMENT; LEAK ORIGINALLY THOUGHT TO BE ON ADJACENT DISTRIBUTION LINE. DISCOVERED ON TL 11/27/2010
| 09-30255- | [10 empty] | 2009-11-16 | [5 empty] | SOUTH SAN FRANCISCO | WAITING FOR SAMPLE
| 10-70001-1 | 132 |  | 30 | Transmission |  | Unknown |  |  | Unknown |  | 2010-09-09 | 2010-09-09 | Other | CLOSED VALVES | Steel/Wrought Iron |  | SAN BRUNO | INFORMATION PROVIDED BY GAS SVPT JOH CORONO ON SITE INCIDENT COMMANDER
56 | 11-30019-1 |  |  | 2 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2011-01-21 | 2011-04-08 | Skinner Clamp - Clamp |  | Steel-Other |  | SAN BRUNO | LEAK OF MAIN; REPAIR GAS MAIN WITH A TWO BOLT SKINNER CLAMP
| 08-20060- | 13-7-F14 |  | 2 | Transmission |  | Valves |  |  | Other | GREASE STEM | 2008-05-25 | 2008-05-28 | Other | GREASED VALVE | Steel/Wrought Iron |  | SAN BRUNO | GREASED VALVE #1466, LEAK STOPPED
| 08-20060- | 109 |  | 2 | Transmission |  | Valves |  |  | Other | GREASED STEM | 2008-05-25 | 2008-05-28 | Other | GREASED VALVE |  |  | SAN BRUNO | GREASED VALVE #1466, LEAK STOPPED. VALVE IN PIT
| 09-10102- | 132 |  | 24 | Transmission |  | Valves |  |  | Other |  | 2009-09-01 | 2009-09-23 | Other | GREASED VALVE | Steel/Wrought Iron |  | SAN BRUNO | GREASED VALVE. MAIN BURIED
56 | 94-25020-1 |  |  | 16 | Transmission |  | Valves |  |  | Other |  | 1994-08-25 | 1995-10-30 | Other |  | Steel/Wrought Iron |  | SAN BRUNO | EVII MULTI. TURN VALVE NO READINGS WITH GAS SCOPE.
56 | 96-30192-1 |  |  | 8 | Transmission |  | Valves |  |  | Other |  | 1996-10-04 | 1996-10-09 | Other |  | Steel/Wrought Iron |  | SAN BRUNO | REPAIRED LEAK ON VALVE
| 09-10109-1 | 101 | 33.68 | 0.25 | Transmission |  | Fitting |  | SS FITTINGS REGULATORS DIAPHRAMS | Construction Defect |  | 2009-09-22 | 2009-10-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN BRUNO | TIGHTENED TUBE FITTINGS
| 08-11005-1 | 132 | 914 | 8 | Transmission |  | Valves |  |  | Other | GREASED VALVE | 2008-09-03 | 2010-01-19 | Other | GREASED VALVE | Steel-Other |  | PACIFICA | VALVE 914 ON TRANSMISSION IN VALVE BOX; GREASED VALVE
| 99-30059- | 101 |  | 20 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party |  | 1999-03-15 | 1999-04-03 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | MILLBRAE | LOMITA PARK PUMP STATION OVER TRANS. LINE; WELDED 20"X18 SPLIT SLEEVE
58 | 97-20381-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1997-07-29 | 1997-08-11 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | BURLINGAME | COULDN'T CLAMP ODD SIZE PIPE. HAD WELD PATCH OVER 3 PITS ON MAIN
82 | 75-40168- |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1975-11-21 | 1975-11-21 | Clamp |  | Steel/Wrought Iron |  | SAN MATEO | INSTALLED 3/4" LEAK CLAMP ON BLOW OFF TO OIL DRIP. BAR TESTED AREA AND FOUND NO OTHER INDICATION OF LEAKAGE
| 11-60099-B |  |  | 02.00" | Distribution Main <= 60 PSIG |  | Line Valve |  |  | Other | DRIED GREASE | 2011-03-16 | 2011-03-22 | Greased - Other |  | Steel-Other |  | SAN MATEO | INLET REGULATOR VALVE. GREASE VALVE-FIXED LEAK
| 10-60113- | 210-1 | 4.99 | 0.75 | Single Service |  | Regulator |  |  | Equipment Malfunction |  | 2010-06-29 | 2010-07-02 | Other | REPLACE REGULATOR | Steel/Wrought Iron |  | HALF MOON BAY | REPLACED REGULATOR TO FIX LEAK
| 09-20073-1 | 210 | 4.6 | 3/4" | Distribution Main |  | Fitting |  |  | Other | PIPE DOPE | 2009-03-25 | 2010-07-30 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | HALF MOON BAY | NO GREASE
| 08-20304-1 | [10 empty] | 2008-05-19 | [5 empty] | HALF MOON BAY | IN REG PIT/HIGH TO HIGH SET NO LEAK FOUND
| 08-20303-1 | [10 empty] | 2008-05-14 | [5 empty] | HALF MOON BAY | NO LEAKS FOUND
| 08-20301-1 | [10 empty] | 2008-05-14 | [5 empty] | HALF MOON BAY | NO LEAKS FOUND
| 08-20300-1 | 0210-01 |  | 02.00" | Transmission |  | Fitting |  |  | Other |  | 2008-05-14 | 2009-02-20 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | HALF MOON BAY | REPAIRED LEAKS ON H TO H SET
| 08-20298-1 | [10 empty] | 2008-05-14 | [5 empty] | HALF MOON BAY | SECTION IN DRAWER IS MISSING. HEAD TO FILE (FIND THE FOLDER)
| 08-20291- | [5 empty] | Fitting | Other | RELIEF | Other |  | 2008-05-13 | 2008-05-13 | Other |  |  |  | HALF MOON BAY | REPAIRED LEAK ON METERIC VALVE/CORRECTED & PERFORMED MAINT ON H-202
| 08-20291- |  |  |  | Transmission |  | Fitting | Other | RELIEF | Other |  | 2008-05-13 | 2008-05-13 | Other |  | Steel/Wrought Iron |  | HALF MOON BAY
| 10-60285- | 132 |  | 2 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | External Corrosion |  | 2010-12-10 | 2010-12-20 | Patch Weld - Weld |  | Steel-Other |  | SAN MATEO | REPAIRED 2" TRANS FEEDERMAIN FEED H TO H 40' S/AT MAIN LOCATION. INSTALLED 2" PCF WELDED WASH OVER ALL PITTED AREAS TO MAKE REPAIRS AND ELEMINATE LEAKS
| 11-60188-A |  |  | 0.75 | Single Service |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2011-06-21 | 2011-06-21 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | BELMONT | REDOPE CAP
|  |  |  | 8 | Distribution Main |  | Valves |  |  | Construction Defect |  | 2007-09-12 | 2007-09-12 | Other | GREASED VALVE | Steel/Wrought Iron |  | REDWOOD CITY | GREASED MAIN VALVE
| 08-20282-1 | [10 empty] | 2008-05-04 | [5 empty] | BELMONT | NO READS. OMIT
| 10-20144- | 0207-01 |  |  | Transmission |  | Valves |  | REG STATION | Other |  | 2010-09-12 | 2010-09-12 | Other | GREASE VALVE | Steel/Wrought Iron |  | REDWOOD CITY | TIGHTEN PLUG ON FILTER
| 95-80213- |  |  | 2 | Transmission |  | Other |  |  | Other |  | 1995-10-07 | 1995-10-17 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EAST PALO ALTO | TIGHTEN CAP TO 2" STL BOTTOM TAP
| 08-20306-1 | WALSH DFM |  | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2008-05-21 | 2010-09-30 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | ATHERTON | INSTALLED 1-4" PLIDCO CLAMP
| 10-60171- |  |  | 2 | Transmission >= 20% SMYS |  | Line Valve |  |  | Construction Defect |  | 2010-09-16 | 2010-12-01 | Greased - Other |  | Steel-Other |  | MENLO PARK | GREASE VALVE, STOPPED LEAK
| 09-20078-1 | L109 |  |  | Transmission |  | Valves |  |  | Other | GREASE VALVE | 2009-03-03 | 2009-04-02 | Other | GREASE VALVE | Steel/Wrought Iron |  | MENLO PARK | GREASE VALVE 303
| 10-60189- | 132 |  |  |  |  | Fitting |  |  |  |  | 2010-09-23 | [5 empty] | STANFORD | VALVE 15.71; VALVE STREAM
| 09-20081- | 109 | 16.51 | 22 | Transmission |  | Other |  | FLANGE | Other |  | 2009-03-31 | 2009-04-07 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | STANFORD | REG PIT SCADA SIT T.L.109; TRANSFERED PLUG ON 1/4 VALVE. TIGHTENED PLUG
58 |  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | BAYSHORE
|  |  |  | 0.3 | Transmission | [6 empty] | 2002-11-26 |  |  |  | Steel/Wrought Iron |  | BURLINGAME
|  |  |  | 2 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | SAN MATEO
|  | DFM 10 |  | 10 | Transmission | [6 empty] | 2004-11-29 |  |  |  | Steel/Wrought Iron |  | SAN MATEO
|  |  |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN MATEO | COVER 102' NO VISUAL-WET SAND
|  | 101 |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | POT HOLE FOR SEWER REPLACEMENT
|  |  |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  |  | 8 | Transmission | [6 empty] | 1989-09-14 |  |  |  | Steel/Wrought Iron |  | SAN MATEO
|  |  |  | 0.08 | Transmission | [10 empty] | Steel/Wrought Iron |  | HALF MOON BAY
[16 empty] | Steel/Wrought Iron |  | HALF MOON BAY
|  | 132 | 4.81 | 0.08 | Distribution Main | Transmission | [9 empty] | Steel/Wrought Iron |  | HALF MOON BAY
|  | 0210-01 | 4.65 | 0.08 | Transmission | [10 empty] | Steel/Wrought Iron |  | HALF MOON BAY | LINE 132
|  | 132 |  | 0.08 | Transmission | Distribution Main | [9 empty] | Steel/Wrought Iron |  | HALF MOON BAY
|  |  |  | 0.05 | Single Service | [10 empty] | Copper |  | SAN MATEO
|  |  |  | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | BELMONT | INSTALL 3/4" STEEL GAS SERVICE OFF 4" STELL FEEDER MAIN; INSTALLED 12'X3/4" SEAMLESS PIPE AND HIGH TO HIGH REG STATION
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | BELMONT | INSTALL 2-32# ANODES-2 WIRES ON MAIN AND G-5 FRAME COVER
58 |  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  |  | 0.24 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN CARL0S | RE-LOCATE VENT STACK DUE TO POPOSED DRIVEWAY (SEE SKETCH ON BACK) 24" T.P. LINE 101 AS BUILT ATTACHED
|  | 147 |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN CARLOS | IN FRONT OF 2238 BRITLAN AVE
82 |  |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1979-07-19 | 1979-07-19 | Clamp |  | Steel/Wrought Iron |  | REDWOOD CITY
|  |  |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | REDWOOD CITY
2 |  |  |  | 2 | [11 empty] | Steel/Wrought Iron |  | REDWOOD CITY
|  | 101 |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | REDWOOD CITY
|  | 101 |  | 20 | Transmission | [6 empty] | 2004-12-03 |  |  |  | Steel/Wrought Iron |  | MENLO PARK
[16 empty] | TR 418 |  | EAST PALO ALTO | INSTALLED NEW 1/2" PLASTIC GAS SERVICE
56 | 90-20265-1 | [10 empty] | 1990-11-16 | [5 empty] | BROADMOOR
56 | 90-20067-1 | [10 empty] | 1990-02-09 | 1991-01-26 |  |  |  |  | DALY CITY | NO LEAKS W/JW
|  | 132 | 45.59 | [8 empty] | 2000-06-12 | 2000-06-14 | Other | WRAP | Steel/Wrought Iron |  | DALY CITY | WRAP MAIN
56 | 94-30143-1 | [10 empty] | 1994-07-06 | [5 empty] | SOUTH SAN FRANCISCO
56 | 91-20664-1 |  |  | 4 | Distribution Main |  | Valves |  |  | Other |  | 1991-09-05 | 1992-07-27 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SOUTH SAN FRANCISCO | REPAIRED PIPING IN PIT
| 08-30087- | 101 | 33.94 | [8 empty] | 2008-06-18 | [5 empty] | SAN BRUNO
| 08-30087- | 101 | 33.94 | [8 empty] | 2008-06-18 | [5 empty] | SAN BRUNO | NO LEAKS. TRANSMISSION LINE
|  | 132 | 43.54 | 30 | Transmission >= 20% SMYS | [10 empty] | Steel-Other |  | SOUTH SAN FRANCISCO | PIPE TO SOIL READ BY GE CORP
|  | 132 | 43.56 | 30 | Transmission >= 20% SMYS | [10 empty] | Steel-Other |  | SOUTH SAN FRANCISCO
|  | 132 | 43.59 | 30 | Transmission >= 20% SMYS | [10 empty] | Steel-Other |  | SOUTH SAN FRANCISCO
|  | 132 | 43.6 | 30 | Transmission >= 20% SMYS | [10 empty] | Steel-Other |  | SOUTH SAN FRANCISCO
|  | 132 | 43.56 | 30 | Transmission >= 20% SMYS | [10 empty] | Steel-Other |  | SOUTH SAN FRANCISCO | PIPE TO SOIL READ BY GE CORP
|  |  |  | 30 | Transmission |  |  |  |  | Other | NONE |  | 2001-11-20 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SOUTH SAN FRANCISCO | G.C. CREWS WELDED 30"X18" SLEEVE
|  | 132 | 42.19 | 30 | Transmission >= 20% SMYS | [10 empty] | Steel-Other |  | SOUTH SAN FRANCISCO | PIPE TO SOIL READ BY GE CORP
|  | 132 | 42.34 | 30 | Transmission >= 20% SMYS | [10 empty] | Steel-Other |  | SOUTH SAN FRANCISCO
|  | 132 | 42.08 | 30 | Transmission >= 20% SMYS | [10 empty] | Steel-Other |  | SOUTH SAN FRANCISCO | PIPE TO SOIL READ BY GE CORP
|  | 132 | 41.6 | 30 | Transmission >= 20% SMYS | [10 empty] | Steel-Other |  | SOUTH SAN FRANCISCO
|  | 132 | 41.32 | 30 | Transmission >= 20% SMYS | [10 empty] | Steel-Other |  | SOUTH SAN FRANCISCO | PIPE TO SOIL READ BY GE CORP
|  | 132 | 40.08 | 30 | Transmission >= 20% SMYS | [10 empty] | Steel-Other |  | SOUTH SAN FRANCISCO
|  |  | 40.05 | [12 empty] | Steel/Wrought Iron |  | SAN BRUNO | 24"TO 30" ???? & APPROX 10' OF 30" PIPE REMOUNT
|  | 132 | 40.05 | 30 | Transmission >= 20% SMYS | [10 empty] | Steel-Other |  | SAN BRUNO | PIPE TO SOIL READ BY GE CORP
|  | 132 | 40.08 | 30 | Transmission >= 20% SMYS | [10 empty] | Steel-Other |  | SAN BRUNO | PIPE TO SOIL READ BY GE CORP
|  |  |  | 6 | Transmission |  | Fitting |  |  | Other | THREADS | 2010-10-29 |  |  |  | Steel/Wrought Iron |  |  | THREADS LEAKING ON GREAE TUBE WERE IT ENTERS
|  | 109 |  | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN BRUNO
|  | 132 |  | 36 | Transmission | [7 empty] | 2010-10-09 | Other | BUFFING | Steel/Wrought Iron |  |  | SCRATCH DID NOT EXCEED 32" DID NOT EXCEED 50" FOR MORE 20 TO 30" MOST OF IT
|  |  |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN BRUNO | APPROX OF 24" PIPE WAS REMOVED
82 | 78-00000- |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-11-02 | 1978-12-11 | Patch Welded |  | Steel/Wrought Iron |  | REDWOOD CITY | REPAIRED LEAK ON ??? 20" LINE LEAK LOCATED 1" FROM WELD JOINT. INSTALL 110 WELDING BAND OVER LEAK AND ACETYLENE WELD, INST 20" WELDING BAND NEXT TO THE110
82 | 78-30272- |  |  | 22 | Transmission | [6 empty] | 1978-10-24 |  |  |  | Steel/Wrought Iron |  | STANFORD
82 | 78-20952- |  |  | 12 | Distribution Main | [6 empty] | 1978-10-03 |  |  |  | Steel/Wrought Iron |  | SAN MATEO
82 | 78-30249- |  |  | 30 | Transmission | [6 empty] | 1978-10-18 |  |  |  | Steel/Wrought Iron |  | WOODSIDE
82 | 80-30510- |  |  | 20 | Transmission |  | Other Welds |  |  | Damage by outside Forces |  | 1980-01-02 | 1980-01-03 | Clamp |  | Steel/Wrought Iron |  | REDWOOD CITY | FOUND CRACK IN WELD INST. A 20' -1 BOLT LEAK CLAMP ON LEAK. CRACK IS APPROX. 21/2" LONG. THIS WAS A ??. PATCH APPROX 21/2"X6"
56 | 86-40021-1 |  |  | 0.75 | Service |  | Other |  |  | Other |  | 1986-01-07 | 1986-01-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | MILLBRAE | NO LEAK ON SERVICE MAIN SHEET; CUT OFF 3/1" SERVICE INSERT 1/2" SERVICE
56 | 85- -1 |  |  | 20 | [11 empty] | Steel-Other |  | MILLBRAE
56 | 84-2 -1 |  |  | 30 | Transmission | [6 empty] | 1984-08-28 |  |  |  | Steel/Wrought Iron |  | DAILY CITY
56 | 84-2 -1 |  |  | 30 | Transmission | [6 empty] | 1984-08-28 |  |  |  | Steel/Wrought Iron |  | DAILY CITY
56 | 86- -1
|  |  |  | 4 | [11 empty] | Steel-Other |  | BRIS. | CUT OFF GAS SER.
56 | 87- -1 | [10 empty] | 00/00/1987 | [6 empty] | TM132
56 | 76- - |  |  | 3 | Distribution Feeder Main | [6 empty] | 00/00/1976 |  |  |  | Steel/Wrought Iron |  | DAILY CITY | TIE-IN FOR GM 492413
| 76-401 0-1 |  |  | 3 | [7 empty] | 1976-06-03 |  |  |  | Steel-Other
56 | 85-40242-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 1986-06-18 | 1986-06-18 | Replace Pipe and/or Service |  | TR 418 |  | DAILY CITY | CUSTOMER HIT 1/2 GAS WITH SHOVEL INST. 2 PREFICTION COUPLINGS AND 1 FT. TR418 P. BUCKLER
|  |  |  | 2 | Distribution Feeder Main | [5 empty] | NOT LEAKING |  | 1974-08-21 |  |  | Steel/Wrought Iron |  |  | 7B8-52 2712
[13 empty] | 1992-11-06 |  |  |  |  | SOUTH SAN FRANCISCO | REPLACE SERVICE AND POP-OUT METER SET OUTSIDE.
|  |  |  | 4 | [11 empty] | Steel-Other |  |  | TIE IN 4727905-1
|  |  |  | 8 | [13 empty] | SOUTH SAN FRANCISCO | TIE IN GM478705
| 83- - |  |  | 20 | [11 empty] | Steel-Other |  |  | MAIN CORD REPORT WO 403-1228-9000
56 | 86- -1 |  |  | 20 | [7 empty] | 00/00/1986 |  |  |  | Steel-Other |  | SOUTH SAN FRANCISCO | C/O 2" T.P. TAP OFF MAIN 101; TAP WAS 2" MUELLER SERV. TEE -CAPPED SAME
| 85- -1 |  |  | 20 | [11 empty] | Steel-Other |  | SOUTH SAN FRANCISCO
| 84- -1 |  |  | 20 | [7 empty] | 00/00/1984 |  |  |  | Steel-Other |  | SOUTH SAN FRANCISCO | 20" PIPE NOT UNCOVERED (WRAP)
| 85- -1 |  |  | 20 | [11 empty] | Steel-Other |  | SOUTH SAN FRANCISCO | WO48153
56 | 85- -1 |  |  | 20 | [11 empty] | Steel-Other |  | SOUTH SAN FRANCISCO | C/O 11/4" T.P. SERV #928
56 | 81- -1 |  |  | 3 | Other | [5 empty] | NONE | 00/00/1981 | 1981-08-05 | Patch Welded |  | Steel/Wrought Iron |  | SOUTH SAN FRANCISCO
| 74-20554-1 | [17 empty] | MAIN INSPECTION ONLY; MAIN INSPECTION ONLY...20" HP. TRANS MAIN O/SIDE...2" HRD 126' S/O ...PIPELINE 3/4" TP SERV. #449 WITH 3/4" STEEL PIPE; 8C3-7 FILE WITH CPA TM101
56 | 84- - |  |  | 2 | [7 empty] | 00/00/1984 |  |  |  | Steel-Other |  | SOUTH SAN FRANCISCO
| 80-20403-1 |  |  | 2 | [11 empty] | Steel-Other |  |  | PAVING ORDERED
| 88-40652-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1988-07-05 | 1988-07-05 | Clamp |  | Steel/Wrought Iron |  | SOUTH SAN FRANCISCO | INST PERM. LEAK CLAMP
56 | 86-40039-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1986-01-24 | 1986-01-24 | Clamp |  | Steel/Wrought Iron
56 | 86- -1 |  |  | 2 | [7 empty] | 00/00/1986 |  |  |  | Steel-Other |  | SOUTH SAN FRANCISCO | REMOVE VALVE BOX AND ABANDON VALVE. INSTALL (2) 2' PCF #H-17161 (CODE 02-2751) PERGS-S C-16.2 AND 2" EV-11 WELD END VALVE (CODE 03-2341) PER GS-5 F-31
|  |  |  | 2.375 | [11 empty] | Steel-Other |  | SOUTH SAN FRANCISCO
|  |  |  | 2 | [11 empty] | Steel-Other |  | SOUTH SAN FRANCISCO | C/O & REMOVE 2" TEMP PL. MAIN; TIE IN 0411854A-87
|  |  |  | 2 | [11 empty] | Steel-Other |  | SOUTH SAN FRANCISCO | C/O 3/4 SERV 06
56 | 79- -1 | [10 empty] | 00/00/1979
| 85-40039-1 |  |  | 2 | [11 empty] | Steel-Other |  | SOUTH SAN FRANCISCO
| 77-40131-1 |  |  | 2 | [7 empty] | 1977-09-27 |  |  |  | Steel-Other |  | SOUTH SAN FRANCISCO | REPAIRED 2" MAIN WITH PERMANENT REPAIR CLAMO @ INST. ANODE.
| 88-40652-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1988-07-05 | 1988-07-05 | Clamp |  | Steel/Wrought Iron |  | SOUTH SAN FRANCISCO | INST. PERM. LEAK CLAMP
56 | 86- -1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1986-03-14 | 1986-03-14 | Clamp |  | Steel/Wrought Iron |  | MILLBRAE | INST. TEP. CLAMP ON MAIN PIT
|  |  |  | 24 | Transmission | [10 empty] | Steel-Other |  | SAN BRUNO | GM 4772885
| 90-40171-1 | 101 |  | 20 | Transmission |  | Fitting |  |  | Corrosion |  | 1990-10-10 | 1990-10-10 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | MILLBRAE | WELD SAV-A-VALVE PLUG & CAP
| 88-40778-1 |  |  | 0.5 | Transmission | STATIC LINE | Body of Pipe |  |  | Corrosion |  | 1988-12-02 | 1988-12-02 | Clamp |  | Steel/Wrought Iron |  | DAILY CITY | ISNT. TEMP 1/2" CLAMP ON 1/2" STATIC LINE SULLAVAN SUB STATION.; REPAIR BY G.C. 2/15/89
|  |  |  | 20 | [11 empty] | Steel-Other |  | PACIFICA | EXPOSED VALVE 1126
|  |  |  | 36 | [11 empty] | Steel-Other |  | DAILY CITY | C/O STATIC LINE
| 82- -1 | [10 empty] | 00/00/1982
|  | 132 |  | 20 | [11 empty] | Steel-Other |  | BRISBANE | C/O SERV MAIN #132
| 91-40078-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1991-05-17 | 1991-05-20 | Patch Welded |  | Steel/Wrought Iron |  | BRISBANE | WELDED FULL CIRCLE SLEEVE OVER CORROSION HOLES; MARTIN REGULATION STATION; LEAK ON 6" RISER AT GROUND LEVEL
58 | [17 empty] | SC | DEPTH CHECK TEST HERE.
58 | [17 empty] | SC | DEPTH CHECK TEST HERE,
82 | 84-30582- | [10 empty] | 1984-11-05 | [5 empty] | WOODSIDE | CLEARED BY LEAK 9/19/1992
82 | 84-30033- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1984-06-14 | 1992-07-28 | Clamp |  | Steel/Wrought Iron |  | SAN CARLOS | PERM REPAIRED
82 | 79-30530-1 |  |  | 4 | Distribution Main | [6 empty] | 1979-07-27 |  |  |  | Steel/Wrought Iron |  | BELMONT
82 | 84-30371- |  |  | 2 | Distribution Main | [6 empty] | 1984-06-29 |  |  |  | Steel/Wrought Iron |  | SAN CARLOS
82 | 84-30372- |  |  | 2 | Distribution Main | [6 empty] | 1984-06-29 |  |  |  | Steel/Wrought Iron |  | SAN CARLOS
82 | 84-30330- |  |  | 2 | Distribution Main | [6 empty] | 1984-06-12 |  |  |  | Steel/Wrought Iron |  | BELMONT
82 | 84-20201- |  |  | 2 | Distribution Main | [6 empty] | 1984-06-08 |  |  |  | Steel/Wrought Iron |  | BELMONT
82 | 84-20172- |  |  | 2 | Distribution Main | [6 empty] | 1984-03-27 |  |  |  | Steel/Wrought Iron |  | BELMONT
82 | 84-30435- |  |  | 2 | Distribution Main | [6 empty] | 1984-09-13 |  |  |  | Steel/Wrought Iron |  | SAN CARLOS
82 | 83-20339- |  |  | 0.75 | Service | [6 empty] | 1983-12-20 |  |  |  | Steel-Other | ; | SAN MATEO
58 | 87-30109- | [10 empty] | 1987-02-18 | [5 empty] | FOSTER CITY
58 | 86-20203- | [10 empty] | 1986-05-23 | [5 empty] | SAN MATEO | 10/7/86 STREET RESURFACED CANNOT GET HOLE DOWN NEAR MAIN
82 | 83-20329- |  |  | 2 | Distribution Main | [6 empty] | 1983-12-14 |  |  |  | Steel/Wrought Iron |  | SAN MATEO
58 | 86-20201- | [10 empty] | 1986-05-23 |  |  |  | Steel/Wrought Iron |  | SAN MATEO
82 | 83-20159- |  |  | 2 | Distribution Main | [6 empty] | 1983-04-29 |  |  |  | Steel/Wrought Iron |  | SAN MATEO
82 | 83-20300- |  |  | 0.5 | Service | [6 empty] | 1983-08-30 |  |  |  | Steel/Wrought Iron |  | SAN MATEO | REPAVED NO HOLE PUNCHED
58 | 85-30168- |  |  | 2 | Distribution Main | [6 empty] | 1985-09-02 | 1985-09-02
58 | 85-30885- |  |  | 0.75 | Service | [6 empty] | 1985-08-20 |  |  |  | Steel/Wrought Iron |  | REDWOOD CITY
58 | 85-30836- |  |  | 2 | Distribution Main | [6 empty] | 1985-08-20 |  |  |  | Steel/Wrought Iron |  | REDWOOD CITY
58 | 85-30813- |  |  |  | Distribution Main | [6 empty] | 1982-08-12 |  |  |  | Steel/Wrought Iron |  | REDWOOD CITY | NO PROB HOLE-IN CEMENT
58 | 85-30477- |  |  | 0.75 | Service | [6 empty] | 1985-02-26 |  |  |  | Steel/Wrought Iron |  | REDWOOD CITY
58 | 85-30330- |  |  | 2 | Distribution Main | [6 empty] | 1985-02-15 |  |  |  | Steel/Wrought Iron |  | REDWOOD CITY
82 | 84-30491- |  |  | 2 | Distribution Main | [6 empty] | 1984-10-02 |  |  |  | Steel/Wrought Iron |  | SAN CARLOS
58 | 85-30803- |  |  | 2 | Distribution Main | [6 empty] | 1985-08-06 |  |  |  | Steel/Wrought Iron |  | REDWOOD CITY
58 | 85-30796- |  |  | 0.75 | Service | [6 empty] | 1985-08-05 |  |  |  | Steel/Wrought Iron |  | REDWOOD CITY
58 | 85-30765- |  |  | 0.5 | Service | [6 empty] | 1985-06-13 |  |  |  | Plastic |  | MENLO PARK
82 | 83-00009- |  |  | 2 | Distribution Main | [6 empty] | 1983-08-19 |  |  |  | Steel/Wrought Iron |  | HILLS
82 | 82-20251- |  |  | 3 | Distribution Main | [6 empty] | 1982-09-07 |  |  |  | Steel/Wrought Iron |  | HILLSBOROUGH
82 | 82-20241- |  |  | 2 | Distribution Main | [6 empty] | 1982-08-16 | [5 empty] | SAN MATEO
82 | 84-30350- |  |  | 2 | [7 empty] | 1984-06-18 |  |  |  | Steel/Wrought Iron |  | SAN CARLOS
58 | 85-30878- |  |  | 2 | Distribution Main | [6 empty] | 1985-08-02 | [5 empty] | REDWOOD CITY
| 09-40059-1 |  |  | 0.5 | Branch Service |  | Riser |  |  | Construction Defect |  | 2009-01-13 | 2009-02-20 | Tighten Cap or Bolt | VALVE | Steel/Wrought Iron |  | BURLINGAME | PIPE DOPE TIGHTENED SOAP NO BUBBLES
[18 empty] | PALO ALTO | #1 FULL INCIRCLEMENT BRUNCH SLEEVE #2 6"X10" SECTION OF 22" PIPE AS A REPAIR
PALO ALTO
58 |  |  |  | 22 | [8 empty] | 1994-05-12 |  |  |  |  | PALO ALTO | STAND BY WHILE OTHER DIG AROUND LINE 109
58 |  |  |  | 22 | [8 empty] | 1991-05-03 | [5 empty] | T4R REPAIRED GAS VALVE OR T.L.109
82 | 78-00000- |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-11-02 | 1978-12-11 | Patch Welded |  | Steel/Wrought Iron |  | REDWOOD CITY | REPAIRED LEAKS ON BOTH 20" LINE LEAK LOCATED 1" FROM WELD. JUST 20" WELDING BAND NEXT TO THE 110
82 | 72-50095-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-04-13 | 1972-04-14 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | REDWOOD CITY | FULL CIRCLE WELDING BAND OVER LEAK & OLD ACETYLENE WELD
|  | 101 |  | 20 | [11 empty] | Steel-Other |  | MENLO PARK | INSPECTION DEPTH CHECK TRANS. LINE 101
|  | 101 |  | 20 | [11 empty] | Steel-Other |  | MENLO PARK | INSPECTION DEPTH CHECK TRANS. LINE 101
|  | 101 |  | 20 | [11 empty] | Steel-Other |  |  | INSPECTION DEPTH CHECK TRANS. LINE 101
|  |  |  | 20 | [11 empty] | Steel-Other |  | MENLO PARK | INSPECTION DEPTH CHECK TRANS. LINE 101
|  |  |  | 22 | [11 empty] | Steel/Wrought Iron |  | REDWOOD CITY | TL 109
|  | 109 |  | 24 | [11 empty] | Steel/Wrought Iron |  | REDWOOD CITY
|  | 132 |  | 24 | [11 empty] | Steel/Wrought Iron |  | MENLO PARK | EXPOSED LINE 132 FOR DEPTH AT CUSTOMERS REQUEST. CUSTOMER WISHES TO DRIVE EQUIPMENT OVER LINE TO EXCAVATE FOR POOL
|  |  |  | 20 | [11 empty] | Steel/Wrought Iron |  | SAN CARLOS | AMERICAN COAST CROSSED 101 TO PUT IN ELECTRIC LINE FOR WATER
|  | 109 |  | 22 | [11 empty] | Steel/Wrought Iron |  | MENLO PARK | EXPOSED LINE 109 FOR DEPTH AT CUSTOMERS REQUEST. CUSTOMER WISHES TO DRIVE EQUIPMENT OVER LINE TO EXCAVATE FOR POOL
|  |  |  | 24 | [8 empty] | 1988-02-08 |  |  | Steel-Other
|  | 132 |  | 24 | [11 empty] | Steel-Other |  | ATHERTON | EXPOSED GAS TRANS LINE
[12 empty] | 1993-04-06 | 1993-04-06 |  |  | Steel-Other |  | PALO ALTO
|  | 132 |  | 24 | [11 empty] | Steel-Other |  | REDWOOD CITY | POT HOLING FOR DEPTH
|  |  |  | 24 | [11 empty] | Steel-Other |  | MENLO PARK | 66.0 45529-81 REMOVED & INSPECTED MAIN LOST ALL TRACE OF GMS. LEAK MUST TRAVELED
|  |  |  | 24 | [11 empty] | Steel-Other
2 |  | 132 |  | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1986-05-10 | 1986-05-19 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | STANFORD | FOUND 4" CAST IRON SEWER RESTING ON TOP TRANSMISION LINE 132- SMALL PIT 1/2'X1/16" DEPP ON TOP PIPE-WELDED FULL CIRCLE-18" WIDE AROUND PIPE (NO LEAKS)
|  | 109 |  | 22.00 & 24.00 | [11 empty] | Steel-Other |  | REDWOOD CITY | LINE 132
|  | 109 |  | 22.00 & 24.00 | [11 empty] | Steel-Other |  | REDWOOD CITY | LINE 132
|  |  |  | 4 | [11 empty] | Steel-Other |  | PALO ALTO | SHUT DOWN OF TRANSMISSION LINE #132; 4" H.P. SEAMLESS STEEL; INSTALLED HIGH VOLUME P.C.F. 4" (SPLIT) FOR AIR LAND MOVER
|  | 132 |  | 24 | [11 empty] | Steel-Other |  | REDWOOD CITY | DEPTH CK. VISIBLY LOCATE LINE 132 FOR EASEMONT LOCATION
|  | 132 |  | 24 | [11 empty] | Steel-Other |  | REDWOOD CITY | DEPTH CK. VISIBLY LOCATE LINE 132 FOR EASEMONT LOCATION
|  | 132 |  | 24 | [7 empty] | 1994-03-25 | 1994-03-25 |  |  | Steel-Other |  | PALO ALTO | DEPTH CHECK TRANSMISSION MAIN
| 95-40009- |  |  | 0.75 | Service |  | Valves |  |  | Corrosion |  | 1995-04-11 | 1995-04-02 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | DALY CITY | REPLACED SET FROM MAIN TO GVB-INSTALLED NEW 2" PLAS VALVE
58 | 90-30216- |  |  | 0.75 | Transmission |  | Fitting |  |  | Construction Defect |  | 1990-09-26 | 1990-09-26 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | REDWOOD CITY
58 | 88-20370-1 |  |  | 30 | Transmission |  | Longitudinal Weld |  |  | Material Failure |  | 1988-10-27 | 1988-10-28 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN MATEO | INSTALLED 1-4 BOLT CALMP TO STOP LEAK
82 | 79-20047- | 132 |  | 30 | Transmission | [6 empty] | 1979-10-16 |  |  |  | Steel/Wrought Iron |  | SAN MATEO | MAYBE ON DISTRIBUTION
| 85-20192- | 132 | [15 empty] | HILLS
| 72-50396- | [16 empty] | SAN MATEO
| 73-01051-1 | 132 | [15 empty] | SANTA CLARA | LEAK ON BOTTOM OF PIPE
| 73-50232- | [16 empty] | ATHERTON | WELDED 4 PATCHES OVER LEAK & DEEP PIT
82 | 78-30269- | 109 |  | 22 | Transmission | [6 empty] | 1978-10-18 |  |  |  | Steel/Wrought Iron |  | ATHERTON | VALVE STEM FROZEN. MUST BE CLEARED AND DIRT REMOVED OR WORKSPACE. THIS IS A DRIP. CHECK TO IS ON SCHEDULE FOR FLOW
82 | 78-30272- |  |  | 22 | Transmission | [6 empty] | 1978-10-24 |  |  |  | Steel/Wrought Iron |  | STANFORD
82 | 77-30449- | 109 |  | 22 | Transmission | [6 empty] | 1977-10-25 |  |  |  | Steel/Wrought Iron |  | STANFORD
| 79-60497- | [16 empty] | PALO ALTO | 11/30/1979 TEMP CLAMPED PATCH OVER LEAK ON TRANS. LINE 101. 12-6-1979 PER REP. MADE BY REPLACING 8" SECT OF 20" MAIN
| 94-30100-1 |  |  | 0.2 | Transmission |  | Valves |  |  | Other |  | 1995-05-10 | 1995-06-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | DALY CITY | BLEAD VALVE TIGHTEND & PLUG TIGHTEND 20" SOUTH OF JOHN DALY BLVD
| 76-20130-1 |  |  | 16 | [14 empty] | GREASED VALVE IN MAN HOLE6-67 LEAK AT GREASE PIT
| 75-00002-1 | [16 empty] | COLMA
| 89-40114-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1989-05-04 | 1989-05-04 | Other | C/O LINE | Steel/Wrought Iron |  | DALY CITY | C/O 112' OF 3/4" STATIC LINE OFF MAIN 132-NOT BEING USED
| 99-30097- | 101 | 38.75 | 24 | Transmission |  | Other |  | GREASE FITTING | Other | NEEDED GREASING | 1999-06-17 | 1999-08-04 | Other | FILLED WITH GREASE | Steel/Wrought Iron |  | BRISBANE | GREASE FITTING WAS LEAKING GREASE VALVE LEAK STOPPED
| 99-30097- | 101 | 38.75 | 24 | Transmission |  | Other |  | GREASE FITTING | Other | NEEDED GREASING | 1999-06-17 | 1999-08-04 | Other | FILLED WITH GREASE | Steel/Wrought Iron |  | BRISBANE | GREASE FITTING WAS LEAKING GREASE VALVE LEAK STOPPED
| 99-30097- | 101 | 38.75 | [8 empty] | 1999-06-17 | [5 empty] | BRISBANE
| 76-20290-1 | [14 empty] | Steel-Other
BRISBANE
BRISBANE
| 83-20196-F | 101 |  | 20 | [11 empty] | Steel-Other |  | BRISBANE | CAP ON 2' FITTING REPAIRED 25' S/S MARKED ON QUARRY RD. CAD WELD WIRES ON S/S OF FLANGE AND BROUGHT ANODE WIRE UP IN BOX
| 88-40675-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1988-08-12 | 1988-08-12 | Patch Welded |  | Steel/Wrought Iron |  | SOUTH SAN FRANCISCO | REPAIR 20" TRANS MAIN 38'X16 PATCH
| 76-40131-1 | [16 empty] | SOUTH SAN FRANCISCO
| 89-40006-1 |  |  | 20 | Transmission |  | Other Welds |  |  | Material Failure |  | 1988-01-06 | 1988-01-06 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SOUTH SAN FRANCISCO | WELDED "SAVER VALVEA' OVER 1" TO 2" CRACK ON MAIN 101
| 83-20195-F | 101 |  | 20 | [11 empty] | Steel-Other |  | SOUTH SAN FRANCISCO
| 80-20049- |  |  | 22 | Transmission |  | Valves |  |  | Other |  | 1986-10-25 | 1987-11-24 |  |  | Steel/Wrought Iron |  | HILLS | VALVE GREASE 11/2/1987.
82 | 74-40085-1 | 101 |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1974-05-13 | 1974-05-13 | Patch Welded |  | Steel/Wrought Iron |  | SAN MATEO | WELDED A COMPLETE CIRCULAR SLEEVE AROUND 20" PIPE. 20"X40". PUT A COMPLETE CIRCULAR SLEEVE OVER EXISTING WELD. PUT A 16"X16" PATCH ON MAIN AND A 10"X8" PATCH. HUNG TWO 17LB ANODES WITH FRAME AND COVER
82 | 72-40050- |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-02-05 | 1972-02-16 | Patch Welded |  | Steel/Wrought Iron |  | SAN MATEO | ARC WELD 3 LARGE PATCHES TO REPAIR LEAKS AND PITS. ALSO ARC WELDED FULL CIRCLE BAND OVRE OLD BUTT WELD
82 | 77-20604- |  |  | 20 | Transmission |  | Valves |  |  | Material Failure |  | 1977-10-31 | 1977-11-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | BELMONT | FOUND SMALL FUSS LEAK ON 4" BRIDLE VALVE. GREASE VALVE. STOP LEAKS
82 | 72-20384-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-02-03 | 1972-03-03 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SAN MATEO | ARC WELDED FULL CIRCLE BAND OVER OLD BUTT WELD AND THE LEAK ALSO FULL CIRCLE BAND 35" LONG OVER DEEP SCRATCH ON TOP OF MAIN. ALSO ARC WELDED SEVERAL LARGE PATCHES OVER DEEP LARGE PIT
82 | 74-20006-1 | 101 |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1974-01-30 | 1974-02-01 | Patch Welded |  | Steel/Wrought Iron |  |  | PIC WELD 1-(12"X12") PATCH AND 2-(3"X3" PATCHES OVER LEAK AND PITS ON 20" MAIN
| 91-50054- | 147 |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1991-05-08 | 1991-05-08 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SAN CARLOS | PATCH TRANS. MAIN LINE #147
82 | 72-50095-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-04-13 | 1972-04-14 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | REDWOOD CITY | ARC WELDED FULL CIRCLE WELDING BAND OVER LEAK & OLD ACETYLENE WELD
82 | 80-30510- | 101 | 17.5 | 20 | Transmission |  | Other Welds |  |  | Damage by outside Forces |  | 1982-01-02 | 1980-01-03 | Clamp |  | Steel/Wrought Iron |  | REDWOOD CITY | FOUND CRACK IN WELD INST. A 20"-1 BOLT LEAK CLAMP ON LEAK. CRACK IS APPROX. 21/2" LONG. THIS WAS SQUARE PATCH. APPROX 21/2"X6"
82 | 78-00000- |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-11-02 | 1978-12-11 | Patch Welded |  | Steel/Wrought Iron |  | REDWOOD CITY | REPAIRED LEAK ON BOTH 20" LINE LEAK LOCATED 1" FROM WELD JOINT. INSTALLED 110 WELDING BAND OVER LEAK AND ACETYLENE WELD. INSTALLED 20" WELDING BAND NEXT TO THE 110
82 | 77-30356- |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1977-11-08 | 1978-05-11 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | REDWOOD CITY | ARC WELDED 8"X8" PATCH OVER ON 20" GAS MAIN (LINE 101)
82 | 78-50330- |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-09-04 | 1978-09-04 | Clamp |  | Steel/Wrought Iron |  |  | INSTALLED 1-12" SKINNER LEAK CLAMPS
82 | 78-50321- | 109 |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-12-18 | 1978-12-18 | Clamp |  | Steel/Wrought Iron |  | ATHERTON | CLAMP INSTALLED
82 | 81-30058- |  |  | 24 | Transmission | [6 empty] | 1981-08-07 |  |  |  | Steel/Wrought Iron |  | ATHERTON
82 | 72-50396- |  |  | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-12-24 | 1972-12-26 | Patch Welded |  | Steel/Wrought Iron |  | ATHERTON | WELDED 10"X10" PATCH CAN MAIN
82 | 78-50321- | 109 |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-12-18 | 1978-12-18 | Clamp |  | Steel/Wrought Iron |  | ATHERTON | CLAMP INSTALLED
82 | 73-50232-1 |  |  | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-05-22 | 1973-06-14 | Patch Welded |  | Steel/Wrought Iron |  | ATHERTON | WELDED 4 PATCHES OVER LEAK AND DEEP PITS
82 | 79-50215- | 132 |  | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-04-19 | 1979-05-01 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | MENLO PARK | WELDED A 24"X FULL CIRCLE ON LINE 132 PIT THE SIZE OF A HOLE LIKE THE SHARPENED AND OF A LEAD PENCIL
82 | 79-50214- | 132 |  | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-04-19 | 1979-05-01 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | MENLO PARK | WELDED A 24"X FULL CIRCLE ON LINE 132 TO REPAIR LEAK
82 | 79-50054- | 109 | 16 | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-02-18 | 1979-03-06 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | STANFORD | WELDED A 2' SLEEVE OVER PITS ON BOTTOM OF LINE 109. SOME OIL BLOWING OUT OF PIT
82 | 73-50194-1 |  |  | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-06-01 | 1973-06-08 | Patch Welded |  | Steel/Wrought Iron |  | MENLO PARK | WELDED 7 PATCHES OVER 2 LEAKS & PITS
82 | 77-30450-1 | 132 |  | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1977-10-27 | 1978-10-24 | Clamp |  | Steel/Wrought Iron |  | MENLO PARK | INSTALLED A 24"X6" LEAK CLAMP & A 15 LBS ON THE 24" TRANS LINE 132.
82 | 75-30188- |  |  | 3 | Distribution Main | [6 empty] | 1975-12-11 |  |  |  | Steel/Wrought Iron |  | STANDFORD | CHECKED FOUND NO INDICATION OF GAS
82 | 75-30063- |  |  | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-02-11 | 1977-11-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | STANFORD | 1/2" PIT LEAKING ON LINE; CHECKED FOUND NO INDICATION OF GAS
82 | 75-30189- | 132 |  | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-10-13 |  | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | STANFORD | DUCT INSIDE OF CATCH BASIN 3' BELOW TOP GAS VENTING 100,000 PPM. CHECKED FOUND NO INDICATION OF GAS
82 | 77-30147-1 |  |  | 22 | Transmission |  | Longitudinal Weld |  |  | Construction Defect |  | 1977-10-25 | 1978-04-19 | Patch Welded |  | Steel/Wrought Iron |  | MENLO PARK | 2 FULL ENCIRCLEMENT BOLTS WELDED ON; ONE OVER BUTT WELD; ONE OVER PIN HOLE IN FLANGE WELD
| 94-80111- |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1994-03-22 | 1994-05-11 | Patch Welded |  | Steel/Wrought Iron |  | PALO ALTO | PATCH LEAKING 8" HP GAS MAIN. INSTALLED NEW ETS
80 |  |  |  | 0.75 | Service |  | Body of Pipe |  |  | Corrosion |  | 1975-04-03 | 1975-04-04 | Replace Pipe and/or Service |  | Steel/Wrought Iron
75-30189 | [17 empty] | LOS GATOS | REPAIRED LEAK ON 3/4" SERVICE BY INSERTING 1/2" NIPAK PLASTIC PIPE. INSTALLLED POWELL RISER KIT. AREA CLEAN DIRT AREA
| 74-03005-1 | 132 | [9 empty] | 1974-04-25 | [5 empty] | PALO ALTO | PUNCHED HOLE OVER LINE #132 NO READINGS. PUNCHED HOLES OVER CITY OF PALO ALTOS 4" GAS ,AIN READINGS OF 100 ON 100% WITH J.W. TURNED OVER TO THE CITY
82 | 77-31513-1 | 132 |  | 24 | Transmission | [6 empty] | 1977-10-25 |  |  |  | Steel/Wrought Iron |  | STANFORD | 8.000 P.P.M IN VALVE. NO OTHER GAS FOUND
| 78-31422- |  |  | 24 | [11 empty] | Steel-Other |  | PALO ALTO | LEAKING 3/4"GAUGE LINES ON LINE #132 AT THE VALVE MADE RAPIR BY REPLACING GAUGE LINE. AREA CLEAR
| 74-60077-2 | [16 empty] | SOUTH SAN FRANCISCO | PERM REP 6" MAIN
56 | 79--1 |  |  | 2 | [11 empty] | Steel-Other |  | SAN BRUNO
| 79-20448-1 |  |  | 2 | [11 empty] | Steel-Other |  | SOUTH SAN FRANCISCO | THIS IS OLD 3/4" GAS CUT OFF. PERM REPAIRED GAS LEAK
82 | 71-20019- |  |  | 2 | Other | H | [5 empty] | 1971-01-27 |  |  |  | Steel/Wrought Iron |  | BURLINGAME
82 | 71-20018- |  |  | 2 | Other | H | [9 empty] | Steel/Wrought Iron |  | BURLINGAME
82 | 71-20017- |  |  | 2 | Other | H | [5 empty] | 1971-01-27 |  |  |  | Steel/Wrought Iron |  | BURLINGAME
82 | 71-20015- |  |  | 2 | Other | H | [5 empty] | 1971-01-27 | 1971-01-27 |  |  | Steel/Wrought Iron |  | BURLINGAME
82 | 71-20022- |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1971-01-26 | 1971-03-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | BURLINGAME | FOUND SMALL PIT LEAKING ON RISER OF W3/4" SERVICE, 1/2" PLASTIC INSERTED IN PLD SERVICE, TESTED AT 100PSIG FOR 15 MIN.
82 | 76-20106-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-08-24 | 1976-08-24 | Clamp |  | Steel/Wrought Iron |  | BURLINGAME | LEAK REPAIRED USING A 2"X3" S&B LEAK CLAMP
82 | 71-20031- |  |  | 2 | Other | H | [5 empty] | 1971-01-26 |  |  |  | Steel/Wrought Iron |  | BURLINGAME | BAR TESTED OVER 3/4" SERVICE AND 4" MAIN-NO LEAKAGE FOUND 4% SCALE-ALSO SOAP TESTED CURB VALVE
82 | 71-20025- |  |  | 4 | Other | H | [5 empty] | 1971-01-26 |  |  |  | Steel/Wrought Iron |  | BURLINGAME
82 | 71-20024- |  |  | 2 | Other | H | [5 empty] | 1971-01-26 |  |  |  | Steel/Wrought Iron |  | BURLINGAME
82 | 71-20023- |  |  | 2 | Other | H | [5 empty] | 1971-01-26 |  |  |  | Steel/Wrought Iron |  | BURLINGAME
82 | 71-20026- |  |  | 2 | Other | H | [5 empty] | 1971-01-26 |  |  |  | Steel/Wrought Iron |  | BURLINGAME
82 | 71-20028- |  |  | 2 | Other | H | [5 empty] | 1971-01-26 |  |  |  | Steel/Wrought Iron |  | BURLINGAME
82 | 71-20029- |  |  | 4 | Other | H | [5 empty] | 1971-07-30 |  |  |  | Steel/Wrought Iron |  | BURLINGAME
82 | 74-20138-1 |  |  | 1 | Other |  | Fitting |  |  | Material Failure |  | 1974-10-17 | 1974-11-07 | Other |  | Steel/Wrought Iron |  | BURLINGAME | LEAKING 3/4" ELL ON CUSTOMERS UNDERGROUND POOL HEATER LINE. BAR TESTED AREA AND FOUND NO OTHER INDICATION OF LEAKAGE
82 | 82-20035- |  |  | 2 | Distribution Feeder Main |  | Fitting |  |  | Construction Defect |  | 1982-06-07 | 1982-06-16 | Other |  | Steel/Wrought Iron |  | BURLINGAME | LEAK ON VALVE FLANGE TIGHTEN BOLTS. SOME STEMS LEAK. REPAIR AND ADD GREASE EXTENSION
82 | 81-20083- |  |  | 2 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1981-10-23 | 1982-06-09 | Other |  | Steel/Wrought Iron |  | BURLINGAME | LEAK VALVE FLANGE-TIGHTENED BOLTS GREASE STEM. LEAKING REPAIR & GREASE EXTENSIONS
58 | 85-20191- |  |  | 2 | Distribution Feeder Main |  | Valves | Fitting |  | Other |  | 1985-10-29 | 1986-08-28 | Tighten Cap or Bolt | OTHER | Steel/Wrought Iron |  | HILLS | TIGHTENED BOLTS ON LEAKING FLANGE
82 | 73-20124-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1973-07-26 | 1973-12-03 | Patch Welded |  | Steel/Wrought Iron |  | BURLINGAME | ARC WELDED 2-4"X 7" PATCHES ON 8" MAIN INST. 9# MAG. ANODE.; ARC WELDED 1-4" X 7" PATCHES ON 8" MAIN INST. 9# MAG. ANODE
82 | 74-20131-1 |  |  | 0.5 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-10-17 | 1974-11-08 | Other |  | Steel/Wrought Iron |  | BURLINGAME | MAN HOLE ON SIDEWALK. 11-8-74 500P.P.M. IN REG PIT. REPAIRED SMALL LEAK IN STATIC LINE IN REG. STATION.; REPAIRED SMALL LEAK ON STATIC LINE FITTING IN REG. STATION.
82 | 71-40207- |  |  | 0.75 | Other | H | [5 empty] | 1971-06-02 |  |  |  | Steel/Wrought Iron |  | BURLINGAME | ODOR COMING OUT OF ELECT. CONDUIT IN WALL. IN WALL OF #1224. CUT SERVICE & PUMPED -HELD OK. BAR TESTED OVER MAIN- NO INDICATION OF LEAK. CLOCKED METERS -DID NOT HOLD TEST. LOCKED METERS-ODOR DISAPPEARED IN ELECT. CONDUIT. HAZARD NOTICE GIVEN TO CUST. HAZARD NOTICES ISSUED BY SERVICEMAN J. MAHONEY FOR 6-2-71 APTS. #1, #2, & #3 AT 1226 BROADWAY METERS LOCKED A/C. R. ABRAMOSKI. LEAK IN HOSUELINE, TAGS ON FILE.
58 | 89-20085-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1989-11-10 |  | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | ARC WLEDED 3 1' X 8" HOLE SA;ES TO STOV LEAKS
82 | 72-20184-1 |  |  | 8 | Distribution Feeder Main |  | Other Welds |  |  | Construction Defect |  | 1972-01-24 | 1972-02-02 |  |  | Steel/Wrought Iron |  | SAN MATEO | REPAIRED LEAKS IN CAN ISNTALL...ABANDONED 2" GAS VALVE. W. SANTA INEZ AVE.; LEAK IN WELL ON CAN INSTALLED OVER ABANDONED 2" GAS VALVE. REPAIRED BYPASS WELDING LEAKS INSTALLED 1-7# ANODE TO 8" MAIN
82 | 72-20490-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-08-31 | 1974-07-19 | Clamp |  | Steel/Wrought Iron |  | SAN MATEO | INSTALLED 2 BOLT SKINNER CLAMP SOAP TESTED OK; AFTER CLAMPING OFF LEAK. I BAR TESTED 50; IN EACH DIRECTION AND OVER SERVICE. NO OTHER GAS FOUND.; ISNTALLED 2 BOLT SKINNER CLAMP ON 3" H.P. GAS MAIN. INSTALLED 9# ANODE. COAP TESTED OK BAR TESTED NOGAT...
82 | 76-20111-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-09-08 | 1976-09-08 | Clamp |  | Steel/Wrought Iron |  | SAN MATEO | LEAK REPAIRED WITHA 2" X 6" S&b CLAMP
82 | 76-40130- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-08-25 | 1976-08-25 | Clamp |  | Steel/Wrought Iron |  | SAN MATEO | LEAKS REPAIRED USING 1- 2" X 8"' FULL CIRCLE AND 1-2" X 6" STANDARD S&B LEAK CLAMPS
82 | 78-20532-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1978-06-27 | 1979-03-26 | Patch Welded |  | Steel/Wrought Iron |  | SAN MATEO | WELDED PATCH ON 6" MAIN TO CLEAR UP LEAK IN...
82 | 74-40068-1 |  |  | 6 | Other |  | Body of Pipe |  |  | Corrosion |  | 1974-04-19 | 1974-04-22 | Patch Welded |  | Steel/Wrought Iron |  | SAN MATEO | ARC WELDED A 5" X 4: PATCH ON 6" MAIN. 9LB. ANODE INSTALLED ON MAIN. SEVERAL ONTHER LEAKS WERE REPAIRED AT THIS LOCATION
58 | 89-30258-1 |  |  | 8 | Transmission |  | Valves |  |  | Other |  | 1989-09-30 | 1989-09-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | HMB | TIGHTENED BODY BLEED PLUG
82 | 79-20047- |  |  | 30 | Transmission | [6 empty] | 1979-10-16 |  |  |  | Steel/Wrought Iron |  | SAN MATEO
58 | 87-00020-1 | [10 empty] | 1987-10-22 | 1988-09-21 | Patch Welded |  | Steel/Wrought Iron |  | SAN MATEO | WELD PATCH (3 PATCHES)
58 | 88-00033-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1988-10-04 | 1988-11-02 | Patch Welded |  | Steel/Wrought Iron |  | SAN MATEO | WELD PATCH MAIN
82 | 73-20674-1 |  |  | 2 | Other |  | Valves |  |  | Material Failure |  | 1973-11-15 | 1973-11-27 | Other |  | Steel/Wrought Iron |  | SAN MATEO | REGULATOR PIT 12/100 IN VENT STACK 11-26-73; REPAIRED RELIEF VALVE IN PIT
82 | 72-40288-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-12-20 | 1972-12-20 | Patch Welded |  | Steel/Wrought Iron |  | SAN MATEO | ARC WELDED PATCH OVER LEAK- INST. 9# ANODE ON MAIN
82 | 72-40059- |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-03-11 | 1972-03-13 | Patch Welded |  | Steel/Wrought Iron |  |  | HAS ARC WELDED WELD PATCH ON 4" MAIN IN A 2'.... WHICH WAS SEVERLY PITTED
82 | 72-00173-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 1972-09-13 | 1973-05-07 | Other |  | Steel/Wrought Iron |  | BELMONT | TIGHTENED LOOSE CAP 2" PCF INST. 9# ANODE ON MAIN.
82 | 77-20602- |  |  | 1.25 | Distribution Main |  | Fitting |  |  | Other |  | 1977-10-20 | 1977-11-18 | Replace Pipe and/or Service |  | Other |  | BELMONT | REPAIR LEAK ON 1/4" GAUGE VALVE INSIDE PIT AGAINST N-WALL. NO OTHER INDICATIONS
82 | 77-50192- |  |  | 0.75 | Other |  | Tap Connection |  |  | Corrosion |  | 1977-09-12 | 1977-09-13 | Weld Over Sleeve or Can |  | Steel/Wrought Iron
82 | 72-50006-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-01-09 | 1972-01-09 | Patch Welded |  | Steel/Wrought Iron |  | SAN CARLOS | PITS & LEAKS DO TO BAD FIELD WRAP; WELDED 3" X 3" PATCH OVER 2 PITS WITH 1/8" HOLES LEAKING.
82 | 78-30148- |  |  | 20 | Transmission | [6 empty] | 1978-11-03 |  |  |  | Steel/Wrought Iron |  | SAN CARLOS | ;
82 | 76-00010-1 |  |  | 2 | Transmission |  | Valves |  |  | Other |  | 1976-10-21 | 1976-10-29 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | REDWOOD CITY
82 | 72-50098-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-04-14 | 1972-04-14 | Clamp |  | Steel/Wrought Iron |  | SAN CARLOS | REPAIR LEAKING 1 1/4" MAIN BY PLACING CLAMP OVER...; MAIN ...TO BE REPLACED ON WOH819-A
82 | 72-50108-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-05-01 | 1972-05-04 | Patch Welded |  | Steel/Wrought Iron |  | SAN CARLOS | REPAIR LEAK 2" HP MAIN BY WELDING 3 PATCHES OVER PITS INSTALLED 9LBS ANODE
82 | 76-50193-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  |  |  | 1976-12-01 | 1976-12-01 | Replace Pipe and/or Service |  | Plastic |  | SAN CARLOS
82 | 72-50016-1 |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-01-14 | 1972-01-14 | Clamp |  | Steel/Wrought Iron |  | REDWOOD CITY | WO 44794-72 CPA- 6; PUT CLAMP ON LEAK WRAPPED AND BACK FILLED.
82 | 75-30015-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-02-03 | 1976-02-17 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | REDWOOD CITY | RECHECKED AFTER...DRILLED HOLES...MANHOLE FOUND NO INDICATION OF GAS. OVER THRANS LINE 101 HIGHEST READINGS WITH T.L.V. WAS 2000P.P.M. IN STREET. CHECKED...BUILDING...FOUND NO INDICATION OF GAS CLASS III; ARC WELDED 5" X 5" PATCH OVER CORROSION LEAK
82 | 72-50005-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by outside Forces |  | 1972-01-12 | 1972-01-12 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | REDWOOD CITY | WRAP DAMAGED 1/2" X 12" LONG ON BOTTOM OF MAIN.; WELDED 3" X 3" & 4" X 8" PATCHES OVER PITS AND LEAKS
82 | 80-30751- |  |  | 2 | Distribution Main |  | Valves |  |  | Material Failure |  | 1980-11-03 | 1980-11-05 | Other |  | Steel/Wrought Iron |  | REDWOOD CITY | 2" VALVE LEAKING- COULD NOT REPAIR BY GREASEING. CAUTION TRANS PRESS. REMOVED OLD GREASE AND REGREASED VALVE STOPPED LEAKING...
82 | 73-50335- |  |  | 2 | Other | PIT BYPASS | Body of Pipe |  |  | Damage by outside Forces | DAMAGED WHEN POLE SET | 1973-10-11 | 1973-10-11 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | REDWOOD CITY | OFFSITE 2" BYPASS AROUND POLE; MOED 1-2" TOP TAP.; REPLACED 2' 9LB ANODE INSTALLED
82 | 73-30023-1 |  |  | 0.5 | Other | GAUGE LINE FOR DIST. PRESS CHART | Other |  |  | Damage by outside Forces |  | 1973-02-09 | 1973-02-09 | Replace Pipe and/or Service |  | Plastic |  |  | REPAIRED 1/2" GAUGE LINE WITH 1/2" ...PLASTIC
82 | 73-30266-1 |  |  | 0.5 | Other | GAUGE LINE OFF 8" MAIN | Fitting |  | COUPLING | Material Failure |  | 1973-06-29 | 1973-07-02 | Replace Pipe and/or Service |  | Plastic |  | REDWOOD CITY | 1/2" PLASTIC SUPPLYING GAUGE A ALARM IN R.C. OFFICE; CRIMP ON FITTINGS ...TO ...REPAIR
82 | 72-30242-1 |  |  | 0.75 | Other |  | Body of Pipe |  |  | Corrosion |  | 1972-04-07 | 1974-10-21 | Other | ABANDON OLD SERVICE
82 | 75-50255- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1975-09-26 | 1975-09-26 | Clamp |  | Steel/Wrought Iron |  | REDWOOD CITY | REPAIR W/2:... BAR CLAMP &...; INSTALLED ONE LEAK CLAMP
8 | 76-50150-1 |  |  | 0.75 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1976-10-21 | 1976-10-29 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | REDWOOD CITY | INSTALLED 1/2" PLASTIC INSERT SERVICE TO REPAIR LEAK.
82 | 80-30510- |  |  | 20 | Transmission |  | Other Welds |  |  | Damage by outside Forces |  | 1980-01-02 | 1980-01-03 | Clamp | PERMANENT REPAIR: REPLACE PIPE AND/OR SERVICE | Steel/Wrought Iron |  | REDWOOD CITY | FOUND CRACK IN WELD INST. A 20" 1 BOLT LEAK CLAMP ON LEAK. CRACK IS APPROX. 2 1/2" LONG. THIS WAS A SQ. PATCH APPROX 2 1/2" X 6" A LEAK REAPIRED.
82 | 77-30355- |  |  | 2 | Transmission |  | Body of Pipe | Valves |  | Construction Defect | WELD | 1977-11-08 | 1979-03-09 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | REDWOOD CITY | STORM DRAIN 14" ONLY...
82 | 77-30356- |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1977-11-08 | 1978-05-11 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | ; REDWOOD CITY | ARC WELDED 8" X 8" PATCH ON 20" GAS MAIN (LINE 101)
8 | 72-50322-1 |  |  | 0.5 | Distribution Main |  | Other Welds |  |  | Material Failure |  | 1972-10-24 | 1972-10-27 | Other |  | Copper |  | REDWOOD CITY
82 | 71-30556-1 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-12-23 | 1971-12-24 | Patch Welded |  | Steel/Wrought Iron |  | ; REDWOOD CITY | LEAK ON 3/4" SER. AND 4" HP. MAIN.
8 | 79-50126- |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1979-06-21 | 1979-06-25 | Clamp |  | Steel/Wrought Iron |  | REDWOOD CITY | INSTALLED 1-2"... TO REPAIR LEAK
82 | 71-50372-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-12-27 | 1971-12-31 | Clamp |  | Steel/Wrought Iron |  | ; REDWOOD CITY | INSTALLED 2- 2" X 3" CLAMPS, 2- 2" X 6" CLAMPS, 1- 2" X 12" CLAMP
82 | 74-30522-1 |  |  | 0.75 | Other |  | Regulator |  |  | Material Failure |  | 1974-06-11 | 1974-06-26 | Other |  | Steel/Wrought Iron |  | MILLBRAE | LEAK IN DIAF. ON 3/4" REG TO 2 ...MAINFOLD INSIDEWALK BOX METERS COUND BE HOT TANKED....
82 | 76-31056-1 |  |  | 1.25 | Other | [6 empty] | 1976-08-02 |  |  |  | Steel/Wrought Iron |  | MENLO PARK
82 | 74-00199-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1974-11-11 | 1974-11-20 | Patch Welded |  | Steel/Wrought Iron |  | MENLO PARK | WATER METER BOX OFF W/SIDE OF SHOW ROOM
82 | 72-50070-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-03-06 | 1972-03-07 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | MENLO PARK | REPAIRED LEAK BY WELDING PATCH OVER PIT. LEAK TEST AT 100LBS 15MIN.
82 | 71-00225- |  |  | 2 | Other | H | [9 empty] | Steel/Wrought Iron |  | MENLO PARK
8 | 72-50001-1 |  |  | 22 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-01-04 | 1972-01-05 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | MENLO PARK | INSTALLED 1/2" PLASTIC TO REPAIR LEAK 3/4" STEEL SER.; ... 1LB ANODE INSTALLED
82 | 71-00226- |  |  | 0.75 | Other | H | [9 empty] | Steel/Wrought Iron |  | MENLO PARK
82 | 71-30311-1 |  |  | 00.75 & 02.00 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1971-12-10 | 1971-12-10 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | EAST PALO ALTO | WELDED 2" X 3" & 2" X 2" PATCHES OVER LEAK IN 2" MAIN & REPLACED SERVICE TO 10 H5 BY INSERTING 1/2" PLASTIC IN 3/4" CASING
82 | 72-30299-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-05-01 | 1972-06-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | EAST PALO ALTO | INSTALLED 1/2" PLASTIC INSERT SERV....INST. 1LB ANODE AT RISER
82 | 71-50013- |  |  | 0.75 | Other | H | Tap Connection |  |  | Corrosion |  | 1971-01-08 | 1971-01-08 | Other |  | Steel/Wrought Iron |  | EAST PALO ALTO | FOUND 2 LEAKS IN EXPOSED PORTION OF APPARENTLY NOT ABANDONED 3/4" STEEL SERVICE AT PORTION OF SERVICE. LEAKING EXPOSED NEAR 2" MAIN CUT AND ABANDONED SERVICE AT MAIN. ALL METERS IN AREA SHOW MOVEMENT OF METER HANDS. A RELATIVLY NEW SERVICE HAS BEEN INSTALLED AT #3034 MEN HATTAN AVE. WITH TEE 20" FROM TEE TO LEAKING SERVICE ON PORTION THERE OF.
82 | 75-20062- |  |  | 20 | Transmission | [6 empty] | 1975-12-16 |  |  |  | Steel/Wrought Iron |  | ; EAST PALO ALTO | DELETE
| 70-MR 34-2 |  |  | 0.5 | Other | H | [5 empty] | 1971-04-08 | 1971-04-08 |  |  | Copper |  | EAST PALO ALTO | PRESSURE TESTED ENTIRE SERVICE AT 100PSI, 15 MINUTES HOLD OK
82 | 71-00220- |  |  | 8 | Other | H | [9 empty] | Steel/Wrought Iron |  | MENLO PARK
82 | 71-00219 |  |  | 8 | Other | H | [9 empty] | Steel/Wrought Iron |  | MENLO PARK
85 | 71-00221- |  |  | 1.25 | Other | H | [9 empty] | Steel/Wrought Iron
82 | 74-30150-1 |  |  | 0.75 | Other | P | Valves |  |  | Other |  | 1974-05-14 | 1974-12-27 | Other |  | Steel/Wrought Iron |  | REDWOOD CITY | BELOW RISER. FOUND INDICATION OF... GAS SERV...600 P.P.M. CLASS III. FOUND CORE OF STOP COCK LEAKING TIGHTENED CORE STOPPED LEAK. BAR TESTED SERVICE & HD JOINING MAIN NO INDICATION OF FUTHER LEAKING. METER SET LEAK
82 | 72-50013-1 |  |  | 2 | Other | PRIMARY TAP FOR... | Fitting |  |  | Material Failure |  | 1972-01-19 | 1972-01-19 | Other |  | Steel/Wrought Iron |  | MENLO PARK
58 | 89-30267-1 |  |  | 3 | Distribution Feeder Main |  | Fitting |  |  | Construction Defect |  | 1989-10-13 | 1990-11-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | WDSE | REDOPED AND TIGHTENED 1" SOUCE VALVE TO STOP LEAK
82 | 78-50321- |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-12-18 | 1978-12-18 | Clamp |  | Steel/Wrought Iron |  | ATHEIZTON
82 | 78-30269- |  |  | 22 | Transmission | [6 empty] | 1978-10-18 |  |  |  | Steel/Wrought Iron |  | ATHARTON | VALVE STEM FROZEN. AREA MUST BE CLEARED AND...REMOVED...THIS IS A DRIP. CHECK...
82 | 77-30148-1 |  |  | 24 | Transmission | [6 empty] | 1977-10-27 |  |  |  | Steel/Wrought Iron |  | ATHARTON
82 | 77-30353- | 109 |  | 30 | Transmission |  | Valves |  |  | Material Failure |  | 1977-11-01 | 1978-03-21 | Other |  | Steel/Wrought Iron |  | WOODSIDE | REPAIRED LEAK ON VALVE ON LINE 109-1/2" PRESS RELIEF...CHECK VALVE...
82 | 78-50270- |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other | LANDSLIDE AREA - PRESSURE CRACKED VALVE | 1978-11-02 | 1978-11-02 | Replace Pipe and/or Service | OTHER | Steel/Wrought Iron |  | WOODSIDE | SEE ATTACHED MAP
58 | 81-50033- |  |  | 3 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1981-03-07 | 1981-03-07 | Other |  | Steel/Wrought Iron |  | PORTOLA | THIS IS A DUPLICATE FORM. ORIGIANL LOST. KEEP FOR RECORD UNTIL UPDATED
82 | 79-50756- |  |  | 3 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1979-06-01 | 1979-09-14 | Other |  | Steel/Wrought Iron |  | PORTOLA VALLEY | GREASED 3-VALVES TO STOP LEAKAGE. RAISED VALVE CASING TO GROUND LEVEL
82 | 75-00208-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion | WRAP DAMAGE | 1975-05-27 | 1975-06-19 | Patch Welded |  | Steel/Wrought Iron |  | WOODSIDE | WELDED PATCH AND 2...
58 | 87-30113- |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1987-03-13 | 1987-03-19 | Clamp |  | Steel/Wrought Iron |  | WOODSIDE
82 | 71-00238- |  |  | 4 | Other | H | [9 empty] | Steel/Wrought Iron |  | ATHERTON
82 | 71-60023-6 |  |  | 0.75 | Other | H | [9 empty] | Steel/Wrought Iron |  | ATHERTON
82 | 71-00247- |  |  | 2 | Other | H | [5 empty] | 1971-02-18 |  |  |  | Steel/Wrought Iron |  | ATHERTON
82 | 71-00245- |  |  | 2 | Other | H | [5 empty] | 1971-02-17 |  |  |  | Steel/Wrought Iron |  | MENLO PARK
82 | 71-00252- |  |  | 8 | Other | H | [5 empty] | 1971-02-19 |  |  |  | Steel/Wrought Iron |  | MENLO PARK
82 | 71-00253- |  |  | 2 | Other | H | [5 empty] | 1971-02-19 |  |  |  | Steel/Wrought Iron |  | MENLO PARK
82 | 76-30148-1 |  |  | 0.25 | Other | C441-AG | Other |  |  | Other |  | 1976-04-02 | 1976-08-10 | Other |  | Copper |  | MENLO PARK
82 | 74-30050-1 |  |  | 2 | Other |  | Valves |  |  | Material Failure |  | 1974-05-02 | 1974-09-17 | Other |  | Steel/Wrought Iron |  | MENLO PARK | GROUND LEAK, GREASE VALVE IN CURB. FOUND GAS IN GAS VALVE FOR TRANSMISSION LINES 109 & 132 - 2000 P.P.M. FOUND GAS IN LARGE GAS REG. PITS. 10,000P.P.M.. FOUND FOAAMER ON 1/4" METRIC VALVE ON UNION P.T. REDOPED AND RETIGHTENED PLUG
82 | 71-00360- |  |  | 0.75 |  |  | Body of Pipe |  |  | Corrosion |  | 1971-03-03 | 1971-08-27 | Bell Joint Clamp |  | Steel/Wrought Iron |  | STANFORD
82 | 75-30473- |  |  | 1.25 | Distribution Feeder Main |  | Valves |  |  | Construction Defect | LEAKING THREADS | 1975-10-28 | 1976-06-10 | Other |  | Steel/Wrought Iron |  | PORTOLA VALLEY
82 | 74-50027- |  |  | 0.75 | Service |  | Body of Pipe |  |  | Damage by outside Forces |  | 1974-01-08 | 1974-01-09 | Replace Pipe and/or Service |  | Copper |  | MENLO PARK | REPLACED SMALL SECTION 2/4" COPPER NEAR THE WELDING TEE AND INSTALLED A...NIPPLE 3/4"...TO 1/2" COPPER. INSTALL 9LB ANODE ON COPPER; CUT OF A SECTION 3/4" COPPER THAT WAS DAMAGED PRESSURE TEST AT 120PSI IN 15 MINUTES, OK
82 | 71-30513-1 |  |  | 0.75 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1971-12-14 | 1971-12-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | LADERA | TIGHTEN 3/4" STOP COCK TO STOP LEAK
82 | 82-30104- |  |  | 6 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1982-01-15 | 1982-02-11 | Other |  | Steel/Wrought Iron |  | STANFORD | FOUND LEAK ON FLANGE TO 6" VALVE REPAIRED LEAK RAISED F&c
82 | 71-00361- |  |  |  | Other | H | [11 empty] | STANFORD
82 | 71-00351- |  |  |  | Other | H | [11 empty] | STANFORD
82 | 71-00350- |  |  |  | Other | H | [11 empty] | STANFORD
58 | 86-30110- |  |  | 2 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1986-01-18 | 1986-10-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | STANFORD
82 | 75-31064- |  |  | 22 | Transmission | [6 empty] | 1975-12-11 |  |  |  | Steel/Wrought Iron |  | ATHERTON | DELETE; TO BE CHECKED WITHIN 60 DAYS
82 | 72-50089-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-03-31 | 1972-03-31 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | ATHERTON | REPLACED 15' OF 4" MAIN; LEAKING OVER SERVER LATERAL AND UNDER CATCH BASIN...
82 | 72-30613-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-12-13 | 1972-12-19 | Patch Welded |  | Steel/Wrought Iron |  | ATHERTON | WELDED 6" PATCH OVER PIT. INST. 356b ANODE ON MAIN
82 | 78-30264- |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-09-27 | 1979-03-27 | Clamp |  | Steel/Wrought Iron |  | ATHERTON | INSTALLED 1- 2 BOLT SKINNER CLAMP ON 4" MAIN IN SWERE TRENCH 10' N ELEC. POLE. NO ROOM TO WELD PATCH
82 | 75-00211-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1975-05-27 | 1975-05-30 | Patch Welded |  | Steel/Wrought Iron |  | ATHERTON | BAR HOLE STRIP OFF ...FOUND LEAK AT...H.P. MAIN LEAKING ON BOTTOM OF MAIN HAD ARC W/ARC WELDING 12" CAN ON ...
82 | 75- - |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1975-05-14 | 1975-05-15 | Patch Welded |  | Steel/Wrought Iron |  | ATHERTON
82 | 72-50095-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-04-13 | 1972-04-14 |  |  |  |  | REDWOOD CITY
82 | 75-00000- |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-11-02 | 1978-12-11 | Patch Welded |  | Steel/Wrought Iron |  | REDWOOD CITY | REPAIRED LEAK ON BOTTOM 20" LINE LEAK LOCATED 1" FROM WELD JOINT. INSTALLED 110 WELDING BAND OVER LEAK AND ACETYLENE WELD. INSTALLED 20" WELDING BAND NEXT TO THE 101
82 | 77-30356- | 101 |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1977-11-08 | 1978-05-11 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | REDWOOD CITY | ARC WELDED 8"X8" PATCH OVER LEAK ON 20" GAS MAIN (LINE 101)
82 | 75-30015-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-02-03 | 1976-02-17 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | REDWOOD CITY; | ARC WELD 5"X5" PATCH OVER CORROSION LEAK
82 | 81-30058- |  |  | 24 | Transmission | [6 empty] | 1981-08-07 |  |  |  | Steel/Wrought Iron
| 08-20286-1 | L101 |  | 0.75 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 2008-05-10 | 2008-07-17 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | BURLINGAME | TIGHTEN PLUG CAP ON METER
78 | 11-10111-1 | 300A |  | 0.75 | Transmission >= 20% SMYS |  | Line Valve |  |  | Unknown |  | 2011-04-19 | 2011-04-24 | Replace Service Valve <2-inch | REPLACE SERVICE VALVE <2 INCH - REPLACE, OTHER | Steel-Other |  | GILROY | READ ON RISER ON HIGH PRESSURE SIDE OF REGULATOR; REPLACED TO BALL VALVE; FOUND 1/4" PLUG VALVE CRACKED @ TANG OLD NORDSTRM VALVE. REPLACED WITH 2000# BALL VALVE. FIXED SMALL FOAMER D/S ON HPR.
| 11-10115-B |  |  | 0.75 | Single Service |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2011-04-19 | 2011-04-22 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SAN MARTIN | 72Y. IN REGULATOR BOX. ODOR, HIGH PRESSURE LINE; REDOPED; TIGHTEN FITTINGS & THD; STAND-BY REMOVED WTR & MUD. T&R FIXED 3 LEAKS ON PIN-OFF TEE CAP; UNION HP, 1/4" PLUG. 2ND CORRECTION TURNED IN FOR UPGRADE HPR SET.
98 | 10-82003-1 | 100 | 13843 | [8 empty] | 2010-09-18 | [5 empty] | SAN JOSE | PRESSURE LIMITING STATION 7A & 7B; V-12; GAS TRANSMISSIONS
98 | 10-88380-1 | 300A | 47047 | 0.75 |  |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-10-21 | 2011-02-24 | Mechanical Repair Fitting - Fitting |  | Steel-Other |  | GILROY | DRIED OUT PIPE DOPE. REAR/O/HOUSE@END OF ROSE IN. 6' FRM REG; NONE; HIGH TO HIGH SHUT IN SO LEAKS COULD BE REPAIRED - SOAP TEST OK
98 | 10-88384-1 | 0833-01 | 0 61 | 0.75 |  |  | Other |  | NO LEAK FOUND | Other |  | 2010-10-22 | 2011-02-10 |  |  | Other |  | GILROY | @ SERVICE TAP H74 HPR; WM IS 3883-C05; NO LEAK FOUND; NO LEAK FOUND @ SERVICE TAP H-74; 3675 HWY 152 HAS PROPANE OFF OF MAP GIVEN PI#3683-C6. THE SERVICE TAP FOUND H74 HAS NO LEAK & "A" INSP ALSO DONE AT SAME TIME. OPERATED GATE VALVE TOO. NO LEAK
78 | 10-81403-1 | 0804-08 | 0 59 | 4 | Distribution Main <= 60 PSIG |  | Other |  | NO LEAK FOUND | Other | NO LEAK FOUND | 2010-09-26 | 2010-10-05 | Other | NONE | Steel-Other |  | SANTA CLARA | 20' S/O PVT DR S/O CENTRAL EXPWY ON LAFAYETTE; FOUND NO LEAK; NO LEAK FOUND; E-17 "A" INSP. DONE 10/05/10. PER REG. MAINT. FORM RESULT - PASS SOAP TEST PIPING GOOD. STATION VALVES OPERATED & LU BED. PIPE & CONDITION GOOD.
| 10-11075-1 |  |  |  | Transmission |  | Valves |  |  | Other | 3/4 PLUG | 2010-10-05 | 2010-12-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | GILROY | SERVICE X ST "P" RD (FIELD SPORTS PARK); 3/4 PLUG TIGHTEN REDOPE; PLUG REDOPE AND TIGHTEN; IN BOX NEXT TO SONIC METER PLUG LOOSE, VALVE IN SMALL VAULT.
78 | 10-81029-1 | 0809-02 | 0 08 | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Other | LOOSE | 2010-09-28 | 2010-12-06 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | MORGAN HILL | AX FRM 2260;VALV IN REGSTA; SAME; TIGHTEN 3/4" H.P. UNION; SOAP TEST OK; SEE ATTACHED MAP
| 10-81120-1 | 0824-02 | 9 | 8 | Transmission |  | Fitting |  |  | Unknown |  | 2010-09-26 | 2010-12-06 | Other | REPAIRED MULTIPLE LEAKS, FITTINGS | Steel/Wrought Iron |  | SAN JOSE | 20" N/O INTERSECTION CREEKLAND CIR & MABURY RD - REG PITS; SAME; FIXED MULTIPLE LEAKS, SOAP TEST OK; SEE SKETCH (ATTACHED)
| 10-81118-1 | 0829-01 | 0 71 | 0.75 | Single Service |  | Other |  | MUELLER CAP | Unknown |  | 2010-09-27 | 2010-12-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MILPITAS | STPDOWN REG VAULT - H.P. CAP LEAKING; REDOPED & TIGHTENED MUELLER CAP IN H.P.R SET. SOAP TEST OK
| 10-81122-1 | 0824-02 | 1 61 | 12 | Transmission |  | Valves |  |  | Unknown |  | 2010-09-26 | 2010-12-03 | Other | GREASED VALVE | Steel/Wrought Iron |  | SAN JOSE | SD/WK TO CHOICE LIQUOR - GAS VALVE LEAKING AGAIN - A4A; CONSTANTLY LEAKING VALVE GREASED AGAIN 2ND ATTEMPT. CORRECTIVE ACTION FORM SUMMITED. T&D TAG TO WORK; GREASED VALVE 2ND TIME TURNED IN 2ND CORRECTIVE TO T&D TO WORK
| 10-81105- |  |  | 6 | Transmission |  | Valves |  |  | Other | DRIED OUT GREASE | 2010-09-26 |  |  |  | Steel/Wrought Iron |  | SANTA CLARA | @ VALVE CASING; COMPLETED 12/6 SEE SCOTTS E-MAIL ATTACHED
78 | 10-10203-1 |  |  | 4 | Transmission >= 20% SMYS |  | Line Valve |  |  | No/Deteriorated Pipe Dope |  | 2010-05-14 | 2010-11-24 | Greased - Other |  | Steel-Other |  | SAN JOSE | ON MONTEREY RD, 100' N/O BLOSSOM HILL RD; LEAK ON VALVE AT STUB 785 TRANSMISSION; GREASED VALVE & RG - SEATED; NOT ABLE TO SEE PIPE, ONLY STEM FOR GREASING. GREASED/SOAP TESTED, OK.
| 10-81182-1 | [10 empty] | 2010-09-27 | [5 empty] | MILPITAS | Y-DOT ON VALV NXT TO ADRS; SAME; T&R PETE & MIKE REPAIRED
| 10-81208-1 | 300B | [9 empty] | 2010-09-29 | [5 empty] | MORGAN HILL | *SCANNED & SENT TO JOHN GILLIO 10/15/10 @ 8:07 AM NOT GAS T&R WORK; AX FRM MOTORCYCLE PARK; SAME
| 10-81063-1 | 300A |  |  | Transmission |  | Valves |  | 3/4 PLUG | Other | DOPE & TIGHTEN | 2010-09-29 | 2010-10-06 | Soap and/or Tape - Other |  | Steel/Wrought Iron |  | SAN JOSE | VAULT N/O REG ST. ENT. GT.; NO SPREAD VALVE T483.59?; SAME; 3/4" PLUG REDOPED & TIGHTEN; REDOPE & TIGHTEN 3/4" PLUG SOAP TEST; SEE ATTACHMENT
| 10-81109- |  |  | 0.75 | Transmission |  | Valves |  | GREASE PLUG | Other | GREASED PLUG | 2010-09-27 | 2010-09-27 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | MORGAN HILL | REG. STA. OVER LINE IN ELECTRIC FENCE LEAKING @ VALVE; REPLACED & GREASED 1/4" PLUG VALVE. SOAP TEST
| 10-81103- |  |  | 0.75 |  |  | Valves |  | PLUG | Other | REPLACE PLUG | 2010-09-26 | 2010-09-26 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | SAN JOSE | INDICATIONS IN VALVE CASING; REPLACED GREASE PLUG. GAS LEAK ON FITTING. SOAP & GAS TRACT PASS.
| 10-81058-1 | 6511 | [9 empty] | 2010-09-28 | [5 empty] | MILPITAS | CGTS VALVE T&D RECHECKED - NO LEAK FOUND; N/E CRNR MCARTHY&HWY237;PKGLOT BHD HOTEL@YELLOWDOT; SAME; AT VALVE #600 MARKED IN YELLOW
| 10-10197-1 |  |  | 20 | Transmission | VALVE | Valves |  |  | Other | NEEDED GREASE | 2010-05-12 | 2010-05-14 | Other | GREASED | Steel/Wrought Iron |  | SAN JOSE | LEAK IN VALVE BOXES V-16, V-I A LOT OF ODOR IN AIR; GREASED VALVE; GREASED VALVE - SOAP TESTED
| 10-10651-1 | [10 empty] | 2010-09-15 | [5 empty] | GILROY | 1% GAS IN VALVE V06-T4G (T&R NEEDS TO GREASE VALVE)
| 10-34223- |  |  | 0.75 |  |  | Valves |  |  | Other | DRIED OUT PIPE DOPE | 2010-09-18 | 2010-09-29 | Other | CLEANED REG. CAPS ON 2 SAV A VALVE 2 GREASE FITTING | Steel/Wrought Iron |  | SAN JOSE | VALVE 11 @ TULLY STATION; CLEARANCE SJ 10-09- BROUGHT PRESSURE DOWN FLAT. VALVE 11 TOTALLY EXPOSED - FOUND LEAKS ON A SAV A VALVE CAPS ON EITHER SIDE OF VALVE. REMOVED CAPS, CLEANED, REDOPED, TIGHTENED - 2 LEAKS ON GREASE FITTING - REMOVED, CLEANED REDOPED, TIGHTENED, SOAP TESTED ALL UNDER PRESSURE - GOOD
| 10-10594-1 | 100 |  | 2 | Transmission |  | Valves |  | A-L100 | Material Failure | GASKET | 2010-09-12 | 2010-09-17 | Other | REPLACE GASKET | Steel/Wrought Iron |  | SAN JOSE | VALVES, BOXES; CLEARANCE SJ-10-08 - REMOVED BONNET ON 2" KENOTEST (720WO9) SERIES 300, BALL VALVE, CLEANED, REPLACED GASKET.
| 10-10235-1 | 300A |  |  | Transmission |  | Other |  | NONE FOUND | Other | NO LEAK FOUND | 2010-05-28 |  | Other | NO LEAK FOUND | Steel/Wrought Iron |  | GILROY | 10' E/O GILROY ON HWY 152; DREG 5363 VLV; LN 300A; DREG 5363 VALVE ON LINE 300A ODOR; NONE NO LEAK FOUND
| 10-20551-1 |  |  | 20 | Transmission |  | Valves |  |  | Unknown |  | 2010-04-09 | 2010-06-29 | Other | GREASED | Steel/Wrought Iron |  | SAN JOSE | E. CAPITOL EXPY / CUNNINGHAM AVE; GREASED & OPERATED VALVE; GREASED VALVE, OPERATED VALVE, SOAP TEST - GOOD
| 10-10211-1 |  |  | 8 | Transmission |  | Valves |  |  | Other | VALVE JUST NEEDED TO BE WORKED |  | 2010-05-20 | Other | WORKED GATE VALVE BACK & FORTH | Steel/Wrought Iron |  | GILROY | LEAK ON VALVE OVER HP MAIN SOUTH SIDE OF STREET; WORKED GATE VALVE - SOAP TESTED - NO BUBBLES ON FOAM
| 10-10187-1 | [5 empty] | Valves |  |  | Other | NEEDED GREASE | 2010-05-12 | 2010-05-14 | Other | GREASE | Steel/Wrought Iron |  | SAN JOSE | LEAK IN VALVE VIXES V-16, V-I A LOT OF ODOR IN AIR; GREASED VALVE - SOAP TESTED
| 10-10187-1 |  |  |  | Transmission | VALVE | Valves |  |  | Other | NEEDED GREASE | 2010-05-12 | 2010-05-14 | Other | GREASED | Steel/Wrought Iron |  | SAN JOSE | LEAK IN VALVE BOXES V-16, V-I, A LOT OF ODOR IN AIR; GREASED VALVE; GREASED VALVE - SOAP TESTED; SEE ATTACHED SHEET
| 10-20550-1 |  |  |  | Distribution Main | VALVE | Valves |  |  | Other | DRIED UP GREASE | 2010-04-09 |  | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN JOSE | GALAHAD & STORY RD HI TO HI BOX IS LEAKING BY TRAN; HI TO HI BOX IS LEAKING BY TRANSMISSION; (FOUND NO LEAK) LEAK E(V-2) VALVE GREASED & TIGHTEN BOLTS; GREASED VALVE, SOAP TEST ( TIGHTENED BOLTS), GAS SENTR BOTH VAULTS - 0, GAS TRACK BOTH VAULTS - 0, TEST WATER BOX - 0
| 09-10275-1 | [10 empty] | 2009-11-23 | [5 empty] | MORGAN HILL | 5% GAS IN SECONDARY ELECTRIC BOX
DRILLED HOLES OVER BOTH MAINS, AND SERVICE. SOAP STEEL VALVE. SOAPED FITTING INSIDE REG VAULT. 11-23-2009; SHUT-IN STATION TO ELIMINATE LEAK. GAS ENGINEERING TO REVIEW ABANDONED/REBUILD OPTIONS.; STATION "SHUT IN" 2/5/10 BY FRED GARCIA ...
| 09-10275-1 |  |  | 2 | Distribution Main |  | Regulator |  |  | Equipment Malfunction |  | 2009-11-23 | 2010-02-05 | Other | SHUT-IN STATION | Steel/Wrought Iron |  | MORGAN HILL | 5% GAS IN SECONDARY ELECTRIC BOX; SHUT-IN STATION THAT WAS VENTING GAS; DRILLED HOLES OVER BOTH MAINS, AND SERVICE. SOAP STEEL VALVE. SOAPED FITTING INSIDE REG VAULT. 11-23-09. SAN JOSE GAS T&R ELIMINATED LEAK BY SHUTTING-IN REG STATION H-13 AT HILL & DIANA. PROBLEM W/2-PILOT REGULATOR
| 09-10275-1 | [10 empty] | 2009-11-23 | [5 empty] | MORGAN HILL | DIANA AVE & HILL RD 5% GAS IN SECONDARY ELECT BOX; OUT OF #2 SPICE BOX USED AS A VENT BOX; DRILLED HOLES OVER HOTH MAINS, AND SERVICE. SOAP STEEL VALVE. SOAPED FITTING INSIDE REG VAULT. 11-23-09
| 09-95708-1 |  |  | 6 | Transmission |  | Valves |  |  | Unknown |  | 2009-07-24 | 2010-02-08 | Other | GREASED VALVE | Steel/Wrought Iron |  | SANTA CLARA | GREASED VALVE; SEE ATTACHED SHEET
| 09-91012-1 |  |  | 2 | Transmission |  | Valves |  | 3 VALVES |  |  | 2009-03-16 | 2009-11-13 | Tighten Cap/Bolt - Fitting | LUBED | Steel/Wrought Iron |  | GILROY | TWO PIPES ON FORM; TRANSMISSION BOX; TIGHTEN TWO LEAKS GREASED 1; REPAIR LEAKS STAGE #1 SOAP TEST/GOOD.
| 09-10013-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other | NORMAL WEAR & TEAR | 2009-01-11 | 2009-03-18 |  |  | Steel/Wrought Iron |  | MORGAN HILL | RISER THREADS; RISER, ON HIGH TO HIGH SET CALLED MOREEN T&R SHE IS TO FIX ON 3/18/09; REPAIRED - LEAKS SOAP TEST OK. TORE APART - RETIGHTEN; SOAP TEST FITTINGS
| 09-93953- |  |  | 0.75 | Transmission |  | Other |  | DRIED OUT PIPE DOPE | Other | DRIED OUT PIPE DOPE | 2009-04-13 | 2009-04-13 | Other | APPLIED PIPE DOPE TO THREADS & RETIGHTENED FITTINGS | Steel/Wrought Iron |  | MORGAN HILL | LEAKING ON HIGH-TO-HIGH SET; HIGH TO HIGH SET SERVING ONE HOUSE. USED HOT TANK TO KEEP GAS ON TO HOUSE. SHUT DOWN HIGH TO HIGH IN ORDER TO MAKE REPAIRS. DISMANTLED & APPLIED PIPE DOPE ON THREADS OF FITTINGS THAT WERE LEAKING.
| 10-21811-1 | 100 | 149.3 | 0.06 | Distribution Main |  | Valves |  |  | Incorrect Operation |  | 2010-11-08 | 2010-11-08 | Tighten Cap/Bolt - Fitting | SOAP AND/OR TAPE | Steel/Wrought Iron |  | MILPITAS | BELOW GROUND AT VALVE BOX 158 NORTH EAST OF ADDRESS; TIGHTEN VALVE ONTO NIPPLE. TIGHTENED 2 VALVE HANDLE, TIGHTENED PLUG
| 10-81020-1 | 1 |  |  | Transmission |  | Valves |  |  | Other | DRY GREASE | 2010-09-27 | 2010-11-19 | Other | GREASE VALVE | Steel/Wrought Iron |  | SAN JOSE | 100' W/O ULTRASONIC MTR VALV LID, Y-DOT; GREASED - VALVE - SOAP TEST OK
| 10-81030 | DREG5392 | 0 | 0.75 | Transmission >= 20% SMYS |  | Other |  | STEEL CAP | No/Deteriorated Pipe Dope |  | 2010-09-28 | 2010-11-18 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | MORGAN HILL | N/O HALF & COCHRANE RDS - 1ST STEPDOWN REG; 1ST STEPDOWN REG OFF TRANSMISSION LINE; TIGHTEN CAP; TIGHTENED CAP TO FIRST STAGE REG PIN OFF. SOAP TEST OK.
| 10-81031-1 | 1 | [9 empty] | 2010-09-28 | [5 empty] | S. JOSE | SURECREEK VLY;2 W VAULTS&FITTING ABOV GRND
| 10-81060-1 | 1 | [9 empty] | 2010-09-28 | [5 empty] | MILPITAS | IN REG STAT ON SILVER CREEK IN VLV 1;DS
| 10-81061-1 | 1 | [9 empty] | 2010-09-28 | [5 empty] | SAN JOSE | IN REG STAT ON SILVER CREEK IN VLV 1;DS
| 10-81101-1 | [10 empty] | 2010-09-25 | [5 empty] | SAN JOSE | IN MEDIAN; YELLOW DOT; IN FRONT OF 15780 ALMADEN E; SCANNED & EMAILED TO: MIKE AVELLA, TODD ARNETT, ERNIE SOMERA, CC: JASON RETDER, SCOTT FANNIN, MAKIBI TAKAGI, MAUREEN FITZGERALD
| 10-81104-1 |  |  | 4 | Distribution Main |  | Fitting |  |  | Equipment Malfunction | LOOSE | 2010-09-26 | 2010-10-23 | Other | TIGHTEN FITTING | Steel/Wrought Iron |  | SAN JOSE | IN VAULT @ BUS STATION ON SNELL N/OF BLOSSOM HILL; TIGHTEN - FITTING; TIGHTEN - FITINGS - SOAP TEST OK
| 10-81110-1 | 1 | [9 empty] | 2010-10-20 | 2010-10-20 |  |  |  |  | GILROY | CALPINE POWER FLNT REG STA;Y-ZIP TIE ON LK; NO LEAK FOUND; ADVISED CUST NO AWARE OF LEAK, COULD NOT FIND LEAK; COULD NOT FIND LEAK
| 10-81112-1 | 1 |  | 0.75 | Service |  | Valves |  |  | Unknown |  | 2010-09-27 | 2010-10-23 | Other | GREASED VALVE | Steel/Wrought Iron |  | GILROY | Y-ZIP TIE ON LK; GREASED VALVE; GREASED VALVE - SOAP TEST OK
| 10-81114-1 | 1 | [9 empty] | 2010-09-27 | [5 empty] | SAN JOSE | 200'W/O CRT ON N/S OF STRORY RD
| 10-81115-1 | 0813-01 | 0 66 | [8 empty] | 2010-09-27 | [5 empty] | SAN JOSE | VLV CASING @ INT/O SILVER CREEK VALLEY RD/FORD RD.; NO GAS FOUND
| 10-81116-1 | 300A |  | 6 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2010-09-27 | 2010-10-21 | Tighten Cap or Bolt |  | Other | STAINLESS STEEL | SAN JOSE | @ REG STATION BEHIND FENCE 1% @ 2 SOUTH REG VAULTS; TIGHTEN 1/2" TEE ON D/S SENSE LINE; TIGHTEN SENSE LINE TEE D/S OF REG. SOAP TEST.
| 10-81117-1 |  |  | 6 | Transmission |  | Unknown |  |  | Unknown |  | 2010-09-27 | 2010-10-23 | Other | NO LEAK | Steel/Wrought Iron |  | SAN JOSE | N/E COR POUGHKEEPSIE/COTTLE @ HIGH VOLTAGE VAULT; @ HIGH VOLTAGE VAULT ON N/E COR @ PAC BE; NO LEAK FOUND; NO - LEAK FOUND SOAP TEST OK
| 10-81123-1 | [10 empty] | 2010-09-26 | [5 empty] | SAN JOSE | NXT TO RRXING NEXT TO AT OR UNDER BUILDING
| 10-81123-1 | [10 empty] | 2010-09-26 | [5 empty] | SAN JOSE | COMPLETED; NXT TO RRXING NEXT TO AT OR UNDER BUILDING; ON DISTRIBUTION/METER SET NO A-FORM NEEDED
| 10-81160-1 | 1 | [9 empty] | 2010-09-27 | [5 empty] | MILPITAS | YELLOW DOT ON SMALL VAULT
| 10-81161-1 | 1 |  | 0.25 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2010-09-27 | 2010-10-23 | Other | TIGHTEN STAINLESS STEEL FITTINGS | Other | STAINLESS STEEL | SAN JOSE | REG VAULT; RETIGHTEN 2 FITTINGS ON SENSE/MAIN REG PIT; TIGHTENED 2 FITTING ON REG PIT SENSE LINE SOAP TEST OK
| 10-81162-1 | 132 | 1 89 | 6 | Transmission |  | Valves |  |  | Incorrect Operation |  | 2010-09-27 | 2010-10-23 | Other | RESEALED GATE VALVE | Steel/Wrought Iron |  | SAN JOSE | VALVE CASING; SAME, CORRECTED; RESEAKED GATE VALVE; RESEALED GATE VALVE - SOAP TEST OK
| 10-81181-1 | 100 | 14805 | [8 empty] | 2010-09-27 | [5 empty] | MILPITAS | DISTRIBUTION/NOT TRANS; REGATE LID Y-DOT
| 10-81181-1 |  |  |  | Distribution Main | [6 empty] | 2010-09-27 | 2010-10-21 |  |  | Steel/Wrought Iron |  | MILPITAS | REGSTA LID Y-DOT; NO LEAK FOUND; LEAK REPAIRED DURING OCTOBER MAINTENANCE; SOAP TEST OK (NO LEAK FOUND) MAINTENANCE WAS PERFORMED IN OCT. LEAK REPAIRED AT THAT TIME.
| 10-81182-1 | [10 empty] | 2010-09-27 | [5 empty] | MILPITAS | Y-DOT ON VALV NXT TO ADRS
| 10-81208-1 | 300B |  | 34 | Transmission |  | Valves |  |  | Other |  | 2010-09-29 | 2010-10-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MORGAN HILL | CGT LEAK NO T&R; CAN'T READ
| 10-81510-1 | 0833-01 | 6 47 | [8 empty] | 2010-10-10 | [5 empty] | GILROY | VALVE COVER AT DRIVEWAY
| 10-81530-1 | 0817-01 | 0 69 | [8 empty] | 2010-10-10 | [5 empty] | SAN JOSE | REPAIRED BY G.C. 10/19/10; D/WY OFF OLINDER CT @ PITS IN DRIVEWAY
| 10-81534-1 | 0817-01 | 0 78 | [8 empty] | 2010-10-10 | [5 empty] | SAN JOSE | S/E CRNR XST/W MCLAUGHLIN;PATCH
| 10-81683 | 300A | 47397 |  | Transmission >= 20% SMYS |  | Fitting |  |  | Other | TIGHTEN | 2010-10-11 | 2010-12-14 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | MORGAN HILL | VALV @XST W/FOOTHILLS; TIGHTEN; TIGHTEN, SOAPED OK; LEAK IN VALVE PIT, STEM LEAKING. VERY LOOSE. TIGHTEN, ALSO LEAK IN REG STATION
78 | 10-81684-1 | 300A | 47397 |  | Transmission >= 20% SMYS |  | Fitting |  |  | Other | TIGHTEN | 2010-10-11 | 2010-12-14 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | MORGAN HILL | 4'W/O ELECPOLE;DIRT CRNRS, VALV 41G8; TIGHTEN; TIGHTENED - SOAP OK, LEAK IN REG STATION (PLUG LEAKING, TIGHTENED); SEE MAP ATTACHED
| 10-81685 | 300A | 47397 |  | Transmission >= 20% SMYS |  | Other |  | SCADA TAP VALVE | Other | RE SEAT | 2010-10-11 | 2010-12-14 | Other | RE SEATED | Steel-Other |  | MORGAN HILL | IN LOSALTOS;XST FOOTHILL;VALE 41 G&C; 15'E/O ELECPOLE BY 1ST METAL STA ON TENN; RESEATED; RE-SEATED VALVE - (PIN OFF) SOAP TEST; SEE ATTACHED SKETCH
| 10-81686-1 | 300A | 47541 | 0.75 | Transmission |  | Regulator |  |  | Other | REG FAILED | 2010-10-11 | 2010-11-16 | Other | REBUILT 1ST. STAG | Steel/Wrought Iron |  | MORGAN HILL | REBUILD 1ST & 2ND STAGES HIGH TO HIGH; HENDRY;W/O HS;YELLOW TIE; NEED TO VERIFY HIGH TO HIGH FEED 1 CUSTOMER; 2 DOG SIGNS WARNING, DOG PRESENT, OWNER NOT @ SITE; 1ST STAGE DIAPHRAGM FAILED; REBUILT 1ST STAGE, SOAPTEST OK; SEE ATTACHED MAP
78 | 11-10124-B |  |  | 2 | Transmission >= 20% SMYS |  | Pressure Control Fittings |  |  | No/Deteriorated Pipe Dope |  | 2011-04-19 | 2011-07-11 | Other | RE-DOPE AND TIGHTEN CAP | Steel/Wrought Iron |  | SAN MARTIN | FOUND AREA DOWN - SPANED AREA - NOTHING FOUND - AJUSTED RECT. SUMMER DRY OUT. AREA UP HAS GOOD CP. OGT9 7-23-11; 40% TRANSMISSION MAIN, FOUND ON SPECIAL SURVEY DURIN OVERPRESSURISED MAIN; REDOPE CAP, TIGHTEN COMPLETION PLUG; REDOPE AND TIGHTEN CAP ON 2" SPLIT CONTROL
78 | 11-10401-B |  |  | 2 | Transmission >= 20% SMYS |  | Pressure Control Fittings |  |  | No/Deteriorated Pipe Dope |  | 2011-07-11 | 2011-07-13 | Other | INSTALL HP CAP RE-DOPE/TIGHTEN CAP | Steel/Wrought Iron |  | SAN MARTIN | 70% OVER TRANSMISSION MAIN 2" STL; TIGHTEN COMPLETION PLUG - INSTALL HP CAP; TIGHTEN COMPLETION PLUG (2 TURNS) INSTALL HP 1400 PSI CAP; RE-DOPE, TIGHTEN, PRESSURE WAS LOWERED FROM 300 PSI TO 55 PSI FOR REPAIR. ALSO USED FLASH SUIT SOAP TEST OK 07-13-11
|  |  |  | 8 | [11 empty] | Steel-Other |  | SAN JOSE | INSPECTION ONLY, SCAN COPY TO MAPPING, THE USUAL PROCESS - SCANNED, MARKED; ADVISED CONTRACTOR ROBERT TO CALL WHEN CROSSING
98 | 10-82003-1 | 100 | 13843 | [8 empty] | 2010-09-18 | [5 empty] | SAN JOSE | PRESSURE LIMITING STATIION 7A & 7B; KAREN - PLEASE GET TO JOHN GILLIO
78 | 10-88047-1 | 300B | 46423 | 0.75 |  |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-22 | 2011-04-19 |  |  | Steel-Other |  | GILROY | REMOVED 3/4 NIPPLE ON INLET SIDE OF HIGH TO HIGH SET AND REDOPED; REMOVED AND REDOPED 3/4" NIPPLE; SEE ATTACHED MAP
78 | 10-88041-1 | 300A |  | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-21 | 2011-02-28 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SAN MARTIN | CAP ON REDUCER RISER MARKED WITH YELLOW TIE; PLEASE SCAN COPY FOR OUR BINDER SEND ORIGINAL TO MAPPING; PIN OFF CAP LEAKING; REDOPED AND TIGHTENED PIN-OFF TEE CAP. SOAP TEST GOOD.
|  | 0821-02 |  | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-09-26 | 2011-03-07 | Deactivated Partial Service | MECHANICAL REPAIR FITTING - FITTING, OTHER | Steel-Other |  | SAN JOSE | SHOULD BE A NEW LEAK #; O/S@3/4" ELBOW W/S OF PROP. NXT TO SD/WK; TIGHTEN FITTING
| 10-11342-1 | [10 empty] | 2010-11-08 | [5 empty] | SAN JOSE | HIGH TO HIGH SET ON SIDEWALK; INFO ONLY; 3/17/11 JOANN = PLEASE HAVE TWC8 TRANSFER INFORMATION FOR COPY OF LEAK SHEET TO ORIGINAL IT WAS DONE UNDER WRONG LEAK # & ADDRESS
98 | 10-88421-1 | 300B | 46052 | 0.75 | Transmission >= 20% SMYS |  | Line Valve | Fitting |  | Other |  | 2010-10-22 | 2011-03-18 | Greased - Other | MECHANICAL REPAIR FITTING - FITTING, OTHER | Steel-Other |  | HOLLISTER | ABOVE GROUND LEAK @REG STATION @REGULAR FITTINGS; REPAIR MULTIPLE LEAKS; HOT TANK
78 | 10-11342-1 |  |  | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-11-08 | 2011-03-07 | Deactivated Partial Service | MECHANICAL REPAIR FITTING - FITTING, OTHER | Steel-Other |  | SAN JOSE | HIGHT TO HIGH SET ON SIDEWALK; HIGH TO HIGH; TIGHTEN FITTING
78 | 10-88048-1 | 300B | 46422 | 0.75 | Transmission >= 20% SMYS |  | Riser Valve Threads |  |  | Other |  | 2010-10-22 | 2011-03-11 | Replace Valve >= 2 inch | MECHANICAL REPAIR FITTING - FITTING | Steel-Other |  | GILROY | 25'N/W FRM HS BY MRKR POLE IN D/WY; NONE; REDOPED & TIGHTEN INLET VALVE REPLACED & 3/4" PIPE HP; 2-2-11 REPAIRED TWO LEAKS. 2-3-11 WENT TO MAPPING. TO GET ASBUILTS. 03-11-11 REPLACED 1/2" VALVE & 3/4" FITTING
78 | 10-81106-1 | 0821-02 |  | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-09-26 | 2011-03-07 | Deactivated Partial Service | MECHANICAL REPAIR FITTING - FITTING, OTHER | Steel-Other |  | SAN JOSE | O/S@3/4" ELBOW W/S OF PROP. NXT TO SD/WK; SAME, SAME, SAME, SAME; TIGHTEN FITTING
78 | 10-81688-1 | 300B | 47364 | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-11 | 2011-02-28 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | MORGAN HILL | 10'E/O ELECPOLE BY TREES HIGH TO HIGH SET BETWEEN PROPERTIES BUSHES; SAME; 1ST & 2ND STAGE MULPT. LEAKS HPR; FITTINGS REDOPED & TIGHTEN ON 1ST & 2ND STAGE HPR SOAP TEST & CLOCK TEST GAS SERVISE. GC WELDER REPLACE INLET 3/4" HP PIPE.
78 | 10-81028-1 | 0809-02 | 0 07 | [8 empty] | 2010-09-28 | [5 empty] | MORGAN HILL | TAGGED W/ZIP TIES;AX FRM 2260 END OF DIANA AVE OVER TRANS. LINE.; TO JOHN GILLIO PICTURE ON BACK, 2/25/11 RESCAN TO GILLIO KAR9
78 | 10-81113-1 | 0809-01 | 199 | 4 |  |  | Line Valve |  |  | Other | PIPELINE UNDER WATER | 2010-09-27 | 2011-02-22 | Greased - Other |  | Steel-Other |  | MORGAN HILL | XST BUTTERFIELD, TRANSMISSION P.M. PLEASE MAKE US A COPY & SCAN; SAME, REG. PIT; GREASED TWO VALVES IN MAN HOLE (INLET & CUTLET); GREASED VALVES. 3 VALVES; SOAP TEST OK
78 | 10-88046-1 | 300A | 46625 | 0.75 |  |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-10-22 | 2011-02-09 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | GILROY | LK ON RISER #MP466.29A MRKD W/Y-TIE; NONE; REDOPED & TIGHTENED NIPPLE - SOAP TEST OK
78 | 10-88046-1 | 300A | 46625 | [8 empty] | 2010-10-22 | [5 empty] | GILROY | LK ON RISER #MP466.29A MRKD W/Y-TIE; NONE
| 10-20601-1 | [10 empty] | 2010-04-29 | [5 empty] | MILPITAS | READINGS FROM BOXES OVER TRANSMISSION LINE BEHIND HOTEL, V-3 (5%), V-600 (1%), V-602 (100%); PARKING LOT
78 | 10-88160-1 | 300A | 46747 | 0.75 |  |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-22 | 2011-02-02 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | GILROY | 35'N/O FENC LINE OFF ST; HIGH TO HIGH SET; REPAIRED LEAK; REPAIRED LEAK. SOAPTEST OK
78 | 10-88049-1 | 300A | 46747 | 0.75 |  |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-22 | 2011-02-02 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | GILROY | XST VIADELCIELO;25'N/O PROP/FNC/LINE BY ST; HIGH TO HIGH SET; REPAIRED LEAK; REPAIRED LEAK, SOAPTEST OK.
78 | 10-81119-1 | 0810-01 | 0 1 | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-09-28 | 2011-01-24 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | GILROY | ON INLET SIDE OF REG OF STP DOWN STATION; SAME; RE-DOPE, TIGHTEN FITTING ON 3/4" H.P. UNION; TIGHTEN 3/4" H. PRESSURE UNION. PAINT HPR SET INSTALLED 1/4" VENT SOAP TESTED, OK.
78 | 10-88023-1 | 0810-01 | [9 empty] | 2010-10-21 | [5 empty] | GILROY | 1/26/11 - PER MER9 - GAS SUC. WAS EMAILED MAIL TO MAPPING; LEAK ON METER AT 2760 ROOP RD. MARKED W/YELLOW TAP MTR# 986099E; NEED 3/4" PROBE HOT TANK SINGLE REG. FISHER S402 SPRAGNE 250-MTR RD 5176
78 | 10-88020-1 | 0810-01 | 20 | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-21 | 2011-01-25 | Mechanical Repair Fitting - Fitting |  | Steel-Other |  | GILROY | LEAK IS AT TAP IN FRONT OF 3240 ROOP RD MARKED YEL; REPLACED & TIGHTENED 3/4" FITTING; NEW 3/4" NIPPLE (FITTING) SOAP TEST PASSED
78 | 10-88023-1 | 0810-01 | [9 empty] | 2010-10-21 | [5 empty] | GILROY | 1/26/11 - PER MER9 - GAS SUC. WAS EMAILED MAIL TO MAPPING; LEAK ON METER AT 2760 ROOP RD. MARKED W/YELLOW TAP MTR# 986099E; NEED 3/4" PROBE HOT TANK SINGLE REG. FISHER S402 SPRAGNE 250-MTR RD 5176
78 | 10-81682-1 | 300B | 47657 | 0.75 |  |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-10-11 | 2011-01-25 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | MORGAN HILL | RISER S/O N RISER;YELLOW TIE; SAME; CLEANED, DOPED, TIGHTENED
78 | 10-81681-1 | 300B | 47728 | [8 empty] | 2010-10-11 | [5 empty] | MORGAN HILL | RISER BHD BLDG ON S/S;YELLOW TIE; SAME, SAME, NO LEAK FOUND; NO LEAK FOUND
78 | 10-81680-1 | 300B | 47728 | [8 empty] | 2010-10-11 | [5 empty] | MORGAN HILL | RISER W/S BLDG YELLOW TIE; SAME, SAME, NO GAS FOUND; NO LEAK FOUND
78 | 10-88042-1 | 300A | 47059 | 0.75 |  |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-10-21 | 2011-01-28 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SAN MARTIN | THREAD IN REDUCER VALVE; CLEANED, DOPED, TIGHTENED
78 | 10-81403-1 | 0804-08 | 0 59 | 4 | Distribution Main <= 60 PSIG |  | Other |  | NO LEAK FOUND | Other | NO LEAK FOUND | 2010-09-26 | 2010-10-05 | Other | NONE | Steel-Other |  | SANTA CLARA | 20' S/O PVT DR S/O CENTRAL EXPWY ON LAFAYETTE; FOUND NO LEAK; NO LEAK FOUND; E-17 "A" INSP DONE 10/05/10 PER REG. MAINT. FORM RESULT - PASS SOAP TEST PIPING GOOD. STATION VALVES OPERATED & LUBED. PIPE & CONDITION GOOD
| 03-50055-1 | [10 empty] | 2003-06-11 | [5 empty] | SAN JOSE | OVER MAIN, PUNCH HOLE OVER MAIN VENTING OUT, LEAK OVER FEEDER MAIN IN STREET, F/O IN STREET NEAR SOUNDWALL
| 95-40173-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | External Corrosion |  | 1995-05-04 | 1995-06-28 | Patch Welded |  | Steel/Wrought Iron |  | SAN JOSE | IN FRONT OF TT&T AUTO SERVICE; 195# F.P. LOWERED TO 60# ARC WELDED 10" LONG HALF SOLE PATCH .375 WALL THICK. OVER CORROSION LEAK ON 8" F.P. MAIN
78 | 93-10084-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1993-02-24 | 1993-06-22 | Patch Welded |  | Steel/Wrought Iron |  | SAN JOSE | ARC WELDED A PATCH OVER THE LEAK
78 | 97-10008-1 |  |  | 8 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1997-01-10 | 1998-03-23 | Other |  | Steel/Wrought Iron |  | SAN JOSE | GREASE VALVE
78 | 92-10208-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | External Corrosion |  | 1992-09-21 | 1992-10-08 | Patch Welded |  | Steel/Wrought Iron |  | SAN JOSE | ARC WELDED A PATCH OVER THE PIT
78 | 97-10003-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Material Failure |  | 1997-01-08 | 1998-04-09 | Other |  | Steel/Wrought Iron |  | SAN JOSE | REGULATION INSTALLED GATE VALVE REPAIR KIT
78 | 95-50200-1 |  |  | 3 | Distribution Feeder Main |  | Fitting |  |  | Other |  | 1995-12-27 | 1995-12-27 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SAN JOSE | PRIMARY PIT. REDOPE AND TIGHTEN CAP
78 | 95-50194-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | External Corrosion |  | 1995-12-08 | 1995-12-08 | Patch Welded |  | Steel/Wrought Iron |  | SAN JOSE | WELD 12"X12" PATCH.
78 | 93-10136-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | External Corrosion |  | 1993-04-07 | 1994-06-06 | Patch Welded |  | Steel/Wrought Iron |  | SAN JOSE | ARC WELDED A PATCH OVER THE LEAK.
78 | 93-10112-1 |  |  | 10 | Distribution Feeder Main |  | Body of Pipe |  |  | External Corrosion |  | 1993-03-12 | 1993-03-29 | Patch Welded |  | Steel/Wrought Iron |  | SAN JOSE | ARC WELDED A PATCH OVER THE LEAK.
78 | 94-40287-1 | [10 empty] | 1994-09-27 | [5 empty] | SANTA CLARA | JW AREA UNABLE TO DEFINE LEAK. - RECHECK IN 2 MONTHS.
78 | 94-40287-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | External Corrosion |  | 1994-09-27 | 1995-10-04 | Patch Welded |  | Steel/Wrought Iron |  | SANTA CLARA | ARC WELDED 12" LONG HALF SOLE PATCH OVER LEAKING CORROSION PIT ON BOTTOM SIDE OF 6" F.P. GAS MAIN.
78 | 94-40287-1 |  |  | 6 | Distribution Feeder Main |  | Body of Pipe |  |  | External Corrosion |  | 1994-09-27 | 1995-10-04 | Patch Welded |  | Steel/Wrought Iron |  | SANTA CLARA | ARC WELDED 12" LONG HALF SOLE PATCH OVER LEAKING CORROTION PIT ON BOTTOM SIDE CORROSION PIT ON BOTTOM SIDE OF 6" F.P. GAS MAIN.
78 | 94-40290-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1994-09-28 | 1994-09-28 | Other |  | Steel/Wrought Iron |  | SANTA CLARA | FOUND LEAKING STEM ON F.P. VALVE II 21 F3B LEAK ELIMINATED BY GREASING OF VALVE BY M&C DEPT.
78 | 94-40290-1 |  |  | 6 | Distribution Feeder Main |  | Valves |  |  | Other |  | 1994-09-28 | 1994-09-28 | Other |  | Steel/Wrought Iron |  | SANTA CLARA | FOUND LEAKING STEM ON F.P. VALVE II 21 F3B LEAK ELIMINATED BY GREASING OF VALVE BY M&C DEPT.
|  |  |  | 4 | [7 empty] | 2011-02-07 |  |  |  | Steel-Other |  | SAN JOSE
| 05-00001-1 | [10 empty] | 2005-10-20 | [5 empty] | HAYWARD | ORIGINALLY REPORTED ONLEAK LOG-SURVEY; 05-00001-1; S/E SIDE OF W. WIN VALVE X-14 E/O RR & TP LINE 153/; @ MAN HOLE IN ST. VALVE X-14 E/O RR & T
| 05-60415 | 101 | 19.43 | 0.75 | Transmission |  | Fitting |  |  | Construction Defect |  | 2005-12-10 | 2005-12-13 | Other | INSTALLED PLUG | Steel/Wrought Iron |  | REDWOOD CITY | POINT; 05-60415-1, RXT7; COPY -D- ON DREG, 40435595; IN FRONT OFF 755 MARSHALL AVE; REMOVED GAUGE & INSTALLED PLUG; INSTALLED PLUG
| 05-00000-1 | [10 empty] | 2005-10-17 | [5 empty] | SAN LEANDRO | ORIGINALLY REPORTED ON LEAK LOG SURVEY; @ BX F&c OF VALVE X-03 TP LINE 153/ELEC SUB STATIO; @ BX F&C OF VALVE X-03 TP LINE 153 NXT TO
| 05-00001-1 | [10 empty] | 2005-10-20 | [5 empty] | HAYWARD | ORIGINALLY REPORTED ON LEAK LOG SURVEY; S/E SID OF W. WIN VALVE X-14 E/O RR& TP LINE 153/; @ MAN HOLE IN ST. VALVE X-14E/O RR & T
| 05-50080-1 | [10 empty] | 2005-11-04 | [5 empty] | SALINAS | 05-50080-1; IGIS MAP; 200' S/O SHERWOOD PL. ON RIGHT SIDE OF SHERWOOD DR.; MAIN INSIDE CASING
| 05-00037 | [10 empty] | 2005-02-01 | [5 empty] | YUBA CITY | 05-00037-1, HCA-N, NOT TRAN IN HPR BOX; W/S N. TOWNSHIP RD AT HPR BOX; 3699 W. TOWNSHIP RD
| 05-20005-1 | 135-01 | [9 empty] | 2005-09-21 | [5 empty] | BOYES SPR | 05-20005-01 KYN2; NOT REPAIRED; AT HPR BOX; AT HPR BOX;
| 05-00210-1 | [10 empty] | 2005-08-14 | [5 empty] | MARYSVILLE | 05-00210-1, HCA-N; FENCP OST AT DRIVEWAY NORTH SIDE
| 05-10132-1 |  |  | 8 | Transmission | [6 empty] | 2005-08-16 | [5 empty] | SAN JOSE | 05/10132-1, HCA-N DFM 0813-082% ON FEEDER MAIN; ON FEEDER MAIN
| 05-11002-1 | 153 | [9 empty] | 2005-05-24 | [5 empty] | FREMONT | 05/11002-1 HCA-N, DREG4865, TI; O/HP VALVE F&C @ D-43 L-153; O/HP F&C @ # D-43 L-153
| 05-20007-1 | [10 empty] | 2005-09-21 | [5 empty] | GLEN ELLEN | 05/20007-1 KYN2; NOT REPAIRED; E/S ARNOLD 250' N/O AGUA CALLENTE RD; AT GUARD RAIL & CULVERT E/S OF ARNOLD DR
| 05-20054-1 | [10 empty] | 2005-10-24 | [5 empty] | WATSONVILLE | 05/20054-1; IGIS T. WRIGHT; HI TO HI SERVICE
| 05-20064-1 | [10 empty] | 2005-11-22 | [5 empty] | PAJARO | 05-20064-1; IGIS MP; BLOW OFF NOT ON MAP; BLOW OFF .5%
| 05-20068-1 | [10 empty] | 2005-11-22 | [5 empty] | AROMAS | 05-20068-1; IGIS MP; HIGH TO HIGH REG NEXT TO VALVE 2 & 20; ____MAX LOOK LIKE____
| 05-20069-1 | [10 empty] | 2005-11-22 | [5 empty] | AROMAS | 05-20069-1; IGIS MP; HIGH TO HIGH BOX; HIGH TO HIGH REG #1 BOX
| 05-20164 | [10 empty] | 2005-05-04 | [5 empty] | ANTELOPE | 05-20164-1 HCA-N, DFDS 3562; TRANSMISSION SEMI-ANNUAL; OVER VALVE #24; OUTSIDE STATION, GROUND TOO WET TO GET M&C TRACK M TO GREASE VALVE WALL GREASE WHEN GROUND DRIES
| 05-40088-1 | [10 empty] | 2005-11-03 | [5 empty] | SEBASTOPOL | 05-40088-1 KYN2; NOT REPAIRED; HWY 116 & OCCIDENTAL RD - SEBASTOPOL AREA; FLANGE VALVE LEAK AT REG #408-CGT TO DRA
| 05-40101-1 | 401 | 233.89 | 0.75 | Transmission |  | Valves |  |  | Unknown |  | 2005-06-23 | [5 empty] | DUNNIGAN | 05-40101-1; SOUTH END OF M-401 INST. BUILDING (GAS RACK); SMALL LEAKS ON MARPAC UNION TYPE VALVES.
| 05-20066-1 | [10 empty] | 2005-11-22 | [5 empty] | AROMAS CO AREA | 05-20066-1; IGIS MP; REG MARKED "R" VAULT "R"; OUT OF VAULT "R"
| 05-20067-1 | [10 empty] | 2005-11-22 | [5 empty] | AROMAS CO AREA | 05-20067-1; IGIS MP; OUT OF VAULT "M"; VAULT "M"
| 05-50031-1 | [10 empty] | 2005-04-21 | [5 empty] | SALINAS | HCA-N TI, DREG 5413, 05-50031-1; WEST SIDE OF HITHCOCK RD OVER VALVE IN FRAME & COVER; VALVE
| 05-50053-1 | [10 empty] | 2005-06-06 | [5 empty] | SALINAS | 05-50053-1 HCA-N; 755 HWY 68 28' W/O MAIL BOY EDGE OF ROAD; MAIN; 755HWY68, LEAK NO 05-50053
| 05-50080-1 | [10 empty] | 2005-11-04 | [5 empty] | SALINAS | 05-50080-1; IGIS MP; 200' S/O SHERWOOD PL. ON RIGHT SIDE OF SHERWOOD DR.; MAIN INSIDE CASING
| 05-80239-1 |  |  | 0.75 | Gathering |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2005-08-17 | 2005-08-17 | Other | CUT & | Steel/Wrought Iron |  | EL CERRITO | ON SERVICE AT RISER; ____AREA; CUT &____
| 05-80128-1 |  |  | 0.5 | Gathering |  | Body of Pipe |  |  | Digin |  | 2005-04-21 | 2005-04-21 | Service Partially Replaced |  | TR 418 |  | BERKELEY | PERCKEN GAS SERVICE; ON SERVICE; INSTALLED___OF 1/2"_____
| 05-80104-1 |  |  | 16 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2005-03-24 | 2005-03-24 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | BERKELEY | DISTRIBUTION HP; ON MAIN, VENTING TO SEWER; ON MAIN VENT TO SEWER, TEMP REPAIRS INSTALLED 16" CLAMP; INSTALLED 16" CLAMP FOR TEMP. REPAIRS (NEEDS TO SEE WHO____
| 05-60199 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 2005-07-26 | 2005-07-26 | Service Partially Replaced |  | TR 418 |  | SAL | ON LINE 24" IN FROM PROPERTY -121' EAST O/SAN JOSE STREET; "DIG-IN"; REPLACED 1' OF DAMAGED PIPE; REPLACED 1' OF 1/2" PLASTIC USING (2) MIT & FIT COUOPLINGS; LINE INSERTED 1 1/4" STREET CASING 1" COPPER CASING
| 05-62705-1 | 131 | 43.28 | 4 | Service |  | Fusion Joint |  |  | Damage by Natural Forces |  | 2005-09-13 | 2005-09-14 | Replace Dist Main < 100 ft |  | Aldyl A (Tan or Gray) |  | SUNOL | OVER 4" MAIN 290' E/O HIGH TO HIGH SET; BOB GAULT; REPLACED 3' OF 4" GAS PIPE & 1-4" FUSION ELBOW; SOAP TESTED FUSIONS; LEAK ON 4" FUSION ELBOW IN 12" CASING 290' E/O HIGH TO HIGH SET.
| 05-42490-1 | 131 | 43.28 | 4 | Service |  |  |  |  | Damage by Natural Forces |  | 2005-12-27 | 2006-01-28 | Replace Partial Service |  | Aldyl A (Tan or Gray) |  | SUNOL | IN EXISTING HOLE OVER 4" SERVICE, 290 E/O HIGH TO HIGH SET; REPAIRED ONE SIDE OF OFFSET, REPAIRED - THE OTHER SIDE OF ELBOWS ON OFFSET IN CASING; ELBOWS; REPLACED THE OFF SET (2) 4" EBOWS BUT FUSION ELBOWS; SOAP TESTED - FUSIONS NO LEAKAGE
| 05-43278 |  |  | 0.5 | Service |  | Body of Pipe | Fusion Joint |  | Material Failure |  | 2005-10-01 | 2005-10-01 |  |  | Copper |  | ST. C | RISER; LEAK MIGRATING UNDER HOUSE FOUNDATION. CUSTOMER IS VERY CONCERNED; REPL. RISER
| 05-60283 |  |  | 0.5 | Gathering |  | Body of Pipe |  |  | Digin |  | 2005-09-23 | 2005-09-23 | Service Partially Replaced |  | TR 418 |  | SACRAMENTO | 100% -63' W/W/PL OF MOHAW VALLEY; OVER SUE BEHIND SIDEWALK
| 05-20208-1 | [10 empty] | 2005-08-12 | [5 empty] | BKSFLD | 3% AT RISER GAS MOVING UNDER___; SVC, LEAK IS ON CUSTOMER'S HOUSELINE S.O. NOTIFIED; CUSTOMER'S HOUSE LINE LEAKING; GAS SERVICE MAN TO CHECK AND SHUTOFF IF NEEDED
| 05-01063 |  |  | 0.75 | Service |  | Fitting |  |  | Digin |  | 2005-04-19 | 2005-04-19 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | GALT ACAMPE | @ POINT OF DAMAGE; GAS SHUT DOWN BY SERVICE MAN PRIOR TO CREW ARRIVAL; SHUT HPR DOWN & CAPPED SVC DUE TO PENDING ALTERATION; SERVICE WAS SHUT OFF @ HPR & CAPPED DUE TO PENDING ALTERATION.; FRACTURED 3/4" STL SVC CAPPED @ ELBOW DUE TO PENDING ALTERATION
| 05-30193 |  |  | 0.75 | Service |  | Riser |  |  | Atmospheric Corrosion |  | 2005-09-16 | 2005-09-16 | Other | CUT DOWN | Steel/Wrought Iron |  | SOUTH SAN FRANCISCO | SERVICE; CUT DOWN RISER REBUILD METER & INSTALLED; CUT DOWN
| 05-52481 |  |  | 0.75 | Service |  | Body of Pipe |  |  | Digin |  | 2005-09-16 | 2005-09-16 | Other | TEMP REPAIR WELD | Steel/Wrought Iron |  | OROVILLE | OPEN TRENCH - FUZZ LEAK 3/4" STL TAIL; 3/4 STL. SERVICE; TEMP REPAIR - TURNED JOB INTO ENGINEERING; TEMP REPAIR WELD; SOAP - TEST WELD TEMP REPAIR; TEMP REPAIR HYDRALIC SQUEEZE WELDED END
| 05-30- | 300B | 467 | 34 | Transmission | [7 empty] | 2005-08-15 | Welded Sleeve/Can - Weld |  |  |  |  | DIV: HOLLISTER; L-300B, M.P.467.0000; TYPE A REINFORCING STEEL SLEEVE A-60.2; A60.2
| 05-42483-1 |  | 7.3322 | 6 | Transmission |  | Body of Pipe |  |  |  |  | 2005-11-10 | 2005-11-11 | Replace TP Main |  | Steel/Wrought Iron |  | SAN RAMON | 1000' SOUTH OF BOLLINGER; REPLACE FIVE FEET OF STEEL DFM; MOUNTIN CASCADE WAS EXCAVATING TO INSTALL WATER MAIN ANDD STRUCK 6 INCH T.R/DFM LINE RUNNING PERMENDICUILAR TO THE EXCAVATION; ECAVATOR CALLED FOX STAND BY PERSON, STAND BY PERSON LOCATED 12, IN. DFM. HOWEVER, THEY DID NOT LOCATE 6 IN DFM, RUNNING PARRALLEE TO 12 IN DFM
|  |  | 6.2 | 6 | Transmission |  | Other |  | GOUGING |  |  | 2005-11-21 | 2005-11-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | YUBA CITY | GOUGING; T/P DFM NOT BROKE & BLOWING SCRATCHED; INSTALLED 6" WELD SLEEVE
| 05-55- | 103 | 17.35 | 12.75 | Transmission | [6 empty] | 2005-12-21 |  | Replaced TP Main |  | Steel/Wrought Iron |  | MONTERY COUNTY | WEST SIDE OF OLD STAGE COACH RD .5 MI NE OF HERBERT; TBD - APPX 700' TO BE REPLACED; OSCAR MARTINEZ WHILE RESPONDING TO A NEAR-BY USA NOTICED LINE 103 EXPOSED FOR ABOUT 30' AT THE W. SIDE OF COUNTY MAINTAINED OLD STAGE RD. LINE WAS INSPECTED BY AREA ENGINEER. T. ARNETT AND G. OVERMAN (TEMP GM'S) FOR CGT HOLLISTER/MILPITAS. MONTERY COUNTY PUBLIC WORKS DEPT. WAS CALLED VARIOUS COUNTY EMPLOYEES SHOWED UP. MANY WERE AWARE THAT THE PIPE LINE WAS IN THE DRAINAGE DITCH. PIPE LINE APPREARED TOBE THE LIMITER AS TO HOW DEEP THE DITCH IS CLEEARED. COUNTY EMPLOYEE'S WERE ONLY GENERALLY AWARE OF THE USA SYSTEM. L103- WAS LOWERED 10% UNTIL REPAIRS ARE COMPLETED
| 05-40- | DREG3724 | 0.14 |  | Transmission | [6 empty] | 2005-10-17 |  | Deactivate #TP Main |  | Steel/Wrought Iron |  | COTATI | DIV: NORTH COAST; DREG 3724, M.P. 0.1353, SRC RTE 1301-01, M.P. 4.500; INTERSECTION OF ARTHUR & CHARELS STREETS; THE NON-LEAKING GOUGE ON A PIPE/ELBOW WELD WAS CUT OUT; SEE EMAIL FROM GARY VOLLBRECHT DATED 10/17/05 AT 6:01PM
| 05-47- | 300-A | 278 | 34 | Transmission | [6 empty] | 2005-12-01 | 2005-12-01 | Other | RECOAT | Steel/Wrought Iron |  |  | DIST: L300N, L-300A, M.P. 278.0000; RECOAT PIPE; RECOAT; ON 12/1/05 @ APPROX. 1:30 PM L-300 N OPERATOR MECHANIC OBSERVED A THIRD PARTY TEMPORARY POLE INSTALLED OVER L-300A @ APPROX. M.P. 278. POLE WAS REMOVED AND LINE WAS EXPOSED. FIVE SCRATCHES WERE FOUND ON LINE CAUSED BY POLE. DEPTH OF SCRATCHES WERE NOT MEASURABLE. INFORMATION WAS COMMUNICATED TO ON-CALL PIPELINE ENGINEER TOM COUPE WHO DIRECTION WAS TO RECOAT SCRATCHES & BACK FILL EXCAVATION.
| 05-50089-1 | 103 |  | 12 | Transmission |  | Body of Pipe |  |  |  |  | 2005-11-05 | 2005-11-20 | Replaced TP Main |  | Steel/Wrought Iron |  | SALINAS | DIV: CENTRAL COAST, L-301, M.P. 19.1733 05-48; REPLACED 9' OF TP MAIN 12" SMLS; SEE ATTACHED TEST DATA; V19.60 IN FARMERS FIELD; CUST DIG INTO 12' TP LINE WHILE RIPPING FIELD. DID NOT CALL USA.
| 05-50- |  |  | 20 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party |  | 2005-10-24 | 2005-10-26 | Other | WELD SLEEVE | Steel/Wrought Iron |  | NOVATO | GOUGE TO 20" GAS MAIN; DIV: NORTH AY L-021G, M.P. 10.8547; 282' NORTH OF N/E PL OF OLIVE AVE; WELDED 20" DIA X 36" REPAIR SLEEVE; WELD SLEEVE; 20"X36" SLEEVE INSTALLED BY GC GAS
| 05-20061-1 | GM174439 |  | 1.25 | Transmission |  | Body of Pipe |  |  | Other | UNKNOWN | 2005-11-10 | 2005-11-15 | Other | 1 1/4 CAP | Steel/Wrought Iron |  | WATSONVILLE | ON TRANSMISSION BACK OF PROPERTY; AT CREEK XING; UNKNOWN; WELD ON 1 1/4 CAP; 1 1/4 CAP; SOAP TESTED LINE 300 PSI OK
| 05-60142 | 101 |  | 4 | Transmission |  | Physical/Mechanical Joint |  |  | Construction Defect |  | 2005-02-16 | 2005-02-25 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | REDWOOD CITY | POINT, 05-60142-1 HCA-N, 0203-5, 40435545-4015 2+ TRANS...=D; ODOR & READINGS OUT OF SEWER BAR; MARKED IN YELLOW 2' OUT FROM CURB; 3/4" SERVICE TEE ON 4" STL.
| 05-11000-1 | 105 |  |  | Transmission |  | Other |  | RELIEVER | Other | WEAR & TEAR | 2005-05-12 | 2005-07-30 | Other |  |  |  | FREMONT | 05-11000-1, HIGH TO HIGH LEAK; TD=D; O/LINE 105 30" E/O TRAIN STATION; WRONG HIGH TO HIGH, NO LEAK FOUND; RELIEVER; WEAR & TEAR; REBUILT LEAKING RELIEVER RELANCE HPE-20
| 03-21451-1 |  |  | 200 | Service |  | Valves |  |  | Construction Defect |  | 2003-09-22 | 2005-03-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN FRANCISO | 03-21451- HCA-N DCUST1434W/S OF QUINT, 30' S/O JERROLD ST GVB; GVB; TIGHTEN BONNETT ON 2" GAGE VALVE
| 05-80068-1 |  | 0.0371 | 2 | Gathering |  | Fitting |  |  | Unknown |  | 2005-02-25 | 2005-03-10 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | RICHMOND | 05-80068-1 HAC-N TRANS DEF-D; DFM 0133-03, M.P. 0.0371, DIV: EAST BAY; ON MAIN, VENTING AT SEWER & STARM MANHOLE; ON MAIN DOWN GRADED TO HOT 2
| 05-80068-1 |  |  | 2 | Gathering |  | Fitting |  |  | Unknown |  | 2005-02-25 | 2005-03-10 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | RICHMOND | ON MAIN, VENTING TO SEWER & STORM; ON MAIN, VENTING TO SEWER AND S DOWNGRADED - VENTED; REDOPED PLUG AND CAP
| 05-10012-1 | 137 | 2.75 | 6 | Transmission |  | Other Welds |  |  | Construction Defect | CRACK ON WELD | 2005-08-12 | 2006-02-15 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | EUREKA | 05-10012-1, L137A, M.P.2.7466, DIV: NORTH COAST, TRANS DEF, D.; MCRAE LN. 600' W/MAPLE LN.; ON 6"L137 TRANSMISSION LINE UNDER REDWOOD TREE, REMOVED STUMP OVER TRANS MAIN & FOUND LEAK - CLAMPED LEAK, REPAIRED TRANS. LEAK. -; CRACK ON WELD; WELDED 6" CAN & REWRAPPED MAIN; FOUND LEAK ON WELD -(BOTTOM OF 6" PIPE) REPAIRS MADE W/12" CAN & X-RAYER)
Steel/Wrought Iron
| 05-10053-1 |  |  | 4 | Distribution Main |  | Valves |  |  | Unknown |  | 2005-04-04 | 2005-04-04 |  |  | Steel/Wrought Iron |  | SAN JOSE | 05-10053-1 HCA-N TRANS DEF-D; DREG4138, M.P...., DIV: SAN JOSE; PUT AFORM ON VALVE; REG PIT LEAK; REG PIT; GREASE VALVES IN REPAIR
| 05-21004-1 |  |  | 1.25 | Service |  | Fitting |  |  | Unknown |  | 2005-01-31 | 2005-04-22 | Other | TIGHTEN FITTING | Steel/Wrought Iron |  | BERKELEY | HCA-N TRANS D, SERVICE DUE 5/1/05; 05-21004-1, DCUST 8364, M.P. 0.0022, DIV: EAST BAY; 301 IN CMB; 301 IN CMB; TIGHTEN 1 1/4 UNION; TIGHTEN FITTING; ALL IN CMB
| 05-11091 |  | 0.02 | 0.75 | Service |  | Valves |  |  | Construction Defect |  | 2005-04-29 | 2005-04-29 | Other | GREASED FITTING. | Steel/Wrought Iron |  | EMERYVILLE | 05-11091-1; HCA-N TRAN DEF-D, DCUST756, M.P. 0.0200; DIV: EAST BAY; 10% & HIGH TO HIGH SET; AT RISER & VALVE; GREASED 3/4" VALVE; GREASED FITTING
| 03-00000-1 |  |  | 0.75 | Service |  | Fitting |  |  | Unknown |  | 2003-10-21 | 2005-04-09 | Other | REPLACED HIGH TO HIGH SET. | Steel/Wrought Iron |  | SAN LEANDRO | 03-00000-1 HCA-N; LEAK, DCUST 8361, M.P.0.0042, AFORMS DREG4289, M.P.0.2826; HIGH TO HIGH SET ON DRWY; HIGH TO HIGH SET ON DRWY, HIGH TO HIGH SET DRWY ENTRANCE, @ HI-HI SET ON DRWY; REPLACED HIGH TO HIGH SET; REPLACED HIGH TO HIGH SET; REPLACED HIGH TO HIGH SET.; (CHARGED TIME TO PM 30435173) (34.5 HOIURS); REPLACED HIGH TO HIGH SET CHANGED HIGH PRESSURE 3/4" VALVE AT HIGH TO HIGH SET. SHUT OFF 3/4" MUELLER TEE AT MAIN TO CHANGE VALVE.
| 05-20061-1 | GM174439 | 0.002 | 1.25 | Transmission |  | Body of Pipe |  |  | Other | UNKNOWN | 2005-11-10 | 2005-11-15 | Other | 1 | Steel/Wrought Iron |  | WATSONVILLE | 05-20061-1 (13 DAY LITE) STUB 8351, M.P.0.002, IGIS MP., DIVE: CENTRAL COAST; SCR RTE: DFM 1816-01, SCRMP: 04.2461; ON TRANSMISSION BACK OF PROPERTY; AT CREEK XING; UNKNOWN; WELD ON 1 1/4 CAP; SOAP...OK
| 05-80025-1 | 103 | 9.37 | 0.75 | Transmission |  | Valves |  |  | Construction Defect |  | 2005-08-31 | 2005-08-31 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | SAN JUAN BAUTISTA | POINT 05-80025-1, PM40137952 D, IGIS, T. WRIGHT, DIV: HOLLISTER, DREG 4252, M.P. 0.0013; SCR RTE L-103. SRC MP. 9.3383 (9.37); GAS VALVE; GAS MAIN; REPLACE 3/4 VALVE BETWEEN T.P. LINE AND H.P.R. HR HOS
| 05-30097 | 109 | 0.3495 | 12 | Transmission |  | Fitting |  |  | Construction Defect |  | 2005-05-06 | 2005-05-19 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | DALY CITY | 05-30093-1 HCA-N DREG 4349,...DIV: PENINSULA; DREG4349, M.P. 0.3495; ON MAIN; ON T.L.; AT REG STATION; WELDED 6" CAN OVER LEAKING 3" HOME MADE CAN
| 05-30108-1 | 109 | 0.3491 | 12 | Transmission |  | Fitting |  |  | Construction Defect |  | 2005-05-19 | 2005-05-19 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | DAILY CITY | HCA-N, DREG4349; 05-30008-1 FOUND IN FIELD D; DREG 4349, M.P. 0.3491, DIV: PENNINSULA; ON MAIN; AT REG STATION; WELDED 6" CAN OVER LEAKING 3" HOMEMADE CAN; REPAIR CAN TESTED PER GS+S STANDARDS T&R CUPERVISOR TO SUBMIT TEST PIPE...PLEASE...WITH THIS AFORM.
| 05-50092 |  |  | 0.75 | Service |  | Physical/Mechanical Joint |  |  | Damage by 3rd Party |  | 2005-04-28 | 2005-04-28 | Other | REPLACE FITTINGS | Steel/Wrought Iron |  | MODESTO | 05-50092-1; HCA-N SERVICE DCUST2797, M.P.0.0173, DIV: YOSEMITE, SRC RTE 722-10, SCR MP. 11.6700; E/SIDE APPROX 1200' N/OF BANGS AVE; HIGH TO HIGH SET TO 4620 DALE RD; REPAIR ENTIRE HPR SET; REPLACE FITTINGS
| 05-20059-1 |  |  | 12 | Transmission |  | Valves |  |  | Construction Defect |  | 2005-02-08 | 2005-08-25 | Other | SEE REPAIR DATA | Steel/Wrought Iron |  | SAN JOSE | 05-20059-1, 8-12-05, 506648, HCA-N, 0824-02, X6.374, LINE X6374 EX 9-9, M.P. 10.0200 TD=D; SRC RTE: DFM 0824-02, M.P. 1.97F/O OVER IN DR. WAY NEXT TO -RR CROSSING; GREASED LEAKING FEEDER PRESSURE VALVE #20; SEE REPORT DATA
| 05-75021-1 | LBFEEDER | 6.3675 | 6 | Transmission |  | Fitting |  |  | Material Failure |  | 2005-08-18 | 2005-10-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | LOS BANOS | 05-75021-1, HCA-N DCUST2609, TD=D, DFM7210-01, M.P. 6.3675, DIV YOSEMITE; FROM TEE ON DFM TO HPR INLET; OVER TEE & HPR 7' W/O H.P.R.; REMOVED CAP REDOPED TIGHTENED-SOAPED OK; FOUND CAP BEING @ 3/4" TAP REMOVED CAP, RE DOPED & TIGHTENED SOAP TESTED OK
| 05-75021 | [10 empty] | 2005-08-18 |  |  |  | Steel-Other |  | LOS BANOS | HCA-N, DCUST 2609; FROM TEE ON DFM TO INLET OF HPR; OVER TEE & @ HPR
| 05-40136-1 | 135-01 | 9.9594 | 6 | Transmission |  | Valves |  |  | Material Failure |  | 2005-09-21 | 2005-09-23 | Welded Sleeve/Can - Weld |  | Other | STEEL | GLEN ELLEN | 05-40136-1 DFM 1305-01, KYN2 M.P. 9.9594; DFM DIV: NORTH COAST; IN BACKYARD NEAR POPLAR TREE/ODOR-UPRATE LEAK; IN BACKYARD NEAR POPLAR TREE/ODOR/ UPRATE; INSTALLED TWO PCF & CAN
| 05-55095- |  | 0.0114 | 0.75 | Transmission |  | Fitting | Regulator |  | Unknown |  | 2005-09-19 | 2005-09-19 | Other | REPLACED HI TO HI SET | Steel/Wrought Iron |  | WOODLAND | 05-55095-1 DCUST8366, M.P. 0.0114; TRANS DEF = D, DIV: SACRAMENTO; AT HI TO HI SET; AT HI TO HI SET; REPLACED HI TO HI SET BY T&R INSTALLED NEW #2 BOX; REPLACED HI TO HI SET
| 05-40013-1 |  | 2.4106 | 0.75 | Transmission |  | Body of Pipe |  |  | Atmospheric Corrosion | EXTERNAL CORROSION | 2005-03-28 | 2005-03-31 | Other | DFM | Steel/Wrought Iron |  | HAYWARD | DIV- MISSION, 05-40013-1, RTE DFM 2402-01, M.P. 2.4106; VF&c OF V-E-14; INTERSECTION OF WATKINS & CST HAYWARD VALVE FRAME & COVER LEAKING.; CUT OFF GAUGE TAP; DFM; SOAP TESTED REPAIR WELD
| 05-40013-1 |  | 2.4106 | 0.75 | Transmission |  | Body of Pipe |  |  | Atmospheric Corrosion | EXTERNAL CORROSION | 2005-03-28 | 2005-03-31 | Other | DFM | Steel/Wrought Iron |  | HAYWARD | DIV: MISSION, 05-40013-1, RTE DFM 2402-01, M.P. 2.4106; VF&C OF V-E-14; INTERSECTION OF WATKINS & C ST HAYWARD VALVE FRAME AND COVER LEAKING; DFM; SOAP TESTED REPAIR WELD
| 05-10039-1 |  | 0.19 |  | Transmission |  |  |  |  | Material Failure |  | 2005-05-26 | 2005-05-26 | Replace Valve < 2 inch |  |  |  | SANTA CRUZ | CENTRAL COAST, 05-10039-1, DREG5133, SRC RTE 1816-50, SRC MP. 0.1900, SO#7057285 HCA-N & DEF=D; @ VALVE B-18-1; @ VALVE # B18-1; REPLACED WITH NEW VALVE @ B-18-1; SEE ATTACHED
| 05-10039-1 |  | 0.19 |  | Transmission |  |  |  |  | Material Failure |  | 2005-05-26 | 2005-05-26 | Replace Valve < 2 inch |  |  |  | SANTA CRUZ | 05-10039-1, CENTRAL COAST, HCA-N TRAN-DEF-D, DREG5133, SRC RTE1816-50, SRC MP. 0.1900, SO#7057285; @ VALVE B-18-1; @ VALVE # B18-1; REPLACED WITH NEW VALVE @ B-18-1; SEE ATTACHEMENT
[18 empty] | STOCKTON | RT-DREG, M.P. 0.01, SCRT 108, SC MP. 32.31; S/E CORNER OF S MAIN & WEST LANE; LINE IS MAPPED AS 4" ACTUAL SIZE IS 6" 32' E/O VALVE OFF OF LINE 108
| 01-02331-1 | 108 | 2917 | 8 | Transmission |  | Valves |  |  | Other |  | 2001-09-19 | 2001-10-19 | Other |  | Steel/Wrought Iron |  | STOCKTON | SCRT= 108, SRCM.P=29.15, RT=DREG, M.P. 0.01; SIERRA NEVADA & PINCHOT; AT PG&e GAS VALVE MAN HOLE (YELLOW LID); GREASED & OPERATED VALVES
| 01-02321-1 | 108 | 2917 | 8 | Transmission |  | Valves |  |  | Other |  | 2001-09-05 | 2001-10-19 | Other |  | Steel/Wrought Iron |  | STOCKTON | N/W CORNER SIERRA NEVADA & PINCHOT ST; NW CORNER AT PG&E MANHOLE; GREASED & OPERATED VALVE
|  |  | 1.91 | [12 empty] | Steel/Wrought Iron |  |  | (SOUTHPORT DFM) DREG4998, M.P. 1.4156, JOB7052817; SKETCH; INSPECTION
|  |  | 1.39 | [12 empty] | Steel/Wrought Iron |  |  | (SOUTH DFM) DREG 4998, M.P. 1.8815, JOB 7052827; SKETCH; INSPECTION
|  | DFM DREG 5476 | 11.01 | [12 empty] | Steel/Wrought Iron |  |  | RT. DREG 5476, (GIS) M.P. 0.2369, JOB8070454
|  | DFM DREG 5476 | 11.01 | [12 empty] | Steel/Wrought Iron |  |  | RT. DREG5476, (GIS) M.P.0.2601, JOB 8040454
|  | 191 | 19.42 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | WALNUT CREEK | DREG 5199, PM#30604395-08; INSPECTION AREA IN SOUTH SIDE LIBRARY PARKING LOT; 2661 OAKGROVE RD. WALNUT CREEK CONTRA COSTA COUNTY, SOUTH SIDE LIBRARY PARKING LOT
|  |  | 1.6151 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIVISION: NORTH VALLEY - 3003596-09 -DREG5461, M.P.1.6151; SOUTH TIE-IN; AFORM
|  |  |  | 6.625 | [11 empty] | Steel/Wrought Iron |  |  | DIVISION: NORTH VALLEY - 30603596-09; DREG 5461, M.P. 2.4533; NORTH TIE-IN
| 08-10020-1 | 118 | 11.34 | [8 empty] | 2008-05-15 | [5 empty] | MADERA | SE CORNER STADIUM & ST MICHELLE; MAIN; MAIN; MAIN
11 |  |  |  | 12 | Gathering |  | Other |  |  | Digin |  | 1997-07-11 | 1997-07-14 |  |  | Steel/Wrought Iron |  | BRENTWOOD | INSTALL FULL INCIRCLEMENT SLEEVE 12"
|  |  |  | 34 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  |  | 12 | Distribution Main | [6 empty] | 1975-04-16 |  |  |  | Steel/Wrought Iron |  | SAN RAFAEL | LINE REPLACED, LUCAS VALLEY RD.
[18 empty] | SAN RAFAEL | LINE REPLACED; 4' OF PIPE EXPOSED DUE TO ERROSION.
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | LODI | SEND ORIG TO BAUTISTA, COPY TO MALDONALDO
|  |  | 0.6614 |  | Transmission | [10 empty] | Steel/Wrought Iron |  | THORTON | ORIG TO RAY BAUTISTA COPY TO ROBT. MALDONALDA; RT-DSBN8862, M.P.0.6614
40 | 74-00548 |  | 16.66 | 12 | Transmission |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1974-07-31 | 1974-08-10 | Other |  | Steel/Wrought Iron |  |  | RT= X6338, M.P.16.6600; VALVE PIT S/O & WEST OF HAM FIELD V-16-66&V16; LINE #21; REPAIRED LEAKING FLANGE; LOC'D INFO PIPE LINE HISTORY BOOK 8-27-79
|  | 400 | 0.0006 | 36 | Transmission | [12 empty] | OAKLEY | RT= STA8975, M.P. 0.0006, PM# 40755078-07; NORTH OF V67 & ANTIOCH GAS TERMINAL; ANTIOCH GAS TERMINAL OAKLEY CONTRA COSTA COUNTY
| 03-50119-1 |  | 0 | 0.75 | Service |  | Body of Pipe | Fitting |  | Damage by 3rd Party |  | 2003-08-04 | 2003-08-04 | Service Partially Replaced |  | Steel/Wrought Iron |  | FRESNO | DCUST77903, M.P. 0.00; CUSTOMER #426243; SALES ORDER # 40304354; AT TEE ON MAIN 533' N/N P.L. TENAYA; AT TEE ON #118; REPLACED 25' OF 3/4" STEEL PIPE; SO#P.M. 8059498; LOADER FELL IN & BROKE 3/4 STL PIPE - REPLACED PIPE FROM TEE ON MAIN TO REG STATION
[16 empty] | Steel/Wrought Iron |  |  | SWINGLE STATION 10"; SO#70451447-04, OD= 082383; SWINGLE STATION 7051147
|  |  | 0.211 | [15 empty] | ROUTE GCUST5750, M.P. 0.2110
|  | 57B | [13 empty] | Steel/Wrought Iron |  |  | VALVE YARD 0.00; PIPING ARRANGEMENT L-57B LAUNCHER MODIFICATION MCDONALD ISLAND COMPRESSOR STA. PROSPECT TIE-IN LOCATION TO BUILD TIE-IN PEICES 1ST LOCATION 24"-1.00" W.T. & 16" 0.680 W.T. 2ND LOCATION 22"-.792 W.T. JOB NUMBER 7008952
80 | 71-01492-1 |  | 1.41 | 4 | Distribution Feeder Main |  | Girth Weld |  |  | Construction Defect |  | 1971-12-31 | 1973-03-02 | Other |  | Steel/Wrought Iron |  | SUNNYVALE | WELD LEAKING ON 6"X6"X4" TEE REWELD WELD ON 6" MAIN INSTALL ANODE JW 50 OVER MAIN AND SERVICE ALL CLEAR.
| 97-80388-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1997-11-01 | 1997-11-01 | Patch Welded |  | Steel/Wrought Iron |  | SAN FRANCISCO | WELD PATCH
24 | 98-00002-1 |  |  | 8 | Distribution Feeder Main |  | Tap Connection |  |  | Construction Defect |  | 1998-10-14 | 1999-03-31 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | HAYWARD | REPAIR; CANNED LEAKING SCREWED FITTINGS
| 99-55050 |  |  | 0.75 | Transmission |  | Drip |  |  | Damage by 3rd Party |  | 1999-10-01 | 1999-10-01 | Other |  | Steel/Wrought Iron |  | MERCED | DID NOT POST LEAK OFF SERVICE; BLOW OFF; CUT AND CAPED OLD BLOW OFF; NO RECORD OF OLD BLOW OFF CUT & WELDED CLOSED
[18 empty] | ANTIOCH | FRONT AND BACK OF ANTIOCH TERMINAL YARD; THIS IS A GRAD 3 LEAK STATION PIPING OPERATING DIAGRAM # 484757
|  | 56 | 0.06 | [14 empty] | ANTIOCH | FRONT AND BACK OF ANTIOCH TERMINAL YARD.; THIS IS A GRADE 3 LEAK. STATION PIPING OPERATING DIAGRAM #484757; PLEASANT CK. 4" COLLECTION LINE EXPOSED 200' AND 800' WEST OF COMP STA. K-8. INSPECTION AT BOTH LOCATIONS
|  | 56 | [16 empty] | UGS, L56C, 0.19; PLEASANT CK. 4" COLLECTION LINE APPROX. 300FT EAST OF WELL 3-2
|  | 56 | [16 empty] | VGS 056B, 0.19; PLEASANT CK. 4" COLLECTION LINE EXPOSED 200' AND 800' WEST OF COMP STA. K-8. INSPECTION SAME AT BOTH LOCATIONS.
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#7039869-05, L-401 &L -002, BETHANY COMPR.; 14750 KELSO RD, BYRON, CA 94514; ALAMEDA COUNTY; BETHANY COMPRESSOR STATION ALAMEDA COUNTY
|  |  |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#7039869-02, L-401 & L-002 BETHANY COMPR.; 14750 KELSO RD. BYRON, CA 94514 ALAMEDA COUNTY; BETHANY COMPRESSOR STATION ALAMEDA COUNTY
|  |  |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7039869-02 L-401 & L-002 BETHANY COMPR.; 14750 KELSO RD. BYRON, CA 94514; ALAMEDA COUNTY; BETHANY COMPRESSOR STATION. ALAMEDA COUNTY
| 01-02046-1 |  |  | 1.25 | Gathering |  | Body of Pipe |  |  | Unknown |  | 2001-01-26 | 2002-01-15 | Service Entirely Replaced |  | Steel/Wrought Iron |  | STOCKTON | ON SERVICE 10FT FROM HOUSE METER; ON SERVICE 10FT FROM HOUSE METER 5202511, AT DEAD GRASS O/SERV, ON ESRVICE 5FT FROM HOUSE; RERAN SERVICE
| 01-40094-1 | 313 |  | 0.75 | Transmission |  | Regulator |  |  | Damage by 3rd Party |  | 2001-10-28 | 2001-10-28 | Other |  | Steel/Wrought Iron |  | BRENTWOOD | ON DAMAGED HIGH TO HIGH REG SET ABOVE GROUND; SAME; REPLACED PIPE REBUILTY REG'S AND SET
| 00-40244-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 2000-10-17 | 2000-10-17 | Mechanical Repair Fitting - Fitting |  | Copper |  | SEBASTOPOL | AROUND SVC TEE; NEAR SVC TEE; INST'D CU TO PL TRANSITION
| 01-40218-1 |  |  | 0.75 | Gathering |  | Body of Pipe |  |  | Digin |  | 2001-11-01 | 2001-11-01 | Other |  | Steel/Wrought Iron |  | SAN JOSE | 87' S/O S/PL OF CROSS WAY ON E/S OF NORTHERN RD; HISSING
| 01-04341-1 |  |  | 1 | Gathering |  | Body of Pipe |  |  | Digin |  | 2001-11-16 | 2001-11-16 | Mechanical Repair Fitting - Fitting |  | TR 418 |  | TRACY | ON SERV 250FT N/OF RISER; ON SERV 250FT N/OF RISER; INST 2-COUPLINGS AND 12"-1"PL
| 01-04020-1 | DFM 121 |  | 0.75 | Transmission |  | Valves |  |  | Digin |  | 2001-07-10 | 2001-07-10 | Replace TP Main |  | Steel/Wrought Iron |  | TRACY | VALVE 2350FT E/OF MIDWAY RD; BLOWING GAS; THREADED PIPE-SCREWED INTO VALVE
| 01-20112-1 |  |  | 0.75 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2001-03-09 | 2001-03-19 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | SACRAMENTO | OVER SVC IN FRONT LAWN; GRASS VERY DEAD (3' RADIUS); 35'BOW
|  | DFM | 0.55 | 6 | [11 empty] | Steel/Wrought Iron |  |  | RUSTIC SALLY...10/12/99
|  |  |  | 16 | [11 empty] | Steel-Other |  | NOVATO | LINE REPLACED; 2862-J4; CONTRACTO POTHOLING MAR
|  |  |  | 12 | [11 empty] | Steel-Other |  | NOVATO | LINE REPLACED; 2862J4; CONTRACTOR POTHOLING
|  |  |  | 03.00 & 06.00 | [11 empty] | Steel-Other |  | SAN RAFAEL, INC | DISTRIBUTION (PLAT2927-H6, 27)
|  |  | 0.6921 | 12 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | PM 30524308, ROUTE DSBN9967, M.P. 6921
...30673937, ROUTE# BD1016, M.P 0.0004
|  |  | 0.0633 | 10.75 | Transmission >= 20% SMYS | [10 empty] | Steel-Other |  |  | MAPPED 6/8/11 KZ.; AR# 42711494 (FTS); LINE 310 STA. 3+43 MP 0.0633; L-310...3+43;; LINE301 STA. 3+34, M.P. 0.0633; LATITUDE. 36 13.35.46495 LONGITUDE, -127 07 42.26053; MISC. COMMENTS/INFOMRAITON: THE DIG WAS LOCATED ABOUT 250' FROM METZ ROAD ON AIRPORT ROAD. THE STREET WAS DUG UP IN THE PROCESS. FOUND FBE COATING THEN PERFORMED HOLIDAY TEST. NO MAJOR INDICATIONS WHERE FOUND OR HOLIDAYS. NEXT E.T.S WIRES WERE CAD WELDED TO THE PIPE. NEXT THE TEST STATION WAS INSTALLED. THEN THE ROAD WAS PAVED OVER.
|  | 310 | 0.0769 | 10.75 | Transmission >= 20% SMYS | [10 empty] | Steel-Other |  |  | MAPPED...; AR#42711495(...), G...5913, M.P. 0.0170,...; ; LINE310 ROUTE GCUST 5913 STA. 4+17MP 0.0769 ; LATITUDE 36 13 35.14168 LONGITUDE -127 07 41.45438;; MISC. COMMENTS/INFORMATION: THIS SITE IS LOCATED IN THE STREET OF THE AIRPORT RD. THERE IS MINIMAL INFORMATION FOR THIS DIG BECAUSE AFTER LOCATING THE PIPE IT WAS DETERMINDED THAT THE PIPE WAS COATED WITH FBE COATING SO THERE WAS NO GRID DONE THERE WAS A SMALL AREA OF WAX TAPE WHEN REMOVED FOUND A GIRTHWELD, THERE WAS VERY SMALL SQUARE THAT WAS MEDIA BLASTED, SO THAT E.T.S. WIRES COULD BE CONNECTED TO THE PIPE. THE WIRES WERE RUN UP INTO A FINK/COUPON, THEN THE HOLE WAS BACKFILLED. BLACK STONE IS REPAVING THE DIG SITE. THERE IS LESS INFORMATION THANUSUAL FOR THIS DIG BECAUSE THE PIPE WAS NOT COMPLETELY MEDIA BLASTED.
|  | 303 |  | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | RT: DREG 5437 M.P. 0.0032; 9'-4" S/O NORTH PL BAULFOUR RD & APPROX 952 EAST OF RANCCH WOOD DR.; INSTALL NEW V-1 ON LINE 4" TP (DREG 5437) TO BALFOUR RD. REG STATION RA07
| 05-50031-1 | 301B | 10.32 | 6 | Transmission |  | Valves |  |  | Other |  | 2005-04-21 | 2006-05-26 | Other |  | Steel/Wrought Iron |  | SALINAS | S RC RTE L-301B, SRC MP, 11.0008, DREG 5413 MP 0.0010; INT OF HITCHCOCK & DAVIS (W/S OVER VALVE); INT. OF HITCHOCK & DAVIS (W/S OVER VELVE...; SAME, VALVE; GREASED VALVE
|  |  | 0.0103 | 2.375 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7049467, ROUTE: DREG4636 M.P. 0.0103
|  |  | 0.0026 | 2.375 | [11 empty] | Steel/Wrought Iron |  |  | SO# 7049467, ROUTE: DREG4659 M.P. 0.0026
|  |  | 0.0016 | 2.375 | Service | [13 empty] | SO# 7049467, ROUTE: DREG4660 M.P. 0.0016
|  |  | 0.0026 | 2.375 | [11 empty] | Steel/Wrought Iron |  |  | SO# 7049467, ROUTE: DREG4661 M.P. 0.0026
|  |  | 0.0006 | 2.375 | Service | [13 empty] | SO# 7049467, ROUTE: DREG4666 M.P. 0.0006
|  |  | 0.0009 | 2.375 | Service | [10 empty] | Steel/Wrought Iron |  |  | SO# 7049467, ROUTE: DREG4669 M.P. 0.0009
|  |  | 0.0006 | 2.375 | [11 empty] | Steel/Wrought Iron |  |  | SO# 7049467, ROUTE: DREG4678 M.P. 0.0006
91 | 97-70075-1 |  | 0.0005 | 12 | Transmission |  | Valves |  |  | Other |  | 1997-09-22 | 1997-09-24 | Other |  | Steel/Wrought Iron |  | CROWSLANDING | RT - DREG 5269, MP -0.0005; GREASED OPERATED VALVE SOAP TEST OK.
| 98-30071-1 |  | 0 | 0.75 | Transmission |  | Valves |  |  | Other |  | 1998-03-19 | 1999-08-15 | Other | GREASE | Steel/Wrought Iron |  | PATTERSON | RT= DREG5270, M.P.= 0; O/MAIN 30' E/O SYCAMORE; LEAK CLEARED BY VALVE BEING GREASED & OPERATED, SEE ATTACHED ORIGINAL A FORM; GREASE
| 98-70001-1 |  | 0.0004 | [8 empty] | 1998-03-19 | 1999-08-15 |  |  |  |  | PATTERSON | THIS IS REPAIRED BY LEAK 98-30071; SEE LEAK 98-30071 FOR REPAIR INFO; SEE LEAK 98-30071 FOR REPORT INFO
|  | 100 | 0.4919 | 10.75 | [11 empty] | Steel-Other |  |  | DREG4180, M.P0. 4919; ; LINE 100 STA. 14+ 17 MP 0.4919 ; LATITUDE 37­°18'47.94794 LONGITUDE -121°47'46.85332 ; ABORN RD. SAN JOSE; ; MISC. COMMENTS/INFORMATION: THIS SITE HAD WELL ADHERED OLD HAA COATING WITH ONE AREA CONTAINING AN EXTRA YELLOW OVERLAY. SMALL ROCK IMPRESSIONS WERE FOUND. SPIRLA MANUFACTURER ROLL MARKS WERE PRESENT, ALONG WITH ONE AREA OF MECHANICAL DAMAGE (SCRATCH % WALL LOSS). NO CORROSION WAS FOUND. PROTAL 7200 WAS USED TO RECOAT THE PIPE AND THE EDGES WERE WAX TAPED TO IMPEDE THE TRANSITION OF THE OLD HAA COATING TO THE NEWLY APPLIED PROTAL 7200. CAD WELDS WET REFERENCE CELL, AND COUPON WERE INSTALLED AT THE D/S EDGE OF INSPECTION.
|  | 191 | 0.0176 | 2.37 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | DREG8705, M.P.0.0176, PM#30603900; 5' WEST OF CARION CT & 1" NORTH OF NORTH PROP LINE CALIFORNIA AVE.; PITTSBURG CONTRA COSTA COUNTY
[16 empty] | Steel/Wrought Iron | ; |  | SO# 7045148, ROUTE: DREG TAP OF L-402 MP20.47, MP. 0.00; 2" DFM AT V-220 FROM L-402
| 03-00000-1 |  |  | 0.75 | Service |  | Fitting |  |  | Unknown |  | 2003-10-21 | 2005-04-09 | Other | REPLACED HIGH TO HIGH SET. | Steel/Wrought Iron |  | SAN LEANDRO | 03-00000-1 HCA-N, LEAK, DCUST 8361, MP 0.0042; A FORM, DREG 4289, MP 0.2926, DIV: MISSION; HIGH TO HIGH SET ON DRWY; HIGH TO HIGH SET ON DRWY, HIGHY TO HIGH SET DRWY ENTRANCE, @ HI-HI SET ON DRWY; REPLACED HIGH TO HIGH SET; (CHARGED TIME TO PM30435173((34.5 HOURS); REPLACED HIGH TO HIGH SET, CHANGED HIGH PRESSURE 3/4" VALVE AT HIGH TO HIGH SET. SHUT OFF 3/4" MUELLER TEE AT MAN TO CHANGE VALVE.
|  | DFM | 1.05 | [15 empty] | DREG M.P.1.05, SOURCE RT 1606-01; CARPENTER RD.; ON ZEPHYR 1 MILE E/O AIRPORT WAY
|  |  |  | 24 | Transmission | [6 empty] | 2003-06-12 | 2003-06-12 | Other | CLEANED & REWRAPPED PIPE | Steel/Wrought Iron |  | WEST SACRAMENTO | ROUTE= DREG TAP OFF L-172A; RE WRAPPED PIPE;
|  | 177 | 47.77 | [15 empty] | DREG 5037, SO# 7046345.04, SCRT=177A, SCMP=47.77
| 01-70135-1 | DFM#2 |  | 4 | Transmission |  | Valves |  |  | Construction Defect |  | 2000-12-21 | 2001-12-21 | Other |  | TR 418 |  | SEASIDE | SCRT=1813.02, SCMP=12.95, RT=DREG, M.P. 0.04; ON HP GAS VALVE OTHER; REPAIRED LEAKING VALVE
|  | 119 |  | 2.375 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | JOB #7052826, NEW VALVE LOCATION; JOB 7052826 ROUTE DREG4474, SOURCE L119 10.64 (SOUTH L119 10.64)
|  |  |  | 3.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM 30296729-04, ROUTE=DREG 5486
|  | 402 | 14.83 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | ANDERSON | RT= DREG 5467, M.P. 0.0091, PM# 30488180; NE/SIDE HWY 273, S/OF SOUTH ST
|  |  |  | 2 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | ROUTE. DEREG 4961, LOCATION 0.0022; 4-13-09, 11:10AM; S/S GARTLINE RD./ BUTHMAN AVE.
|  |  | 0.6276 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLAND | 011-02, M.P. 0.6276, PM# 30603491
|  |  | 0.7548 | [12 empty] | Steel/Wrought Iron |  | OAKLAND | PM# 30603491, RT=0111-02 M.P. 0.7548; BEACH ST.
| 01-55000-1 | DFM |  | 8 | Transmission |  | Valves |  |  | Other | GASKET | 2001-02-02 | 2001-02-03 | Other | REPLACE | Steel/Wrought Iron |  | OAKLAND | COPY; DFM 0117-01 ALAMEDA FEEDER; VALVE X-33; VALVE X-33; REPLACED VALVE X=33 8" GASKETS & REMOVED VALVE INSTALLED... & SPOOL.
72 | 98-55027-1 |  | 30 | 8 | Transmission |  | Body of Pipe |  |  | Digin |  | 1998-04-24 | 1998-04-24 | Replace Pipe |  | Steel/Wrought Iron |  | BERENDA | 11=A, EAST BAY; REPL. 6' - 8" TRANS MAIN.; REPLACED 6'X8 TP MAIN...REPAIRED., NOTE: INST .2.9 WALL PIPE
35 | 98-30055-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Digin |  | 1998-07-24 | 1998-07-27 | Replace Pipe |  | Steel/Wrought Iron |  | FORTUNA | 125 EAST BAY; REPLACED 27" OF DAMAGED PIPE
|  |  | 0.09 | [12 empty] | Steel/Wrought Iron |  |  | EAST BAY DIVISION, RICHMOND DFM 0132.01, M.P. 0132.01; MEEKER ST 400 W/O MARINA WAY PARKWAY - RICHMOND LINE 105A
|  | 105B | M-21 | [12 empty] | Steel/Wrought Iron |  | HERCULES | SO# 7038705-02, 105 B DREG, MP 4.59, EAST BAY DIVISION RICHMOND (HERCULES); SYCAMORE AVE. & LUPINE RD. HERCULES
| 01-80441-1 |  | 0.04 | 6 | Transmission |  | Valves |  |  | Other |  | 2001-07-14 | 2001-07-25 | Other |  | Steel/Wrought Iron |  | BERKELEY | RT 0136.04 M.P. 0.04; AT ZONE VLV H14 ON W/S, 22' S/O N/P/L W/ CRS CAMP; ON 3/4" TP BLOW VLV.; REPLACED 3/4" TP VLVS ON BLOW-OFF/GAUGE
| 01-55000-1 | DFM | 0.25 | 8 | Transmission |  | Valves |  |  | Other |  | 2001-02-02 | 2001-02-03 | Other |  | Steel/Wrought Iron |  | OAKLAND | RT 0117-01, M.P.0.25; VALVE X-33; VALVE X-33; REPLACED GASKETS AND REMOVED VALVES INST
|  |  | 0.05 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLAND | RT. 0109.01, M.P. 0.05; 921 98TH AVE.
|  |  | 1.1054 | 8 | Transmission | [6 empty] | 2004-08-30 |  |  |  | Steel/Wrought Iron |  | RICHMOND | SO# 7048659, ROUTE 0123.01, M.P. 1.1054; WELD ON ONE ONE INCH SAVA-A-VALVE
|  |  | 0.1252 | 8 | Transmission | [6 empty] | 2004-08-30 |  |  |  | Steel/Wrought Iron |  | RICHMOND | SO# 7048659, ROUTE 0123-01, M.P. 0.1252; KAY RD.; WELD ON ONE ONE INCH SAVE-A-VALVE
|  |  | 0.661 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLAND | DIV: EAST BAY, SO#702406-05, RTE.: DFM 0111-01; M.P., 0.6610; BEACH ST.
|  |  | 0.7465 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLAND | DIV.: EAST BAY, SO# 7024206-05, RTE.: DFM 0111-01, M.P. 0.7465
|  |  | 0.3105 | 8.63 | Transmission | DFM | [12 empty] | 0107-02, M.P. 0.3105, JOB 7058065
|  | 0111-02 | 2.5753 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLAND BAY BRIDGE | SO# 7046153, ROUTE 0111-02, M.P. 2.5753; TREASURE ISLAND DFM RELOCATION; REPALCED & RELOCATED BY ARB INC.; TESTED LINE FROM OAKLAND BAY BRDIGE TO 1000 SHORT OFMETER SET @ TREASURE ISLAND. TESTED WITH NITROGEN FOR 1 1/2 HRS. @ 520 PSI. rEPLACED & RELOCATED 1100'; SO# 7046153
|  |  |  | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | ALAMEDA | ...1.0819; 12" DFM 0117-01; NEPTUNE PARK; 876 NORTH OFF ATLANTIC AVE ON WEBSTER ST.; ADDED A 2" SAV-A-VALVE OVER GOUGE ON SOUTH END OF TIE-IN. IN ACCORDANCE W/ S4134
|  |  |  | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | ALAMEDA | ...RT...;12 DFM 0117-01; 1526 NORTH OF ATLANTIC AVE OR WEBSTER ST.; NO REPAIRS MADE/ NORTH TIE-IN
| 08-30080 |  |  | 0.75 | Transmission |  | Body of Pipe | Unknown |  | Unknown |  | 2008-10-02 | 2008-10-03 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | PINOLE | DIV EAST BAY, 30684030-09, DREG5645, M.P. 0.2858, SRC RTE: SP3, ON OR NEAR GAS VALVE FV-18; INSTALLED NEW PLUG & STL CAP.; LEAK THOUGHT TO BE ON 6" HP DOWNLOADED, FOUND ON T.P. MAIN NEXT DAY REPAIRS MADE. VENTED ON DAY FOUND!! SOAP TESTED AFTER REPAIR...MONITORED WHILE BRINGING PRESSURE BACK UP.; INSTALLED 3" CAN OVER 3/4 SERV. TEE
|  | 0116-01 |  | 3 | Transmission | [13 empty] | RT 0116-01, M.P. 0.0...; PM# 30631288
|  | 132 | 42.25 | 30 | Transmission |  |  |  |  | Damage by 3rd Party | DIGIN, OTHER-NONE |  | 2001-11-20 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | S.S.F. | NOTE BY DMKG 11/4/10; NOT LEAKING DAMAGE WAS REPAIRED BY INSTALLING A SLEEVE; 8050196, L-132, MP - 42.25; S/W/C CHESTNUT & ANTOINETTE; NONE; G.C. CREWS WELDED 30"X18" SLEEVE
[16 empty] | Steel/Wrought Iron |  | ATHERTON | SO# 7045115, ROUTE 0205.01, M.P.0651A; WALSH RD & VALLET RD
|  |  | 0.7373 | [12 empty] | Steel/Wrought Iron |  | ATHERTON | SO# 7045115, ROUTE 0205-01, M.P. 0.7373; 450 WALSH RD
82 | 75-00209 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1975-05-27 | 1975-07-28 | Patch Welded |  | Steel/Wrought Iron |  | ATHERTON | W. VIS OPPOSITE DRIVEWAY REPAIRED LEAK ON 4" HOLE.... ARC WELDED A 10"X15" PATCH ON THE BOTTOM OF THE 4"
82 | 72-50089-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-03-31 | 1972-03-31 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | ATH | REPLACED 15" OF OF 4" MAIN LEAKING OVER SEWER LATERAL & UNDER CATCH BASIN. INST M9455 ANODE AT RISER
82 | 78-30264- |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-07-27 | 1979-03-27 | Clamp |  | Copper |  | ATHERTON | INSTALLED 1-2 BOLT SKINNER CLAMP ON 4" MAIN IN SEWER TRENCH 10' N ELEC POLE. NO ROOM TO WELD PATCH SERV.
82 | 75-30974 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1975-10-28 | 1976-04-12 | Patch Welded |  | Steel/Wrought Iron |  | ATHERTON | LEAK ON BOTTOM 4" (HP) MAIN ARC WELDED ON PATCH 2"X3"; WATER METER BN ALONG SIDEWALK
82 | 77-30402 |  |  | 4 | Distribution Main | [6 empty] | 1977-12-01 |  |  |  | Steel/Wrought Iron |  | ATHERTON | S/W COR 3'M/ELEC POLE
82 | 72-30613-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1972-12-13 | 1972-12-19 | Patch Welded |  | Steel/Wrought Iron |  | ATHERTON | WELDED 6" PATCH OVER PIT. INST. 35.6B ANODE ON MAIN
82 | 75-5- |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1975-05-14 | 1975-05-15 | Patch Welded |  | Steel/Wrought Iron |  | ATHERTON | REPAIRED 34" ...8" X 4" PATCH OVER LEAK; LEAKING AT TOP OF WELD
82 | 75-00211-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1975-05-27 | 1975-05-30 | Patch Welded |  | Steel/Wrought Iron |  | ATHERTON | BAR HOLE STRIP... FOUND LEAK...LEAKING ON BOTTOM OF MAIN. HAD ARC ...WELDING 12" CAN ON
56 | 98-30157 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Digin |  | 1998-09-10 | 1998-09-11 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | DALY CITY | 206' N/W OF PARK PLAZA WELDED 20" BAND
| 94-80111 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1994-03-23 | 1994-05-11 | Patch Welded |  | Steel/Wrought Iron |  | PALO ALTO | PATCH LEAKING 9" HP GAS MAIN INSTALLED NEW ETS
58 | 90-30222-1 |  |  | 8 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1990-10-24 | 1990-10-24 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | HAD ARC WELDERS INSTALL 3-8"X8" PATCHES TO STOP LEAKS
82 | 71-00220 |  |  | 8 | Other | H | [9 empty] | Steel/Wrought Iron |  | MENLO PARK | NOGAR WITH I WON 470 IN. PTT BAY SEWERS WATER VALVES FIRST
82 | 71-00219 |  |  | 8 | Other | H | [9 empty] | Steel/Wrought Iron |  | MENLO PARK | NO GASES 470 SCALE SEWERS WATER UNLESS W J.W. FISSETS
82 | 77-30254 |  |  | 8 | Distribution Main | [6 empty] | 1977-09-06 |  |  |  | Steel/Wrought Iron |  | MP | 01/15/1979 NO INDICATION OF GAS IN VAULTS; P.T.T. VAULTS
82 | 72-50403 |  |  | 8 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1972-12-29 | 1973-01-02 | Patch Welded |  | Steel/Wrought Iron |  | MENLO PARK | ARC WLED 4"X4" PATCH OVER P.T. INSTALL 9# ANODE.
|  |  |  | 8 | [11 empty] | Steel-Other |  |  | 05-3-94 - NO LEAKS- INSPECTION ONLY; ABANDON 2" GAS MAIN - INSTALL NEW 4" PLASTIC GAS MAIN TO 11/2" HIGH TO HIGH REG SET
82 | 71-00211 |  |  | 8 | Other | H | [5 empty] | 2011-02-11 |  |  |  | Steel/Wrought Iron |  | REDWOOD CITY | NO GAS WITH J.W. ...
|  | 0405-01 | 23.95 | 6 | Transmission |  | Body of Pipe |  |  |  |  | 2006-06-27 | 2006-06-28 | Other | SEE ABOVE | Steel/Wrought Iron |  | ST. HELENA | S.O. 8078876; NOTE: PIPE WAS NOT LEAKING; E/S ST. HELENA HWY 1/4 MILE N/O EHLERS LN; INSTALLED 2" BYPASS, CUT OUT DAMAGED 6" SECTION OF PIPE; CONTRACTOR DENTED TRANSMISSION MAIN WHILE EXCAVATING FOR STORM DRAIN; * NOTE- PIPE WAS DAMAGED ON THE NIGHT OF 6/26/06 & BACKFILLED. WE WERE NOT NOTIFIED UNTIL APPROX 10 AM ON 6/27/06.
| 95-03638-1 |  |  | 10 | Transmission |  | Other Welds |  |  | Unknown |  | 1995-11-03 | 2001-04-27 | Other | REWELD TEE | Steel/Wrought Iron |  | CM | PUSTED 6-20-01, NORTH BAY DIVISION, DFM 0401.01; CRACKS IN STREET; CRACKS N STREET; CRACKS IN STREET; CRACKS IN STREET; CRACKS IN STREET; (WITHIN 3 MONTHS0; WELDED UP AROUND TEE; REWELD TEE
[16 empty] | Steel/Wrought Iron |  | NAPA | RTE DREG, NORTH BAY (0407), WM2710 E-4, E5, 30# 8039196; SOLANO AVE, VALVE #13
[16 empty] | Steel/Wrought Iron |  |  | NORTHBAY DIV, ROUTE 0410-01, PLAT SHT. 2842-I8; VALLEJO, SOLANO COUNTY
|  |  | 4.55 | [12 empty] | Steel/Wrought Iron |  |  | DFM 0406.01,M.P. 4.54, NAPA SO#7033654.02
|  |  | 4.7 | [12 empty] | Steel/Wrought Iron |  | NAPA | DFM 0406.01,M.P. 4.70 SO# 7033654-02 NAPA
|  | DFM |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 12" MARE ISLAND DFM 0403-01, M.P. 1.51, SOLANO AVE @ TUULUMNE ST, 8051718-02; WATER IS INSIDE WRAP PIPE HAS BEEN PREVIOUSLY DAMAGED WITH REPAIRS MADE OVER SCRACH HOME MADE SAVE A NIPPLE & REINFERING PAD. PIPE HAS UNREPAIRED DENT 1 1/2 IN DIAMETER 1/8" DEEP, COROSION PIT DEPTH OF .150 THAT WILL BE REMOVED AND HOME MADE REPAIR NIPPLE THAT WILL STAY ON PIPE SOUTH SIDE WHEN INSTALLING NEW DOG LEG
|  |  |  | 3 | [9 empty] | Other | NDT | Steel/Wrought Iron |  | NAPA | SO#7004160, RT=DCUST OFF L-0408-01, M.P. 0.92, M.P. 0.03 LOCATION #14;
|  | DFM | 2.45 | 2 | Transmission | [8 empty] | Other | NDT |  |  |  | SP#7004160, RT=DREG OFF 0408-012.45, M.P. 2.45; LOCATION #9; NDT; VALVE IS SANDWICHED BETWEEN PHONE DUCTS & ELECTIRCAL DUCTS
|  | DFM | 2.45 | 3 | Transmission | [8 empty] | Other | NDT | Steel/Wrought Iron |  |  | SO# 7004160, RT= DREG OFF 0408-01, M.P. 2.45; 3A; NDT
|  | DFM | 2.26 | 4 | Transmission | [8 empty] | Other | NDT | Steel/Wrought Iron |  |  | SO# 7004160, RT= DREG OF 0408-O1, M.P. 2.26; #5
[16 empty] | Steel/Wrought Iron |  | NAPA | SO# 7004160, RT= DREG OFF 1-0408-01, MPI =13, MP 0.01; REPLACING V-132; S/S PUEBLO AVE 14' E/O JEFFERSON ST - NAPA, INC
|  | DFM |  | 2 | Transmission | [8 empty] | Other | NDT | Steel/Wrought Iron |  |  | SO# 7004160, RT= DREG OFF 0408-01, M.P. 1.79, LOCATION 8; PIPE TO SOIL NOT TAKEN AT THIS LOCATION
|  | DFM | 2.26 | 4 | Transmission | [8 empty] | Other | NDT | Steel/Wrought Iron |  |  | SO# 7004160, RT= DREG OFF 0408-01, M.P. 2.26, #4; NDT; VALVE V-111 IS NOT OPERATABLE, ELECTRIC DUCTS RESTING ON PIPE, VALVE HAS BEEN CANNED
|  |  | 4.05 | 10 | [11 empty] | Steel/Wrought Iron |  |  | SO# 7004160, RT= DREG OFF 0408-01, M.P. 4.05, COLFIELD 10"; SOUTH
|  | DFM | 4.71 | 8 | Transmission | [7 empty] | 2001-10-01 | Patch Welded |  | Steel/Wrought Iron |  | NAPA | SO# 7004160, RT= DREG OFF 0408-01, M.P. 4.71, 8" LINCOLN; LINCOLN & SOLANO; WELDED PFC OVER SCRACH & 2" SAVE-A-VALVE; PREASURE CONTORL FITTING WAS WELDED OVER SCRACES ALSO 2" SAVE-A-VALVE WAS WELDED OVER GOUGE PER BOB FASSCIT
|  |  | 4.44 | 8 | [11 empty] | Steel/Wrought Iron |  |  | SO# 7004160, RT=0407.01 M.P. 4.44; SAMPLE LOCATION 50 FFROM F.O.C. ON SOUTH END OF TURN AROUND
|  |  | 1.83 | [12 empty] | Steel/Wrought Iron |  |  | SO# 7004160, RT=0408.01 M.P.1.83; TRANCAS 93' W/O BEARD RD. - SERVICE TO HPR AT 1000 TRANCAS ST QUEEN OF THE VALLEY HOSPITAL, WALL MAP 2710, PLAT SHEET G-8
|  | DFM | 1.83 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7004160, RT=0408.01, M.P. 1.83, #7; PIPE TO SOIL NOT TAKEN AT THIS LOCATION; QUEEN OF THE VALLEY HOSPITAL, TEE SHOWS EXTREMELY POOR WELDING WITH CENTER PUNCH LEAKING REPAD.
|  | DFM | 0.56 | 6 | Transmission | [8 empty] | Other | NDT | Steel/Wrought Iron |  | NAPA | SO# 7004160, RT=0408.01, M.P. 0.56 LOCATION #16
|  | DFM |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7004160, RT=0408.01, M.P. 2.01, LOCATION #6; PIPE TO SOIL NOT TAKEN AT THIS LOCATION
|  | DFM | 0.98 | 4 | [9 empty] | Other | NDT | Steel/Wrought Iron |  | NAPA | SO# 7004160, RT=0408.01, MP 0.98, LOCATION 13
|  | DFM | 0.88 | 4 | Transmission | [8 empty] | Other | NDT | Steel/Wrought Iron |  | NAPA | SO# 7004160, RT=0408.01, M.P. 0.88, LOCATION #15
|  |  | 0 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | NAPA | SO# 7004160, RT=0408.01, M.P. 0.00, 6"
|  | DFM | 2.45 | 4 | Transmission | [8 empty] | Other | NDT |  |  |  | SO# 7004160, RT=0408.01,M.P. 2.45, ABAN. PIPE, #3; PIPE & WRAP IN EXTREMLY POOR CONDITION; CORROSION ITS 40% OF PIPE WALL THICKNESS CGT NOTIFITED ON 1-18-01, POSSIBLE LEAK IN AREA. AERA WAS FLAMED PACKED.
|  | DFM | 2.47 | 4 | Transmission | [8 empty] | Other | NDT | Steel/Wrought Iron |  |  | SO# 7004160, RT=0408.01, M.P. 2.47LOCATION #2
|  | DFM | 2.62 | 4 | [9 empty] | Other | NDT | Steel/Wrought Iron |  | NAPA | SO# 7004160, RT=0408.01, M.P. 2.62, LOCATION #1
|  |  |  | 4 | [11 empty] | Steel/Wrought Iron |  | NAPA | SO# 7004160, RT=0408.01, M.P. 1.61; E/S OF JEFFERSON ST. 103' S/O TRANCAS ST. - NAPA INC;
[16 empty] | Steel/Wrought Iron | OTHER |  | SO# 7045468, ROUTE 0407.01 M.P. 5.39; STEEL; 8" DFM CROSSING SOLANO; SO# 7045468, RT=0408.02, MP 1.03.; TEST LOCATION 6" TP DFM; SO# 7045468, ROUTE 0408.02, MP 1.04; TEST LOCATION 6" TP DFM
|  |  | 5.5 | [12 empty] | Steel/Wrought Iron |  |  | SO# 7045468, ROUTE# 0407.01, M.P. 5.50; TOOK WRAP FROM 6" D.M.F, WRAP DROPS OFF WHILE DIGGING NEXT TO PIPE
|  |  | 5.41 | [15 empty] | SO# 7033651, ROUTE: DFM 0402-01, M.P. 5.41
|  |  | 0 | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  |  | SO# 7033651; ROUTE- DFM 0401-0,M.P. 0.00 (SAN RAFAEL REG STA)
|  |  | 0.49 | [15 empty] | RT=0408.06, MP-0.49, SO# 7033660-03
|  |  | 0 | [15 empty] | RT=0405.06, M.P. 0.00, SO# 7033660-03
|  | 0403-01 | 3.45 | 12.75 | Transmission | [12 empty] | VALLEJO | ROUTE 0403-01, M.P. 3.47; MARE ISLAND DFM; *PIPE-TO-SOIL= 1150MV @ NEARBY MONITORING ETS (NEBRASKA & MARIN); GPS COORDINATES NORTHING (Y) 4218524, EASTING (X) 565030
|  |  | 4.4725 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 6" DFM 0406 HWY 221 NAPA, API 5L X-42 ERW .188 W.T.; SO# 7033661, ROUTE 0406.01, M.P. 4.4725; EXPOSED SECTION FOR TIE-IN; NEW PIPE INSTALLED ON ORDER 703366
|  |  | 3.8512 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 6" DFM 0406 HWY 221 NAPA, API 5L X-42 ERW .188 W.T.; SO# 7033661, ROUTE 0406.01M.P.3.8512; MAGNOLIA DR. EXPOSED PIPE FOR TIE-IN
SO# 7030085, ROUTE 0405.01; MP 27.5692
|  |  | 2.6124 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 6" DFM 0406 HWY 221; SO# 7033662, ROUTE: 0406.01, M.P. 2.6124
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | NAPA | 4" TAP OFF OF DFM 0406 NAPA
|  |  | 3.2593 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 6" DFM 0406 HWY 221; SO# 7033662, ROUTE: 0406.01, M.P. 3.2593
|  |  | 0.45 | 8.63 | [8 empty] | 2004-04-29 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  |  | 8063338; INST'D 8"X36" REPAIR SLEEVE (WELDED); RT. 0407-01, M.P.0.45 (GIS 0.4328), JOB 8063338; INST'D 8" X 36" REPAIR SLEEVE ON EXPOSED PIPE OVER CREEK
|  |  | 5.4207 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT. 0405-01, M.P.5.4207 JOB 7040708
|  |  |  | 3.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT. 0408-03/DFDS3552, M.P. .0.0, JOB 7040708; WATER MAIN IS IN DIRECT CONTACT WITH 3" GAS NO ROOM EVEN TO PUT SOME DERON BETWEEN THE TWO
|  |  | 0.1773 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT. 0408-03, M.P. 0.1773, JOB 7040708
|  |  | 1.9875 | [12 empty] | Steel/Wrought Iron |  | ANGWIN | 7050456-04, DFM 04705-02, M.P. 1.9875, DIV: DNBY; 670 TERRY LAND; RAISED CONCRETE FOOTING.
|  |  | 1.9954 | [12 empty] | Steel/Wrought Iron |  | ANGWIN | 7050456-04, DFM 0405-02, M.P. 1.9954, DIV: DNBY; 670 TERRY LANE; COVER WILL VARY BETWEEN 60 & 40" DEPENDING ON STEPS TO BE INSTALLED BY CUSTOMER; FITTING IS APROXMITLY 30" FROM BOTH SOUTH & EAST RETAINING WALLS. ALSO FITTING ABOUT 30" HORAZONTAL COVER THIS MAY CHANGE DUE TO STEPPING BY CUSTOMER
|  |  | 2.0012 | [12 empty] | Steel/Wrought Iron |  | ANGWIN | 7050456-04, DFM 0405-02, M.P. 2.0012, DIV: DNBY; 670 TERRY LANE; INSPECTION PINT RIGHT WERE PIPE GOES UNDER RETAINING WALL, PIPE WAS ABOVE GROUND FOR APROX 15" STICKING OUT OF GROUND 2" DUG BACK TO WERE PIPE HAD WRAP AND RE WRAPPED PIPE PER GARY VOLLBUICK
|  |  | 19.9589 | 6 | [11 empty] | Steel/Wrought Iron |  | ST. HELENA | SO# 7050305, ROUTE: 0405-01M.P.19.9589; CHANX LN & HWY 29; INSTALLED 76" OFFSET TO REMOVE OLD 2" VALVE
|  |  | 19.9872 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | ST. HELENA | ROUTE 0405-0, 1M.P. 19.9872, SO 8055576
|  |  | 20.13 | 6 | Transmission | [12 empty] | ST. HELENA | ROUTE 0405-01, M.P. 20.1300; E/S HWY 29 N/O SULFUR SPRINGS; REPLACE FIRE VALVE FOR DIRT REG
|  |  | 20.3369 |  | Transmission | [10 empty] | Steel/Wrought Iron |  | ST. HELENA | ROUTE 0405-01, M.P. 20.3369, SO# 8055576; REPLACE 3/4 FIRE VALVE NORDSTROM ANSI 300
|  |  | 20.4605 |  | Transmission | [10 empty] | Steel/Wrought Iron |  | ST. HELENA | SO# 7050305, ROUTE 0405-01, M.P. 20.4605; DOWDELL DV. & HWY 29; INSTALLED 26" OF NEW STHEEL GR. B SEEMLESS TO REMOVE OLD 2" VALVE
[5 empty] | Transmission | [10 empty] | Steel/Wrought Iron |  | ST. HELENA | 0405-01, 805576, M.P. 20.4779; APPROX 77' NORTH OF DOWDELL & HWY 29; REPLACED FIRE VALVE FOR DIST REG, 3/4 NORDSTROM ANSI 300 MAIN IS UNDER PHONE PACKAGE
|  |  | 20.8088 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | ST. HELENA | SO# 8055576, ROUTE: 0405.01, M.P. 20.8088, 8055576; HWY 29 & CHARTER OAK
|  |  | 21.8816 |  | Transmission | [12 empty] | ST. HELENA | SO# 7050305, ROUTE: 0405-01, M.P. 21.8816; HWY 29 & PRATT AVE; INSTALLE 8" CLOG LEG AROUND REG STATION, INSTALL NEW REG STATION
|  |  | 0.494 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | ST. HELENA | SO# 8055576, ROUTE: 0405-06, M.P. 0.4940, 8055576; REPLACE FIRE VALVE 3/4 NORDSTROM PLUG VALVE ANSI300
|  |  | 0.0468 | 2 | Transmission | \ | [9 empty] | Steel/Wrought Iron |  | VALLEJO | SO# 7050405, ROUTE: 0403-04; M.P. 0.0468, NEBRASKA ST. VALLEJO
|  |  | 0 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | VALLEJO | SO# 7050405, ROUTE 0403.04, M.P. 0.0; NEBRASKA ST. VALLEJO
|  |  | 22.6925 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 7053266; DIV: NORTH BAY, DFM 0405-01, M.P. 22.6925; SO# 7053266-06; HWY 29 ST. HELENA
|  |  | 4.7081 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | NAPA | 8062977, PG 7 OF 9; N/A; (DIG IN), DIV: NORTHBAY, SO# 8062977-04, DFM 0407-01, M.P. 4.7081; THIS WAS A DIG-IN I CAME TO BACK FILL BELL HOLES ONLY. I DO NOT KNOW HOW 8" TP STL IS TIED
|  |  | 1.6638 | [14 empty] | SAN RAFAEL | IDA ST. SAN RAFAEL 200' N/O SECOND ST. 7' OUT; RT= 0401.01, M.P. 1.6638
| 76-00107-1 |  |  | 12 | Distribution Feeder Main |  | Other |  |  | Other |  | 1976-02-18 | 1978-05-24 | Other |  | Steel/Wrought Iron |  |  | P.T. & t MANHOLE IDA ST SAN RAFAEL, .03% IN TRANS MAIN PIT NO ODOR; REP. LK ON FLANGE, LEAK# OTHER SIDE, RT= 0401-01, M.P. 1.6757
|  |  |  | 12 | [11 empty] | Steel/Wrought Iron |  | SAN RAFAEL | RT= 0401-01, M.P. 1.7092; SEE ATTACHED DRAWING; EXPOSED 12" MAIN IN ORDER TO RAISE GAS MAIN AND CLEAR CONTACT WITH 8" CI WATER MAIN FOR CORROSION DEPT.
|  |  | 1.94 | 12 | [13 empty] | SAN RAFAEL | RT=0401-01, M.P.1.94
|  |  | 2.058 | 12 | [11 empty] | Steel/Wrought Iron |  | SAN RAFAEL | RT= 0401-01, M.P. 2.0580; INST'D E.T.S
|  |  | 2.199 | 12 | [11 empty] | Steel-Other |  | SAN RAFAEL | RT= 0401-01, M.P. 2.199; INST'D E.T.S.
|  |  | 2.3469 | 12 | [11 empty] | Steel-Other |  | SAN RAFAEL | RT= 0401-01, M.P. 2.3469; INSTALLED 1/2" STL. SERVICE TO LOAD CENTRAL; FAIRHILLS LINE
|  |  |  | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL | BACKHOE TOOTH HIT 16" GAS MAIN. TOOTH SCRAPPED WRAP OFF MAIN. NO DAMAGE TO MAIN; MAIN INST'D ON GM124863 IN 1954 WATER CO. DUG INTO MAIN WHILE INSTALLING WATER MAIN PIPE WRAPPED BY MMWD, INSPECTED BY W. ...
|  |  | 2.3628 | 12 | [11 empty] | Steel-Other |  | SAN RAFAEL | RT= 0401-01, M.P. 2.3628
|  |  | 2.381 | 12 | [13 empty] | SAN RAFAEL | RT= 0401-01, M.P. 2.3810; INSTALL E.T.S.
|  |  | 2.4339 | 10 | [11 empty] | Steel/Wrought Iron |  | SAN RAFAEL | RT= 0401-01, M.P. 2.4339; PUT ...PIPE AROUND MAIN
|  |  | 2.4635 | 10 | [11 empty] | Steel-Other |  | SAN RAFAEL | RT= 0401-01, M.P. 2.4635; PUT CORAGRATED PIPE AROUND PIPE
| 99-80156-1 | DFM |  | 12 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1999-10-20 | 1999-11-24 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SAN RAFAEL | 1.% RIGHT OF GATE ALSO IN ELECT. TRENCH & BROCKEN STORM DRAIN IN FRONT OF GA; ORDER IN AIR, R/GATE TO SUBSTATION; GC INSTALLED & WELDED 2-12" PLIDCO CLAMPS ON MAIN
|  |  | 2.5398 | 10 | [11 empty] | Steel-Other |  | SAN RAFAEL | RT= 0401-01, M.P. 2.5398; DEPTH CHECK
|  |  | 2.5521 | 10 | [14 empty] | RT= 0401-01, M.P. 2.5521
|  |  |  | 10 | [11 empty] | Steel-Other |  | SAN RAFAEL | RT= 0401-01, MP= 2.6286, 2.6398
|  |  |  | 10 | [11 empty] | Steel-Other |  | SAN RAFAEL | RT= 0401-01, M.P. 3.3309, INSTALLED ETS
|  |  | 3.3545 | 10 | [13 empty] | SAN RAFAEL | RT= 0401-01, M.P. 3.3545, INSTALLED ETS 355-?
|  |  | 3.3833 | 10 | [11 empty] | Steel-Other |  | SAN RAFAEL | RT= 0401-01,M.P. 3.3833, (INSTALLED ETS) WHERE 10" TURNES UP MEADOW FROM IRWIN (RIGHT AT BEND)
40 | 97-05006-1 |  | 2.6805 | 10 | Distribution Feeder Main |  | Girth Weld |  |  | Construction Defect |  | 1997-06-16 | 1998-06-10 | Patch Welded |  | Steel/Wrought Iron |  | SAN RAFAEL | RT= 0401-01, M.P.2.6805, 2986-B6; WELD AT BASE OF SVC TEE LEAKING PINNED SVC AND REWELDED SVC TEE
|  |  | 5.2115 | 16 | [11 empty] | Steel-Other |  | CORTE MANDERA | RT= 0401-01, M.P. 5.2115, C/O 3/4" STI. SERVICE
|  |  | 5.4084 | 20 | [11 empty] | Steel-Other |  | GREENBRAG | RT= 0401-01, M.P. 5.4084; INSTALLED ETS.
|  |  | 5.5055 | 16 | [11 empty] | Steel-Other |  | GREENBRAE | RT=0401-01, M.P. 5.5055; INSTALLED ETS, INSTALLED MAIN MARKER.
|  |  | I-04.00 | [14 empty] | CORTE MADERA | 0401-13, M.P. 0.4070; S/W CORNER OF ESTRADA LN. & PALOMA DR. 2-07 & 2-08
|  | 2050M | V-5.16 | 2.875 | [11 empty] | Steel/Wrought Iron |  | LARKSPUR | 0401-01, MP= 4.9181, 0401-01; END OF REDWOOD HWY & GREENBRAE BOARDWALK; CUT-OFF AND WELD ON 2" STL. CAPS ON BOTH VALVE 0-42 AND VALVE 0-44 ON THE DOWN STREM SIDE OF BOTH VALVES. (BOTH VALVES ARE ABANDON IN PLACE.) ABANDON AND REMOVE REG. STA. #37
|  |  |  | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | CORTE MADERA | 0401-01, M.P. 6.5369; DON CAMPBELL - GREASED AND OPERATED VALVE I-02. VALVE OPERATES PROPERLY. WITTNESSED BY TIME THOMAS. DON ALSO OPERATED THE BLOW OFF SOUTH OF VALVE I-02. 10" GEAR VALVE.; DON CAMBELL (CONTRACTOR FOR C.G.T.) SERVICE VALVE I-02 AND 3" BLOW-OFF VALVE BACK TO OPERATIONAL STATUS; VALVE I-02: 10" VALVE, W/ECTENSION; 3" BLOW-OFF VALVE: FLANGE, GATE VALVE, ANSI 300 EV-II, (3" BLOW-OFF VALVE ON THE SOUTH END OF I-02)(NO BLOW-OFF VALVE ON THE NORTH SIDE OF I-02); CONTRACTOR: DON CAMPBELL VALVE & ENGINEERING ... 2490 ANSELMO DR. CORONA, CA 92879; G.C. FOREMAN: KEN POWER 1/17/08; G.C. ENG.: TROY ZACHARY
|  |  | 0.0029 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  | CORTE MADERA | 0405.01, M.P. 0.0029; DON CAMPBELL-CAMPBELL VALVE & ENGINEERING CO. GREASED VALVE I-03. OPERATED VALVE. VALVES OPERATES PROPERLY. WITTNESSED BY TIM THOMAS & CHRIS SANDERS; DON CAMPBELL (CONTRACTOR FOR C.G.T.) SERVICE VALVE I-03 BACK TO OPERATIONAL STATUS; CONTRACTOR: CAMPBELL VALVE AND ENGINEERING CORP. 2490 ANSELMO DR. CORONA, CA. 92879; G.C. FOREMAN: KEN POWER 1/15/08; G.C. ENG: TROY ZACHARY
|  |  | 2.2991 | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT=0402-01, M.P. 2.2991
|  |  |  | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LOCATION UNKNOWN DUPLICATE
| 91-00001-1 | 0405 02 | 1.93 | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1991-03-15 | 2009-06-29 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | ANGWIN | PM# 40938918, ROUTE = 0405.02, M.P. 1.93; ...THE STREET FROM VALVE 70, (RI...; 20' ACROSS STREET FROM VALVE 70; 20' ACROSS STREET FRM VLV 70 O/MAIN; 20' ACROSS ST. FROM VALVE 70 ON MAIN; WELDED OUT PLIDCO REPAIR CLAMP; WELD SEALED PLIDCO FITTIN & SOAP TESTED; A.) FOUND CANNED SERVICE TEE WITH LEAKING PLUG. WELDED SAVE-A-VALVE ON END OF CAN TO REPAIR B.) FOUND EXTERNAL CORROSSION ON BOTTOM OF PIPE. INSTALLED PLIDCO REPAIR CLAMP WELD SEALED THE CLAMP BODY. WRAPPED CLAMP AND ADJACENT PIPE WITH WAX TAPE.
|  |  | 19.47 | [15 empty] | RT= 0405-01, M.P. 19.47, SO# 7033660-03
|  |  | 19.44 | [15 empty] | RT=0405.-01, M.P. 19.44, SO# 7033660-03
|  |  | 19.29 | [15 empty] | RT= 0405-01, M.P. 19.29, SO# 7033660-03
|  |  | 19.27 | [15 empty] | RT= 0405-01,M.P.19.27 SO# 7033660-03
|  |  | 19.14 | [15 empty] | RT= 0405-01, M.P. 19.14, SO# 7033660-03
|  |  | 0.7421 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT= 0405-01, M.P. 0.7421 NORTH BAY DIV, SO# 7049209; (SAN RAFAEL)
|  |  | 0.7124 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT= 0402-01, M.P. 0.7124 NORTH BAY DIV., SO# 7049209; ( SAN RAFAEL)
|  | 0407-01 | 0.01 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT=0407-01, M.P.0.010; .219 WAT AS MEASURED BY ATS (REPORT ATTACHED) SMLS PIPE; WELL THICKNESS MEASUREMETNS TAKEN IN 2008. INSPECTION FORM FILLED OUT BY DMKG- DREW KELLY IN 2009 TO RECORD W/T/ MEASUREMENTS. I WAS NOT PRESENT DURING EXCAVATION. NOTE: 4 SITES WERE MEASURE FOR WT BETWEEN MP 0-1.88 AND FOUND THICKER THAN AS RECORDED IN GIS. PRIOR VALVES WERE RETAINED IN EIS AS THIS IS INSUFFICIENT SAMPLING
| 91-00001-1 | 0405 02 | 1.93 | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1991-03-15 | 2009-06-29 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | ANGWIN | RAY COPY, ORIIGINAL SENT TO BARA HOGAN, RT= 0405.02, M.P. 1.93; CRYSTAL SPRINGS RD.; ...OSS THE STREET FROM VALVE 70, (RE...; 20' ACROSS THE STREET FROM VALVE 70; 20' ACROSS STREET FRM VLV 70 O/MAIN; 20' ACROSS ST. FROM VALVE 70 ON MAIN; (REPAIR REQUIRED WITHIN 90 CALENDAR DAYS); WELDED OUT PLICO REPAIR CLAMP; WELD SEALED PLIDO FITTING & SOAP TESTED.; A.) FOUND CANNED SERVICCE TEE WITH LEAING PLUG. WELDED SAVE-A-VALVE ON END OF CAN TO REPAIR, B.) FOUND EXTERNAL CORROSSION ON BOTTOM RT PIPE. INSTALLED PLIDCO REPAIR CLAMP. WELD SEALED THE CLAMP BODY. WRAPPED CLAMP ADJACENT PIPE WITH WAX TAPE.
| 09-00161-1 | 6-0404-4 | 2.54 | 6 | Transmission |  | Other |  | BUTT WELD | Weld Failure |  | 2009-12-03 | 2010-02-18 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | BENICIA | OPPISITE ADDRSS BEHIND WALK; PLIDCO CLAMP REPAIR; ON BUTT WELD; PLIDCO SPLIT SLEEVE # 1803517-1000WP
|  |  |  | 6 | Transmission | [7 empty] | 2010-02-18 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  |  | ON BUTT WELD; PLIDCO SPLIT SLEEVE # 1803517/1OOO WP/WEC PH7; MAY FLUX TESTED; LONG- 122.15849303778444, LAT 38.0549072532538 3M EMS MARKER PLACED TO ALLOW FUTURE LOCATE; NOTE BY DREW KELLY: 1000# PLIDCO CLAMP INSTALLED AND WELDED OUT TO PREVENT FUTURE LEAKAGE. PIPE AND CLAMP WERE WAX TAPED.; PLIDCO SPLIT SLEEVE 3 M MARKERS INSTALLED IN BACKFILL FOR FUTURE. LOCATE # 1803517 1000 WP/ WCC PH7 - S/N WELDED 100% MAS FLUX TESTED AND SOAP TESTED
|  | 0407-01 | 1.8813 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | TIE-IN 8" DFM NORTH END FOSTER RD. NAPA, DIVISION: NORTH BAY 30603532-09, DFM 0407-01; AFORM FILE NORTH BAY DFM 0407-01; INSTALLED NEW 8" DFM. PIPE INSPECTED AT NORTH P.C.E. FOSTER RD. NAPA
|  | 0405-01 | 1.8532 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | NAPA | 10" DFM AT ST. FRANCIS CIR AND FOSTER RD. NAPA, DIVISION: NORTH BAY, 30603532-09 (DREG 3951, MP 0.00) DFM 0405-01, M.P. 1.8532; INSPECTION TAKEN AT 2" PINOFF TEE ON 10" TRANSMISSION MAIN
|  | 0407-01 | 0.0097 | 1.25 | Transmission | [10 empty] | Steel/Wrought Iron |  | NAPA | 1 1/4" THAT FEES REG. 101 FOSTER RD. NAPA, DIVISION: NORTH BAY, 30603532-09; DREG 3951, M.P. 0.0097; INSPECTION TAKEN ON 1 1/4" STL. THAT FEEDS REG. 101 NAPA
|  | 0407-01 |  | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 1311 FOSTER RD. 3/4" SERVICE OFF NEW 8" DFM, DIVISION: NORTH BAY, 30603532-09, DCUST6786, M.P. 0.0036, SRC RTE 0407-01, SRCM 1.4643; INSPECTION TAKEN ON 3/4" STL. THAT FEEDS HPR TO 1311 FOSTER RD.
|  | 0407-01 |  | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | NAPA | FOSTER RD. AND HILTON AVE REG 45 NAPA, DIVION: NORTH BAY, 30603532-09, DREG 3950, SACRTE 0407-01, SRC MP 1.3832; INSPECTED 3/4" LINE TAHT FEEDS REG 45
|  | 0407-01 |  | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 1351 FOSTER RD. NAPA 3/4" STL SERVICE, DIVISION: NORTH BAY, 30603532-09, DCUST 9821, M.P.0.0040, SRC RTE 0407-01, SRC MP 1.3351; INSPECTION TAKEN ONN 3/4" STL THAT FEEDS HPR TO 1351 FOSTER RD
|  | 0407-01 | 1.0568 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | NAPA | SOUTH TIE-IN ON FOSTER RD. NAPA, DIVISION: NORTH BAY 30603532-09, DFM 0407-01; INSTALLED NEW 8" DFM ON FOSTER RD NAPA
|  | 0407-01 | 0.4346 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIVISION: NORTH BAY, 30603532-09, NORTH TIE-IN ON STANLEY LN. NAPA, DFM 0407-01; INSTALL 8" T.D. WILLIAMSON FITTING (BOTTOM TAP) ONTO EXISTING 8" DFM 0407-01
|  | 0407-01 | 0.4111 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIVSION: NORTH BAY, 30603532-09, SOUTH TIE-IN ON STANLEY LN. NAPA, DFM 0407-01; INSTALL 8" T.D. WILLIAMSON FITTING (BOTTOM TAP) ONTO EXISTING 8" DFM 0407-01
|  |  | 2.88 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | VALLEJO | DFM 0403-01; INSPECTION LOCATION AT INTERSECTION OF EL DORADO AND NEBRASKA ST IN VALLEJO
|  |  | 0.1801 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | RT. 1613-05, PM# 30667180; 565' E/O DAVIS RD.
|  |  | 0.2057 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | RT-1613-05, PM# 30667180
|  |  | 3.06 | [15 empty] | 1601-03; 8" MACARTHUR FEEDER; LOCATION 3(4) 750 FEET N/O LOCATION #3
|  |  | 2.91 | [15 empty] | 101-03; 8" MACARTHUR FEEDER, LOCATION #3 800 FEET N/O LOCATION 2
|  |  | 2.76 | [15 empty] | 1601.03; 8" MACARTHER FEEDER, LOCATION #2 750 FEET N/LOCATION #1
|  |  | 2.62 | [15 empty] | 1601-03; 8" MACARTHER FEEDER, LOCATION #1 4475 MACARTHUR RD @ 1/10 MILE N/O LORRAINE (TRACY)
|  | DFM | 3.9225 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | ROUTE DFM 1601.03; N/A STANDBY
|  |  | 5.7676 | 8 | Transmission | [12 empty] | TRACY | RT=1601-03
|  |  | 5.8492 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | RT=1601-03; 650 FS NORTH DR 11TH ST IN EAST ST.
|  |  | 5.8697 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | RT= 1601-03; EAST ST N/O TWELFTH ST
|  |  | 6.0228 | 8 | [11 empty] | Steel/Wrought Iron |  | TRACY | DFM 1601-03
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | LOCATION 0.0951; W/O MAC ARTHUR DR.
|  |  | 0.5294 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | DFM 1601-09
|  | DFM | 0.16 | [15 empty] | 1602-01; W YOSEMITE AVE. BETWEEN AIRPORT WAY & FISHBACK MANTECA
|  |  | 0.24 |  | Transmission | [12 empty] | MANTECA | 1602-01; YOSEMITE AVE D.F.M 8" E/OF AIRPORT WAY - MANTECA
|  |  | 0.28 | [14 empty] | MANTECA | 1602-01
|  |  |  | 8 | [13 empty] | MANTECA | ROUTE 1602-01; MP 0.8691?
|  |  | 1.6264 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | MANTECA | PLAT SHEET; RT=1602.01, MP - +/- 1.6264; 3116 - B8; (MANTECA 100PSIG DFM); PLAT SHEET 3116-B8
|  | 1602-01 | 1.1177 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | MANTECA | GIS, L-1602-01
|  |  | 1.68 | [12 empty] | Steel/Wrought Iron |  | MANTECA | JOB# 7022765; GSV# 1602-01
|  | 1602-1 | 1.97 | [12 empty] | Steel/Wrought Iron |  | MANTECA | L-1602-1; JOB 7022765; GSV# 1602-01, MP 1.97; SOMASTIC WRAP ON TOP & SIDES OF PIPE. LITTLE OR NO WRAP FOUND ON BOTTOM, GSAVE# 1602-01 MP 1.97
|  |  | 0.0812 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | MANTECA | RT= 1603-01
|  |  | 0.5046 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | MANTECA | SO# 7064177, DFM 1603-01; MOVE 8" DFM OVER TO NEW 8" BORED UNDER UP TRACKS
|  |  | 0.5857 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7064177, DFM 1603.01; MOVE 8" DFM OVER TO NEW 8" BORED UNDER UP TRACKS
|  |  |  | 8 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | LATHROP | STOCKTON, 1603-01, 0.8916; *POT-HOLED TODAY FOUND 8" MAIN 5' DEEP. * BORED FROM S/TO NORTH TO E/SIDE OF ELEC. POLE (NO. 2-55) THEY WENT 3 1/2' DEEP. P.S. 8" GAS MAIN IS 77' N/OF FOG-LINE FROM S/SIDE OF LOUISE AVE.
|  |  | 1.1749 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | LATHROP | ROUTE M1603-01, MP ~1.1749
|  |  | 1.1829 | 8 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | LATHROP | DIV: STOCKTON, DFM 1603-01
|  | 1603-01 | 1.2243 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT=1603-01
|  |  | 0.0035 | [14 empty] | MANTECA | ROUTE=1603.03
|  | LOUISE DFM | 0.4224 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | LATHROP | DFM 1603-03; POTHOLE FOR BORE ONLY
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | STOCKTON DFM 1605-01
|  |  |  | 6 | [11 empty] | Steel/Wrought Iron |  | STOCKTON | STOCKTON DIVISON DFM # 1605-01; EXPOSED ON STANDBY FOR (D.SS.) WATER LINE
|  | 1607-01 | 1.1796 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | L1607-01
|  |  | 1.75 | 6.625 | [11 empty] | Steel/Wrought Iron |  |  | ROUTE 1607-01, JOB#7027985
|  |  | 1.69 | 8.625 | [11 empty] | Steel/Wrought Iron |  |  | ROUTE 1607-01, JOB# 7027985
|  |  | 0.01 | 12.75 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | STOCKTON | SO# 7046073-03; RT= 1608-01
|  |  | 0.6078 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | RT=1608.01, STOCKTON DIVISION
|  |  | 0.715 | 12 | [11 empty] | Steel/Wrought Iron |  | STOCKTON | RT-1608-01
|  |  | 0.7963 | 12 | Transmission | [13 empty] | RT = 1608-01
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | STOCKTON, 1608-01, 1.0740
|  |  | 1.25 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | STOCKTON DIV, RT=1608-01
|  | 108 | 27.87 | 12 | [11 empty] | Steel/Wrought Iron |  |  | PIPE INSPECTION DATA, STATION STOCKTON DIV; ROUTE 1608-01, OD 089443; SO# 70318132; INSTALLED 12" TDW M-STOPP
|  | 108 | 27.87 | [12 empty] | Steel/Wrought Iron |  |  | STATION, PIPE INSPECTION REPORT, STOCKTON DIV; ROUTE 1608-01, OD 089443; REMOVE REGS & PIPE BETWEEN V-6&7 INSTALL 4" STL CAPS
|  | 108 | 2.7495 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | DIV: STOCKTON; DFM 1609-01; L-108 "D" -?
|  |  |  | 4 | [11 empty] | Steel/Wrought Iron |  | STOCKTON | STOCKTON DIVISION, DFM 1610-01; TEICHERT.... EXPOSED 4" GAS MAIN TO INSTALL WATER LINE
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | STOCKTON DIVISION 1611-01; I RE WRAPPED EXPOSED PIPE
|  | F-12 | 1.6 | [14 empty] | N. STOCKTON | RT=1611-01
|  |  | 1.65 | [14 empty] | STOCKTON | RT-1611-01
|  |  | 0.1189 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ROUTE 1611-030; SWAN ROAD & TAM O'SHANTER DR. STOCKTON; N-SEG 108 STA 6+76 ROUTE 16114-03, MP 0.1189, LATIT 38 00 37.67232, LONG-127 17 46.18684 18.3 ac VOLTS ON 10" INCH GAS PIPE
|  |  | 1.8532 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | N. STOCKTON | 1613-01
|  |  | 2.1513 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | 1613-01; * G.C. CREW INSTALLED POLE APPROX 84' E/OF MAILBOX AT 3494 8-MILE DR, 26" N/OF 8" GAS MAIN, AT N/SIDE OF 8-MILE RD
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | 1613.01
|  |  | 0.3039 | 6 | [11 empty] | Steel/Wrought Iron |  | N. STOCKTON | RT: 1613-05; POL HOLE 3
|  |  | 0.4188 | 6 | [11 empty] | Steel/Wrought Iron |  | N STOCKTON | RT: 1613-05
|  |  | 0.4834 | 6 | Transmission | [12 empty] | STOCKTON | 1613-05
|  |  | 0.5711 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | 1613-05
|  |  |  | 8 |  | DFM | [9 empty] | Steel/Wrought Iron |  |  | L-1613; 155.77
93 | 98-01116-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Digin |  | 1998-10-02 | 1998-10-02 | Replace Pipe |  | Steel/Wrought Iron |  | STOCKTON | REPLACE 3 1/2 FEET OF MAIN
93 | 98-01116-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Digin |  | 1998-10-02 | 1998-10-02 | Replace Pipe |  | Steel/Wrought Iron |  | STOCKTON | REPLACE 3 1/2 FEET OF MAIN
|  |  | 1.6668 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | 1613.06
|  |  | 0.5581 | 6 | Transmission | [12 empty] | STOCKTON | POSTED IN GIS 1/3/11, L - 1613.05
|  | 1613-05 | 0.5422 | 6 | Transmission | [10 empty] | Steel-Other |  | STOCKTON | L-1613-05
|  | 1613-05 | 0.5608 | 6 | [11 empty] | Steel-Other |  | STOCKTON | L-1613-05
|  |  | 1.73 | 4 | Transmission | [12 empty] | STOCKTON | 1613-06
|  |  | 7.182 | 12.12 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  | 7.1778 | 12.12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ROUTE DFM 1615-04, MP 7.1778, MP 7.1868; FOX RIVER PAPER- RIPON; REG SET- TO MODES 7044966
|  |  | 1.73 | [14 empty] | STOCKTON | 1613.06
|  |  | 3.7258 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | LODI | RT=1614-01; DFM 1614-01, MP 3.7311
|  |  | 3.731 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | LODI | RT=1614.01
|  |  | 3.744 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | LODI | RT=1614-01
|  |  | 0.2112 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | WOOD BRIDGE | SO#7051307, ROUTE 1614-04; WELD TDW TYPE FITTING ON AREA CHECK TO RUN PIPE ACROSS RD. TO NEW BRIDGE. T.C. INSPECTION CO. EX-RAY
|  |  | 0.2419 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | WOOD BRIDGE | SO# 7051307, ROUTE 1614-04; LOWER SAC. 79' SOUTH OF BRIDGE; WELDED TDW FITTING ON AREA TO RUN PIPING ACROSS RD. TO NEW BRIDGE CROSSING, T.C. INSPECTION CO EX-RAY
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 30623013, ROUTE = 1614-04, MP 0.2628, MP 0.4126; D7M WAS LOWERED FROM 48" TO 90" FROM R.R. CROSSING 777' NORTH TO BRIDGE ON L. SACRAMENTO RD.; THE A FORM WAS FOR THE NORTH AND SOUTH LOCATION
|  |  | 0.4584 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | WOODBRIDGE | RT=1614-04
|  |  | 0.5007 |  | Transmission | [10 empty] | Steel/Wrought Iron |  | WOODBRIDGE | RT=1614-04
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | WOODBRIDGE | RT-1614-04; A LOT OF BLACK TOP IN PROSPECT HOLE, AUGUSTA ST.
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | WOODBRIDGE | A LOT OF BLACK TOP IN PROSPECT HOLE, AUGUSTA ST
|  |  | 0.657 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | WOODBRIDGE | RT=1614-04; BLACK TOP IN PROSPECT HOLE, MOKELUMNE
|  |  | 0.6757 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | WOODBRIDGE | RT - 1614-04
|  |  | 0.87 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | LODI | RT=1614-08
|  |  | 1 | [14 empty] | LODI | ROUTE 1614-08
|  |  | 0.01 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | LODI | 1614-13
|  |  | 0.3143 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | LODI | RT=1614-13
|  | DFM |  | 8 | Transmission | [12 empty] | LODI | L-1614-13;NO LEAK MAIN EXPOSED TO INSTALL STORM DRAIN; NO LEAK; NO REPAIR/STANDBY ONLY; STOCKTON DIVISION, ROUTE 1614-13
|  |  | 2.863 | 6 | [13 empty] | LODI | ROUTE 1614-13
|  |  | 1.1819 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | LODI | DIV: STOCKTON; DFM 1614-13
|  |  | 0.66 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 1614-21; OAK & STOCKTON
|  |  | 0.98 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | LODI | 1614-21; WALNUT
|  |  | 1.03 | 6 | [14 empty] | 1614-21; STOCKTON 100' MP O LODI
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | ROUTE= 1615-01, MP - 12.3273, ROUTE 7221-15, MP -0.0206. DIV= YOSEMITE, JOB 7052912-04; EXPOSED ONLY THE TOP TO GET DEPTH OF LINE
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | WEST RIPON 7041126; ROUTE 1615.01
|  |  |  | 12.75 | [11 empty] | Steel-Other |  |  | JOB 7___1712, LINE 1615-01, MP__.03; INSTALLED 12" STOPPLE FTL AND TEMP. BYPASS
|  |  | 5.17 | [14 empty] | RIPON | 1615-01
|  |  | 5.3371 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | STOCKTON DIVISON, RT=1615-01
|  |  | 5.33 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | STOCKTON DIV, RT=1615-01
|  | 1615-01 | 5.58 | 12 | Transmission | [7 empty] | 2007-07-26 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | RIPON | DIG-IN REPAIR 8055083, RT=1615-01, MP= 5.584, STOCKTON DIVISION; MODESTO RIPON 12" DFM INSPECTION REPORT; TYPE B SLEEVE INSTALLED OVER GOUGE (13" LONG 0.156" DEEP); NO LEAK
|  | 1615-01 | 10.2769 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | L-1615-01; 12" 1615-01, MP 10.2769, JOB 8078738
|  |  | 6.67 | 12 | Transmission | [12 empty] | RIPON | 1615-01
|  | 1615-01 | 10.2914 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | L - 1615-__, MP 10.2914; 2-S+00; 12" 1615-01, M.P. 10.2914, JOB 8078738
|  | 1615-01 | 10.3565 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | L-1615-01, MP 10.3565, JOB 8078738
|  | 1615-01 | 10.4069 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 12" 1615-01, M.P. 10.4069, JOB 8078038; 9-6+50
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 12" 1615-01, JOB 8078738
|  | 1615-01 | 10.5306 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 18-5=8475; 12" 1615-01, JOB 8078738
|  | 1615-01 | 10.5912 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 22-9425; 12" 1615-01, JOB 8078738
|  | 1615-01 | 10.651 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 26-10475; 12" 1615-01, JOB 8078738
|  | 1615-01 | 10.7544 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 34-12+75; 12" 1615-01, JOB 8078738
|  |  |  | 12 | Transmission | 30 | [9 empty] | Steel/Wrought Iron |  | MODESTO | 30 11+75; 12" 1615-01, JOB 8078738
|  | 1615-01 | 10.8956 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 39-14+00; 12" 1615-01, JOB 8078738
|  | 1615-01 | 10.9858 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 44-15+25; 12" 1615-01, JOB 8078738
|  | 1615-01 | 11.0131 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 48-16-25; 12" 1615-01, JOB 8078737
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 53 17+50; 12" 1615-01, JOB 8078738
|  |  | 11.6744 | 12 | [13 empty] | SALIDA | ROUTE 1615-01, PM 30604131; TIE-IN 12" TRANS MAIN
|  | 1615-01 | 11.1761 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 59 19-00; 12" 1615-01, JOB 8078738
|  | 1615-01 | 11.2192 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 63- 20+00; 12" 1615-01, JOB 8078738
|  | 1615-01 | 11.2749 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 68 214 25; 12" 1615-01, JOB 8078738
|  |  | 11.2751 | 12.75 | Transmission | [12 empty] | SALIDA | ROUTE-1615-01, PM 30604131
|  | 1615-01 | 11.2947 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 12" 1615-01, JOB 8078738
|  | 1615-01 | 11.3667 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 77-23+50; 12" 1615-01, JOB 8078738
|  | 1615-01 | 11.5339 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 86-25+75; 12" 1615-01, JOB 8078738
|  | 1615-01 | 11.5995 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODEST; MODESTO | PL 24-150; 12" 1615-01, JOB 8078738
|  | 1615-01 | 11.5995 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | PL 24-150; 12" 1615-01, JOB 8078738
|  | 1615-01 | 11.6491 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 92-27+25; 12" 1615-01, JOB 8078738
|  | 1615-01 | 11.7029 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 96 -28+25; 12" 1615-01, JOB 8078738
|  | 1615-01 | 11.7909 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 99-29400; 12" 1615-01, JOB 8078738
|  | 1615-01 | 11.8336 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | S/W CORNER OF DALE & RORRAN___; 12" 1615-01, JOB 8078738
|  | 1615-01 | 11.8491 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 103/30+25; 12" 1615-01, JOB 8078738
|  |  |  | 16 | Transmission | [10 empty] | Steel-Other |  |  | JOB 70017.2, LINE 1615-04; INSTALL 16" STOPPLE FTL. AND TEMP BYPASS.; WEST RIPON 7041126, ROUTE 1615-04, MP 0.0141
| 01-02324-1 |  | 4.13 | 12 | Transmission |  | Valves |  |  | Other |  | 2001-09-07 | 2001-10-15 | Other |  | Steel/Wrought Iron |  | RIPON | PG&e VALVE AT N. SIDE OF WEST RIPON ROAD; PG&E VALVE AT N/SIDE OF WEST RIPON ROAD; OPERATED VALVE (MULTI TURN) LUBED
|  |  | 5.11 | [14 empty] | RIPON | 1615-04
|  | DFM | 5.6252 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | DFM 1615-04, DIV: STOCKTON; POTHOLE FOR STANDBY ONLY; POTHOLE FOR BORE
|  |  | 6.0576 | 12 | Transmission | [12 empty] | RIPON | DFM 1615-04, DORY 4-27-10
|  |  | 6.33 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | 1615-04
|  | F-01 | 6.4856 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | STOCKTON DIVISION, RT=1615-04
DELTA | 01-02291-1 |  | 6.63 | 12 | Transmission |  | Valves |  |  | Other |  | 2001-08-06 | 2001-09-26 | Other |  | Steel/Wrought Iron |  | RIPON | RT = 1615-04
|  |  | 0.0032 | 8 | Transmission | [6 empty] | 2003-09-29 |  |  |  | Steel/Wrought Iron |  | TRACY | SO#7038133, ROUTE 1617-01; EAST OF L-162A MLV; TDW LOCATION WEST OF L-162A MLV., GRANT LINE
|  | 162 |  | 8 | Transmission |  |  |  |  | Other | NO LEAK OR DAMAGE |  |  |  |  | Steel/Wrought Iron |  |  | RT=1617-01, MP-0.0048, RT=162A, MP-6.60 & MP - 6.61; NO LEAKING OR DAMAGE; 10.00
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | L-1617-01; LOCATION: 0.4810
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | ROUTE: 1617-01, LOCATION: 0.5237
|  |  | 0.7567 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | RT= 1617-01
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | STOCKTON 1619-01, 0.6014
|  | 108 | 0.2215 | 108 | [13 empty] | STOCKTON | RT=1621-01; L-108
|  |  | 0.2556 | [14 empty] | STOCKTON | RT= 1621-01, PM# 41237959; *WRAP NOT DISTURBED NO INSPECTION COMPLETED; THE PIPE WRAP WAS NOT DISTURBED SO NO MAIN INSPECTION WAS COMPLETED. DEPTH AT POT-HOLE LOCATION 48"
|  |  | 0.3812 | [14 empty] | STOCKTON | RT=1621-01, PM# 41237959; * WRAP NOT DISTURBED NO INSPECTION COMPLETED; THE PIPE WAS NOT DISTURBED SO NO MAIN INSPECTION WAS COMPLETED. DEPTH AT POT-HOLE LOCATION 36"
|  |  |  | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | DFM 1621-01, M.P. 1.0638, FOR DREG 4940, MP 1.0600, DIV: STOCKTON, SO# 7054485-05; AREA CHECK WHILE INCAPSULATING A LEAKY VALVE THAT FEEDS REG PIT.
|  |  | 1.5011 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | RT=1621-01
|  |  | 0 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | STOCKTON DIVISION, DFM 1621-03
|  | 140 |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | GAULT | STOCKTON DIV., DFM 1625-01; 40-3 GM 46398871
|  | 140 | 9.4193 | 6 | Transmission |  | Other |  | NO LEAK | Other | NO LEAK |  |  | Other | NO REPAIR | Steel/Wrought Iron |  | GALT, CO AREA | DFM 1625-01, DIV: STOCKTON; STANDBY ONLY, NO LEAK; NO LEAK; NO REPAIR; PIPE EXPOSED FOR STANDBY ONLY
|  | 140 |  | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | ACAMPO | DCUST 8303, MP 0.0002; DIV: STOCKTON, SRC RTE 1625-01, SRC MP 9.4189; N/A; STANDBY ONLY
|  | 140 | 9.4191 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | ACAMPO | DFM 1625-01; DIV: STOCKTON; N/A; STANDBY ONLY
|  | 139 | 0.06 | 3 | Transmission | [10 empty] | Steel/Wrought Iron |  | ACAMPO | 1625-05
|  | 139 | 0.15 | 3 | Transmission | [10 empty] | Steel/Wrought Iron |  | ACAMPO | 1625-05; 1/2 WAY BETWEEN JAHANT & WOODSON
|  |  |  | 3 | Transmission | [10 empty] | Steel/Wrought Iron |  | ACAMPO | 1625-05; LINE 139 150 YD S/O WOODSON
|  | 159 |  | 3 | Transmission | [13 empty] | ROUTE 1625-05; STOCKTON DIVISION; NO LEAK; NO REPAIR
|  |  | 0.1935 | 6 | Transmission | [12 empty] | STOCKTON | RT= 1641-01
|  | 197 | 0.02 | 6 | Transmission | [12 empty] | MARTELL | RT= 1642-01; (LINE 197) STOCKTON DIV; MARTELL; L-197 IN MARTELL
|  |  | 0.002 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ROUTE: DREG 4931; CORNER OF WEST RIPON RD & MANTECA RD HPR LOCATION; CUT IN 700 TO 400 PSI HPR FOR FUTURE, TIE BACK TO EXISTING 400 TO 55PSI HPM.
|  |  | 0.0022 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE: DREG 7932; HPR ON WEST RIPON RD.; CUT IN 700 TO 400 PSI HPR FOR FUTURE, THEN TIED BACK TO EXISTING 400 TO 55 HPR
|  |  | 0.0021 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | HPR SET AT CORNER OF WEST RIPON AND AUSTIN RD.; AREA CHECKED WHILE INSTALLING A 700 TO 400 PSI HPR THEN TIE TO EXISTING 400 TO 55 PSI HPR
|  |  | 6.5188 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ROUTE: DFM 1615-04; RIPON 7044966
|  |  | 0.0062 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE: DCUSS 1844; HPR LOCATION; AREA CHECK WHILE WELDING A 3/4 SPLIT FITTING TO SHUT OFF GAS TO CUT IN A 700 TO 400 PSI HPR SET THEN TIE BACK TO EXISTING 400 TO 55 PSI HPR SET
|  |  |  | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE: D CUST 1837; HPR LOCATION; USED 4' OF 1/2", ONE TEE & 2-90° MET FITS; AREA CHECKED WHILE DIGGING TO PIN OFF ON MAIN TO CUT IN A 700 TO 400 PSI HPR SET, THEN TIEING BACK TO EXISTING 400 TO 55 PSI HPR SET
|  |  | 0.0113 | 0.75 | Transmission | [12 empty] | RIPON | ROUTE: D CUST 1833; HPR LOCATION; AREA CHECK WHILE WELDING A 3/4 SPLIT TO SHUT OFF SERVICE TO CUT IN A 700 TO 400 PSI HPR SET, THEN TIE BACK TO 400 TO 55 PSI HPR SET.
|  |  | 0.0113 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE= DCUST 1831; HPR LOCATION; AREA CHECKED, WHEN WELDING ON 3/4 SPLIT TO SHUT OFF MAIN TO CUT IN 700 TO 400 HPR FOR FUTURE THEN TIE BACK TO EXISTING 400 TO 55 PSI HPR.
|  |  | 0.005 | [12 empty] | Steel/Wrought Iron |  |  | ROUTE= DCUST 1768; HPR LOCATION
|  |  | 6.8744 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE = 1615.04, DEACTIVATED DCUST 1855; SERVICE PIN OFF TEE AT 12" MAIN; AREA CHECK WHILE CUTTING OUT SEC OF 3/4 PIPE TO WELD A CAP, TO ABANDON OR DEACTIVATE THE SERVICE AT THE PIN OFF TEE ON 12" MAIN
|  |  | 0.011 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE: DCUST 1840; HPR LOCATION; PL. CONECTIONS, ONE PEFECTION 90° AREA CHECKED WHILE WELDING 3/4 SPLIT TO CUT IN A 700 TO 400 PSI HPR SET, THEN TIE BACK TO EXISTING 400 TO 55 PSI HPR SET. USED 46" OF NEW 1/2 PL.
|  |  | 0.011 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE = DCUST 1839; HPR LOCATION; AREA CHECKED WHILE WELDING A 3/4 SPLIT FITTING ON TO SHUT OFF GAS TO CUT IN A 700 TO 400 PSI HPR SET THEN TIE BACK TO EXISTING 400 TO 55 PSI HPR SET.
|  |  | 0.0179 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | MANETECA | ROUTE= DREG 8181; HPR LOCATION (DIST. REGS); AREA CHECKED WHILE CUTTING IN A 700 TO 400 PSI HPR SET, THEN TIEING BACK TO EXISTING 400 TO 55 PSI HPR SET IN LINE VALVE WAS USED TO SHUT OFF SERVICE.
|  |  | 0.0007 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE= DCUST1856; HPR LOCATION; AREA CHECKED WHILE CUT IN IN A 700 TO 400 PSI HPR SET, THEN TIEING IT BACK TO EXISTING 400 TO 55 PSI HPR SET, EXISTING OLD STYLE REG WAS CHANGED TO NEW STYLE
|  |  | 0.0065 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE= DCUST 8180; HPR LOCATION; AREA CHECKED WHILE CUTTING IN A 700 TO 400 PSI HPR SET, THEN TIEING IT BACK TO EXISTING 400 TO 55 PSI HPR. IN LINE VALVE WAS USED TO SHUT OFF MAIN.
|  |  | 0.0103 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | DCUST 1851; HPR LOCATION BRANCH SERVICES; AREA CHECKED WHILE WELDING A 3/4 SPLIT FITTING ON TO SHUT OFF SERVICE, THEN CUT IN A 700 TO 400 PSI HPR SET, AND TIE BACK TO EXISTING 400 TO 55 PSI HPR SET
|  |  | 0.0017 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | AREA CHECK WHILE WELD ON A 3/4 SPLIT TO SHUT OFF GAS TO CUT IN A 700 TO 400 PSI HPR SET, THEN TIE BACK TO EXISTING 400 TO 55 PSI HPR SET.
|  |  | 0.0043 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE= DCUST 1853; HPR; AREA CHECKED WHILE WELDING A 3/4 SPLIT ON TO SHUT OFF GAS TO CUT IN A 700 TO 400 PSI HPR SET, THEN TIE BACK TO EXISTING 400 TO 55 PSI H.P.R. SET
|  |  | 0.01 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE= DCUST 1854; HPR LOCATION; AREA CHECKED WHILE CUTTING IN A 700 TO 400 PSI HPR SET, THEN TIEING BACK TO EXISTING 400 TO 55 PSI HPR SET. IN LINE VALVE WAS USED TO SHUT OFF SERVICE.
|  |  | 0.0017 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE= DCUST 1843; HPR LOCATION; AREA CHECK WHILE WELDING A 3/4 SPLIT FITTING ON TO SHUT OFF GASS TO HPR SERVICE, TO CUTIN A 700 TO 400 PSI HPR SET THEN TIE BACK TO EXISTING 400 TO 55 PSI HPR SET.
|  |  | 0.001 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE = DCUST 1845; HPR LOCATION; AREA CHECK WHILE CUTTING IN A 700 TO 400 PSI HPR SET THEN, TIEING IT TO EXISTING 400 TO 55 PSI HPR SET. PIN OFF AT MAIN WAS USED TO SHUT OFF GAS FEED.
|  |  | 0.011 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE = DCUST 1841; HPR LOCATION; AREA CHECKED WHILE, WELDING A 3/4 SPLIT TO CUT IN A 700 TO 400 PSI HPR SET, THEN TIEING IT TO THE EXISTING 400 TO 55 PSI HPR. A 36" PEACE OF 1/2" PL. PIPE WAS USED TO TIE BACK TO HOUSE SERVICE
|  |  | 0.001 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE= DCUST 1842; HPR LOCATION; AREA CHECKED WHILE DIGGING UP PIN OFF TIE ON 12" MAIN TO SHUT OFF SERVICE, THEN CUT IN A 700 TO 400 PSI HPR SET, THAT TIES INTO EXISTING 400 TO 55 PSI HPR SET.
|  |  | 0.0012 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | MANTECA | ROUTE = DCUST 1805; HPR LOCATION; AREA CHECKED WHILE WELDING ON A 3/4 SPLIT FITTING TO SHUT OFF SERVICE TO CUT IN A 700 TO 400 PSI HPR SET THEN TIE BACK TO EXISTING 400 TO 55 PSI HPR.
|  |  | 0.005 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE = DCUST 1806; HPR LOCATION; AREA CHECKED WILL CUTTING IN A 700 TO 400 PSI HPR SET, THEN TIEING BACK TO EXISTING 400 TO 55 PSI HPR SET. PIN OFF AT 16" MAIN WAS USED TO SHUT OFF SERVICE.
|  |  | 0.0015 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | MANTECA | ROUTE = DCUST 8178; HPR LOCATION; AREA CHECKED WHILE CUTTING IN A 700 TO 400 PSI HPR SET, THEN TIEING BACK TO THE EXISTING 400 TO 55 PSI HPR, PIN OFF AT 16" MAIN WAS USED TO SHUT OFF SERVICE.
|  |  | 0.01 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | MANTECA | ROUTE= DCUST 1808; AREA CHECK WHILE WELDING A 3/4 SPLIT FITTING ON TO SHUT OFF MAIN, THEN CUTTING IN A 700 TO 400 PSI HPR AND TIEING BACK TO EXISTING 400 TO 55 PSI H.P.R.
|  |  | 0.101 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | MANTECA | ROUTE = DCUST 1809; AREA CHECKED WHILLE WELDING A 3/4 SPLIT FITTING ON TO SHUT OFF SERVICE AND CUT IN A 700 TO 400 PSI HPR SET THEN TIE IT BACK TO THE EXISTING 400 TO 55 PSI HPR SET.
|  |  | 0.01 | 0.75 | Transmission | [12 empty] | MANTECA | ROUTE= DCUST 1810; AREA CHECKED WHILE WELDING ON A 3/4 SPLIT FITTING TO SHUT OFF SERVICE, AND CUT IN A 700 TO 400 PSI HPR SET, THEN TIE BACK TO EXISTING 400 TO 55 PSI HPR SET
|  |  | 0.001 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | MANTECA | ROUTE = DCUST 1811; HPR LOCATION; AREA CHECKED WHILE CUTTING IN A 700 TO 400 PSI HPR SET THEN TIEING IT BACK TO EXISTING 400 TO 55 PSI HPR SET. PIN OFF TEE AT 16" MAIN WAS USED TO SHUT OFFE SERVICE.
|  |  | 0.01 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | MANTECA | ROUTE = DCUST 1812; AREA CHECKED WHILE WELDING A 3/4 SPLIT FITTING TO SHUT OFF SERVICE, THEN CUTTING IN A 700 TO 400 PSI HPR SET, AND TIEING BACK TO EXISTING 400 TO 55 PSI HPR SET.
|  |  | 0.015 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | MANTECA | ROUTE = DCUST 1813; HPR LOCATION; AREA CHECKED WHILE CUTTING IN A 700 TO 400 PSI HPR SET, THEN TIEING BACK TO EXISTING 400 TO 55 PSI HPR SET. PIN OFF AT 16" MAIN WAS USED TO SHUT OFF MAIN.
|  |  | 0.0025 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | DUCST 1814; HPR LOCATION; CUT IN 700 TO 400 PSI HPR TIED BACK TO EXISTING 400 TO 55 PSI HPR. USE PIN OFF AT MAIN TO SHUT OFF SERVICE.
|  |  | 0.01 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE= DCUST 1815; HPR LOCATION; CUT IN NEW 700 TO 400 PSI HPR IN FRONT OF EXISTING 400 TO 55 PSI HPR FOR FUTURE, USE 3/4 SPLIT TO SHUT OFF SERVICE
|  |  | 0.002 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | MANTECA | ROUTE = DCUST 1816; CUT IN 700 TO 400 PSI HPR & TIED BACK TO EXISTING 400 TO 55 PSI HPR USED 3/4 SPLIT TO SHUT OFF SERVICE.
|  |  | 0.001 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE = DCUST 1828; CUT IN 700 TO 400 PSI HPR IN FRONT OF EXISTING 400 TO 55 PSI HPR USED PIN OFF AT MAIN TO SHUT OFF SERVICE.
|  |  | 0.0027 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE = DCUST 1817; HPR LOCATION; CUT IN 700 TO 400 PSI HPR THEN TIE BACK TO EXISTING 400 TO 55 PSI HPR USE 3/4 SPLIT TO SHUT OFF MAIN
|  |  | 0.001 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE = DCUST 1818; HPR LOCATION; CUT IN 700 TO 400 PSI HPR THEN TIED BACK TO EXISTING 400 TO 55 PSI HPR, USED PIN OFF AT MAIN TO SHUT OFF SERVICE
|  |  | 0.001 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE = DCUST 1819; HPR LOCATON; WELD ON 3/4 SPLIT, CUT IN 700 TO 400 PSI HPR & TIE BACK TO EXISTING 400 TO 55 HPR USED 3/4 SPLIT TO SHUT OFF SERVICE
|  |  | 0.0025 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE = DCUST 1820; HPR LOCATION; AREA CHECKED WHILE WELDING A 3/4 SPLIT FITTING ON TO SHUT OFF GAS TO SERVICE, THEN CUTTING IN A 700 TO 400 PSI HPR SET, AND TIEING BACK TO EXISTING 400 TO 55 PSI HPR SET
|  |  | 0.0017 | 1 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE= DCUST 1822; 1ST SAGE HPR 700 TO 400 PSI LOCATION; CUT IN 700 TO 400 PSI HPR IN FRONT OF EXISTING 400 TO 55 PSI HPR. USE PIN OF AT MAIN TO BLOW DOWN LINE, FROM MAIN TO 2ND HPR WS 1" PIPE
|  |  | 0.0133 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE = DCUST 1824; 1ST & 2ND STAGE HPR LOCATION; WELD SPLIT FITTING TO CUT IN 700 TO 400 PSI. HPR THEN TIE BACK TO EXISTING 400 TO 55 PSI HPR.
|  |  | 0.0037 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE = DCUST 1825; 1ST & 2ND STAGE HPR LOCATION; WELD SPLIT FITTING TO CUT IN 700 TO 400 PSI HPR THEN TIE BACK TO EXISTING 400 TO 55 PSI HPR.
|  |  | 0.0027 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE = DCUST 1826; 1ST & 2ND STAGE HPR LOCATONS; WELD SPLIT FITTING TO CUT IN 700 TO 400 PSI HPR THEN TIE BACK TO EXISTING 400 TO 55 PSI
|  |  | 0.0125 | 0.75 | Transmission | [12 empty] | RIPON | ROUTE = DCUST 1827; HPR LOCATION; WELD 3/4 SPLIT TO CUT IN 700 TO 400 PSI HPR & TEE BACK TO EXISTING 400 TO 55 PSI HPR.
|  |  | 0.0105 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE = DCUST 1828; 3/4" GAS SERVICE AT HPR LOCATION; 3/4 SPLIT WELDED ON TO SHUT OFF MAIN, 700 TO 400 PSI HPR CUT IN & TIED BACK TO EXISTING 400 TO 55 PSI HPR. 3' PEACE OF NEW 1/2" PLASTIC WAS USED TO TIE IN 2ND STAGE HPR TO SERVICE LINE TO HOUSE
|  |  | 0.003 | 0.75 | Transmission | [12 empty] | RIPON | ROUTE = DCUST 1829; 16" MAIN PIN OFF TO 1ST & 2ND STAGE HPR LOCATIONS; AREA DUG UP TO CUT IN 700 TO 400 PSI HPR THEN WELDED BACK TO EXISTING 400 TO 55 PSI HPR. USED PIN OFF AT 16" MAIN TO SHUT OFF SERVICE.
|  |  | 0.0093 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE = DCUST 8179; HPR LOCATION; AREA CHECK, WELD 3/4 SPLIT TO SHUT OFF MAIN TO CUT IN 700 TO 400 PSI HPR, THEN TIE BACK TO EXISTING 400 TO 55 PSI HPR.
|  |  | 0.002 | 0.75 | Transmission | [12 empty] | RIPON | ROUTE = DCUST 1830; HPR LOCATION; USED PIN OFF ON 16" MAIN TO SHUT OFF GAS TO CUT IN 700 TO 400 PSI HPR SET, THEN TIE BACK TO EXISTING 400 TO 55 PSI HPR.
|  |  | 0.001 |  | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON; | ROUTE = DCUST 1834; HPR LOCATION; AREA CHECKED WHILE WELDING ON 3/4 SPLIT FITTING TO CUT IN A 700 TO 400 PSI HPR THEN TIE BACK TO EXISTING 400 TO 55 PSI HPR.
|  |  | 0.003 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE = DCUST 1835; HPR LOCATION; AREA CHECK WHILE WELDING ON 3/4 SPLIT FITTING TO SHUT OFF MAIN & TO CUT IN A 700 TO 400 PSI HPR SET, THEN TIE BACK TO EXISTING 400 TO 55 PSI H__
|  |  | 0.0118 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIPON | ROUTE = DCUST 1836; HPR LOCATION; AREA CHECKED WHILE WELDING 3/4 SPLIT TO CUT IN A 700 TO 400 PSI HPR SET, THEN TIE BACK TO EXISTING 400 TO 55 PSI HPR SET.
|  |  | 0.0435 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | SUTTER HILL | 1642-01; JOB 7055686; AREA CHECK WHEN WELDING ON A T.D.W. FITTING FOR A SERVICE TAP
|  |  | 0.0965 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | GCUST5856, M.P.0.0965
|  | DFM |  | 6 | [13 empty] | TRACY | GRANT LINE & LINCOLN
[18 empty] | STOCKTON | DREG 4892; SW CORNER OF ZEPHER & AIRPORT
|  |  |  | 2 | [11 empty] | Plastic |  |  | 2" DISTRIBUTION; PLA SHT 3112-H4
|  |  | 0.0074 | 2 | [11 empty] | Steel/Wrought Iron |  | STOCKTON | TAP TO DIRT RED; DREG 4940; DIV: STOCKTON; SO# 7054485-05; AREAS CHECKED WHILE CUTTING IN A NEW FIRE VALVE & INCAPSULATING OLD 2" VALVE THAT FEED RED PIT.
|  | 108D | 1.8212 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | ROUTE: GCUST 5842
|  |  |  | 2 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | SC RT 1607-01 MP. 0.11, DREG 4893 MP 0.0085, PU# 30727113; 2" MULLER LOCATION & VALVE TIED TO 8" STL MAIN; AREA CHECKED WHEN REPLACING A 2" VALVE JOB # 30727113
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | SCRT = 1607-1, DREG 4393, MP 0.0062; PU# 30727113; 8" MAIN & 2" TP VALVE & MULLER TAP LOCATION; AREA CHECKED WHEN REPLACING A 2" VALVE JOB # 30727113
|  | 1603-01 | 0.7972 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | LATHROP | POSTED IN GIS, L-1603-01; 2112 LOUISE AVE;
|  |  | 3.2335 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | LODI | 1614-01, PM# 30677563; HIGH SIDE TAP FITTING AREA; AREA CHECKED WHEN WELDING FITTING FOR NEW DIST REG. STA JOB# 30677563
|  |  |  | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | LODI | STUB 10682; PM# 30677563; 90' WEST OF NEW DIST REG STR; AREA CHECKED WHEN DOING HPR C/O FOR JOB# 30677563
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | L-1611-03; R 210' S/O SWAIN R W/0 I5
|  | 1611-03 | 3.2009 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | L-1611-03
|  | MTY#2DFM | 1.44 | 10 | Transmission |  | Drip | Valves |  |  |  | 2000-10-17 | 2000-10-17 | Other | 2" STL CAP WELDED | Steel/Wrought Iron |  | MONTEREY CO. | SO# 7032965; ROUTE# 1813-02; REMOVED 2" FLANGED DRY VALVE (LEAKING) & WELDED 2" STL CAP; REPLACED WRAP ACROSS CREEK
|  | MTY DFM1 | 13.9 | [8 empty] | 2000-10-02 |  |  |  | Steel/Wrought Iron |  | MTY | ROUTE# 1815-02, SO# 7032525; INSPECTED MP. 13.9, DFM MTY#1, GSAVE SHOWS RTW MP 13.49-13.58
|  | DFM2 | 3.4 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | WATSONVILLE | L-1814-01, SO# 7031566
|  |  |  | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  | SANTA CRUZ | INSPECTION ONLY; BOTTLE C @ NORTH END; NO LEAKAGE; WRAP REMOVED IN 4 INCH STRIP AROUND THE PIPE AND ULTRASONIC WALL THICKNESS TAKEN AT EIGHT LOCATIONS AROUND THE PIPE (PART OF 10-YEAR INSPECTION). PIPE IS IN EXCELLENT CONDITION. EXPOSED PIPE WAS SANDBLASTED AND DEVTAR 247 EPOXY APPLIED.
|  |  |  | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  | SANTA CRUZ | INSPECTION ONLY; BOTTLE C 496 FT. FROM NORTH END; NO LEAKAGE; WRAP REMOVED IN 4 INCH STRIP AROUND THE PIPE AND ULTRASONIC WALL THICKNESS TAKEN AT EIGHT LOCATIONS AROUND THE PIPE (PART OF 10-YEAR INSPECTION) PIPE IS IN EXCELLENT CONDITION. EXPOSED PIPE WAS SANDBLASTED AND DEVTAR 247 EPOXY APPLIED.
|  |  |  | 30 | Transmission | [7 empty] | 2002-10-31 | Other | GRIND OUT GAUGE | Steel/Wrought Iron |  | SANTA CRUZ | NO LEAKAGE; MAGNETIC PARTICLE TESTED BEFORE AND AFTER GRINDING; BACK HOE GAUGED BOTTLE F WHILE EXCAVATING FOR 10 YEAR INSPECTION. 1.) TWO GOUGES ON CAP (0.02" DEPTH 11/2" AWAY FROM WELD) 2 O'CLOCK (LOOKING SOUTH) 2.) ONE GOUGE OR SCRATCH RUNNING ON BODY OF PIPE 2 O'CLOCK (LOOKING SOUTH), 7 1/2" AWAY FROM END CAP WELD (GOUGE <0.01" DEEP). REPAIR INCLUDED MAGNETIC PARTICLE TESTING BEFORE & AFTER GRINDING (NO CRACKING FOUND).
|  |  |  | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  | SANTA CRUZ | INSPECTION ONLY; WRAP WAS REMOVED IN 6" STRIP AROUND THE PIPE ABOUT 14" FROM THE END OF PIPE AND ON THE CAOP. WELL THICKNESS WAS MEASURED AT 8 LOCATIONS ON THE BODY OF PIPE AS WELL AS THE CAP. PIPE WAS IN GOOD CONDITION, THE 2" DRIP PIPE HAS DISBONDED WRAP AND LIGHT RUST. ALL EXPOSED PIPE WAS SAND BLASTED AND DECTAR 247 EPOXY WAS APPLIED
|  |  |  | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  | SANTA CRUZ | INSPECTION ONLY; BOTTLE G 463FT FROM NORTH END. FOUND WRAP DISBONDED ON BOTTOM OF (30") PIPE, WITH LIGHT RUST ON PIPE. WRAP WAS REMOVED IN 4 INCH STRIP AROUND THE PIPE AND ULRASONIC WALL. THICKNESS TAKEN AT EIGHT LOCATION AROUND THE PIPE (PMT OF 10-YEAR INSPECTION). PIPE IS IN GOOD CONDITION. RUST WAS WIRE-BRUSHED, PIPE WAS SANDBLASTED AND DEVTAR 274 EPOXY APPLIED.
|  |  |  | 30 | Transmission | [7 empty] | 2002-10-31 | Other | GRIND OUT GOUGE | Steel/Wrought Iron |  | SANTA CRUZ | NO LEAKAGE; MAGNETIC PARTICLE TESTED BEFORE AND AFTER GRINDING; GOUGE ON BOTTLE H CAUSED BY BACKHOE BUCKET EXCAVATING FOR 10-YEAR INSPECTION OF BOTTLE G. REPAIR INCLUDED MAGNETIC PARTICLE TESTING BEFORE AND AFTER GRINDING. (NO CRACKING FOUND) EXPOSED PIPE WAS SANDBLASTED AND DEVTAR 247 EPOXY APPLIED.
|  |  |  | 34 | Transmission | [7 empty] | 2002-10-31 | Other | GRIND OUT GOUGE | Steel/Wrought Iron |  | SANTA CRUZ | NO LEAKAGE; MAGNETIC PARTICLE TESTED BEFORE AND AFTER GRINDING; SCRATCH/GOUGES ON BOTTLE K CAUSE BY BACKHOE BACKET (EXCAVATING FOR INSPECTION OF BOTTLE L) REPAIR INCLUDED MAGNETIC PARTICLE TESTING BEFORE AND AFTER GRINDING (NO CRACKING FOUND).
|  |  |  | 34 | Transmission | [7 empty] | 2002-10-31 | Other | GRIND OUT SCRATCH | Steel/Wrought Iron |  | SANTA CRUZ | MAGNETIC PARTICLE TESTING BEFORE AND AFTER GRINDING; 37" SCRATCH ON TOP OF PIPE AT THE VERY END OF 34" PIPE. REPAIR INCLUDED MAGNETIC PARTICLE TESTING BEFORE AND AFTER GRINDING. (NO CRACKING FOUND). EXPOSED PIPE WAS SANDBLASTED AND DEVTAR 247 EPOXY WAS APPLIED.
|  |  |  | 34 | Transmission | [7 empty] | 2002-10-31 | Other | GRIND OUT GOUGES | Steel/Wrought Iron |  | SANTA CRUZ | NO LEAKAGE; MAGNETIC PARTICLE TESTED BEFORE AND AFTER GRINGING; LINGHT RUST ON TOP OF PIPE WHERE COATING HAS FAILED. THE REST OF THE COATING IS WELL ADHERED TO THE PIPE. TWO GOUGES ON TOP OF PIPE ABOUT 5 INCHES APART, BOTH CAUSED BY BACKHOE BUCKET EXCAVATING FOR 10 YEAR INSPECTION. REPAIR INCLUDED MAGNETIC PARTICLE TESTING BEFORE AND AFTER GRINDING. ( NO CRACKING FOUND).
|  | 1813-02 |  | 10.75 | Transmission | DFM | [9 empty] | Steel/Wrought Iron |  | MARINA | WRO TIE-IN, CONTRACTOR INSTALLED BARE *SEE BACK.; RELOCATE 10" DFM 1813-02
|  |  | 8.8541 | 10 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 301F | 7.94 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | sO#7049207-03, RT DF7117, LINE1813-02; REPALCE V-2
|  | 1818-01 | 2.1687 | 12.75 | Transmission | DFM | [12 empty] | 7048968, M.P. 2.1687, ROUTE 181-01; RELOCATE 12" DFM 1818-01 @ WASHINGTON ST & CENTER, SANTA CRUZ
|  | 1891-01 | 0.0002 | 6.62 | Transmission | [13 empty] | SO#70528004, RT STUB ... 1889-01, M.P. 0.0002
|  |  | 1.05 | 6.625 | [11 empty] | Steel/Wrought Iron |  |  | SO#7057907, RT 1816-50, M.P. 1.05; SANTA CRUZ UNDERGROUND HOLDER
|  |  | 1.05 | 10.75 | [11 empty] | Steel/Wrought Iron |  |  | SO#7057901, RT 1816.50, M.P. 1.05; SANTA CRUZ UNDERGROUND HOLDER
|  |  | 1.5083 | 4.5 | Transmission >= 20% SMYS | [10 empty] | Steel/Wrought Iron |  |  | DFM 1823-01, M.P. 1.5083, SO#7057366-06; DIV CENTRAL COAST
|  |  | 14.0774 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | CAPITOLA | RT= 1816-01, M.P. 14.0774; INSTALLED 10" TDW SIDE OUT FITTING
|  |  | 0.119 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | CAPITOLA | RT-1816-02, MP.0.1190; INSTALLED 10" MUELLER L.S. FITTING
|  |  | 14.66 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | CAPITOLA | INSTALLED 10: TDW SIDE OUT FITTING
| 08-10006-1 | 8-1816-15 |  | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2008-02-11 | 2008-04-16 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | SANTA CRUZ | ISNTALLED SPECIAL 6 BOLT TRANSMISSION MAIN CLAMP
|  | 181 | 2.8783 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE 181 STA. 4+29; STEEL 1818-01; MP. 2.8783; LATIT 35 57 58.35579, LONG-122 02 1298369; ; MISC. COMMENTS INFORMATION: THIS SITE IS LOCATED IN FRONT OF ADDRESS 142 ACADIA AVENUE IN SANTA CRUZ, CA. THE NEAREST CROSS STREET IS SEASIDE STREET. THE SITE IS ASPHALT. THE SITE WAS SAW CUT. DUE TO A FLUX OF WATER AT 7", 16" ABOVE T.O.P. AND FLX OF SEWER 16" ABOVE T.O.P. JUST OUTSIDE THE 10' INSPECTION AREA THE DIG WAS MAINLY HAND DUG IN VERY ROCKY SOIL. WATER WAS PRESENT IN DITCH. A WATER SAMPLE WAS TAKEN AND TURNED INTO ATS. THE WATER IN THE DITCH WAS PUMPED OUT. MT PERFORMED BY ATS. NO LINER INDICATIONS WERE FOUND. NO CORROSION FOUND UPON INSPECTION. THE PIPE WAS WAX TAP COATED WITH A LAYER OF TUF-N-NUFF DUE TO THE WATER WITHIN THE DITCH. COUPON ETS WAS INSTALLED IN A G-5 CRISTY BOX. NATIVE SOIL WAS USED AROUND ETS. SITE WAS BACKFILLED WITH IMPORTED SAND AND SLURRY. SITE WAS PAVED WITH ASPHALT.
|  | 181 | 4.668 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DONE CHECKED; LINE 181 STA. 12+87; ROUGHT 1818-01; MP 4.6680; LATIT 36 57 28.08757, LONG -122 03 45.20490; MISC. COMMENTS/INDORMATION: THIS SITE IS LOCATED AT THE END SCHAFFER RD. ON THE WEST SIDE UNDER A VERY LARGE TREE. THE NEAREST CROSSS ROAD IS DELAWARE AVE. THE TREE IS LOCATED ON COLLEGE PROPERTY AND IS ENVIRONMENTALLY PROTECTED FOR BIRDS AND RED LEGGED TREE FROGS. DUE TO THE PORTECTED ENVIRONMENT, ON 5/3/2010 BIOLOGIST FROM PG&E ANDREA HENKE AND RACHEL WOISTENHOME FROM GANDA ARRIVED ON SITE TO CHECK FOR SAFETY OF SPECIES AND GIVE EVERYONE TRAINING. BOB DALE WITH PG&E WAS ALSO ON SITE. THE TOP TWO FEET OF SITE DUG OUT WAS PUT INTO A SEPERATE SPOIL PILE TO BE PLACED BACK ON TOP WHEN DIG IS COMPLETED PER THE DIRECTION OF THE BIOLOGISTS. THE REMAINING SPOIL NATIVE SOIL WAS PUT INTO A SECONDD PILE TO BE USED AS THE MAIN BACK FILL WITH THE DITCH AREA. EXISTING COATING WAS PARTIALLY DEGRADED AND HAD RUST A LONG ENTIRE PIPE LENGTH. SITE WAS INSPECTED BY GANDA BIOLOGIST DAILY PRIOR TO WORK BEING PERFORMED. A RECTIFIER ID#75 ON SHAFFER RD @R/R ON CP AREA 3675-01 IS LOCATED JUST WEST OF THE DIG SITE ON A POLE. UPON INSPECTION MINOR CORROSION LESS THAN 20 % FOUND. ETS WIRES WERE CAD WELDED AT THE D/S EDGE. THE PIPE WAS RECOATED WITH PROTAL 7200. SITE WAS BACKFILLED WITH NATIVE SOIL. THE FOLIAGE FROM THE TREE LIMBS THAT WERE REMOVED WERE PLACED ON TOP OF DIG SITE PER GANDA BIOLOGIST REQUEST. THIS DIG SITE IS LOCATED NEAR AN ANODE BED ACCORDING TO PG&E.
|  | 1818-01 | 9.7573 | 12 | Transmission | [6 empty] | 2010-09-21 |  |  |  | Steel/Wrought Iron |  | SANTA CRUZ
|  | 181 | 0.09 | 3.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE 181 STA 0+19; ROUGHT DF 3430; MP 0.0900; LATIT 37 02 16.71252, LONG -122 02 30.16643; LOCKWOOD LN. & GRAHAM RD. SCOTTS VALLEY; ; MISC. COMMENTS/INFORMATION: THIS SITE IS LOCATED ON THE WEST SIDE OF LOCKWOOD LN. IN THE SOILD. IN SCOTTS VALLEY, CA. IT IS IN A RESIDENTIAL NEIGHBORHOOD. THE DIG WAS POTHOLED AND HAND DUG DUE TO FLX WITHIN DITCH AREA. NO 4-PIN TEST WAS ABLE TO BE PERFORMED DUE TO HOMEOWNER NOT ALLOWING ACCESS TO PROPERTY. UNPON INSPECTION NO CORROSION FOUND. DUE TO ENVIRONMENTALS WAX TAPE WAS USED TO RECOAT PIPE WITH A LAYER OF TUFF-N-NUFF. NATIVE SOIL WAS USED AROUND ETS AREA. REFRENCE CALL WAS PLACED STREAM LINE OF PIPE. DITCH WAS BACKFILLED WITH IMPORTED SAND. SOIL COMPACTION WAS DONE A LAYER OF TOPSOIL WAS PLACED ON TOP.
|  | 181 | 0.08 | 8.62 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SCOTTS VALLEY ; LINE 181; STA 4+63 MP; ROUGHT DREG5130; LATIT 37 02 17.22212, LONG -122 02 29.36888; ; MISC. COMMENTS/INFORMATION THIS SITE WAS LOCATED BENEATH AN INCLINED DRIVEWAY AND HAD OLD HAA COATING WITH SEVERAL ROOT IMPRESSIONS. ALL P/S READS FELL BELOW STANDARD- 850MV, BUT THE RECRIFIER FOR THAT AREA WAS OFF DURING DATA COLLECTION. A SHAVED DSAW WAS LOCATED AT 4:00. THE PIPE WAS CLEAN AND HAD NO CORROSION PRESENT. IT WAS RECOATED WITH PROTAL 7200 AND THE EDGES WERE WAS TAPED TO IMPEDE THE TRANSITION OF THE OLD HAA COATING TO THE NEWLY APPLIED PROTAL 7200.
|  | 300 | 0.0207 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | MABURY RD. SAN JOSE; LINE 300, 0824-01 SATt, 0+87 MP 0.0207; LATIT 3722 33.90185, LONG, 121 51 18.57129
|  | 300 | 0.0207 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | MABURY RD. SAN JOSE; LINE 300, 0824-01 SAt 0+97 MP0.0207; LATIT 37 22 33.90185, LONG 121 51 18.57129
| 03-50055-1 |  | 1.7178 | 16 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2003-10-29 | 2003-10-29 | Other | WELD OVER CORROSION PITTS | Steel/Wrought Iron |  | SAN JOSE | RAN BEADS OVER CACH PITT FILL THEM JUST OVER FLUSH OF MAIN; SOAP TEST WELDS
[16 empty] | Steel/Wrought Iron |  |  | LINE ROUTE 034-01 JOB#7046085RELOCATE 16" DFM (WRO); JOB 7046085
|  |  | 0.07 | 6 | Transmission | [6 empty] | 2002-08-23 |  |  |  | Steel/Wrought Iron |  | SAN JOSE
|  |  | 0.1 | 12 | Transmission | [6 empty] | 2002-08-26 |  |  |  | Steel/Wrought Iron |  | SAN JOSE
|  | 0824-02 | 3.5915 | 12.75 | Transmission | [12 empty] | SAN JOSE | TIE-IN & REMOVE BYPASS FOR SERVWD PROJECT
|  | 0824-02 | 3.5733, 3.5527 | 12.75 | Transmission | [12 empty] | SAN JOSE | TIE-IN & REMOVE BYPASS FOR SEVWD PROJECT
|  | 0822-01 | 0.33 | 2.375 | Transmission | DFM | [9 empty] | Steel/Wrought Iron |  | MORGAN HILL | SO#7047095; TRANSFER 2" FEEDER TO NEW 6" DFM
|  | 0822-01 | 0.05 | 6.625 | Transmission | DFM | [9 empty] | Steel/Wrought Iron |  | MORGAN HILL | SO#7047095; INSTALL NEW 6" DFM ON COCHRANE RD. TIE-IN AT THE S/W CORNER OF PEET
|  |  | 0.0206 | 2.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | MORGAN HILL | SO#7048453; RELOCATE REG. PIT
|  |  |  | 06.00 & 12.00 | [11 empty] | Steel/Wrought Iron |  | SANTA CLARA
|  | CURTNER |  | 10.00 & 12.00 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | SAN JOSE | sO#7047232-04
INSPECTION ONLY; SO#7060729-07; PIPE EXPOSED TO INSTALL CP LINES (46" COVER). PIPE EXPOSED. INSTALLED CAPS AS PART OF JOB# 7060729
|  |  |  | 2 | [11 empty] | Steel/Wrought Iron |  | SAN JOSE | DIV: SAN JOSE; SO#2009193-06
|  | KING DFM | [15 empty] | MILPITAS
|  | KING DFM | [15 empty] | MILPITAS | R05030614, LOC#8
|  | KING DFM | [15 empty] | MILPITAS
|  | TAYLOR 12" | 3.06 | 12 | Transmission | [12 empty] | SAN JOSE | 0824-02, M.P. 3.06
|  | 0822-01 | 0.4041 |  | Transmission | DFM | [9 empty] | Steel/Wrought Iron |  | MORGAN HILL | SO#7047095; *NEW INSTALLATION OF 6" DFM WEST TIE-IN
| 08-20069-1 | LAFAYATTE DFM | 0.05 | 6 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2009-02-06 | 2009-07-28 | Replace TP Main |  | Steel/Wrought Iron |  | SANTA CLARA | STEEL 6" DFM REPAIRED BY G.C. GAS. WELDED ON 6" CONTROL, CLOSED VALVE INSTALLED 41" OF NEW 6".; WHERE'S THE VALVE??
| 08-20069-1 | [10 empty] | 2008-02-06 | [5 empty] | SANTA CLARA | PM41041264
| 08-20069-1 | [10 empty] | 2008-02-06 | [5 empty] | SANTA CLARA | PM#408723-72; RECHECK ORDER SAP 40894994; REPAIRED BY G.C.
|  |  | 0.3818 | 10 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | PM30639855
|  |  | 0.4462 | 10 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | PM#30639855; INSTALL 101' 16" CASING
|  |  | 1.5627 | 16 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | PM#30639855
|  |  | 1.6406 | 16 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | PM#30639855
|  |  | 1.688 | 16 | Distribution Main | GATHERING | [9 empty] | Steel/Wrought Iron |  |  | PM#30639855
|  |  | 1.116 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 41132106; SOAP TESTED TIE-IN WELDS AT LINE PRESSURE
|  |  | 2.8246 | 1.05 | Transmission | [10 empty] | Steel/Wrought Iron |  | GLENN BARN | #4113406
|  |  | 0.3622 | 3.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 41132106; SOAP TEST 2 TIE-IN WELDS & TEE WELD AT LINE PRESSURE & CAP
|  | 177A | 0.0163 | 6 | Distribution Main | [10 empty] | Steel/Wrought Iron | ; |  | DISTRIC: MERIDIANL DIVISION NORTH VALLEY; SO#30603628-09; SOAP TESTED FITTINGS
|  |  |  | 2.37 | [11 empty] | Steel/Wrought Iron |  |  | DIV- NORTH VALLEY, SO#30349758-05
|  |  | 1.1391 | [12 empty] | Steel/Wrought Iron |  |  | DIV. NORTH VALLEY, TIE-IN LOCATION A, 7058285-05
|  |  | 1.1551 | [12 empty] | Steel/Wrought Iron |  |  | DIV, NORTHVALLEY, TIE-IN LOCATION B, #7058285-05
|  |  | 2.825 | [15 empty] | SO#7044711-03
|  |  | 2.9564 | [15 empty] | SO#7044711-03
|  | ENT. FDR | 1.26 | [12 empty] | Steel/Wrought Iron |  | REDDING | SO#7034925-01
|  | 177 | 1.24 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | #7030805-00; RED BLUFF REG STA.
|  | ENT FDR | [13 empty] | Steel/Wrought Iron |  | REDDING | ISNTALLED 2" CAP (STL) ON 2" STUB 5' 6" DEEP
|  | 1001-01 | 0.76 |  | Transmission | [10 empty] | Other | 0.188 | RED BLUFF | JOB#7036869-01; REPLACED CAP
|  | 1001-01 | 0.85 | [12 empty] | Steel/Wrought Iron | .187 WALL | RED BLUFF | JOB# 7036869-01; INSTALLED NEW CAP VARIDIED VALVE
|  | 1001-01 | 1.57 | [12 empty] | Other | .188 D.P. | RED BLUFF | JOB 7036869-01
|  |  | 0.82 | [15 empty] | SO#7036666; TIE IN...
|  | 1001-01 | 1.74 | [12 empty] | Steel/Wrought Iron |  | RED BLUFF | JOB 7036869-01; DO TO DEPTH OF MAIN WE WERE UNABLE TO INSPECT MAIN FOR PITTING OR D.T. WALL THICKNESS
| 04-52436-1 |  | 7.1146 | 6.625 | Distribution Main | TRANSMISSION | Fitting | Other Welds | UNKNOWN | Construction Defect | WELD | 2004-01-23 | 2004-03-15 | Replace Dist Main >= 100 ft |  | Steel/Wrought Iron |  | OROVILLE | SO#7050550; REPLACED 97' OF 5" (TP) DFM; REPLACED 97' OF 6.625 X42 .188WT. AND 2 PCF'S TO REPAIR LEAK
|  | BURNEY | 82.33 | 2.375 | Transmission | [10 empty] | Steel/Wrought Iron |  | BURNEY | PM 30296820
|  | BURNEY | 82.33 | 2.375 | Transmission | [10 empty] | Steel/Wrought Iron |  | BURNEY | PM 30296820
|  | BURNEY |  | 2.375 | Transmission | [10 empty] | Steel/Wrought Iron |  | BURNEY | PM3029682
|  |  |  | 4.5 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | BURNEY | PM3029682
|  |  | 7.3756 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#7053493-05; OROVILLE DFM REPLACEMENT - REFER# 7053453
|  |  | 7.1182 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | OROVILLE D.F.M. REPLACEMENT ORDER #7053493
|  |  |  | 3.5 | Transmission | [13 empty] | PM 30349751-05, DIV NORTH VALLEY
|  | 177A |  | 1.05 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM30349755-05, DIV, NORTH VALLEY
|  | 402 | 30.68 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM 30435748-05; 4" TP STL EXPOSED SEE PM 30435748 REPAIR INLET VALVE
|  |  | 7.0078 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | NORTH TIE-IN LOCATION ORDER #7054309
|  | 401 | 69.41 | 2.375 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | JOB #507060930 SKETCH 4 OF 4. REBUILD PRI. REG STAT. BROWN RD. MCARTHUR
|  | 400 | 69.38 | 2.375 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | JOB # 507060930 SETCH 3 OF 4 REBUILD PRI REG. STA. BROWN RD. MCARTHUT
|  | 400 | 69.38 | 2.375 | Transmission | [10 empty] | TR 418 |  |  | JOB #507060930 SKETCH 4 OF 4. REBUILD PRI. REG. STA. BROWN RD. MCARTHUR
|  |  | 0.2116 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | REDBLUFF | SO#7054311-06
|  |  | 0.1076 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | REDBLUFF | SO#7054311-06
|  |  | 0.0282 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  | REDBLUFF | SO#7054311-06; CUT OFF 25 E/O 6" BT. DUE TO REG. STA. SENSINS LINES
|  |  | 0.3 | 16 | Transmission |  | Other |  | GAUGE | Digin |  | 2002-01-07 | 2002-01-08 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | FRESNO | NOTIF#100613426; G.C. WELDED SLEEVE OVER GOUGE; HOP TOE FROM FLOYD JOHNSON STRUCK AND GOUGED 16" BOLT MAIN. G.C. IS TO WELD SLEEVE OVER GOUGE
|  |  | 0.0031 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | KERMAN | PM#30693462-09
| 05-40065-1 |  | 8.5055 | 2 | Transmission |  | Valves |  |  | Other | MECHANICAL | 2005-03-03 | 2005-03-18 | Replace Valve >= 2 inch |  | Steel/Wrought Iron |  | HEALDSBURG | REPLACED VALVE; INSTALLED NEW 6" PCF TO REPLACE LEAKING VALVE. WORK DONE ON STANDING ORDER 7055831; WELDED NEW 6" PCF ON NORTH SIDE WELDED NEW 2" VALVE
|  |  | 4.81 | 8 | [11 empty] | Steel/Wrought Iron |  |  | SO#7057286-06
|  | 1309-01 | 0.8036 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | JOB 7041671; VAN DUZEN RIVER DFM RELOCATION 7041671 NORTH SIDE OF RIVER; EXPOSED LINE FOR TIE-IN
|  | 1309-01 | 0.9794 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | JOB 7041671; EXPOSED LINE FOR TIE-IN
|  | 1302-02 | 6.87 | [12 empty] | Steel/Wrought Iron |  | SEBASTOPAL
|  | 1302-02 | 7.67 | [12 empty] | Steel/Wrought Iron |  | SEBASTOPAL | 341 FEET NORTH OF P/L FARMER JOB7031685
|  | 1302-02 | 7.78 | [12 empty] | Steel/Wrought Iron |  | SEBASTOPAL | JOB 7031685
|  | 1302-02 | 8.26 | [12 empty] | Steel/Wrought Iron |  | SEBASTOPAL
|  | 1302-02 | 8.8 | [12 empty] | Steel/Wrought Iron |  | SEBASTOPAL | JOB 7031685 PHASE 1
|  |  | 4.99 | 8 | [11 empty] | Steel-Other |  |  | NORTH COAST DIV. ROUTE1307-01, M.P. 4.99; PIPE TP SOIL -850
|  |  | 5.32 | 6 | [7 empty] | 2001-05-03 |  |  |  | Steel-Other |  |  | NORTH COAST DIV, ROUTE1307-01, SO#7033656-01; 6" T.D.W. FITTING IS 11.5' FOR ...PIPE TO SOIL -922
| 00-40070-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2000-04-10 | 2000-10-07 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | SANTA ROSA | CENTRAL COAST DIV, ROUTE 1303-01; REPAIR CK. OK;
| 00-40070-1 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  |  | 2000-10-07 | Clamp |  | Steel/Wrought Iron |  |  | ISNT. 6" CLAMP ON DFM LINES FOUND TWO BAD PITS IN PIPE LEAKING 4" APART
| 02-40115-1 |  |  | 6 | Transmission |  | Fitting | Physical/Mechanical Joint |  | Construction Defect |  | 2002-07-10 | 2002-07-11 | Replace TP Main |  | Steel/Wrought Iron |  | SEBASTOPAL | REMOVED LEAKING DRESSOR FITTING AND WELDED IN 2' OF 6" PIPE; S.O. & ASSIGNED 8053798
|  |  | 0 | 3.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | PETALUMA | SO#7038805-02; DENMAN REG STATION, PETALUMA 0800129
|  |  | 0 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  | PETALUMA | INSPECTION POINT; DENMAN FLAT REG STATION PETALUMA 0800129
|  |  | 9.15 | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | SO#30236897; * PIPE TO SOIL, OTHER SIDE, 975
| 01-30008-1 | 137C | 165 | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2007-02-13 | 2001-02-13 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | EUREKA | BUBBLES IN CREEK; INSTALL 4" CAN
|  |  | 9.5737 | [15 empty] | SO#7045674, ROUTE 1302-02
|  |  | 0.0009 | [15 empty] | SO# 7045674, ROUTE DREG4606
|  |  | 9.9138 & 9.8423 | [15 empty] | SO#7045674, ROUTE 1302-02
|  |  | 10.4783 & 10.0358 | [15 empty] | SO#7045674, ROUTE 130202
|  |  | 9.7323 & 9.7553 | [15 empty] | SO#7045674, ROUTE 1302-02
|  |  | 0.0011 | [12 empty] | Steel/Wrought Iron |  |  | JOB 7027031
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  | 0.7509 | 3 | Transmission
|  |  | 25.3132 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | JOB 7027031
|  |  | 26.468 | 3 | Transmission
|  |  | 26.2744 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | JOB 7027031
|  |  | 21.8553 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | JOB 7027031
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  |  | 3 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  | 25.9892 | 6 | Transmission | [8 empty] | Other | PITTS .090 NUMEROUS | Steel/Wrought Iron |  |  | JOB 7027031
|  |  | 0.0069 | 10 | Transmission | [13 empty] | JOB 7027031
|  |  | 0.0069 | 2 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DREG4681, SOURCE RT 1305-02, M.P. 0.0069
|  |  | 26.9607 | 2 | [13 empty] | SANTA ROSA | COLLEGE AVE, SANTA ROSA; STUB 6138; SOURCE RT1305-01, M.P. 26.9607
|  |  | 21.997 | 0.75 | [11 empty] | Steel/Wrought Iron
|  |  | 21.99 | 7 | [11 empty] | Steel/Wrought Iron |  |  | 1305-01
|  |  | 2.681 | [12 empty] | Steel/Wrought Iron |  |  | 3" PIPE (4?); 1303-05, M.P. 2.68110
|  |  | 2.6785 | 8 | [14 empty] | 8" PIPE; 1303-05, M.P. 2.6785
|  |  | 21.3713 | 2 | [11 empty] | Steel/Wrought Iron |  |  | 2" PIPE; 1305-01, M.P. 21.3713
|  |  | 1.2137 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 1301-01, M.P. 1.2137
|  |  | 23.97 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DREG4679, OFF DFM 305-01, M.P. 23.97, 4" T.P. DFM
|  |  | 1.3207 | 8 | [14 empty] | LOCATION OF INSPECTION
|  |  | 1.5539 | 8 | [14 empty] | JOB 7027031
|  |  | 7.842 | [15 empty] | SO7046023
|  |  | 0.0793 | [15 empty] | SO#7046025
|  |  | 7.5818 | [15 empty] | SO#7046023
|  |  | 9.5478 | [15 empty] | SO#7052328-05
|  |  | 9.6299 | [15 empty] | SO#7052328-04
|  |  | 2.664 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | FULTON | FULTON DFM 7053346 6" TIE-IN RIVER ROAD. DFM 1307-01 MP 02.2664
|  |  | 0.4027 & 0.3159 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | FULTON | FULTON DFM 7053346 6" TIE-IN RIVER ROAD WEST END. DFM 1307-01 MP 0.4027 & MP 0.3159
|  |  | 0.3092 | 6 | [11 empty] | Steel/Wrought Iron |  | FULTON | FULTON DFM 7053346 6" VALVE SET RIVER ROAD DFM 1307-01 MP 0.3092
|  | 1307-01 | 0.0248 | [12 empty] | Steel/Wrought Iron |  | FULTON | FULTON DFM 7053346 FULTON & RIVER ROAD 3" TIE-IN. DFM 1307-02 MP 0.0248
|  | 1307-01 | 9.83 | [12 empty] | Steel/Wrought Iron |  |  | JOB 7048667; EAST SIDE OF HEALDSBURG BRIDGE
|  |  | 0.0017 | 6.625 |  |  | Other |  | BURNED HOLE IN 6" MAIN WHILE WELDING ON FITTING | Atmospheric Corrosion |  | 2005-10-31 | 2005-10-31 | Other | WELD SAVE-A-VALVE. OVER LEAK | Wrought Iron |  | GRATON | LOC B; LOWERED MAIN TO 50PSI TO MAKE REPAIR
|  |  | 11.6935 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | NORTH COAST DIV; SO7048666
|  |  | 12.0004 | 3.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#7048666
|  |  | 10.4795 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#7059665-06; HWY 116 AND OCCIDENTAL RD. SEBASTOPAL
| 05-40088-1 |  |  | 6 | Transmission |  | Valves |  |  |  |  | 2005-11-03 | 2006-12-02 | Replace Valve >= 2 inch |  | Steel/Wrought Iron | ; | SEBASTOPAL | FLANGE VALVE LEAK AT REG #408-CGT TO DRA...; SAME REG STATION TO BE REPLACED THIS SUM...; REPLACED VALVE
|  |  | 1.2372 & 1.3801 | 8.63 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#70556245-07
|  |  | 0.5647 | 6.25 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | MAIN INSPECTION REPORT FULTON DFM NORTH TIE-IN 7053346-07. DFM 1307-01 MP 0.5647
|  |  | 0.402 | 6.25 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | MAIN INSPECTION REPORT FULTON DFM SOUTH TIE-IN 7053346-07 DFM 1307-01 MP 0.4020
|  |  | 26.2241 | [12 empty] | Steel/Wrought Iron |  |  | SO#7053845; USED 2" FLEXHOSE FOR TEMP BYPASS. RE0USED EXISTING 8" PCF'S FOR SHUTDOWN
| 99-58075-1 |  |  | 2 |  |  | Drip |  |  | Damage by 3rd Party |  | 1999-10-01 | 1999-10-01 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | SONOMA | REMOVED VALVE, INSTALLED DEAD END CAP; SEE MR. CUNNIGHAM ABOUT REMAINING 2" DRIP
|  |  | 21.84 | 8 | [11 empty] | Steel/Wrought Iron |  |  | SO#7035593-01; INSTALLATION FITTING
|  |  | 22.02 | [12 empty] | Steel/Wrought Iron |  | SANTA ROSA | SO#7035593-01; SANTA ROSA; PIPE TO SOIL TEST ON 8" D.F.M.
| 03-40082-1 | 1305-01 | 26.38 | 8 | Transmission |  | Body of Pipe |  |  | Atmospheric Corrosion | DIG-IN | 2003-10-25 | 2003-10-25 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SANTA ROSA | AO#8060468; INSTALLED (2) 8" REPAIRS LEAKS X.500WT; SOAP TEST & X-RAY
|  |  | 4.353 | 8.625 | [14 empty] | SO#7049467
|  |  | 5.8406 | 6.625 | [11 empty] | Steel/Wrought Iron |  |  | SO#8067538; 253' N/O CENTER OF AGUA CALIENTE. CREEK SONOMA HWY 12
|  |  | 5.8524 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#8067538; 293' N/O AGUA CALIENTE CREEK CENTER. HWY 12 SONOMA
|  |  | 5.8939 | 6.625 | [11 empty] | Steel/Wrought Iron |  |  | SO# 8067538; 510' N/O CENTER OF AGUA CALIENTES CREEK HWY 12 SONOMA
|  |  | 8.6005 | 6.205 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#8067538; 16545 ARNOLD RD. H.P.R.
|  |  | 8.9687 | 8.625 | [11 empty] | Steel/Wrought Iron |  |  | SO#8067538;
|  |  | 9.7003 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 8067538; ARNOLD DR.
|  |  | 9.7181 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#8067538; 98' N/S P/L MADRONE RD. ON ARNOLD RD. GLEN ELEN
|  |  | 9.8093 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 8067538; 532' FEET N/O N/PL MADRONE RD. INSPECTION POINT (ON ARNOLD DR. 15341)
|  |  | 10.0419 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#8067538
|  |  | 10.1204 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#8067538; 84' S/O SOUTH P/L MARTIN SF ON ARNOLD RD. GLEN ELEN
|  |  | 10.3464 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 8067538
|  |  | 12.8492 | 8.625 | Transmission | [13 empty] | SO# 7049467
|  |  | 13.8285 | 8.625 | [11 empty] | Steel/Wrought Iron |  |  | SO#8067538
|  |  | 13.9133 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#8067538; DUNBAR RD. S/O HWY 12 271'
|  |  | 13.9766 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7049467; DUNBAR RD. & HWY 12
|  |  | 15.7946 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#7049467;
|  |  | 16.3913 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#7049467; HWY 12 & GREE ST. KENWOOD AT THE 2" FIRE VALVE
|  |  | 16.6765 | 6.625 | [11 empty] | Steel/Wrought Iron |  |  | SO#7049467
|  |  | 16.9684 | 6.625 | [11 empty] | Steel/Wrought Iron |  |  | SO#8067538; INSPECTED 6" D.F.M. AT VALVE TEE TO D. REG. STATION #736
|  |  | 17.1539 | 6.625 | Transmission | [13 empty] | SO#7049467
|  |  | 18.381 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7049467
|  |  | 18.776 | 6.625 | Transmission | [13 empty] | SO#8067538
| 03-40082-1 | 1305-01 | 26.3802 | 8 | Transmission |  | Body of Pipe |  |  | Atmospheric Corrosion | DIG-IN | 2003-10-25 | 2003-10-25 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SANTA ROSA | SO#8060468; INSTALLED (2) 8" REPAIRES LEAKS X.500WT.
|  |  | 4.74 | [12 empty] | Steel/Wrought Iron
|  |  | 0.03 | [12 empty] | Steel/Wrought Iron
| 08-02034-1 |  | 9.0892 | 8 | Transmission | DFM | Body of Pipe |  |  | External Corrosion |  | 2008-04-08 | 2009-12-18 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | COTATI | 8" SERIES 300 MUELLER PCF; 1" SAVE-A-VALVE WEST SIDE; 2" SAVE-A-VALVE GAST SIDE
| 08-13813-1 | DFM-SONOMA | 2.38 | 6 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2008-03-18 | 2008-11-19 | Other | PCF (WELDED) NOT TAPPED MUELLER ANSI 150# | Steel/Wrought Iron |  | SONOMA | ANSI 150 MUELLER TO REPAIR THE LEAK, NOT TAPPED BECAUSE CORROSION PIT WAS 6" LONG & A LEAK CLAMP IS ONLY 5" LONG. A PCF IS 9" LONG
|  | 1302-01 | V-30.26 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  | COTATI | 8.625" DFM 1302-01, 0.219" W.T., X-41 ERW.
|  | 1302-02 | V-30.26 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  | COTATI | 8.625" DFM 1302-02, 0.172" W.T., X-42 ERW
| 09-00320-1 | DFM1301 | 28.82 | 8 | Transmission |  | Valves |  |  | Material Failure |  | 2009-03-25 | 2009-04-07 | Replace TP Main |  | Steel/Wrought Iron |  | PENNGROVE
| 08-02037-1 |  | 3.0253 | 8 | Transmission |  | Valves |  | ABOVE DRIP | Other | VARIOUS LEAKS ON VALVE | 2008-04-09 | 2009-08-27 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | COTATI | CUT OUT VALVE AND DRIP REPLACE W/... CAN; REMOVED LEAKING NORDSTROM FITTING REPLACE W/ 6' 8" STEEL PIPE, INSTALLED 1-8" ANSI 300 MEULLER THIN WALL LINE STOPPER & UTILIZED V -30-30 FOR SHUT DOWM
| 08-02036-1 | 1301-01 | 1.56 | 8 | Transmission |  | Drip |  |  | Unknown |  | 2009-04-09 | 2009-10-09 | Other | REPLACED 4' TRANS PIPE | Steel/Wrought Iron |  | PENNGROVE | REMOVED DRIP; REMOVE DRIP
| 08-02035-1 |  | 0.7103 | 8 | Distribution Main |  | Valves |  |  | Other | LEAKING VALVES | 2008-04-09 | 2009-09-10 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | PETALUMA | CUT OUT 4 VALVES AND BRIDEL; CUT OUT 4 VALVES AND BRIDEL CONNECTED 2 REG. 484 INSTALLED 7'CM8"/ ALSO CUT OFF REG 484 FROM DIST. SIDE
|  |  | 0.53 | 2 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | REWRAPPED 4' EXPOSED 2" IN PIPE IN DIRT ROAD. RECONSTRUCTED ROAD TO GIVE PIPE 10" OF COVER PIPE LOOKS TO HAVE BEEN EXPOSED IN OTHER AREAS OF ROAD AND BACKFILL WITH DRAIN ROCK BY OTHERS. PIPE SHOWS ECIDENCE OF BEING WALKED ON BY TRACK EQUIPMENT. PIPE HAS UNIFORTUNATLY SPACED DENTS INDICATING DAMAGE BY TRACK LAYING EQUIPMENT. RECOMED FURTHER PROSPECTLY TO SEE THE EXTENT OF PIPE THAT SHOULD BE REPLACED AT THE VERY LEAST ROAD ...FURTHER RECONSTRUCTION TO ...MOVE COVER ASAP
|  |  | 3.076 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | REPLACED 6" VALVE
|  |  | 3.0102 | 6 | [5 empty] | Other |  | 2009-08-07 | 2009-08-08 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SONOMA | WHILE DIGGING UP SERVICE TEE HOOKED ABANDONED SERVICE TEE THAT WAS UNMARKED 4' AWAY GOING OPPOSITE DIRECTION. CUT OFF TEES AND SLEEVED MAIN.
|  |  | 2.8543 | 6 | Transmission | [6 empty] | 2009-08-07 |  |  |  | Steel/Wrought Iron |  |  | PM# 30715912; 6" LINE STOPPER TO REMOVE HOME MADE SERVICE TEE FROM MAIN & SERVICE REGS.
|  |  | 3.031 | 6 | Transmission | [6 empty] | 2009-08-07 |  |  |  | Steel/Wrought Iron |  | SONOMA | PM 30715912; 6" LINE STOPPED TO REMOVE HOME MADE SERVICE TEES FROM MAIN AND SERVICE REGS.
|  |  | 1.7361 | 4.5 | Transmission | [6 empty] | 2008-07-28 |  |  |  | Steel/Wrought Iron |  | SACRAMENTO | 30635910-08; REPLACE NON-OPERABLE VALVE
|  |  | 1.1047 | 16 | Transmission | [6 empty] | 2008-11-03 |  |  |  | Steel/Wrought Iron |  | FOLSOM | PM 30581287-08
|  | 108 | 3.9425 | 8 | Transmission | [10 empty] | Cast Iron |  | SACRAMENTO | LIE 108 ROUGHT 0608-01 SEGMENT 129C; MP 3.9425; LATIT 38 28 39.24703, LONG -121 23 48.68104; WILBER WAY SACRAMENTO.; ; MISC. COMMENTS/ INFORMATION: THIS SITE CONTAINED A CASING 50' IN LENGTH. RUBBER END SEALS IN GOOD CONDITION WHEN PRESENT ON EITHER END, AS WELL AS LINK SEALS WITH 12 BOLTS. WHEN THE END SEALS WERE REMOVED, WATER RUSHED OUT OF THE CASING; A SAMPLE WAS COLLECTED AND GIVEN TO PG&E ATS FOR ANALYSIS (6.0PH). SOUTH EDGE A-FRAME AND PCM TESTING WERE NOT PERFORMED PER MIKE WEST AND AS OF 6/9/10 ALL CASING PROCEDURES WERE REINSTATED PER LEE HAYNES (SEE NOTES IN CASING WORKBOOD). A CASING VENT WAS PRESENT AT THE SOUTH END AT 12:00 ALONG WITH AN ETS, WHILE THE NORTH END REVEALED A BURIED AND CUT-OFF CASING VENT AT 6:00 AND TEST LEADS. THE ENTIRE 50' LENGTH OF CASING WAS REMOVED PER MIKE WEST. THEREFORE, NO POST-REMEDIATION OF AS-LEFT DATA NEEDED TO BE COLLECTED IN THE CASING WORKBOOK.. THE PIPE WAS SANDBLASTED, AN INSPECTION WAS PERFORMED ON THE ENTIRE 50' OF PIPE. ETS WIRES WERE ATTACHED AT THE SOUTH END. THE PIPE WAS RE-COATED WITH PROTAL 7200. THE SITE WAS BACKFILLED WITH IMPORTED SAND AND SASE ROCK. A COMPACTION TEST WAS PERFORMED. ASPHALT WAS LAID.
|  |  | 1.886 | [8 empty] | 2007-11-05 | 2007-11-06 | Welded Sleeve/Can - Weld |  |  |  | WEST. SACRAMENTO | 40761703; CUT IN 4" CAN
|  |  | 0.02 | [12 empty] | Steel/Wrought Iron |  | ARBUCKLE | SO7039925-01
|  |  | 1.80 ->1.93 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO7041408-02; PLAT2525, MAP H4, BLCOK 90; INSPECTION POINT SACTO FLOATER DFM
|  |  | 3.29 | [12 empty] | Steel/Wrought Iron |  | SACRAMENTO
|  |  | 3.97 | 6.625 | [11 empty] | Other | X-42 |  | GM7033525
|  |  | 4.21 | 6.625 | [11 empty] | Other | X-42 |  | GM7023525; CUT & CAPPED EXIST. ...DFM
|  |  | 4.07 | 6.625 | [11 empty] | Other | X-42 ERW |  | GM7023525CUT & CAPPED EXIST 0.188" DFM
50 | 97-55009-1 |  |  | 0.75 | Transmission |  | Body of Pipe |  |  | Digin |  | 1997-03-18 | 1997-03-18 | Replace Pipe |  | Steel/Wrought Iron |  | WEST SACRAMENTO | LOCATED SERVICE AND MAIN OPENED A 4' X 5" HOLE OVER THE GAS TEE AND PLUGED OFF THE SERIVCE. THERE WAS NO U.S.A. MARKER
52 | 97-60081-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1997-05-17 | 1997-05-17 | Replace Pipe |  | Steel/Wrought Iron |  | ELK GROVE | REPLACED 5' OF 4" .237 WT. PIPE INSTALLED ONE 2" SAV-A-VALVR AND ONE 1" SAV-A-VALVE
|  |  | 0.0809 | [12 empty] | Wrought Iron |  |  | SO 7046253-05; INSPECTION
|  |  | 0 | 08.62 & 04.50 | Transmission | [13 empty] | WELD UP 8" & 4" TO FITTINGS (P.C.F.) ON S. RIVER RD
| 98-53076-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1998-08-13 | 1998-08-13 | Clamp |  | Steel/Wrought Iron |  | VACAVILLE | INSTALLED 4" CLAMP & WRAPPED PIPE
|  |  | 2.03 | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | JOB#7045805
|  |  | 1.64 | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | JOB7045805
|  |  | 2.2515 | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | SO 7052329; RELOCATED 500' OF 4" D.F.M.
|  |  | 1.4366 | 0.35 | Transmission | D.F.M. | [9 empty] | Steel/Wrought Iron |  |  | 7053506 40' NORTH OF CMF ENTRANCE, #7053506-04
|  |  | 1.6119 | 3.5 | Transmission | D.F.M. | [9 empty] | Steel/Wrought Iron |  |  | JOB 7053506 AT BOTTOM TAP 6"
|  |  | 1.16 | 3.5 | Transmission | D.F.M. | [9 empty] | Steel/Wrought Iron |  |  | JOB 7053506 AT DIST. REG. SET.
|  | 604.01 | 4.69 | 6.625 | [14 empty] | SO7054093; INSPECTION
|  | 604.01 | 5.13 | 6.625 | [14 empty] | SO7054093; INSPECTION
|  |  | 16.44 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO7044266-06; INSPECTION POINT
|  |  | 16.39 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7044266-03; INSPECTION POINT
|  |  | 14.17 | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 8049736-02; SEE ATTACHED SHEET
|  | 0611-09 | 15.5749 & 15.6000 | [12 empty] | Steel/Wrought Iron |  |  | 7052046-04; INSPECTION POINT. ALTER 8" TP DFM TO CLEAR BUFFALO CREEK "BOX" CULVERT.
| 01-20268-1 | FEEDER | 7.93 | 4 | Transmission |  | Valves |  |  | Unknown |  | 2001-09-17 | 2001-12-19 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | R. CORDOVA | FOUND LEAK ON BOTTOM OF BALL VALVE. NO HA...; PLUG LEAK REPAIRED ON BOTTOM OF BALL VAL.
|  |  | 21.88 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 7044269; INSTALLED (2) 10' MUELLER FITTINGS AND OFF-SET
|  |  | 21.86 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 7044269; INSTALLED (2) 10" MUELLER FITTING AND OFF-SET
|  |  | 0.1876 | [12 empty] | Steel/Wrought Iron |  |  | SO7054025-05; INSPECTION
52 | 93-20025-1 |  |  | 12 | Distribution Feeder Main |  | Girth Weld |  |  | Material Failure |  | 1993-01-13 | 1993-01-14 | Replace Pipe |  | Steel/Wrought Iron |  | SACRAMENTO | REPLACED 3' OF 12" STL MAIN 1 BOLT WELD AND 1 SLEEVE
|  | 116 | 2.6915 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | SACRAMENTO | SACRAMENTO DOS RIOS ST. & N B ST. ; LINE 116 MP 2.6915; LATIT 38 35 25.43411 LONG -121 2910.14084
|  | 116 | 1.0685 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | SACRAMENTO | SACRAMENTO 3RD ST.; LINE 116 MP 1.0685; LATIT 38 34 54.19738, LONG -121 30 12.8702; ; GAS PIPE IS PROTECTED BY A HALF OF PIECE OF PIPE. THIS PIPE RUNS OVER THE WAL WAY GOING UNDER HWY5 TO OLD TOWN SACRAMENTO
|  |  | 0.10 & 0.13 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO7040348-03
|  | 0615-01 | 2.4 | 4 | Distribution Main |  |  |  |  | Damage by 3rd Party | DIG IN | 2000-11-07 | 2000-11-07 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SACRAMENTO | SO 8039920; TWO DEEP GOUGES 11" APART USING 4" WELD SLEEVE
|  |  | 0.04 | [12 empty] | Steel/Wrought Iron |  |  | SO 7039045-01
| 04-56000-1 |  | 0.42 | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2004-02-19 | 2004-02-20 | Other | SAV-A-VALVE WELDED OVER HOLE | Steel/Wrought Iron |  | COLUSA | JOB #8063040; 2209' FROM TAP TO LEAK LOC. 3 SPONS GROM BEGINNING OF DIRT RD. TO LOCATION MINUS 20'
|  | 0630-01 | 1.4 | [12 empty] | Steel/Wrought Iron |  | COLUSA | SO 7038130-01
|  | 0630-01 | 1.41 | [12 empty] | Steel/Wrought Iron |  | COLUSA | SO70381130-01
|  | 0630-01 | 1.4 | [12 empty] | Steel/Wrought Iron |  | COLUSA | SO#7038130-01
|  | DCUST |  | 6.25 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE DCUST (OFF 108 63.16) JOB 7034393 & 7019485; CAN'T TELL WHERE THIS IS. TIE-IN...
|  | 158 | 5.72 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | YOLO TOWN | L 0646-01 MP 5.72 JOB 7043123; DONE WITH SOFT DIG TECHNOLOGY EXPOSING 1' OF PIPE FOR G.T.S. INSTALL
|  | 158 | 5.74 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | YOLO TOWN | DONE WITH SOFT DIG TECHNOLOGY EXPOSING 1' PIPE FOR G.T.S. INSTALL
|  | 158 | 5.75 | 6 | Transmission | [12 empty] | YOLO TOWN | L0646-01 MP 5.74 JOB 7043123; DONE WITH SOFT DIG TECHNOLOGY EXPOSING APPROX 1' PIPE FOR E.T.S. INSTALL
|  | 0646-01 | 9.64 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | YOLO TOWN | L0646-01 MP9.64 JOB 7043123; DONE WITH SOFT DIG TECHNOLOGY EXPOSING APPROZ 1' OF PIPE FOR E.T.S. INSTALLATION
|  | 0646-01 | 9.62 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | YOLO TOWN | L0646-01 MP 9.62 JOB 7043123
|  | 0646-01 | 9.62 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | YOLO TOWN | L0646-01 MP 9.62 JOB 7043123; DONE WITH SOFT DIG TECHNOLOGY EXPOSING APPROX 1' OF PIPE FORE E.T.S. INSTALLATION
|  |  | 2.36 | 4.5 | Transmission |  | Body of Pipe |  |  | Digin | (BORE) | 2002-09-12 | 2002-09-12 | Replace TP Main |  | Steel/Wrought Iron |  | SACRAMENTO | INST. (2) 4" PCF (BT) SER. 30 & 119' OF 4" STL. PIPE .237" WT.; SEE ATTACHED DRAWING
|  |  | 0.36 | [12 empty] | Steel/Wrought Iron |  |  | SO#8051776
|  |  | 0 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO7038709
|  |  | 14.1 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO7038709
|  |  | 0 | 6.62 | Transmission | [13 empty] | SO7038709
|  | AIRPORT FEEDER | 0.40 & 0.55 | 04.50 & 02.375 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO7044268-03; AIRPORT FEEDER; INSPECTION POINT
|  |  | 17.46 | 10 | Transmission |  | Fitting | [8 empty] | Steel/Wrought Iron |  | FOLSOM | SO7043963-02
|  |  | 1.64 | 8.65 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO 70413258" MAIN AT AT LAS SPUR AREA R.T. PROJECT
| 01-55046-1 | 158 |  | 6 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2001-06-25 | 2001-07-12 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron | ; | WOODLAND | USED 6" LEAK REPAIR CLAMP
| 02-20138-1 |  | 0.36 | 6 | Transmission |  | Body of Pipe |  |  | Other | DING IN PIPE | 2002-04-09 | 2003-08-12 | Other | SLEEVE | Steel/Wrought Iron |  | SAL. | WELDED SLEEVE AND SAV-A-VALVE OVER BAD SPOT ON TRANS MAIN. ; WELDED SLEEVE OVER SMALL HOLE IN TRANS. MAIN.
|  |  | 2.6 | 8.62 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO7041326; LOCATION 03+60
|  |  | 2.66 | 8.62 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO7041326; LOCATION 0+00
|  |  | 2.28 | 8.62 | Transmission | DFM 8" | [9 empty] | Steel/Wrought Iron |  |  | SO 7041326 ABANDONED ROUT 0617-14; "SEE ATTACHED"
|  |  | 1..50, 1.52, 1.55, 1.70, 1.93, & 2.09 |  | Transmission | VARIOUS | [12 empty] | SO 7041326 ABANDON ROUTE 0617-14; VARIOUS. "SEE ATTCHED" FOR ABANDONMENT OF 8" D.F.M.- FOLSOM
|  |  | 1.49 | 8.62 | Transmission | D.F.M. | [12 empty] | SO#7041326 ABANDON; "SEE ATTACHED"
|  |  | 0.8032 | 8 | Transmission | D.F.M. | [9 empty] | Steel/Wrought Iron |  | FOLSOM | SO7046207; NISPECTION POINT
|  |  | 1.9191 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | FOLSUM | ...281-A1 STAND BY 12" D.F.M.; STAND BY
|  |  | 1.9397 | 12 | Transmission | [6 empty] | 2004-09-22 |  |  |  | Steel/Wrought Iron |  | FOLSUM | ...281-A1 STANDBY 12" D.F.M.; STAND BY
|  |  | 1.8942 | 12 | Transmission | [6 empty] | 2004-09-22 |  |  |  | Steel/Wrought Iron |  | FOLSUM | ... 281-A1 STAND BY 12" D.F.M.; STAND BY
|  |  | 1.8927 | 12 | Transmission | [6 empty] | 2004-09-22 |  |  |  | Steel/Wrought Iron |  | FOLSUM | TBM 281-A1 STAND BY 12" D.F.M.; STAND BY
|  |  | 0.0022 | 2.375 | Transmission | DFM | [9 empty] | Steel/Wrought Iron |  |  | JOB # 7053506;; AT V58 CRPSS TIE;; SORRTE. DREG4040, MP. 002; STUB 7893, MP. 0097; (DSAC) 7053506-04
|  |  | 2.44 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SACRAMENTO DIVISION DFM 0605-01, M.P. 2.4400; SO# 7050306-05; INSTALLED NEW VALVE; BEAR CREEK CANAL
|  |  | 0.0294 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 4'' DFM TAP; SIERRA DIV.; 7048308 WHITE ROCK ROAD DFM 0617-06; RELOCATION DRE 4863 MP 0.0294; TIE. IN LOCATION 3.
|  |  | 18.8527 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 10'' DFM SIERRA DIV.;; 7048308-05 WHITE ROCK ROAD DFM 0617-06; RELOCATION MP 18.8527;; TIE-IN LOCATION.;
|  |  | 19.2819 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 10'' DFM SIERRA DIV.; 7048308-05 WHITE ROCK ROAD DFM 0617-06 RELOCATION MP 19.2819;; TIE-IN LOCATION 2
|  |  | 19.5366 & 19.5876 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 10''DFM SIERRA DIV.;; 7048308-05; WHITE ROCK ROAD DFM LOCATION; 0617-06;; MP 19.5366; MP 19.5876;; TIE-IN LOCATION 1-A & 1-B
|  |  | 0.53 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | STUB8208 M.P. 0.5300 JOB 7057168 OLD ROUTE 0013-10; VALVE D-83 ABANDONED IN PLACE
|  |  | 0.5396 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT = 0613-10;; STUB8207 M.P. 0.5396 JOB 7057168 OLD RT 0613-10; ABANDONED VALVE D-23 IN PLACE INSTALLED 4" BLIND FLANGE 60" COVER;
|  |  | 4.5137 & 4.5430 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RTE. 0615-01; M.P. 4.5137; M.P. 4.5430; SO# 7057025-05; DIV: SACRAMENTO
|  | 604.01 | 0.0006 | 3.5 | [14 empty] | SO # 7054093; ROUTE = STUB8271; MP 0.0006;; ; CUT OFF IDLE PARRALLEL T.P. MAIN! 3" STL;
|  |  | 0.1618 | 6 | [14 empty] | EXISTING 6'' DFM;; DIV: SACRAMENTO SO# 7054313-05 DFM 0615-02, M.P. 0.1618
|  |  | 0.8627 | 4 | [14 empty] | EXISTING 4'' DFM;; DIV: SACRAMENTO SO # 7054313-05; DFM 0615-01, MP 0.8627
|  |  | 3.2837 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAC. COUNTY | FOLSOM DFM TIE-IN # 7054526 16'' DFM;; RT. 0617-08 MP 3.2837 JOB 7054526;;
|  |  | 8.9108 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAC. COUNTY | FOLSOM DFM TIE-IN # 7054526 8'' DFM;; RT. 0617-06 MP 8.9108 JOB 7054526;
|  |  | 9.9853 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | FOLSOM DFM EAST END. 8'' # 7054526;; RT. 0617-06 MP 9.9853 JOB 7054526;;
|  |  | 9.8686 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | FOLSOM DFM DIG-IN REPAIR 8'';; RT. 0617-06 MP 9.8686 JOB 7054526; MADISON AVE (SCOTT'S SEADOOD) ARB DAMAGE LINE DURING CONST. OF NEW 16" DFM; INSTALLED A 8" X 24" REPAIR SLEEVE 02-1077; ;
|  |  | 1.16 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 0604-14 M.P. 1.16 (DEACTIVATED) JOB 7058147; INSPECTION ;
|  |  | 4.76 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | STUB 8476 M.P. 4.76 JOB 7058147; INSPECTION
|  |  | 16.35 | 10 | Transmission |  | Girth Weld |  |  |  |  | 2005-09-28 | 2005-10-01 | Deactivate #TP Main | REPLACE TP MAIN | Steel/Wrought Iron |  | FOLSOM | ROUTE 0617-06; MP 16.35; SACRAMENTO DIV.; SO # 7058609;; REPLACED 120' OF 10''-250 WALL X 52 - REPLACED 4''-237 WALL G&B SMTS 10'; LEAK AT FOLSOM DFM LNG TAP
|  |  | 0.0343 | 2 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | ROUTE DREG4040;; M.P. 0.0343;; # 7058446;; SACRAMENTO DIV.;;
|  |  | 5.9393 | 8 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | ROUTE 0604-07 #7058446, M.P. 5.9393, SACRAMENTO DIV
|  |  | 12.9854 & 13.0118 | 12.75 | [11 empty] | Steel/Wrought Iron |  |  | TEST 1; ROUTE DFM 0617-14; M.P. 0.0426; SO# 7045253;; ROUTE 0617-06; M.P. 12.9854; 13.0118; INSPECTION
|  |  | 0.7415 | [15 empty] | TEST 2; SO# 7045253; ROUTE 0617-14; M.P. 0.7415; INSPECTION SITE 8" O.D. X 0.172 W.T.
|  |  | 0.9657 | 6 | [11 empty] | Steel/Wrought Iron |  |  | SO # 7045253; ROUTE 0617-15; M.P. 0.9657; TEST 4; INSPECTION
|  |  | 0.0006 | 6 | Transmission | [13 empty] | SO # 7045253 & SO # 8061201; ROUTE - 0617-15; M.P. 0.0006; INSPECTION
|  |  | 0.0323 | [15 empty] | TEST 5 SO # 7045253 $ SO # 8061201; ROUTE = DREG4089 M.P. 0.0323; INSPECTION SITE
|  |  | 6.9201 | [15 empty] | SO # 7045253 & SO # 8061201; INSPECTION SITE
|  |  | 0.8088 | [15 empty] | TEST 6 SH 2 DETAIL 2; ; SO # 7045253 & 8061201; ROUTE DREG 4088 M.P. 0.8088
|  |  | 9.823 | [15 empty] | TEST 5 SO# 7045253 & SO # 8061201;; ROUTE 0617-06; MP 9.8230; ISLOATION POINT TEST 5-B +12
|  | 0.0446 | [16 empty] | TEST 2; SO # 7045253 & SO # 8061201; ROUTE 0617-14 M.P. 0.0446; INSPECTION SITE
|  |  | 20.6519 | [15 empty] | SO # 7045253 & SO # 8061201; ROUTE 0617-06 M.P. 20-6519; REG STATION A-512 ELDORADO HILLS; INSPECTION SITE
|  |  | 10.795 | [15 empty] | SO # 7045253 & SO # 8031201 ; ROUTE = 0617-06 M.P. 10.7950; TEST 5.; FOLSOM DFM UP-RATE; INSPECTION SITE
|  |  | 10.8776 | [15 empty] | TEST 5; SO # 7045253 & SO # 8061201; ROUTE: 0617-06 M.P. 10.8776; INSPECTION SITE AT NEW VALVE LOCATION 8" X 0.188 W.T.
|  |  | 11.0124 | [15 empty] | SO # 7045253 & SO # 8061201; ROUTE: 0617-06 M.P. 11.0124; INSULLATING FITTING; INSPECTION SITE
|  |  | 0.9854 | [15 empty] | TEST 3; SO # 8061201; ROUTE 0617-06; M.P. 0.9854; 12" X 0.281 W.T. AT INSPECTION SITE
|  |  | 12.9844 | [15 empty] | TEST 3; SO # 7045253 & SO # 8061201; ROUTE 0617-06 MP 12.9844; 12" X 0.281 W.T. AT INSPECTION SITE
|  |  | 11.5251 | [15 empty] | TEST 3; SO # 7045253 & SO # 8061201; ROUTE: 0617-06 M.P. 11.-5251; INSPECTION SITE
|  |  | 13.8980, 13.9806, & 14.1216 | 10.75 | [11 empty] | Steel/Wrought Iron |  |  | TEST 1A; ROUTE = 0617-06 M.P. 13.8980; M.P. 13.9806; M.P. 14.1216; ; SO # 7045253; 8061201; INSPECTION 84" COVER
|  |  | 0.0521, 0.0009 | 12.75 | [11 empty] | Steel/Wrought Iron |  |  | TEST 3; ROUTE = 0617-01; M.P. 0.0521; SO # 7045253 & SO # 8061201; ROUTE = 0617-03 M.P. 0.0009; ROUTE X-69 5 M.P. 0.0012;; SACRAMENTO DIV.
|  |  | 7.7921 | [15 empty] | SO # ...045253 & SO # 8061201 ROUTE 0617.06 M.P. 7.7921; ISOLATION POINT TEST 6
|  |  | 0.4953 | [15 empty] | TEST 6; SO # 1045253 & SO # 8061201; ROUTE : 0617-09 M.P. 0.4953;
|  |  | 7.7096 | [15 empty] | SO # 7045253 & SO # 8061201; ROUTE: 0617-06 M.P. 7-7096
|  |  | 5.347 | [15 empty] | TEST 6; SO # 7045253 & SO # 8061201; ROUTE: 0617-06 M.P. 5.3470
|  |  | 11.2907 |  | Transmission | [10 empty] | Steel/Wrought Iron |  | FOLSOM | JOB # 7056247; ROUTE: DFM 0617-06; M.P. 11.2907; CGT 7056247; 12'' TDW FITTING;
|  |  | 12.651 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | KKT= 0604-06, M.P.-1.2651; PM# 7056492; PLAT SHEET # 2715F7; 4" SPLIT P.C.F. 3' OFF V-49 BOTH DIRECTIONS
|  |  | 1.4676 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM # 7056492; PLAT SHEET # 2715 F7; ; RT= 0604-06, M.P. 1.46 6;; P.M. # 7056492; PLAT SHEET 2715 F7;; ; NOTE: REMOVED VALVE FRAME & COVER V-49 IN OPERABLE-LEFT IN OPEN OPSITION. REMOVED VALVE EXTENSION & GREASE FITTING EXTENSION BACKFILLED IN PLACE (48 INCHES COVER ON PIPE SEAN HILL G.C. GAS 6-28-06 FORMAN)
|  |  | 0.7376 | 8 | Transmission | DFM | [9 empty] | Steel/Wrought Iron |  |  | 0617-14 M.P. 0.7376 JOB 7060731; VALAVE -130
|  |  | 0.7463 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 0617-14; M.P. 0.7463; JOB 7060731; VALVE D-130
|  |  | 4.0496 | 6 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | DIVISION: SACRAMENTO; SO # 7062825-07 DFM 0602-01; M.P. 4.0496; SOUTH TIE-IN.
|  |  | 4.0602 | 6 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | DIVISION: SACRAMENTO; SO # 7062825-07; NORTH TIE-IN; DFM 0602-01; M.P. 4.0602
|  |  |  | 6 | Distribution Main | [7 empty] | 2008-02-07 | Other | NEW LINE |  |  |  | PM 30606358; INSTALLED NEW LINE, DUE TO LEAK IN CREEK; (CHINA SLOUGH), CO RD 17. YOLO.
|  |  |  | 6 | Distribution Main | [7 empty] | 2008-02-07 | Other | NEW LINE | Steel/Wrought Iron |  |  | RT=0646-01; M.P.=6.8973; P.M. 30606358; INSTALLED NEW LINE, DUE TO LEAK IN CREEK. (CHINA SLOUGH) CO RD 17-YO LO.
|  |  | 0.0294 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 4'' DFM TAP SIERRA DIV.; 7048308 WHITE ROCK ROAD DFM 061706 RELOCATION DREG 4863 M.P. 0.0294; TIE-IN LOCATION 3; NEW 10" STL X42 ERW
|  |  | 4.5137 & 4.5430 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RTE. 0615-01; M.P. 4.5137; M.P. 4.5430; SO # 7057025-05; DIV.: SACRAMENTO
|  |  | 0.0192 | 2 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 0634-01; M.P. 0.0192; SO # 8086016
|  |  | 4.56 | 8.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | LAGUNA AREA | 0607-01 M.P. 4.56; INSPECTION POINT, CLEARED CONTACT WITH PAC BELL GROUND ROD. NO DAMAGED TO GAS MAIN. TBM 358 E-5 WM/PS 2654 F8 8LAGUNA AREA. SACRAMENTO COUNTY
| 03-20302 |  | 0.6939 | 10.75 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2003-12-08 | 2003-12-09 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SAC. | INSTALLED FULL ENCIRCLEMENT SLEEVE OVER CORROSION LEAK; S.O. 8061037; RT=0611-02; M.P.- 0.6939; PAGE 5 OF 9; TBM 317-F3; REPAIR LOCATION. INSTALLED FULL ENCIRCLEMENT SLEEVE. 10.75" ID STEEL, ASTM A-SIDE GRADE TO 35,000 SMYS .500" W.T. OS PER GS & C A 60
|  |  | 0 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ROUTE 0609-03; M.P. 0.00; JOB 7019486
|  |  | 6.1784 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | (STUB 8717) 0607-01 M.P. 6.1784 JOB 7055668
|  |  | 0.6919 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 0607-01 M.P. 0.6919; SO # 7055727;
|  |  | 1.3784 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 0618-10; M.P. 1.3784; P.M. 30635174; ABANDON 10" DFM, NEW 10" DFM
|  |  | 1.4684 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 0678-10; M.P. - 1.4684; P.M. # 30635174 ; ABANDON 10" DFM, NEW 10" DFM
|  |  | 19.5838 | 10.75 | [11 empty] | Steel/Wrought Iron |  |  | RT = 0617-06; M.P. = 19.5838; P.M. # 30617416
|  |  | 4.0713 | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | P.M. # 7055245; RT = 0630.01; M.P. - 4.0713;
|  |  | 0.7975 | 12.75 | Transmission | [7 empty] | 2009-04-29 | Clockspring - Other |  | Steel/Wrought Iron |  |  | CALLED JERRY MONROW SR. GAS ENGINEER SACRAMENTO. JERRY MADE THE DISICISION TO INSTALL A CLOCKSPRING; 0617-06; MP = 0.7975; 40+99; 16'' REPAIR LENGTH PER ... 6-8-09 QA M...
|  |  | 0.7975 | 12.75 | Transmission | [7 empty] | 2009-04-29 | Clockspring - Other |  | Steel/Wrought Iron |  |  | CALLED JERRY MONROE SR. GAS ENGINEER SACRAMENTO. JERRY MADE THE DISCISION TO INSTALL A CLOCKSRPING; DUPLICATE 0617-06; M.P. = 0.7975; 40+99
|  |  |  | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 3+65; 0617-15; MP = 0.1733
|  |  | 0.0705 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 0617-01; M.P. = 0.0705;
|  | 815.01 | 1.43 | 8.62 | Transmission |  | Body of Pipe |  |  |  |  | 2005-05-23 | 2005-05-23 | Other |  | Steel/Wrought Iron |  | WEST SACRAMENTO | (I) 0.010" GAUGE GRAND OUT/ 0.150" DENT- NO ACTION REQ'D. PIPE RECOATED, BACKFILLED; DUPLICATE - ORIGINAL LOST; SO # 8072004; RECITE - DREG 4998; M.P. 1.4697; (I) 0.010'' GAUGE- GROUND OUT / 0.150'' ... - NO ACTION REQ'D; PIPE RECOATED, BACKFILLED.; NOTE: THIS IS A DUPLICATE A1 FORM, ORGINAL FORM LOST. CONTRACT EXCAVATOR WAS INSTALLING (2) 60" SEWER MAINS UNDER 8" SOUTHPORT DFM. THE PG&E STANDBY PERSON WAS TOLD A BACKHOE WAS BEING BROUGHT IN TO FINISH THE EXCAVATION NEAR THE DF,. THE EXCAVATOR OPERATOR GOT TIRED OF WAITING AND PROCEEDED TO DIG WHEN THE STAND BY PERSON WALKED AWAY FROM THE JOB SITE. THERE WAS (1) 0.010" GOUGE AND A 0.150" DEEP DENT (3" X3"). PER UO S4134, THE GROUND OUT AND MAG PARTICLE TESTED AND THE AREA RECOATED.
|  | 0615-01 | 4.4 | 8 | Transmission |  |  |  |  | Digin | DAMAGE BY 3RD PARTY | 2005-09-13 | 2005-09-13 | Soap and/or Tape - Other | OTHER= GROUND OUT ROUGH EDGES ON GOUGE MAG PARTICLE FOR CRACKS | Steel/Wrought Iron |  | SACRAMENTO | ...OUT DENT W/ BUFFING WHEEL, MAG PARTICLE GOUGE AREA (...R), REWRAP W/ WAK TAPE; DENT: 3'' WIDE/ 16 1/2'' LONG/ .330'' DEEP (3.8% DD); GOUGE: 0.020'' @ DEEPEST POINT/ 21'' LONG
|  |  | 1.1788 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIVISION SACRAMENTO; PM 30604181; DFM 0019-05; MP: 1.1788; TIE-IN EAST END OF STONE BLVD. WEST SACRAMENTO STATION 21+64; PM 30604181.
|  |  | 0.4119 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIVISION SACRAMENTO; PM 30604181; DFM 0619-05; M.P. 0.4119; TIE-IN WEST END OF STONE BLVD. WEST SACRAMENTO, CA. STATION 0+22; PM 30604181
|  | 116 | 1.0693 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | SACRAMENTO | (2) ALREADY IN GIS: "FS 48+22"; ROUTE 0613-01; M.P. 1.0693; (SOURCE ... 116?); LAT = 38.58172149; LONG = -121.5034131; K ... 1/11/20; SACRAMENTO 3RD ST.; LINE 116 M.P. 1.0685; LATIT 38 34 54.19738; LONG - 121 30 12.28702; GAS PIPE IS PROTECTED BY A HALF OF A PICE OF PIPE; THIS PIPE RUNNES OVER THE WALK AWAY GOING UNDER HWY 5 TO OLD TOWEN SACRAMENTO.
|  | 116 | 2.6915 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | (3) ALREADY IN GIS "FS 6+23"; ROUTE 0613-01; (SOURCE RTE 116?); M.P. 2.6933; LAT = 38.59039836; LONG = -121.4861502; KZ 1/11/10.; SACRAMENTO DOS RIOS ST. & N B ST.; LINE 116; M.P. 2.6915; LATIT 38 35 25.43411; LONG -121029 10.14084.
|  |  | 0.8035 | 2.37 | Transmission | [13 empty] | P.M. # 30701316; ROUTE = 0643-01; M.P. = 0.8035;
|  |  | 1.4618 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SACRAMENTO DIV.; P,M. 30604181-09; ROUTE: 0600-05; M.P.: 1.4618;
|  | 188A | 1.4248 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE 118 A STA. 22+47; ROUGHT 0611-02; M.P. 1.4248; LATIT. 38 31 55.74902; LONG - 121 27 36.63826;; COATING WAS IN ROUGH SHAPE, VERY DRY, BRITTLE, AND DISBONDED. SUFFERED SOME ROOT DAMAGE AS WELL. MINOR CORROSION PRESENT, AS WELL AS THREE EXTERNAL CORROSION CELLS WITH GREATER THAN 10% WALL LOSS FOUND. LIGHT SURFACE RUST AND CALCAREOUS DEPOSITS PRESENT.
|  |  | 2.6933 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | SACRAMENTO | INSPECTION; ROUTE 0613-01; M.P. 2.6933.; SACRAMENTO DOS RIOS ST. & N B ST. ROUTE 0613-01; M.P. 2.6933. LATIT. 38 35 25.43411; LONG - 121 29 10.14084.; (A-FORM ALREADY ENTERED)
|  | 188A | 1.4248 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DFM 0611-02 MP 1.4248 KABL.; LINE 118 A STA. 22+47. ROUGHT 0611-02. MP 1.4248. LATIT. 38 31 55.74902, LONG. -121 27 36.63826; 38.53215 LAT ; -121.46015 LON.; COATING WAS IN ROUGH SHAPE, VERY DRY, BRITTLE, AND DISBONDED. SUFFERED SOME ROOT DAMAGE AS WELL. MINOR CORROSION PRESENT, AS WELL AS THREE EXTERNAL CORROSION CELLS WITH GREATER THAN 10% WALL LOSS FOUND. LIGHT SURGACE RUST AND CALCAREOUS DEPOSITS PRESENT.
|  | 119 | 14.8797 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | FOLSOM | DFM 0617-06 MP 14.87...; LINE 119 STA. 10+95 ROUGHT 0617-06; MP 14.8797; LATIT. 38 39 37.60999, LONG -121 07 53.09504; EAST BIDWELL ST. FOLSOM; MISC. COMMENTS/ INFORMATION: THIS SITE WAS LOCATED IN THE CENTER MEDIAN OF EAST BIDWELL STREET IN FOLSOM, ADHERED AND NO CORROSION OR MECHANICAL DAMAGE WAS FOUND. THE PIPE WAS RECOATED WTIH PROTAL 7200 AND THE EDGES WERE WAX TAPED TO IMPEDE THE TRANSITION OF THE OLD TAPE COATING TO THE NEWLY APPLIED PROTAL 7200.; 38.66043/-121.13139.
|  | 116 | 1.1987 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | SACRAMENTO | DFM 0613-01 MP 1.1887. K... ; LINE 116 STA. 54+80; ROUGHT 0613-01; MP 1.1987; LATI. 38 35 00.0718 LONG -121 30 09.47951; 1ST. & 3RD. ST. SACRAMENTO. MISC. COMMENTS/INFORMATION: DIG INSPECTION LENGTH WAS SHORTENED TO 6'-0'' DUE TO INTERFERENCE FROM CONCRETE THRUST BLOCKS FOR WATER MAIN POST INDICATOR VALVES; (PIV'S), PER MIKE WEST. THE CONCRETE ENCOMPASSES BOTH THE 6'' WATER MAIN AND 12.75 GAS MAIN. REMOVING CONCRETE WOULD NULLIFY THE PURPOSE OF THE THRUST BLOCKS. PROTECTION FOR THE PIV'S AND ANY VIBRATIONS FROM USING A JACK HAMMER COULD DAMAGE THE WATER AND GAS MAINS. THERE WERE ONLY 2'' OF SAND SURROUNDING THE GASLINE BEFORE THE CONCRETE WAS REACHED (SEE PHOTO #XX). A GIRTH WELD WAS PRESENT 1'-5'' FROM THE U/S EDGE. NO CORROSION OR MACHANICAL DAMAGE WAS FOUND. THE PIPE WAS RECOATED WITH PROTAL 7200 AND THE EDGES WERE WAX TAPED TO IMPEDE THE TRANSITION OF THE OLD TAPE COATING TO THE NEWLY APPLIED PROTAL 7200. ; 38.58335/-121.50263
|  | 119 | 13.0077 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | FOLSUM | DFM 0617-06 MP 13.0102; KABL; ; LINE 119 STA. 106+06; ROUGHT 0617+06; MP 13.0077; LATIT. 38 39 42.90531, LONG -121 09 28.53636; BLUE RAVINE RD. * RILEY RD. FOLSUM; 38.66190/-121.15793.; ; MISC. COMMENTS/INFORMATION: THIS DIG SITE IS LOCATED ON BLUE RAVINE ROAD AT THE INTERSECTION OF RILEY ROAD AND BLUE RAVINE ROAD IN FOLSOM, CA. IT IS LOCATED AT V-D-106 IN SOIL. A HIGH VOLTAGE ELECTRIC POWER POLE WAS HELD UP BY SMUD SACRAMENTO MUNICIPAL UTILITY DISTRICT DURING EXCAVATION. MEARS HIRED BAY AREA TRAFFIC SOLUTIONS FOR TRAFFIC CONTROL. THE DITCH WAS FULL OF WATER. A VAC TRUCK WAS BROUGHT IN TO REMOVE WATER FROM DITCH. GROUND WATER SAMPLE WAS TAKEN AND GIVEN TO ATS. THE READ PRIOR TO EXCAVATION WAS SCROLLING FROM -803/-584V. INSPECTOR JIM AIRD WAS NOTIFIED. NEAR OHP AND WATER FILLED DITCH. READ AFTER ETS WIRES ATTACHED -860V. DUE TO EXCESSIVE WATER WITHIN THE DITCH, AND THE EXISTING ETS WIRES NOT BEING ATTACHED TO THE PIPE, NEW ETS WIRES WERE CAD WELDED AT THE U/S EDGE AND COVERED WITH WAX TAPED. THE VALVE PIPES AND THE 6'' DISTRIBUTION GAS LINE WERE ALSO WAX TAPPED. FOR THESE REASONS, NO INSPECTION WAS TO BE DONE PER MIKE WEST. A COUPON ETS WAS INSTALLED WITH NATIVE SOIL. THE DITCH WAS BACKFILLED WITH IMPORTED SAND AND TOP SOIL. JWA LANDSCAPE COMPANY WAS HIRED BY MEARS TO COMPLETE THE REPLACEMENT OF THE GRASS. A 3/4'' PVC LINE WAS DAMAGED DURING EXCAVATION AND REPAIRED.
|  | 119 | 12.9559 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | FULSOM | DFM 0617-06 MP 12.9991; ; LINE 119 STA. 103+79; ROUGHT 0617-06;; MP 12.9559; LATIT. 38 39 43.23732, LONG. -121 09 30.84717; RILEY WT. & BLUE RAVINE RD. FOLSUM; 38.66181/-121.15798;; MISC. COMMENTS/INFORMATION: THIS DIG SITE IS LOCATED ON RILEY ROAD AT THE INTERSECTION OF RILEY ROAD AND BLUE RAVINE ROAD IN FOLSOM, CA. DO NO MATCH ... IN THE BIKE LANE AND SIDE-WALK. MEARS HIRED BAY AREA TRAFFIC SOLUTIONS FOR TRAFFIC CONTROL. THE DIG SITE WAS SAW CUT. THE SITE WAS MOSTLY SOLID ROCK NEEDING TO BE JACK HAMMERED OUT. WATER WAS IN DITCH AREA. SAMPLE COLLECTED AND GIVEN TO ATS. THIS SITE IS AT AN ANGLE POINT. THERE IS ALSO A 4'' DISTRIBUTION GAS LINE WITHIN THE DITCH. COATING WAS WELL ADHERED TO THE PIPE. CORROSION , 20% WAS FOUND. GRID WAS DONE ON ANGLE POINT. ETS WIRES WERE CAD WELDED AT THE D/S EDGE. PIPE WAS WAX TAPED DUE TO WATER IN DITCH AREA. PIPE WAS COVERED WITH A LAYER OF TUFF-N-NUFF. DITCH WAS BACKFILLED WITH IMPORTED SAND AND BASE ROCK. ;
| 09-20010- | 0614-13 | 0.01 | 6 | Transmission |  | Valves |  |  | Material Failure |  | 2009-01-05 | 2009-01-06 | Replace TP Main |  | Steel/Wrought Iron |  | SACRAMENTO | DIVISION: SACRAMENTO; PM 30681911-09; DFM 0614-13; PM 30681911; FOR REPAIR; GIS MP 0.0136;;
|  |  | 3.5297 | 8 | Transmission |  | Body of Pipe | [5 empty] | 2009-09-21 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SACRAMENTO | PUT SLEEVE OVER GOUGE ON MAIN DONW AT A LATER DATE UNKNOWN; DIVISION: SACRAMENTO; MACK DFM MP -3.52; 41154086-09; DFM 0608-01; GIS MP 3.5297;; THIRD PARTY CONTRACTOR NOTIFIED PG&E THAT EXPOSED 8'' GAS LINE HAD BEEN DAMAGED BY A PRIOR CONTRACTOR (UNKNOWN NAME/DATE). PG&E ENGINEER (JERRY MONROE) VERIFIED DAMAGE HAD OCCURRED SEVERAL MONTHS/YEARS PRIOR.
|  | 108 | 0.1566 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | SACRAMENTO | DIV: SACRAMENTO; 0609-03; MP 0.1566; ; LINE 108 SEGMENT 103C ROUGHT 0609-03;; MP 0.1538; ; LATIT. 38 29 45.55118, LONG. -121 28 14.88201; ; FLORIN RD. SACRAMENTO.; ; MISC. COMMENTS/INFORMATION: THIS SITE IS LOCATED OFF OF FLORIN ROAD NEAR THE RAILROAD TRACKS IN SACRAMENTO, CA. THE NEAREST CROSSROADS ARE FLORIN ROAD AND INDIAN LN. THE SITE IS ON THE WEST EDGE OF THE CAING CROSSING THE TRACKS. AN COUPON ETS WITH BOTH PIPE AND CASING WIRES AND A CUT OFF PIECE OF A CASING VENT WERE AT LOCATION UPON ARRIVAL. INITIAL AS-FOUND TESTING WAS PERFORMED ON 6/8/2010. BOTH CASING WIRES AND PIPE WIRES READ THE SAME 1.033V. ON 6/23/2010 CREWS RETURNED TO DIG SITE WITH RAILROAD REPRESENTATIVE, SMUD, AND LOCATERS FOR UNDERGROUND UTILITIES. THIS SITE HAS A LOT OF OVERHEAD AND UNDERGROUND INTERFERENCE. ; WEST EDGE CASING SHOWED CASING WAS FILLED WITH WAX. MIKE WEST WAS NOTIFIED ON 6/23/2010 AND CAME TO SITE. MIKE INSTRUCTED MEARS TO DIG OUT BOTH ENDS OF CASING, REMOVE EXISTING SEALS TO EXAMINE WAX AND PIN BRAZE MONITORING ELECTRODES FOR PROFILE TECHNOLIGIES TESTING TO BE PERFORMED. NO BELL HOLE INSPECTION IS TO BE DONE PER MIKE WEST. ; POST EXCAVATION, DOUBLE EXISTING RUBBER END CASING SEALS WERE INTACT. PLASTIC WEDGES AT 5 O'CLOCK AND 7 O'CLOCK POSITION WERE FOUND BETWEEN THE GALVANIZED CORRUGATED STEEL CASING AND THE PIPE. THE CASING WAS WAX FILLED. THE COATING WAS BOTH PLASTIC AND WAX TAPE. AN ANGLE POINT WAS EXPOSED WITHIN THE DITCH AREA. ; ON 6/28/2010 INSTALLATION OF MONITORING ELECTRODES FOR PROFILE TECHNOLOGIES WERE INSTALLED. ALL CASING PROCEDURES WERE PERFORMED THROUGHOUT. READS ON ETS WIRES AND DIRECT WERE SAME P/S & C/S. PG&E INSPECTOR WAS NOTIFIED. NEW TRENTON WAX END SEALS WERE PUT ON AND SITE WAS BACKFILLED WITH NATIVE SOIL. ORIGINAL ETS WIRES WERE USED AS WELL AS THE EXISTING VENT PIPE WITH AN ADDITIONAL PIECE ADDED. MONITORING ELECTRODE WIRES WERE PULLED UP WITH THE ETS WIRES AND INSTALLED INTO A G-5 CRISTY BOX FOR FUTURE MONITORING. READS ON P/S & C/S REMAINED THE SAME.
|  | 108 | 0.1672 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | SACRAMETO | DIV.: SACRAMENTO; DFM 0609-03; MP 0.1672; ; DIG ON EAST SIDE OF CASSING; LINE 108 SEGMENT 103C ROUGHT 0609-03; MP 0.1690; FLORIN RD. SACRAMENTO.; ; MISC. COMMENTS/INFORMATION: THIS SECTION OF CASING IS 63' LONG AND ONCE THE EDGES WERE DUG UP, IT WAS FOUND TO HAVE BEEN PREVIOUSLY WAXED. THE EAST EDGE HAD NO VISIBLE CASING VENT OR TEST LEADS, BUT DURING EXCAVATION BURIED TEST LEADS AND A CASING VENT ATTACHED AT THE 6:00 POSITION FOUND. ALSO, FOREIGN LINE CROSSINGS WERE PRESENT: TWO USA MARKED ELECTRICAL CONDUITS AND SEVERAL UNMARKED RAILROAD CONTROL CABLES. THE RAILROAD CONTROL CABLES WERE SPLIT OPEN DURING EXCAVATION AND AN IMMEDIATE REPAIR WAS MADE ON 6/25/10. MIKE WEST INSTRUCTED NOT TO REMOVE ANY CASING OR COATING AND THAT NO DE INSPECTION WAS REQUIRED SINCE THE CASING WAS ALREADY WAXED AFTER HE CAME TO EXAMINE THE SITE ON 6/23/10. HE ALSO INSTRUCTED THAT A MONITORING SYSTEM BE PUT IN PLACE, SO PROFILE TECHNOLOGIES CAME OUT ON 6/28/10 TO PIN-BRAZE SEVERAL ELECTRODES AND TAKE MONITOR READINGS. THE EDGE OF THE CASING WAS THEN SEALED WITH A TRENTON WAX END SEAL AND HELD IN PLACE BY TWO METAL BANDS ON 6/29/10. AN ETS AND NEW CASING VENT WERE INSTALLED IN THE SITE WAS BACKFILLED ON 6/30/10.
|  | 220 | 0.0075 | 3.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | DIXON | DIV.: SACRAMENTO; LINE 0600-01; MP 0.0074.; DIXON; LINE 220 STA. 0+31; MP 0.0075; LATIT. 38 28 02.02567, LONG. -121 48 13.99038; PEDRICK. RD. & VAUGHN RD.;; ; MISC. COMMENTS/INFORMATION: THIS SITE IS LOCATED AT THE NORTHEAST CORNER OF PEDRICK RD. AND VAUGHN RD. IN DIXON, CA. IN THE WESTBOUND TRAFFICE LANE. IT IS IN ASPHALT. ; TRAFFIC CONTROL WAS USED FROM BAY AREA TRAFFIC SOLUTIONS. ASPHALT WAS SAW CUT AROUND DITCH AREA. DURING EXCAVATION AN UNKNOWN FLX (UNMARKED) WAS DISCOVERED WITHIN DITCH AREA AT 5' 2.5 DEPTH. EXISTING COATING WAS WELL ADHERED TO PIPE. NO CORROSION FOUND UPON INSPECTION. NEW ETS WIRES WERE CAD WELDED AT THE D/S EDGE.; PIPE WAS RECOATED WITH PROTAL 7200 AND WAX TAPED ON EDGES TO IMPEDE TRANSITION. NATIVE SOIL WAS RETAINED AND USED AROUND INSTALLATION OF ETS. REFERENCE CELL WAS PLACED STREAMLINE AT THE D/S EDGE. COUPON ETS WAS INSTALLED IN G-5 CRISTY BOX AT D/S EDGE. SITE WAS BACKFILLED WTIH IMPORTED SAND AND BASE ROCK. SOIL COMPACTION WAS PERFORMED. ASPHALT WAS LAID.
|  | 108 | 0.1564 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | SACRAMENTO | (1) WEST SIDE OF ... 0609-03 M.P. 0.1564.; LINE 108 SEGMENT 103C ROUGHT 0609-03; MP 0.1538; LATIT. 38 29 45.55118, LONG. -121 28 14.88201; FLORIN RD SACRAMENTO.; ; MISC. COMMENTS/ INFORMATION: THIS SITE IS LOCATED OFF OF FLORIN ROAD NEAR THE RAILROAD TRACKS IN SACRAMENTO, CA. THE NEAREST CROSSROADS ARE FLORIN ROAD AND INDIAN LN. THE SITE IS ON THE WEST EDGE OF THE CASING CROSSING THE TRACKS. AN COUPON ETS WITH BOTH PIPE AND CASING WIRES AND A CUT OFF PIECE OF A CASING VENT WERE AT LOCATION UPON ARRIVAL. INITIAL AS-FOUND TESTING WAS PERFORMED ON 6/8/2010. BOTH CASING WIRES AND PIPE WIRES READ THE SAME 1.033V. ON 6/23/2010 CREWS RETURNED TO DIG SITE WITH RAILROAD REPRESENTATIVE, SMUD, AND LOCATERS FOR UNDERGROUND UTILITIES. THIS SITE HAS A LOT OF OVERHEAD AND UNDERGROUND INTERFERENCE. ; WEST EDGE CASING SHOWED CASING WAS FILLED WITH WAX. MIKE WEST WAS NOTIFIED ON 6/23/2010 AND CAME TO SITE. MIKE INSTRUCTED MEARS TO DIG OUT BOTH ENDS OF CASING, REMOVE EXISTING SEALS TO EXAMINE WAX AND PIN BRAZE MONITORING ELECTRODES FOR PROFILE TECHNOLIGIES TESTING TO BE PERFORMED. NO BELL HOLE INSPECTION IS TO BE DONE PER MIKE WEST. ; POST EXCAVATION, DOUBLE EXISTING RUBBER END CASING SEALS WERE INTACT. PLASTIC WEDGES AT 5 O'CLOCK AND 7 O'CLOCK POSITION WERE FOUND BETWEEN THE GALVANIZED CORRUGATED STEEL CASING AND THE PIPE. THE CASING WAS WAX FILLED. THE COATING WAS BOTH PLASTIC AND WAX TAPE. AN ANGLE POINT WAS EXPOSED WITHIN THE DITCH AREA. ; ON 6/28/2010 INSTALLATION OF MONITORING ELECTRODES FOR PROFILE TECHNOGLIES WERE INSTALLED. ALL CASING PROCEDURES WERE PERFORMED THROUGHOUT. READS ON ETS WIRES AND DIRECT WERE SAME P/S & C/S. PG&E INSPECTOR WAS NOTIFIED. NEW TRENTON WAS END SEALS WERE PUT ON AND SITE WAS BACKFILLED WITH NATIVE SOIL. ORIGINAL ETS WIRES WERE USED AS WELL AS THE EXISTING VENT PIPE WITH AN ADDITIONAL PIECE ADDED. MONITORING ELECTRODE WIRES WERE PULLED UP WITH THE ETS WIRES AND INSTALLED INTO A G-5 CRISTY BOX FOR FUTURE MONITORING. READS ON P/S AND C/S REMAINED THE SAME.
|  | 108 | 0.169 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | SACRAMENTO | (I) EAST SIDE OF CASING O... M.P. 0.1673.; ; DIG ON EAST SIDE OF CASSING; LINE 108 SEGMENT 103C ROUGHT 0609-03; MP 0.1690; FLORIN RD SACRAMENTO.; ; MISC. COMMENTS/INFORMATION: THIS SECTION OF CASING IS 63' LONG AND ONCE THE EDGES WERE DUG UP, IT WAS FOUND TO HAVE BEEN PREVIOUSLY WAXED. THE EAST EDGE HAD NO VISIBLE CASING VENT OR TEST LEADS, BUT DURING EXCAVATION BURIED TEST LEADS AND A CASING VENT ATTACHED AT THE 6:00 POSITION WERE FOUND. ALSO, FOREIGN LINE CROSSINGS WERE PRESENT: TWO USA MARKED ELECTROCAL CONDUITS AND SEVERAL UNMARKED RAILROAD CONTROL CABLES. THE RAILROAD CONTROL CABLES WERE SPLIT OPEN DURING EXCAVATION AND AN IMMEDIATE REPAIR WAS MADE 6/25/10. MIKE WEST INSTRUCTED NOT TO REMOVE ANY CASING OR COATING AND THAT NO DE INSPECTION WAS REQUIRED SINCE THE CASING WAS ALREADY WAXED AFTER HE CAME TO EXAMINE THE SITE ON 6/23/10. HE ALSO INSTRUCTED THAT A MONITORING SYSTEM BE PUT IN PLACE , SO PROFILE TECHNOLOGIES CAME OUT ON 6/28/10 TO PIN-BRAZE SEVERAL ELECTRODES AND TAKE MONITOR READINGS. THE EDGE OF THE CASING WAS THEN SEALED WITH A TRENTON WAX END SEAL AND HELD IN PLACE BY TWO METAL BANDS ON 6/29/10. AN ETS AND NEW CASING VENT WERE INSTALLED AND THE SITE WAS BACKFILLED ON 6/30/10.
|  |  | 0 | 2 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ROUTE: DF 1031; COPY 0601-01; PM 30604318; MP:0.00.; PM 30604318; PAGE 1-B; FAXED. ; PM 30604318; PAGE 2-B; FAXED.; CUT & CAPPED FOUR 2'' VALVES WELDED TO LINE 36''-400 & REMOVED VALVES 4.2.1&3 ALSO DEACTIVATED 2'' PIPE BETWEEN THESE VALVES & ABANDONED REG. SET.
|  |  | 0.0941 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM 3060 4318; ROUTE: 0601-01; MP: 0.0941; COPY.; PM 30604318; PAGE 1-A; FAXED;; PM 30604318; PAGE 2-A; FAXED;; CUT & CAPPED 6''-0601-01 DEACTIVATING OLD VACA-DIXEN REG SET 2'-2'' NORTH OF 6'' PCF & ISNTALLED PIPE LINE MARKER ABOVE PCF.
|  | 0600-03 | 1.8508 | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | DIXON | 30604322; DFM 0600-03; MP 1.8508; ; NEW SECTION OF PIPE .280 WALL 6.6250. D API GR-B SMLS.; INSTALLED 2-6'' PCF'S (MEULLER) 2-2'' SVC. STOP TEES FOR BYPAST + 2-SAV-A-VALVES 1''. REMOVED VALVE-V-15.72 AND 6'' DRESSER. INSTALLED 154'' OF TESTED 6'' SH. PIPE.
|  |  | 6.97 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | SACRAMENTO | # 41089757; RT 06119- OCT; MP 6.97;; WE BROUGHT UP THE DESIGN FROM 8 1/2' TO 6 1/2. THE STORM BOTTOM IS AT 4'6''. NO NEED TO BE AT 8'6''.;
|  |  | 1.7463 | 4.5 | Transmission | [6 empty] | 2008-07-28 |  |  |  | Steel/Wrought Iron |  | SACRAMENTO | DIVISION" SACRAMENTO; 30635910-08; SRO.RTE.DFM 0609-02, MP 1.7463; DREG 4047; MP 0.0012.; REPLACE NON-OPERABLE VALVE.
|  |  | 2.627 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | # 30649331; RT: 0618-03; MP: 2.627;;
|  |  | 0.0142 | 4 | Single Service | [6 empty] | 2010-06-12 |  |  |  | Steel/Wrought Iron |  | SACRAMENTO | PM # 30758581; ROUTE DCUST 10739; MP 0.0142; SOURE RT: 0613-02; SAC. DIV.
|  |  | 0.0044 | 4.5 | Transmission | [6 empty] | 2008-08-01 |  |  |  | Steel/Wrought Iron |  | SACRAMENTO | DEACTIVATED DCUST 0657; SOURE RT 0613.02; MP 0.0044; PM # 30618530; SAC DIV.; INSTALLED SEPARATOR AND 3 SPOOLS;
|  |  | 0.0215 | 6 | Transmission | [6 empty] | 2010-07-24 |  |  |  | Steel/Wrought Iron |  | SACRAMENTO | SACRAMENTO DIV.; RT= 0614-24; MP = 0.0215; PM# 30733858; ; EASTERN AVE/MARCONI AVE "INTERSECTION"; ; WE CUT OUT EXISTING SIX INCH VALVE, AND REPLACED WITH A STRAIGHT PIECE OF 6'' PIPE. PUT A SAVER VALVE ON 6'' TO PURGE REMAINING GAS OUT OF LINE AND TO USE A AIR MOVER ON. SO WE COULD PUT 10'' VALVE IN. ; TESTED PIPE. SOAP TESTED WELDS WHEN INSTALLED.
|  |  | 0.0009 | 10 | Transmission | [6 empty] | 2010-07-24 |  |  |  | Steel/Wrought Iron |  | SACRAMENTO | RT = 0614-24; MP - 0.0009; PM # 30733858; ; EASTERN/MARCONE AVE W/SIDE EASTERN;; WE EXPRESSED 15' OF EXISTING 10''. SOUTH OF THE VAULT. 18'' FROM EDGE OF VAULT TO CENTER OF 10'' MAIN. TOP IS 46'' DEEP. WE PUT A 10'' PCS ON THE 10''. SAVER. CUT 46'' OF 10'' OUT. PUT A 10'' VALVE IN PLACE OF MAIN. ; X-RAYED WELDS AND SOAP AT LINE PRESSURE.
|  |  | 0.2597 | 3 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | 0619-02/STUB10844; MP 0.2597; PM # 30692045; PM -30692045; PM - 30692045;; USED EXISTING 6'' MUELLAR TO PLUG AND CAP 3'' GAS MAIN AND ABANDED 1.404' OF 3'' GAS MAIN.
|  |  |  | 3 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | 0619-02/MP 0.0283; PM# 30692045; PM # 30692045; PM # 30692045.; INSTALLED 3'' - LINE STOPPER F.T.G. TO CUT AND CAP 3'' - AND ABANDONED 1,404' OF 3'' GAS MAIN.
|  |  |  | 4 | Single Service | [6 empty] | 2010-06-12 |  |  |  | Steel/Wrought Iron |  | SACRAMENTO | PM # 30858...; ROUTE DCUST 10739; MP 0.0142; SOURCE RT. = 061...; SAC. DIV. ; INSTALL SEPERATOR AND 3 SPOOLS.
|  |  | 0.0004 | 4.5 | Transmission | [6 empty] | 2008-08-01 |  |  |  | Steel/Wrought Iron |  | SACRAMENTO | DEACTIVATED DCST 8657; MP - 0.0044; PM # 3061853; SAC. DIV.
|  |  | 5.74 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO # 7039965-03; RT = 1501-02; MP - 5.74;
|  |  | 4.26 | 6 | [11 empty] | Steel/Wrought Iron |  | YUBA CITY | SO # 7039966; ROUTE 1501-02; MP 4.26
|  |  | 0.07 | 4 | [11 empty] | Steel/Wrought Iron |  | YUBA CITY | SO # 7034466; ROUTE: 1501-13; MP 0.07;
|  |  | 4.42 | 6 | [11 empty] | Steel/Wrought Iron |  | YUBA CITY | SO # 7039966; ROUTE 1501-02; MP 4.42;
|  |  | 0.0146 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO # 1055135; ROUTE 1519.04; MP= 0.0146
|  |  | 5.78 | 6.625 | Transmission | [7 empty] | 2002-04-08 | Other | SLEEVE | Steel/Wrought Iron |  |  | SO # 8052519-02; ROUTE 1501-02; MP - 5.78; P.5 OF 13; P.6 OF 13; SEE ATTACHED;
|  |  | 6.2584 | 6.625 | Transmission | [7 empty] | 2005-11-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  |  | REPAIRED GAUGE BY INSTALLING A 24" LONG SLEEVE; RT = 1509-05; MP - 6.2584; SO # 8074477; SUN SWEET PROPORT YURBA CITY WEST OF KOHLS DEPT. STORE.
|  |  | 6.48 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  | YUBA CITY | ROUTE 1509-05; MP 6.48; JOB 7038268; CALPINE YUBA CITY METER SET; INSPECTION LOCATION
|  |  | 0 | [12 empty] | Steel/Wrought Iron |  | YUBA CITY | SO # 7038131-01; ROUTE 1514-02; MP - 0.00; 4/11; 11/11
|  |  | 0 | [12 empty] | Steel/Wrought Iron |  | YUBA CITY | SO # 7038131-01; ROUTE 1514-02; MP - 0.00; 9/11; 11/11
|  |  | 6.67 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO # 7039965-03; RT = 1501-01; MP - 6.67
|  |  |  | 3.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO # 7039965-03; RT = DREG; SCRT = 1501-01; SCMP - 6.38
|  |  | 0 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO # 8062796-04; RT = 1508-01; MP - 0.00
|  |  | 7.3809 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO # 7046205; ROUTE 1511-01; MP 7.3809;
|  |  | 0.3342 | 6.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIV. SIERRA; L-1519-01; MP 0.3342; (TIE-IN FOR 12'' DFM 1519-04); SO # 7054566-05; 6'' BOTTOM TAP.
|  |  | 0.9758 | 6.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIV. SIERRA; L-1519-01; MP 0.9758; (SP. TIE-IN FOR 12'' DFM 0519-04); SO # 7054566-05; 6'' BOTTOM TAP.
|  |  | 0.0006 | 4.52 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO # 7046507-06; DREG 4563; MP 0.0006; SIERRA DIV.; INSTALLED PRESSURE TAP ONLY.
|  |  | 0.1165 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | ROCKLIN | SO # 7046507; DIV. SIERRA; DREG 4563; M.P. 0.1165; SO # 7046507-0
|  | L-123 | 2.57 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  | LINCOLN | RT= 1523-01; M.P. 25833; JOB7060614-06
|  |  | 0.7798 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | NORTH TIE-IN LOCATION (NOBLE RD. SECTION) ORDER # 7059048; RT. 1502-11; M.P. 0.7798; JOB 7059048;
|  |  | 1.091 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SOUTH TIE-IN LOCATION (NOBLE RD. SECTION) ORDER # 7059048; RT. 1502-11 M.P. 1.0910 JOB 7059048;
|  |  | 1.38 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SOUTH TIE-IN LOCATION (WOODRUFF LN. SECTION) ORDER # 7059048; RT. 1502-11 M.P. 1.3800 JOB 7059048;
|  |  | 1.6815 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | NORTH TIE-IN LOCATION (WOODRUFF LN. SECTION) ORDER # 7059048; RT. 1502-11 M.P. 1.6815 JOB 7059048;
|  |  | 0.5 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | ROSEVILLE | SO # 7040025; RT=1518-01; M.P. - 1.13
|  |  | 0.0057 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  | ROSEVILLE | SO # 7040025; ROUTE # 1518-01; MP 0.0057;
|  |  | 0.1625 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  | ROSEVILLE | SO # 7040025; ROUTE # 1518-01; M.P. 0.1625;
|  |  | 0.4181 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  | ROSEVILLE | SO # 7040025; ROUTE 1518-01; MP 0.4181;
|  |  | 0.5892 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  | ROSEVILLE | SO # 7040025; ROUTE 1518-01; M.P. 0.5892;
|  |  | 0.6971 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  | ROSEVILLE | SO # 7040025; ROUTE = 1518-01; M.P. 0.6971;
|  |  | 0.7917 | 4.50; 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  | ROSEVILLE | SO # 7040025; ROUTE 1518-01; M.P. 0.7917;
|  |  | 0.852 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | ROSEVILLE | SO # 7040025; ROUTE 1518-01; MP 0.8520
|  |  | 0.9159 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | ROSEVILLE | SO # 7040025; ROUTE 1518-01; MP 0.9159;
|  |  | 1.0331 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | ROSEVILLE | SO # 7040025; ROUTE 1518-01; MP 1.0331
|  |  | 1.1974 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | ROSEVILLE | SO # 7040025; ROUTE 1518-01; MP 1.1974
|  |  | 1.2897 | 4.5 | Transmission | [12 empty] | ROSEVILLE | SO # 7040025; ROUTE 1518-01; MP 1.2897;
|  |  | 1.5703 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | ROSEVILLE | SO # 7040025; ROUTE 1518-01; MP 1.5703.
|  |  | 0.7894 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 1512-01 M.P. 0.7894; P.M. 30604040
|  |  | 3.9 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 050A MP 3.90; PM # 30604040;
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM # 30604384; RT=1519....; MP - 2...294;; FRONT OF ADDRESS 5000 ROCKLIN RD. OR SIERRA COLLEGE
|  |  | 0.0562 | 6.625 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | PM 30604212; ROUTE: DSBN 9968; MP - 0.0562; SIERRA DIV.
|  |  | 8.8773 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 30604157; RT = 1501-01; MP - 8.8773;; INSTALLED 6'' PCF TO REROUTE; EXISTING 4'' TO BE C/OFF AND RETIRED TO MAKE ROOM FOR REROUTE OFF HWY 133499.
|  | 121 | 0.5754 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | YUBA CITY | DIV. SIERRA; LINE 1509-01 MP 0.5752; ; LINE 121 STA. 7+67;; ROUGHT 1509-01; MP 0.5754; ; LATIT. 39 08 37.04858, LONG. -121 39 20.14108;; HARTER RD. YUBA CITY.; ; THE OLD TAPE COATING AT THIS SITE WAS IN GREAT SHAPE AND WELL ADHERED. UPON INSPECTION NO CORROSION WAS FOUND. THE PIPE WAS RECOATED WITH PROTAL 7200 AND THE EDGES WERE TAPED TO IMPEDE THE TRANSITION OF THE OLD TAPE COATING TO THE NEWLY APPLIED PROTAL 7200.
|  | 131 | 1.8885 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | DUBLIN | RT: 2408-11 MP: 1.8885; 2/19/10; ; LINE 131 STA. 1+04;; ROUGHT 2408-11;; MP 1.8885; ; DOUGHERTY RD. DUBLIN
|  | 131 | 1.8762 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | DUBLIN | RT: 2408-11; M.P.: 1.8762; 2/19/10;; LINE 131 STRA. 0+38; ; ROUGHT 2408-11; ; MP 1.8762; ; DOUGHERTY RD. DUBLIN.;
|  |  | 0.0014 | 3.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ROUTE 2405-01; MP 0.0014
|  |  | 0.0654 | 4.5 | Transmission | [13 empty] | JOB: GM=7049027-04;; ROUTE: RTE=2405-01;; MILE POINT: MP=0.0654;; ;
|  |  | 0.0399 | 4.5 | Transmission | DFM | [12 empty] | JOB: GM=7049027-04;; ROUTE: RTE=2405-01;; MILE POINT: MP=0.0399
|  |  | 4.97 | [12 empty] | Steel/Wrought Iron |  |  | SO # 7045291-03; ROUTE # 2508-05; MP 4.97
|  |  | 0.96 | [12 empty] | Steel/Wrought Iron |  |  | SO # 8050796-02; RT = 2408-11; MP - 0.96; MISSION DIV.
|  |  | 3.57 | [12 empty] | Steel/Wrought Iron |  |  | SO # 7043785-02; APROX LOC 2408-11; MP 3.57
|  |  | 5.18 | [12 empty] | Steel/Wrought Iron |  | SAN RAMON | SO # 7044352-03; RT=2408-11; MP - 5.18; ; 6.625''; WT 0.156; MP 5.18 SAN RAMON BLACKHAWK
|  |  | 7.37 | [12 empty] | Steel/Wrought Iron |  | SAN RAMON | SO # 7044352-03; RT = 2408-11; MP - 7.37; 6.625'' WT 0.156; MP 7.37 SAN RAMON BLACKHAWK
|  |  | 7.5 | 6.63 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIV.: MISSION; SO # 7055509-05 (SOUTH TIE IN); DFM 2408-11; MP 7.5000
|  |  | 7.5586 | 6.63 | Transmission | DFM | [9 empty] | Steel/Wrought Iron |  |  | DIV: MISSION; SO # 7055509-05 (NORTH TIE IN); DFM 2408-11; MP 7.5586; BOLLINGER CANYON RD
|  |  | 0.4981 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO # 40889349; ROUTE = 2408.05; MP = 0.4981;; GENERAL INSPECTION IN CONNECTION W/ JOB 40889349 FULL CASING W/ GEL.
|  |  | 0.0053 | 3.5 | Transmission | [10 empty] | Steel/Wrought Iron | N; |  | SO # 30632238; ROUTE = DREG 4281; MP 0.0053; GENERAL INSPECTION ONLY - IN CONNECTION WITH RELOCATION WORK ON PM 30632238
|  |  | 0.0706 | 3.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO # 30632238; ROUTE = DREG 4281; MP: 0.0706; INSPECTION ONLY - IN CONNECTION WITH RELOCATION WORK ON 30632258
| 06-42475-1 | 2408-05 | 8.53 | 8.63 | Transmission |  | Body of Pipe |  |  |  |  | 2006-11-20 | 2006-11-21 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | DUBLIN | DIANNA OLSEN; RT = 2408-05; MP - 8.53
| 07-62717-1 | 2408-05 | 10.06 | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2007-04-26 | 2007-04-26 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | PLEASANTON | TIM SSCHEELE (925) 324-8662; 7065505; RT = 2408-05; MP = 10.0603; ; PLIDCO MECHANICAL CLAMP WAS INSTALLED TO MAKE REPAIR.
|  |  |  | 12 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2000-10-10 | 2000-10-10 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | DUBLIN | JOB # SO# 8039243; ROUTE # 2408-05; P.6 OF 6.; WELDED SLEEVE OVER CORROSION PIT
|  |  | 2.3834 | 12 | [7 empty] | 2007-02-08 |  |  |  | Steel-Other |  | SAN RAMON | RT = 2408-17; MP = 2.3834; PM #30509670 NEW GAS SERVICE JOB; G.C. CREW INSTALLED 12" MUELLER LINE STOPPER CREW ENCOUNTERED PROBLEMS WHILE DRILLING OUT NEW SERVICE TEE AND HAD TO ISOLATE SECTION OF 12" DFM TO REMOVE MUELLER DRILLING EQUIPMENT
|  |  | 0.11 | 8.63 | Transmission | [13 empty] | MISSION DIVISION; ROUTE = DSPF 3530; MP 0.1100
|  |  |  | 8.63 | Transmission
|  |  | 0.0266 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  | 0.2076 | 6.625 | Transmission | DFM | [12 empty] | RT = DREG 4868; MP - 0.2076; SO # 7051407-04; SCRT = 105N; DIV = MISSION.
|  |  | 3.3476 | 12 | [11 empty] | Steel-Other |  |  | SO # 7048006-04; RT = 2403-12; MP - 3.3426;
|  |  | 1.5535 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | (BURBANK PB''ST); DIV. MISSION; DFM 2402-01, MP 1.5535; SO # 7053325-06.
|  |  | 1.822 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | (MYRTLE & "C" ST); DIV.: MISSION; DFM 2402-01, MP 1.8220; SO # 7053325-06
|  |  | 1.63 |  | Transmission |  | Other |  | RELOCATE | Other | RELOCATE |  |  | Other | OFF-SET |  |  | HAYWARD | MISSION DIV.; DFM 2402-01; MP 1.63; SO # 8051516-02; NO LEAK! RELOCATE FOR CITY OF HAYWARD.
|  |  | 6.79 | 6 | [11 empty] | Steel-Other |  | FREMONT | MISSION DIV.; RT 2403-01; SEG. 192; MP - 6.79
|  |  | 6.23 | 8 | [11 empty] | Steel-Other |  | FREMONT | MISSION DIV.; RT. 2403-01; SEG 179.2; MP. 6.23
|  |  |  | 8 | [11 empty] | Steel-Other |  |  | SO # 6043325-01; ROUTE 2408-14
|  |  | 0.02 | 3 | [11 empty] | Steel/Wrought Iron |  |  | SO # 7036157-03; SRCMP = 42.38; SRCRT = 131; RT = DFDS LINE # 2407-01; MP - 0.02
|  | 2407-01 | 0.02 | 4 | [11 empty] | Steel/Wrought Iron |  |  | SO # 7036151-03; SRCRT 131; SRCMP 42.38; RT = DFDS, MP - 0.02; LINE # 2407-01.
| 01-42441-1 | BLACKHAW |  | 6 | Transmission |  | Body of Pipe |  |  | Digin |  | 2001-07-09 | 2001-07-09 | Deactivate #TP Main |  | Steel/Wrought Iron |  | SAN RAMON | ISOLATED SECTION OF MAIN/BLOW DOWN
| 03-42413-1 | 0 | 1.49 | 4 | Transmission |  | Body of Pipe |  |  | Digin |  | 2003-05-29 | 2003-05-29 | Replace TP Main |  | Steel/Wrought Iron |  | PLEASANTON | SO # 8058697-03; RT = GCUST 5896; SCRT = 2408-01; SCMP = 1.4900; PG 12 OF 12; REPLACED 9' OF 4'' STEEL
|  |  | 0.1322 | [12 empty] | Steel/Wrought Iron |  |  | SO # 7041909-03; SCRT = 42408-01; W.T. 0.141; GCUST 5896; M.P. 0.1322;
|  |  | 0.102 | [12 empty] | Steel/Wrought Iron |  |  | SO # 7047909-03; 4''; SCRT = 2408-01; W.T. 0.141; GCUST 5896; MP 0.1020
|  |  | 0.1255 | 8.63 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM # 30664032; ROUTE 2403-01; MP 0.1255.; GENERAL INSPECTION IN CONNECTION W/ DFM REPL. SMITH ST. @ UNION CITY BLVD., U.C. PM 30664032; JR (JERA)
|  |  | 0.1099 | 8.63 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM # 30664032; ROUTE 2403-01; MP. 0.1099.; GENERAL INSPECTION IN CONNECTION W/ DFM REPL. SMITH ST. @ UNION CITY BLDV. UNION CITY. PM 30664032. JR. JERA.
|  | 2408-11 | 3.00-3.57 | [15 empty] | DIVISION: MISSION; PM: 30654660; DFM: 2408-11; MP: 3.00-3.57.; CONCRETE CAP OVER PIPELINE; SEE ATTACHED MAP, PHOTO; T.S...LL.
|  |  | 3.57 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIVISION: MISSION; PM: 30654660; DFM: 2408-11; MP: 3.57.; INSPECTION ONLY IN CONNECTION W/ WORK PERFORMED ON PM 30654660.
| 08-62709-1 |  | 6.5414 | 6 | Distribution Main |  | Valves |  |  | Other |  | 2008-04-10 | 2009-09-24 | Other |  | Steel/Wrought Iron |  | PLEASANTON | ROUTE 2408-05; MP 6.5414; DREG 53.14; PM # 40893580; MP 0.0005; ON VALVE FRAME & COVER HWY 580 & SCARLE...; GREASED VALVE; SOAP RESTED VALVE D-06
|  |  | 2.8706 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM # 30674644; ROUTE 2403-12; MP 2.8706
|  |  | 2.8706 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM # 30674644; ROUTE: 2403-12; MP 2.8706.; GENERAL INSPECTION IN CONNECTION W/ WORK ON PM 30674644.
|  |  | 0.0015 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIVISION: MISSION; 30672124-10; STUB 10562; MP 0.0015; SRC RTE 2408-04; SRC MP 2.7725.; GENERAL INSPECTION IN CONNECTION W/ WORK ON PM 30672124 C/O EXIST REG STA. + MOVE TO FRANCISCO & SANTA RITA. JR.
|  |  | 2.1029 | 8.63 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIVISION: MISSION; 30672124-10; DFM 2408-04; MP 2.1029.
|  |  | 5..44 | 6.63 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIVISION: MISSION; PM 30672057-09; DFM 2403-01; MP 5.44.; GENERAL INSPECTION IN CONNECTION W/ WORK ON PM 30672057.
|  |  | 1.6176 | 6.62 | Service | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | DIVISION: DIABLO; 30687158-10; DFM 3012-01; MP 1.6176; (DOW CHEMICAL).; ; DFM 3012; SERVICE LINE TO DOW CHEMICAL PLAN + GAS METER SET; PITTSBURG; CONTRA COSTA COUNTY.
| 03-26125-1 | 3017-01 | 5.64 | 8 | Transmission |  | Body of Pipe |  |  | Other |  | 2006-08-06 | 2008-12-13 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | DANVILLE | 165' SOUTH OF EL ALAMO CT. DANVILLE; AS-BUILT FOR 41021306; L-3017-01; M.P. 5164; USED WELDED HIGH PRESSURE CLAMP, PLIDICO CLAMP, OVER 1.2 APPARENT MANUFACTURE FLAW CRACK
| 10-43057- | 3017-01 | 7.52 | 8.625 | Transmission |  | Body of Pipe | Other | 1/2'' NIPPLE ON 8'' MAIN | External Corrosion |  | 2009-11-09 | 2009-11-17 | Other | REMOVED CORODED PIPE NIPPLE AND REPLACED WITH NEW. | Steel/Wrought Iron |  | DANVILLE | AS- BUILT; RT = 3017-01; MP - 7.52.; CUT OFF CORRODED NIPPLE THAT WAS WELDED DIRECTLY TO MAIN. WELDED ON NEW THRED-O-LET AND INSTALLED NEW NIPPLE AND VALVE (3/4''). PIPELINE AT 0 PSIG DURING INSTALL.
|  |  | 5.47 | 8.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | PLEASANT HILL | DFM 3006-01; MP - 5.47.
|  |  | 5.06 | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | PLEASANT HILL | DIABLO DIVISION; L-3006-01; MP 5.06; JOB 7039818;
|  |  | 0.0807 | 3 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | (SRC, RTE - L-114; M.P. 12.5439); 7051412-04; DFM 3021-01; M.P. 0.0807; DIV: DIABLO (DDIA)
|  |  | 0.0021 | 3.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | DISCOVERY BAY | RT = 3022-01; MP - 0.0021; INSPECTION AREA
|  |  | 0.4336 | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | MARTINEZ | SO # 8084540; ROUTE - 3006-01; MP 0.4336;
|  |  | 0.4642 | 6.25 | Transmission | [10 empty] | Steel/Wrought Iron |  | MARTINEZ | SO # 8084540; ROUTE 3006-01; MP - 0.4642
|  |  | 0.0032 | 2.37 | Transmission | [10 empty] | Steel/Wrought Iron |  | MARTINEZ | RT = 3003-02; MP = 0.0032; PM # 30604209.; INSPECTION AREA ONLY FOR 2'' B.T. FITTING LOCATION.
|  |  | 0.2653 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | MARTINEZ | RT = 3003-02; MP = 0.2653; PM # 30604209
|  | 0.9753 | 0.9753 | 34 | [11 empty] | Other | APISL. GR Z-52 | NEAR CITY OF ANTIOCH | DISTRICT: LOS MEDANOS; DFM 3009-01; MP 0.9753.; 34" STEEL PIPE T.P. 0.438" W.T. APISL GR X- SL, DSAW; INSPECTION ARC
|  |  | 0.9937 | 34 | [11 empty] | Other | APISL GR X-52 | NEAR CITY OF ANTIOCH | DISTRICT: NULL (MIRANT); FORGN10083, MP 0.9937; 20" STEEL PIPE T.P. 0.375" W.T. APISL G-B, SMLS
|  | 300 | 1.91 | 6.66 | Transmission | [10 empty] | Steel/Wrought Iron |  | LAFAYETTE | ROUTE: 3002-01; MP: 1.4630; ORDER # 30677709;; ; +- 1/8 MILE SOULE OF MOUNT DIABLO BLVD.; +- 1/2 MILE WEST O F RISA RD.; LAFAYETTE RESERVOIR; LAFAYETTE; CONTRA COSTA COUNTY; DFM 3002-1.
|  | 300 | 1.3838 | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | LAFAYETTE | ROUTE: 3002-01; M.P.: 1.3838; JOB: 30677709.; +- 1/8 MILE SOULE OF MOUNT DIABLO BLVD.; +- 5/8 MILE WEST O F RISA RD.; LAFAYETTE RESERVOIR; LAFAYETTE; CONTRA COSTA COUNTY; DFM 3002-1.
|  |  | 7.5228 | 8.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | DANVILLE | 3017-01; MP 7.5228; 30744841; 307448441;; DFM 3017 REPLACE DANVILLE #2; DR INLET FIRE VALVE V-88; FRONT ST. DANVILLE; CONTRA COSTA COUNTY.
|  |  | 0.0003 | 8.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | DANVILLE | STUB 10845; MP 0.0003; 30744941; 30744841.; DFM 3017 REPLACE DANVILLE #2; DR INLET FIRE VALVE V-88; FRONT ST. DANVILLE; CONTRA COSTA COUNTY.
|  |  | 0.0003 | 8.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | DANVILLE | STUB ...0847; MP 0.0003; 30744841.; DFM 3017 REPLACE DANVILLE #2; DR INLET FIRE VALVE V-88; FRONT ST. DANVILLE; CONTRA COSTA COUNTY.
|  |  | 0.98 | 8 | Gathering | [7 empty] | 2001-11-13 | Other | ... ; INSTALLED FINK WITH ... | Steel/Wrought Iron |  | BAKERSFIELD | DFM 6602-01; MP 0.98; KERN DIV.; SO # 7037309-01.; INSTALLED FINK WITH (2) ... 8" E.B. FEEDER
|  |  | 1.95 | 8 | Gathering | FEEDER | [6 empty] | 2001-11-13 |  |  | Steel/Wrought Iron |  | BAKERSFIELD | DFM 6602-01; MP 1.95; KERN DIV.; SO # 7037309-01; INSTALLED 2 #12 LOCATING WIRES ON MAIN
|  |  | 3.6 | 8 | Transmission | [7 empty] | 2001-09-17 | Other | INSTALLED E.T.S. | Steel/Wrought Iron |  |  | DFM 6602-01; MP 3.60; KERN DIV.; SO # 7037309-01; INSTALLED (2) WIRE E.T.S.OFF OF E.B FEEDER; INSTALL NEW ETS.;
|  |  | 4.97 | 8 | Transmission | [7 empty] | 2001-09-07 | Other | INSTALLED E.T.S. | Steel/Wrought Iron |  | BAKERSFIELD | DFM 6602-01; MP 4.97; KERN DIV.; SO # 7037309-01.; INSTALLED (2) E.T.S. WIRES WITH G-5 BOX OFF OF E.B. FEEDER
|  |  | 5.46 | 4 | Transmission | [7 empty] | 2001-09-06 | Other | INSTALLED E.T.S. | Steel/Wrought Iron |  | BAKERSFIELD | DFM 6602-01; MP 5.46; KERN DIV.; SO # 7037309-01; INSTALLED G-S E.T.S. OFF OF E.B. FEEDER IN PIT.
|  |  | 7.86 | [15 empty] | RT = 6605-01; MP - 7.86; EDWARD AFB PRIMARY REG STATION; 082404.
| 09-40049-1 | DFM | 2.13 | 8 | Transmission |  | Girth Weld |  |  | Weld Failure |  | 2009-03-13 | 2009-03-15 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | RIDGECREST | DFM 6612-01; PM # 41074458; ROUTE = DREG 5496; MP = 2.13.; WELDS WERE INSPECTED BY KEVIN RAWLINS OF VALLEY INDUSTRIAL X-RAY.; WELDS WERE INSPECTED BY KEVIN RAWLINS OF VALLEY INDUSTRIAL X-RAY.
| 97-20500-1 | 4760F04 | 2.97 | 8 | Transmission |  | Girth Weld |  | PIN HOLE | Construction Defect |  | 2009-01-08 | 2009-01-10 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | RIDGECREST | DFM 6612-01; PM # 41074458; ROUTE DREG 5496; MP 2.95; 6 OF 12. ; REPAIRED W/ MECHANICAL H.P/ FITTING FLIDCO; 8''; SER # 8038205
|  | 148 | 12.0208 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | RT: 7221-10; MP: 12.0200.; LINE 148 STA. 20+55; ROUGHT 7221-10; MP 12.0208; LATI 37 42 14.55638 LONG -121 02 49.77557; BANGS AVE & DALER DR. MEDESTO
|  |  | 9.8478 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-10 M.P. 9.8478; JOB 8078738;
|  |  | 9.8863 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-10; M.P. 9.8863; JOB 8078138.
|  |  | 9.9365 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-10; M.P. 9.9365; JOB 8078738;
|  |  | 9.9909 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-10; M.P. 9.9909; JOB 8078738
|  |  | 10.1593 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-10; M.P. 10.1593; JOB 8078738.
|  |  | 10.1937 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 16'' 7221-10; M.P. 10.1937; JOB 8079738.
|  |  | 10.4329 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-10; M.P. 10.7329; JOB 8078738
|  |  | 10.6572 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-10; M.P. 10.6572; JOB 8078738
|  |  | 10.85 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-10; M.P. 10.8500; JOB 8078738.; 20' TOWARDS PROPERTY 3/4'' SERVICE 23'' DEPTH.
|  |  | 10.9979 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-10; M.P. 10.9979; JOB 8078738.
|  |  | 11.071 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-10; M.P. 11.0710; JOB 8078738
|  |  | 9.4847 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ROUTE = 7221-10; MP - 9.4847
|  |  | 11.2231 | 16 | [11 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-10; M.P. 11.2231; JOB 8078738
|  |  | 11.1545 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-10; M.P. 11.1545; JOB 8078738;
|  |  | 11.296 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-10; M.P. 11.2960; JOB 8078738.
|  |  | 11.2994 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-10; M.P. 11.2994; JOB 8078738
|  |  | 11.3714 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-10; M.P. 11.3714; JOB 8078738.
|  |  | 11.3888 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-10; M.P. 11.3888; JOB 8078738
|  |  | 11.3951 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-10; M.P. 11.3957; JOB 8078738.
|  |  | 11.3971 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-10; M.P. 11.3971; JOB 8078738.
|  |  | 11.8447 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | RT. 7221-10; M.P. 11.8447; JOB 7052911-05
|  |  | 11.8798 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | RT. 7221-10; M.P. 11.8798; JOB 7052911-05
|  |  | 12.0827 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | RT. 7221-10; M.P. 12.0827; JOB 7052911-05
|  |  | 11.4334 | 16 | [11 empty] | Steel/Wrought Iron |  | MODESTO | MP = 11.4334; RT. = 7221-10
|  |  | 10.0458 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-01; M.P. 10.0458; JOB 8078738
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 72211-01; M.P. 10.0980; JOB 8078738
|  |  | 10.1991 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-01; M.P. 10.1991; JOB 8078738
|  |  | 10.2616 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-01; M.P. 10.2616; JOB 8078738.; 1/2'' PT. GAS SERVICE ... OVER 16'' TP MAIN.
|  |  | 10.3219 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-01; M.P. 10.3219; JOB 8078738
|  |  | 10.3791 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-01; M.P. 10.3791; JOB 8078738. ; THE ...DEPTH DUE TO ...
|  |  | 10.435 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-01; M.P. 10.4350; JOB 8078738
|  |  | 10.4559 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-01; M.P. 10.4559; JOB 8078738.; NOT ABLE TO ... 20' TOWRDS PROPERTY W/OUT DIGGING UP THEIR YARD.
|  |  | 10.5363 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-01; M.P. 10.5363; JOB 8078738
|  |  | 10.598 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-01; M.P. 10.5980; JOB 8078738.; LONG SIDE SERVICE.
|  |  | 10.7082 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-01; M.P. 10.7082; JOB 80787338.; ... SERVICE ...
|  |  | 10.8063 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-01; M.P. 10.8063; JOB 8078738.; 3/4'' LONG SIDE SERVICE
|  |  | 11.2524 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 16'' 7221-01; M.P. 11.2524; JOB 8078738
|  |  | 11.8516 | 16 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | MODESTO | RT. 7221-01; M.P. 11.8516; JOB 7052911-05.
|  |  | 1.5672 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 3324 ORESTIMBA RD., NEWMAN; VALLEY SUNDRIED PRODUCTS; JOB # PM 30339647-04; ROUTE = 7220-01; MILE POINT = 1.5672.
|  |  | 12.2817 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | RT. 1615-01; M.P. 12.2817; JOB 7052911-05
|  |  | 12.2894 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | RT. 1615-01; M.P. 12.2894; JOB 7052911-05.
|  |  | 12.3474 |  | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | RT. 1615-01; M.P. 12.3474; JOB 7052911-05
|  |  | 2.2757 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | TUELOCK | DIVISION: YOSEMITE; SO# 7050110-05; DFM 7216-01; M.P. 2.2757.
|  |  | 9.4773 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | MADERA | RT. 7209-01; M.P. 9.4773; JOB 7053751; INST. 60 LB. ANODE WITH E.T.S. MARKER; INSTALLED 60LB ANODE WITH E.T.S. MARKER
|  |  | 9.5682 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | MADERA | INSTALLED.... ANODE WITH E.T.S. ....; RT. 7209-01; M.P. 9.5682; JOB 7053751.; INST. 60LB ANODE WITH E.T.S. MARKER; INST. 60 LB ANODE WITH E.T.S. MARKER
|  |  | 2.72 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | YOSEMITE DIV.; L-7211-01; MP - 2.72; INSPECTED PIPE 6" OR "B" ERW
[16 empty] | Steel/Wrought Iron |  | RIVERBANK | 2) YOSEMITE DIV.; ROUTE 7228-16; SEQ. 402
[16 empty] | Steel/Wrought Iron |  | RIVERBANK | 1) 7228-16-SEG ...; YOSEMITE DIV.; ROUTE 7228-16; SEQ. 402.
|  |  | 5.59 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 7228-16; MP 5.59; YOSEMITE DIV.
|  |  | 5.44 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 7228-11; M.P. 5.44; YOSEMITE DIV.
|  |  | 0 | 8 | [11 empty] | Steel/Wrought Iron |  |  | L-7228-35; MP 0.00; 8" STL; SEE ATTACHMENT "A"
|  |  | 9.29 | 6 | [14 empty] | L-7228-01; M.P. 9.29; 6" STL.; SEE ATTACHMENT "B"
|  | 108 | 0.36 |  |  |  | Girth Weld | [5 empty] | 2001-06-29 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  |  | SO# 8047876-01; ROUTHE 7228-36; MP 0.36; YOSEMITE DIV; ; REPLACED 10' SECTION OF 8" .188 W. T.
|  |  |  | 8.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | ... JOB 7030817.
|  |  |  | 8.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | JOB 7039817; SEE ATTACHED SHEET FOR LOCATION
|  |  | 3.41 | [12 empty] | Steel/Wrought Iron |  | RIVERBANK | SO # 7044525-02;; RT = 7228-01;; M.P. 3.41;
|  |  | 0 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | LIVINGSTON | SO# 7038570;; L-7202-01;; M.P. 0.00;
|  |  | 0.0463 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | PM# 30306177;; RT- 7224-15;; M.P. 0.0463;; iNST 6" SEE 300' B.T. MUELLER FOR TIE IN
|  |  | 0.079 | 8 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | MODESTO
|  |  | 0.6482 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | INST. TP WILLIAMS SIDE OUT FITTING FOR TIE IN 8" MAIN TO BE UPGRADED TO T.P. PRESSURE
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | UPGRADED FROM DIST. TO T.P.
|  |  | 1.2278 | 6 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  | 5.38 | 4.25 | Transmission | [7 empty] | 2003-06-24 | Replace TP Main | Welded Sleeve/Can | Steel/Wrought Iron |  | OAKDALE
|  |  | 1.62 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | LOS BANOS | POTHOLE #1
|  |  | 2.4 | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | LOS BANOS | POTHOLE #2
|  |  | 2.6 |  | Service | Transmission | [9 empty] | Steel/Wrought Iron |  | LOS BANOS | POTHOLE #3; CUT OFF & ABANDON H.P.R. AND SER. PER PAN PARTING TON 8-18-04 SER TEE ON MAIN VALVE TEE 1440
|  |  | 3.94 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | LOS BANOS | 4
|  | 300A | 404.35 | 0.75 | Service | Transmission | [9 empty] | Steel/Wrought Iron |  | LOS BANOS | POTHOLE #5; DUG UP TEE TO MAKE SURE IT WAS A 144 VALVE TEE. WRAP CAP & BACKFILL OK BOB D....
|  |  | 3.93 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | LOS BANOS | POTHOLE #8
|  |  | 5.2974 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | LOS BANOS | POTHOLE #11; INSPECTED MUELLER TO MAKE SURE IT WAS 300 SER. IT WAS CHECKED LID AREA ON MUELEER ON... BOBBY D....
|  |  | 0.3392 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  | ESCALON
|  |  | 0.3783 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  | ESCALON
|  |  | 0.5865 | [14 empty] | MERCED
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | INST. 3/4" SAV-A-VALVE FOR TIE-IN
|  |  | 0.6187 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | MERCED | REMOVE/ 8" VALVE ISNT. 2" CAN WT 188
|  |  | 1.6581 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | MERCED
|  |  | 2.1304 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | MERCED
|  |  | 4.54 & 4.59 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKDALE | C/O FOR SUBWAY AT LOCATION OF WILLOWOOD DR.
|  |  | 5.2674 & 5.0481 | 04.00 & 06.00 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKDALE | A/B CROSS TIE FROM 4" TO 6"
|  |  | 0.002 | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | MADERA
|  |  | 0.1087 | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | MADERA
|  |  | 0.8146 | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | MADERA
|  |  | 0.1197 | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | MADERA
|  |  | 1.4703 | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | MADERA
|  |  | 2.0359 | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | MADERA
|  |  | 2.7175 | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | MADERA
|  |  | 2.7335 | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | MADERA
|  |  | 0.1898 | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | MADERA
|  |  | 0.2005 | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | MADERA
|  |  | 0.2191 | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | MADERA
|  |  | 12.3273 & 0.0206 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | EXPOSED ONLY THE TOP TO GET DEPTH OF LINE
|  |  | 0 | [12 empty] | Steel/Wrought Iron |  | CERES | REPLACE 6" VALVE
|  |  | 3.8006 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | MODESTO | 8" T.P. STL. MAIN OUTSIDE
|  |  | 0.4759 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | PATTERSON
|  |  | 0.5358 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | PATTERSON
|  |  | 0.1069 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | PATTERSON
|  |  | 0.122 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | PATTERSON
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | PATTERSON
|  |  | 0.1955 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | PATTERSON
|  |  | 0.1384 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | LOS BANOS | 6" TO WILLIOM SIDE OUT; CUT OUT 3'
|  |  | 0.0771 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | LOS BANOS | 6" T.D. WILLIOM SIDE OUT
|  |  | 3.8241 | 4 | Transmission | [7 empty] | 2004-09-29 | Other | WRAP REPAIR |  |  | OAKDALE | 4" T.P. GAS MAIN 5" DEEP
|  |  |  | 4 | Transmission | [7 empty] | 2004-09-29 | Other | WRAP REPAIR |  |  | OAKDALE | 4" T.P. GAS MAIN 5" DEEP
|  |  | 4.1041 | 4 | Transmission | [8 empty] | Other | REPAIR WRAPE | Steel/Wrought Iron |  | OAKDALE | MAIN 16" DEEP
|  |  |  | 4 | Transmission | [8 empty] | Other | REPAIR WRAPE | Steel/Wrought Iron |  | OAKDALE | MAIN 16" DEEP
|  |  | 4.3074 | 4 | Transmission | [7 empty] | 2004-09-24 | Other | WRAPE REPAIR | Steel/Wrought Iron |  | OAKDALE | MAIN 21" DEEP
|  |  |  | 4 | Transmission | [7 empty] | 2004-09-24 | Other | WRAPE REPAIR | Steel/Wrought Iron |  | OAK DALE | MAIN 21" DEEP
|  |  | 4.5201 | 4 | Transmission |  |  |  |  | Damage by 3rd Party |  |  | 2004-09-21 | Other | WRAPE | Steel/Wrought Iron |  | OAKDALE
|  |  |  | 4 | Transmission |  |  |  |  | Damage by 3rd Party |  |  | 2004-09-21 | Other | WRAPE | Steel/Wrought Iron |  | OAKDALE
|  |  | 4.76 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIVERBANK | G.C. GAS, AS BUILT
|  | 148 | 9.4542 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | SALIDA | SALIDA, KLEMAN CT LINE 148 MP9.4542 LATIT 37, 42, 41.73299 , -121 05 03.3746 LONG
|  | 307 | 0.1249 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | MENDOTA | LINE 307 STA.9+54 ROUTE 7207-01 MP 0.1249 LAT. 36 33 56.92787 LONG. -120 23 00.02389 BELMONT AVE MENDOTA
|  |  | 0.0004 | 6 | Transmission | [10 empty] | Steel/Wrought Iron
| 08-35160 | 118 | 0.0271 & 0.00 | 4 | Transmission |  | Valves |  |  | Other |  | 2008-10-30 |  |  |  | Steel/Wrought Iron |  | LIVINGSTON | LEAK AT TRANS VALVE ON L. 118; REMOVED 4" VALVE, #9 @ L.V STATION, EXISTING FLANGE'S REMAIN. INSTD 11 3/4 FLANGED SPOOL, ETS WIRES INSTD ON SPOOL
| 10-21769 |  | 3.5795 | 10 | Transmission |  | Valves | Other | GASKETS | Other | CRACK GASKET | 2010-03-23 | 2010-03-29 | Other | REPLACE GASKETS 10" VALVE 2 4" VALVES | Steel/Wrought Iron |  |  | PULLED 10" VALVE & 2 4" VLVE REPLACED GASKET
|  |  | 0.59 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | MENDOTA | MENDOTA BELMONT AVE MP 0.59 LATT 36 44 56.98042 LONG 120 22 32.83628
|  |  | 0.63 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | MENDOTA | MENDOTA BELMONT AVE MP 0.63 LATT 36 44 56.97341 LONG 120 22 44.30162
|  | 8807-02 | 1.7314 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | SUNNYVALE | NOTE: NO LEAK, JOB SCOPE TO C/O EXISTING 10" DFM; CUT OFF EXISTING 10" DFM UNDER CAL-TRAIN R/R
|  | 8807-02 | 1.7757 | 10.75 | Transmission | DFM | [11 empty] | SUNNYVALE | NOTE: NO LEAK, JOB SCOPE TO C/O EXISTING DFM; CUT OFF EXISTING 10" DFM UNDER CAL-TRAIN R/R
|  | 8807-01 | 8.41 |  | Transmission | [10 empty] | Steel/Wrought Iron |  | SARATOGA
|  | 8805-03 | 6.24
|  |  |  | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | NO LEAK INSPECTION ONLY; SEE JOB SKETCH FROM A 7061810
|  |  | 0.0684 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | INSPECTION ONLY; SEE AS-BUILT FOR 7060406, SIERRA VISTA REG STATION REBUILD.
| 09-91389-1 | DREG4014 | 0.0232 | 3 | Transmission | DFM | Body of Pipe |  |  | External Corrosion |  | 2009-08-25 | 2009-09-29 | Replace TP Main |  | Steel/Wrought Iron |  | MARYSVILLE | REMOVED 62" 3" MAIN WITH NEW TESTS;; BAR HOLES MID STREET & CURB;
|  | 50 | 1.54 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | TIED IN NEW SEL. OF 8" MAIN W/ BTM TAP PCF EAST TIE IN HOLE SEE SHEET 2 OF 2 DETAIL 2 SEC A #7044648
|  | 50 | 1.57 | [15 empty] | WEST TIE IN HOLE CORNER OF BIZZ JOHNSON DR & 4TH ST. SEE DETAIL 1 ON SHEET 2 OF 2 7044648
|  | 50 | 1.54 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | TIED IN NEW SEC. OF 8" MAIN W/BTM TAP PCF EAST TIE IN HOLE SEE SHEET 2 OF 2 DETAIL 2 SEC B #7044648
|  | 50 | 1.57 | [15 empty] | WEST TIE IN HOLE. CORNER OF BIZZ JOHNSON DR & 14TH ST. SEE DETAIL 1 ON SHEET 2 OF 2 7044648
|  | 050B | 7.7775 | [12 empty] | Steel/Wrought Iron
| 09-60096-1 | 50 |  | 0.75 | Transmission |  | Other |  |  | Construction Defect |  | 2009-07-16 |  |  |  | Steel/Wrought Iron |  | GRIDLEY | IN FRT OF ADDRESS; SEE OLD LEAK # 09-60079-1; NO LEAKAGE FOUND DELETE
| 09-60079-1 | 50 |  | 0.75 | Transmission |  | Other |  |  | Construction Defect |  | 2009-06-16 | 2009-06-19 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | GRIDLEY | IN FRT OF ADDRESS; SEE NEW LEAK # 09-60096-1; SOAP TEST OK 1" VALVE TEE CAP LEAKING TIGHTENED CAP
| 09-60079-1 | [10 empty] | 2009-06-16 | [5 empty] | GRIDLEY | 1308 HWY 99, GRIDLEY REPAIRED ON 6/19/09; IN FRT OF ADDRESS
| 09-90176-1 |  | 17.2982 | [8 empty] | 2009-03-19 | [5 empty] | GRIDLEY | SVC TAP OFF MAIN; NO LEAKAGE FOUND DELETE
| 09-90175-1 | [10 empty] | 2009-03-19 | [5 empty] | GRIDLEY | SVC TAP OFF MAIN; SVC TEE AT MAIN
|  | 050A | 35.3722 |  | Transmission
|  | 050A | 36.7377 |  | Transmission
|  | 050A |  | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SEE ATTACHED
|  | 50 | 23.24 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PRIMARY CONTRACTOR: ROCKFORD CORPORATION - ROCKFORD WELDER FABRICATED TIE-IN PIECE; PG&E GC GAS DEPT.: INSTALLED/WELDED TIE-IN PIECE - SEE ATTACHED SKETCH FOR DETAILS.; PG&E LINE 50 HWY 99 RELOCATION, BIGGS, CALIF.
|  | 50 | 26.1942 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 8" NORTH TIE IN ON L-50, MP 26.1942; JOB # 30676701
|  | 050A | 26.73 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PG&E LINE-50 HWY 99 RELOCATION, BIGGS, CALIF.; PRIMARY CONTRACTOR - ROCKFORD CORPORATION - ROCKFORD WELDER FABRICATED TIE-IN PIECE AND INSTALLED PIECE TO BOTTOM OF 12" CON (703-K) OFF PCF-B/T.; PGE GC-GAS-INSTALLED PCF-B/T 30 WITH 12" CAN 703-K.; SEE ATTACHED FOR LOCATION AND DETAILS
| 09-60090-1 | 50A | 18.2589 | 0.75 | Transmission |  | Other |  | GREASE FITTING IN FIRE VALVE | Construction Defect |  | 2009-06-24 | 2009-12-17 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | GRIDLEY | SOURCE ROUTE = L50A MP 18.2589
| 10-00072- | 50 | 11.55 | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-14 | 2010-10-26 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | LIVE OAK | GAS OVER TRANSMISSION LINE 50' NORTH OF CORNER; FOUND CORROSION LEAK ON PIPE. PUT ON PLIDCO LEAK CLAMP, SOAP TESTED AT LINE PRESSURE AND BACKFILLED.
|  | 056B | 0.06 | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | LOC #10 4" LINE TP L-056B MP - 0.06 JOB # 7032489-00
|  | 56 | 0.09 | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | LOC #13 4" LINE TP 056C MP - 0.09 JOB # 7032489-00
|  | 56 | 0.13 | 8.62 | [11 empty] | Steel/Wrought Iron |  |  | LOC #9 8" LINE TP L-056B MP - 0.13 JOB # 7032489-00; NOTE 3" WATER LINE PVC IN SAME TRENCH AS 8" GAS 12" ABOVE AT THIS LOCATION IN NATIVE BACKFILL
|  | 56 | 0.19 | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | LOC #11 4" LINE TP L-056B JOB # 7032489-00 MP 0.19
|  | 56 | 0.19 | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | LOC #12 4" LINE TP L-056C JOB # 7032489-00 MP 0.19
|  | 206 | 0.22 | 12.75 | [11 empty] | Steel/Wrought Iron |  |  | LOC #15 12" LINE TP L-206 JOB # 7032489-00 MP 0.22
|  | 056B | 0.23 | 8.62 | [11 empty] | Steel/Wrought Iron |  |  | LOC #8 8" LINE TP L-056B JOB # 7032489-00 MP 0.23; NOTE: 3" PVC WATER LINE IN SAME TRENCH AS 8" GAS 12" ABOVE AT THIS LOCATION IN NATIVE BACKFILL
|  | 56 | 0.34 | 8.62 | [11 empty] | Steel/Wrought Iron |  |  | LOC #6 8" LINE TP L-056B JOB # 7032489-00 MP 0.34; NOTE: 3" PVC & WATER VALVE THIS LOCATION. PLV IN SAME TRENCH AS 8" MAIN DIRECTLY ON TOP 12" SEPERATION.
|  | 56 | 0.36 | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | LOC #7 4" LINE TP L-056 JOB # 7032489-00 MP 0.36
|  | 206 | 0.52 | 12.75 | [11 empty] | Steel/Wrought Iron |  |  | LOC #14 12" TP L-206 JOB # 7032489-00 MP 0.52; WRAP AND PIPE AT THIS LOCATION WERE IN EXCELLENT CONDITION PER VISUAL INSPECTION.
|  | 56 | 0.53 | 8.62 | [11 empty] | Steel/Wrought Iron |  |  | LOC #4 8" LINE TP L-056B JOB # 7032489-00 MP 0.53
|  | 056B | 0.54 | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | LOC #5 4" LINE TP L-056A JOB # 7032489-00 MP 0.54
|  | 56 | 0.6 | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | LOC #3 4" LINE TP L-056A JOB # 7032489-00 MP 0.60
|  | 56 | 0.6 | 8.62 | [11 empty] | Steel/Wrought Iron |  |  | LOC #2 8" LINE TP L-056A JOB # 7032489-00 MP 0.60
|  | 56 | 0.89 | 8.62 | [11 empty] | Steel/Wrought Iron |  |  | LOC #1 8" LINE TP L-056B JOB # 7032489-00 MP 0.89
|  | 56 |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | CONCORD | COMPRESSOR AREA PIPE INSPECTION 13-1" WEST OF V 509; COMPRESSOR AREA DRAWING 487484 LOS MEDANOS GAS STORAGE FACILITIES CONCORD; CONTRA COSTA COUNTY
|  | 56 |  | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | CONCORD | COMPRESSOR AREA PIPE INSPECTION 9'-2" WEST OF V508; COMPRESSOR AREA DRAWING 487484 LOS MEDANOS GAS STORAGE FACILITIES CONCORD; CONTRA COSTA COUNTY
|  | 56 |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | CONCORD | DEHYDRATION AREA PIPE INSPECTION BETWEEN V 600, 621 & 622; DEHYDRATION AREA DRAWING 487134 LOS MEDANOS GAS STORAGE FACILITIES CONCORD; CONTRA COSTA COUNTY
|  | 56 |  | 4.5 | [11 empty] | Steel/Wrought Iron |  | CONCORD | DEHYDRATOR AREA PIPE INSPECTION 18'-1" S/O V614; DEHYDRATOR AREA DRAWING 487134 LOS MEDANOS GAS STORAGE FACILITIES CONCORD: CONTRA COSTA COUNTY
|  |  |  | 2.37 | [11 empty] | Steel/Wrought Iron |  | CONCORD | COMPRESSOR AREA PIPE INSPECTION 6' - 4" NORTH OF V-D; COMPRESSOR AREA DRAWING 487484 LOS MEDANOS GAS STORAGE FACILITIES CONCORD; CONTRA COSTA COUNTY
|  | 57A | 13.78 | 18 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | ALINE 57A STATE HWY 4 X-ING SOUTH OF BALFOUR RJ. BRENTWOOD; CONTRA COSTA COUNTY
|  | 57A | 13.78 | 18 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | LINE 57A RAILROAD X-ING CONTRA COSTA COUNTY SOUTH OF BALFOUR RD. BRENTWOOD
|  | 57A | 16.58 | 18
|  |  | 0.1732 | 8.62 | Gathering | [10 empty] | Steel/Wrought Iron |  | MCDONALD ISLAND | WELL TO TURNERCUT STATION SAN JOAQUIN COUNTY; CONNECTED 2 #8 WIRE FOR NEW LEAD TO RECTIGIER #8 MCDONALD ISLAND.
|  | 057A | 0.1406 | [15 empty] | FOUND PIPE TO BE BARE EXCEPT SOME TRACE OF MASTIC COATING WHEN INSTALLING ETS 150' WEST OF MCDONALD #12 WELL
|  | 057A | 0.0011 | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | WHISKEY SLOUGH STATION | WHISKEY SLOUGH STATION MCDONALD ISLAND SAN JOAQUIN COUNTY
|  | 057A | 0.0025 | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | WHISKEY SLOUGH STATION
|  | 57B | 16.6 | 22
|  | 057B | 12.32 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | NOTE: INSTALLED LITTLE FINK ETS STATION 2 WIRE BLACK ON 1 1/4 CONDUIT POLE
|  | 57B | 13.78 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | LINE 57B RAILROAD & STATE HWY 4 CROSSING SOUTH BALFOUR RD.; BRENTWOOD; CONTRA COSTA COUNTY
|  | 057B | 12.32 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | NOTE: INSTALLED LITTLE FINK ETS STATION 2 WIRE BLACK ON 1 1/4" CONDUIT POLE
|  | 57B | 10.93 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | NOTE: INSTALLED LITTLE FINK ETS STATION 2 WIRE BLACK ON 1 1/4" CONDUIT POLE
|  | 057B | 12.32 | 22 | Transmission | [12 empty] | BRENTWOOD | NOTE: INSTALLED LITTLE FINK ETS STATION 2 WIRE BLACK ON 1 1/4" CONDUIT POLE
|  | 057B | 10
|  | 57B | 9.72 | [14 empty] | BRENTWOOD | 469' SOUTH OF ANGLE POINT. 2-20" CONCRETE WATER DRAIN 12" BETWEEN CONCRETE LINE AND 57-B
|  | 57B | 3.44 | 22 | Transmission | [7 empty] | 2007-04-25 | Other | GROUND OUT SCRATCH | Steel/Wrought Iron |  |  | DAMAGE ONLY; PIPE GAUGE WAS GROUND OUT AND PIPE RECOATE
|  |  |  | 6.63 | Transmission | [10 empty] | Steel/Wrought Iron |  | MCDONALD ISLAND | MCS YARD MCDONALD ISLAND
|  |  |  | 18 | Transmission | [10 empty] | Steel/Wrought Iron |  | MCDONALD ISLAND | MCS YARD AT MCDONALD ISLAND TO MCS COMPRESSORS
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MCDONALD ISLAND | MCS YARD MCDONALD ISLAND
|  |  |  | 6.63 | Transmission | [10 empty] | Steel/Wrought Iron |  | MCDONALD ISLAND | MCS YARD AT MCDONALD ISLAND
|  | 57B | 0.085 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  | MCDONALD ISLAND | WEST OF MASTER METER STATION AREA NO. 8 SAN JOAQUIN COUNTY
|  | 57B | 6.07 | 22 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 057B | 5.32 | 1.05 | Service | [10 empty] | Steel/Wrought Iron |  | BACON ISLAND
|  | 57B | 0.0097 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  | MCDONALS ISLAND | VALVE LOT,A REA NO. 8 MASTER METER STATION MCDONALS ISLAND STATION
|  | 57B | 0.0002 | [12 empty] | Steel/Wrought Iron |  | MCDONALD ISLAND | LINE 57B PG LAUNCHER/RECIEVER MCDONALD ISLAND COMPRESSOR STATION. MCDONALD ISLAND. SAN JOAQUIN COUNTY
|  | 57B | 0.0025 | [12 empty] | Steel/Wrought Iron |  | MCDONALD ISLAND | LINE 57B 24" ABOVE GROUND PIPING FOR PIG LAUNCHER; 24" O.D. STEEL PIPE 1.00" W.T. API SL GR X-52
|  | 57B | 0.0125 | [12 empty] | Steel/Wrought Iron |  | MCDONALD ISLAND | 22" O.D. STEEL PIPE 0.742" W.T. API SL GR X-60
|  | 57B |  | 16 | Transmission | [12 empty] | MCDONALD ISLAND | MCDONALD ISLAND COMPRESSION STATION AREA 8; MCDONALD ISLAND COMPRESSOR STATION MASTER METER STATION AREA 8 MCDONALD ISLAND SAN JOAQUIN COUNTY
|  | 57A |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | MCDONALD ISLAND COMPRESSOR STATION AREA 7 MCDONALD ISLAND SAN JOAQUIN COUNTY
|  | 57B | 1.0006 | [12 empty] | Steel/Wrought Iron |  | MCDONALD ISLAND
|  | 057A | 7.0713 | 18 | Transmission | [10 empty] | Steel/Wrought Iron |  | PALM TRACT
|  | 57B | 16.7762 | [12 empty] | Steel/Wrought Iron |  | BRENTWOOD | 22" LINE TO PIG LAUNCHER
|  | 57B | 16.7783 | [12 empty] | Steel/Wrought Iron |  | BRENTWOOD
|  | 57B | 16.7814 | [12 empty] | Steel/Wrought Iron |  | BRENTWOOD | 20" PIPE TO LINE 3034"-11" TO 11' -10' 2" WEST OF LINE 57B 22.00"; 20" STEEL PIPE
|  | 57B | 16.7834 | [12 empty] | Steel/Wrought Iron |  | BRENTWOOD | 12" PIPE HAD OIL
|  | 57B | 16.7884 | [12 empty] | Steel/Wrought Iron |  |  | OIL IN 22" PIPE
|  | 57B | 16.7875 | [12 empty] | Steel/Wrought Iron |  | BRENTWOOD | 12" PPIPE TO LINE 131 2'-6" WEST OF 22" LINE 57B; OIL IN 12" PIPE
|  | 57B | 16.7875 | [12 empty] | Steel/Wrought Iron |  | BRENTWOOD | OIL IN LINE 8"
|  | 57B | 16.8 | [12 empty] | Steel/Wrought Iron
|  | 57A | 13.01 | 18 | Transmission | [7 empty] | 2008-05-22 | Type B Sleeve - Weld |  | Steel/Wrought Iron |  |  | REPAIR GOUGING WITH TYPE B SLEEVE; GUY WIRE INSTALLED BY THIRD PARTY HIT AND DAMAGED L-57A
|  | 65 |  | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | CONCORD | LOS MEDANOS STORAGE FACILITY GAS WELL 9C PAD C
[16 empty] | Steel/Wrought Iron |  |  | BLACK WIRES TO 16", LINE INSTALLED BIG FINK ETS FOR LINE 65 GATHERING & CLEAN UP, WHITE WIRES TO 4" LINE
[16 empty] | Steel/Wrought Iron |  |  | BLACK WIRES TO 8" LINE, WHITE WIRES TO 4" LINE, INSTALLED BIG FINK ETS FOR LINE 165 GATHERING & CLEAN UP
[16 empty] | Steel/Wrought Iron |  |  | BLACK WIRES TO 8" LINE, WHITE WIRES TO 4" LINE, INSTALLED BIG FINKS ETS FOR LINE 65 GATHERING & CLEAN UP
[16 empty] | Steel/Wrought Iron |  |  | BLACK WIRES TO 8" LINE, WHITE WIRES TO 7" LINE, INSTALLED BIG FINK ETS FOR 65 GATHERING & CLEAN UP
[16 empty] | Steel/Wrought Iron |  |  | BLACK WIRES TO 8" LINE, WHITE WIRES TO 7" LINE, INSTALLED BIG FINK ETS FOR 65 GATHERING & CLEAN UP
|  | 65 | 0 | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  | CONCORD | GINO #3 GAS WELL PAD A LOS MEDANOS GAS STORAGE FACILITY CONCORD CONTRA COSTA COUNTY
|  | 65 |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  | CONCORD | LOS MEDANOS COMPRESSOR STATION CONCORD: CONTRA COSTA COUNTY
|  | 065-2 | 0.0031 | 6.62 | Gathering | [10 empty] | Steel/Wrought Iron |  | CONCORD | LOS MEDANOS GAS STORAGE FACILITIES PAD B GAS WELLS CONCORD; CONTRA COSTA COUNTY
|  | 065-2 | 0.0031 | 6.62 | Gathering | [10 empty] | Steel/Wrought Iron |  | CONCORD | LOS MEDANOS GAS STORAGE FACILITIES PAD B GAS WELLS CONCORD; CONTRA COSTA COUNTY
|  | 065-2 | 0.0031 | 6.62 | Gathering | [10 empty] | Steel/Wrought Iron |  | CONCORD | LOS MEDANOS GAS STORAGE FACILITIES PAD B GAS WELLS CONCORD; CONTRA COSTA COUNTY
|  | 65 |  | 06.625 & 04.50 | Gathering | [7 empty] | 2009-06-16 | Replace TP Main |  | Steel/Wrought Iron |  | CONCORD | PITTING OVER ENTIRE PIPE, CANNOT MEASURE ACCURATELY; PAD B LOS MEDANOS GAS STORAGE FACILITIES CONCORD; CONTRA COSTA COUNTY
|  | 65 |  | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | CONCORD | ROUTE 065 LOS MEDANOS COMP. STA; BETWEEN V-48 V105
|  | 100 | 142.2 | [15 empty] | SNIRE HOLE FOR L100 PIGGING PROJECT LOCATION AT BRENFORD AND WENLOCK IN VACANT LOT. SOUTH SIDE OF BRENFORD
|  | 100 | 141.23 | [15 empty] | SNIFF HOLE FOR L100 PIGGING PROJECT LOCATION AT VAN WINKLE LN & GALAHAD AVE IN PARK ON NORTH SIDE OF VAN WINKLE LN.
|  | 100 | 144.96 | [15 empty] | IN RIGHT OF WAY LAND STRIP ALONG FWY 6-80 AT END OF DAHLIA CT DOUBLE DOORS GO THROUGH. USA # 0333270
|  | 100 | 147.62 | 20 | Transmission |  | Girth Weld | [10 empty] | MILPITAS | GPS FILE 072516A LOC #1
|  | 100 | 147.71 | 20 | [13 empty] | MILPITAS | GPS FILE 0601111 LOCATION 5
|  | 100 | 147.7177 | [14 empty] | MILPITAS | POTHOLE FUTURE VTR PROPOSED SITE. LINE 100 030622 USA TICKET IN THE PARKING LOT OF ADDRESS 760 E. CAPITOL AVE/APPIAN ENGINEERING
|  | 100 | 147.77 | 10 | Transmission |  | Girth Weld |  |  |  |  | 2000-02-13 | [5 empty] | MILPITAS | GPS FILE # R0021417A LOC #2
|  | 100 | 145 | 20 | [13 empty] | MILPITAS | GPS FILE 060111A LOCATION 6
|  | 100 | 147 | [15 empty] | GPS FILE # PRESCHOL
|  | 100 | 146.09 | 20 | Transmission |  | Girth Weld | [10 empty] | SAN JOSE
|  | 100 | 138.9422 | [15 empty] | USA # 0036281 DANIEL MALONEY DR AND BRIGADOON WAY (INTERSECTION). DALEO TRENCHED ACROSS LINES AT THIS LOCATION. NOTICE THAT L100 IS SHALLOW HERE (28") OF COVER.
|  | 100 | 145.58 | 20 | Transmission | [10 empty] | Steel/Wrought Iron | SMLS | MILPITAS | LOC #3 GPS FILE R081315A
|  | 100 | 146.6 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  | MILPITAS | LOC #1 GPS R081317A
|  | 100 | 147.84 | [14 empty] | MILPITAS | LOCATION 1 NEW PIPE LESS THAN 1 YR
|  | 100 | 138.43 | [15 empty] | LINE 100 AT LOCATION IS FAIRLY SHALLOW
|  | 100 | 141.14 | 20 | Transmission | [7 empty] | 2001-12-10 |  |  | Steel/Wrought Iron |  | SAN JOSE | FROM NOV 14TH 2011 TO DEC 10TH WE OPEN CUT CAPITAL EXPRESSWAY AND REMOVED THE CORRIGATED NESTABLE CASING AND CENTRALIZERS. WE FOUND 3 LOCATIONS THAT HAD CONTACT BETWEEN THE CASING AND THE TRANSMISSION LINE. WE CLEANED THE EXISTING TAR COATING, AND APPLIED "STACKWRAP" AS A HOVER COAT ON THE FULL LENGTH OF THE EXCAVATIONS.
|  | 100 | 141.33 | 20 | Transmission |  | Girth Weld | [10 empty] | SAN JOSE | CASING CONTRACT JOB #8033940
|  | 100 | 140.8 | [15 empty] | TULLY & CAPITOL
|  | 100 |  | 20 | Transmission | [12 empty] | MILPITAS | GPS FILE #R112315A33F LOC #5
|  | 100 | 147.8 | 20 | Transmission | [12 empty] | MILPITAS | GPS FILE R112315ASSF LOC #4
|  | 100 | 147.89 | [15 empty] | LOCATION #3
|  | 100 | 147.97 | [14 empty] | MILPITAS | LOCATION #5
|  | 100 | 147.75 | 20 | Transmission |  | Girth Weld
|  | 100 |  | 20 | Transmission |  | Girth Weld |  |  |  |  | 2000-02-13 | [5 empty] | MILPITAS | VOID; GPS FILE #021417A LOC# 3 - THIS FILE HAS LOC #3 @ 47 IN COVER - THIS PT. (LOC #3) IS ON 300A
|  | 100 | 148 | 24 | [13 empty] | MILPITAS | 060615B LOC #3
|  | 100 | 1148.12 | 24 | [13 empty] | MILPITAS | ... END CAP BY HEALD COLLEGE NEW 100
|  | 100 | 147.83 | 20 | Transmission |  | Girth Weld |  |  |  |  | 2000-02-13 | [5 empty] | MILPITAS | GPS FILE # R021418A LOC# 1
|  | 100 | 148 |  | Transmission |  | Girth Weld | [10 empty] | MILPITAS | R0606 B LOC #1
|  | 100 | 148.15 | 20 | Transmission |  | Girth Weld | [10 empty] | MILPITAS | OLD LINE 100
|  | 100 | 147.93
|  | 100 | 148.15 | 24 |  |  | Girth Weld | [10 empty] | MILPITAS | NEW LINE 100
|  | 100 | 1148.32 | 24 | Transmission | [12 empty] | MILPITAS | GPS FILE # R112315ASSF LOCATION #1
|  | 100 | 148.37 | 24 | [13 empty] | MILPITAS
|  | 100 | 148.57 | 20 | Transmission |  | Girth Weld | [11 empty] | GPS FILE R030115A LOC#1
|  | 100 | 148.61 | [12 empty] | Steel/Wrought Iron
|  | 100 | 148.62 | 20 | Transmission |  | Girth Weld | [10 empty] | MILPITAS | GPS FILE RO32318A
|  | 100 | 148.52 | 20 | Transmission |  | Girth Weld | [10 empty] | MILPITAS | GPS FILE R030115A LOC #3
|  | 100 | 148.52 | [14 empty] | MILPITAS
|  | 100 | 148.52 | [14 empty] | MILPITAS
|  | 100 | 148.61 | 20 | [14 empty] | GPS FILE 060111A LOCATION 2
|  | 100 | 148.69 | 20 | Transmission | [12 empty] | MILPITAS | GPS FILE 072516A LOC #3
|  | 100 | 149.22 | 20 | Transmission | [12 empty] | MILPITAS
|  | 100 | 149.4 | 20 | Transmission | [12 empty] | MILPITAS | LOCATION #1
|  | 100 | 149 | 20 | Transmission | [12 empty] | MILPITAS | LOCATION #2
|  | 100 | 149.44 | 20 | Transmission | [12 empty] | MILPITAS | LOCATION #3
|  | 100 | 149.29 | 20 | Transmission |  | Girth Weld | [10 empty] | MILPITAS | GPS FILE 120216B LOC #3
|  | 100 | 149.43 | 20 | [14 empty] | GPS FILE R052410A SSF
|  | 100 | 149.47 | 20 | [14 empty] | GPS FILE R052410A SSF
|  | 100 | 149.5 | 20 | Transmission | [12 empty] | MILPITAS | GPS FILE R1206181A
|  | 100 | 149.52 | 20 | [14 empty] | GPS FILE R052410A SSF
|  | 100 | 149.86 | [15 empty] | POTHOLING BY TRAVIS BIANCHI AMARCER. CORNER OF BARBER LN & BELLEW DR. IN GRASS AREA. 11' FROM CURBINE. 84" DEPTH
|  | 100 | 149.63 | 20 | [14 empty] | GPS FILE 052410A SSF
|  | 100 | 150.04 | 24 | Transmission | [7 empty] | 2002-10-01 | Other | RECOAT | Steel/Wrought Iron |  |  | REMOVED CASING, REPAIRED COATING POWER CRETED WAX TAPE OVER EXISTING COATING; REMOVED CASING, STEEL PIPE AND NESTABLE CORRIGATION, COATING WAS POOR WHERE NESTABLE CORRIGATION WAS USED. LIGHT SURFACE RUSTING ONLY. PART OF LINE WAS COATED WITH WAX TAPE. THE PART UNDER AND AJSENT TO CALAVERAS WEST HAD OLD COATING. SAND BUSTED AND RECOATED WITH POWER CRETE. THE RUST WAS OVERCOATED WITH WAX TAPE - STEVE JAMESON.
|  | 100 | 147.8 | [14 empty] | MILPITAS | USA #0038089 EXARO POTHOLING... FOUND PIPE L100 AT 61.5" DEEP. COATING WAS FBE GREEN STUFF. ACORDING TO GSAVE IT IS 24" OD IN THIS AREA. LOCATION IS IN STREET THE RIGHT LANE ON CAPITAL AVE ON ST. SOUTH OF MONTEGAGE EXPY. APROX 375' FROM TRACKS ON SOUTH END CAPITOL.
|  | 100 | 139.5 | [15 empty] | INSPECTION DIG FOR L100 @ INTERSECTION OF CALLE DE LAS ESTRELLA AND PETTIGREW DRIVE, USA 0229253. THIS LOCATION FOUND GIRTH WELD, PM # 41312859
|  | 100 | 139.5 | [15 empty] | INSPECTION DIG FOR L100 @ INTERSECTION OF CALLE DEL LAS ESTRELLA AND PETTIGREW DRIVE SAN JOSE. USA # 0279253. THIS IS LOCATION OF DENT & GAUGES. 14'9" FROM GIRTH WELD. MEARS ENGINEERS TO TAKE MEASUREMENTS. PM#41312859
|  | 101 | 3.0125 | 0.36 | Transmission | [10 empty] | Steel/Wrought Iron
[12 empty] | 2010-12-07 | [5 empty] | SANTA CLARA | FOUND 36" LINE 101 - INSIDE 44" CASING, 4' STEEL ON TOP OF 101 - NO VALVE FOUND
|  | 101 | 3.0247 | 36 | [5 empty] | Previously Damaged |  |  | 2010-12-15 | Grinding - Other |  | Steel/Wrought Iron |  |  | REG, I FOUND THIS A-FORM & PICTURES FOR L-101 MP 3.03 @ LAFEYETTE. I KNOW I SENT YOU WHAT I HAD BEFORE & YOU ALREADY MAPPED BUT WASN'T SURE YOU HAD A COPY OF THIS. - GEORGE PM # 41363152; LIGHT SCORE MARKS ON GAS MAIN. WRAP CONDITION POOR DUE TO GOUGING BY POWER EXCAVATION EQUIPMENT. DAMAGE WAS DISCOVERED AND HAD BEEN CAUSED BY PREVIOUS EXCAVATION AT WORK SITE.; ORIGINAL JOB SCOPE WAS TO VERIFY AN EXISTING 4" VALVE. ELECTROLYTIC CONTACT BETWEEN CASING & MAIN WAS DISCOVERED AND CORRECTIVE ACTION ATTAMPT MADE, COATING DAMAGE & SUPERFICIAL GOUGES WERE DISCOVERED, THEY WERE DUE AT SOME POINT PREVIOUSLY TO EXCAVATION IN 12/10.
|  | 101 | 10.3657 | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  | PALO ALTO | EXTERNAL INSPECTION OF L101 AT SNIFF HOLE. NO METALLIC PIPE INSPECTION BEYOND COATING FORM COMPLETED BY JIM NORTHAUTT 12-8-10 INSPECTED BY 3RD PARTY
|  | 101 | 10.7308 | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | EXTERNAL INSPECTION OF L101 AT SNIFF HOLE. NO METALLIC PIPE INSPECTION BEYOND COATING FORM COMPLETED BY JIM NORTHAUTT 12-8-10 INSPECTED BY 3RD PARTY
|  | 101 | 27.72 |  | Transmission
|  | 101 | 27.75 |  | Transmission
|  | 101 | 32.17 | [12 empty] | Steel/Wrought Iron |  | MILBRAE
| 99-30059 | 101 | 32.57 | 20 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party |  | 1999-03-15 | 1999-04-03 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | MILLBRAE | LOMITA PARK PUMP STATION OVER TRANS. LINE; WELDED 20"X18 SPLIT SLEEVE
[13 empty] | 1999-03-11 | Welded Sleeve/Can - Weld |  |  |  | MILLBRAE | INSTALLED 2 - 20"X18" SPLIT SLEEVES
|  | 101 | 37.05 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | NO SKETCH OR GAS. POSTED AFORM INSPECTION AT BOTH ENEDS OF 7017908-02 TIE-IN LOCATIONS
| 99-30097- | 101 | 38.75 |  |  |  | Other |  | GREASE FITTING | Other | NEEDEED GREASING | 1999-06-17 | 1999-08-01 | Other | FITTED WITH GREASE | Steel/Wrought Iron |  | BRISBANE | GREASE FITTING WAS LEAKING GREASED VALVE LEAK STOPED
56 | 99-30097-1 | 101 | 38.75 | 24 | Transmission |  | Other |  |  | Other |  | 1999-06-17 | 1999-08-04 | Other |  | Steel/Wrought Iron |  | BRISBANE
|  | 101 | 90.23 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DEPTH DETERMINED BY PROBING. DEPTH OF 30" CASING TOP WAS 11'-1". DEPTH TAKEN IN MIDDLE AT NORTHERN CROSSWALK ON BAYSHORE BLVD @ SUNNYDALE. DREW KELLY - TRANSMISSION PIPLINE ENGR. NOTE: PIPE IS LOCATED JUST UNDER MUNI'S CONCRETE PAD. TL101
|  | 101 | 40.23 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN FRANCISCO | PIPE WAS EXPOSED BY VACCUUM EXCAVATION PRIOR TO MICRO BORING BY CITY OF S.F. DEPTH TO TOP OF THE 30" CASING WAS 11' 2" WHICH CLOSELY MATCHES THE AS BUILT. TODD ARNET WAS ON SITE AND RECORDED THE DEPTH. I. DREW KELLY FILLED OUT THIS FORM TO HAVE THE DEPTH RECORDED. THE EXCAVATION WAS IN THE ASPHALT AT THE EDGE OF THE CONCRETE BASE FOR THE MUNI TRACKS. TL101 MP 40.23
|  | 103 | 0.41 | 12 | [11 empty] | Steel/Wrought Iron
|  | 103 | 0.45 | [12 empty] | Steel/Wrought Iron |  |  | 0.48 IN G-SAVE PMP1, 750' NORTH OF GROF ROAD IN HOLLISTER
|  | 103 | 0.53 | [12 empty] | Steel/Wrought Iron |  |  | MP 0.53 IN G-SAVE PMN; 500' NORTH OF GROF ROAD IN HOLLISTER
|  | 103 | 0.55 | [12 empty] | Steel/Wrought Iron |  |  | MP 0.57 IN G-SAVE PMN, 265' NORTH OF GROF ROAD IN HOLLISTER
|  | 103 | 0.6 | [12 empty] | Steel/Wrought Iron |  |  | 0.62 IN G-SAVE PMN, 15' NORTH OF GROF RD IN HOLLISTER
|  | 103 | 4.18
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | HOLLISTER | IN NARROW STRIP BETWEEN SAN JUAN RD & SAN JUAN HOLLISTER RD.
|  | 103 | 4.11 | [14 empty] | HOLLISTER | POTHOLING W/ VACF FOR L-103 12" TP @ SAN JUAN RD. ADJACER TO HOLISTER LANDSCAPE SUPPLY & ANOTHER SPOT AT EAGLE RECYCLING FOUND AT DEPTH OF 51" & ANOTHER AT SPOT SAN BENITO AUTO WRECKING IN GRASS AREA BEHIND TREES AT DEPTH OF 47"
|  | 103 | 4.4201 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 103 | 4.8 | 12.75 | Transmission
|  | 103 | 4.87 | 12.75 | [11 empty] | Steel/Wrought Iron
|  | 103 | 12.9 | 12 | Transmission | [6 empty] | 2010-01-29 |  |  |  | Steel/Wrought Iron |  | SALINAS | PIPE EXPOSED BY EROSION. ADDITIONAL PIPE WITH BARE COVER.
|  | 103 | 10.5 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | SALINAS | RECOADED LINE TO MAKE REPAIRS BEFORE INSTALLING; ERCON PROJECT WHILE EXCAVATING FOR ERCON WALL WE FOUND 2 OLD PIPE SUPPORTS THAT WERE BURRIED, WE FOUND SOME CORROSSION BETWEEN THE PIPE & OLD SUPPORT SADDLE. AREAS WERE INSPECTED & MEASURED PITTING. RECOATED 15' WITH POWER CRETES. BACKFILLED AND BUILT ERCON BAG WALL.
|  | 103 | 15.1 | [15 empty] | THIS LOCATION IS AT THE GABILAN CREEK BRIDGE & THE PIPE WAS RUNNING UNDER THE CREEK. L-103 IS A 12" PIPELINE WITH A WALL THICKNESS OF .250 & MOP OF 350 PSIG. THE NEW PIPE IS .281 WALL THICKNESS & IS SPANNED OVER THE CREEK. OPERATING MAP #383061-48 & PIPELINE SURVEY SHEET M.P. 15.00-17.53, CENTER COORDINATE 625436.365330,4070309.732985
|  |  |  | 12.75 | Transmission | [13 empty] | RELOCATE 683' OF 12" GAS MAIN
|  | 103 | 17.98 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | SALINAS | INSTALL 12" CHECK VALVE
|  | 103 | 15.3 | 12 | Transmission | [6 empty] | 2010-09-08 |  |  |  | Steel/Wrought Iron |  | SALINAS | APPROX 300 FT SOUTH OF SPAN
|  | 105-A | [13 empty] | Steel/Wrought Iron |  |  | 2212 7TH ST - BERK LINE 105-A
|  |  |  | 24 | [11 empty] | Steel/Wrought Iron |  | EL CERRITO
|  | 105A | 7.99 | [12 empty] | Steel/Wrought Iron |  |  | POTERO AVE 50' W/O SO. 20TH
|  | 105A | 48.91 | [12 empty] | Steel/Wrought Iron |  |  | SO. 8TH ST. 51' S/0 FLORIDA AVE. LINE 105-A RELWND.
|  |  | 44.9567 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | RICHMOND | OMSPECTION AREA 4 L" COVER M.P. 40.95
|  |  | 45.6265 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | RICHMOND
|  | 105A | 45.31 | [15 empty] | SEE ATTACHMENT
|  | 105A | 45.59 | [15 empty] | SEE ATTACHMENT
|  | 105A | 45.2 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | RICHMOND | LINE 105A 24" STEEL TP MAIN 36' 2 M.P. 45.18
|  | 105B | 0.29 | [12 empty] | Steel/Wrought Iron |  |  | 1002 LILLIAN ST. CROCET
|  | 105B | 6.6 | [12 empty] | Steel/Wrought Iron |  |  | 2235 SAN PABLO AVE PINOLE T-105b
|  | 105B | 7.12 | [12 empty] | Steel/Wrought Iron |  |  | ON SAN PABLO AVE 124' E/O 3RD AVE. PINOLE T-105B
|  | 105B | 8.04 | [12 empty] | Steel/Wrought Iron |  |  | ON SAN PABLO AVE 184" W/O BELMONT WAY PINOLE T-105B
|  | 105 | 10.61 | [12 empty] | Steel/Wrought Iron |  |  | SAN PABLO AVE & LANCASTER DR. RICHMOND T-105B
|  | 105 | 11.11 | [12 empty] | Steel/Wrought Iron |  |  | 20TH & RUMRILL BLVD. SAN PABLO; 20TH & RUMRILL BLVD SAN PABLO T-105B
| 09-80061 | 105B | 0.0041 | 0.5 |  |  | Other Welds |  |  | Other | WELD NOT FINISHED | 2009-06-15 | 2009-09-10 | Fill Weld - Weld |  | Steel/Wrought Iron |  | HERCULES | PM 41150160 AS-BUILT L-105B, DF8282 MP. 0.0041; FINISHED OFF WELD THAT WAS INCOMPLETE; SOAP TEST ONLY; SEE ATTACHED SKETCH (4OF4) FOR AS-BUILT DETAILS. THIS VALVE LEAKING N-62
|  | 105A | 44.99 | [15 empty] | SEE ATTACHMENT
| 00-51001-1 | 105A | 39.59 | 30 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 2000-06-20 | 2000-06-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EMERYVILLE | 301 ON CAP ON SERV. TEE C/O SERVICE AND REDOPED/RETIGHTENED CAP; REPAIRED LEAKING CAP ON SERV. TEE.
|  | 107 | 13.12 | [15 empty] | SEE DRAWING ON BACK
|  | 107 | 13.98
|  | 107 | 14 | [15 empty] | ON BACK
|  | 107 | 14.01 | [12 empty] | Steel/Wrought Iron |  |  | ON BACK
|  | 107 | 14.75 | [15 empty] | N/A, N/A, N/A, N/A
|  | 107 | 14.79 | [15 empty] | N/A, N/A, N/A, N/A
|  | 107 | 15.124 | 2 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | FOUND IN CONNECTION W/ WORK ON 30604337 REMOVE V-15.27 L-107 CARROYO RD.; LINE 107 LOOKING WEST PIPE...
|  | 107 | 16.73
|  | 107 | 16.79 | [12 empty] | Other
|  | 107 | 18.83 | [12 empty] | Steel/Wrought Iron |  |  | ON BACK; INSTALLED E.T.S. STATION
|  | 107 | 19.04 | [12 empty] | Steel/Wrought Iron |  |  | ON BACK; INSTALLED E.T.S. STATION
|  | 107 | 19.05 | [12 empty] | Other
|  | 107 | 19.15 | [12 empty] | Other
|  | 107 | 19.35 | [12 empty] | Other
|  | 107 | 19.36 | [12 empty] | Steel/Wrought Iron |  |  | ON BACK; INSTALLED E.T.S. STATION
|  | 107 |  | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | IN CONNECION W/ 7045166; LINE 107
|  | 107 | 22.3453 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | IN CONNECTION W/ 7045166 LINE 107
|  | 107 | 23.4520 & 23.4805 | 22 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 107 | 25.02 | 24
|  | 107 | 25.04 | 24
|  | 107 | 26.5 | [15 empty] | MEANS PROJECT TO RCOUNT INSPECTION DIG. LINE 107, U.S.A. #0211799 LOCATION IS IN FREMONT ON THE MOUNTAIN SIDE APPROX 1000 FEET FROM MAIN BLVD
|  | 107 | 26.65 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE 107 STA. 8+47; MP 26.65; LATIT 37 32 4.933265, LONG -121 55 49.47802; ; MISC. COMMENTS/INFORMATION: SITE WAS EXCAVATED AT ORIGINAL STATIONING CALLED OUT ON DE SHEET. AFTER EXCACATION WE HAD 8' OF BARE PIPE EXPOSED ON U/S END AND 2' OF PIPE COATED WITH TAPE COAT ON D/S END. DECISION WAS MADE TO MOVE INSPECTION 7' 5" D/S FROM ORIGINAL STATION PER MIKE WEST ON 8/2/2010. ON 8/3/2010 PIPE WAS EXCAVATED BY HAND DIGGIN. THEY EXPOSED 3' 5" OF BARE PIPE AND 6'7" OF TAPE COATED PIPE FOR A TOTAL OF 10' EXPOSED FOR INSPECTION. ON 8/3/2010 TWO GIRTH WELDS WERE FOUND UNDER COATING, ONE AT 4' 5" FROM THE U/S EDGE AND ONE AT 8' 4". A 45" ELBOW WAS PARTIALLY EXPOSED AT D/S END OF DITCH. FOUND GENERAL CORROSION FROM U/S EDGE TO GIRTH WELD #1/ ON 8/4/2010 MT WAS PERFORMED BY ATS AND FOUND NO LINEAR INDICATIONS. PIPE COATED WITH WAX TAPE, WRAPPED WITH TUFF-N-NUFF, ETS WIRES CAD-WELDED TO PIPE, AND 32LBS. ANODE WAS PLACED IN DITCH ON 3:00 OF PIPE AT D/S END OF DITCH AND WIRES WERE RAN INTO ETS WITH THE WIRES ATTACHED TO PIPE. PIPE WAS BACKFILLED ON 8/4/2010.; ; LOCATION IS AN APPROXIMATE DISTANCE OF 200' UP HILL OFF OF MISSION CLEIO AVE. SITE IS I FREMONT CA., 450' N/W OF THE INTERSECTION OF MISSION BLVD. AND MISSION CLEIL AVE.
|  | 107 | 27.42 | [15 empty] | LOCATION ON U.S.A. MAP
|  | 107 | 27.71 | 36 | Transmission | [13 empty] | ;
|  | 107 | 27.8 | 36 | Transmission | [12 empty] | FREMONT
|  | 107 | 27.9 | [15 empty] | PIPE NOT EXPOSED. DEPTH DETERMINED BY PROBING AFTER 4' EXCAVATION
|  | 107 | 28.05 | 36 | [14 empty] | GPS FILE R10132A
|  | 107 | 28.6 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  | FREMONT
|  | 107 | 28.1 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  | FREMONT | GPS FILE R081815A
|  | 107 | 30.04 | 36
|  | 107 | 30.2 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  | FREMONT | GPS FILE R101321A LOC #2
|  | 107 | 30.3 | [15 empty] | DEPTH DETERMINED BY PROBING
|  | 107 | 30.42 | [15 empty] | IN NURSERY 48' FROM FENCE LINE
|  | 107 | 33.6 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | TIE-IN LOCATION FOR THE REPLACEMENT OF L-107 N.MP. 33.60 ORDER NUMBER 7036396
|  | 107 | 34 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | TIE-IN LOCATION FOR THE REPLACEMENT OF LINE 107 N/ MP.34.00 ORDER NUMBER 7036396
|  | 107 | 34.27 | 34 | Transmission |  |  |  |  | Other | BORE DAMAGE | [6 empty] | FREMONT
|  | 107 | 34.12 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | TIE-IN OF LINE 107 REPLACEMENT PROJECT GM7036396
|  | 107 | 34.3 | [12 empty] | Steel/Wrought Iron |  |  | TIE-IN LINE 107 REPLACEMENT PROJECT, GM 7036396
|  | 107 | 35.72 | [15 empty] | STAND BY FOR NEARS. PORT OF CDA PROJECT. DUG UP LINE 107 AND FOUND PIPE TO BE 9' DEEP AND BARE IN THIS LOCATION. DIXON LANDING RD. AREA DEAR 880 FWY
|  | 107 | 35.97 | 36 | [11 empty] | Steel/Wrought Iron |  | FREMONT | HAVE A 3" GATE TOP VALVE, WITH AN UNDER 5/22 REINFORCEMENT POD
|  | 107 | [16 empty] | 5 LOCATIONS POR HOLED GPS FILE #MC CARTHY
|  | 107 | 37.65 | [15 empty] | AT BEHIND 430 MCCARTHY RANCH OF MC CARTHY RD. L-107 MP. 37.65
|  | 107 | 28.9 | [14 empty] | FREMONT | MEARS INSPECTIO DIG ON LINE 107 RIGHT ON THE ANGLE POINT OF LINE
|  | 108 | 0.03 | 16 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 108 | 4.6 | 24 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 108 | 8.78 | 24.16 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 108 | 8.8 | [12 empty] | Other |  |  | TIE-IN. NEWLY INSTALLED 16" PIPE INSTALLED 03.
|  | 108 | 11.47 | 16 | [11 empty] | Steel-Other
|  | 108 | 11.5 | 16 | Transmission | [10 empty] | Other | NEW STEEL PIPE |  | NEWLY INSTALLED 16" PIPE IN 02. TIE IT. NEWLY INSTALLED 16" PIPE IN 03
|  | 108 | 11.53 | 16 | [11 empty] | Steel-Other
|  | 108 | 11.53 | 16 | [11 empty] | Steel-Other
|  | 108 | 11.72 |  | Transmission | [10 empty] | Steel/Wrought Iron |  | MANTECA | WEST RPON VALVE YARD. INSPECTION POINT L-108
|  | 108 | 11.73 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | EXPOSED 24" LINE 108 FOR TIE-IN. "A" FORM FOR INSPECTION ONLY BY WAYNE SWILLEY INSPECTOR M.T.S.I.
|  | 108 | 12.61 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MANTECA
|  | 108 | 12.7 | 16 | Transmission | [12 empty] | MANTECA
|  | 108 | 12.76 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MANTECA
|  | 108 | 12.9 | 16 | Service | [10 empty] | Steel/Wrought Iron
|  | 108 | 13.72 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MANTECA | MAIL ORIG TO RAY BAUTISTA/ COPY OF TO ROBT MACDONALDO; ROUTE: L-108 LOCATION: 13.715 4-13-09 5:00PM
|  | 108 | 13.95 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | MANTECA
|  | 108 | 14.13 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | EXISTING 24" LINE 108 EXPOSED TO MAKE TIE-IN OF NEW PIPE LINE. INSPECTION ONLY. "A" FORM MADE BY WAYNE SWILLEY M.T.S.I.
|  | 108 | 14.65 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | MANTECA
|  | 108 |  | 24 | [11 empty] | Steel-Other |  |  | INSTALLED 4" SERVICE TEE & VALVE TO SERVE. REG. MA-HP50
|  | 108 | 15.63 & 15.66 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | MANTECA
|  | 108 | 16.32 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | MANTECA
|  | 108 | 16.37 & 16.39 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | MANTECA
|  | 108 | 16.46 | 24 | Transmission | [12 empty] | MANTECA
|  | 108 | 18.89 | [14 empty] | MANTECA
|  | 108 | 23.62 | 24 | [13 empty] | STOCKTON
|  | 108 | 25.84 | [14 empty] | STOCKTON
|  | 108 | 26.07 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | *THE CITY OF STKN. WAS GOING TO CROSS UNDER THE 24" AND A 6" DIST. MAIN THE 24" IS 77" DEEP, THE 6" IS 54" DEEP. THEY DECIDED TO ABANDON THIS PROJECT ON (6/16/10). THEY BACKFILLED THE TRENCH TODAY TAPF
|  | 108 | 26.08 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON
|  | 108 | 26.24 | 24 | Transmission >= 20% SMYS | [10 empty] | Steel/Wrought Iron |  | STOCKTON
|  | 108 | 26.26 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | ORIG TO RAY BAUTISTA COPY OF TO ROBT MALDONALDO
|  | 108 | 26.44 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON
|  | 108 | 26.6 | [14 empty] | STOCKTON
|  | 108 | 26.64 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | SENT TO RAY BAUTISTA CC: MALDONALDO
|  | 108 | 27.11 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON
|  | 108 | 26.99 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | ORIG TO BAUTISTA COPY TO MALDONALDO;
|  | 108 | 27.11 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON
|  | 108 | 27.17 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | ORIG TO RAY BAUTISTA COPY TO ROBT. M.
|  | 108 | 27.86 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | ORIG TO RAY BAUTISTA COPY TO MALDONALDO
|  | 108 | 31.38 | 24 | [11 empty] | Steel/Wrought Iron |  | STOCKTON | SENT TO RAY BAUTISTA, COPY TO ROBT. MALDONALDO
|  | 108 | 34.16 | 24 | Transmission | [12 empty] | STOCKTON
|  | 108 | 38.16 & 38.12 | 16 | Transmission | [12 empty] | LODI
|  | 108 | 42.67 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | LODI | ORIG TO RAY BAUTISTA; COPY TO ROBT. MALDONALDO
|  | 108 | 43.9998 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | RURAL LODN
|  | 108 | 48.55 | [14 empty] | THORTON
|  | 108 | 48.61 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | THORTON | UNIVERSAL FOREST PRODUCTS- SPUR TRACK - NEW
|  | 108 | 48.73 | [14 empty] | THORTON
|  | 108 | 50.68 | 16 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 108 | 61.666 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | MAIN LINE VALVE 61.66 LINE 108
|  | 108 | [13 empty] | Steel/Wrought Iron
|  | 108 | 62.85 | [15 empty] | ELK GROVE; LINE 108 MP 62.8531; LATIT 38 25 30.11845, LONG -121 27 24.34861; ; THROW WALL CORROSION; THERE IS VERY LITTLE ASPHALT COTING ON THE GAS PIPE;
|  | 108 | 63.49 | 16 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 108 | 66.79
|  | 108 | 67.39 | [15 empty] | JOB 7019485
|  | 108 | 50.56 | 24 | [11 empty] | Steel/Wrought Iron
|  | 108 |  | 8 | [13 empty] | STOCKTON
|  | 108 | 63.47 | [6 empty] | External Corrosion |  |  | 2009-12-12 | Welded Sleeve/Can - Weld |  |  |  | ELK GROVE | DUG UP AN EXISITING 16" P.C.F. AND PLUGGED THE MAIN DOWN. WRAPPED AND BACK FILLED
|  | 108 | 63.459 | 16.75 | Transmission |  | Body of Pipe |  |  | External Corrosion |  |  | 2009-12-12 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | ELK GROVE | CUT OUT 12' OF EXISITING MAIN WITH A PCF 16" IN THE 12'. AND REPLACED IT WITH A VALVE AND 6" BYPASS ON THE SOUTH END OF VALVE. INCASE WE HAVE TO TIE INTO THE EXISITING 10"
|  | 108 | 63.459 | 16.75 | Transmission |  | Body of Pipe |  |  | External Corrosion |  |  | 2009-12-12 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | ELK GROVE | CUT OUT 12' OF EXISITING MAIN WITH A PCF 16" IN THE 12', AND REPLACED IT WITH A VALVE AND 6" BYPASS ON THE SOUTH END OF VALVE. INCASE WE HAVE TO TIE INTO THE EXISITNG 10"
|  | 108 | 62.8387 | [14 empty] | ELK GROVE | INSTALLED SAV-A-VALVE; WELDED ON SAV-A-VALVE FOR GAS SNIFFER
| 09-20641- | 108 | 62.85 | 16 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2009-12-09 | 2009-12-11 | Replace TP Main |  | Steel/Wrought Iron |  | ELK GROVE | REPLACED 9.5' 16" SH; L-108 MP 62.8531 LATIT 38 25 30.11845, LONG -121 27 24.34861; THROUGH WALL CORROSION. ; VERY LITTLE ASPHALT COATING ON PIPE LINE
|  | 109 | 0 | 36 | Transmission | [12 empty] | MILPITAS
|  | 109 | 0 | 36 | Transmission | [12 empty] | MILPITAS
|  | 109 | 8.91 | 24 | Transmission | [10 empty] | Wrought Iron |  | S
|  | 109 | 8.99 | 24 | Transmission | [10 empty] | Steel/Wrought Iron
| 03-60335 | 109 | 16.1243 | 22 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2003-12-16 | 2003-12-17 | Patch Welded |  | Steel/Wrought Iron |  | PALO ALTO | WELDED IN POSITION
[16 empty] | Steel/Wrought Iron |  | PALO ALTO
|  | 109 | 43.6211 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE 109 STA. 9+34 MP 43.6211; LOCATION DAILY CITY SULLIVAN AVE; LATIT 37 41 22.05858, LONG 122 28 20.35498
|  | 109 |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE 109 STA. 9+43 MP 43.6211; LOCATION DAILY CITY SULLIVAN AVE.; LATIT. 37 41 22.05858, LONG 122 28 20.35498
|  |  |  | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE 109 STA. 26+89 MP 43.9133; 87TH ST. AND JUNIPERO SERRA BLVD. DAILY CITY; LATIT 37 41 35.77353 LONG, 122 28 16.08488; ; FOUND HOT APPLIED ASPHALT AND TAP COATING APPARENTLY THERE WAS A TIE IN MADE AT THIS POINT
|  | 109 | 43.75 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE 109 STA 17+13 DAILY CITY; LATIT 37 41 26.13800, LONG 122 28 15.94756; MP 43.7508
|  | 109 |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE 109 STA. 9+43 MP. 43.6211; LOCATION DAILY CITY SULLIVAN AVE. ; LATIT 37 41 22.05858, LONG 122 28 20.35498
|  | 109 | 43.6211 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE 109 STA. 9+43 MP 43.6211; LOCATION DAILY CITY SULLIVAN AVE. ; LATIT 37 41 22.05858, LONG 122 28 20.35498.; ; CHECK LAT, LONG OK (KZ 1/11/2009); LATITUDE= 37.68946072; LONG= 122.4723208
|  | 109 | 43.5061 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE 109 STA 1+23; MP 43.5061; DAILY CITY SULLIVAN AVE; LATIT 12 22 820.30808, LONG 37 41 13.98870
|  | 111A | 5.711 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | FRESNO | 2" TAPPED STRAIGHT OUT OF MAIN THEN 2" VALVE AND 2" SERVICE TO 2" RISER. C/O 2" AT LANGE VALVE INSTALLED BLEND TURNED BACK ON VALVE. TO SOAP TEST (OK) SHUT VALVE LEFT 18" STUB
|  | 11B | 0.0153
|  | 11A | 2.6285 | 12
|  | 11A | 18.7123 | 12 | Service | [10 empty] | Steel/Wrought Iron
|  |  |  | 4 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | RETIRE GATHERING LINE 4" TO 68-15 FERRY RD. DUR HAM. FROM UNIT #1 NO 52-22 ALMOND ORCHARD
|  |  |  | 4 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | VERNDLIS UNIT # 26-14 TO 64-15; 64-15 TO CUTOFF LOCATION AT WINDSOCK AT AIRSTRIP
|  |  |  | 2.04 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | VERNALIS UNIT #2 334-22 -2 STL. AT V-22 CUT OFF BY 8" MAIN
|  |  |  | 4.02 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | EVACUATE AT CUT OFF POINT FROM MACIEL BROS NORTH 2" TIE TO 4" MAIN A82+95
|  |  |  | 2.04 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | EVACUATE T.G.W. #26-9 RISER TO MAIN LOCATION 2" GRO.B SMLS .154WT LIQUID OUT OF RISER
|  |  |  | 2.04 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | EVACUATE PAVLON 14-9 -2" GRD.B SMLS- KOTHER RD. COMPLETELY FULL OF FLUID AT RISER LOCATION
|  |  |  | 4 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | TLW #67-5 SEC .5T3S R-6E WELL LOCATION
|  | 114-1 | 8.1797 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLEY | LINE 114-1 LAURITZEN HARBOR VALVE PIT
|  | 114 | 8.1882 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLEY | LINE 114 LAURITZEN HARBOR VALVE PIT.
|  | 114 |  | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ANTIOCH TERMINAL; #1 HOLE LINE 114 ATS SEE ATTACHED MAP S/E WRME ATS
|  | 114 |  | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ANTIOCH TERMINAL; #2 HOLE LINE 114 ATS SEE ATTACHED MAO S/E CORNER ATS
|  | 114 |  | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ANTIOCH TERMINA; #3 HOLE LINE 114 SEE ATTACHED MAP. S/E CORNER ATS
|  | 114 |  | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ANTIOCH TERMINAL; #4 HOLE LINE 114 ATS SEE ATTACHED MAP S/E CORNER ATS
|  | 114 |  | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLEY | OAKLEY, CONTRA COSTA COUNTY.
|  | 114 | 9.0385 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLEY | OAKLEY CONTRA COSTA COUNTY
|  | 114 |  | 12.37 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLEY | ANTIOCH TERMINAL- STATIONING PIPLINE KICKER LINE FOR LAUCHER. SO 7055669; ANTIOCH GAS TERMINAL OAKLEY, CONTRA COSTA COUNTY
| 99-00002-1 | 114 | 7.29 | 16 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1999-07-15 | 1999-08-25 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SHERMAN ISLAND | NEW CROSS TIE VALVE INSTALLED FROM L-114 TO STANPAL 4 LINE APPROX 800' OF L-114
| 99-00002-1 | 114 | 7.29 | 16 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1999-07-15 | 1999-08-25 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SHERMAN ISLAND | NEW CROSS TIE VALVE INSTALLED FROM L114 TO TANPAL 4 LINE APPROX 800' OF L114
|  | 114 | 8.31 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLEY | LAURITZEN HARBOR OAKLEY
|  | 114-1 | 8.308 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLEY | LAURITZEN HARBOR OAKLEY NEAR U.S.A. V 8.31 LINE 114 CONTRA COSTA COUNTY
|  | 114 | 9.03+/- | [12 empty] | Steel/Wrought Iron |  | ANTIOCH
|  | 114 | 9.02+/- | [12 empty] | Steel/Wrought Iron |  | ANTIOCH
|  | 114 | 12.7 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | BRENTWOOD CONTRA COSTA COUNTY
|  | 114 | 12.69 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | BRENTWOOD CONTRA COSTA COUNTY
|  | 114 | 13.64 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | BRENTWOOD CONTRA COSTA COUNTY
|  | 114 | 13.5 | [12 empty] | Steel/Wrought Iron |  | BRENTWOOD | INSTALLED C.P. STATION BIG FINK TYPE "A"
|  | 114 | 13.71 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | BRENTWOOD CONTRA COSTA COUNTY
|  | 114 | 13.73 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | BRENTWOOD CONTRA COSTA COUNTY
|  | 114 | 13.75 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | BRENTWOOD CONTRA COSTA COUNTY
|  | 114 | 15.98+/- | [12 empty] | Steel/Wrought Iron |  | BRENTWOOD
|  | 114 | 16.48 | 22
|  | 114 |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | BRENTWOOD GAS TERMINAL; STATION PIPING LINE 114, BRENTWOOD, CONTRA COSTA COUNTY
|  | 114 |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | BRENTWOOD GAS TERMINAL; STATION PIPING LINE 114, BRENTWOOD, CONTRA COSTA COUNTY
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | BRENTWOOD GAS TERMINAL STATION PIPING, BRENTWOOD CONTRA COSTA COUNTY
|  | 114 | 18.6011 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | MARCH CREEK RD. & CAMINO DIABLO BLVD. +/- 2 WEST OF BYRON: CONTRA COSTA COUNTY
|  | 114 | 20.6557 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | G.C. WELD ON 1" SAV-A-VALVE FOR MONITORING
|  | 114 | 20.88 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | G.C. WELD ON 1" SAVE-A-V-ALVE FOR MONITORING
|  | 114 | 26.1472 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | INSPECTION ONLY WHILE INSTALLING CATHODIC CABLE ON L-114 @ MP 26.6 PM#30675182
|  | 114 | 26.9267 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | NORTH TIE-IN LINE 114 PAGE 2 OLD JOB# 7042512 OLD JOB#30603496; NORTH TIE-IN LINE 114 PAGE 1 OLD JOB#0425...OLD JOB# 30683496. DISTRICT: TRACY PM 30603496-07 RTE l-114 mP .26.9267; NORTH TIE-IN LINE 114 PAGE 3 OLD JOB # 7042512 NEW JOB # 30603496; EXPOSED 45' EXISITING 22" PIPE LINE 114 FOR TIE-IN
|  | 114 | 27.6448 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 30' EXISITING 22" LINE 114 FOR TIE-IN
|  | 114 | 27.77 | [15 empty] | TIE-IN HOLE FOR LINE 114 HYDRO TEST
|  | 114 | 27.6693 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | EXISITING PIPE AT SOUTH TIE-IN FOR 30303496 REPLACEMENT JOB
|  | 114 | 27.68 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | @SOUTH TIE-IN LOC L 114 RELIC 7044-2512/30603496 TOE-ON 11/30/2007
|  | 114 | 27.91 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  | LIVERMORE | 114 MP 27.9112 JOB 8069196; LINE 114 MP. 27.91 LIVERMORE; ALAMEDA COUNTY TO VALVE 26.84 PRIVATE ROAD
|  | 114 | 28.96 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  | LIVERMORE | 114 MP. 28.9575 JOB 8069196; LIEN 114 MP 28.96 LIVERMORE; ALAMEDA COUNTY TO VALVE 26.84
|  | 114 | 28.76 | 22 | Transmission | [10 empty] | Steel/Wrought Iron |  | LIVERMORE | 114 MP. 28.9598 JOB 8069196; LINE 114 MP28.96 LIVERMORE; ALAMEDA COUNTY TO VALVE 26.84
|  | 114 | 28.97 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | LIVERMORE | 114 MP. 28.97 BLOWDOWN JOB 8069196; DALTON AVE VALVE YARD. LIVERMORE; ALAMEDA COUNTY.
|  | 114 | 28.98 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  | LIVERMORE | LINE 114 STA. 1+71 ROUTH 114; MP 28.9800; ARNEST ST. & RAYMOND RD LIVERMORE
|  | 114 | 30.78 | [15 empty] | SOUND WALL TO BE BUILT OVER LINE 114
|  | 114 |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | 2" SAVE-A-VALVE INSTALLED NORTH OF V130. VALVE 85 REPLACEMENT PROJECT; BRENTWOOD GAS TERMINIAL BRENTWOOD; CONTRA COSTA COUNTY.
|  | 114 |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | (INSTALLED V-85) DIRSTRIC TRACY; 30604264-09 L-114; 24" V85 REPLACEMENT L-114. +/-58' N/O V130 TO +/- 69 N/O V130. BRENTWOOD GAS TERMINIAL; BRENTWOOD, CONTRA COSTA COUNTY; BRENTWOOD GAS TERMINAL BRENTWOOD; CONTRA COSTA COUNTY
|  | 114 |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | DISTRICT TRACY, 30604264-09 L-114; 2" GAUGE TAP INSTALLED SOUTH OF V16.59 VALVE 85 REPLACEMENT PROJECT,; BRENTWOOD GAS TERMINAL BRENTWOOD; CONTRA COSTA COUNTY
|  | 116 | 9.6 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 12" TIE-IN E/O MLV #9.60 W. CAPITOLA AVE. L-116 MP 9.80; 7038330-02
|  | 116 | 12.3762 | 16 | Transmission >= 20% SMYS | [10 empty] | Steel-Other |  | WEST SACRAMENTO | MAPPED 6/8, AR#4271493 L-114 MP.12.3762 (STA 211+68); ; LINE 116 STA. 211+68 MP. 12.3762; LATITUDE 38 32 24.73935 LONGITUDE -121 31 10.14869; SOUTH RIVER RD. WEST SACRAMENT; ; MISC. COMMENTS/INFORMATION: THIS SITE CONTAINED TAPE COATING THAT WAS IN EXCELLENT CONDITION, BUT DID HAVE THREE PATCHES PRESENT. UPON INSPECTION NO CORROSION WAS FOUND. PIPE WAS RECOATED WITH PROTAL 7200 AND THE EDGES WERE WAX TAPED TO IMPEDED THE TRANSITION FROM THE OLD TAPE COATING TO THE NEWLY APPLIED PROTALL 7200. CAD WELDS, WET REFERENCE CELL, AND COUPON WERE ALL INSTALLED AT THE D/S EDGE OF INSPECTION.
|  | 116 | 12.85 | [12 empty] | Steel/Wrought Iron |  |  | L-116 MP. 12.85 SO#7039486-01
| 06-55038- | 116 | 3.77 | 12.75 | Transmission |  | Body of Pipe |  |  |  |  | 2006-07-17 | 2006-07-19 | Other | INSTALLED (3) CLOCK SPRINGS | Steel/Wrought Iron |  | DAVIS | L-116, 3.77; INSTALLED (3) 12" CLOCK SPRINGS TO REPAIR 24" LONG GOUGE IN PIPE; A PG&E CONTRACTOR STRUCK AND DAMAGED 12" L-116 WHILE DIGGING A HOLE TO REPLACE AN EXISTING ROTTED POLE. THE TP. GAS LINE WAS NOT PROPERLLY MARKED, SO THE CONTRACTOR WILL NOT BE BILLED. THE AUGER CAUSED AA GOUGE IN 24" LONG @1:00 TO 2:30 O'CLOCK AREA ON THE PIPE. THE AUGER STRUCK THE 12" L-116 38' WEST OF THE PIPELINE MARKER ANGLE POINT. THERE WAS NO GAS LOSS.
|  | 118A | 60.2513 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | JOB # 30603843 L-118A MP 60.2513 NORTH TIE-IN LOCATION ; JOB #30603843 NORTH TIE-IN LOCATION L118A MERCED CAPACITY PROJECT
|  | 118 | 56.8479 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | JOB #30603843 L-118A MP. 56.8479 SOUTH TIE-IN LOCATION ; JOB #30603843 SOUTH TIE0IN LOCATION- L-118A MERCED CAPACITY PROJECT
|  | 118 | 22.0813 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 118A MP 22.0813 PM#30603674
|  | 118B | 18.4822 | 12 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party | [5 empty] | Steel/Wrought Iron |  | MADERA | SO#7048546, ROUTE 118B MP. 18.4822
|  | 118B | 18.5627 | 12 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party | [5 empty] | Steel/Wrought Iron |  | MADERA | SO#7048546, ROUTE 118B, MP. 18.5627
|  | 118B | 18.5615 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MADERA | SO# 70485546, ROUTE 118B, MP. 18.5615
|  |  | 18.5918 | 12 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party | [7 empty] | MADERA | SO# 7048546, ROUTE 118B, MP. 18.5918
|  |  | 30.3714 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | MADERA | SO# 7048546, ROUTE 118A, MP. 30.3714
|  |  | 30.3975 | 8.625 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party | [5 empty] | Steel/Wrought Iron |  | MADERA
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT= 118A MP 36.03 PM# 30603674
|  | 118B | 18.5568 | 12 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party | [7 empty] | MADERA | SO# 7048546, ROUTE 118B, MP. 18.5568
|  | 118 | 18.5644 | 8 | [8 empty] | 2003-09-03 | Other | GRIND OUT GOUGES IN 7' SECTION OF PL. | Steel/Wrought Iron |  | MADERA | SO# 7048546, ROUTE 118B, MP. 18.5644; L 118 12" 565' N/O LINE MARK N/O AVE 18 1/2 IN MADERA. ...AUSTIN HASTINGS HAD G.C. CREW...
|  | 118 | 30.7898 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-118A MP. 30.7898, YOSEMITE DIV. 706367-06; LINE 118A MADERA SOUTH OF AVE 18 1/2 AND DRY CREEK.
|  | 118A | 30.2701 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-118A MP 30.2701 YOSEMITE DIV. 7060367...; LINE 118A MADERA 615' S/E OF AVE 18 1/2
|  | 118A | 30.5942 | 8.625 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party | [7 empty] | MADERA | SO#7048546, ROUTE 118A, MP. 30.5942
| 03-55044-1 | 118A | 30.41 | 8.62 | Transmission |  | Body of Pipe |  |  | Digin |  | 2003-08-22 | 2003-08-23 | Replace TP Main |  | Steel/Wrought Iron |  | MADERA | SO#7048911-03, RT 118A, M.P. 30.40; REPLACED 51FT. L-118
|  |  |  | 6 | Distribution Main | [12 empty] | LIVINGSTON | SO#7058370, STUB TAP OFF 118-1, MP 0.00
|  | 118A | 30.5131 | 8.25 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party | [7 empty] | MADERA | SO#7048546, ROUTE 118A, M.P. 30.5131
|  |  | 118A & 118B | 08.00 & 12.00 | Transmission | [10 empty] | Steel/Wrought Iron |  | MADERA | L-118A L-118B } SEE BACK FOR MILE POINTS; MAP 3771-C3 ALL MEASUREMENTS MADE BY PROBING
|  | 118A & 118B |  | 08.00 & 12.00 | Transmission | [10 empty] | Steel/Wrought Iron |  | MADERA | L118A, L118B } SEE BACK FOR MILEPOINTS; LINE 118 ALL MEASUREMENTS MADE BY PROBING MAP 3771-CS
| 98-55041-1 | 118 | 15.1 | 12 | Transmission |  | Body of Pipe |  |  | Digin |  | 1998-10-30 | 1998-10-30 |  |  | Steel/Wrought Iron |  | MADERA | L-118B, MP. 15.1; C/O AND REPLACED 8' OF 12" STL PIPE
|  | 118B | 27.15 | [12 empty] | Steel/Wrought Iron |  | CHOWCHILLA | L-118B MP 27.15 SO# 7036870-01
| 02-55001- | 118 | 30.22 | 12.75 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party | DIG IN | 2002-01-24 | 2002-01-24 | Replace TP Main |  | Steel/Wrought Iron |  | CHOWCHILLA | REPLACE 15' OF 12" STEEL PIPE
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | MADERA | 118A MP. 18.6141 JOB 30470934
|  | 118 | 83.7 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | TURLOCK | L-118 MP 83.70 PM# 30603845
|  | 118A | 17.06 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | HILMAR/TURLOCK | L-118A, MP 17.06, 30603842 ;
|  | 118 | 70.35 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SOUTH TIE-IN. DIV: YOSEMITE, 7043587-05, L-118A MP 70.3557
|  | 118 | 72.3 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIV: YOSEMITE. NORTH TIE-IN. 7043587-05 L-118A MP 72.3275
|  | 118 | 54.7414 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | MERCED | DOV: YOSEMITE L-118A MP. 54.7414 PM# 32048353-06
|  | 118A | 77.2242 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIVISION YOSEMITE SO#7055765-07 L-118A, MP 77.2242 (EAST END TIE-IN); INSTALLED 16" STL. MAIM. TIE-IN W/8" BOTTOM TAP
|  | 118A | 0.2302 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | ATWATER | GM#30603958 ROUTE= L-118A-2, MP. 0.2302
|  | 118 | 78.1108 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIV: YOSEMITE (WEST END TIE-IN) SO# 7055765-07 L-118 0, MP. 78.1108; INSTALLED 16" STL. MAIN. TIE IN W/8" BOTTOM TAP
|  | 118 | 20.58 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM 30657859, ROUTE 118B, MP. 20.58
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | MADERA | 118B M.P. 5.9154 JOB 30470934
|  |  |  | 2 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIVISION SACRAMENT; RT= 119B, M.P. 3.13 STUB 8780 MP. 0.0011; STUB 8782 M.P. 0.0010; SO# 871577-06
|  | 119A | 0.0583 | [12 empty] | Steel/Wrought Iron |  |  | A FORM FILE JOB#7049546 L-119A M.P. 0.0583; INSTALLED 1 1/4" SERV. TO GAS STATION.
|  | 119A | 3.87 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 12" TIE IN E/O SWINGLE JUNCTION. 119A MP. 3.87 7038330-02
|  | 119A | 92.2977 |  | Transmission >= 20% SMYS | [7 empty] | 2011-05-31 |  |  | Steel-Other |  |  | AR#42711770; GROUND OUT MACANIL DAMAGGE & MAGED & UT PIPE; ; ; LINE 119A ROUTE 119 A STA. 23+56 M.P. 92.2977; LATITUDE 38 34 44.51158 LONGITUDE -121 34 15.04938; ; MISC COMMENTS/INFORMATION: THIS ISTE CONTAINED THIN HAA COATING THAT WAS SLIGHTLY DISBONDED AND MISSING IN ONE AREA. UPON INSPECTION NO CORROSION WAS FOUND BUT THERE WAS AN AREA OF MECHANICAL DAMAGE PRESENT. THE DEEPEST SECTION MEASURED 0.038" WITH A PIT GAUGE, 12.61% (0.038"/0.3125" NOMINAL WALL X 100=12.61%). THE AREA WAS BUFFED OUT AND AFTERWARD THE MINIMAL WALL REMAINING WAS 0.266" MEASURED WITH A UT GAUGE (ORIGINAL LOCAL WALL THICKNESS WAS 0.301"). THE PIPE WAS RECOATED WITH PROTAL 7200 AND THE EDGES WERE WAX TAPED TO IMPEDE THE TRANSITION OF THE EXISITNG HAA COATING TO THE NEWLY APPLIED PROTA 7200. CAD WELDS, A WET REFERENCE CELL, AND A COUPON WERE ALL INSTALLED AT THE D/S EDGE OF THE INSPECTION. SAND WAS PLACED AROUND THE PIPE AND THE REMAINDER OF THE SITE WAS BACKFILLED WITH NATIVE SOIL.
|  | 119A | 9.67 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 12" TIE-IN W/O ,LV#9.68 ROADWAY YARD. L-119A M.P. 9.67 7038330-02
|  | 119A | 9.69 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 12" TIE-IN E/O MLV# 9.68 ROADWAY YARD. 119a M.P. 9.69 703833-02
|  | 119 | 10.64 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | TIE-IN @CHP ACADEMY L-119A M.P. 10.64 703330-02
|  | 119A | 11.55 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | TIE-IN 10" BRIAR GARDEN HWY. 119A 11.85 7038330-02
|  | 119A | 11.36 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 119A M.P. 11.36 PIECED TO REPLACE 11.35 & 11.36 GARDEN HWY 7038330-02
|  | 119A | 11.37 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | TIE-IN 10" BRIAR @ 12" MAIN GARDEN HWY; 119A M.P. 11.37 7038330-02
|  | 119A |  | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 12" TIE-IN SAFFLOWER FIELD 119A M.P.... 7038330-02
|  | 119A | 11.7 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 16" TIE IN @ SADDLOWER FIELD, 119A MP. 11.70, 7038330-02
|  | 119A |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 16" TIE-IN I-80 SOUNDWALL 119A MP....7038330-02
|  | 119A | 11.91 | 20 | [11 empty] | Steel/Wrought Iron |  |  | 20" TIE-IN I-80 SOUNDWALL 119A M.P. 11.91, 7038330-02
|  | 119A | 13.13 & 13.12 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | TIE-IN @ W. RUMANIO AVE E/O ORCHARD WAY, MATUMAS CANAL, 119A M.P. 13.13 & 13.12
|  |  | 14.04 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#7038709, ROUTE 119A (ABANDONED) M.P. 14.04
|  |  | 14.05 | 20 | [11 empty] | Steel/Wrought Iron |  |  | SO#7038709, ROUTE 119A, M.P. 14.05
|  |  | 14.48 | 12 | Transmission | [13 empty] | 119A M.P. 14.48 SO# 7038567-01
|  |  | 16.43 | 12.75 | Transmission | [13 empty] | SO# 7038709, ROUTE: 119A (N. SACRAMENTO UGIS), M.P. 16.43
|  | 119 | 11.7 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7051425 ROUTE 119A, M.P. 11.7092; TIE-IN NEW 20" TP TO EXISTING 16"
|  | 119 | 11.07 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | TIE IN NEW 20" TO EXISTING 20" T.P.
|  | 120 |  | 4 | Gathering | [7 empty] | 2004-12-15 |  |  | Other | X42 | W/ SUTTER | SO#7046766-04 STUB7915 (L-120-1) GMER; ABANDONMENT BC 77
|  | 120 | 0 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RETIRE SUTTER CREEK VALLEY LOT. INSTALLED 16'4" 4" TO TIELINE 120 TO FEED CUSTOMERS ON WYNCOOP RD.
|  | 120 | 1.3818 | 4 | [11 empty] | Steel/Wrought Iron |  |  | RETIRE KIONE MASTER METER. ABANDON 6" LINE 120 FROM CORNER OF WYNCOOP RD + SOUTH BUTTE RD TO KIONE MASTER METER.
|  | 121 | 3.52 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  | SUTTER
|  | 121 | 4.69 | 6.625 | Transmission | [7 empty] | 2002-04-05 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  |  | SUTTER COUNTY 5 MILES WEST OF YUBA CITY. SEE ATTACHED MP.
|  | 121 | 4.4719 | [15 empty] | ABANDONED SECTION OF 6" L-121.
|  | 121 | 4.9134 | [15 empty] | ABANDON SECTION L-121; NEW 6" LINE 121; INSPECTION SITE APPROX 416' WEST OF HUMPHREY ROAD L-121 LOCATED IN RICE FIELD
|  | 123 | 1.8894 | [15 empty] | EXCAVATED LINE FOR INSTALLATION OF STOP PLUG COATING GOOD LOW COVER 40". 617+00.
|  | 123 | 2.1123 | [15 empty] | EXISTING LINE HAS BEEN BLASTED + COATED WITH PROTOL. WAX COATED AT EXISTING COVER. LOW COVER 27". 606 + 07.
|  | 123 | 2.5329 | [12 empty] | Steel/Wrought Iron |  |  | EVACUATED LINE FOR TIE-IN COATING GOOD LOW COVER 40". 584 + 04.
|  | 123 | 13.7445 | 12 | Transmission |  | Other |  | NO LEAK |  |  |  | 2010-02-23 | Other | USED GRINDER TO FEATHER OUT GOUGES AND MAGNAFLUXED. | Steel/Wrought Iron |  |  | BACKHOE WAS DIGGING SHORT TRENCH FOR TIE-IN PIECE AND CAME IN CONTACT WTIH 12' LINE, PUTTING 3 SMALL GOUGES IN PIPE. PIPELINE ENGINEER WAS CONTACTED. TO FIX IT WE GROUND DOWN GOUGES SMOOTH AND MAGNAFLUXED PIPE THEN WRAPPED. WRAPPED OUT FROM DIGGING ... HOLE. PIPE WAS EXPOSED 10' AWAY.
|  | 123 | 0.04 | 16 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 123 | 1.06 | [12 empty] | Steel/Wrought Iron |  |  | TIE-IN POINT; INSPECTION POINT
|  | 123 | 1.06 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | INSTALLED 16: ST.; INSPECTION POINT
|  | 123 | 1.63 | 12.75" | [11 empty] | Steel/Wrought Iron |  |  | 12.750" O.D. API SL GRD B. SMLS; TIE-IN; INSPECTION POINT
|  | 123 | 3.2582 | [12 empty] | Steel/Wrought Iron
|  | 123 | 3.42 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | ROSEVILLE | TIE IN FOR NEW LINE TO POWER PLANT.; BASELINE REG STATION; TIE IN ONLLY
|  | 123 | 4.32 | 3.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | ROSEVILLE | INSIDE STATION OD0822-03
|  | 123 | 3.4959 | [12 empty] | Steel/Wrought Iron
|  | 123 | 3.4702 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | ROSEVILLE | BASELINE REG. STA.
|  | 123 | 6.8435 | 12 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 123 | 6.4732 | 12 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 123 | 9.4751 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | COMPLETED BY DON STEWART FOR RICK SUMMERS.
|  | 123 | 9.5268 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | COMPLETED BY DON STEWART FOR RICK SUMMERS
|  | 123 | 11.03 | [15 empty] | MP 11.04 TIE IN
|  | 123 | 11.58 | [15 empty] | MP 11.59 TIE IN
|  | 123 | 12.33 | 12 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party | DIG-IN | 2002-10-18 | 2002-10-21 | Other | BUFF + REWRAP | Steel/Wrought Iron |  |  | TRANSMISSION ON STAND BY; NO LEAK - MINOR SCRATCH IN T.P. MAIN.; BUFFED SCRATCH + REWRAPPED; GOUGE SANDED OUT WITH A GRIT 60 SANDING DISC TO A TOTAL DEPTH 0.045. DAMAGE AREA INSPECTED BY MAG. PANTIDE AND FOUND IN SOUND CONDITION. GTK 11/7/02
|  | 123 | 11.5596 | 16 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 123 | 12.0167 | 16 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 123 | 12.0118 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | LINCOLN
|  | 123 | 12.6329 | 16 | Transmission | [12 empty] | LINCOLN
|  | 123 | 12.7756 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 16" RELOCATE EAST END.
|  | 123 | 12.5772 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 16" RELOCATE WEST END.
|  | 123 | 1.739 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | ROSEVILLE
|  | 123 | 4.1168 | 12 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 123 | 1.864 | 12 | [11 empty] | Steel/Wrought Iron |  |  | INSTALLED 2" VALVE TEE ON 12" LINE 123.
|  | 123 |  | 2 | [11 empty] | Steel/Wrought Iron |  |  | INSTALLED 2" MUELLER H17161 PCF ON 2" EXISTING FEED TO INCREASE FLOW.
|  | 123 | 1.0484 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SITE CONTAINED A 45-DEGREE BEN WITH TWO GIRTHWELDS. GW#1 WAS 2'11" FROM THE U/S EDGE AT 4286811.625M(NORTHING) AND 644999.109M (EASTING), WHILE GW#2 WAS 4'6" FROM THE U/S EDGE AT 4286810.853M (NORTHING) AND 645000.177 (EASTING). THE BEND CONTAINED OLD WAX TAPE COATING WITH A PROTECTIVE ROCKGUARD LAYER THAT HAD A PLASTIC BACKING WHICH HAD BEEN INFRINGED BY SMALL ROOTS, WHILE THE REMAINDER OF THE STRAIGHT PIPE HAD FBE COATING ATTACHED. ONLY THE WAX TAPED PORTION OF THE ANGLE POINT WAS REMOVED AND INSPECTED PER MIKE WEST; THE REMAINING FBE COATING WAS HOLIDAY TESTED USING A COIL AT 2,500 VOLTS AND ANY VOIDS WERE REPAIRED WITH PROTAL 7200. NO CORROSION OR MECHANICAL DAMAMGE WAS FOUND ON THE ANGLE POINT, AND A UT GRID WAS COMPLETED AT THE 6:00 POSITION. THE ANGLE POINT WAS RECOATED WITH PROTAL 7200 AND A COUPON AND REFERENCE CELL WERE INSTALLED AT THE BEND.
|  | 124B | 5.97 | 16 | [11 empty] | Steel/Wrought Iron |  |  | JOB # 30604279. LINE 124B CAL TRANS HWY 65 BY-PASS RELOCATION.; EAST TIE-IN AREA
|  | 124A | 7.0702 | 16 | [11 empty] | Steel/Wrought Iron
|  | 124A | 6.9 | 16 | [11 empty] | Steel/Wrought Iron
|  | 124B | 6.33 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | SHERIDAN | RHMO 30604279 7/18/08. 8" LINE 124 RELOCATION CAL TRANS HWY 65 PROJECT. SHERIDAN, CA.
|  | 124B | 6.7 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | SHERIDAN | RHMO 30604279 7/18/08. 8" LINE 124 RELOCATION CAL TRANS HWY 65 PROJECT. SHERIDAN, CA.
|  | 124A | 6.01 | 16 | Transmission | [12 empty] | SHERIDAN | RHMO 30604279 7/18/08. 8" LINE 124 RELOCATION CAL TRANS HWY 65 PROJECT. SHERIDAN, CA.
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | SHERIDAN | JOB #30604279 16" LINE 124B. CAL TRANS HWY 65 BYPASS RELOCATION.
|  | 124A | 20.64 |  | Transmission | [10 empty] | Steel/Wrought Iron
|  | 124B | 1.02 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SOUTH FITTING
|  | 124B | 0.0256 | 8 | Transmission | [6 empty] | 2004-07-23 |  |  |  | Steel/Wrought Iron |  | LINCOLN | REMOVING DIRT AND PAVEMENT FOR CONSTRUCTION OF TURN LANES. EXCAVATION 24" DEEP. CONCRETE CAP INSTALLED.
|  | 124A | 0.2415 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | JOB 8065400. 80' PIPE RECOATED WITH EXPOXY - 3 COATS. CWGRIP 235.
|  | 124B | 0.85 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  | LINCOLN | NORTH FITTING
|  | 124A-1 | 22.98 | 12.75 | Transmission
|  | 124B | 5.92 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | SHERIDAN | JOB #30604279 LINE 124A CAL TRANS HWY 65 BY PASS RELOCATION. SHERIDAN, CA.
|  | 124B | 7.0302 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | SHERIDAN | JOB #30604279 LINE 124A CAL TRANS HWY 65 BY PASS RELOCATION. SHERIDAN, CA.
| 06-30038-1 | 126B | 4.13 | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2006-12-22 | 2006-12-22 | Other | PLETCO CLAMP | Steel/Wrought Iron |  | EUREKA | INSTALL 4" PLETCO CLAMP; INSTALLED 4" PLETCO CLAMP. INSTALLED EM MARKER.
| 06-20001-1 | 200B3-3 | 0.1486 | 12 |  |  | Drip |  |  |  |  | 2006-02-06 | 2006-02-10 | Other | REMOVE DRIP | Steel/Wrought Iron |  | RIO VISTA | REPAIRS WERE MADE BY REMOVING DRIP SVM @ LEAK LOCATION. COVER @ FLANGE IS 30"...
| 06-17401-1 | 174 |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2006-05-08 | 2006-05-23 | Other | CUT AT CAP | Other | X42 | ARBUCKLE | SUSPECT INTERNAL CORROSION; CUT + CAPPED 3" STUB.
| 06-19503-1 |  |  | 10 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2006-04-17 | 2006-04-26 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | ISLETON
| 06-19504-1 | 195 | 0.32 | 6 |  |  | Body of Pipe |  |  | Internal Corrosion |  | 2006-04-26 | 2006-05-01 | Other | PLIDCO LEAK CLAMP | Steel-Other |  | RIO VISTA | REPAIRED LEAK USING A 6" PLIDCO CLAMP.
| 06-40001-1 | 400 | 149.19 |  |  |  | Valves |  |  | Other | STEM SEAL | 2006-06-07 |  |  |  | Steel/Wrought Iron |  | GERBER
| 09-40008-1 | 400 | 149.19 |  |  |  | Valves |  |  | Other | STEM SEAL | 2006-06-07 |  |  |  | Steel/Wrought Iron |  | GERBER | LEAK NUMBER 09-40008-1 <- CHANGE TO 06-40001-1
| 09-40008-1 | 400 | 149.19 |  |  |  | Valves |  |  | Other | STEM SEAL | 2006-06-07 |  |  |  | Steel/Wrought Iron |  | GERBER
| 06-30401-1 | 304 | 3.11 | 12 | Gathering |  | Valves |  |  |  |  | 2006-04-06 | 2008-12-09 | Other | REPLACE GREASE STE. |  |  | TRACY | L-304, M.P. 3.11 VALVE V-A; NOT COMPL'D '06, EXPECTED SOMEONE TO GRA...
| 06-30401-1 | 304 | 3.11 | 12 | Gathering |  | Valves |  |  |  |  | 2006-04-06 | [5 empty] | TRACY | LINE 304 M.P. 3.11 VALVE LOT VALVE "A"; WAS NOT COMPLETED IN '06. THEY EXPECTED SOMEONE ELSE TO GRADE LEAK-(SUPERVISOR, ENGINEER); 5.4.10. DOWNGRADE CRITERIA IS NOT CLEAR TO TRACY DISTRICT.
| 06-30401-1 | 304 | 3.11 | 12 | Gathering |  | Valves |  |  |  |  | 2006-04-06 | [5 empty] | TRACY | LINE 304 M.P. 3.11 VALVE LOT VALVE "A"
| 06-19502-1 | 195 | 0 | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2006-04-08 | 2006-04-25 | Other | PLIECO LEAK CLAMP |  |  | ISLETON | REPAIRED LEAK USING A 8" PLIECO LEAK CLAMP.; INSTALLED 8" PLIDCO LEAK CLAMO SER# 2586903B
| 06-19501-1 | 195 | 0.3199 | 6 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2006-02-16 | 2006-03-08 | Other | PLIECO LEAK CLAMP | Steel/Wrought Iron |  | RIO VISTA | INSTALLED 6" PLIDCO LEAK CLAMP.
| 06-16801-1 | 195 | 0.3584 | 6 |  |  | Body of Pipe |  |  |  |  | 2006-01-09 | 2006-02-23 |  |  | Steel/Wrought Iron |  | ISLETON | INSTALLED LEAK CLAMP; INST. 6" PLIDCO CLAMP.
| 06-30029-1 | 12L177 | 124.9 | 12 | Transmission |  | Body of Pipe |  |  | Construction Defect |  | 2006-08-19 | 2006-08-19 | Other |  | Steel/Wrought Iron |  | MAD RIVER | LEAK ON 12L177; SHUT DOWN LINE (REPLACED 16' 12" ON 08/12; SOAP @ VISUAL GC AREA 7 WELDED PIPE.
| 06-30202-1 | 302-023 | 0.16 | 6.25 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2006-05-30 | 2006-09-27 | Weld Over Sleeve or Can |  | Other | X52 | GRIMES | BUBBLES IN RICE FIELD REPORTED BY VINTAGE; INSTALLED 28" OF .280 WT PIPE.
| 06-30201-1 | 302-095 | 4.67 |  | Gathering | [6 empty] | 2006-01-09 | 2006-01-13 | Tighten Cap or Bolt |  |  |  | GRIMES | AREA FLOODED - BUBBLES NEAR V-402 AND ALCOHOL POT BOX. 2-LEAK REPAIRED - CAP ON GAUGE LINE - PLUG ON ALCOHOL POT; RAY - LEAK #06-30201-1 L-302 NEAR V-402 - REPAIRED BY TIGHTENING CAP + PLUG ONLY.
| 05-16901-1 | 169 | 5.1 | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2005-04-11 | 2005-04-23 | Other | WELDED NEW PIPE SECTION |  |  | E/O WILLOWS | CUT OUT = REPLACED 179' OF 16" L-169
| 05-10039-1 |  |  |  | Transmission |  |  |  |  | Material Failure |  | 2005-05-26 | 2005-05-26 | Replace Valve < 2 inch |  |  |  | SANTA CRUZ | @ VALVE B-18-1; REPLACED WITH NEW VALVE @ V-18-1; SEE ATTACHMENT
| 05-40013-1 | 2402-1 | 2.4106 | 0.75 | Transmission |  | Body of Pipe |  |  | External Corrosion | ATMOSPHERIC CORROSION | 2005-03-28 | 2005-03-31 | Other | DFM | Steel/Wrought Iron |  | HAYWARD | INTERSECTED OF WATKINS & C ST. HAYWARD. VALVE FRAME & COVER LEAKING; CUT OFF GAUGE TAP; SOAP TESTED REPAIR WELD.
| 05-20001-1 | 200 | 0.7647 | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2005-01-18 | 2005-03-11 | Mechanical Repair Fitting - Fitting |  |  |  | RIO VISTA | BUBBLES IN FIELD; INSTALLED PLIDCO LEAK CLAMP; INSTALLED 8" PLIDCO LEAK CLAMP SERIAL # 2271450. MAOP 1000 PSI VITON SEALS. PRODUCT P55.
| 05-30046 | 125 |  | 12 | Transmission |  | Drip |  |  | External Corrosion |  | 2005-11-08 | 2005-11-09 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | FORTUNA | INSTALLED 12" REPAIR SLEEVE OVER CORROSION LEAK.
| 05-10017-1 | 126B | 4.97 | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  |  | 2007-02-15 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | EUREKA | INSTALLED 4" T.P. CLAMP.
| 05-30012- | 125 |  | 6 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2005-03-26 | 2005-04-02 | Other | BLEW DOWN PIPE | Steel/Wrought Iron |  | FORTUNA | FOUND LEAK ON T.P. L125 AT BYPASS STATION. INSTALLED 6" PLIDCO CLAMP; FOUND LEAK ON BOTTOM OF 6" T.P.
| 05-40001-1 | 401 | 197.8 | [8 empty] | 2005-06-24 | 2006-05-05 |  |  |  |  | MAXWELL | PRIMARY SEAL - GOV - 1B REPAIRED. NOTHING FOUND OR DETECT. NO LEAK DETECTED. LEAK IS UNDETECTABLE AT THIS TIME. VALVE WAS INSTALLED + SEAL GREASED.
| 05-40001-1 | 401 | 197.8 | [8 empty] | 2005-06-24 | 2006-05-05 |  |  |  |  | DELEVAN | LEAK IS UNDETECTABLE AT THIS TIME. VALVE WAS INSTALLED + SEAL GREASED.
| 05-40101-1 | 401 |  | 0.75 | Transmission |  | Valves |  |  | Other | LOOSE UNIONS | 2005-06-23 | 2005-07-16 | Tighten Cap or Bolt |  |  |  | DUNNIGAN | SMALL LEAKS ON MARPAC UNION TYPE VALVES. REPAIRED BY TIGHTENED UNIONS ON VALVES.
| 05-40101-1 | 401 | 233.89 | 0.75 | Transmission |  | Valves |  |  | Unknown |  | 2005-06-23 | [5 empty] | DUNNIGAN | SMALL LEAKS ON MARPAC UNION TYPE VALVES.
| 05-40101-1 | 401 | 283.89 | 0.75 | Transmission |  | Valves |  |  | Unknown |  | 2005-06-23 | [5 empty] | DUNNIGAN | SMALL LEAKS ON MARPAC UNION TYPE VALVES.
| 05-30202-1 | 302-224 | 0.2454 | 6 | Gathering | SERVICE |  |  |  | Internal Corrosion | SUSPECT | 2005-11-28 | 2005-12-08 | Other | NEW PIPE |  |  | MERIDIAN | BUBBLES NEAR GAS WELL PAD; SEE DRAWING
| 05-30201-1 | 302-217 | 1.9209 | 8 | Gathering |  | Body of Pipe |  |  | Damage by 3rd Party |  | 2005-04-17 | 2005-04-26 | Other | SAVE-A-VALVE |  |  | SUTTER | BULLET HOLE IN PIPE BETWEEM WELL BU#56 AND BU#60. ISOLATED AND BLOWN DOWN UNTIL REPAIRS ARE MADE.; WELDED SAVE-A-VALVE OVER BULLET HOLE CASE #1-05-001198 SUTTER CO. SHERIFF.
| 05-20004-1 | 200B1-1 | 1.2768 | 6 | Gathering |  | Body of Pipe |  |  | Damage by 3rd Party | DIG-IN | 2005-10-06 | 2005-10-07 | Welded Sleeve/Can - Weld |  |  |  | RIO VISTA | CONTRACTOR HIT 6" L-200 WITH RIPPER. INSTALLED 51" CAN.
| 05-20002-1 | 200A3-7 | 0.0066 | 6 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2005-02-16 | 2005-02-17 | ABANDON |  |  |  | RIO VISTA | 6" L-200 NEAR...; GPS FILE: 6 IN L-200 LEAK .SSF.
| 05-19501-1 | 195 | 0.4376 | 10.75 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2005-05-31 | 2005-06-27 | Welded Sleeve/Can - Weld |  |  |  | RIO VISTA | INSTALLED REPAIR SLEEVE; INSTALLED 10" REPAIR SLEEVE.
| 05-05701-1 | 57A | 6.37 | 18 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2005-01-04 | 2005-01-05 | Welded Sleeve/Can - Weld |  |  |  | DISCOVER BAY | WELDED 18" X 24" X .375, X50 SMYS REPAIR SLEEVE.
| 05-00207-1 |  | 6.2852 | 6 | Transmission |  | Body of Pipe |  |  | Digin |  | 2005-08-10 | 2005-08-10 | Other | REPLACED C/O TRANS. MAIN | Steel/Wrought Iron |  | YUBA | REPLACE 42" OF 6" STEEL PIPE.
| 05-00002-1 | 153 |  | 4 | Transmission |  | Valves |  |  |  |  | 2005-10-20 | 2005-12-06 | Other | GREASED & WORKED VALVE. | Steel/Wrought Iron |  | HAYWARD | EXCAVATED VALVE, WORKED & GREASED, LEAK WAS CORRECTED
| 05-00002-1 | [10 empty] | 2005-10-20 | [5 empty] | HAYWARD
| 05-10012-1 | 137A | 2.75 | 6 | Transmission |  | Other Welds |  |  | Construction Defect | OTHER- CRACK ON WELD | 2005-09-12 | 2006-02-15 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | EUREKA | WELDED 6" CAN + REWRAPPED MAIN; FOUND LEAK ON WELD (BOTTOM OF 6" PIPE) REPAIRS MADE W/12" CAN + X-RAYER.
| 05-50089-1 | 103 | 19.1733 | 12 | Transmission |  | Body of Pipe |  |  |  |  | 2005-11-19 | 2005-11-20 | Replaced TP Main |  | Steel/Wrought Iron |  | SALINAS | REPLACED 9' OF TP MAIN 12" SM/S; CUST DUG INTO 12' TP LINE WHILE RIPPING FIELD. DID NOT CALL USA.; SEE ATTACHED TEST DATA
|  |  | 16.35 | 10 | Transmission |  | Other |  | GIRTH WELD |  |  | 2005-09-28 | 2005-10-01 | Deactivate #TP Main | REPLACE TP MAIN | Steel/Wrought Iron |  | FOLSOM | REPLACED 120' OF 10" - 250 WALL X 52 - REPLACED 4' - 237 WALL GD B SMTS 10'
| 04-30201-1 | 302E | 3.073 | 8 | Transmission |  |  |  |  | Internal Corrosion | SUSPECT | 2004-10-21 | 2004-10-28 | Mechanical Repair Fitting - Fitting |  |  |  | SUTTER/ YUBA CITY | CALPINE EE SUSPECT PG+E L-302 OF LEAK NEAR CANAL - PG+E VERIFIED WITH FLAME PACK UNIT.; INSTALL 5" LEAK CLAMP.
| 04-30201-1 | 302E | 3.073 | 8 | Transmission |  |  |  |  | Internal Corrosion | SUSPECT | 2004-10-21 | [5 empty] | SUTTER/ YUBA CITY
| 04-19501-1 | 195 | 0.3993 | 6 | Gathering |  | Body of Pipe |  |  | Unknown |  | 2004-02-16 | 2004-03-10 | Mechanical Repair Fitting - Fitting |  |  |  | RIO VISTA | GAS BUBBLING IN DITCH.; INSTALLED 6" LEAK CLAMP; PLIDCO LEAK CLAMP SCR #2392620 MAOP 1000 PSI.
|  |  |  | 6.625 | [5 empty] | Internal Corrosion |  |  | 2004-03-10 |  |  | Steel/Wrought Iron |  |  | INSTALLED PLIDCO CLAMP SERIAL #2392620 MAOP 1000 PSI IN CENTER OF DITCH. GPS FILE # R042213A.
| 04-19001-1 | 190 | 16.08 | 16 | Transmission |  | Fitting |  |  | Construction Defect |  | 2004-05-04 | 2004-06-23 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | COALINGA | INSTALLED 4" PIPE W/ CAP OVER 3/4" GAUGE LINE VALVE. REPAIR SMALL GAS LEAK FROM THREADED GAUGE LINE. INSTALLED 4" PIPE W/ CAP OVER OLD GAUGE LINE AND RELOCATED 3/4" GAUGE LINE CLOSER TO V-16.08.
| 04-12801-1 | 128 | 13.98 | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2004-10-14 | 2004-10-18 | Other | CAN |  |  | WILLOWS | EMPLOYEE FOUND LEAK WHEN LOCATING GAS LINE FOR FARMER - DEAD VEGETATION.; REPLACED WITH 5 FT OF PRETESTED PIPE;
| 04-12801-1 |  |  | 4 | Transmission |  |  |  |  | Internal Corrosion |  |  | 2004-10-18 | Replace TP Main |  | Steel/Wrought Iron |  |  | REPLACED WITH 5' OF TESTED 4.500 X .237 BR B SMLS.
| 04-30001- | 125 |  | 6 | Transmission |  |  |  |  | Internal Corrosion |  |  | 2004-01-13 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | FORTUNA | NORTH COAST DIVISION LEAK.
| 04-30001-1 |  |  | 6 | Gathering |  | Unknown |  |  | Unknown |  | 2004-01-01 | 2004-01-10 | Other | CLOSED VALVE | Steel/Wrought Iron |  | FORTUNA | BUBBLES. CLOSED VALVES 36, 32, 112, 72, 29, 825.
| 04-30140-1 | [10 empty] | 2004-08-20 | [5 empty] | PALO ALTO | AFORM REMOVED ON GA MAP. LEAK IS ON PALO ALTO DISTRIBUTION SYSTEM. SEE NOTE.
| 04-30140-1 | 109 | 12.4168 | [8 empty] | 2004-08-20 | [5 empty] | PALO ALTO
| 04-30140-1 | [10 empty] | 2004-08-20 | [5 empty] | PALO ALTO | FLAME PACKED ALL OF LINE 109 IN INTERSECTION OF ARASTRADERO & MCKELLAR AND NO GAS WAS FOUND. 14' SOUTH OF TRANS LINE IS PALO ALTO DISTRIBUTION VALVE. ONLY GAS FOUND WAS IN FRAME AND COVER. PULLED COVER & VERIFIED LEAK WITH LEAK SOAP. BILL LAKE WILL CONTACT CITY OF PALO ALTO TO MAKE THEM AWARE THAT LEAK IS ON THEIR FACILITY.
| 04-30140-1 | [10 empty] | 2004-08-20 | [5 empty] | PALO ALTO | OVER MAIN IN INTERSECTION
| 04-26135-1 | DANV. FEEDER | 4.72 | 8 | Transmission |  | Fitting |  |  | Construction Defect |  | 2004-09-28 | 2006-03-23 | Tighten Cap or Bolt | OTHER=NEW GASKET | Steel/Wrought Iron |  | ALAMO | INSTALLED NEW GASKET IN PCV + TIGHTENED BOLTS.
| 04-40101-1 | 400 |  | 36 | Transmission |  | Fitting | Valves |  |  |  | 2001-05-04 | [5 empty] | BURNEY | L-400 LEAK IS LOCATED IN GRAVEL AROUND VLV.
| 04-40101-1 | 400 | 24.6 | [8 empty] | 2004-05-04 | [5 empty] | BURNEY | L-400, VALVE 1
| 04-40101-1 | 400 | 24.6 | 34 | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2004-05-04 | 2009-09-14 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | BURNEY | TRANSITION COATING NEEDED. GPS N 41.64919 W 121.31688.
| 04-20002-1 | 200 |  | 4 | Gathering |  | Body of Pipe |  |  | Digin |  | 2004-07-13 | 2004-07-13 | ABANDON |  |  |  | RIO VISTA | LINE RETIRED. POSSIBLY K-11, K-15, K-16, K-20 VALVE LOT.
| 04-19301-1 | 193-018 | 0.4993 | 6.625 | Gathering |  | Unknown |  |  | Unknown |  | 2004-02-24 | 2004-03-23 | Other | LEAK SECTION |  |  | ORLAND | FLOODED RANGE LAND (SMALL BUBBLES). CUT & CAPPED LEAK SECTION SO #7050695. LEAK SECTION RETIRED. C/O 6"AT READ 7 TO RETIRE #12-1 LEAK; LEAK SECTION = CUT, CAPPED, PIGGED OUT, INERTED AND RETIRED. DID NOT EXCAVATE FLOODED FIELD TO PERFORM LEAK INSPECTION C3; UPRATED 6" TO TP PRESSURE TO FEED HIGH-HIGH SET. INSTALLED 1" VALVE TEE.
| 04-40101-1 | 400 | 24.6 | 34 | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2004-05-04 | 2009-09-14 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | BURNEY | TRANSITION COATING NEEDED. GPS N 41.64919 W 121.31688
| 04-40101-1 | [10 empty] | 2004-05-04 | [5 empty] | BURNEY
| 04-40101-1 | 400 | 24.6 | [8 empty] | 2004-05-04 | [5 empty] | BURNEY | L-400, VALVE 1
| 04-40101-1 | 400 | 24.6 | [8 empty] | 2004-05-04 | [5 empty] | BURNEY | L-400, VALVE 1
| 04-40101-1 | 400 | 24.6 | [8 empty] | 2004-05-04 | [5 empty] | BURNEY | L-400, VALVE 1
| 04-40101-1 | 400 | 24.6 | [8 empty] | 2004-05-04 | [5 empty] | BURNEY | LEAK SAME AS 01-40004-4, 04-40101-1. ASSIGNED NEW LEAK # 04-40101-1. ORIGINAL LEAK # WAS 01-40004-1 ??
| 04-40101-1 | 400 |  | 36 | Transmission |  | Fitting | Valves |  |  |  | 2004-05-04 | [5 empty] | BURNEY | LEAK IS LOCATED IN GRAVEL AROUND VLV.
| 04-40101-1 | 400 | 24.6 | [8 empty] | 2004-05-04 | [5 empty] | BURNEY
| 04-40101-1 | 400 | 24.6 | [8 empty] | 2004-05-04 | [5 empty] | BURNEY
| 04-40101-1 | 401 | 24.61 | 36 | Transmission |  | Fitting | Valves |  |  |  | 2004-05-04 | [5 empty] | BURNEY | LEAK IS LOCATED IN GRAVEL AROUND VLV.
| 01-40004-1 | 400 | 24.6 | 20 | Transmission |  | Valves |  |  | Unknown |  | 2002-05-05 | [6 empty] | VALVE 1 LOCATED IN GRAVEL AROUND VLV.
| 01-40004-1 | 400 | 24.6 |  | Transmission |  | Valves |  |  | Unknown |  | 2001-04-16 | [6 empty] | 01-4010119-1; VALVE 1
| 04-40001-1 | 400 | 197.83 | 36 |  |  | Physical/Mechanical Joint | Valves |  | Unknown |  | 2004-06-04 | 2006-05-05 | [5 empty] | DEVELAN COMPRESSOR STATION; LEAK REPAIRED OVER ->;. LEAK IS UNDETECTABLE. TEST UNIT HEATH DETECTO - PAK III; CONTRACTOR MADE REPAIR OF LEAK AND IT WAS CHECKED WITH GAS RANGER. LEAK IS AT ZERO. D. MACLEAN 4-15-10.
| 04-40002-1 | 400 | 197.83 | 36 |  |  | Physical/Mechanical Joint | Valves |  | Unknown |  | 2004-06-04 | 2006-05-05 | Other | GREASE |  |  |  | DEVELAN COMPRESSOR STATION; LEAK REPAIRED OVER.; LEAK IS CURRENTLY UNDETECTABLE; CONTRACTOR MADE REPAIR OF LEAK AND CHECKED WITH GAS RANGER. LEAK IS AT ZERO. D. MACLEAN 4-15-10
| 04-40003-1 | 400 | 197.83 | 36 | Transmission |  | Physical/Mechanical Joint | Valves |  | Unknown |  | 2004-06-04 | [6 empty] | DEVELAN COMPRESSOR STATION; LEAK HAS GOTTEN WORSE. LEAKING WROTE #2 WORKING ANNUAL RECHECK. LEAK SEEM TO BE SHOW MORE SIGN WR# 139046.
| 04-30202-1 |  |  | 6 | [5 empty] | Internal Corrosion | SUSPECT | 2004-10-21 | [5 empty] | SUTTER/ YUBA CITY | FLAME PACK-NO READ
| 04-40001-1 | 400 | 197.83 | 36 | Transmission |  | Physical/Mechanical Joint | Valves |  | Unknown |  | 2004-06-04 | [6 empty] | LEAK HAS GOTTEN WORSE. LEAKING WROTE #2 WORKING. LEAK SEEM TO BE SHOW MORE SIGN WR #139046.
| 04-30202-1 |  |  | 6 | Gathering |  |  |  |  | Internal Corrosion | SUSPECT | 2004-10-21 | [5 empty] | SUTTER / YUBA CITY | EMPLOYEE FOUND LEAK DURING FLAME PACK BEFORE EXCAVATING LINE FOR PREVIOUS LEAK
| 04-30202-1 |  |  | 6 | [5 empty] | Internal Corrosion | SUSPECT | 2004-10-21 | [5 empty] | SUTTER / YUBA CITY | FLAME PACK - NO READ. FLAME PACK - NO READ. RMLD UNIT - NO READ.
| 04-30202-1 |  |  | 6 | [5 empty] | Internal Corrosion | SUSPECT | 2004-10-21 | [5 empty] | SUTTER / YUBA CITY | FLAME PACK - NO READ
| 04-30202-1 |  |  | 6 | Gathering |  |  |  |  | Internal Corrosion | SUSPECT | 2004-10-21 | [5 empty] | SUTTER / YUBA CITY | EMPLOYEE FOUND LEAK DURING FLAME PACK BEFORE EVACUATIONG LINE FOR PREVIOUS LEAK.
| 04-30202-1 | 302E | 2.3662 | 6 | Transmission |  |  |  |  | Internal Corrosion | SUSPECT | 2004-10-21 | [5 empty] | SUTTER / YUBA CITY; | EMPLOYEE FOUND LEAK DURING FLAME PACK BEFORE EVACUATING LINE FOR PREVIOUS LEAK.
| 04-20001-1 | 200 | 0.8657 | 12 | Gathering |  | Body of Pipe |  |  | Unknown |  | 2004-03-09 | 2004-03-15 | Other | CUT DRIP LINE |  |  | RIO VISTA | GAS BLOWING IN FIELD.; 3/4" DRIP LINE ON L-200 NEAR V-87; 3/4" DRIP LINE CRACKED DUE TO EARTH MOVEMENT. CUT AND CAPPED DRIP LINE. 3/4" DRIP LINE CONCRETE PAD; GPS FILE #R042214B.SSF.
|  | 200 |  | 01.05 / 12.750 | Transmission | DRIP LINE | Body of Pipe | Drip | DRIP LINE | Material Failure | BROKEN |  | 2004-03-15 |  |  | Steel/Wrought Iron |  |  | 12" LINE 200 LEAK NEAR VALVE 87. 8063406 BROKEN 3/4" DRIP LINE OFF 2" BLOW DOWN; 3/4" DRIP LINE INSTALLED 3/4" CAP ON. DRIP LINE INSTALLED 2" 600 BLIND FLANGE ON 2" BLOW DOWN VALVE. NOTE NOT SURE WHERE 3/4" LINE FOES POSSIBLE TO NEIL HAMILTON JUNCTION.
| 04-19502-1 | 195 |  | 6 | Gathering |  | Body of Pipe |  |  | Unknown |  | 2004-08-03 | [5 empty] | ISLETON
| 04-19502-1 |  |  | 6.625 | Transmission | TO DIST REG |  |  |  | Internal Corrosion |  | 2004-08-10 | 2003-08-12 |  |  | Steel/Wrought Iron |  | ISLETON | INSTALLED 4' OF .188 WELL AP: 5LX42 ERW PIPE AND 7 DEGREE ANGLE. 1" SAV-A-VALVE ROLLED 45 DEGREES TO NORTH.
| 04-19302-1 | 193-027 | 0.03 | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2004-10-05 | 2004-10-13 | Other | CAN |  |  | N/W ORLAND | REPAIRED WITH 45" OF .280 SANDS BACK GROUND TO .156 6"; NOTE: PIPE BACK GROUND TO MATCH EXISTING .156 PIPE.
| 04-14101-1 | 141 | 3.4794 | 6 | Gathering |  | Body of Pipe |  |  | Unknown |  | 2004-02-19 | 2004-02-20 | ABANDON |  |  |  |  | LINE CUT AND CAPPED FOR RETIREMENT; LINE TO BE RETIRED.
| 04-14101-1 | 141 | 3.6 | 6 | Gathering |  | Body of Pipe |  |  | Unknown |  | 2004-02-19 | 2004-02-20 | ABANDON |  |  |  |  | LINE CUT AND CAPPED FOR RETIREMENT; LINE TO BE RETIRED.
| 03-40007-1 | 400 | 115.26 | 36 | Transmission |  | Fitting | Other | FITTING TUBING FLANGE BOLTS | Equipment Malfunction |  | 2003-05-05 | 2009-09-17 | Other | TRP-31 | Steel/Wrought Iron |  | BURNEY | GPS N 40 DEGREES 30.168'. W 121 DEGREES 57.1569'.
| 03-40007-1 | 400 | 115.26 | 36 | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2003-05-05 |  |  |  | Steel/Wrought Iron |  | BURNEY | GPS N 40 DEGREES 30.168'. W 121 DEGREES 57.169'.
| 03-40007-1 | 400 | 115.26 | [8 empty] | 2003-05-05 | [5 empty] | BURNEY
| 03-40007-1 | 400 | 115.26 | [8 empty] | 2003-05-05 | [5 empty] | BURNEY
| 03-40007-1 | 400 | 115.26 | [8 empty] | 2003-05-05 | [5 empty] | BURNEY
| 03-40007-1 |  | 115.26 | [8 empty] | 2003-05-05 | [5 empty] | BURNEY | V 115.26. NONE. VENTED.
| 03-40007-1 |  | 115.26 | [8 empty] | 2003-05-05 | [5 empty] | BURNEY | V 115.26. NONE. VENTED.
| 03-40007-1 | 400 | 115.26 | 36 | Transmission |  | Fitting | Valves |  |  |  | 2003-05-05 | [5 empty] | BURNEY | V - 115.26. GRAVEL AREA AROUND VLV.
| 03-50055-1 |  | 1.7178 | 16 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2003-10-29 | 2003-10-29 | Other | WELD OVER CORROSION PITTS | Steel/Wrought Iron |  | SAN JOSE | ON FEEDER MAIN (PITTS ON TOP OF MAIN); RAN BEADS OVER EACH PITT FILL THEM JUST OVER FLUSH OF MAIN; (SOAP TEST WELDS); WELDED UP 5 CORROSION PITT HOLES
| 03-40006-1 |  | 115.26 | 36 | Transmission |  | Fitting | Valves |  | Unknown |  | 2003-05-05 | [5 empty] | BURNEY | NO LEAK FOUND C2. NONE.
| 03-40006-1 |  | 115.26 | 36 | Transmission |  | Fitting | Valves |  |  |  | 2003-05-05 | [5 empty] | BURNEY | V-2. GRAVEL AREA AROUND VLV. NO LEAK FOUND.
| 03-40006-1 | 400 | 115.26 | 20 | Transmission |  | Fitting | Valves |  |  |  | 2003-05-05 | [5 empty] | BURNEY | V-2. GRAVEL AREA AROUND VLV.
| 03-40005-1 | 400 | 24.6 | [8 empty] | 2003-05-06 | [5 empty] | BURNEY
| 03-40005-1 |  |  | 36 | Transmission |  | Fitting | Valves | [9 empty] | BURNEY | V-24.68 LEAK LOCATION IS IN GRAVEL AROUND VLV.
| 03-40005-1 | 400 | 24.6 | 36 | Transmission |  | Fitting | Valves |  |  |  | 2003-05-06 | [5 empty] | BURNEY | V-24.60. LEAK LOCATION IS IN GRAVEL AROUND VLV.
| 00-40002-1 | 400 | 24.6 |  | Transmission |  | Physical/Mechanical Joint |  |  | Other | 1" BAD VALVE | 2000-04-25 | [5 empty] | TIOWESTA | 03-40005-1
| 03-40005-1 | 400 | 24.6 | 36 | Transmission |  | Fitting | Valves |  |  |  | 2003-05-06 | [5 empty] | BURNEY | V-24.60. LEAK LOCATION IS IN GRAVEL AROUND VLV.
| 03-40005-1 | 400 | 24.6 | [8 empty] | 2003-05-06 | [5 empty] | BURNEY
| 03-40005-1 |  |  | 36 | Transmission |  | Fitting | Valves |  |  |  | 2003-05-06 | [5 empty] | BURNEY
| 03-40005-1 | 400 | 24.6 | 36 | Transmission |  | Fitting | Valves |  |  |  | 2003-05-06 | [5 empty] | BURNEY
| 03-40004-1 | [10 empty] | 2003-05-03 | [5 empty] | BURNEY | 03-40004-1; 05-40004-1
| 03-40004-1 | 400 | 48.64 | [8 empty] | 2003-05-03 | [6 empty] | RAY NEED #. VALVE B. CONTINUE TO CHECK.
| 03-40004-1 | 400 | 48.64 | [8 empty] | 2003-05-03 | [5 empty] | BURNEY | RAY NEED #. VALVE B. CONTINUE CHECK.
| 03-40003-1 | 400 | 24.6 | [8 empty] | 2003-05-06 | [5 empty] | BURNEY
| 03-40003-1 |  |  | 30 | Transmission |  | Fitting | Valves |  |  |  | 2003-05-06 | [5 empty] | BURNEY | V-2 LEAK LOCATED IN GRAVEL AROUND VALVE.
| 03-40003-1 | 400 | 24.83 | 30 | Transmission |  | Fitting | Valves |  |  |  | 2003-05-06 | [5 empty] | BURNEY | V-2 LEAK LOCATED IN GRAVEL AROUND VLV.
| 03-40002-1 | 400 | 233.87 | 36 | Transmission |  | Unknown |  |  | Unknown |  | 2003-06-13 | 2004-06-25 | Tighten Cap or Bolt |  |  |  | DUNNIGAN | STEM TO OPERATOR MLV 223.87. LEAK IS NON-DETECTABLE.
| 03-40002-1 | 400 | 233.89 | 36 | Transmission |  | Unknown |  |  | Unknown |  | 2003-06-13 |  |  |  | Steel/Wrought Iron |  | DUNNIGAN | MLV 233.87 (STEM TO OPERATOR).
| 03-40002-1 | 400 | 233.87 | 36 | Transmission |  | Unknown |  |  | Unknown |  | 2003-06-13 |  |  |  | Steel/Wrought Iron |  | DUNNIGAN | MLV 233.87 (STEM TO OPERATOR).
| 03-40001-1 | 400 | 149.18 | 0.75 | Transmission |  | Unknown |  |  | Unknown | OTHER-SEAL ON VALVE NOT WORKING. | 2003-06-13 | 2003-07-08 |  |  |  |  | GERBER | GREASE/ VENT LINE ON MLV 149.18.; LEAK HAS BEEN REPAIRED BY GREASING; SEAL ON WEEKLY WORK SCHEDULE.
| 03-40001-1 | 400 | 149.18 | 0.75 | Transmission |  | Unknown |  |  | Unknown |  | 2003-06-13 |  |  |  | Steel/Wrought Iron |  | GERBER | COVER LINK FOR MLV 149.18.
| 03-40001-1 | 400 | 149.18 | 0.75 | Transmission |  | Unknown |  |  | Unknown |  | 2003-06-13 |  |  |  | Steel/Wrought Iron |  | GERBER | COVER LEAK FOR MLV 149.18.
| 03-30601-1 | 306 | 49 | 20 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party |  | 2003-04-01 | 2003-04-02 |  |  | Steel/Wrought Iron |  |  | WELDED SPLIT REPAIR BOND; D-6 TRACTOR RIPPED INTO MAIN L-306 M/P/ 49.
| 03-30201-1 | 302 |  | 6 | [5 empty] | Internal Corrosion | SUSPECT INTERNAL CORROSION | 2003-02-14 | 2003-05-19 | ABANDON | OTHER-RETIRED |  |  | SUTTER COUNTY | 6" L-302 IS ISOLATED. V-206 IS CLOSED. MAP 484001 2 OF 2 CLY 148. GRID N-2. GATHERING LINE. PER ENGINEERING, LINE WILL BE ABANDONED AT V-206.; RETIRED ALL PIPE FROM V-206 SOUTH. S.O.#7046545.
| 03-30201-1 | 302 | 1.7 | 6 | [5 empty] | Internal Corrosion | SUSPECT INTERNAL CORROSION | [6 empty] | SUTTER COUNTY | 6" L-302 IS ISOLATED. V-206 IS CLOSED. MAP 484001 2 OF 2 CLY 148. GRID N-2. GATHERING LINE. PER ENGINEERING, LINE WILL BE ABANDONED AT V-206.
| 03-30202-1 | 302 |  | 6 | [5 empty] | Internal Corrosion | SUSPECT INTERNAL CORROSION. | 2003-02-14 | 2003-05-19 | ABANDON | OTHER- RETIRED |  |  | SUTTER COUNTY | 6" L-302 IS ISOLATED. V-206 IS CLOSED. MAP 484001 2 OF 2 CLY 148. GRID N-2. GATHERING LINE. PER ENGINEERING, LINE WILL BE ABANDONED AT V-206.; RETIRED ALL PIPE FROM V-206 SOUTH. S.O.#7046545.
| 03-30202-1 | 302 | 1.49 | 6 | [5 empty] | Internal Corrosion | SUSPECT INTERNAL CORROSION | 2003-02-14 | [5 empty] | SUTTER COUNTY | 6" L-302 IS ISOLATED. V-206 IS CLOSED. MAP 484001 2 OF 2 CLY 148. GRID N-2. GATHERING LINE. PER ENGINEERING, LINE WILL BE ABANDONED AT V-206
| 03-30203-1 | 302 |  | 6 | [5 empty] | Internal Corrosion | SUSPECT INTERNAL CORROSION | 2003-02-14 | 2003-05-19 | ABANDON | OTHER- RETIRED |  |  | SUTTER COUNTY | 6" L-302 IS ISOLATED. V-206 IS CLOSED. MAP 484001 2 OF 2 CLY 148. GRID N-2. GATHERING LINE. PER ENGINEERING, LINE WILL BE ABANDONED AT V-206.; RETIRED ALL PIPE FROM V-206 SOUTH. S.O.#7046545.
| 03-30203-1 | 302 | 0.65 | 6 | [5 empty] | Internal Corrosion | SUSPECT INTERNAL CORROSION | 2003-02-14 | [5 empty] | SUTTER COUNTY | 6" L-302 IS ISOLATED. V-206 IS CLOSED. MAP 484001 2 OF 2 CLY 148. GRID N-2. GATHERING LINE. PER ENGINEERING, LINE WILL BE ABANDONED AT V-206.
| 03-30204-1 | A302 |  | 6 | Gathering |  |  |  |  | Internal Corrosion | SUSPECT INTERNAL CORROSION | 2003-02-14 | 2003-05-19 | ABANDON | OTHER-RETIRED |  |  | SUTTER COUNTY | 6" L-302 IS ISOLATED. V-206 IS CLOSED. MAP 484001 2 OF 2 CLY 148. GRID N-2. GATHERING LINE. PER ENGINEERING, LINE WILL BE ABANDONED AT V-206.; RETIRED ALL PIPE FROM V-206; SOUTH. S.O.#7046545.
| 03-30204-1 | 302 | 7.61 | 6 | Gathering |  |  |  |  | Internal Corrosion | SUSPECT INTERNAL CORROSION | 2003-02-14 | [5 empty] | SUTTER COUNTY | 6" L-302 IS ISOLATED. V-206 IS CLOSED. MAP 484001 2 OF 2 CLY 148. GRID N-2. GATHERING LINE. PER ENGINEERING, LINE WILL BE ABANDONED AT V-206.
| 03-30205-1 | 302 |  | 6 | Gathering |  |  |  |  | Internal Corrosion | SUSPECT INTERNAL CORROSION. | 2003-02-14 | 2003-05-19 | ABANDON | OTHER-RETIRED |  |  | SUTTER COUNTY | 6" L-302 IS ISOLATED. V-206 IS CLOSED. MAP 484001 2 OF 2 CLY 148. GRID N-2. GATHERING LINE. PER ENGINEERING, LINE WILL BE ABANDONED AT V-206.; RETIRED ALL PIPE FROM V-206; SOUTH. S.O.#7046545.
| 03-30205-1 | 302 | 7.08 | 6 | Gathering |  |  |  |  | Internal Corrosion | SUSPECT INTERNAL CORROSION | 2003-02-14 | [5 empty] | SUTTER COUNTY | 6" L-302 IS ISOLATED. V-206 IS CLOSED. MAP 484001 2 OF 2 CLY 148. GRID N-2. GATHERING LINE. PER ENGINEERING, LINE WILL BE ABANDONED AT V-206.
| 03-30206-1 | 302 |  | 8 | Transmission | GATHERING (PREVIOUSLY) | Body of Pipe |  |  | External Corrosion |  | 2003-02-14 | 2003-03-26 | Other | SAVE-A-VALVE |  |  | SUTTER COUNTY | LEAK ON 8" L-302. LINE IS ISOLATED - V-324 IS CLOSED. MAP #484001 CHG 148 SHT 2 OF 2. GRID N-4. - LOCAL TRANSMISSION LINE.; WELDED 2" MUELLER SAVE-A-VALVE OVER PIT. X-RAYED PIT; 3/4" PIT ISOLATED TO ONE SPOT.
| 03-30206-1 | 302 | 3.9 | 8 | [5 empty] | External Corrosion | INTERNAL CORROSION -(SUSPECT INTERNAL CORROSION). | 2003-02-14 | [5 empty] | SUTTER COUNTY | LEAK ON 8" L-302. LINE IS ISOLATED - V-324 IS CLOSED. MAP #484001 CHG 148 SHT 2 OF 2. GRID N-4. - LOCAL TRANSMISSION LINE.
| 03-30207-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2003-05-17 | 2003-11-04 | ABANDON | OTHER-RETIRED |  |  |  | GAS BUBBLES IN FLOODED RICE FIELD.; RETIRED WITH CUT & CAP S.O. #7047607.; ISOLATED AND BLOWN DOWN. PIPE WILL BE RETIRED AT LATER DATE. V-400 CLOSED PERMANENTLY.
| 03-30207-1 |  |  | 6 | Gathering |  | Body of Pipe |  | SUSPECT | Internal Corrosion |  | 2003-05-17 | 2003-11-04 | ABANDON | OTHER-RETIRED |  |  |  | GAS BUBBLES IN FLOODED RICE FIELD.; RETIRED WITH CUT & CAP S.O. #7047607.; ISOLATED AND BLOWN DOWN. PIPE WILL BE RETIRED AT LATER DATE. V-400 CLOSED PERMANENTLY.
| 03-22001-1 | 220 | 6.07 | 10 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party | DIG-IN | 2003-10-15 | 2003-10-16 | Welded Sleeve/Can - Weld |  |  |  | SOLANO COUNTY | GAS BLOWING IN FIELD. INSTALLED 59" CAN.
| 03-22001-1 | 220 | 6.07 | 10 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party | DIG-IN | 2003-10-15 | 2003-10-16 | Welded Sleeve/Can - Weld |  |  |  | SOLANO COUNTY | GAS BLOWING IN FIELD.; INSTALLED 59" CAN.
|  | 220 | 6.6047 | [15 empty] | SO8060341
|  |  |  | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron
| 03-20801-1 | 208 | 2.37 | 8 | Gathering |  |  |  |  | Internal Corrosion |  | 2003-04-11 | 2003-04-25 | Other | WELDED SAVE-A-VALVE |  |  | SAN JOAQUIN COUNTY | FOUND DURING ANNUAL LEAK SURVEY.; WELDED 2" SAV-A-VALVE ON PIPE.
| 03-20001-1 | 200 | 0.16 | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2003-03-27 | 2003-04-08 | Mechanical Repair Fitting - Fitting |  |  |  | DIXON | GAS BLOWING.; INSTALLED 8" LEAK CLAMP.; NO SERIAL # ON PLIDCO SLEEVE PER BAM7.
| 03-20002-1 | 200 | 0 | 4 | Gathering |  | Body of Pipe |  |  | Digin |  | 2003-03-26 | 2003-03-26 | Other | CUT AND CAP |  |  | RIO VISTA | 7046069 GC DIGIN - 30# ISOLATED.; GAS BLOWING; LINE CUT AND CAPPED ON BOTH SIDE OF DAMAGE.
| 03-20003-1 | 200 | 0.59 | 6 | Gathering |  | Body of Pipe |  |  | Unknown |  | 2003-04-01 | 2003-06-11 | ABANDON |  |  |  | RIO VISTA | GAS BLOWING.; LINE CUT AND CAPPED AT V-242.
| 03-19601-1 | 196 | 0.39 | 6 | Gathering |  | Body of Pipe |  |  | Unknown |  | 2003-07-15 | 2003-07-23 | ABANDON |  |  |  | SAN JOAQUIN COUNTY | GAS BLOWING; LINE TO BE RETIRED DOWNSTREAM OF JACKSON WELL CONNECTION; LINE CUT AND CAPPED.
| 03-19501-1 | 195 | 0 | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2003-09-30 | 2003-10-06 | Mechanical Repair Fitting - Fitting |  |  |  | SACRAMENTO COUNTY | GAS BLOWING.; INSTALL 6" PLIDCO LEAK CLAMP.
| 03-17701-1 | 177 | [9 empty] | 2003-06-13 | 2005-06-28 | Other | WELDED IN SPOOL PIECE |  |  | GERBER | CHECK & MONITOR. ; CHECK VALUE REMOVED 6-28-05. ; CHECK VALVE REMOVED BY GC. VAULT CAVED IN & BACKFILLED.
| 03-17701-1 | 177 |  | 12 |  |  | Other |  | HINGE PACKING SEALS | Unknown | [5 empty] | Steel/Wrought Iron |  |  | L-177 CHECK VALVE #23 VAULT.
| 03-17401-1 | 174 | 0 | 10 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2003-05-16 | 2003-06-05 |  |  |  |  | ARBUCKLE | LEAK FOUND DURING YEARLY SURVEY - DRAWING #082647 RE. 19 LEAK AREA BETWEEN V-16 & V-13. INCLUDING 16" OFFSET DRIP. LEAK ISOLATED AND BLOWN DOWN TO 100 PSIG, AWAITING REPAIR.; REPLACED 10" PIPE BETWEEN V-13 & V-16 (90FT TOTAL) S.O. #8058597.
[16 empty] | Steel/Wrought Iron |  |  | REPLACE 10" W/90' .365 GR.B SML. 3/4" SUPPLY CUT + CAP FROM GAUGE LINE 6" SIDE.
| 03-16901-1 | 169 | 5.12 | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion | OTHER- SUSPECT INT. CORROSION | 2003-12-01 | [5 empty] | E/O WILLOWS | RICE FIELD 100 YDS S/E V-230.
| 03-16901-1 | 169 |  | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion | OTHER-SUSPECT INT. CORROSION | 2003-12-01 | 2003-12-03 | Welded Sleeve/Can - Weld |  |  |  | E/O WILLOWS | RICE FIELD 100 YDS S/E V-230.; REPLACED 81" OF 16" PRETESTED PIPE.
| 03-16901-1 | 169 | 5.1337 | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion | OTHER-SUSPECT INT. CORROSION | 2003-12-01 | 2003-12-03 | Welded Sleeve/Can - Weld |  |  |  | E/O WILLOWS | RICE FIELD 100 YDS S/E V-230. ; CUT OUT AND REPLACED WITH 811/ 4" OF EMERGENCY PIPE.
| 03-13101-1 | 131 | 45.5 | 24 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2003-01-21 | 2003-03-05 | Patch Welded |  |  |  | FREMONT/ ALAMEDA CO. | 8 X 10 WELD PATCH.
| 03-60335 | 109 | 16 | 22 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2003-12-16 | 2003-12-17 | Patch Welded |  | Steel/Wrought Iron |  | PALO ALTO | WELDED IN POSITION; REPAIR AREA : 25' NW FROM TIP OF TRAFFIC ISLAND.
[16 empty] | Steel/Wrought Iron |  | PALO ALTO
| 03-00501-1 | SP5 | 5.78 | 8 | Transmission | BLOW-OFF | Physical/Mechanical Joint | Other | BURIED FLANGE |  |  | 2003-04-10 | 2003-05-09 | Welded Sleeve/Can - Weld |  | Other | GRADE B PIPE | ANTIOCH | REMOVED EXISTING BURIED FLANGE. WELDED IN STRAIGHT PIPE CAN; REMOVED LEAKING FLANGE - INSTALLED CAN. REPLACED FLANGE ITEM # 68 WITH STRAIGHT PRE-TESTED PIPE. DRAWING #48678.
| 02-40101-1 | 401 | 82.34 | [8 empty] | 2002-05-03 | [5 empty] | BURNEY
| 02-40101-1 | 401 | 82.34 | [8 empty] | 2002-05-03 | [5 empty] | BURNEY
| 02-40101-1 | 401 | 82.34 | 42 |  |  | Unknown |  |  | Unknown |  | 2002-05-03 | [6 empty] | 08-40001-01; VL.; GOV1 (REPLACED 9-11-01).; GOV2 (REPLACED 9-11-01)
| 02-40101-1 | 401 | 82.34 | 42 |  |  | Unknown |  |  | Unknown |  | 2002-05-03 | [6 empty] | VL. ; GOV1 (REPLACED 9-11-01). ; GOV2 (REPLACED 9-11-01)
| 02-40001-1 | 400 | 48.64 | [8 empty] | 2002-05-05 | [5 empty] | BURNEY | VALVE 2
| 02-40001-1 | 400 | 48.64 | 36 | Transmission |  | Unknown |  |  | Unknown |  | 2002-05-05 | [6 empty] | VALVE 2
| 02-40001-1 | 400 | 48.64 | 36 | Transmission |  | Unknown |  |  | Unknown |  | 2002-05-05 | [6 empty] | VALVE 2
| 02-31801-1 | 318 |  | 3 | Gathering |  | Valves |  |  | Unknown |  | 2003-03-18 | 2002-03-21 | Other | REPLACED |  |  |  | LEAK AROUND VALVE BODY (3" V-B) AT BLACK BUTTE STATION.; REPLACED VALVE S.O. #1004563.
| 02-31402-1 | 314 | 28.12 | 10 | Transmission |  |  |  |  | Construction Defect | EXTERNAL CORROSION | 2002-12-04 | 2003-01-08 | Welded Sleeve/Can - Weld |  | Steel-Other |  | VICTORVILLE | HOLIDAY IN WRAP CAUSED BY MOVEMENT WHILE ON SKIDS DURING INSTALLATION; LEAK REPAIRED.
| 02-30301-1 | 303 | 39.38 | [8 empty] | 2002-10-09 | [5 empty] | FREMONT | IN GROUND AROUND MLV.
| 02-30301-1 | 303 | 39.38 | [8 empty] | 2002-10-09 | [5 empty] | FREMONT | IN GROUND AROUND MLV.
| 02-30301-1 | 303 | 39.38 | [8 empty] | 2002-10-09 | [5 empty] | FREMONT | LEAK RECHECK.
| 02-30301-1 | 303 | 39.38 | [8 empty] | 2002-10-09 | [5 empty] | FREMONT | LEAK RECHECK.
| 02-30301-1 | 303 | 39.38 | [8 empty] | 2002-10-09 | [5 empty] | FREMONT | LEAK RECHECK
| 02-30301-1 | 303 | 39.38 | [8 empty] | 2002-10-09 | [5 empty] | FREMONT | LEAK RECHECK
| 02-30301-1 | 303 | 39.38 | [8 empty] | 2002-10-09 | [5 empty] | FREMONT | LEAK RECHECK
| 02-30205-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-05-08 | 2002-05-30 | Other | CAPPED & RETIRED LEAK SECTION | Steel/Wrought Iron |  | S/E MERIDIAN | BUBBLES IN FLOODED FIELD. ISOLATED AND BLEED DOWN.; RETIRED PIPE LEAKING TO MOBIL-WOOD #4-1 S.O. #70433786
| 02-30204-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-04-18 | 2002-05-10 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | S/E MERIDIAN | INSTALLED 8" PLENICO LEAK CLAMP
| 02-30204-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-04-18 |  |  |  | Steel/Wrought Iron |  | S/E MERIDIAN | WILL SCHEDULE REPAIR ME 02-14
| 02-30203-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-04-18 | 2002-05-10 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | S/E MERIDIAN | INSTD PLEDICO 8" LEAK CLAMP
| 02-30203-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-04-18 |  |  |  | Steel/Wrought Iron |  | S/E MERIDIAN | WILL SCHEDULE REPAIR ME-02-14
| 02-30202-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-03-28 | 2002-04-16 | Other | 56 3/4 OF NEW PIPE | Steel/Wrought Iron |  | GRIMES | PITS IN SECTION REMOVED, PLUS TIE IN SECTIONS .090 DEEP
| 02-30202-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-03-28 |  |  |  | Steel/Wrought Iron |  | GRIMES | ISOLATED AND BLEW DOWN
| 02-30201-1 | 302E |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-01-10 | 2002-02-21 | Weld Over Sleeve or Can |  |  |  | S/O SUTTER | BUBBLES IN FLOODED FIELD; CUT OUT TEE AND REPLACED WITH 109" OF PRETESTED PIPE
| 02-30101-1 | 301A | 0.01 | 20 | [7 empty] | 2002-04-03 | 2002-08-06 |  |  |  |  | HOLLISTER | RE-CHECKED, NO ACTION REQUIRED. WILL RE-CHECK NEXT SURVEY
| 02-30101-1 | 301A | 0.01 | 20 | [7 empty] | 2002-04-03 | [5 empty] | HOLLISTER
| 02-30001-1 | 300A | 183.72 | 34 | Transmission |  | Longitudinal Weld |  |  |  |  | 2002-11-22 | 2003-01-23 | Weld Over Sleeve or Can |  |  |  | HINKLEY, CA | WELD BAND; REPAIRED HOT W/BAND
| 02-20801-1 | 208 | 2.47 | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-04-20 | 2002-05-30 | Weld Over Sleeve or Can |  |  |  | SAN JOAQUIN COUNTY | INSTALLED 4" CAN PRETESTED PIPE; SHUT-IN AND BLEW DOWN L-208 4-20-02 UNTIL REPAIRED. REPAIRED & BACK IN SERVICE 5-30-02
| 02-20801-1 | 208 | 2.47 | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-04-20 | 2002-05-30 | Weld Over Sleeve or Can |  |  |  | SAN JOAQUIN COUNTY | INSTALLED 4' CAN PRETESTED PIPE; SHUT-IN AND BLEW DOWN L-208 4-20-2002 UNTIL REPAIRED. REPAIRED & BACK IN SERVICE 50-30-02
| 02-20003-1 | 200 | 0.12 | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-11-11 | 2002-11-19 | Weld Over Sleeve or Can |  |  |  | RIO VISTA | BUBBLES IN DITCH; INSTALLED 48" CAN; GPS FILE R11256A L-200
| 02-20002-1 | 200 | 0.55 | 6 | Gathering |  | Drip |  |  | Damage by Natural Forces |  | 2002-02-06 | 2001-02-07 | ABANDON |  |  |  | RIO VISTA | 1" LINE TO OFFSET DRIP BROKE AT THREADED VALVE, DRIP LINE CUT AND CAPPED
| 02-19501-1 | 195 | 0 | 6 | Gathering |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2002-04-05 | 2002-05-07 | Mechanical Repair Fitting - Fitting |  |  |  | RIO VISTA / SAC. COUNTY | INSTALLED LEAK CAP
| 02-19301-1 | 193 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion | SUSPECT INTERNALS | 2002-01-03 | 2002-04-10 | ABANDON |  |  |  | W/O ORLAND | CAPPED BOTH ENDS AND RETIRED CROSSING
| 02-17201-1 | 172A | 29.33 | 18 | Transmission |  | Body of Pipe | Other | CRACK | Unknown |  | 2002-05-29 | 2002-06-05 | Other |  |  |  | ARBUCKLE | FOUND CRACK @ 30' CLOCK LOOKING SOUTH REPAIR #8053217 INSTALLED 59 1/2" CAN
| 02-16802-1 | 168 | 0.11 | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-06-20 | 2002-07-18 | Weld Over Sleeve or Can |  |  |  |  | INSTALLED 26" CAN
| 01-40006-1 | 400 | 24.6 | [8 empty] | 2002-05-05 | [5 empty] | TIONESTA | VALVE B; STILL EXPOSED
| 01-40006-1 |  | 24.6 | [8 empty] | 2002-05-05 | [6 empty] | 09-40010-1 WHEN LEAK...GRADE 0....NEEDS TO GET A NEW LEAK # FOR GRADE 3; DON HATTING 1530.632.1871 NOT....
| 01-40006-1 | 400 | 24.6 | 16 |  |  | Valves |  |  | Unknown |  | 2002-05-05 | [6 empty] | LEAK IN GRAVEL AROUND VALVE VENTED
| 01-40006-1 | 400 | 24.6 | 16 | Transmission |  | Valves |  |  | Unknown |  | 2002-05-05 | [6 empty] | VALVE B; LEAK IS IN GRAVEL AROUND VLV
| 01-40006-1 | 400 | 24.6 | [8 empty] | 2001-04-16 | [6 empty] | VALVE B
| 01-40006-1 | 400 | 24.6 | [8 empty] | 2002-05-05 | [6 empty] | VALVE B
| 01-40006-1 | 400 | 24.6 | [8 empty] | 2002-05-05 | [6 empty] | VALVE B
| 01-40006-1 | 400 | 24.6 | [8 empty] | 2002-05-05 | [6 empty] | VALVE B
| 01-40006-1 | 400 | 24.6 | 16 |  |  | Valves |  |  | Unknown |  | 2002-05-05 | [6 empty] | V-B; LEAK IN GRAVEL AROUND VALVE VENTED
| 01-40006-1 | 400 | 24.6 | 16 |  |  | Valves |  |  | Unknown |  | 2002-05-05 | [6 empty] | V-B; LEAK IN GRAVEL AROUND VALVE
| 01-40006-1 | 400 | 24.6 | [8 empty] | 2001-04-16 | [6 empty] | VALVE B
| 01-40006-1 | 400 | 24.6 | 16 | Transmission |  | Valves |  |  | Other | STEM LEAKING | 2002-05-05 | 2010-08-06 | Other | INJECT NEW STEM PACKING | Steel/Wrought Iron |  | TIONESTA | ADDED MORE STEM PACKING L-400 VALVE B. TIONEST COMP. STA.
| 01-40006-1 | 400 | 24.6 | [8 empty] | 2002-05-05 | [6 empty] | VALVE B
| 01-40006-1 | 400 | 24.6 | 16 |  |  | Valves |  |  | Unknown |  | 2002-05-05 | [6 empty] | V-B; LEAK IN AT GRAVEL IN GROUND VALVE VENTED
| 01-40006-1 | 400 | 24.6 | 16 | Transmission |  | Valves |  |  | Unknown |  | 2002-05-05 | [6 empty] | VALVE B; LEAK IS IN GRAVEL AROUND VALVE
| 01-40006-1 | 400 | 24.6 | [8 empty] | 2010-04-16 | [6 empty] | VALVE B
| 01-40005-1 | 400 | 24.6 | 16 | Transmission |  | Valves |  |  | Other | STEM LEAKING | 2002-05-05 | 2010-05-19 | Other | INJECT NEW STEM PACKING | Steel/Wrought Iron |  | TIONESTA | WORK REQUEST 153199; STEM PACKING L-400 VALVE A TIONESTA COMP. STA.
| 01-40005-1 | 400 | 24.6 | [8 empty] | 2002-05-05 | [6 empty] | VALVE A
| 01-40005-1 | 400 | 24.6 | [8 empty] | 2002-05-05 | [6 empty] | VALVE A
| 01-40005-1 | 400 | 24.6 | [8 empty] | 2002-05-05 | [6 empty] | VALVE A
| 01-40005-1 | 400 | 24.6 | [8 empty] | 2002-05-05 | [6 empty] | VALVE A
| 01-40005-1 | 400 | 24.6 | 16 |  |  | Valves |  |  | Unknown |  | 2002-05-05 | [6 empty] | VALVE A; LEAK IN GRAVEL; VENTED 2 VLV; VENTED
| 01-40005-1 | 400 | 24.6 | 16 |  |  | Valves |  |  | Unknown |  | 2002-05-05 | [6 empty] | VALVE A; LEAK IN GRAVEL AROUND VLV
| 01-40005-1 | 400 | 24.6 |  | Transmission |  | Valves |  |  | Unknown |  | 2002-04-16 | [6 empty] | VALVE A
| 01-00401-1 | SP4 | 3.92 | 12.75 | Transmission |  | Body of Pipe |  |  | Atmospheric Corrosion | EXTERNAL CORROSION | 2001-08-01 | 2001-08-06 | Other | INSTALL PIPE |  |  | RIO VISTA | DITCH CROSSING; INSTALLED 5B' P 5/8" OF 12" PIPE
| 01-40004-1 | 400 | 24.6 |  | Transmission |  | Valves |  |  | Unknown |  | 2001-04-16 | [6 empty] | VALVE 1; ASSIGNED NEW LEAK # 04-40101-1 SEE 2004 LEAK FOLDER
| 01-40004-1 | 400 | 24.6 | 30 | Transmission |  | Valves |  |  | Unknown |  | 2001-04-16 | [6 empty] | VALVE LOCATED IN GRAVEL AROUND VLV
| 01-40003-1 | 400 | 197.83 |  | Transmission |  | Unknown |  |  | Unknown |  | 2001-06-07 | 2004-06-04 | Other | CUT & CAPPED |  |  | MAXWELL | INSPECT & MONITOR DRIP TANK NORTH END OF YARD; TANK CAPPED & TAKEN OUT OF SERVICE
| 01-40003-1 | 400 | 197.83 | 2 | Transmission |  | Physical/Mechanical Joint | Valves |  |  |  | 2001-06-07 | [6 empty] | INSPECT + MONITOR OUT OF SERVICE DRIP TANK
| 01-40003-1 | 400 | 197.83 | 2 | Transmission |  | Physical/Mechanical Joint | Valves |  |  |  | 2001-06-07 | [6 empty] | INSTALL & MONITOR OUT OF SERVICE DRIP TANK
| 01-40003-1 | 400 | 197.8 | 36 | Transmission |  | Valves | Unknown |  |  |  | 2001-06-07 |  |  |  | Steel/Wrought Iron |  | DELEVAN, CA | OUT OF SERVICE - DRIP TANK; OUT OF SERVICE - DRIP TANK
| 01-40003-1 | 400 |  | 36 | Transmission |  | Unknown | Valves |  |  |  | 2001-06-07 |  |  |  | Steel/Wrought Iron |  | DELEVAN | OUT OF SERVICE DRIP TANK
| 01-40002-1 | 400 | 197.83 | 36 | Transmission |  | Valves |  |  | Other | PACKING | 2001-06-03 | 2002-04-16 | Tighten Cap or Bolt |  |  |  | MAXWELL | INSPECT & MONITOR PACKING ADJUSTED; PACKING TIGHTENED LEAK REPAIRED
| 01-40002-1 | 400 | 197.85 | 36 | Transmission |  | Physical/Mechanical Joint | Valves |  |  |  | 2001-06-07 | [5 empty] | DELEVAN | INSPECT + MONITOR KNOWN LEAK
| 01-40002-1 | 400 | 197.8 | 36 | Transmission |  | Valves | Unknown |  |  |  | 2001-06-07 |  |  |  | Steel/Wrought Iron |  | DELEVAN
| 01-40002-1 | 400 | 197.83 | 36 | Transmission |  | Physical/Mechanical Joint | Valves |  |  |  | 2001-06-07 | [5 empty] | DELEVAN | GRADE 2 LEAK; INSTALL & MONITOR KNOWN LEAK
| 01-40002-1 | 400 |  | 36 | Transmission |  | Valves | Unknown |  |  |  | 2001-06-07 |  |  |  | Steel/Wrought Iron |  | DELEVAN
| 01-40001-1 | 400 | 180.97 | 36 | Transmission |  | Valves |  |  | Other | SEAL PROBLEM | 2001-01-09 | 2002-04-06 |  |  |  |  | WILLOWS | STEM LEAK - NON-SEASONAL LEAK REPAIRED FMRZ AS AIRCRAFT VEG. SURVEY. STARTING IN 2003.; GREASE FITTING BROUGHT UP ABOVE GROUND & GREASED VALVE TO STOP LEAK
| 01-40001-1 | 400 | 180.27 |  |  |  | Valves | Other | STEM LEAK | Unknown |  | 2001-01-09 | [5 empty] | WILLOWS | STEM LEAK - WON'T CLEAN
| 01-40001-1 | 400 | 180.27 |  | Transmission |  | Valves | Other | STEM SEAL | Unknown |  | 2001-01-09 | [5 empty] | WILLOWS | STEM LEAK - NON GREASABLE
| 01-31601-1 | 316 |  | 6.62 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2001-12-02 | 2001-12-14 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | BETHEL ISLAND | WELDED 3' SLEEVE OVER HOLE; NOTE: PIPE IN BAD CONDITION HEAVY PITTING. PITTING LOCATED AT 2:00 TO 4:00 O'CLOCK & 7:00 TO 10:00 O'CLOCK
| 01-30215-1 | 302E | 3.8 | 8 | Gathering |  |  |  |  | Internal Corrosion | SUSPECT | 2001-10-31 | [5 empty] | SE/O MERIDIAN / SUTTER | WILL MONITOR LEAK WEEKLY; CANCEL PER EMAIL
| 01-30214-1 | 302 |  | 4 | Gathering |  | Body of Pipe | Other |  | Internal Corrosion |  | 2001-10-22 | 2001-11-28 | Other | REPLACED PIPE AROUND WELL PAD |  |  | GRIMES | REPLACED PIPE AROUND PRODUCER WELL PAD; SECTION OF PIPE UINDER PRODUCERS FACILITIES AND 8' DEEP COULD NOT REMOVE PIPE FOR INSPECTION INSTD NEW PIPE AROUND FACILITIES AND 60" DEEP
302
| 01-30214-1 | 302 |  | 4 | Gathering |  | Other |  |  | Internal Corrosion |  | 2001-10-22 | [5 empty] | GRIMES | LEAK FOUND BY FARMER BURNING FIELD. * ISOLATED LINE - V50 CLOSED BLOCK VALVE CLOSED. (*= TURNED IN BY GAS PRODUCER)
| 01-30213-1 | 302E | 2.31 | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-10-16 | [5 empty] | S/O SUTTER | BUBBLES IN WATER AT EDGE OF ROAD - ISOLATED PIPELINE; CANCEL PER EMAIL
| 01-30208-1 |  |  | 3 | Gathering |  | Other Welds |  |  |  |  | 2001-10-09 | 2001-10-09 | Other |  |  |  | S/O MERIDIAN | * STEVE WATERS TO CONFIRM AS BUILT DRAWINGS FOR THICKNESS AND GRADE; GROOVED OUT BOTTOM AND REWELDED.; LEAK ON WELD GROUND OUT BOTTOM AND REWELDED
| 01-30212-1 | 302E | 12.25 | 3 | Gathering |  | Other Welds |  |  |  |  | 2001-10-09 | [5 empty] | S/O MERIDIAN | CREW FOUND 6X6X3 TEE LEAKING AT 3" WELD (BOTTOM) * REPAIRS TO BE DONE ON 10-12-01; * STEVE WATERS TO CONFIRM AS BUILT DRAWINGS FOR THICKNESS AND GRADE;
| 01-30211-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-07-02 | [5 empty] | S/O GRIMES | BUBBLES IN FLOODED FIELD; 3-6FT W/O V-399; WILL PLACE ON RETIREMENT LIST; RETIRE ON SO#6088523-02
| 01-30210-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-06-06 | 2001-08-27 | Welded Sleeve/Can - Weld |  |  |  | 8 MI S/E OF MERIDIAN | BUBBLES IN IRRIGATED CORN FIELD. ISOLATED AND BLOWN DOWN. AWAITING PAYMENT FOR REPAIRS.; CUT OUT AND REPLACED WITH TESTED PIPE SO#8047916; LEAK REPAIR
| 01-30210-1 |  |  | 4 | [7 empty] | 2001-06-06 | [5 empty] | 8 MI S/E OF MERIDIAN | BUBBLES IN IRRIGATED CORN FIELD
| 01-30209-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-03 | [5 empty] | S/E MERIDIAN | CANCEL PER CASE
| 01-30208-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-03 | [5 empty] | S/E MERIDIAN | CANCEL PER CASE
| 01-30207-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-08-20 | [5 empty] | S/E MERIDIAN | CANCEL PER CABE
| 01-30207-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-03 | [5 empty] | S/E MERIDIAN | CANCEL PER CABF
| 01-30206-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-03 | 2001-08-28 | Mechanical Repair Fitting - Fitting |  |  |  | S/E MERIDIAN | INSTALL LEAK CLAMP; INSTALLL LEAK CLAMP SOAP @ 200PS. X-RAY SHOWS LIGHT PITTING.
| 01-30206-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-03 | 2001-08-28 | Mechanical Repair Fitting - Fitting |  |  |  | S/E MERIDIAN | INSTALL LEAK CLAMP; INSTALL LEAK CLAMP SOAP @ 200 PS. X-RAY SHOWS LIGHT PITTING *
| 01-30206-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-03 | [5 empty] | S/E MERIDIAN
| 01-30205-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-03 | 2001-08-27 | Mechanical Repair Fitting - Fitting |  |  |  | S/E MERIDIAN | INSTALL LEAK CLAMP; INSTALL LEAK CLAMP SOAP @200PSI
| 01-30205-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-03 | 2001-08-27 | Mechanical Repair Fitting - Fitting |  |  |  | S/E MERIDIAN | INSTALL LEAK CLAMP
| 01-30205-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-03 | [5 empty] | S/E MERIDIAN
| 01-30204-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-03 | 2001-08-27 | Mechanical Repair Fitting - Fitting |  |  |  | S/E MERIDIAN | INSTALL LEAK CLAMP; INSTALL LEAK CLAMP SOAP @ 200PSI
| 01-30204-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-03 | 2001-08-27 | Mechanical Repair Fitting - Fitting |  |  |  | S/E MERIDIAN | INSTALL LEAK CLAMP; INSTALL LEAK CLAM SOAP @ 200 PSI
| 01-30204-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-03 | [5 empty] | S/E MERIDIAN
| 01-30203-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-05 | 2001-06-15 | Welded Sleeve/Can - Weld |  |  |  | S/O GRIMES | BUBBLES IN FLOODED RICE FIELD PRODUCER... PRODUCTION TO ISOLATE LEAK AREA. 20 PSIG SUCTION SYSTEM U.S. OF ANDRETTI #11 M.M; INSTALLED 9' CAN
| 01-30203-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-05-07 | [5 empty] | S/O GRIMES | BUBBLES IN FLOODED RICE FIELD PRODUCER SHUT-IN PRODUCTION TO ISOLATE LEAK AREA. 20 PSIG SECTION SYSTEM U.S. OF ANDEROTTI #11 M.M.
| 01-30202-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-03-12 | 2001-08-30 | Other | NEW BORE |  |  | S/O SUTTER | LARGE BUBBLES IN WATER AND MUD ON DITCH BANK (ISOLATED & BLOWN DOWN); REPLACED LIVE OAK CANCEL CROSSING WITH A NEW BORE
| 01-30202-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-03-12 | [5 empty] | S/O SUTTER
| 01-30201-1 | 302 | 1.21 | 4 | [7 empty] | 2001-03-09 | [5 empty] | GRIMES
| 01-30201-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-03-09 | 2001-03-21 | Other | REPLACED |  |  | GRIMES | BUBBLES IN FIELD CLOSED VALVES TO ISOLATE - PIPING BLOWN DOWN; ISNTALLED NEW 3" PIPE FROM TAP VALVE TO RISER BLOCK VALVE
| 01-30002-1 | 300A | 106.42 |  |  |  | Girth Weld |  |  | Construction Defect |  | 2001-09-10 |  | Weld Over Sleeve or Can |  |  |  | LUDLOW | FACTORY WELD FAILURE
| 01-30041-1 | 300A | 76.72 |  |  |  | Longitudinal Weld |  |  | Construction Defect |  | 2001-09-21 |  | Welded Sleeve/Can - Weld |  |  |  | WEST AMBOY | INSTALL SLEEVE; ISSUED WK#28226
| #NAME? | 300A | 77.4 | 34 |  |  | Longitudinal Weld |  |  | Material Failure | [7 empty] | AMBOY
|  | 300A | 76.4 | [8 empty] | 2001-09-21 | [5 empty] | WEST AMBOY
| 01-20801-1 | 208 | 1.5 | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-04-25 | 2001-05-08 | Other | WELD CAP |  |  | TRACY/STOCKTON | CUT & CAP L-208 GATHERING ABANDONED LATHROP WEST GATHERING; L-208 LEAK REPAIR & ABANDONMENT.
| 01-20801-1 | 208 |  | 8 | [7 empty] | 2001-04-25 | [5 empty] | TRACY/STOCKTON
| 01-20003-1 | 200 | 0.83 | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-12-01 | 2001-12-11 | Mechanical Repair Fitting - Fitting |  |  |  | RIO VISTA | 8" LEAK CLAMP INSTALLED, LINE DOWNSTREAM OF TAP FOR P. COOK 14 RETIRED
| 01-20002-1 | 200 |  | 4.5 | Gathering |  | Other |  | PIPE CRACKED |  |  | 2001-08-29 | 2001-08-29 | ABANDON |  |  |  | RIO VISTA | NO REPAIRS MADE - LINE WILL BE RETIRED
| 01-20001-1 | 200 | 0.42 | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-03-02 | 2001-03-14 | Other | LEAK CLAMP |  |  | RIO VISTA | INSTALL 6" PLIDCO LEAK CLAMP; INSTALLED LEAK CLAMP. WRAPPED 30' OF PIPE
| 01-19601-1 | 196 |  | 6.625 | Gathering |  | Body of Pipe |  |  | External Corrosion | INTERNAL CORROSION | 2001-07-08 | 2001-08-10 |  |  |  |  | STOCKTON | REPLACED 600' OF 6" LINE WITH 3" PIPE AND INSTALLED NEW 3" METER TUBE
|  | 195 | 0.77 | 4 | Gathering | [6 empty] | 2001-07-10 | 2001-07-16 | Weld Over Sleeve or Can |  |  |  |  | INSTALLED REPAIR SLEEVE; DIG IN NO LEAK
|  | 195 |  | 4 | Gathering | [6 empty] | 2001-07-10 | 2001-07-16 | Weld Over Sleeve or Can |  |  |  |  | INSTALLED REPAIR SLEEVE
| 01-19501-1 | 195 |  | 8 | Gathering |  | Other |  | GASKET LEAK | Material Failure |  | 2001-02-07 | 2001-02-28 | Other | NEW GASKET |  |  | RIO VISTA | REPLACE NEW GASKET AND BOLTS IN
| 01-19001-1 | 190 |  | 0.75 | Transmission |  | Drip |  |  | Digin |  | 2001-06-28 | 2001-06-28 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | AVENAL | SEE STORY ON AFORM
| 01-19001-1 | 190 | 0 | 0.75 | Transmission |  | Drip |  |  | Digin |  | 2001-06-28 | 2001-06-28 | ABANDON |  |  |  | AVENAL | CLOSED 3/4" PLUG VALVE ..., CUT & CAPPED; STEWART DUNCAN DEMOLITION PULLED A 3/4" PLUG VALVE FROM THE 3/4" ...UPLINE. AREA HAD BEEN USED, VALVE OPENED + PRESUMED DEAD, THE 3/4" LINE WAS NOT ON ANY POINTS, NO ONE KNEW WHAT IT WAS FOR. THE LINE WAS TRIPLE VALVED, I-ABOVE GROUND, 2-BELOW. WE OPENED THE TOP VALVE, NO FLOW, THE 2ND VALVE WAS CLOSED. THE 3RD VALVE WAS OPEN. DURING THE DEMO WORK THE TOP TOP VALVE WAS PULLED OFF, NO FLOW SHORTLY THEIR AFTER THE 2ND VALVE WAS PULLED OFF, 3/4" T.P. LINE PRESS. BLOWING, ALL EQUIPMENT WAS TURNED OFF, NO FIRE OR INJURIES TO ... SAN JOSE WAS NOTIFIED, GAS WAS REROUGHTED, NO SERVICE INTERRUPTIONS ... THE DAMAGED SECTION OF L-190 WAS ISOLATED + REPAIRED BY PG&E EMPLOYEES ON THE SITE.
| 01-16701-1 |  |  | 4 | Gathering | SERVICE | Body of Pipe | Tap Connection |  | Digin |  | 2001-10-25 | 2001-10-25 | Mechanical Repair Fitting - Fitting |  |  |  | COLUSA | THREADED PIPE AND INSTALLED NEW VALVE; INCIDENT REPORT 20001#011660 10/25/01
| 01-16701-1 | 167 | 0.23 | 4 | Gathering | SERVICE | Tap Connection |  |  | Digin |  | 2001-10-25 | [5 empty] | COLUSA | GC GAS STRUCK A SERVICE TEE WHILE EXCAVATING LINE: HAS BEEN DOWNGRADED TO DISTRIBUTION ON 10-16-2001
| 01-40005-1 | 400 | 24.6 | [8 empty] | 2002-05-05 | [5 empty] | TIONESTA
| 00-40001-1 | 400 | 197.83 | 36 |  |  | Mechanical Joint |  |  | Other | GASKET | 2000-05-01 | [5 empty] | MAXWELL
| 00-40001-1 | 400 | 197.83 | 36 |  |  | Mechanical Joint |  |  | Other | GASKET | 2000-05-01 | [5 empty] | MAXWELL
| 00-40001-1 | 400 | 197.83 | 36 |  |  | Physical/Mechanical Joint |  |  | Other | GASKET | 2001-05-01 | [5 empty] | MAXWELL | LEAK SEEM'S TO BE SHOW MORE SIGN W.R. 139046 CLOSE CURRENT W.R. 164429
| 00-40001-1 | 400 | 197.83 | 36 | Transmission |  | Physical/Mechanical Joint | Valves |  | Unknown |  | 2004-06-04 | [6 empty] | LEAK SEEM TO BE SHOW MORE SIGN WR# 139046
| 00-40001-1 | 400 | 197.83 |  |  |  | Valves |  |  | Other | GASKET | 2000-05-01 | [5 empty] | MAXWELL
| 00-40001-1 | 400 | 197.83 | 16 | Transmission |  | Valves |  |  | Other | GASKET | 2000-05-01 | [5 empty] | MAXWELL | LEAK AT VALVE BODY FLANGE. CHECK & MONITOR
| 00-40001-1 |  | 197.83 |  | Transmission |  | Physical/Mechanical Joint | Valves |  | Unknown |  | 2001-05-01
| 00-40- | 400 | 197.83 | 36 | Transmission |  | Physical/Mechanical Joint | Valves |  | Unknown |  | 2000-05-01
| 00-40001-1 |  | 197.83 |  | Transmission |  | Physical/Mechanical Joint | Valves |  | Unknown |  | 2000-05-01
| 00-40001-1 |  | 197.83 |  | Transmission |  | Physical/Mechanical Joint | Valves |  | Unknown |  | 2000-05-01
| 00-40001-1 |  | 197.83 |  | Transmission |  | Physical/Mechanical Joint | Valves |  | Unknown |  | 2000-05-01 | [6 empty] | WRITING FOR CLARIFICATION HOW SYSTEM INTEGRITY AS TO WHETHER OR NOT THIS IS A GRADE 2 OR 3 5/30/00
| 00-40101-1 | 401 | 129.37 |  | Transmission |  | Valves | Other | GREASE STEM | Other | SEAL | 2000-03-13 | 2002-03-18 | Other | GREASED |  |  | RED BLUFF | VALVE GREASED. AIR PATROL NOW COMPLETING VEG. SURVEY. 5-7-03
| 00-40101-1 | 401 | 124.37 | 42 | Transmission |  | Unknown |  |  |  |  | 2000-03-13 | [5 empty] | RED BLUFF
| 00-40101-1 | 401 | 129.37 | 42 | Transmission |  | Unknown |  |  |  |  | 2000-03-13 | [5 empty] | RED BLUFF
| 00-40101-1 |  | 129.37 | 42 | Transmission |  | Unknown |  |  |  |  | 2000-03-13 | [5 empty] | RED BLUFF
| 00-40101-1 |  | 129.37 | 42 | Transmission |  | Unknown |  |  |  |  | 2000-03-13 | [5 empty] | RED BLUFF
| 00-40004-1 | 400 | 82.33 |  | Transmission |  | Valves |  |  | Unknown |  | 2000-04-26 | 2001-09-04 | Other |  |  |  | BURNEY | DRILL HOLES + EXPOSE AROUND FLANGES
| 00-40004-1 | 400 | 82.33 |  | Transmission |  | Valves |  |  | Unknown |  | 2000-04-26 | [5 empty] | BURNEY
| 00-40003-1 | 400 | 82.33 |  |  |  | Fitting |  |  | Material Failure |  | 2000-04-26 | 2001-09-04 | Other |  |  |  | BURNEY | 08-40001-1
| 00-40003-1 | 400 | 82.33 |  |  |  | Fitting |  |  | Material Failure |  | 2000-04-26 | [5 empty] | BURNEY
| 00-40002-1 | 400 | 24.6 |  |  |  | Physical/Mechanical Joint |  |  | Material Failure | OTHER-1" BALL VALVE | 2000-04-25 | [5 empty] | TIONESTA
| 00-40002-1 | 400 | 24.6 |  | Transmission |  | Physical/Mechanical Joint |  |  | Material Failure | OTHER-1" BALL VALVE | 2000-04-25 | [5 empty] | TIONESTA | 03-40005-1
00-302XX-1
| 00-30204-1 | 302 |  | 6 | [7 empty] | 2000-05-26 | [5 empty] | GRIMES | PIPELINE INSTALLED AND BLOWN DOWN SAME DAY. AWAITING REPAIR GAS PRODUCER TO PAY FOR REPAIR
| 00-30204-1 | 302 |  | 6 | [7 empty] | 2000-05-26 | [5 empty] | GRIMES | PIPE INSTALLED & AWAITING REPAIR PER JOE VILLADANDO
| 00-30203-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Digin |  | 2000-05-24 | 2000-05-25 | Other |  |  |  | SUTTER | INSTALL 63' NEW DOGLEG WITH 6' EACH OVER BENDS
| 00-30202-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | External Corrosion | INTERNAL CORROSION | 2000-02-29 | 2000-05-18 | Other | 7' PIPE |  |  | COLUSA | REPAIR LEAK WITH 7' .188 WT PRETESTED PIPE #7007086
| 00-30202-1 |  |  | 4 | Gathering | [6 empty] | 2000-02-29 | [5 empty] | COLUSA
| 00-30201-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2000-01-18 | 2000-03-03 | Other | 2' PIPE |  |  | S/O SUTTER | PRODUCER SUTION <100PSIG UPSTREAM OF KELLOGG #2 M.M.; REPLACED WITH 2' OF .188WT PRETESTED PIPE JOB #7029948
| 00-30204-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2000-05-26 | 2000-12-07 | Weld Over Sleeve or Can |  |  |  | GRIMES | REPLACED 4FT OF TESTED PIPE; PIPELINE INSTALLED AND BLOWN DOWN SAME DAY. AWAITING REPAIR GAS PRODUCER TO PAY FOR REPAIR
| 00-30205-1 | 302 | 9.17 | 30 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2000-08-16 | 2000-08-17 | Welded Sleeve/Can - Weld |  |  |  | S/O GRIMES | REPLACED WITH 88 3/4" PRETESTED PIPE (1/8" PIN HOLE)
| 00-30205-1 | 302 |  | 20 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2000-08-16 | [5 empty] | S/O GRIMES
| 00-30206-1 |  |  | 24 | Gathering |  | Drip |  |  | Internal Corrosion |  | 2000-08-25 | 2001-07-24 | ABANDON | OTHER- RETIRED |  |  | S/O MERIDIAN | BYPASSED DRIP BY WELDING 16" X 6" REDUCTION TO SCRUBBER INLET.
| 00-20001-1 | 200 |  | 6.625 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2000-06-23 | 2000-07-06 | Other |  |  |  | HASTING ISLAND | INSTALLED LEAK CLAMP
| 00-20002-1 | 200 |  | 0.5 | Gathering |  | Drip |  |  | Damage by 3rd Party |  | 2000-11-06 | 2000-11-07 | Other | INST. VALVE |  |  | RIO VISTA | INSTALL NEW VALVE; VALVE REPLACED WITH NEW 1/2" VALVE
| 00-19501-1 | 195 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion | UNKNOWN | 2000-10-06 | 2000-11-16 | Mechanical Repair Fitting - Fitting |  |  |  | RIO VISTA | INSTALLED LREAK CLAMP, INTERNAL CORROSION PERFORATED PIPE
| 00-17401-1 | 302 |  | 10 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2000-06-30 | 2000-08-01 | Other | WELD CAP |  |  | ARBUCKLE | WELD CAP WITH SAV-A-VALVE TO ... 4' STUB WITH OLD TAP VALVE.
| 00-16901-1 |  |  | 6 | [5 empty] | Internal Corrosion |  | 2000-05-04 | [5 empty] | WILLOWS | PIPELINE TO BE RETIRED ON SO 6047783, CLEARANCE ME-00-32 PIPELINE ISOLATED AND BLOWN DOWN
| 00-16901-1 | 169 |  | 6 | [5 empty] | Internal Corrosion |  | 2000-05-04 | [5 empty] | WILLOWS | BUBBLES IN FLOODED RICE FIELD
| 00-16901-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2000-05-04 | 2001-02-01 | Other | RETIRED |  |  | WILLOWS | PIPELINE TO BE RETIRED ON S0# 6047783, CLEARANCE ME 00-32. PIPELINE ISOLATED AND BLOWN DOWN
| 00-16701-1 | 169 | 1.13 | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2000-02-25 | 2000-08-03 | Weld Over Sleeve or Can |  |  |  | PRINCETON | INSTALLED 36" PRETESTED 12" .28I PIPE WITH SAV-A-VALVE
| 00-16702-1 |  |  | 12 | Gathering | CONV. TO DISTRIBUTION | [5 empty] | 2000-08-08 | [5 empty] | PRINCETON
| 00-16702-1 | 167 | 1.3 | 12 | [7 empty] | 2000-08-08 | [5 empty] | PRINCETON
| 00-16702-1 | 167 | 1.3 | 12 | [7 empty] | 2000-08-08 | [5 empty] | PRINCETON
| 00-16703-1 | 167 | 1.18 | 12 | Gathering | CONV. TO DISTRIBUTION | Body of Pipe |  |  | Internal Corrosion |  | 2000-08-08 | 2001-02-28 | Other | REPLACE |  |  | PRINCETON | NONE REPLACED WITH TESTED PIPE ON 12-15-99; REPLACED 25' 8" OF 12" PIPE. SOUTH TIED TO PREVIOUS LEAK REPLACEMENT OF .281 Y42ERW
| 00-16704-1 |  |  | 12 | Gathering | CONV. TO DISTRIBUTION | [5 empty] | 2000-08-08 | [5 empty] | PRINCETON
| 00-16704-1 | 167 | 1.34 | 12 | [7 empty] | 2000-08-08 | [5 empty] | PRINCETON
| 00-16704-1 | 167 | 1.34 | 12 | [7 empty] | 2000-08-08 | [5 empty] | PRINCETON
| 00-14501-1 | 145 | [9 empty] | 2000-07-20 | 2000-07-22 |  |  |  |  | DIXON | INSTALL 24" 4" PIPE
| 00-14301-1 | 143 |  | 6.25 |  |  | Body of Pipe |  |  | Internal Corrosion |  | 2000-07-13 | 2000-07-14 |  |  |  |  | DIXON | CUT AND CAP LINE
| 00-14302-1 | 143 |  | 6.62 | Gathering |  | Body of Pipe |  |  | Other | SENT FOR ANALYSIS | 2000-08-20 | 2000-08-16 | Other | PIPE REPLACEMENT |  |  | DIXON/SOLANO CO. | INSTALL 48" OF NEW 156 WALL X 42 ERW 6" PIPE PRETESTED EMERGENCY STOCK
| 00-14303-1 | 143 |  |  | Gathering |  | Body of Pipe |  |  | Unknown |  | 2000-08-20 | 2000-09-24 | Other | NEW DOGLEG |  |  | DIXON / SOLANO COUNTY | FABRICATE AND INSTALL NEW DOGLEG OVER CULVERT
|  |  |  | 12 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2000-10-10 | 2000-10-10 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | DUBLIN | WELDED SLEEVE OVER CORRISON PIT
|  | 1501-01 |  | 4 | Transmission |  | Body of Pipe |  |  | Digin |  | 2000-06-12 | 2000-06-12 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | YUBA CITY CA | GE GAS MADE REPAIRS; ALL SOAP TESTED, BY CREW
| 10-11029-1 | 153 | 25.34 | 24 | Transmission |  | Girth Weld |  |  | External Corrosion |  | 2010-02-23 | 2010-02-25 | Other |  | Steel/Wrought Iron |  | OAKLAND | REPLACED 5' OF 24" PIPE
| 09-00085-1 | 21E | 95.91 | 12 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2009-06-18 | 2009-06-18 | Welded Sav-A-Valve - Weld |  | Steel/Wrought Iron |  | HOPLAND | SOAP
| 10-00017-1 | [10 empty] | 2010-03-17 | [5 empty] | OLIVEHURST
| 10-40008-1 | [10 empty] | 2010-03-04 | [5 empty] | KING CITY
| 10-70010-1 | 177A | 48.85 | [8 empty] | 2010-03-27 | [5 empty] | RED BLUFF
| 10-20530-1 | 311 | 8.7 | [8 empty] | 2010-03-29 | [5 empty] | BORON
| 10-20529-1 | 311 | 17.39 | [8 empty] | 2010-03-29 | [5 empty] | BORON
| 09-00161-1 | 6-0404-4 |  | 6 | Transmission |  | Other |  |  | Weld Failure |  | 2009-12-03 | 2010-02-18 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | BENICIA | PLIDCO SPLIT SLEEVE #1803517/1000WP/WCCP; SOAP TEST/MAG FLUX TEST
| 10-00099-1 | 21 |  | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2010-03-22 |  |  |  | Steel/Wrought Iron |  | COTATI
| 08-50095-1 | 103 | 1.7 | 0.75 | Branch Service |  | Valves |  |  | Other |  | 2008-11-21 | 2010-02-26 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | SALINAS | REPLACED SERVICE VALVE; REPLACED DEFECTIVE STOPCOCK WITH A NEW STOCK COCK- SOAP TEST 10 MINUTES
| 09-35004-1 |  |  | 0.75 | Single Service |  | Valves |  |  | Other |  | 2009-06-09 | 2010-03-08 | Other |  | Steel/Wrought Iron |  | MERIDIAN | CLOSE VALVE, DOPE & TIGHTEN PLUG; SLOCE METRIC DOPE & TIGHTEN PLUG- SOAP TESTED
| 08-25018-1 | 132 | 0 | 30 | Transmission |  | Valves |  |  | Other |  | 2008-09-17 | 2010-02-17 | Other |  | Steel/Wrought Iron |  | HILLSBOROUGH | GREASED VALVE TO SOTP LEAK; GREASED VALVE #177
| 08-25019-1 | 109 | 3.055 | 3 | Transmission |  | Valves |  |  | Other |  | 2008-09-17 | 2010-02-15 | Other |  | Steel/Wrought Iron |  | SAN MATEO | GREASED VALVE TO STOP LEAK; GREASED VALVE V-1 IN REG PIT
| 09-50426-1 | 301G | 16.82 | 0.75 | Distribution Main |  | Valves |  |  | Other |  | 2009-10-27 | 2010-01-14 | Other |  | Steel/Wrought Iron |  | SALINAS | REPLACED BYPASS VALVE AND TIGHTENED UNION; HOT TANKED MAIN AND REPLACED BYPASS VALVE AND REPAIRED UNION
| 08-00059-1 | 021E |  | 1 | Distribution Main |  | Other |  |  | Other |  | 2008-04-30 | 2009-12-02 | Other |  | Steel/Wrought Iron |  | UKIAH | TIGHTEN TEE CAP
| 06-30401-1 | 304 | 3.11 | 12 | Gathering |  | Valves |  |  | Other |  | 2006-04-06 | 2008-12-09 | Other |  | Other |  | TRACY
| 09-35081-1 | 116 |  | 1 | Transmission |  | Other |  |  | Other |  | 2009-10-16 | 2009-12-29 | Other |  | Steel/Wrought Iron |  | DAVIS | REPLACED O-RINGS IN CAP; REPLACED O-RINGS IN CAP OF PIN-OFF TEE
| 09-35082-1 | 116 |  | 1 | Transmission |  | Other |  |  | Other |  | 2009-10-16 | 2009-12-29 | Other |  | Steel/Wrought Iron |  | DAVIS | REPLACED O-RINGS IN CAP
| 09-50557-1 | MTY1 |  | 12 | Transmission |  | Unknown |  |  | Unknown |  | 2009-12-16 | 2010-01-13 | Other |  | Steel/Wrought Iron |  | SALINAS | GREASED VALVE 4.08
| 09-50333-1 | 187 | 0.17 | 0.75 | Transmission |  | Valves |  |  | Other |  | 2009-10-09 | 2010-01-06 | Other |  | Steel/Wrought Iron |  | SALINAS | FEW LUB FITTINGS LEAKING - GREASED VALVE; FOUND FEW SMALL LEAKS AT VALVE SITE SVQ12, GREASED VALVE
| 09-50427-1 | 301A | 19.47 | 0.75 | Distribution Main |  | Other |  |  | Other |  | 2009-10-27 | 2010-01-08 | Other |  | Steel/Wrought Iron |  | PRUNEDALE | TIGHTENED UNION FITTING; LEAK ON UNION- REPAIRED BY TIGHTEN
| 09-10130-1 | 173 |  | 4 | Distribution Main |  | Valves |  |  | Other |  | 2009-12-03 | 2010-01-15 | Other |  | Steel/Wrought Iron |  | ROCKLIN | ADDED MORE GREASE
| 09-02161-1 | 173 |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2009-11-03 | 2010-01-22 | Other |  | Steel/Wrought Iron |  | NEWCASTLE | GREASED
| 09-02163-1 | 173 |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2009-11-03 | 2010-01-22 | Other |  | Steel/Wrought Iron |  | PENRYN | GREASED
| 09-02165-1 | 173 |  | 0.25 | Transmission |  | Valves |  |  | Other |  | 2009-11-03 | 2010-01-22 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ROCKLIN | GREASED PLUG & TIGHTENED
| 09-04387-1 | 173 |  | 6 | Transmission |  | Valves |  |  | Other |  | 2009-11-03 | 2010-01-15 | Other |  | Steel/Wrought Iron |  | LOOMIS | ADDED GREASE
| 09-10032-1 | 173 |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2009-09-25 | 2010-01-22 | Other |  | Steel/Wrought Iron |  | NEWCASTLE | GREASED
| 09-80110-1 | 402/DFM | 16.73 | 0.25 | Transmission |  | Valves |  |  | Other |  | 2009-06-03 | 2009-11-19 | Other |  | Steel/Wrought Iron |  | REDDING | TIGHTENED METRIC VALVE CORE
| 09-33313-1 | 210B |  | 6 | Distribution Main |  | Valves |  |  | Unknown |  | 2009-10-06 | 2010-01-04 | Other |  | Steel/Wrought Iron |  | SUISUN | RESEATED CHECK VALVE TO STOP LEAK; RESEATED BODY BLEED CHECK VALVE -SOAP TESTED- NO LEAKS
| 09-30201-1 |  |  | 6 | Gathering |  | Valves |  |  | Other |  | 2009-06-09 | 2009-06-10 | Other |  | Steel/Wrought Iron |  | PALO ALTO | FOAMS ON REG SET
| 09-20018-1 | [10 empty] | 2009-03-25 | [5 empty] | WATSONVILLE
| 09-10216-1 | [10 empty] | 2009-06-04 | [5 empty] | SANTA CRUZ
| 09-33314-1 | [10 empty] | 2009-10-06 | [5 empty] | VACAVILLE
| 09-35080-1 | 116 | [9 empty] | 2009-10-16 | [5 empty] | DAVIS
| 09-23282-1 | 108 | [9 empty] | 2009-12-18 | [5 empty] | SACRAMENTO
| 09-80111-1 | 402/DFM | 21.41 | 6 | Transmission |  | Other |  |  | Other |  | 2009-06-03 | 2010-01-14 | Other |  | Steel/Wrought Iron |  | REDDING | SOAP TEST
| 10-20505-1 | DREG5496 | 2.97 | [8 empty] | 2010-01-11 | [5 empty] | RIDGECREST
| 10-20506-1 | [10 empty] | 2010-01-25 | [5 empty] | EDWARDS
| 10-30054-1 | 0 |  | 4 | Transmission |  | Fitting |  |  | Other |  | 2010-01-11 |  |  |  | Steel/Wrought Iron |  | GUSTINE
| 10-50002-1 | 301F | [9 empty] | 2010-01-04 | [5 empty] | SALINAS
| 10-50003-1 | 301F | [9 empty] | 2010-01-04 | [5 empty] | SALINAS
| 10-50004-1 | 301F | [9 empty] | 2010-01-04 | [5 empty] | SALINAS
| 10-50005-1 | 301F | [9 empty] | 2010-01-05 | [5 empty] | SALINAS
| 10-50006-1 | 301F | [9 empty] | 2010-01-05 | [5 empty] | SALINAS
| 10-90321-1 | 174 | [9 empty] | 2010-01-11 | [5 empty] | ARBUCKLE
| 10-90322-1 | 174 | [9 empty] | 2010-01-11 | [5 empty] | ARBUCKLE
| 10-90323-1 | 174 | [9 empty] | 2010-01-11 | [5 empty] | ARBUCKLE
| 09-40013-1 | 310 | [9 empty] | 2009-02-24 | [5 empty] | KING CITY
| 09-40010-1 | 310 | [9 empty] | 2009-02-24 | [5 empty] | KING CITY
| 09-40011-1 | [10 empty] | 2009-02-24 | [5 empty] | KING CITY
| 09-02164-1 | 6-173 |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2009-11-03 | 2010-01-27 | Other |  | Steel/Wrought Iron |  | PENRYN | REPLACED V-TEE CAP & O-RINGS
| 09-30255-1 | 132 | 42.99 | 30 | Transmission |  | Girth Weld |  |  | Weld Failure |  | 2009-11-16 | 2010-02-02 | Type B Sleeve - Weld |  | Steel/Wrought Iron |  | SOUTH SAN FRANCISCO | INS'D 30 IN SLEEVE, 625 WT X 60
| 10-00049-1 | 21 |  | 12 | Transmission |  | Other |  |  | Equipment Malfunction |  | 2010-02-10 | 2010-02-12 | Other |  | Steel/Wrought Iron |  | SANTA ROSA | REPLACED EQUAL REV VALVE IN INTERNAL PLU
| 10-10006-1 | [10 empty] | 2010-02-25 | [5 empty] | SANTA CRUZ
| 10-10007-1 | [10 empty] | 2010-02-25 | [5 empty] | SANTA CRUZ
| 10-10009-1 | [10 empty] | 2010-02-25 | [5 empty] | SANTA CRUZ
| 10-33001-1 | 143 |  | 3 | Transmission |  | Valves |  |  | Other |  | 2010-02-08 |  |  |  | Steel/Wrought Iron |  | DIXON
| 10-43067-1 |  | 180.39 | [8 empty] | 2010-02-24 | [5 empty] | MARTINEZ
| 10-20010-1 | [10 empty] | 2010-01-25 | [5 empty] | STANFORD
| 10-00064-1 | 21 | [9 empty] | 2010-02-18 | [5 empty] | PETALUMA
| 09-30005-1 | 300A | 274.69 | 34 | Transmission |  | Other |  |  | Unknown |  | 2009-04-28 | 2009-07-23 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | KETTLEMAN CITY | REMV'D UNIBOLT CAP, CLEANED & REPL'D CAP; JULY 0 LEAKS
|  |  | 0.2381 | 12 | [11 empty] | Steel/Wrought Iron |  | WOODRIDGE | 1614.04 M.P. 2.2381; INSPECTIONS & LEAKS; DONE VERSION: JULY_LEAKS_INSP; ALL 4; CHECKED & POSTED, 8/24/08
|  |  | 0.4326 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | WOODRIDGE | 1614.04 MP. 0.4326
|  |  | 0.0736 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DSBN9194 MP. 0.0736
| 09-00137-1 | 50 |  | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2009-07-08 | 2009-07-17 | Other |  | Steel/Wrought Iron |  | LIVE OAK | OEOA T CT HCA; INSTALL 8" LEAK CLAMP / GC WELD OUT;
| 09-00050-1 | 6040501 |  | 2 | Transmission |  | Other |  |  | Other |  | 2009-06-04 | 2009-07-03 | Other |  | Steel/Wrought Iron |  | ST. HELENA | REPAIRED LEAKS ON 2" MUELLER VALVE TEES; SOAP TEST
| 09-00465-1 | 1307-01 |  | 2 | Transmission |  | Valves |  |  | Unknown |  | 2009-07-09 | 2009-08-07 | Other |  | Steel/Wrought Iron |  | WINDSOR | V-A & V-B SHILOH & CONDE LN. WINDSOR
| 09-00467-1 | [10 empty] | 2009-07-13 | [5 empty] | PETALUMA
| 09-00472-1 | 021E | 68 | [8 empty] | 2009-07-13 | [5 empty] | HEALDSBURG
| 09-11402-1 | 114 | 8.18 |  | Transmission | [6 empty] | 2009-07-08 | [5 empty] | OAKLEY
| 09-20112-1 | [10 empty] | 2009-07-02 | [5 empty] | BAKERSFIELD | 375 T LT
| 09-20113-1 | 375 | [9 empty] | 2009-07-02 | [5 empty] | BAKERSFIELD | 375 T LT
| 09-21404-1 | DFM |  | 8 | Transmission |  | Valves |  |  | Construction Defect |  | 2009-06-16 |  |  |  | Steel/Wrought Iron |  | SACRAMENTO
| 09-30030-1 | 126A | 10.78 | 6 | [7 empty] | 2009-07-28 | [5 empty] | EUREKA | LEAK OVER 6" GAS TRANSMISSION MAIN.
| 09-35017-1 | [10 empty] | 2009-07-21 | [5 empty] | ARBUCKLE | 0634-01 D DFM.
| 09-50126-1 | 301B |  | 0.75 | Single Service |  | Valves |  |  | Other |  | 2009-05-07 | 2009-07-01 | Other |  | Steel/Wrought Iron |  | SALINAS | DCUST2526 D SERY; STOPCOCK VALVE; LEAKING BELOW STOPCOCK - REPAIRED.
| 09-50165-1 | 103 | 23.55 | [8 empty] | 2009-07-06 | [5 empty] | SALINAS
| 08-50092-1 | 301C | 14.41 | 0.75 | Distribution Main |  | Other |  |  | Unknown |  | 2008-11-21 | 2009-07-03 | Other |  | Steel/Wrought Iron |  | SALINAS | GREASED VALVE AND REPLACED RELIEF; NON G-15 3/4" PIPE.
| 08-80076-1 | DFM |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2008-06-23 | 2009-07-20 | Other |  | Steel/Wrought Iron |  | GLENBURN | DELETES; GREASE VALVE - SOAP TEST.
| 09-02138-1 | DFM |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2009-04-29 | 2009-07-23 | Other |  | Steel/Wrought Iron |  | LODI | TIGHTENED 3/4" VALVE.
| 09-50142-1 | 103 | 23.55 | [8 empty] | 2009-05-23 | [5 empty] | SALINAS
| 09-70384-1 | DFM |  | 12 | Transmission |  | Valves |  |  | Other |  | 2009-04-01 | 2009-06-30 | Other |  | Steel/Wrought Iron |  | FOLSOM | TIGHTENED 1/2" STL GREASE STEM & GREADED V
| 09-00201-1 | 2 |  | 26 | Transmission |  | Unknown |  |  | Unknown |  | 2009-03-09 | 2009-07-03 | Other |  | Steel/Wrought Iron |  | TRACY | GAS SUPPLY REGULATE GASKET AND TUBING FI; JULY 09. PRE. MAPPED. NOW REPAIRED. NO BOOKMARKS?..
| 09-00204-1 | 2 |  | 26 | Transmission |  | Unknown |  |  | Unknown |  | 2009-04-06 | 2009-07-03 | Other |  | Steel/Wrought Iron |  | TRACY
| 09-19001-1 | 190 | 0 | 12 | Transmission |  | Other |  |  | Unknown |  | 2009-04-02 | 2009-06-05 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | AVENAL
| 09-30601-1 | 306 | 0 | 20 | Transmission |  | Valves |  |  | Unknown |  | 2009-04-02 | 2009-06-08 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | AVENAL
| 09-30602-1 | 306 | 0 | 20 | Transmission |  | Unknown |  |  | Unknown |  | 2009-04-02 | 2009-06-08 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | AVENAL
| 09-60081-1 | 50 |  | 8 | Transmission |  | Fitting |  |  | Construction Defect |  | 2009-06-17 | 2009-07-08 | Replace TP Main |  | Steel/Wrought Iron |  | OROVILLE | REPLACED 42' OF TP PIPE.
| 09-60096-1 | 50 |  | 0.75 | Transmission |  | Other |  |  | Construction Defect |  | 2009-07-16 |  |  |  | Steel/Wrought Iron |  | GRIDLEY
| 09-90106-1 | 167 | [9 empty] | 2009-07-14 | [5 empty] | LIVE OAK | LEAK @ ELBOW & UNION 50' FROM HOUSE @ REG STATION.
| 09-80110-1 | 402/DFM | 16.73 | [8 empty] | 2009-06-03 | [5 empty] | REDDING
| 09-80112-1 | 402/DFM | [9 empty] | 2009-06-03 | [5 empty] | REDDING | DREG 7541 D SERV.
| 09-80116-1 | 402/DFM | 23.99 | [8 empty] | 2009-06-03 | [5 empty] | REDDING | DREG5479 T1 SERV.
| 09-80117-1 | 402/DFM | 23.99 | [8 empty] | 2009-06-03 | [5 empty] | REDDING | DREG5479 T1 SERV.
| 09-80118-1 | 402/DFM | [9 empty] | 2009-06-08 | [5 empty] | COTTONWOOD | DREG4246 D SERV.
| 09-60087-1 | [10 empty] | 2009-06-24 | [5 empty] | OROVILLE | 1027-04 T DFM.
| 09-60088-1 | [10 empty] | 2009-06-24 | [5 empty] | GRIDLEY | 50A T LT.
| 09-60089-1 | [10 empty] | 2009-06-24 | [5 empty] | GRIDLEY | 50 A T LT.
| 09-60090-1 | [10 empty] | 2009-06-24 | [5 empty] | GRIDLEY | DCUST928 D SERV.
| 09-60091-1 | [10 empty] | 2009-06-24 | [5 empty] | GRIDLEY | 50A T LT.
| 09-80061-1 | [10 empty] | 2009-06-15 | [5 empty] | HERCULES | BD9325
| 09-35004-1 | [10 empty] | 2009-06-09 | [5 empty] | MERIDIAN | 0630-01 TP DFM.
| 09-35002-1 | [10 empty] | 2009-06-11 | [5 empty] | WILLIAMS | GCUST7854 TC SERV.
| 09-35003-1 | [10 empty] | 2009-06-12 | [5 empty] | DUNNIGAN | DREG4987 T1 SERV.
| 09-35001-1 | [10 empty] | 2009-06-11 | [5 empty] | WILLIAMS | 0638-02 T1 DFM.
| 09-20045-1 | [10 empty] | 2009-06-03 | [5 empty] | WATSONVILLE | DREG5104 D SERV.
| 09-20046-1 | [10 empty] | 2009-06-03 | [5 empty] | WATSONVILLE | DREG5102 D SERV.
| 09-20048-1 | [10 empty] | 2000-06-03 | [5 empty] | AROMAS | RCUST2214 D SERV.
| 09-20049-1 | [10 empty] | 2009-06-03 | [5 empty] | AROMAS | DREG 5189 D SERV.
| 09-20343-1 | [10 empty] | 2009-06-18 | [5 empty] | DURHAM | DREG4012 D SERV.
| 09-20362-1 | [10 empty] | 2009-06-25 | [5 empty] | DURHAM | 50A T LT.
| 09-20570-1 | [10 empty] | 2009-06-26 | [5 empty] | KRAMER | 6614-01 T DFM. PLUG ON TOP OF PRIMARY FILTER.
| 09-21138-1 | [10 empty] | 2009-06-04 | [5 empty] | SACRAMENTO | BD8442 N/A BD.
| 09-21139-1 | [10 empty] | 2009-06-04 | [5 empty] | CITRUS HEIGHTS | 0617-06 TP DFM
| 09-21158-1 | [10 empty] | 2009-06-10 | [5 empty] | SACRAMENTO | 0615-01 TP DFM.
| 09-21160-1 | [10 empty] | 2009-06-11 | [5 empty] | SACRAMENTO | DFDS3562 T SERV.
| 09-21161-1 | [10 empty] | 2009-06-11 | [5 empty] | SACRAMENTO | 0618-03 T DFM.
| 09-21167-1 | [10 empty] | 2009-06-12 | [5 empty] | SACRAMENTO | 0613-01 TP DFM.
| 09-21177-1 | 119B | [9 empty] | 2009-06-15 | [5 empty] | SACRAMENTO | 0617-01 T DFM.
| 09-21220-1 | [10 empty] | 2009-06-24 | [5 empty] | SACRAMENTO | 0639-01 T DFM.
| 09-30026-1 | [10 empty] | 2009-05-30 | [5 empty] | ARCATA | 137D D LT.
| 09-20042-1 | [10 empty] | 2009-06-03 | [5 empty] | AROMAS | 181A T LT.
| 09-20043-1 | 191 | [9 empty] | 2009-06-03 | [5 empty] | WATSONVILLE | GCUST5864 TC SERV.
| 09-20044-1 | [10 empty] | 2009-06-03 | [5 empty] | WATSONVILLE | DFDS 3654 TP DFM.
| 09-20039-1 | [10 empty] | 2009-06-02 | [5 empty] | WATSONVILLE | 1816-01 T1 DFM.
| 09-20041-1 | [10 empty] | 2009-06-02 | [5 empty] | WATSONVILLE | 1816-01 T1 DFM.
| 09-10216-1 | [10 empty] | 2009-06-04 | [5 empty] | SANTA CRUZ | 1818-01 T DFM.
| 09-30201-1 |  |  | 6 | Gathering |  | Valves |  |  | Other |  | 2009-06-09 | 2009-06-10 | Other |  | Steel/Wrought Iron |  | PALO ALTO | GCUST5814 TC SERV HCA.; FOAMS ON REG SET
| 09-20013-1 | 181B |  | 6 | Transmission |  | Other |  |  | Unknown |  | 2009-03-27 | 2009-05-14 | Other |  | Steel/Wrought Iron |  | PAJARO | B.D. 361.; CLEAN "O" RINGS
| 08-50076-1 | 301C | 16.15 | 0.75 | Distribution Main |  | Regulator |  |  | Atmospheric Corrosion |  | 2008-11-21 | 2009-06-23 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | SALINAS | DREG5416 D SERV TXPS.; LEAK ON HI TO HI SET REPLACED DOWN STREAM STOPCOCK
| 09-50077-1 | 187 | 63.44 | 0.75 | Distribution Main |  | Regulator |  |  | Other |  | 2009-04-10 | 2009-06-25 | Other |  | Steel/Wrought Iron |  | SALINAS | DCUST 2193 D SERV.; REMARKS OLD HI2HI SET REPLACED WITH REG STATION.; REPLACED H2H REG FISHER 627
| 09-00231-1 | 021E | 66 | 2 | Distribution Main |  | Fitting |  |  | Other |  | 2009-03-21 | 2009-06-16 | Other |  | Steel/Wrought Iron |  | HEALDSBURG | 021E T LT.; REMOVE, REDOPE, REINSERT 2" COMPLETION P
| 08-35003-1 | DFM |  | 1 | Transmission |  | Fitting |  |  | Unknown |  | 2008-11-05 | 2009-06-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | DUNNIGAN | DREG 4987 T1 SERV TXPS.; TIGHTEN CAP
| 05-40001-1 | 401 | 1978 | 42 | Transmission |  | Unknown |  |  | Unknown |  | 2005-06-24 | 2006-05-05 | Other |  | Other |  | DELEVAN COMPR. STA. | LEAK IS UNDETECTABLE, VLV WAS INSTALLED &
| 09-70029-1 | 177 | 88.8 | 0.75 | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-05-13 | 2009-05-14 | Other |  | Steel/Wrought Iron |  | HARRISON GULCH | REG 5040 T1 SERV TXPS; SOAP TEST.
| 09-50077-1 | 187 | 63.44 | [8 empty] | 2009-04-10 | [5 empty] | SALINAS
| 09-70260-1 | DFM | [9 empty] | 2009-04-02 | [5 empty] | FOLSOM | DCUST8593 T1 SERV.
| 09-53056-1 | DFM |  | 6 | Transmission |  | Valves |  |  | Other |  | 2009-02-04 | 2009-04-01 | Other |  | Steel/Wrought Iron |  | DIXON | 0600-05 D DFM
| 09-50108-1 | 301A | [9 empty] | 2009-04-27 | [5 empty] | SALINAS | DFDS3693 D SERV.
| 09-50107-1 | 301A | [9 empty] | 2009-04-25 | [5 empty] | MOSS LANDING | GCUST5911 TC SERV.
| 09-35038-1 | 118 | 37.58 | [8 empty] | 2009-04-06 | [5 empty] | FAIRMEAD | DREG4433 T1 SERV.
| 09-20500-1 | [10 empty] | 2009-04-18 | [5 empty] | SAN LEANDRO | 153 T LT.
| 09-20021-1 | [10 empty] | 2009-04-21 | [5 empty] | WATSONVILLE | 1816-05 W1 DFM.
| 09-20501-1 | [10 empty] | 2009-04-18 | [5 empty] | SAN LEANDRO | DF8158 T1 SERV.
| 09-40022-1 | 310 | [9 empty] | 2009-03-26 | [5 empty] | KING CITY | GCUST5913 TC SERV.
| 09-35035-1 | 183 | 6.28 | [8 empty] | 2009-03-30 | [5 empty] | FIREBAUGH | 183 T LT.
| 09-70384-1 | [10 empty] | 2009-04-01 | [5 empty] | FOLSOM | 0617-06 T DFM.
| 09-35006-1 | [10 empty] | 2009-03-31 | [5 empty] | YOLO | 172A T LT.
| 09-30015-1 | 137D | 15 | 10 | Transmission |  | Girth Weld |  |  | Weld Failure |  | 2009-03-26 | 2009-03-27 | Other |  | Steel/Wrought Iron |  | ARCATA | CUTT-OFF 3' - 16" CASING & REPAIRED GIRTH W; SOAP TESTED, VISUAL & POST X-RAY/MAG FLEX.
| 09-70089-1 | 1815-02 |  | 0.75 | Transmission |  | Regulator |  |  | Other |  | 2009-03-26 | 2009-04-01 | Other |  | Steel/Wrought Iron |  | MONTEREY | REGULATOR; REGULATOR WAS LEAKING ON FITTING (3/4") BYPASSES SERVICE AND REPAIRED FITTING ON TRANSMISSION SIDE (INLET).
| 09-20002-1 | [10 empty] | 2009-05-18 | [5 empty] | EUREKA | 126B T. NOT HCA. HUMBOLDT LT. TXPS.
| 09-00503-1 | SP5 |  |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-05-18 | [5 empty] | ANTIOCH | HCA T SP5 TXPS.
| 09-35018-1 | 116 | [9 empty] | 2009-05-12 | [5 empty] | DAVIS | 116 T HCA YOLO.
| 09-50114-1 | 187 | [9 empty] | 2009-04-28 | [5 empty] | SALINAS | HARKINS STATION/187 T. NOT HCA. MONTEREY TXPS.
| 09-50139-1 | [10 empty] | 2009-05-23 | [5 empty] | SALINAS | DFDS 3572 SEG 204. VALVE MP 0.00. NOT HCA. MONTEREY TXPS.
| 09-50133-1 | 103 | [9 empty] | 2009-05-23 | [5 empty] | SALINAS | GCUST5870. TC. NOT HCA. MONETERY TXPS.
| 09-50140-1 | 103 | [9 empty] | 2009-05-23 | [5 empty] | SALINAS | DREG4257. TI. NOT HCA. NOTEREY TXPS.
| 09-33112-1 | 210 |  | 12 | Transmission |  | Tap Connection |  |  | Weld Failure |  | 2009-05-14 | 2009-05-14 | Fill Weld - Weld |  | Steel/Wrought Iron |  | SUISUN | WELDED PINHOLE LEAK
| 09-02138-1 | [10 empty] | 2009-04-29 | [5 empty] | LODI | 1614-08 SEG 301. HCA TI. TXPS.
| 09-33081-1 | [10 empty] | 2009-05-01 | [5 empty] | VICTORVILLE | LEAK ON VLV W-12 IN CROSSWALK. 0604-01 SEG 106. T HCA. SOLANO TXPS.
| 09-50142-1 | 103 | 23.65 | [8 empty] | 2009-05-23 | [5 empty] | SALINAS | STATION / 103. T HCA. MONTEREY TXPS. ROSSI REG ST., SHERWOOD DRIVE BOTH BANKS LEAKING.
| 09-50141-1 | 103 | [9 empty] | 2009-05-23 | [5 empty] | SALINAS | 103 SEG 135. T HCA. MONTEREY TXPS.
| 09-50137-1 | 103 | [9 empty] | 2009-05-23 | [5 empty] | SALINAS | 103 SEG 144. T HCA. MONTEREY TXPS.
| 09-40005-1 | 400 | 97.66 | [8 empty] | 2009-05-26 | [5 empty] | RED BLUFF | 400 T. NOT HCA. SHASTA TXPS DUPLICATE.
| 09-10209-1 | [10 empty] | 2009-05-27 | [5 empty] | SANTA CRUZ | 1818-01 T DFM.
| 09-19101-1 | 191 | 5.43 | [8 empty] | 2009-05-29 | [5 empty] | ANTIOCH
| 09-20004-1 | [10 empty] | 2009-05-30 | [5 empty] | ARCATA | 137D D LT.
| 09-20007-1 | [10 empty] | 2009-05-30 | [5 empty] | ARCATA | 137D D LT.
| 09-00420-1 | DFM 1301 | 28.82 | 8 | Transmission |  | Valves |  |  | Material Failure |  | 2009-05-30 |  |  |  | Steel/Wrought Iron |  | PENNGROVE | 1301-01 T DFM.
| 09-33156-1 | DFM | [9 empty] | 2009-05-13 | [5 empty] | DIXON | 0600-03 T DFM.
| 09-35000-1 | [10 empty] | 2009-06-11 | [5 empty] | PRINCETON | DREG4969 D SERV.
| 09-50145-1 | 103 | [9 empty] | 2009-05-30 | [5 empty] | SALINAS | 103T LT. MONTEREY FISH - H2H SET 5 X 8 LEAKING.
| 09-50146-1 | 103 | [9 empty] | 2009-05-30 | [5 empty] | SALINAS | 103 T LT.
| 09-60081-1 | [10 empty] | 2009-06-17 | [5 empty] | OROVILLE | 1027-12 D DFM.
| 09-00401-1 | [10 empty] | 2009-01-13 | [5 empty] | OAKLEY | READING AT VAULT LID. SP4Z. HCA NON-LEAK. TIGHTENED CAP PER RUDY LEAL.
| 09-11401-1 | 3009-01 | 0.08 | [8 empty] | 2009-01-13 | [5 empty] | OAKLEY | 3009-01 TC DFM.
| 09-70033-1 | [10 empty] | 2009-02-10 | [5 empty] | MARINA | T DFM 1813-02.
| 09-70043-1 | [10 empty] | 2009-02-13 | [5 empty] | MONTEREY | 1815-02 T DFM.
| 09-70087-1 | 1815-2 |  | 2 | Transmission |  | Valves |  |  | Other |  | 2009-03-26 | 2009-04-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MONTEREY | DREG 5088 D SERV.
| 09-70046-1 | [10 empty] | 2006-02-13 | [5 empty] | MONTEREY | 1815-02 T DFM.
| 09-70047-1 | [10 empty] | 2009-02-13 | [5 empty] | MONTEREY | 1815-02 T DFM. LEAK AT HPR SET LOW IN RAVINE MARKED IN YELLOW PT.
| 08-00033-1 | 021-E | 13591 | [8 empty] | 2008-04-28 | [5 empty] | WILLITS | DREG3857 T1 SERV. ON REG U79 LEAK ON UNION IN SECONDARY BOX.
| 08-00034-1 | 021-E | 13579 | [8 empty] | 2008-04-28 | [5 empty] | WILLITS | DREG 3856 T1 SERV.
| 08-00036-1 | 021-E | 13472 | [8 empty] | 2008-04-28 | [5 empty] | WILLITS | DREG3855 D SERV.
| 08-00037-1 | 021-E | 13368 | [8 empty] | 2008-04-28 | [5 empty] | WILLITS | 021E T LT. ION REG U75 LEAK ON TEE CAP IN PRIMARY BOX.
| 08-00038-1 | 021-E | 13353 | [8 empty] | 2008-04-28 | [5 empty] | WILLITS | 021E T LT. LEAK IN SECONDARY BOX ON REG @ T133.53.
| 08-00039-1 | 021-E | 13331 | [8 empty] | 2008-04-28 | [5 empty] | WILLITS
| 08-00040-1 | 021-E | 13304 | [8 empty] | 2008-04-28 | [5 empty] | WILLITS | LEAK IN PRIMARY BOX ON UNION. REG U 72. 021E T LT.
| 08-00041-1 | 021-E | 12419 | [8 empty] | 2008-04-29 | [5 empty] | REDWOOD VALLEY
| 08-00043-1 | 021-E | 12395 | [8 empty] | 2008-04-29 | [5 empty] | REDWOOD VALLEY
| 08-00044-1 | 021-E | 12395 | [8 empty] | 2008-04-29 | [5 empty] | REDWOOD VALLEY | D REG 3848 T1 SERV. NOT IN GIS 6/3/9. LEAK ON BOTTOM CAP IN SECONDARY BOX. REG. U 56.
| 08-00068-1 | 021-E | 9931 | [8 empty] | 2008-05-01 | [5 empty] | HOPLAND | DREG3815 T1 SERV. LEAK ON BOTTOM 3/4" CAP IN SECONDARY BOX. REG U06.
| 09-20058-1 | 101 |  | 8 | Transmission |  | Fitting |  |  | Construction Defect |  | 2009-03-17 |  |  |  | Steel/Wrought Iron |  | BRISBANE | 101 LT HCA NON LEAK PER D MCKORKLE.
| 09-53027-1 | DFM | [9 empty] | 2009-02-07 | [5 empty] | VACAVILLE | DREG40436 D SERV.
| 09-02015-1 | [10 empty] | 2009-02-03 | [5 empty] | ACAMPO | 1625-01 D DFM.
| 09-70045-1 | [10 empty] | 2009-02-13 | [5 empty] | MONTEREY | DREG 5085 D SERC TXPS. THERE IS AUTHOR OF 09-70045-1 LEAK NUMBER.
| 09-80105-1 | DFM | [9 empty] | 2009-05-23 | [5 empty] | SHASTA LAKE CITY | DREG5485 T1 SERV.
| 09-80106-1 | 402 | 36.23 | [8 empty] | 2009-05-23 | [5 empty] | MOUNTAIN GATE | DREG5490 T1 SERV.
| 09-80107-1 | 402 | 30.68 | [8 empty] | 2009-05-26 | [5 empty] | REDDING | DREG5484 T1 SERV.
| 09-80108-1 | 402 | 31.72 | [8 empty] | 2009-05-23 | [5 empty] | REDDING | 402 T LT.
| 09-80109-1 | [10 empty] | 2009-05-23 | [5 empty] | SHASTA LAKE CITY | DREG5489 D SERV.
| 09-00502-1 | SP5 |  |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-05-18 | [5 empty] | ANTIOCH | HCA T SP5.
| 09-40004-1 | 400 | [9 empty] | 2009-05-26 | [5 empty] | TULELAKE | 400 T. NOT HCA. MODOC.
| 09-05601-1 |  | 056A |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-04-30 |  |  |  | Steel/Wrought Iron |  | RIO VISTA | T LINE 056A. PLEASANT CREEK AREA. NOT HCA TXPS.
| 09-05602-1 | 056A |  |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-04-30 | [5 empty] | RIO VISTA | T L056A PLEASANT CREEK NOT HCA TXPS.
| 09-00033-1 | [10 empty] | 2009-04-24 | [5 empty] | PETALUMA | 021G T. NOT HCA. SONOMA LT. TXPS.
| 09-35016-1 | 116 | [9 empty] | 2009-05-12 | [5 empty] | DAVIS | 116T HCA YOLO TXPS.
| 09-50120-1 | 187 | [9 empty] | 2009-05-01 | [5 empty] | SOLEDAD | 187 SEG 144.4
| 09-10200-1 | [10 empty] | 2009-05-21 | [5 empty] | SANTA CRUZ | DREG5143 T 215. NOT HCA. SANTA CRUZ TXPS.
| 09-40046-1 | 187 | [9 empty] | 2009-05-04 | [5 empty] | GREENFIELD | GCUST5871 TC. NOT HCA. MONTEREY COUNTY. TXPS.
| 09-40044-1 | 187 | [9 empty] | 2009-05-04 | [5 empty] | GREENFIELD | L187 SEG 125 T. NOT HCA. MONTEREY COUNTY TXPS.
| 09-00037-1 | 021E | 13691 | [8 empty] | 2009-05-09 | [5 empty] | WILLITS | DREG3860 T SERV. NOT HCA. MENDOCINO TXPS. VALVE @ U-782, VALVE NEEDS GREASED.
| 09-00036-1 | 021E | 13247 | [8 empty] | 2009-05-09 | [5 empty] | WILLITS | REG STATION RIDGEWOOD + LAKEWOOD DR. D SERV TXPS MENDOCINO. GAUGE TAP LEAK.
| 09-20015-1 | [10 empty] | 2009-03-26 | [5 empty] | AROMAS | END OF ANTON PLACE K14 REG. ST CUSTOMER SMELLS GAS.
| 09-80014-1 | 300A | [9 empty] | 2009-04-23 | [5 empty] | HOLLISTER | DREG5362 T1 SERV.
| 09-80018-1 | 300A | [9 empty] | 2009-04-23 | [5 empty] | HOLLISTER | DREG5362 T1 SERV.
| 09-00035-1 | 021E | 12758 | [8 empty] | 2009-05-08 | [5 empty] | REDWOOD VALLEY | DREG3854 T SERV NOT HCA. MENDOCINA TXPS. LEAK IN VALVE BOX AT REG U-65.
| 09-00034-1 | 021E | 12758 | [8 empty] | 2009-05-08 | [5 empty] | REDWOOD VALLEY | DREG3854 T SERV. NOT HCA. MENDOCINO TXPS. LEAK IN PRIMARY BOX ON REG U-65.
| 09-00033-2 | 021E | 12668 | [8 empty] | 2009-05-08 | [5 empty] | REDWOOD VALLEY | LEAK IN BOTH PRIMARY BOXES, ON CAP & FLOW TUBE.DUPLICATE LEAK # AS PETALUMA, DREG3852 T SERV NOT HCA. MENDOCINO TXPS.
| 09-00032-1 | 021E | 12354 | [8 empty] | 2009-05-08 | [5 empty] | REDWOOD VALLEY | DREG 3486T SERV NOT HCA. MENDOCINO TXPS.
| 09-00031-1 | 021E | 12395 | [8 empty] | 2009-05-08 | [5 empty] | REDWOOD VALLEY | DREG3848T SERV. NOT HCA. MENDOCINO TXPS. LEAK IN PRIMARY BOX, ON CAP REG. U-56.
| 09-20003-1 | [10 empty] | 2009-05-23 | [5 empty] | CUDDEBACK | DREG5044 T NOT HCA. SERV TXPS.
| 09-00294-1 | 21C |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2009-05-13 |  |  |  | Steel/Wrought Iron |  | COTATI | REG. STATION 1302-02. T NOT HCA. SONOMA COUNTY TXPS.
| 09-40037-1 | 187 | [9 empty] | 2009-05-01 | [5 empty] | SOLEDAD | DREG5177. D NOT HCA. MONTEREY TXPS.
| 09-40036-1 | 187 | [9 empty] | 2009-05-01 | [5 empty] | SOLEDAD | DCUST2165. D NOT HCA. MONTEREY TXPS.
| 09-50118-1 | 187 | [9 empty] | 2009-05-01 | [5 empty] | SOLEDAD | GCUST5874. D NOT HCA. MONTEREY TXPS.
| 09-50119-1 | 187 | [9 empty] | 2009-05-01 | [5 empty] | SOLEDAD | STATION / GCUST5874. D NOT HCA. MONTEREY TXPS.
| 09-40083-1 | 187 | 28.16 | [8 empty] | 2009-05-18 | [5 empty] | KING CITY | DCUST2149 D. NOT HCA. MONTEREY.
| 09-40082-1 | 187 | 11.77 | [8 empty] | 2009-05-16 | [5 empty] | KING CITY
| 09-40047-1 | 187 | [9 empty] | 2009-05-04 | [5 empty] | KING CITY | DCUST2147 D. NOT HCA. MONTEREY COUNTY TXPS.
| 09-40051-1 | 187 | [9 empty] | 2009-05-08 | [5 empty] | KING CITY | DCUST2143 D. NOT HCA. MONTEREY COUNTY TXPS.
| 09-40048-1 | 187 | [9 empty] | 2009-05-06 | [5 empty] | KING CITY | DREG5174 D. NOT HCA. MONTEREY COUNTY TXPS. JOLON AND PINE CANYON - 2ND H TO H SET LEAK.
| 09-40042-1 | 187 | [9 empty] | 2009-05-04 | [5 empty] | KING CITY | DCUST2148 D. NOT HCA. MONTEREY COUNTY TXPS. HASM/LINE TAG - FISHER BLOW-OFF LEAKING AT UNION.
| 09-50116-1 | 187 | [9 empty] | 2009-04-30 | [5 empty] | GONZALES | DCUST2171 D. NOT HCA. MONTEREY COUNTY TXPS.
| 09-50128-1 | [10 empty] | 2009-05-08 | [5 empty] | CHUALAR | DCUST2180 D. NOT HCA. MONTEREY COUNTY TXPS. HWY 101 SOUTH, H TO H SET BYPASS LEAKING.
| 09-40045-1 | 187 | [9 empty] | 2009-05-04 | [5 empty] | GREENFIELD | DREG5775 IN STATION D. NOT HCA. MONTEREY COUNTY TXPS.
| 09-02188-1 | [10 empty] | 2009-05-08 | [5 empty] | LODI | 1614-13 D. NOT HCA. SAN JOAQUIN TXPS.
| 09-02169-1 | [10 empty] | 2009-05-06 | [5 empty] | LODI | DREG4920 D. NOT HCA. SAN JOAQUIN CTY TXPS.
| 09-20152-1 | [10 empty] | 2009-05-07 | [5 empty] | SANTA CLARA | 0804-03 OR 0804-05 D. NOT HCA. SANTA CLARA COUNTY TXPS.
| 09-50136-1 | 103 | [9 empty] | 2009-05-23 | [5 empty] | SALINAS | DREG4255 D. NOT HCA. MONTEREY TXPS.
| 09-50127-1 | 301B | [9 empty] | 2009-05-07 | [5 empty] | SALINAS | DCUST2103 D NOT HCA MONTEREY TXPS. M2 - H&H SET LEAKING MARKED IN YELLOW.
| 09-40038-1 | 187 | [9 empty] | 2009-05-01 | [5 empty] | SOLEDAD | DREG5178 D. NOT HCA. MONTEREY TXPS.
| 09-20001-1 | 1310-01 | 1.26 | [8 empty] | 2009-05-13 | [5 empty] | FERNBRIDGE | DREG4723 D. NOT HCA SERV. HUMBOLDT TXPS.
| 09-50115-1 | [10 empty] | 2009-04-30 | [5 empty] | SALINAS | 187 SEG 158.1 T. NOT HCA. MONTEREY TXPS. POTTER RD. VALVES ST 187 60.03, ALL VALVE LEAKING.
| 09-40034-1 | 187 | [9 empty] | 2009-05-01 | [5 empty] | SOLEDAD | STATION / 187 SEG 137.2 T. NOT HCA. MONTEREY TXPS.
| 09-50132-1 | 103 | [9 empty] | 2009-05-23 | [5 empty] | SALINAS | DCUST1143 D. NOT HCA. MONTEREY TXPS.
| 09-50138-1 | [10 empty] | 2009-05-23 | [5 empty] | SALINAS | DCUST1143 D. NOTHCA. MONTEREY TXPS.
| 09-50123-1 | 301B | [9 empty] | 2009-05-07 | [5 empty] | SALINAS | DCUST2530 D. NOT HCA. MONTEREY TXPS. H TO H SET 1/2 SHUT OFF LEAKING.
| 09-35017-1 | 116 | [9 empty] | 2009-05-12 | [5 empty] | DAVIS | 116T HCA. YOLO TXPS.
| 09-40035-1 | 187 | [9 empty] | 2009-05-01 | [5 empty] | SOLEDAD | 187 SEG 137 T. NOT HCA. MONTEREY TXPS.
| 09-50124-1 | 301B | [9 empty] | 2009-05-07 | [5 empty] | SALINAS | DCUST2528 D. NOT HCA. MONTEREY TXPS. H TO H SET LEAK.
| 09-50125-1 | 301B | [9 empty] | 2009-05-07 | [5 empty] | SALINAS | DCUST2527 D. NOT HCA. MONTEREY TXPS.
| 09-50126-1 | 301B | [9 empty] | 2009-05-07 | [5 empty] | SALINAS | DCUST2526 D. NOT HCA. MONTEREY TXPS.
| 09-50134-1 | 103 | [9 empty] | 2009-05-23 | [5 empty] | SALINAS | DCUST1136 D. NOT HCA. MONTEREY TXPS.
| 09-40043-1 | 187 | [9 empty] | 2009-05-04 | [5 empty] | GREENFIELD | 187 SEG 125 T. NOT HCA. MONTEREY COUNTY TXPS.
| 09-80043-1 | 400 | 84.19 | [8 empty] | 2009-05-07 | [5 empty] | BURNEY | DREG5457 D. SERV NOT HCA. SHASTA TXPS.
| 09-53070-1 | [10 empty] | 2009-05-11 | [5 empty] | DIXON | 220 SEG109 T. NOT HCA. SOLANO TXPS.
| 09-80042-1 | 400 | 84.19 | [8 empty] | 2009-05-07 | [5 empty] | BURNEY | DREG5457 D. SERV NOT HCA. SHASTA TXPS.
| 09-50135-1 | 103 | [9 empty] | 2009-05-23 | [5 empty] | SALINAS | DREG 4255 D. NOT HCA. MONTEREY TXPS.
| 09-70238-1 | 1813-02 | [9 empty] | 2009-05-04 | [5 empty] | MARINA | T NOT HCA. TXPS MONTEREY COUNTY.
| 09-02185-1 | [10 empty] | 2009-05-07 | [5 empty] | LODI | 1614-03 SEG 319. TI NOT HCA. SAN JOAQUIN TXPS.
| 09-50121-1 | 3001B |  | 2 | Distribution Main |  | Regulator |  |  | Material Failure |  | 2009-05-07 | 2009-05-07 | Other |  | Steel/Wrought Iron |  | SPRECKELS | DREG5414 D SERV.; WE FOUND GAS LEAKING THROUGH THE REG VENT - REBUILT THE GENERATOR.
| 06-21020-1 |  |  | 0.75 | Single Service |  | Mechanical Joint |  |  | Unknown |  | 2006-02-09 | 2009-05-21 | Other |  | Steel/Wrought Iron |  | BERKELEY | DCUST8364 D SERV. TXPS.
| 09-00314-1 | 21E | 82.53 | 12 | Transmission |  | Valves |  |  | Other |  | 2009-03-20 | 2009-03-28 | Other |  | Steel/Wrought Iron |  | CLOVERDALE | 021E T LT HCA TXPS.
| 09-70049-1 | [10 empty] | 2009-02-13 | [5 empty] | MONTEREY | DREG5084 D SERV TXPS. THERE IS ANOTHER LEAK WITH THE SAME #.
| 09-70028-1 | 177 | 88.8 | 0.75 | Transmission |  | Fitting |  |  | Other |  | 2009-05-13 | 2009-05-14 | Tee Fused Over Defect - Plastic |  | Steel/Wrought Iron |  | HARRISON GULCH | DREG5040 T1 SERV.; SOAP TEST.
| 09-00015-1 | [10 empty] | 2009-04-26 | [5 empty] | RIPON | 1615-04 T DFM. ROUTE: DCUST1818 MP:O. LEAK ON HPR@7919 RIPON RD, RIPON.
| 09-00022-1 |  | 5.74 | [8 empty] | 2009-04-08 | [5 empty] | NAPA | 021B T LT. HPR LEAKING.
| 09-00029-1 | 021E | 10500 | [8 empty] | 2009-04-29 | [5 empty] | UKIAH | DREG3820 T1 SERV. LEAK IN VALVE BOX, T-105.00 U-09.
| 09-20012-1 |  | 9.68 | [8 empty] | 2009-03-26 | [5 empty] | AROMAS
| 09-20013-1 |  | 10.198 | [8 empty] | 2009-03-27 | [5 empty] | PAJARO
| 09-20014-1 |  | 10.1248 | [8 empty] | 2009-03-27 | [5 empty] | PAJARO
| 09-20015-1 |  | 0.0099 | [8 empty] | 2009-03-26 | [5 empty] | AROMAS | DREG5155. D SERV. END OF ANTON PLACE K14 REG. ST CUSTOMER SMELLS GAS.
| 09-20016-1 |  | 2.0875 | [8 empty] | 2009-03-26 | [5 empty] | AROMAS
| 09-20017-1 |  | 15.3271 | [8 empty] | 2009-03-26 | [5 empty] | PAJARO
| 09-80012-1 | 300A | [9 empty] | 2009-04-23 | [5 empty] | HOLLISTER | DREG5361 T1 SERV.
| 09-80013-1 | 300B | [9 empty] | 2009-04-23 | [5 empty] | HOLLISTER | DREG5390 T1 SERV.
| 09-80014-1 | 300A | [9 empty] | 2009-04-23 | [5 empty] | HOLLISTER | DREG5362 T1 SERV.
| 09-80015-1 | 300A | [9 empty] | 2009-04-23 | [5 empty] | HOLLISTER | PREG5360 T1 SERV.
| 09-80018-1 | 300A | [9 empty] | 2009-04-23 | [5 empty] | HOLLISTER | PREG5362 T1 SERV.
| 09-80019-1 | 300B | [9 empty] | 2009-04-23 | [5 empty] | HOLLISTER | DREG5389 T1 SERV.
| 09-80020-1 | 301A | [9 empty] | 2009-04-25 | [5 empty] | SAN JUAN BAUTISTA | I AND VII LEAK .5. DREG5421 T1 SERV.
| 09-80021-1 | 300A | [9 empty] | 2009-04-25 | [5 empty] | TRES PINOS | PREG T1 SERV. CALLENS RANCE, FIRE VALVE IN BOX 1% 435.35.
| 09-80017-1 | 300B | [9 empty] | 2009-04-23 | [5 empty] | HOLLISTER | DCUST2498 T1 SERV. HH SET FISHER FLOW OFF.
| 09-80022-1 | 300B | [9 empty] | 2009-04-25 | [5 empty] | TRES PINOS | DREG5385 T1 SERV.
| 09-80023-1 | 300A | [9 empty] | 2009-04-25 | [5 empty] | TRES PINOS | DREG5356 T1 SERV.
| 09-80024-1 | [10 empty] | 2009-04-27 | [5 empty] | HOLLISTER | PREG5419 T1 SERV.
| 09-80025-1 | [10 empty] | 2009-04-27 | [5 empty] | HOLLISTER | PREG5419 T1 SERV.
| 09-90167-1 | 167 |  | 2 | Transmission |  | Fitting |  |  | Unknown |  | 2009-03-18 | 2009-04-08 | Other |  | Steel/Wrought Iron |  | GRIDLEY | PREG 8722 D SERV;. SOAP TEST OK REDOPED AND TIGHTENED VALVE.
| 09-50072-1 | 187 | 62 | 8 | Transmission |  | Body of Pipe |  |  |  |  | 2009-04-03 | 2009-04-04 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | SHUT VALVES AT 2 LOCATIONS - CUT OUT DAMAGED PIPE; FARMER USING BULLDOZER WITH RIPPER PLOWING FIELD STRUCK A 8" TRANSMISSION LINE (#187). USA NOT CALLED.
| 09-50111-1 | [10 empty] | 2009-04-27 | [5 empty] | SALINAS | 1823-01 T DFM.
| 09-00028-1 | 021E | 104.73 | [8 empty] | 2009-04-29 | [5 empty] | UKIAH | DREG3819. T1 SERV.
| 09-00024-1 |  | 14.3826 | [8 empty] | 2009-04-16 | [5 empty] | NAPA
| 09-20018-1 |  | 3.3235 | [8 empty] | 2009-03-25 | [5 empty] | WATSONVILLE
| 09-20019-1 | 181B | [9 empty] | 2009-03-26 | [5 empty] | AROMAS
| 09-20020-1 | [10 empty] | 2009-04-21 | [5 empty] | WATSONVILLE | DREG5447 D SERV.
| 08-00035-1 | 021-E | 13504 | 0.25 | Transmission |  | Valves |  |  | Unknown |  | 2008-04-28 | 2009-04-11 | Other |  | Steel/Wrought Iron |  | WILLITS | DCUST849 T1 SERV.; REPAIRED LEAK ON BODY BLEED VALVE.
| 08-40002-1 | 210A | 1.42 | 32 | Transmission |  | Other |  |  | Unknown |  | 2008-08-29 | 2009-01-07 | Other |  | Steel/Wrought Iron |  | DIXON | TIGHTENED MISC, FITTING ON METER.
| 09-02037-1 |  |  | 0.75 | Single Service |  | Regulator |  |  | Other |  | 2009-03-17 | 2009-04-09 | Other |  | Steel/Wrought Iron |  | LODI | DCUST 2223 T1 SERV.
| 09-53026-1 | DFM |  | 4 | Transmission |  | Valves |  |  | Other |  | 2009-02-04 | 2009-04-01 | Other |  | Steel/Wrought Iron |  | DIXON
| 08-60042-1 |  |  | 2 | Distribution Main |  | Other Welds |  |  | Unknown |  | 2008-09-11 | 2009-05-08 | Fill Weld - Weld |  | Steel/Wrought Iron |  | OROVILLE | SOAP TEST OK WELDED ON 1/4" NIPPLE.
| 09-15038-1 |  | 105N | 6 | Transmission |  | Other Welds |  |  | Weld Failure |  | 2009-03-17 | 2009-04-24 | Replace TP Main |  | Steel/Wrought Iron |  | ALAMEDA | RAN 12" TP AROUND LEAK SITE FOR STREET W.
|  | 300A | 496.24 |  | Transmission | [12 empty] | SAN JOSE | POTHOLE FOR ARB L100 PROJECT BORING OPERATIONS.
|  | 132 | 40.9074 | 30 | Transmission | [7 empty] | 2009-05-14 | Grinding - Other |  | Steel/Wrought Iron |  |  | THE PIPE WAS STRUCK BY ELECTRIC GROUND ROD AT SOME TIME IN PAST. THE GROUND ROD SHORTED THE TRANSMISSION LINE CP SYSTE. TROUBLE SHOOTING ID'D THE GROUND ROD. WHEN REMOVED, THE GROUND ROD WAS FOUND BENT FROM STRIKING THE GAS LINE. THE PIPELINE WAS EXPOSED AND AN ATS REPRESENTATIVE CONDUCTED A MAGNETIC PARTICLE AND VISUAL INSPECTION. SEVERAL MICRO GOUGES WERE FOUND. THE GOUGES WERE COMPLETELY REMOVED BY VERY LIGHT GRINDING (.01") AND POLISHING. MAGNETIC PARTCLE INSPECTION DETERMINED THAT THERE WAS NO SURFACE CRACKING. NOTE: THE SITE WAS 1' WEST OF AND 1' SOUTH OF THE ELECTRIC POLE IN THE REAR YARD. THE STRIKE WAS AT THE 1:00 POSITION OF THE PIPE.
| 08-30039-1 | 137D | 17 | 10 | Transmission |  | Girth Weld |  |  | Weld Failure |  | 2008-09-17 | 2009-03-18 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | ARCATA | INSTALLED PLEDCO CLAMO & WELDED.; SOAP TESTED & VISUAL.
| 09-50009-1 | 301F |  | 2 | Single Service |  | Regulator |  |  | Atmospheric Corrosion |  | 2009-01-13 | 2009-04-10 | Other |  | Steel/Wrought Iron |  | SALINAS | REPAIRED LEAK ON SET REG. SINGLE SERVICE.
| 08-20006-1 | 200 |  | 10 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-08-20 | 2008-08-22 | Other |  | Steel/Wrought Iron |  | RIO VISTA | CONTACTED N JENEST.
| 91-00001-1 | 40502 | 193 | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1991-03-15 | 2009-06-29 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | ANGWIN | WELDED OUT PLIDCO REPAIR CLAMP; DIFFERENT EDIT VERSION. 09_60081-1. CHECKED & POST 8-24-09. SERIAL # 3145529.
| 09-20071-1 | 147 | 2.35 | 0.25 | Transmission |  | Body of Pipe |  | OTHER-1/4 WELDED PIPE | External Corrosion |  | 2009-03-27 | 2009-06-13 | Welded Sav-A-Valve - Weld |  | Steel/Wrought Iron |  | SAN CARLOS | ABANDONED GAUGE TAP, INSTALLED NEW SAV-A-VALVE GAUGE TAP; TL WAS DEPRESSURIZED, THE LEAKING NIPPLE CUT OFF AND A SAV-A-VALVE USED TO MAKE THE REPAIR.
| 09-10013-1 |  | 0 | 0.75 | Single Service |  | Fitting |  |  | Other |  | 2009-01-11 | 2009-03-18 | Other |  | Steel/Wrought Iron |  | MORGAN HILL | DCUST9525 D SERV; REPAIRS - LEAKS SOAP TEST OK.; SOAP TEST FITTINGS.
| 08-20069-1 | 0804-05 |  | 6 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2008-02-06 | 2009-07-28 | Replaced TP Main |  | Steel/Wrought Iron |  | SANTA CLARA
| 09-80016-1 | 300B | [9 empty] | 2009-04-23 | [5 empty] | HOLLISTER
| 08-02037-1 | 1301-01 | 3.0343 | 8 | Transmission |  | Valves |  |  | Other |  | 2008-04-09 | 2009-08-27 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | COTATI | CUT OUT VALVE AND DRIP REPLACE W/ 8" CAN; RECEIVED : 9/16/09. COMPLETE: 9/17/09. EDIT VERSION: AUGUST LEAKS DONE CHECKING POSETED 9/19/09, WEL. AUGUST 09 LEAKS.
| 09-10210-1 | 1818-01 | 5.6471 | [8 empty] | 2009-05-27 | [5 empty] | SANTA CRUZ
| 09-30536-1 | 7226-01 | 1.2351 | [8 empty] | 2009-08-07 | [5 empty] | MODESTO
| 09-50208-1 | [10 empty] | 2009-08-01 | [5 empty] | SALINAS | GCUST5867 TC SERV. BOOKMARK WRONG? NEW BOOKMAK. ADB7.LEAK.AUG09-50208-1.
| 09-50209-1 | 1822-01 | 3.2563 | [8 empty] | 2009-08-01 | [5 empty] | SALINAS | 1822-01 TP DFM.
| 09-50210-1 | GCUST5869 | 30102 | [8 empty] | 2009-08-01 | [5 empty] | SALINAS
| 09-50211-1 | [10 empty] | 2009-08-01 | [5 empty] | SALINAS | 1822-01 T DFM.
| 09-50212-1 | [10 empty] | 2009-08-01 | [5 empty] | SALINAS | 1822-01 TP DFM.
| 09-50213-1 | [10 empty] | 2009-08-01 | [5 empty] | SALINAS
| 09-70471-1 | [10 empty] | 2009-07-29 | [5 empty] | MONTEREY | DREG5091 T1 SERV.
| 09-80032-1 | [10 empty] | 2009-08-14 | [5 empty] | HOLLISTER
| 09-80040-1 | [10 empty] | 2009-08-22 | [5 empty] | HOLLISTER | DREG5419 T1 SERV.
| 09-00320-1 | DFM 1301 | 28.82 | 8 | Transmission |  | Valves |  |  | Material Failure |  | 2009-03-25 | 2009-04-07 | Replace TP Main |  | Steel/Wrought Iron |  | PENNGROVE
| 09-80044-1 | 300B | [9 empty] | 2009-08-28 | [5 empty] | PAICINES | BD602 N/A BD. ENTERED INTO GIS 11/20/09.
| 09-40092-1 | 187 | [9 empty] | 2009-08-28 | [5 empty] | KING CITY | ENTERED INTO GIS 11/20/09
| 09-20194-1 | [10 empty] | 2009-09-15 | [5 empty] | ANTIOCH | DREG5648 T1 SERV. ENTERED INTO GIS 11/20/09.
| 09-20195-1 | [10 empty] | 2009-09-15 | [5 empty] | PITTSBURG | DREG 5640 T1 SERV. ENTERED INTO GIS.
| 09-80195-1 | DFM |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2009-09-18 |  |  |  | Steel/Wrought Iron |  | GLENBURN | DREG4262 D SERV. ENTERED INTO GIS 11/20/09.
| 09-10109-1 | [10 empty] | 2009-09-22 | [5 empty] | SAN BRUNO | ENTERED INTO GIS 11/20/09.
| 09-56007-1 | [10 empty] | 2009-08-28 | [5 empty] | BUTTE CITY | DCUST979 D SERV. ETNERED INTO GIS 11/20/09.
| 09-21830-1 | DFM | [9 empty] | 2009-08-25 | [5 empty] | ANTELOPE | 0618-05 D DFM.
| 09-21831-1 | DFM | [9 empty] | 2009-08-25 | [5 empty] | ANTELOPE | 0618-02 D DFM. ENTER INTO GIS 11/20/09.
| 09-21832-1 | [10 empty] | 2009-08-26 | [5 empty] | SACRAMENTO | DREG 4096. ENTERED INTO GIS 11/20/09.
| 09-21833-1 | DFM | [9 empty] | 2009-08-27 | [5 empty] | ANTELOPE | DREG4093 D SERV. ENTERED INTO GIS 11/20/09.
| 09-09159-1 | 140 | [9 empty] | 2009-09-03 | [5 empty] | ACAMPO | 1625-01 D DFM. ENTERED INTO GIS 11/23/09.
| 09-53106-1 | 150 | 8.95 | 6 | Transmission |  | Body of Pipe |  |  |  |  | 2009-09-01 | 2009-09-01 | Replaced TP Main |  | Steel/Wrought Iron |  | DIXON | REPLD. 78" DAMAGED MAIN; FARMER PERFORMING RIPPING OF EXIST. TOMATO FIELD FOR FUTURE WALNUT ORCHARD STRUCK 6" L-150 TRANS. MAIN, RUPTURING PIPELINE & CAUSING DOWNSTREAM CUST. OUTAGES. OPERATOR WAS NOT INJURED. NO USA CALLED. OPERATOR CLAIMED HE WAS NOT AWARE OF PRESENCE OF PIPELINE. EQUIPMENT-D8 CUT W/ 42" RIPPER BLADES; PG&E WAS NOT CONTACTED PRIOR TO RIPPING OPERATION.
| 09-90065-1 | 50 |  | 0.75 | Single Service |  | Body of Pipe |  |  | External Corrosion |  | 2009-07-06 | 2009-09-15 | Fill Weld - Weld |  | Steel/Wrought Iron |  | LIVE OAK | DCUST924 D SERV. ENTERED INTO GIS 11/28/09; C/O CORROSION SPOT/ REPAIR WITH CIRCUMFERE.
| 09-91461-1 | DFM | [9 empty] | 2009-08-27 | [5 empty] | MARYSVILLE | DCSUT 1649 D SERV. ENTERED INTO GIS 11/23/09.
|  | 132 | 1 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SUNNYVALLE, LAKEHAVEN DR.; LINE 132, M.P. 1.00; LATIT 37 23 45.27890, LONG -122 00 19.09294
| 09-35018-1 | 116 | [9 empty] | 2009-05-12 | [5 empty] | DAVIS | 116 T HCA YOLO. GRADE 0.
| 09-21220-1 | [10 empty] | 2009-06-24 | [5 empty] | SACRAMENTO | 0639-01 T DFM. GRADE 0.
| 09-00025-1 | [10 empty] | 2009-03-24 | [5 empty] | AMERICAN CANYON | 021H T LT. GRADE 0.
| 08-50096-1 | 103 | 22.21 | [8 empty] | 2008-11-20 | [5 empty] | SALINAS | EAST LAUREL AT NATIVIDAD - LEAK IN VALVE.
| 09-17703-1 | [10 empty] | 2009-09-03 | [5 empty] | CORNING
| 09-80061-1 | 105B |  | 0.5 | Transmission |  | Girth Weld |  |  | Other |  | 2009-06-15 | 2009-09-10 | Fill Weld - Weld |  |  |  | HERCULES | FINISHED OFF WEL WAS WAS INCOMPLETE.
| 09-02138-1 | [10 empty] | 2009-04-29 | [5 empty] | LODI | 1614-08 SEG 301 HCA TI NON LEAK. CANNOT FIND LEAK IN GIS. TIGHTENED.
| 09-80024-1 | [10 empty] | 2009-04-27 | [5 empty] | HOLLISTER | DREG5429 T1 SERV. NON-LEAK. TIGHTENED.
| 09-50165-1 | 103 | 23.55 | [8 empty] | 2009-07-06 | [5 empty] | SALINAS | NON-LEAK.
| 09-70384-1 | [10 empty] | 2009-04-01 | [5 empty] | FOLSOM | 0617-06 T DFM. NON-LEAK. TIGHTENED. CANNOT FIND LEAK.
| 09-20500-1 | [10 empty] | 2009-04-18 | [5 empty] | SAN LEANDRO
| 09-10429-1 |  | 0.0056 | [8 empty] | 2009-10-05 | [5 empty] | SANTA CRUZ | DREG5121 D SERV.
| 09-10430-1 |  | 1.7052 | [8 empty] | 2009-10-05 | [5 empty] | SANTA CRUZ | 1816.15 T1 DFM.
| 09-10431-1 |  | 1.6568 | [8 empty] | 2009-10-05 | [5 empty] | SANTA CRUZ | 1816-15 T1 DFM.
| 09-20288-1 |  | 0.2551 | [8 empty] | 2009-10-06 | [5 empty] | PALO ALTO | GCUST5815 TC SERV.
| 09-22133-1 | DFM | 0 | [8 empty] | 2009-10-10 | [5 empty] | SACRAMENTO | DREG4094 T1 SERV.
| 09-40095-1 |  | 46.5961 | [8 empty] | 2009-10-08 | [5 empty] | SOLEDAD
| 09-40096-1 | DCUST9623 | 0 | [8 empty] | 2009-10-08 | [5 empty] | SOLEDAD
| 09-40097-1 | 187 | 0.005 | [8 empty] | 2009-10-09 | [5 empty] | SOLEDAD
| 09-50332-1 | 301C | 17.2599 | [8 empty] | 2009-10-09 | [5 empty] | SALINAS
| 09-50333-1 |  | 60.1024 | [8 empty] | 2006-10-09 | [5 empty] | SALINAS | POTTER RD. REG. - ALL VALVES LEAKING X-10%.
| 09-50425-1 | 301-B | 6.79 | 12 | Transmission |  | Body of Pipe |  |  |  |  | 2009-10-23 | 2009-10-23 | Replaced TP Main |  | Steel/Wrought Iron |  | SALINAS | REPLACED DAMAGED PART OF MAIN / VALVES; FARMER WAS RIPPING FIELD AND HIT THE GAS LINE.
| 09-80046-1 |  | 0.93 | [8 empty] | 2009-10-20 | [5 empty] | HOLLISTER | DREG5388 T1 SERV.
| 09-80047-1 |  | 0.0013 | [8 empty] | 2009-10-21 | [5 empty] | HOLLISTER | DFDS3686 T1 SERV.
| 09-80048-1 |  | 0.0093 | [8 empty] | 2009-10-16 | [5 empty] | HOLLISTER | DREG5385 T1 SERV.
| 09-80196-1 | 402 | 35.83 | [8 empty] | 2009-09-24 | [5 empty] | MOUNTAIN GATE | DREG5490 T1 SERV.
| 09-80199-1 | 402 | 29.36 | [8 empty] | 2009-09-29 | [5 empty] | REDDING | DREG5483 T1 SERV.
| 09-80200-1 | 402 | 28.78 | [8 empty] | 2009-09-29 | [5 empty] | REDDING | DCUST25880SERV.
| 09-80201-1 | 402 | 27.98 | [8 empty] | 2009-09-29 | [5 empty] | REDDING | 402 T LT.
| 09-80202-1 | 402 | 30.68 | [8 empty] | 2009-09-24 | [5 empty] | REDDING | REG STA 50 AT S/BOX; SOUTH BOX
| 09-80203-1 | 402 | 30.68 | [8 empty] | 2009-09-24 | [5 empty] | REDDING | REG STA 50 AT S/E VALVE; S/E VALVE
| 09-92967-1 |  | 0.0025 | [8 empty] | 2009-09-30 | [5 empty] | OAKLAND | AT PG&E GAS VALVE BOX
| 09-01146-1 | DFM | 0.0004 | [8 empty] | 2009-10-12 | [5 empty] | YUBA CITY | LEAK IN V-1 200' E/O HWY 99 ON OSWALD
| 09-01147-1 | DFM | 3.6788 | [8 empty] | 2009-10-12 | [5 empty] | YUBA CITY | LEAK ON HIGH TO HIGH SET
| 09-10032-1 | 173 | 0 | [8 empty] | 2009-09-25 | [5 empty] | NEWCASTLE | @ GAS VALVE 227
| 09-10033-1 | 173 | 0 | [8 empty] | 2009-09-25 | [5 empty] | AUBURN | @ GAS VALVE 229
| 09-33311-1 |  | 0.3009 | [8 empty] | 2009-09-22 | [5 empty] | VACAVILLE | AT WEST REG PIT.
| 09-33312-1 | 210B | 11.4125 | 12 | Transmission |  | Mechanical Joint |  |  | Other |  | 2009-10-05 | 2009-10-05 | Other |  | Steel/Wrought Iron |  | SUISUN | N/E CORNER HWY 12 AND EMPEROR DR, SUISUN CITY; AT BLOW OFF NEAR STATION - CREW CALLED; SOAP TEST; SOAP TEST AFTER REPAIR. REPLACED FLATTENED "O" RING - MADE NEW "O" RING, TESTED WITH LINE PRESSURE - NO LEAKS.
| 09-33313-1 | 210B | 0.5722 | [8 empty] | 2009-10-06 | [5 empty] | SUISUN | SUISUN/FAIRFIELD REG STATION, SUISUN CITY; AT V-46 ABOVE GROUND AT REG STATION
| 09-33314-1 |  | 18.7592 | [8 empty] | 2009-10-06 | [5 empty] | VACAVILLE | 1000' EAST OF GORDON RD ON S SIDE OF THE ROAD; OVER MAIN
| 09-33315-1 |  | 0.8739 | [8 empty] | 2009-10-07 | [5 empty] | VACAVILLE | SE CORNER OF NEW HORIZON WY AND VACCA VALLEY PKWY; AT VALVE SOUTH OF REG PIT 6-60
| 09-35079-1 | DFM | 0.0197 | [8 empty] | 2009-10-11 | [5 empty] | WOODLAND | S/E CORNER OF GIBSON & CO.RD. 101; AT REG PIT (SOUTH)
| 09-35080-1 | 116 | 0.03 | [8 empty] | 2009-10-16 | [5 empty] | DAVIS | DAVIS REG STATION, 2ND ST AND "L" ST, DAVIS; REG STATION #1 SPLICE BOX
| 09-35081-1 | 116 | 0.03 | [8 empty] | 2009-10-16 | [5 empty] | DAVIS | N/E COR 2ND & L ST-G5 BOX #2; G-5 BOX #2 AT REG STATION
| 09-35082-1 | 116 | 0.03 | [8 empty] | 2009-10-16 | [5 empty] | DAVIS | N/E COR L & 2ND ST-G5 BOX #3; G-5 BOX #3 AT REG STATION
| 09-35083-1 | DFM | 0.011 | [8 empty] | 2009-10-23 | [5 empty] | ZAMORA | CO RD 93B ZAMORA REG STATION; LEAK AT V-2 AT REG STATION
| 09-35084-1 | 172 | 69.81 | [8 empty] | 2009-10-26 | [5 empty] | DAVIS | SWINGLE REG STATION, DAVIS; VENT STACK TO V-22R PIT
| 09-35194-1 |  | 0.6646 | [8 empty] | 2009-10-07 | [5 empty] | LIVINGSTON | STEFANI & CROWELL ST - SOUTH VAULT AT REG STATION; MAIN-SOUTH VAULT AT REG STN; A-FORM, LK 09-10428-1, DATE FOUND 10/05/2009, CITY SANTA CRUZ. [COPIED ON THE SAME FORM AS LK # 09-35194-1]
| 09-35196-1 | 118 | 0.01 | [8 empty] | 2009-10-07 | [5 empty] | LIVINGSTON | NE CORNER C & 6TH STS AT VALVE FRAME & COVER
| 09-35230-1 | 118 | 0 | [8 empty] | 2009-10-22 | [5 empty] | MADERA | PINE & ALMOND STS - VAULT ON LINE 118
| 09-35231-1 | 118 | 2.7198 | [8 empty] | 2009-10-22 | [5 empty] | MADERA | PECAN AVE & STADIUM - VAULT ON LINE 118
| 09-91389-1 | DREG4014 |  | 3 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2009-08-25 | 2009-09-29 | Replace TP Main |  | Steel/Wrought Iron |  | MARYSVILLE | BAR HOLES MID STREET & CURB; HCH PIPE LINE; REMOVED 62" 3" MAIN WITH NEW TEST
| 08-00032-1 | 021-E | 136.04 | 0.75 | Distribution Main |  | Other |  |  | Unknown |  | 2008-04-28 | 2009-08-29 | Other |  | Steel/Wrought Iron |  | WILLITS | IN REG U 80 SECONDARY BOX BELOW CAP
| 08-00045-1 | 021-E | 12370 | 0.75 | Transmission |  | Regulator |  |  | Other |  | 2008-04-29 | 2009-10-16 | Other |  | Steel/Wrought Iron |  | REDWOOD VALLEY | LEAK ON TEE CAP & FILTER IN PRIMARY BOX. REG. U 58; NEEDS REG CHANGE
| 08-00051-1 | 021-E | 122.14 | 0.75 | Distribution Main |  | Valves |  |  | Unknown |  | 2008-04-29 | 2009-10-16 | Other |  | Steel/Wrought Iron |  | REDWOOD VALLEY | LEAK ON VALVE IN SECONDARY BOX. REG. 52
| 08-00054-1 | 021-E | 121.49 | 0.75 | Transmission |  | Fitting |  |  | Unknown |  | 2008-04-29 | 2009-08-26 | Other |  | Steel/Wrought Iron |  | REDWOOD VALLEY | LEAK ON ELBOW IN PRIMARY BOX. REG. U 46
| 08-00058-1 | 021-E |  | 0.75 | Distribution Main |  | Valves |  |  | Unknown |  | 2008-04-30 | 2009-10-20 | Other |  | Steel/Wrought Iron |  | UKIAH | LEAK ON VALVE IN SECONDARY BOX. REG. U 30; TIGHTEN VALVE
| 08-00060-1 | 021-E |  | 0.75 | Transmission |  | Other |  |  | Unknown |  | 2008-04-30 | 2009-06-06 | Other |  | Steel/Wrought Iron |  | UKIAH | LEAK ON TEE CAP & BYPASS IN PRIMARY BOX. REG. U101
| 09-00031-1 | 021-E | 123.95 | 0.75 | Transmission |  | Other |  |  | Unknown |  | 2009-05-08 | 2009-06-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | REDWOOD VALLEY | LEAK IN PRIMARY BOX, ON CAP REG, U-56
| 09-00036-1 | 021E | 132.47 | 0.75 | Distribution Main |  | Valves |  |  | Unknown |  | 2009-05-09 | 2009-08-29 | Other |  | Steel/Wrought Iron |  | WILLITS | GUAGE TAP LEAK
| 09-70038-1 |  |  | 0.5 | Distribution Main |  | Fitting |  |  | Other |  | 2009-02-10 | 2009-09-17 | Other |  | Steel/Wrought Iron |  | CARMEL | NON-LEAK; AQUIJITO ROAD AND HIGHWAY 1, IN YELLOW AT PIT; AREAS MARKED IN YELLOW PAINT AT PITS; RE-DOPE FITTINGS
| 09-50165-1 | 103 | 23.55 | 6 | Transmission |  | Valves |  |  | Other |  | 2009-07-06 | 2009-10-02 | Other |  | Steel/Wrought Iron |  | SALINAS | NON-LEAK; CALIFORNIA REG. STATION - OPERATING REGULATOR; CONTROL VALVE - VALVE 3 STEM; REPLACED BY MK/CAMPBELL VALVE - REPLACED
| 09-20017-1 | 181A | 15.3271 | 0.25 | Transmission |  | Fitting |  |  | Other |  | 2009-03-26 | 2009-11-10 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | PAJARO | DELETE 1/4" PIPE NON-LEAK; SAN JUAN & RXR TRACKS K15 & K16 - YELLOW ZIPTIES; REDOPE AND TIGHTEN
| 09-40013-1 | 310 | [9 empty] | 2009-02-24 | [5 empty] | KING CITY | DELETE NON-GIS PIPE; FIRE VALVE & HH SET LEAKING - REG 5PH SET 1%; PAINTED YELLOW
| 09-80013-1 | 300B | 459.43 | 0.75 | Distribution Main |  | Regulator |  |  | Other |  | 2009-04-23 | 2009-07-11 | Replace Partial Service |  | Steel/Wrought Iron |  | HOLLISTER | BROWN TRAILER - DIST. REG 17X30 BOX; REPAIRED LEAKS - SOAP TEST
| 09-80032-1 | 103 | 9.66 | 2 | Distribution Main |  | Other |  |  | Other |  | 2009-08-14 | 2009-10-30 | Other |  | Steel/Wrought Iron |  | HOLLISTER | 549 MISSION VINEYA; NEW O RING - REDOPE FITTINGS
| 09-21832-1 | DFM |  | 4 | Transmission |  | Valves |  |  | Other |  | 2009-08-26 | 2009-11-09 | Other |  | Steel/Wrought Iron |  | SACRAMENTO | REG A-62 N/E COR ROSEVILLE/BUTTERNUT; T&R CALLED REPAIR
| 09-00148-1 | 4041001 | 0.47 | 2 | Transmission |  | Other |  |  | Other |  | 2009-10-28 | 2009-10-29 | Other |  | Steel/Wrought Iron |  | VALLEJO | FAIRGROUNDS DR & SERENO; (CGT) NORTHERN PIT OF REG. 50; REPLACED BAD "O" RING ON FILTER CAP; SOAP TEST
| 09-00746-1 | 173 | [9 empty] | 2009-11-03 | [5 empty] | NEWCASTLE | LEAK AT R-221 IN ST ACROSS FROM ADDRESS
| 09-01148-1 | DFM | 0.006 | [8 empty] | 2009-10-28 | [5 empty] | YUBA CITY | LEAK IN V-1
| 09-01150-1 | DFM | 0.2874 | [8 empty] | 2009-10-28 | [5 empty] | YUBA CITY | LEAK IN V-10
| 09-01152-1 | 1511 | [9 empty] | 2009-11-06 | [5 empty] | OLIVEHURST | LEAK IN VALVE
| 09-02160-1 | 173 | [9 empty] | 2009-11-03 | [5 empty] | AUBURN | LEAK AT V-228 IN STREET ACROSS FROM ADDRESS
| 09-02161-1 | 173 | [9 empty] | 2009-11-03 | [5 empty] | NEWCASTLE | LEAK AT V-225 IN ST ACROSS FROM ADDRESS
| 09-02162-1 | [10 empty] | 2009-11-03 | [5 empty] | NEWCASTLE | LEAK AT V-224 COVER NEXT TO HIGH TO HIGH
| 09-02163-1 | 173 | 10.7564 | [8 empty] | 2009-11-03 | [5 empty] | PENRYN | VALVE COVER 50 YRDS RT OF ADDRESS
| 09-02164-1 | [10 empty] | 2009-11-03 | [5 empty] | PENRYN | LEAK AT VALVE 214 IN STREET
| 09-02166-1 | DFM | 4.7089 | [8 empty] | 2009-11-09 | [5 empty] | GRANITE BAY | BARTON REG #411
| 09-04386-1 | 173 | [9 empty] | 2009-11-03 | [5 empty] | LOOMIS | LEAK AT R-445 BY ADDRESS
| 09-04387-1 | 173 | 7.6305 | [8 empty] | 2009-11-03 | [5 empty] | LOOMIS | LEAK IN VALVE IN ST AT TAYLOR & CIRCLE DR
| 09-04571-1 | 123 | 6.5337 | [8 empty] | 2009-11-10 | [5 empty] | ROSEVILLE | LEAK AT -6.50 VALVE LID -2
| 09-04572-1 | 123 | 6.5336 | [8 empty] | 2009-11-10 | [5 empty] | ROSEVILLE | V-6.50 LEAK AT VALVE LID - E
| 09-04573-1 | 123 | 6.5336 | [8 empty] | 2009-11-10 | [5 empty] | ROSEVILLE | V-6.50 LEAK AT VALVE LID-1
| 09-04574-1 | 123 | 6.5335 | [8 empty] | 2009-11-10 | [5 empty] | ROSEVILLE | LEAK AT VALVE V-6.50
| 09-04575-1 | 173 | [9 empty] | 2009-11-10 | [5 empty] | ROSEVILLE | IN REG BOX P
| 09-04576-1 | 173 | [9 empty] | 2009-11-10 | [5 empty] | ROSEVILLE | IN REG BOX M
| 09-21519-1 |  | 3.14 | [8 empty] | 2009-11-14 | [5 empty] | SAN JOSE | MCKAY AVE & LUNDY IN VALVE 1463
| 09-22711-1 | DFM | 0.4935 | [8 empty] | 2009-11-03 | [5 empty] | ORANGEVALE | 100'N FROM S/E CRNR HAZEL AVE/PERSHING AVE
| 09-22712-1 | DFM | 0.4997 | [8 empty] | 2009-11-03 | [5 empty] | ORANGEVALE | 130'N FROM S/E CORNER OF HAZEL AVE & PERSHING AVE
| 09-22730-1 | DFM | [9 empty] | 2009-11-12 | [5 empty] | FOLSOM | AT VALVE D-67 IN RAVINE
| 09-22731-1 | DFM | 0.0335 | [8 empty] | 2009-11-12 | [5 empty] | FOLSOM | FOLSOM-AUBURN RD, 250' N OF GREENBACK LN
| 09-40010-1 | 310 |  | 2 | Single Service |  | Fitting |  |  | Unknown |  | 2009-02-24 | 2009-11-21 | Other |  | Steel/Wrought Iron |  | KING CITY | GUAGE LEAK AND BY VALVE; PAINTED RED, PAINTED RED VALVES, SAME AREA; BYPASSED THE METER SET AND MADE REPASS; VALVE IS LEAKING - CUSTOMER VALVE
| 09-40138-1 |  | 0.0311 | [8 empty] | 2009-11-14 | [5 empty] | KING CITY | KING CITY REG V-8; LEAK AT KING CITY REG V-8
| 09-40139-1 | 187 | 0.0017 | [8 empty] | 2009-11-20 | [5 empty] | KING CITY | OFF AIRSTRIP & OASIS SAN BERNABE WINERY; LEAK AT GAS VALVE
| 09-40140-1 | 187 | 0.0134 | [8 empty] | 2009-11-23 | [5 empty] | KING CITY | SAN BERNABE WINERY (OFF OASIS); IN GROUND NEXT TO HIGH TO HIGH SET
| 09-50491-1 |  | 0.019 | [8 empty] | 2009-11-02 | [5 empty] | SALINAS | POTTER DIST SET (MARK IN YELLOW PRINT); LEAK AT POTTER DIST
| 09-50492-1 |  | 0.0019 | [8 empty] | 2009-11-02 | [5 empty] | SALINAS | 24999 POTTER; LEAK AT HIGH TO HIGH SET
| 09-50494-1 | DFM | [9 empty] | 2009-11-02 | [5 empty] | SALINAS | 2400 POTTER
| 09-50495-1 |  | 0.0097 | [8 empty] | 2009-11-02 | [5 empty] | SALINAS | 23940 POTTER RD.; LEAK AT HIGH TO HIGH SET
| 09-50496-1 |  | 0 | [8 empty] | 2009-11-02 | [5 empty] | SALINAS | 23820 POTTER RD; LEAK AT HIGH TO HIGH SET
| 09-50497-1 |  | 0.1191 | [8 empty] | 2009-11-02 | [5 empty] | SALINAS | 23840 POTTER RD.; LEAK AT HIGH TO HIGH SET (FISHER B/OFF)
| 09-50499-1 |  | 0 | [8 empty] | 2009-11-09 | [5 empty] | SALINAS | 23640 POTTER RD.; LEAK AT HTO HIGH SET & REG
| 09-50536-1 | DFM18 | 2.74 | 4 | Transmission |  | Other Welds |  |  | Other |  | 2009-11-19 | 2009-11-19 | Fill Weld - Weld |  | Steel/Wrought Iron |  | SALINAS | SRS36 - 6% IN BOX NIPPLE OFF MAIN (WELD); REWELD LEAKING GAUGE NIPPLE ON 4" TP MAIN - SOAP TEST OK
| 09-60135-1 |  | 0.0008 | [8 empty] | 2009-11-19 | [5 empty] | GRIDLEY | V-343
| 09-80335-1 |  | 42.341 | [8 empty] | 2009-11-11 | [6 empty] | [ ANOTHER A-FORM HAS BEEN COPIED TO THIS FORM, LK # 09-02165-1, DATE FOUND 11/03/2009, CITY ROCKLIN, TP LINE # 173]; LEAK AT V-444 AT ROCKLIN REG ST; FULL CIRCLE SLEEVE REPAIR BY GC WELDERS; CONTRACTOR BORING TO INSTALL FIBEROPTIC BORED INTO 20" TP. MAIN
| 09-81437-1 | 111 | 25.2541 | 8 | Transmission |  | Girth Weld |  |  | Weld Failure |  | 2009-01-20 | 2009-11-17 | Other |  | Steel/Wrought Iron |  | FRESNO | MAIN WEST OF VALENTINE; 50' WEST OF INTERSECTION IN GVB; VALVE BOX; WELD ON CONTROL FITTING
| 09-91652-1 | 103 | 9.37 | 0.75 | Transmission |  | Valves |  |  | Construction Defect |  | 2009-11-07 | 2009-11-07 | Other |  | Steel/Wrought Iron |  | SAN JUAN BAUTISTA | VALVE BOX; REPLACED GREASE FITTING; REPLACED BAD GREASE FITTING, SOAP TEST OK
| 09-92856-1 | 173 | [9 empty] | 2009-11-04 | [5 empty] | PENRYN | IN VALVE BOX V-214
| 09-93007-1 | 173 | 0.0042 | [8 empty] | 2009-11-04 | [5 empty] | LOOMIS | REG PIT
| 09-20017-1 | 181A |  | 0.25 | Transmission |  | Fitting |  |  | Other |  | 2009-03-26 | 2009-11-10 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | PAJARO | DELETE NON-LEAK 1/4" NON-GIS; SAN JUAN & RXR TRACKS K15 & K16 - YELLOW ZIPTIES; REDOPE AND RETIGHTEN; DOPED FITTING - SOAP TEST - REPAIRED LEAKS
| 09-50137-1 | 103 | 25.47 | 12 | Transmission |  | Valves |  |  | Other |  | 2009-05-23 | 2009-11-20 | Other |  | Steel/Wrought Iron |  | SALINAS | PAJARO AND SAN MIGUEL, SALINAS - VAULT; GREASED VALVES
| 09-50141-1 | 103 |  | 8 | Transmission |  | Valves |  |  | Other |  | 2009-05-23 | 2009-11-20 | Other |  | Steel/Wrought Iron |  | SALINAS | NON-LEAK; NATIVIDAD & E. LAUREL 2% VAULT - VALVE V22.21; MARK YELLOW, READING AT VALVE-SAME AREA, GREASED VALVE; FOUND V1 LEAKING - GREASED; GREASED AND LUBED VALVES IN PIT
| 09-50213-1 | 301F |  | 0.5 | Transmission |  | Clamp |  |  | Unknown |  | 2009-08-01 | 2009-10-23 | Other |  | Steel/Wrought Iron |  | SALINAS | ESPINOSA VALVE ST. 301F AND OTHER VALVE; CUT AND RETHREAD; PIPE CUT AND RETHREADED - SOAP TEST OK
| 09-00035-1 | 021E | 127.58 | 0.75 | Single Service |  | Valves |  |  | Unknown |  | 2009-05-08 | 2009-11-04 | Other |  | Steel/Wrought Iron |  | REDWOOD VALLEY | LEAK IN VALVE BOX AT REG U-65; GREASED VALVE TO STOP LEAK; SOAPED
| 09-10109-1 | 101 | 33.68 | 0.25 | Transmission |  | Fitting |  |  | Construction Defect |  | 2009-09-22 | 2009-10-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN BRUNO | PCV, 24, 336, 25, 1 & REG 27 MARKED IN YELLOW PAIN; TIGHTENED TUBE FITTINGS
| 09-10130-1 | 173 | 6.0299 | [8 empty] | 2009-12-03 | [5 empty] | ROCKLIN | 375' SW OF 4335 PACIFIC-GAS VALVE
| 09-10280-1 | 0813-07 | 0.1093 | 6 | Transmission |  | Valves |  |  | Other |  | 2009-12-09 | 2009-12-09 | Other |  | Steel/Wrought Iron |  | SAN JOSE | MONTERERY HWY & BLOSSOM HILL RD 100% GAS ON VALVE
| 09-22863-1 | DFM | 1.044 | [8 empty] | 2009-11-23 | [5 empty] | SACRAMENTO | VALVE D-46 PALM AVE W/O I-80
| 09-23042-1 |  | 0.984 | [8 empty] | 2009-12-08 | [5 empty] | ELK GROVE | BIG HORN BLVD 400' W/ AMBER DR. AT V-38 IN STREET
| 09-23095-1 |  | 0.0009 | [8 empty] | 2009-12-08 | [5 empty] | ELK GROVE | AT VALVE A-34 IN STREET
| 09-35259-1 | 118G | 0.01 | [8 empty] | 2009-12-15 | [5 empty] | MERCED | CHILDS REG STATION - NEW BOX IN ROAD
| 09-50426-1 | 301-G | 0.0009 | [8 empty] | 2009-10-27 | [5 empty] | SALINAS | SRS-76 HIGH TO HIGH SET; LEAK AT HIGH TO HIGH SET SRS (76)
| 09-50427-1 | 301-A | 0.0079 | [8 empty] | 2009-10-27 | [5 empty] | PRUNEDALE | SRS-57; LEAK ON UNION HI TO HI SET
| 09-50557-1 | MTY-1 | 4.04 | [8 empty] | 2009-12-16 | [5 empty] | SALINAS | 4.08 VALVE PIT; LEAK AT VALVE 4.08 PIT
| 09-50558-1 | MTY-1 | 0.0178 | [8 empty] | 2009-12-16 | [5 empty] | SALINAS | PIT SRS-83; LEAK AT PIT SR-83
| 09-75078-1 | AV13 DFM | 1.64 | 0.75 | Single Service |  | Other |  |  | Equipment Malfunction |  | 2009-12-08 | 2009-12-09 | Other |  | Steel/Wrought Iron |  | MADERA | HPR SET; AT PROPERTY LINE - HPR; REPLACE HPR TYPE REG & RELIEF
| 09-60090-1 | 50 |  | 0.75 | Transmission |  | Other |  |  | Construction Defect |  | 2009-06-24 | 2009-12-17 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | GRIDLEY | V-305; SOAP TEST OK
| 09-20042-1 | [10 empty] | 2009-06-03 | [5 empty] | AROMAS | 2001-2003 SAN JUAN RD.; LEAK AT HIGH TO HIGH J-20, NO LEAK FOUND (DELETED)
| 09-10209-1 | [10 empty] | 2009-05-27 | [5 empty] | SANTA CRUZ | 84' NORTH OF HOLDER BUNKER FRAME AND COVER; NO LEAK FOUND (DELETED)
| 08-50095-1 | 103 | 1.7 | [8 empty] | 2008-11-21 | [5 empty] | SALINAS | 1222 MERRILL ROAD, SALINAS; NO LEAK FOUND (DLEETED THIS LEAK)
| 09-10019-1 | DFM |  | 3 | Transmission |  | Other |  |  | Construction Defect |  | 2009-02-03 | 2009-12-22 | Other |  | Steel/Wrought Iron |  | SCOTTS VALLEY | REPLACED FILTER IN REG; LOCKWOOD LANE, SCOTTS VALLEY, REG. K02-IN BOX; REPLACED LEAKING FILTER, SOAP TEST OK
| 09-20014-1 | [10 empty] | 2009-03-27 | [5 empty] | PAJARO | VALVE V10.2
| 09-20049-1 |  |  | .0.75 | Single Service |  | Valves |  |  | Other |  | 2009-06-03 | 2009-11-19 | Other |  | Steel/Wrought Iron |  | AROMAS | INTERSECTION OF SAN JUAN RD & QUAIL HILL LN.; AT VALVE B-77 WEST SIDE OF SAN JUAN RD AT RISER
| 09-40015-1 | 187 | [9 empty] | 2009-02-27 | [5 empty] | KING CITY | TIGHTENED NON-LEAK; HIGHWAY 101/E1 CAMINO REAL SOUTH, KING CITY; BY PASS VALVE & VALVE #1 - ALL PAINT YELL
| 09-21139-1 | DFM |  | 0.75 | Transmission |  | Other |  |  | Other |  | 2009-06-04 | 2009-12-14 | Other |  | Steel/Wrought Iron |  | CITRUS HEIGHTS | NOT ON TRANS; AT VALVE D-52C; REPAIR LEAK AT BODY BLEED ELBOW FITTING
| 09-21160-1 | 119 |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2009-06-11 | 2009-12-14 | Other |  | Steel/Wrought Iron |  | SACRAMENTO | NOT ON TRANS; AT V-24 OUTSIDE OF STATION; V-24; REPAIR LEAK AT GREASE FITTING
| 09-21167-1 | DFM |  | 0.5 | Transmission |  | Other |  |  | Other |  | 2009-06-12 | 2009-12-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SACRAMENTO | NON-LEAK NOT ON TRANS; S/E CORNER RICHARDS BLVD % DOS RIOS AVE, SACRAMENTO; AT VALVE B-31 1' B.O.W.; REPAIR LEAK @ GREASE FITTING CAPS
| 09-21177-1 | 119B |  | 0.75 | Transmission |  | Riser |  |  | Other |  | 2009-06-15 | 2009-12-21 | Other |  | Steel/Wrought Iron |  | SACRAMENTO | NON-LEAK NOT ON TRANS; W/S INTERSECTION OF PALM AVE AND ROSEVILLE RD, SAC; AT VALVE V-6.86 NEXT TO RAILROAD TRACKS; REMOVD REDOPED & TIGHTENED VLV
| 09-40011-1 | [10 empty] | 2009-02-24 | [5 empty] | KING CITY | NON GIS PIPE; .5 2 X 3 CON. BOX; PAINT RED
| 09-40095-1 | [10 empty] | 2009-10-08 | [5 empty] | SOLEDAD | NON-LEAK; HWY 101; O.P. VALVE 46.63
| 09-40096-1 | [10 empty] | 2009-10-08 | [5 empty] | SOLEDAD | NON-LEAK; SILLMAN RD.
| 09-40097-1 | 187 | [9 empty] | 2009-10-09 | [5 empty] | SOLEDAD | NON-LEAK; H 2 H SET IN BOX 2%
| 09-50120-1 | 187 | [9 empty] | 2009-05-01 | [5 empty] | SOLEDAD | NON-LEAK; OFF HIGHWAY 101 - H&H SET FISHER BLOW OFF
| 09-50146-1 | 103 | [9 empty] | 2009-05-30 | [5 empty] | SALINAS | NON-LEAK; H2H SET BYPASS VALVE 2%; MARK YELLOW
| 09-60089-1 | [10 empty] | 2009-06-24 | [5 empty] | GRIDLEY | NON-GIS PIPE; HPR BOX
| 09-60091-1 | [10 empty] | 2009-06-24 | [5 empty] | GRIDLEY | NON-GIS PIPE; HPR BOX
| 09-60088-1 | [10 empty] | 2009-06-24 | [5 empty] | GRIDLEY | NON-GIS PIPE; IN FRONT OF ADRESS @ HPR BOX
| 09-70032-1 | [10 empty] | 2009-02-10 | [5 empty] | MONTEREY | STATION PIPE END OF 1813-02, NON-LEAK; FIGUEROA AND FRANKLIN STS INSIDE PIT MARKED YELLOW; INSIDE BIG FRANK AT PIT MARKED YELLOW
| 09-70034-1 | 301 | [9 empty] | 2009-02-10 | [5 empty] | MARINA | NON-LEAK; RESERVATION RD. AT DEL MONTE - MARKED IN YELLOW; AREA MARKED WITH YELLOW X PAINT
| 09-70037-1 | [10 empty] | 2009-02-10 | [5 empty] | SEASIDE | NON-LEAK; LA SALLE ST. AND FREMONT AVE. MARKED YELLOW; LA SALLE AND FREMONT - VALVE ON LASALLE
| 09-70260-1 | DFM |  | 2 | Distribution Main |  | Valves |  |  | Unknown |  | 2009-04-02 | 2009-11-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | FOLSOM | TIGHTENED NON-LEAK; FIRE VLV FROM TRANSMISSION TO HPW FOLSOM PRISON; TIGHTEN GREASE FITTING ELBOW
| 09-92967-1 | [10 empty] | 2009-09-30 | [5 empty] | OAKLAND | NON-LEAK; AT PG&E GAS VALVE BOX
| 09-00190-1 | 40501 | 25.6743 | 4 | Transmission |  | Other Welds |  |  | Construction Defect |  | 2009-12-09 | 2010-03-26 | Other |  | Steel/Wrought Iron |  | ST HELENA | B/T MAIN & HPR - 4' W/O FENCELINE; (CGT) B/T MAIN & HPR, 4' W/O FENCELINE, (5YR) IN HPR BOX, O/SVC TEE TO HPR; CUT-OUT SVE TEE & PIPE, REPLACED 2' TL &
| 10-00016-1 | 50 | 11.2749 | 8 | Transmission |  | Fusion Joint |  |  | Construction Defect |  | 2010-03-16 | 2010-04-15 | Replace TP Main |  | Steel/Wrought Iron |  | LIVE OAK | INT. OF FIR ST. & LARKIN - 50' S/O FIR NEAR PATCH; REPLACED 35" SPOOL REPLACED FITTING; REMOVED LEAKING FITTING AND REPLACED W/35" SPOOL
| 10-00023-1 | 21E | 111.94 | [8 empty] | 2010-04-15 | [5 empty] | UKIAH | IN VALVE BOX IN STREET. T111.94; GRADE O PER SEFF MORRIS
| 10-10160-1 |  | 0.001 | [8 empty] | 2010-04-16 | [5 empty] | SANTA CRUZ | INTERSECTION OF CLINTON & OWEN
| 10-20010-1 | 4-0408-1 | 2.4747 | 4 | Transmission |  | Unknown |  |  | Unknown |  | 2010-04-08 | 2010-04-13 | Deactivate #TP Main |  | Steel/Wrought Iron |  | NAPA | TRANCAS BRIDGE OVER NAPA RIVER; NEXT TO WATER-EAST SIDE OF RIVER-NORTH A PSI LOWERED TO 60 PSI; CUT OFF MAIN GOING TO RIVER
| 10-20536-1 | 311 | 6.6834 | [8 empty] | 2010-04-16 | [5 empty] | RIDGECREST | VALVE 6.71 ON LINE 311. LEAK AT VALVE IN CASING.
| 10-20550-1 |  | 0.0161 | [8 empty] | 2010-04-09 | [5 empty] | SAN JOSE | GALAHAD & STORY RD HI TO HI BOX IS LEAKING BY TRANSMISSION
| 10-33010-1 | 210 | 0.5608 | [8 empty] | 2010-04-07 | [5 empty] | SUISUN | V-C N SIDE OF HWY12
| 10-33011-1 | 210 | 0.5577 | [8 empty] | 2010-04-07 | [5 empty] | SUISUN | VAULT TO S/E OF V-C N/S HWY12 (HCA)
| 10-33012-1 | 210 | 0.5534 | [8 empty] | 2010-04-07 | [5 empty] | SUISUN | V-B N/S OF HWY12 (HCA)
| 10-33014-1 | 210 | [9 empty] | 2010-04-07 | [5 empty] | SUISUN | V-7 NE SIDE OF HWY12(HCA)
| 10-33015-1 | 210 | 0.0007 | [8 empty] | 2010-04-07 | [5 empty] | SUISUN | V-1 (WHEEL VLV) NW OF INTERSCTN. (HCA)
| 10-33017-1 | 210 | [9 empty] | 2010-04-09 | [5 empty] | SUISUN | V-4.88-B, NORTH SIDE; V-4.88-B, N OF CREED RD.
| 10-33018-1 | 210 | [9 empty] | 2010-04-09 | [5 empty] | SUISUN | V-1 N OF DENVERTON VLV LOT
| 10-33020-1 | 143 | 0.5339 | [8 empty] | 2010-04-23 | [5 empty] | DIXON | @ V-1'
| 10-33021-1 | 220 | [9 empty] | 2010-04-23 | [6 empty] | HI-TOHI SET 11' BACK OF ROAD
| 10-35007-1 |  | 0.7134 | [8 empty] | 2010-04-14 | [5 empty] | WOODLAND | CACHE CREEK METER STATION. CAPAY VALLEY; AT GAUGE TAP ABOVE MAIN VLV.
| 10-35023-1 | 134 | 7.9932 | [8 empty] | 2010-04-02 | [5 empty] | GILL RANCH | VALVE T-64 GILL RANCH-VAULT W/WOODED TOP V-17.94
| 10-35026-1 | 134 | 7.35 | [8 empty] | 2010-04-02 | [5 empty] | MADERA | NW CORNER OF INTERSCTN AVE 5 1/2 & RIVER GROVE
| 10-35027-1 | 134 | 7.34 | [8 empty] | 2010-04-02 | [5 empty] | MADERA | NE CORNER INTERSECTN AVE 5 1/2 & RIVER GROVE
| 10-35028-1 | 134 | 6.55 | [8 empty] | 2010-04-02 | [5 empty] | MADERA | VAULT AT NE CORNER OF INTERSCTN AVE 5 1/2 & RD 28
| 10-35030-1 | 307 | 18 | [8 empty] | 2010-04-09 | [5 empty] | MENDOTA | AT VALVE R14 IN REG STATION PAINTED YELLOW; AT VALVE IN REG STA
| 10-35031-1 | 307 | 18 | [8 empty] | 2010-04-09 | [5 empty] | MENDOTA | AT HPR AT REG STA RD17-LID PAINTED YELLOW
| 10-35032-1 | 307 | 4.09 | [8 empty] | 2010-04-09 | [5 empty] | MENDOTA | PANOCHE & NEWCOMB RDS AT HPR BOX
| 10-35033-1 | 307 | 6.75 | [8 empty] | 2010-04-09 | [5 empty] | MENDOTA | W NORTH & S LYON AVE - HPR BOX S/O INTERSECTION
| 10-35034-1 | DFM | 1.18 | [8 empty] | 2010-04-09 | [5 empty] | MENDOTA | HPR IN FENCED AREA NEXT TO ROAD; HPR - BELMONT DFM
| 10-35035-1 |  | 14.99 | [8 empty] | 2010-04-23 | [5 empty] | MADERA | REG STA RG47-HPR BOX 300' E/O WESTBERRY
| 10-54002-1 | 172 | 1.6332 | [8 empty] | 2010-04-19 | [5 empty] | WILLIAMS | LEAK ON VALVE 3 IN DRIVEWAY AT ADDRESS (NAAS)
| 10-70017-1 | 177A | 85.73 | [8 empty] | 2010-04-23 | [5 empty] | PLATINA | 1ST STAGE BOX AT GUAGE TAP
| 10-70018-1 | 177A | 85.73 | [8 empty] | 2010-04-23 | [5 empty] | PLATINA | 2ND STAGE BOX AT REG
| 10-35029-1 | 134 | 27.0486 | [8 empty] | 2010-04-01 | [5 empty] | FIREBAUGH | 10' EAST OF LINE MARKER W/BASE PAINTED YELLOW; ARBIOS REG STATION
| 10-70020-1 | 177A | 78.21 | [8 empty] | 2010-04-23 | [5 empty] | PLATINA | 1ST STAGE BOX AT BYPASS CAP
| 10-70021-1 | 177A | 78.21 | [8 empty] | 2010-04-23 | [5 empty] | PLATINA | 3RD STAGE BOX AT BYPASS CAP
| 10-50006-1 | 301-F |  | 2 | Single Service |  | Other |  |  | Other |  | 2010-01-05 | 2010-04-01 | Other |  | Steel/Wrought Iron |  | SALINAS | 384 ESPINOSA RD.; LEAK AT HIGH TO HIGH SET; PER IGIS - CUT OFF HERE; INLET BYPASS VALVE AND VARIOUS FITTING, GREASED & TIGHTENED; REPAIRED GAS LEAK AT REG STATION 4-1-10
| 10-20506-1 | JPL FEED | 0.002 | 3 | Transmission |  | Valves |  |  | Construction Defect |  | 2010-01-25 | 2010-04-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EDWARDS | 3" VALVE IN CASING JPL FEEDER EAFB; TIGHTENED NUTS ON TOP OF VALVE COLLAR; SOAP TESTED
| 09-80201-1 | 402 | 27.98 | [8 empty] | 2009-09-29 | [5 empty] | REDDING | HILLTOP DR AT PEPPERTREE - VALVE 27.98; NO LEAK FOUND
| 10-40008-1 | [10 empty] | 2010-03-04 | [5 empty] | KING CITY | GUAGE LEAK AND BY VALVE; VALVES, NO LEAK FOUND (DELETED)
| 09-21161-1 | [10 empty] | 2009-06-11 | [5 empty] | SACRAMENTO | ROSEVILLED RD 100' N/O HOME DEPOT PARKING LOT; V-123 PER CHUCK WARREN
| 09-50332-1 | [10 empty] | 2009-10-09 | [5 empty] | SALINAS | HARKINS REG ST. -1% ON TWD VALVE OUTSIDE OF FENCE
| 09-40096-1 | 187 | 45.13 | 0.75 | Branch Service |  | Fitting |  |  | Damage by Earth Movement |  | 2009-10-08 | 2010-05-24 | Other |  | Steel/Wrought Iron |  | SOLEDAD | SILLMAN RD.; READING AT H TO H SET VALVEM.P45.13, SAME AREA; REPAIRED ALL LEAKS & FITTINGS
| 10-00125-1 | 21 | 24.25 | 16 | Transmission |  | Fitting |  |  | Other |  | 2010-05-03 |  |  |  | Steel/Wrought Iron |  | PETALUMA | LEFT EDGE OF DWAY APPROACH OVER LINE 21; OVER TP MAIN IN DWAY NEXT TO ETS
| 10-02243-1 |  | 1.2593 | [8 empty] | 2010-05-13 | [5 empty] | TRACY | VALVE EAST OF HOLLY DR. N/S OF ROAD
| 10-02244-1 | [10 empty] | 2010-05-15 | [5 empty] | TRACY | HOLLY DR & SLOAN CT; N/S OF INTERSECTION. MARKED WITH YELLOW
| 10-03020-1 |  | 17.56 | [8 empty] | 2010-05-05 | [5 empty] | AUBURN | AUBURN REG #234 MT. VERNON RD.; 1ST STAGE INLET TO VALVE #1
| 10-03021-1 |  | 0.0016 | [8 empty] | 2010-05-05 | [5 empty] | ROCKLINE | ROCKLIN REG #406 - YANKEE HILL RD.; LEAK @ VALVE 444
| 10-04105-1 |  | 0.0007 | [8 empty] | 2010-05-05 | [5 empty] | LINCOLN | VALVE #1 VALVE PIT ACROSS FROM THUNDER VALLEY
| 10-06155-1 |  | 0.0039 | 0.75 | Single Service |  | Body of Pipe |  |  |  |  | 2010-05-06 | 2010-05-06 | Replace Partial Service |  | Steel/Wrought Iron |  | MANTECA | REPLACED 11' OF 3/4" STEEL SERV ON HIGH SIDE/HPR.; CONTRACTOR HIT 3/4" TRANSMISSION SERV. WHILE DIGGING TO REPLACE TRANSMISSION MAIN
| 10-10004-1 | SANTA CR | 1.6 | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2010-02-12 | 2010-05-03 | Other |  | Steel/Wrought Iron |  | SANTA CRUZ | EDGE OF ROADWAY BETWEEN DRIVEWAYS; PLIDCO SPLIT AND SLEEVE; INSTALLED 8" REPAIR CLAM HPPLIDCO SPLIT AND SLEEVE SOAPTEST FOR LEAKS - TORQUE TO 91 FT LBS
| 10-10227-1 |  | 0.0351 | [8 empty] | 2010-04-22 | [5 empty] | DAVENPORT | OVER TRANSMISSION MAIN 168' N OR 5199 N. COAST RD
| 10-10228-1 |  | 0.0319 | [8 empty] | 2010-04-22 | [5 empty] | DAVENPORT | HIGH TO HIGH SET ON RISER
| 10-20001-1 | 177 | 191.91 | [8 empty] | 2010-05-24 | [5 empty] | EUREKA | APROX 1530' S/MYRTLE AVE.; 20' WEST OF POLE #1046757
| 10-21282-1 | 119 | 0.0092 | [8 empty] | 2010-05-14 | [5 empty] | SACRAMENTO | LEAK ON HI-TOHI REG SET A-41; LEAK ON HI-TO-HI REG. SET A-41
| 10-21290-1 | 119 |  | 2 | Transmission |  | Valves |  |  | Other |  | 2010-05-24 | 2010-05-24 | Other |  | Steel/Wrought Iron |  | FOLSOM | FOLSOM PRISON MTR BY-PASS VLV (THREADS BOTH SIDES)
| 10-21336-1 | 123 | [9 empty] | 2010-05-19 | [5 empty] | ANTELOPE | @ V-125 (D-125)
| 10-33024-1 |  | 18.6423 | [8 empty] | 2010-04-29 | [5 empty] | CORDELIA | OVER T.P. MAIN 4' BACK OF ROAD; OVER T.P. MAIN
| 10-33028-1 | [10 empty] | 2010-05-03 | [5 empty] | DIXON | HI TO HI TO THE NORTH
| 10-33029-1 | [10 empty] | 2010-05-03 | [5 empty] | DIXON | AT VALVE SOUTH OF HI TO HI SET
| 10-33030-1 | [10 empty] | 2010-05-03 | [5 empty] | DIXON | HI TO HI SET TO NORTH
| 10-33036-1 | 150 | [9 empty] | 2010-05-12 | [5 empty] | DIXON | HI-TOHI BOX TO MTR#60759813
| 10-35015-1 | 172A | 0.009 | [8 empty] | 2010-04-28 | [5 empty] | ZAMORA | ZAMORA ORGANIC FARM 3/4" STL SVC, LEFT MARK ON LID
| 10-35017-1 | 150 | [9 empty] | 2010-05-05 | [5 empty] | DAVIS | #3 HI-TOHI BX SSIDE OF TRACKS
| 10-35018-1 | 150 | [9 empty] | 2010-05-05 | [5 empty] | DAVIS | HI-TOHI BX S SIDE OF RR TRACKS BEHIND 17F ARBORETUM
| 10-35020-1 |  | 0.0003 | [8 empty] | 2010-05-03 | [5 empty] | YOLO | VALVE #1 YOLO TOWN REG.
| 10-35029-1 | 220 | 0.4855 | [8 empty] | 2010-05-07 | [5 empty] | WOODLAND | @ METER SET ON VLV (YELLOW ZIP TIE)
| 10-35030-1 | 220 | 31.7475 | [8 empty] | 2010-05-07 | [5 empty] | WOODLAND | @ ABOVE GRND REG. PIPE (YLLW ZIP TIE)
| 10-35031-1 | 220 | 31.7493 | [8 empty] | 2010-05-07 | [5 empty] | WOODLAND | @ MULTIPLE G-5 BOXES LINE172&220 XTIE STATION
| 10-21335-1 | 119 | [9 empty] | 2010-05-21 | [5 empty] | SACRAMENTO | @ V-5 PIT IN STATION
| 10-35032-1 | 116 | 0.0004 | [8 empty] | 2010-05-13 | [5 empty] | WEST SACRAMENTO | REG STATION V-2; LEAK ON S. RIVER RD. REG. STA. V-2
| 10-35036-1 | 220 | 0.0478 | [8 empty] | 2010-05-13 | [5 empty] | DAVIS | 4" BYPASS VLV PAST MTR#199566 (MRKD W/ZIPTIE); UC DAVIS COGEN
| 10-35037-1 | 220 | 0.2422 | [8 empty] | 2010-05-13 | [5 empty] | DAVIS | METRIC FTTING MRKD W/ZIPTIE MTR#9543068'; CNG COMP. STA
| 10-35041-1 | 172 | 70.8616 | [8 empty] | 2010-05-11 | [5 empty] | DAVIS | @ VALVE V-1 30'S OF RR TRACKS
| 10-35045-1 | 220 | 0.0004 | [8 empty] | 2010-05-07 | [5 empty] | WOODLAND | @ VALVE V-4
| 10-80186-1 | 402/SVC | 38.15 | [8 empty] | 2010-05-20 | [5 empty] | MOUNTAIN GATE | LEHIGH CEMENT - INLET VALVE
| 10-80190-1 | 402 | 28.78 | [8 empty] | 2010-05-25 | [5 empty] | REDDING | NORTH BOX AT TRAILER PARK
| 10-80191-1 | 402 | 22.12 | [8 empty] | 2010-05-25 | [5 empty] | REDDING | STAR DR & EASTSIDE RD - REG STA 22
| 10-80192-1 | 402 | 22.12 | [8 empty] | 2010-05-25 | [5 empty] | REDDING | STAR DR & EASTSIDE RD - REG STA 22
| 10-80193-1 | 402 | 18.42 | [8 empty] | 2010-05-25 | [5 empty] | REDDING | LATONA RD & EASTSIDE RD - REG STA 94
| 10-80194-1 | 402 | 16.73 | [8 empty] | 2010-05-25 | [5 empty] | ANDERSON | SPRING GULCH RD & HWY 273 - REG STA 13; EAST BOX
| 10-80195-1 | 402 | 16.73 | [8 empty] | 2010-05-25 | [5 empty] | ANDERSON | SPRING GULCH RD & HWY 273 - REG STA 13; WEST BOX
| 10-80196-1 | 402 | 14.76 | [8 empty] | 2010-05-25 | [5 empty] | ANDERSON | BARNEY ST & HWY 273 - REG STA 10; MIDDLE BOX
| 10-80197-1 | DFM | 0.53 | [8 empty] | 2010-05-25 | [5 empty] | SHASTA LAKE CITY | SMITH RD & PINE GROVE AVE - REG STA 53; SOUTH BOX
| 10-80198-1 | DFM | 0.53 | [8 empty] | 2010-05-25 | [5 empty] | SHASHA LAKE CITY | SMITH RD & PINE GROVE AVE - REG STA 53; NORTH BOX
| 10-80200-1 | 402/DFM | 23.99 | [8 empty] | 2010-05-25 | [5 empty] | REDDING | BRESLAUER LN & EASTSIDE RD - REG STA 25; SECOND STAGE
| 10-80201-1 | 402/DFM | 23.99 | [8 empty] | 2010-05-25 | [5 empty] | REDDING | BRESLAUER LN & EASTSIDE RD - REG STA 25; 3RD STAGE
| 10-99511-1 | 105 | 0.001 | 0.75 | Transmission |  | Valves |  |  | Other |  | 2010-03-15 | 2010-05-03 | Other |  | Steel/Wrought Iron |  | SAN LEANDRO | L OF V-16 NEAR #3 BOX; IMDERGROUND L IN SIDE OF REG FROM FENCE; REPLACED O RINGS
| 09-70471-1 |  |  | 2 | Distribution Main |  | Other |  |  | Other |  | 2009-07-29 | 2010-05-05 | Other |  | Steel/Wrought Iron |  | MONTEREY | 7TH & SLOAT N/E CORNER - READING AT 4" STACK @ REG; REPLACED FLANGE GASKET AND NEW BOLTS; FOUND INLET FLANGE TO FILTER FOAMING - REPLACED GASKET AND BOLTS AND GREASED ALL VALVES
| 10-00023-1 | 21E | 111.94 | [8 empty] | 2010-04-15 | [5 empty] | UKIAH | IN VALVE BOX IN STREET. T111.94; NO LEAK FOUND
| 10-20001-1 | 200C7-3 | 0.34 |  | Gathering |  | Unknown |  |  | Unknown |  | 2010-06-22 |  |  |  | Other |  | FAIRFIELD | FROM DRAINAGE DITCH TO LEVEE, @ 150' L X 50' W
| 10-20215-1 | 119DFM | [9 empty] | 2010-05-19 | [5 empty] | SACRAMENTO | @ 4" BLW DWN STACK NEAR REG STA. NE COR OF INTERSC
| 10-21359-1 | 119 | 12.1852 | [8 empty] | 2010-06-05 | [5 empty] | SACRAMENTO | @ V-12.15
| 10-21361-1 | DFM |  | 0.75 | Transmission |  | Fitting |  |  | Other |  | 2010-06-05 | 2010-06-05 | Other |  | Steel/Wrought Iron |  | RANCHO CORDOVA | HIGH-TO-HIGH BOX; FOREIGN MATL. UNDER REG-REPL REG SEAT
| 10-21367-1 | DFM | 0.0015 | [8 empty] | 2010-06-01 | [5 empty] | SACRAMENTO | @ V-D52D IN SIDEWALK, MADISON&FAIR OAKS
| 10-21368-1 | DFM | 521.43 | [8 empty] | 2010-06-01 | [5 empty] | SACRAMENTO | @ V-D52E IN SIDWLK,SW COR MADISON&FAIR OAKS
| 10-21390-1 | DFM | 0.0513 | [8 empty] | 2010-06-02 | [5 empty] | SACRAMENTO | @ V-71 225'NE OF COR WATT&ARDEN IN SIDEWALK
| 10-21392-1 | DFM | [9 empty] | 2010-06-01 | [5 empty] | FOLSOM | @ V-109, NE INTRSCTN BLUE RAVINE&SIBLEY
| 10-21421-1 | DFM | [9 empty] | 2010-06-12 | [5 empty] | SACRAMENTO | @ VLV B-01 (C-01?) 2'S OF CURB
| 10-21426-1 | DFM | 1.5977 | [8 empty] | 2010-06-14 | [5 empty] | SACRAMENTO | LEAK @ V-1
| 10-21454-1 | DFM | 0.6451 | [8 empty] | 2010-06-21 | [5 empty] | SACRAMENTO | @ REG PIT ON COR BY KFC
| 10-21455-1 | DFM | 0.0032 | [8 empty] | 2010-06-21 | [5 empty] | SACRAMENTO | @ HI-TO-HI BOX
| 10-21456-1 | DFM | 0.0022 | [8 empty] | 2010-06-21 | [5 empty] | SACRAMENTO | @ HI-TO-HI SET IN BX (PRESS. VLV)
| 10-33040-1 | 210 | 0.0186 | [8 empty] | 2010-05-26 | [5 empty] | SUISUN | VLV IN GRASS AREA 425 LOPES, COR FULTON & LOPES
| 10-33041-1 | 210 | 0.0253 | [8 empty] | 2010-05-26 | [5 empty] | SUISUN | FIRST BOX CLOSEST TO LOPES, COR LOPES & FULTON
| 10-33042-1 | 210 | 0.0211 | [8 empty] | 2010-05-26 | [5 empty] | SUISUN | 2ND BOX FURTHEST FROM LOPES RD, COR LOPES & FULTON
| 10-80210-1 | DFM/402 | 21.41 | 4 | Transmission |  | Valves |  |  | Unknown |  | 2010-06-01 | 2010-06-17 | Other |  | Steel/Wrought Iron |  | REDDING | VALVE 226; SOAP TEST
| 10-35092-1 | AVE 9 DF | 9.6191 | [8 empty] | 2010-06-25 | [5 empty] | MADERA | GOODWIN & RANDALL WAYS-VALVE AT SW CORNER-RB67; O/MAIN AT VALVE
| 10-80223-1 | 402 | 31.72 | [8 empty] | 2010-06-17 | [5 empty] | REDDING | HPR SET ON CROOKED OAK LN - WEST BOX
| 09-35002-1 | DFM |  | 0.75 | Single Service |  | Other |  |  | Other |  | 2009-06-11 | 2010-05-28 | Other |  | Steel/Wrought Iron |  | WILLIAMS | VALVE (V-2) ON MEYERS RD; RETIGHTED-REDOPED CAPS; SOAP RESTED-REMOVED, REDOPED & TIGHTENED
| 10-00049-1 | 21 |  | 12 | Transmission |  | Other |  |  | Equipment Malfunction |  | 2010-02-10 | 2010-02-12 | Other |  | Steel/Wrought Iron |  | SANTA ROSA | LINE 21 IN SIDEWLAK WEST OF HOUSE ON RIGHT OF WAY; REPLACED EQUAL REV VALVE IN INTERNAL PLU
| 10-54002-1 | 172 | [9 empty] | 2010-04-19 | [5 empty] | WILLIAMS | LEAK ON VALVE 3 IN DRIVEWAY AT ADDRESS(NAAS); NO LEAK FOUND-@PINOFF TEE TO V-2 (09-350)
| 10-00125-1 | 21 |  | 16 | Transmission |  | Fitting |  |  | Other |  | 2010-05-03 | 2010-06-10 | Other |  | Steel/Wrought Iron |  | PATALUMA | LEFT EDGE OF DWAY APPROACH OVER LINE 21; OVER TP MAIN IN DWAY NEXT TO ETS, 16" LINE 21 @ 2" SAV-A-VALVE; REPLACED INTERNAL PLUG ON 2" SAV-A-VALVE; SOAP TEST
| 10-10228-1 |  |  | 0.75 | Single Service |  | Valves |  |  | Atmospheric Corrosion |  | 2010-04-22 | 2010-06-07 | Other |  | Steel/Wrought Iron |  | DAVENPORT | HIGH TO HIGH SET ON RISER; REPLACED HPR SET
| 09-10210-1 | 1818-01 | 5.6 | 12 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2009-05-27 | 2010-06-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SANTA CRUZ | WILDER RANCH OVER TP MAIN; LATE RECHECK COULDN'T LOCATE EXACT LEAK; JON B REPAIR ON 41097513
| 09-40036-1 | 187 |  | 0.75 | Single Service |  | Fitting |  |  | Other |  | 2009-05-01 | 2010-05-25 | Other |  | Steel/Wrought Iron |  | SOLEDAD | 2% H&H SET #2596153X; SAME AREA (YELLOW PAINT); DRY SEALANT; REPAIRED LEAKING FITTINGS
| 09-31405-1 | 314 | 8.76 | 12 | Transmission |  | Valves |  |  | Other |  | 2009-10-07 | 2010-06-22 | Other |  | Steel/Wrought Iron |  | BARSTOW | N 34 47.547 W 117 14.452
| 09-80105-1 | DFM | 32.8 | 6 | Transmission |  | Valves |  |  | Unknown |  | 2009-05-23 | 2010-06-14 | Other |  | Steel/Wrought Iron |  | SHASTA LAKE CITY | REG. STA. 53 ON SMITH RD.; VALVE 253 - NORTH BOX; SOAP TEST
| 09-80116-1 | 402/DFM | 23.99 | 3 | Transmission |  | Valves |  |  | Other |  | 2009-06-03 | 2010-06-10 | Other |  | Steel/Wrought Iron |  | REDDING | BRESLAUER LN & EASTSIDE RD - REG STA 25; VALVE 225 & 331; SOAP TEST
| 10-80186-1 | 402/SVC | 38.15 | 8 | Transmission |  | Valves |  |  | Unknown |  | 2010-05-20 | 2010-06-10 | Other |  | Steel/Wrought Iron |  | MOUNTAIN GATE | LEHIGH CEMENT - INLET VALVE
|  |  |  | 0.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | AREA CHECKED WHEN DOING HPR C/O FOR JOB # 30677563
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | LODI | HIGH SIDE TAP FITTING AREA; AREA CHECKED WHEN WELDING FITTING FOR NEW DIST REG. STA JOB# 30677563
|  |  |  | 2 | Distribution Main | [10 empty] | Aldyl A (Tan or Gray) | PE 2406/2708 (Yellow) | LODI | TIE-IN LOCATION FROM NEW DIST REG STA TO EXISTING 2" ADDY LA PL. PIPE; AREA CHECKED WHEN TIE-IN NEW DIST REG STA. TO EXISTING 2" ALDY/A PL. SERVICE MAIN. JOB # 30677563
|  |  |  | 2 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | 2" MULLER LOCATION & VALVE TIED TO 8" STL MAIN; AREA CHECKED WHEN REPLACING A 2" VALVE JOB # 30727113
|  |  | 0.1103 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | AREA CHECKED WHEN REPLACING A 2" VALVE JOB # 30727113
|  | 108 | 28.2371 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON
|  |  | 1.0674 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | 8" MAIN IS 6' DEEP. THERE GOING 14' DEEP.
|  | 108B | 2.3458 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON
| 10-60460-1 |  | 8.8633 | [8 empty] | 2010-08-17 | [5 empty] | YUBA CITY | VALVE NEXT TO REG STATION 113 & 99 HWY; LEAK AT VALVE
| 10-50165-1 | 301B | 7.8394 | 12 | Transmission |  | Body of Pipe |  |  |  |  | 2010-08-28 | 2010-08-30 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SALINAS | REPAIR SLEEVE WELDED OVER DAMAGE - WELD WAS X-RAYED AND MAGNETIC PARTICLE TESTED - SOAP TES; THE PIPE WAS HIT DUE TO A TRACTOR CLEARING OUT A DITCH ADJACENT TO THE FIELD; USA NOT CALLED
| 09-40035-1 | 187 | 40.01 | 0.75 | Single Service |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2009-05-01 | 2010-08-12 | Replace Partial Service |  | Steel/Wrought Iron |  | SOLEDAD | SOUTH OF 40.01 VALVE H&H SET, MARKED IN RED; REPLACED 7" SECTION OF 3/4" STEEL PIPE - SERVICE IS TRANS. PRESSURE
| 09-10431-1 |  | 165.68 | 1.25 | Single Service |  | Other |  |  | Construction Defect |  | 2009-10-05 | 2010-08-11 | Other |  | Steel/Wrought Iron |  | SANTA CRUZ | SERVICE TEE AT TP MAIN; LEAK MIGRATING; REPLACED CAP TO PINOFF TEE; REPLACED 1/25 CAP TO PINOFF TEE SOAP TEST AND WRAPPED
| 10-02244-1 | HOLLY FE | 0 | 0.75 | Transmission |  | Valves |  |  | Other |  | 2010-05-15 | 2010-08-04 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | TRACY | HOLLY DR & SLOAN CT; REPLACED WITH NEW 3/4" STL WELD ON VALVE; CREW REPAIRED LEAK WITH OVER 20 WELDER. SOAP TEST
| 09-20073-1 | 210 | 4.6 | 0.75 | Distribution Main |  | Fitting |  |  | Other |  | 2009-03-26 | 2010-07-30 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | HALF MOON BAY | IN REG. PIT BEHIND BUILD ON R/S OLD OBESTOR WINERY; NO LEAKAGE
| 08-02043-1 | 21 | 26.222 | 8 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 2008-04-16 | 2010-07-15 | Other |  | Steel/Wrought Iron |  | SANTA ROSA | OVER MAIN UNDER SIDEWALK; INSTALLED 8" CLAMP ON T-P
| 10-60113-1 | 0210-1 | 4.99 | 0.75 | Single Service |  | Regulator |  |  | Equipment Malfunction |  | 2010-06-29 | 2010-07-02 | Other |  | Steel/Wrought Iron |  | HALF MOON BAY | IN H&H SET BOX; PUT A FLAG NEAR RISER; REPLACED REGULATOR, T&R REPLACED; REPLACED REGULATOR TO FIX LEAK
| 10-35029-1 | 220 |  | 8 | Single Service |  | Valves |  |  | Other |  | 2010-05-07 | 2010-08-04 | Other |  | Steel/Wrought Iron |  | WOODLAND | @ METER SET ON VLV (YELLOW ZIP TIE); GREASED & OPERATED; GREASED & OPERATED 6" SOWNSTREAM VLV SOAP TESTED NO LEAKAGE
| 09-00022-1 | 021B | 5.744 | 0.75 | Single Service |  | Fitting |  |  | Other |  | 2009-04-08 | 2010-07-27 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | NAPA | DELETE; HPR LEAKING; (CGT) HPR LEAKING, HOR LEAKING. 0% W/ CGI, NO READINGS W/CGI - 2% W/FLAMEPAK; TIGHTENED CAP
| 09-00027-1 | 12-21H | 9.3722 | 0.75 | Single Service |  | Valves |  |  | Other |  | 2009-03-24 | 2010-08-06 | Other |  | Steel/Wrought Iron |  | AMERICAN CANYON | DELETE; LINE 21 - .5 MILES S/O WATSON LN.; DELETE; HPR LEAKING; (CGT) INSIDE VALVE BOX (3/4" INCLINE VAL, , LEAK ON VALVE. NO CGI READING., LEAK ON VALVE; GREASED VALVE; SOAP TEST
| 09-20016-1 | 181B | 2.1 | 0.75 | Transmission |  | Valves |  |  | Other |  | 2009-03-26 | 2010-08-20 | Other |  | Steel/Wrought Iron |  | AROMAS | V 2.10; SAME AREA;GREASED VALVES AND FLUSHED G. BUTTONS
| 09-04574-1 | 123 |  | 16 | Transmission |  | Other |  |  | Unknown |  | 2009-11-10 | 2010-06-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ROSEVILLE | LEAK AT VALVE V-6.50; TIGHTENED PIN-OFF TEE
| 09-04573-1 | 123 |  | 12 | Transmission |  | Other |  |  | Unknown |  | 2009-11-10 | 2010-06-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ROSEVILLE | V-6.50 LEAK AT VALVE LID-1;TIGHTENED PIN-OFF TEE
| 09-04572-1 | 123 |  | 6 | Transmission |  | Other |  |  | Unknown |  | 2009-11-10 | 2010-06-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ROSEVILLE | V-6.50 LEAK AT VALVE LID -E; TIGHTENED CAPS ON PIN-OFF TEE
| 10-35027-1 | 134 | 7.34 | 2 | Transmission |  | Valves |  |  | Unknown |  | 2010-04-02 | 2010-06-25 | Other |  | Steel/Wrought Iron |  | MADERA | VALVE; GREASED VALVE TO FIX LEAK
| 10-21456-1 | DFM |  | 0.75 | Transmission |  | Other |  |  | Other |  | 2010-06-21 | 2010-06-21 | Other |  | Steel/Wrought Iron |  | SACRAMENTO | @ HI TO HI SET IN BOC (PRESS VLV); REBUILT HPR TYPE REG & RESET RELIEF
| 09-04571-1 | 123 |  | 12 | Transmission |  | Other |  |  | Unknown |  | 2009-11-10 | 2010-06-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ROSEVILLE | LEAK AT 6.50 VALVE LID -2; TIGHTENED PIN-OFF TEE
| 10-35007-1 |  |  | 0.25 | Single Service |  | Fitting |  |  | Other |  | 2010-04-14 | 2010-06-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | WOODLAND | AT GAUGE TAP ABOVE MAIN VLV; TIGHTENED 1/4" NIPPLE FOR GAUGE TAP; TIGHTENED 1/4" FITTING FOR GAUGE TAP ONINLET METER SET.
| 10-33015-1 | 210 |  | 6 | Transmission |  | Valves |  |  | Other |  | 2010-04-07 | 2010-07-06 | Other |  | Steel/Wrought Iron |  | SUISUN | V-1 (WHEEL VLV) NW OF INTERSECTION (HCA); GREASED VALVE AND PARTIALLY OPERATED; GREASED AND PARTIALLY OPERATED- SOAP TESTED CLEAR- CHECKED WITH CGI NO READS
8 | 09-80008-1 | 300B | 423.92 | 1 | Transmission >= 20% SMYS |  |  |  |  | Unknown |  | 2009-03-05 | 2010-09-01 | Other |  |  |  | HOLLISTER | AT VALVE #1- SUMMIT RANCH REG. STATION; PAINT YELLOW; REPLACED O-RINGS ON VALVE STEM; REPLACE O-RINGS ON TP INLET VALVE STEM, CLEANED STEM, SOAP TEST OK.
8 | 09-80017-1 | 300B |  | 0.75 | Single Service |  | Other |  |  | Other |  | 2009-04-23 | 2010-09-08 | Other |  |  |  | HOLLISTER | MARK YELLOW; SAME AREA; SAME AREA MARKED IN YELLOW; SAME AREA; REPLACED VARIOUS FITTING LEAKS ON SET; T&R CREW REPAIRED VARIOUS GAS LEAKS AT HPR SET.
8 | 09-80023-1 | 300A | 416.83 | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2009-04-25 | 2010-06-15 | Other |  |  |  | TRES PINOS | SAME AREA; SAME AREA; SAME AREA; RESEALED O-RINGS
5 | 09-50114-1 | 187 | 65.7 | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2009-04-28 | 2010-09-01 | Other |  |  |  | SALINAS | SAME; IN VAULT; IN VALVE FRAME AND COVER; REPLACE AND LUBE ORINGS; REPAIRED GAS LEAK ON VALVE TEES FOR SCADA LINES REPLACED OLD DRY O-RINGS IN MUELLER TEES
5 | 10-50002-1 | 301F | 3.81 | 0.75 | Single Service |  |  |  |  | Unknown |  | 2010-01-04 | 2010-08-29 | Replace Service Valve <2-inch |  |  |  | SALINAS | LEAK AT HIGH TO HIGH SET (YELLOW PAINT); LEAK AT HIGH TO HIGH SET- YELLOW PAINT; REPLACED INLET VALVE; REPLACED LEAKING INLET VALVE DURING SHUT DOWN AT DIGIN ON LINE 301B
4 | 09-40042-1 | 187 |  | 0.75 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2009-05-04 | 2010-10-27 | Other |  |  |  | KING CITY | MARK YELLOW; SAME AREA; SAME AREA; REPAIRED LEAK ON FITTING; REPLACED FITTING & VALVE
4 | 09-40047-1 | 187 |  | 0.75 | Single Service |  | Other |  |  | Other |  | 2009-05-04 | 2010-10-05 | Other |  |  |  | KING CITY | SAME AREA; YELLOW PAINT; REPLACED REG AND RELIEF- REDOPPED; FOUND LEAK ON BYPASS VALVE, INLET TO REG AND H2 RELIEF ON D.S. VALVE, REPLACED HPR REG WITH FISHER 627, REPLACED H20R RELIEG AND D.S. VALVE, REDOPPED AND....
58 | 08-20306-1 | WALSH DF |  | 4 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | External Corrosion |  | 2008-05-21 | 2010-09-30 | Mechanical Repair Fitting - Fitting |  |  |  | ATHERTON | ...HE INTERSECTION BY THE S IN STREET; LINE OF TALLWOOD & WALSH IN THE MIDDLE...; SAME; INSTALL PLIDCO CLAMP; INSTALL 1-4" PLIDCO CLAMP
8 | 09-80046-1 | 300B |  | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2009-10-20 | 2010-11-11 | Other |  | Steel-Other |  | HOLLISTER | LEAK ON VALVE NO #2; NO LEAK; NO REPAIR MADE- FOUND ALREADY REPAIRED; SOAP TEST OK
5 | 09-50128-1 | 187 |  | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2009-05-08 | 2010-11-05 | Other |  |  |  | CHUALAR | YELLOW PAINT; SAME AREA; YELLOW PAINT; INSTALLED LUBE PITTING LUBED; INSTALLED LUBE FITTINGS IN INLET VALVE AND BYPASS VALVE AND LUBED VALVES, PAINTED HPR= SOAP TEST OK
87 | 09-80107-1 | 402 | 30.68 | 4 | Transmission >= 20% SMYS |  | Line Valve |  |  | Equipment Malfunction |  | 2009-05-26 | 2010-11-18 | Replace Main Valve >= 2-inch |  | Steel-Other |  | REDDING | VALVE 250- N/W VALVE; VALVE 250; VALVE 250; NO GAS FOUND; REPLACED VALVE 250- N/W/ VALVE
4 | 09-40051-1 | 187 |  | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2009-05-08 | 2010-11-05 | Other |  |  |  | KING CITY | SAME AREA (YELLOW PAINT); INSTALLED LUBE FITTINGS- LUBED; INSTALLED LUBE FITTINGS AND LUBED VALVES, REPLACED D.S. VALVE AND RESEALED FITTINGS, PAINTED HPR SET, SOAP TEST OK, FOUND HPR OFF AND LEFT IT OFF.
76 | 10-10009-1 | DFM9 |  | 0.75 | Single Service |  | Regulator/Pilot |  |  | Atmospheric Corrosion |  | 2010-02-25 | 2010-12-20 | Other |  | Steel-Other |  | SANTA CRUZ | LEAK ON HIGH TO HIGH SET; ATMOSPHERIC CORROSION, PITTEED AND LEAKING; REPLACED HPR SET; USED HP PRETESTED SEAMLESS PIPE NIPPLES TO REPAIR- SOAP TEST OK
8 | 10-80185-1 | 300B |  | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-09-13 | 2010-12-10 | Other |  | Steel-Other |  | PAICINES | LEAK AT HIGH SIDE VALVE; REBUILT SET; REBUILT THE HPR SET- SOAP TEST OK
20 | 10-05018-1 | 123 |  | 6 | Transmission >= 20% SMYS |  |  |  |  | Construction Defect |  | 2010-09-11 | 2010-09-23 | Other |  |  |  | LINCOLN | REGULATOR FOR VALVE15; REBUILT ACTUATOR
5 | 10-50200-1 | 103 | 66 | 0.75 | Transmission >= 20% SMYS |  | Other |  |  | Unknown |  | 2010-10-08 | 2011-01-03 | Other |  | Steel-Other |  | SALINAS | LEAK AT RELIEF VALVE; REPLACE RELIEF; REPLACE H202 RELIEF, CHECK LOCK UP, SET PRESS AT 40#, SOAP TEST OK
5 | 10-50197-1 | MTY#1 | 8.19 | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Unknown |  | 2010-10-07 | 2010-12-27 | Other |  | Steel-Other |  | SALINAS | ABOVE GROUND ON BYPASS VALVE HPR 366...;INSTALLED NEW FITTING
8 | 10-80187-1 | 300B |  | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-09-13 | 2010-12-07 | Soap and/or Tape - Other |  |  |  | PAICINES | 2 STAGE ON TAP;REMOVED PIN-OFF CAP; REMOVED THE PIN-OFF CAP SOAP TEST OK
52 | 10-21367-1 | DFM | [9 empty] | 2010-06-01 | [5 empty] | SACRAMENTO | @ V-D52D IN SIDEWALK, MADISON & FAIR...; DELETE
91 | 99-30189-1 |  |  | 0.75 | Single Service |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 1999-08-09 | 2010-12-15 | Other |  | Steel-Other |  | RIVERBANK | O/MAIN AT SVC TEE; O/SVC 15' W/O PAVEMENT 12' N/O TEE HPR?; SAME; AT HPR; INST. NEW REG AND RELIEF
11 | 10-00072-1 | 50 | 11.55 | 8 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-14 | 2010-10-25 | Mechanical Repair Fitting - Fitting |  |  |  | LIVE OAK | FOUND CORROSION LEAK ON PIPE. PUT ON PLIDCO LEAK CLAMP, SOAP TESTED
43 | 09-00178-1 | 0405-02 |  | 4 | Transmission >= 20% SMYS |  |  |  |  | Construction Defect |  | 2009-12-02 | 2010-11-30 | Replace #TP Main < 50 ft |  | Steel-Other |  | ST. HELENA | (CGT) O/4" TP MAIN 457' W/O DRIVEWAY TO; (5YR) O/4" TP MAIN 457' W/O DRIVEWAY TO; O/4" TP MAIN W/O DRIVEWAY TO ADDRESS; LEAK ON 4" TP MAIN 200' W/O D/W TO ADDRESS; REPLACE 5' OF 4" STL PIPE
24 | 10-00200-1 | 131 |  | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Weld Failure |  | 2010-11-16 | 2010-11-19 | Fill Weld - Weld |  |  |  | LIVERMORE | OUTSIDE REG PIT 3' FROM BOX; OUTSIDE REG PIT 3' FROM BOX; RE-WELDED 45 DEGREE SOCKET WELD FITTING; NOTIFIED PIPE ENFINEER/ SOAP TESTED
44 | 10-00339-1 | 1 |  | 8 | Transmission >= 20% SMYS |  | Drip |  |  | Construction Defect |  | 2010-09-29 | 2010-10-21 | Replace #TP Main < 50 ft |  |  |  | PENNGROVE | AT INTER. 20' FROM EDGE OF ORH; SAME, YELLOW CIRCLE; CUT OUT DRIP; REPLACE DRIP W/42" SECTION OF 8" PIPE. DIANE MATSON DID TEST
11 | 10-06021-1 | 121 |  | 3 | Distribution Main >60 PSIG and <20% SYMS |  | Line Valve |  |  | Other |  | 2010-11-17 | 2010-11-17 | Greased - Other |  | Steel-Other |  | YUBA CITY | LEAK IN REG PIT TURNED OVER TO T&R; GREASED VALVE
93 | 10-06301-1 | DFM-14 |  | 0.75 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Equipment Malfunction |  | 2010-11-02 | 2010-11-02 | Other |  |  |  | RIPON; | RELIEF BLOWING, BAD REG.; ISNTALLED NEW HPR REG.; REBUILT HPR BOX, INSTALLED NEW FISHER 627
56 | 10-10108-1 | 101 |  | 2 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-09-13 | 2010-09-13 | Other |  |  |  | DAILY CITY
78 | 10-10590-1 | 100 |  | 6 | Transmission >= 20% SMYS |  | Fitting |  |  | Unknown |  | 2010-09-11 | 2010-09-12 | Other |  |  |  | SAN JOSE; | LEAK FROM GREASE BUTTON HAD TO REPLACE; GREASE BUTTON LEAKING @ V-3414-CBD, REPLACED GREASE BUTTON, SOAP TEST GOOD
78 | 10-10594-1 | 100 |  | 2 | Transmission >= 20% SMYS |  |  |  |  | Material Failure |  | 2010-09-12 | 2010-09-17 | Other |  |  |  | SAN JOSE | POSTED IN GIS 2/16/11; TULLY STA.; HCA?; REPLACE GASKET; CLEARANCE SJ-10-08, REMOVED BONNET ON 2" KENDTEST (720W09) SERIES 300, BALL VALVE, CLEAKNED, REPLACED GASKET
78 | 10-10651-1 | 0833-04 |  | 8 | Transmission >= 20% SMYS |  | Fusion Joint |  |  | Other |  | 2010-09-15 | 2010-11-04 | Fill Weld - Weld |  |  |  | GILROY | POSTED IN GIS 2/16/11; 0833-04; TP DFM.; WELDED OVER THREADS; SOAP TESTED.
76 | 10-20112-1 | 181 |  | 0.75 | Single Service |  | Fitting |  |  | Other |  | 2010-09-28 | 2010-09-28 | Other |  |  |  | PAJARO | POSTED IN GIS 2/16/11; DCUST 2083; D; SERV.; REPLACED UNION & COUPLING REDOPED; FIXED LEAK ON DOWN TREAM UNION & COUPLING & RE-DOPE.
58 | 10-20144-1 | 109 |  | 2 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-09-12 | 2010-09-12 | Other |  |  |  | REDWOOD CITY | PODYRF IN GIS 2/16/11; 0207-01; D DFM.
76 | 10-20324-1 | 1816-20 |  | 3 | Gathering |  | Fitting |  |  | Other |  | 2010-10-21 | 2010-10-21 | Other |  |  |  | WATSONVILLE | POSTED IN GIS 2/16/11; DFDS 3654; TP DFM.; RLSC NOT IN IGIS;
76 | 10-20327-1 | 1 |  | 0.75 | Single Service |  |  |  |  | Unknown |  | 2010-10-19 | 2010-10-19 | Other |  |  |  | WATSONVILLE | POSTED IN GIS 2/16/11; DCUST 1947; D SERV.; INSTALLED A GREASE FITTING; INSTALLED LUBE FITTING & OPERATED LUBED VALVE.
24 | 10-20881-1 | 105 |  | 8 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Other |  | 2010-10-22 | 2010-10-22 | Other |  |  |  | SAN LORENZO | POSTED IN GIS 2/16/11; SAN LORENZO; STA; HCA; REPAIRED LEAKING NEEDLE VALVE ON D/S SEN.
78 | 10-21119-1 | 0821-02 |  | 10 | Transmission >= 20% SMYS |  | Girth Weld |  |  | Weld Failure |  | 2010-06-17 | 2010-09-14 | Welded Sleeve/Can - Weld |  |  |  | SAN JOSE | POSTED IN GIS 2/16/11; 0821-02; D DFM; WELDED A 24'' LONG SLEEVE OVER LEAKING WE; WELDED A 24'' LON GSLEEVE OVER LEAKING WELD ON 10'' T.P. MAIN. SLEEVE WAS X-RAYED & SOAP TESTED @ LINE PRESSURE O.K.
52 | 10-21287-1 | 116 |  | 1 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-05-13 | 2010-12-06 | Other |  | Steel-Other |  | SACRAMENTO | POSTED IN GIS 2/17/11; SAC LOAD CTR. 1' SNT PIPE; REPLACED O-RINGS IN CAPS; REPLCAED O-RINGS IN CAPS & SOAP TESTED FOR LEAKS NO MORE LEAKS.
78 | 10-21702-1 | 300A | 502.12 | 34 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-09-11 | 2010-09-13 | Other |  |  |  | MILPITAS | POSTED IN GIS 2/17/11; 300A; T BB HCA; CLEANED PLUG THREAD AND REPLACE; GENERAL INFORMATION DUG UP MLV 502.12 300A APPROXIMATELY 10' EXPOSED FOUND 2ND BODY CAVITY PLUG LEAKING. CLEANED AND REPLACED PLUG. LINE SIZE 34''.
78 | 10-21707-1 | 132 |  | 24 | Transmission >= 20% SMYS |  | Fitting |  |  | Unknown |  | 2010-09-12 | 2010-09-12 | Mechanical Repair Fitting - Fitting |  |  |  | SAN JOSE | POSTED IN GIS 2/17/11; 132; T LT HCA; TIGHTEN SENSING LINE FITTING & SOAP TESTED OK.
78 | 10-21708-1 |  |  | 3.5 | Distribution Main <= 60 PSIG |  | Fitting |  |  | Other |  | 2010-09-12 | 2010-09-12 | Mechanical Repair Fitting - Fitting |  |  |  | SAN JOSE | POSTED IN GIS 2/17/11; DFDS 3586; D DFM; RESEAL PIPE PLUG & SOAP TESTED OK.
78 | 10-21811-1 | 100 | 14.93 | 6 | Distribution Main >60 PSIG and <20% SYMS |  |  |  |  | Incorrect Operation |  | 2010-11-08 | 2010-11-08 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | MILPITAS | POSTED IN GIS 2/17/11; DFDS3570; D DFM; TIGHTENED VALVE;
78 | 10-30003-1 | 300A | 502.12 | 34 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-09-11 | 2010-09-13 | Other |  |  |  | MILPITAS | POSTED IN GIS 2/17/11; 300A; T BB HCA; BODY CAVITY PLUG CLEANED & REPL. PLUG LIN;
43 | 10-30109-1 | 6-0406-1 |  | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Construction Defect |  | 2010-09-10 | 2010-09-10 | Other |  |  |  | NAPA | POSTED IN GIS 2/17/11; DCUST 862; D SERV; REPLACED LEAKING BLOW-OFF IN HPR BOX; SOAP TEST.
80 | 10-30678-1 | 132 |  | 16 | Transmission >= 20% SMYS |  | Fitting |  |  | Construction Defect |  | 2010-09-11 | 2010-09-12 | Tighten Cap/Bolt - Fitting |  |  |  | MT. VIEW | POSTED IN GIS 2/17/11; X6430; T DFM HCA; REDOPED CAP AND TIGHTEN; SOAP TEST
80 | 10-30737-1 | 8805-04 |  | 2 | Transmission >= 20% SMYS |  |  |  |  | Construction Defect |  | 2010-09-30 | 2010-10-01 | Replace Main Valve >= 2-inch |  | Steel-Other |  | MT. VIEW | POSTED IN GIS 2/17/11; DREG 5618; D SERV.; REPLACE VALVE; REPLACE VALVE-SOAP TEST;
80 | 10-31111-1 | 132 |  | 8 | Single Service |  |  |  |  | Other |  | 2010-09-12 | 2010-09-12 | Other |  |  |  | PALO ALTO | POSTED IN GIS 2/17/11; GCUST ...814; TC SERV HCA; GREASE VALVE SOAP TEST.
72 | 10-35216-1 | 118 | 6.59 | 0.75 | Single Service |  | Other |  |  | Other |  | 2010-09-30 | 2010-10-12 | Other |  |  |  | MADERA | POSTED IN GIS 2/17/11; DCUST 1220; D SERV; REPLACED RELIEF VALVE; REPLACED RELIEF VALVE; REPLACED RELIEF VALVE SOAP TEST OK.
66 | 10-20044-1 | SCG |  | 2 | Transmission >= 20% SMYS |  | Line Valve |  |  | No/Deteriorated Pipe Dope |  | 2010-03-09 | 2010-12-03 | Remove/Replace Completion Plug Fitting |  | Steel-Other |  | SHANDON | POSTED IN GIS 2/16/11; UTREG 6323; D SERV.; SHUT VALVE OFF AND REPAIRED LEAK; FOUND LEAK ON BLEED LINE AT BOTTOM OF THE VALVE. SHUT VALVE AND REPAIRED LEAK.
72 | 10-35229-1 | 118 |  | 0.75 | Distribution Main >60 PSIG and <20% SYMS |  | Fitting |  |  | Other |  | 2010-11-24 | 2010-11-24 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | MADERA | POSTED IN GIS 2/17/11; STUS 6107; TI LT HCA; TIGHTENED NUT ON 3/4'' VALVE
5 | 10-50167-1 | 301-B |  | 0.75 | Single Service |  |  |  |  | Other |  | 2010-09-09 | 2010-09-13 | Other |  |  |  | SALINAS | POSTED IN GIS 2/17/11; DCUST 2522; D SERV.; REPLACED VALVE; REPLACED 7 GREASE FITTING
5 | 10-50173-1 | 301B |  | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-09-30 | 2010-12-09 | Soap and/or Tape - Other |  | Steel-Other |  | SALINAS | POSTED IN GIS 2/17/11; DCUST 2525; D SERV.; REPAIRED THE LEAKS, SOAP TESTED OK.
5 | 10-50189-1 | 187 |  | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-10-01 | 2010-12-23 | Mechanical Repair Fitting - Fitting |  | Steel-Other |  | SALINAS | POSTED IN GIS 2/17/11; DCUST 2190; D SERV.; REBUILT HPR SET-SOAP TESTED OK.
5 | 10-50194-1 | 301B | 6 | 12 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | Digin/Excavation |  | 2010-10-02 | 2010-10-03 | Other |  |  |  | SALINAS | POSTED IN GIS 2/17/11; 301B; T LT; CLOSE 2 VALVES, BLOW DOWN PIPE, REPLACE; JASON BRUNI TESTED PIPE 10/2/2005.
5 | 10-50194-1 |  |  | 12 | Transmission | [12 empty] | SALINAS | FARMER WAS RIPPING FIELD AND STRUCK A 12'' TRANSMISSION LINE. OPERATOR WAS TOLD NOT TO RIP OVER GAS LINE AND DID NOT RAISE RIPPER ON LAST PASS.
5 | 10-50300-1 | 1 |  | 0.75 | Single Service |  | Regulator/Pilot |  |  | Other |  | 2010-10-19 | 2010-10-19 | Other |  |  |  | SALINAS | POSTED IN GIS 2/17/11; DCUST 2104; D SERV.; REPLACE REG H-202, TIGHTENED FITTINGS; REPLACED REG & RELIEF & RESEALED FITTINGS
72 | 10-55032-1 | 186 |  | 6 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | Digin/Excavation |  | 2010-11-29 | 2010-11-30 | Replace #TP Main < 50 ft |  | Steel-Other |  | CHOWCHILLA | POSTED IN GIS 2/17/11; 186; T LT; INSTALLED 41'' OF 6'' PRETESTED PIPE BY GC; 42'' CAN OF 6'' PRETESTED GC NEWMAN. 452'' SE OF REG PIT, RA50 TRIANGLE T RANCH.
72 | 10-55032-1 |  |  | 6 | Transmission | [12 empty] | ESCALON | CONTRACTOR RIPPED FIELD HIT AND DAMAGED 6" STEEL TRANS PIPE. ; EXCAVATOR WAS TOLD TO STAY 20-30 FT. AWAY WHILE RIPPING THE AREA.
50 | 10-55104-1 | DFM |  | 6 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | Internal Corrosion |  | 2010-10-26 | 2010-10-27 | Mechanical Repair Fitting - Fitting |  |  |  | YOLO | POSTED IN GIS 2/17/11; 0646-01; T DFM; SOAP TESTED @ LINE PRESS., 3118335 VITON SEAL 1000MAOP 6'' PLIDCO.
50 | 10-55105-1 | DFM |  | 1 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-11-03 | 2010-11-03 | Other |  |  |  | DAVIS | POSTED IN GIS 2/17/11; DCUST 988; D SERV.; SEE COMMENT "ASBUILT" SECTION; MULTIPLE LEAKS ON 1ST STAGE REG DIAPHRAM HEAD BOLTS, AND AT THEADS TO REG & VALVE.MULTIPLE LEAKS ON MONITOR THREADS TO BODY & AT THREADS TO VALVE. MULTIP.
9 | 10-56009-1 |  |  | 0.75 | Single Service |  | Body of Pipe |  |  | Digin/Excavation |  | 2010-10-20 | 2010-10-22 | Replace Partial Service |  | Steel-Other |  | COLUSA | POSTED IN GIS 2/17/11; 172A T LT; UNMAPPED HPR; EM INSTALLED AT PIN OFF TEE LOCATION;
9 | 10-56009-1 |  |  | 0.75 | Service | [13 empty] | RIPPING FIELD - RIPPED INTO .75 STL SERVICE.
13 | 10-60088-1 | 167 | 15.24 | 0.75 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | Previously Damaged |  | 2010-10-05 | 2010-10-06 | Other |  |  |  | RICHVALE | POSTED IN GIS 2/17/11; 167 T LT; HPR; SOAP TEST OK.
58 | 10-60186-1 | 109 |  | 0.25 | Transmission >= 20% SMYS |  | Fitting |  |  | Construction Defect |  | 2010-09-23 | 2010-09-27 | Other |  |  |  | STANFORD | POSTED IN GIS 2/17/11; DFD53590; TC SERV; FOOTHILL EXPY, PALO ALTO; REPAIRED BY DAG. REDOPED 1/4'' PLUG ON GAUGE TAP.
58 | 10-60285-1 | 132 |  | 2 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | External Corrosion |  | 2010-12-10 | 2010-12-10 | Patch Weld - Weld |  | Steel-Other |  | SAN MATEO | POSTED IN GIS 2/17/11; DCUST 810; D SERV.; HIGH TO HIGH 40' S/ OF 6'' MAIN. INSTALL.
56 | 10-70001-1 | 132 |  | 30 | Transmission >= 20% SMYS |  | Unknown |  |  | Unknown |  | 2010-09-09 | 2010-09-09 | Other |  |  |  | SAN BRUNO | POSTED IN GIS 2/17/11; 132; T LT HCA.
7 | 10-70364-1 | 1 |  | 0.75 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Other |  | 2010-10-18 | 2010-10-18 | Other |  |  |  | MONTEREY | POSTED IN GIS 2/17/11; DREG SO86; D SERV.; REBUILT STATION - GREASED BYPASS VALVE; REBUILT REG STA - GREASED AND OPERATED BYPASS VALVE.
8 | 10-80185-1 | 300-B |  | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-09-13 | 2010-12-10 | Other |  | Steel-Other |  | PAICINES | POSTED IN GIS 2/17/11, 300B; T BB; REBUILT SET; REBUILT THE HPR SET - SOAP TESTED OK.
8 | 10-80186-1 | 300B |  | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-09-15 | 2010-12-07 | Soap and/or Tape - Other |  | Steel-Other |  | PAICINES | POSTED IN GIS 2/17/11; 300B; T BB; REPAIRED THE LEAKING PIN OFF TEE;
5 | 10-50305-1 | 301C |  | 0.75 | Single Service |  |  |  |  | Atmospheric Corrosion |  | 2010-11-15 | 2011-02-09 | Mechanical Repair Fitting - Fitting |  | Steel-Other |  | SALINAS | POSTED IN GIS 2/22/11; ... ; D SERV.; REPAIR GAS LEAK AT REG UPSTERAM AND DOWNSTREAM UNIONS. CHECK FOR LOCK UP GOOD - REPLACED RELIEF H202 REPLACE RELIEF METRIC VALVE - AF/AL PRESS SET AT 25.
91 | 10-50252-1 | 7226-01 |  | 8 | Distribution Main >60 PSIG and <20% SYMS |  | Fusion Joint |  |  | Weld Failure |  | 2010-10-06 | 2010-10-30 | Replace #TP Main < 50 ft |  | Steel-Other |  | MODESTO | POSTED IN GIS 2/22/11; 72... ; TI DFM; INST. NEW PIPE;
48 | 10-33042-1 | 210 | [9 empty] | 2010-05-26 | [5 empty] | SUISUN | POSTED IN GIS 2/16/11; DREG 5266; TI SERV.;
48 | 10-33041-1 | 210 | [9 empty] | 2010-05-26 | [5 empty] | SUISUN | POSTED IN GIS 2/16/11; DREG 5266; TI SERV.;
8 | 10-80187-1 | 300-B |  | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-09-13 | 2010-12-07 | Soap and/or Tape - Other |  |  |  | PAICINES | POSTED IN GIS 3/1/11; DCUST 9120; D SERV.; REMOVED PIN-OFF CAP; REMOVED THE PIN-OFF CAP SOAP TEST OK.
5 | 10-50070-1 | 1881-01 | 2.74 | 2 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-03-18 | 2010-03-18 | Other |  |  |  | SALINAS | POSTED IN GIS 3/1/11; DEL MONTE & WILLIAMS STA 2'' STA PIPE; GREASED VALVE; VALVE LEAKING FROM GREASE STEM, GREASED VALVE SOAP TEST OK.
93 | 10-06130-1 | 106 | 2917 | 8 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-04-14 | 2010-04-14 | Other |  |  |  | STOCKTON | POSTED IN GIS 3/11/11; 1641-01; TI DFM; LUBED VALVE/STAND PIPE; SOAP.
52 | 10-20274-1 | DFM |  | 8 | Transmission >= 20% SMYS |  | Fitting |  |  | Construction Defect |  | 2010-08-18 | 2010-08-18 | Tighten Cap/Bolt - Fitting |  |  |  | SACRAMENTO | POSTED IN GIS 3/1/11; 0651-01; T DFM HCA; TIGHTENED BRASS PLUG DOPED & TIGHTENED C; SOAP TESTED.
78 | 10-10595-1 | 100 |  | 20 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-09-12 | 2010-09-12 | Other |  |  |  | SAN JOSE | POSTED IN GIS 3/1/11; 0821-01; TP DFM; OPERATE VALVE; OPERATE VALVE. SOAP & GAS TRACT OK.
40 | 10-20202-1 | 21 | 19.93 | 12 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-11-06 | 2010-11-07 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SAN ANSELMO | POSTED IN GIS 3/1/11; DF 3226; TI SERV.; TIGHTENED PLUG, GREASED VLV, CHANGED FLA.; TIGHTENED PLUG, LOBED VALVE, CHANGED OUT FLANGE GASKET & BOTLS ON B/O VALVE.
8 | 10-80346-1 | 300B | 455.11 | 2 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Other |  | 2010-12-24 | 2010-12-24 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | HOLLISTER | POSTED IN GIS 3/1/11; ... ; TI SERV.; TIGHTENED BOLTS REG DIAFRAM HOUSING, SOA; TIGHTENED BOLTS AROUND REG DIAFRAM HOUSING - SOAP TEST OK.
| 09-40006-1 | 400 | 297.88 | [8 empty] | 2009-07-27 | [5 empty] | ANTIOCH | POSTED IN GIS 3/1/11; 1/2'' GAUGE TUBING IN STATE;
78 | 10-10594-1 | 100 |  | 2 | Transmission >= 20% SMYS |  |  |  |  | Material Failure |  | 2010-09-12 | 2010-09-17 | Other |  |  |  | SAN JOSE | POSTED IN GIS ...; ROUTE = BLANK; TULLY STA; HCA?; REPLACE GASKET; CLEARANCE SJ-10-08 - REMOVED BONNET ON 2'' KENDTEST (720W09) SERIES 300, BALL VALVE, CLEANED, REPLACED GASKET.
78 | 10-10595-1 | 100 |  | 20 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-09-12 | 2010-09-12 | Other |  |  |  | SAN JOSE | POSTED GIS ... ; ROUTE = BLANK; OPERATE VALVE; OPERATE VALVE. SOAP & GAS TRACT OK.
78 | 10-21707-1 | 132 |  | 24 | Transmission >= 20% SMYS |  | Fitting |  |  | Unknown |  | 2010-09-12 | 2010-09-12 | Mechanical Repair Fitting - Fitting |  |  |  | SAN JOSE | POSTED IN GIS ...; ROUTE = BLANK; TIGHTEN SENSING LINE FITTING & SOAP TESTED OK.
72 | 10-35229-1 | 118 |  | 0.75 | Distribution Main >60 PSIG and <20% SYMS |  | Fitting |  |  | Other |  | 2010-11-24 | 2010-11-24 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | MADERA | POSTED IN GIS ...; 3/4'' STA PIPE; TIGHTENED NUT ON 3/4'' VALVE;;
24 | 10-20881-1 | 105 | 23.03 | 8 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Other |  | 2010-10-22 | 2010-10-22 | Other |  |  |  | SAN LORENZO | POSTED IN GIS 5/2... ; SAN LORENZO STA HCA; REPAIRED LEAKING NEEDLE VALVE ON D/S SEN.;
43 | 05-00058-1 | 0407-1 |  | 6 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | External Corrosion |  | 2005-08-19 | 2011-04-04 | Other |  | Steel-Other |  | YOUNTVILLE | POSTED IN GIS 5/12/...; 0407-01 D DFM; INSTALLED PLIDCO CLAMP;;
78 | 10-30003-1 | 300A | 502.12 | 34 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-09-11 | 2010-09-13 | Other |  |  |  | MILPITAS | POSTED IN GIS 5/2 ....; BODY CAVITY PLUG CLEANED & REPL PLUG LIN;
5 | 09-50492-1 | 1812-13 |  | 1.5 | Transmission >= 20% SMYS |  | Bell Joint |  |  | Other |  | 2009-11-02 | 2011-04-27 | Other |  | Steel-Other |  | SALINAS | DELETED FOR GIS 5/2 ...; NON-LEAK DELETE; REDOPE AND TIGHTEN; REMOVE NIPPLE, REDOPE AND TIGHTEN, SOAP TEST OK.
5 | 10-50004-1 | 301-F |  | 3 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2010-01-04 | 2011-04-27 | Other |  | Steel-Other |  | SALINAS | DELETED ...; NON-LEAK DELETE; GREASED AND OPERATED VALVE, TIGHTENED UN; TIGHTENED LOOSE UNION AND GREASED AND OPERATED VALVE, SOAP TEST OK.
78 | 10-21702-1 | 300A | 502.12 | 34 | Transmission >= 20% SMYS |  | Other |  | 34 | Other |  | 2010-09-11 | 2010-09-13 | Other |  |  |  | MILPITAS | POSTED IN GIS 6/27/11; CLEANED PLUG THREAD AND REPLACE; GENERAL INFORMATION DUG UP MLV 502.12 300A APPROXIMATELY 10' EXPOSED FOUND 2ND BODY CAVITY PLUG LEAKING. CLEANED AND REPLACED PLUG. LINE SIZE 34''.
50 | 10-35031-1 | 220 |  | 0.75 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-05-07 | 2011-04-29 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | WOODLAND | UPDATED GIS 6-27-11; DREG 7074; TI SERV.; NON-LEAK DELETE; REDOPED THREADS & SOAP TESTED; SOAP TESTED AT LINE PRESSURE.
98 | 11-52001-1 | 109 |  | 1 | Transmission >= 20% SMYS |  | Other |  |  | Material Failure |  | 2011-01-15 | 2011-01-15 | Other |  | Steel-Other |  | COLMA | A'' STA PIPE; REPAIRED & REBUILT VOLUME BOOSTER, SOAP TE;
44 | 11-00058-1 | DFM-NONE |  | 4 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | Weld Failure |  | 2011-03-08 | 2011-03-08 | Other |  |  |  | SANTA ROSA | POSTED IN GIS 6-23-11; 1307-02; D DFM; LINE CLOSED AT PITS; NEED TO FIX LEAK ON WELD.
30 | 11-43005-1 | 3 |  | 1.05 | Transmission >= 20% SMYS |  | Other Mechanical Joint |  |  | Other |  | 2011-01-05 | 2011-03-31 | Replace Main Valve < 2-inch |  | Steel-Other |  | CONCORD | POSTED IN GIS 6-23-11; 2'' STA PIPE; RPLCD 3/4'' VLV OPERATED PIN OFF T'S TO ST; RPLCD 3/4''VLV ON REG#13. LKNG PACKNG GALND OPERATED PINOFF T'S THAT CONTROL REG #21&22, OPERATED VLVS STOPPD FROM LKING.
91 | 11-50098-1 | F00007 |  | 1.05 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2011-04-05 | 2011-05-03 | Other |  | Steel-Other |  | ESCALON | POSTED IN GIS 6-23-11; DCUST 3058; D SERV.; INSTALLED NEW REG & RELIEF.
13 | 11-60026-1 | DFM |  | 4 | Transmission >= 20% SMYS |  | Threads |  |  | Other |  | 2011-04-12 | 2011-04-29 | Other |  | Steel-Other |  | OROVILLE | POSTED IN GIS; 1027-09 D DFM;
52 | 11-21302-1 | 0671-08 |  | 1.05 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2011-04-13 | 2011-04-13 | Mechanical Repair Fitting - Fitting |  | Steel-Other |  | FAIR OAKS | POSTED IN GIS 6-21-11; 0617-08; TP DFM; SOAP TEST OK.
7 | 11-70059-1 | 181302 | 12.95 | 4 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | Other |  | 2011-04-12 | 2011-04-12 | Welded Sav-A-Valve - Weld |  | Steel-Other |  | SEASIDE | POSTED IN GIS 6-21-11; DREG 5072; D SERV.; WELDED THEAD O LET OVER HOLE AND PLUGGE; SAN BLASTER PUNCTURED HOLE IN 4'' BRIDAL PIPING, WELDED THREAD O LET/SAVE A VALVE OVER HOLE AND PLUGGED - SOAP TEST OK.
35 | 11-30009-1 | 125 |  | 4 | Transmission >= 20% SMYS |  | Girth Weld |  |  | Internal Corrosion |  | 2011-03-21 | 2011-03-22 | Fill Weld - Weld |  | Steel-Other |  | FORTUNA | POSTED IN GIS 6-21-11; 125; GG-U; REPAIR WELD; SOAP TEST.
70 | 11-70085-1 | 111 |  | 1.05 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | Other Natural Forces |  | 2011-03-22 | 2011-03-22 | Skinner Clamp - Clamp |  | Steel-Other |  | FRESNO | POSTED IN GIS 6-22-11 <- COULD NOT FIND; I POSTED A ...W...L 6/29/11; DCUST7107; D SERV.; CLAMP;
52 | 11-21308-1 | 108 |  | 1.05 | Transmission >= 20% SMYS |  | Other Welds |  |  | Construction Defect |  | 2011-05-03 | 2011-05-04 | Fill Weld - Weld |  | Steel-Other |  | SACRAMENTO | POSTED IN GIS 6-22-11; 3/4'' STA PIPE; IRAKING ELBOW REWELDED; LEAKING 3/4'' STEEL-ELBOW LEAKING-REWELDED BY KLF7.
13 | 09-60135-1 | 167 |  | 2 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2009-11-19 | 2011-05-10 | Tighten Cap/Bolt - Fitting |  | Aldyl A (Tan or Gray) |  | GRIDLEY | DREG 8722 D SERV.; DELETED FROM GIS 6-27-11; NON-LEAK DELETE;
13 | 09-60135-1 | 167 |  | 2 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2009-11-19 | 2011-05-10 | Tighten Cap/Bolt - Fitting |  | Aldyl A (Tan or Gray) |  | GRIDLEY | DREG 8722 D SERV.; DELETED FROM GIS 6-27-11; NON-LEAK DELETE.
4 | 09-40139-1 | 187 |  | 2 | Transmission >= 20% SMYS |  |  |  |  | Other |  | 2009-11-20 | 2011-05-10 | Other |  | Steel-Other |  | KING CITY | DCUST2140 D SERV.; DELETED FROM GIS 6-27-11; NON-LEAK DELETE; GREASED AND OPERATED, SOAP TEST OK; GREASED AND OEPRATED VALVES, SOAP TEST OK.
78 | 10-30003-1 | 300A | 50212 | 34 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-09-11 | 2010-09-13 | Other |  |  |  | MILPITAS | BODY CAVITY PLUG CLEANED & REPL PLUG LIN.
| 04-30001- | 125 |  | 6 | [5 empty] | Internal Corrosion |  |  | 2004-01-13 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | FORTUNA | FIELD COLLECTION AND BYPASS STATION.
|  |  |  | 3 | Transmission
|  |  |  | 4 | Service | [6 empty] | 2006-02-25 |  |  |  | Steel/Wrought Iron |  | FORTUNA | 12" DEEP IN READ.
|  | 125 |  | 3 | Gathering | [6 empty] | 2006-02-25 |  |  |  | Steel/Wrought Iron |  | FORTUNA | 18" COVER IN ROAD.
|  | 126B | 4.3568 | 4 | Transmission | [6 empty] | 2005-09-27 |  |  |  | Steel/Wrought Iron |  | EUREKA | 4" LINE 12BB- EUREKA ERCOM REPAIR; HEAVY RUST & PITTING ALONG A 25' SECTION OF PIPE. 2 PLIDCO SLEEVES WERE INSTALLED TO REPAIR PITTED PIPE. SER# 2323583. N. 450-44948. E.398.813. SER#2323573. N.450-4953. E.398.813.
|  | 126A | 4.6696 | 6 | Transmission | [6 empty] | 2005-09-27 |  |  |  | Steel/Wrought Iron |  | EUREKA | 6" LINE L-126A ERCON REPAIR. SO#7048668
|  | 126B | 6.3892 | [15 empty] | JOB 7053790.
|  |  | 0 | [15 empty] | JOB 7053790.
|  | 128 | [13 empty] | Steel/Wrought Iron |  |  | WILLOWS REG STA; REPLACED 40 1/8 END TO END.
|  | 128 | 15.24 | [12 empty] | Steel/Wrought Iron |  |  | WILLOWS REG STA OD 087580; REPLACE VALVE 1 + 7.
|  | 158 | 10 | [9 empty] | 2002-04-26 |  |  | Other | GRB SLEEVES |  | REMOVE OLD VALVE 16 TIE-IN WITH NEW LINE; SOAP @100 PSI. SEE AS BUILTS.
|  | 128 | 9.99 | 3.5 | Transmission | [7 empty] | 2002-04-26 |  |  | Other | SMLS |  | SO #7032725-02. REMOVE OLD VALVES - PIPING. INSTALL NEW STUFF; SOAP TEST @ 100 PSI. SEE AS BUILTS.
|  | 131 | 0.07 | 10.75 | [11 empty] | Steel/Wrought Iron |  |  | 10" MAIN SO SIDE OF BRANNA ISL RD. JOB #6088923. DETAIL 6.
|  | 131 | 0.53 | 10.75 | [11 empty] | Steel/Wrought Iron |  |  | 10" MAIN NORTH OF VALVE 0.54. JOB 6088925. DETAIL 8.
| 99-00003-1 | 131 | 7.38 |  | Transmission |  |  |  |  | Other | WELD DEFECT | 1999-11-02 | [5 empty] | SHERMAN ISL. | ODORANT SMELL, BUBBLING SOUND. INSTALL A NEW 4" BLOW DOWN STACK.
| 85-57003-1 | 131 |  | 12 | Transmission |  | Girth Weld |  |  | Other |  | 1985-07-29 | 1985-10-17 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | REPAIRED LEAK. INSTALL 54" OF 12" PIPE. 330WT API - 5LX GR X-432 ERW. SEE DWG. REPAIRED ON GM 446942-5.
|  | 131 | 17.84 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | NORTH TIE-IN @ BRENTWOOD TERMINAL. SO 7051905. PM 30603529; LINE 131 SOUTH OF BRENTWOOD GAS TERMINAL: BRENTWOOD; CONTRA COSTA COUNTY.;
|  | 131 | 18.78 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | SO 7051905. PM 30603529. SOUTH TIE-IN; LINE 131 SOUTH OF BRENTWOOD GAS TERMINAL: BRENTWOOD; CONTRA COSTA COUNTY.;
|  | 131 | 18.7725 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#7048313; MARSH CREEK RD. & CAMINO DIABLO BLVD. +- 2 WEST OF BYRON : CONTRA COSTA COUNTY.
|  | 131 | 20.88 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD AREA | BE WELD ON 1" SAVE-A-VALVE FOR DRAFTING.
|  | 131 | 25.5 | [15 empty] | COVER ON PIPE 28".
|  | 131 | 26.876 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM# 30675182; INSPECTION ONLY WHILE INSTALLING CATHODIC CABLE ON L-131 @ MP 26.6.
|  | 131 | 24.8831 & 24.8948 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7040545
|  | 131 | 27.03 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7040545. 131-114-303 CROSS TIE.
|  | 131 | 32.3801 & 32.3835 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7040545.
|  | 131 | 38.521 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7040545.
|  | 131 | 38.7169 & 38.7232 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7040545.
|  | 131 | 43.6915 & 43.7374 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7040545.
|  | 131 | 46.3400 & 46.3423 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7040545.
|  | 131 | 50.47 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7040545. NEW MLV V-80. IRVINGTON STATION FREMONT JR.
|  | 131 | 31.8976 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DISTRICT: TRACY. 30603675-09; GENERAL INSPECTION @ TIE IN LOCATION FOR L 131 MP 32.35 OFFSET FOR "NEW PORTOLA" IN LIVERMORE. FM 30603675.
|  | 131 | 31.9368 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DISTRICT: TRACY. 30603675-09. SOUTH TIE-IN; ENERAL INSPECTION @ TIE IN LOCATION FOR L 131 MP 32.38. OFFSET FOR "NEW PORTOLA" IN LIVERMORE. FM 30603675.
|  | 131 | 32.37 | 24 | Transmission
|  | 131 | 36.68 | 24 | Transmission |  |  |  |  | Construction Defect | EXTERNAL CORROSION |  | 2002-09-30 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  |  | SO# 805486. NON-LEAKING DENT & CORROSION REPAIR NEEDED PER BOB FASSETT 8-323-7226. 24 1/8" I.P., 1/2" WT, A441. 50,000 PSI. PPC36710, CODE 02-2735; WELDED SLEEVE OVER DENT.
|  | 131 | 38.56 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DISTRICT: TRACY. SO#7055156-07. INSPECTION @ TIE-IN POINTS.
|  | 131 | 38.7036 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DISTRICT: TRACY. SO#7055156-07. INSPECTION @ TIE-IN POINTS.
|  | 131 | 42.35 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | JOB 30628831. COAT COND FAIR; ON HECH HECY (S.F. WATER DISTRICT) PROPERTY IN SUNOL, CA. ACCESS NORTHERN TIE-IN LOCATION 2 1/2 MILES ALONG DIRT ROADS AND TRAILS. ACCESS SOUTHERN TIE-IN LOCATION 500' ACROSS FIELD FROM GATE.
|  | 131 | 42.38 | [12 empty] | Steel/Wrought Iron |  |  | SO#7036865-03. "P" TIE-IN 24".
|  | 131 | 42.42 | [12 empty] | Steel/Wrought Iron |  |  | SO#7036865-03. "P" TIE-IN 24".
|  | 131 | 43.17 | [15 empty] | CUT OUT OLD DRIP AND REPLACE PIPE 16 DEGREE MITES AND 5' OF PIPE.
|  | 131 | 43.85 | [15 empty] | GPS: R072321B/ OR MP 43.860. ANDRUDE RD. NEAR NURSERY AT "NEW EARTH", GRAVEL RD. MP 43.86 MITER BEND.
|  | 131 | 44.98 | [15 empty] | GPS: RO72321A/ MP 44.97 SHERIDAN BEND SSR. AT SHERIDAN RD ON TOP OF HILL ABOVE DISTRICT REG STATION. MP 44/97. MITER BEND.
|  | 131 | 45.95 | 24
|  | 131 | 33.34 | [14 empty] | LIVERMORE | PM 30660805; COUPON INSTALLATION JOB #30660803. DATE INSTALL 3-26-09. COORDINATES, NORTHING 4171710.571, EASTING 605668.058.
|  | 131 | 46 | 24 | Transmission |  | Girth Weld | [10 empty] | FREMONT
|  | 131 | 46.34 | 24 | Transmission |  | Valves | [10 empty] | FREMONT | DID NOT POST ON GS. NUT... VALUE IS BEING REPLACED...; VALVE HAS A LEAK LOCATED IN STEM PACKING.
|  | 131 | 46.38 | [15 empty] | LINE 131 PIGGING PROJECT. REMOVING PITS/ VALVES ON MISSION HILL OPEN. NOTE: POOR CONDITION ON WRAP. WRAP IS FALLING OFF PIPE. PIPE CONDITION UNDERNEATH IS HEAVY RUST.
|  | 131 | 48.737 | 24 | [11 empty] | Steel/Wrought Iron |  |  | SO# 7045165; INSTALLED IN 194K ON GM 73427.
|  | 131 | 48.86 | [12 empty] | Steel/Wrought Iron |  | FREMONT | GPS FILE R0826AA. LOC#1.
|  | 131 | 49.6959 | [14 empty] | FREMONT | DIST. MILPITAS; POTHOLED FOR STEM UPGRADING WORK. NOTE: PROPSED HOUSE (STRUCTURE) TO BE BUILT IN CLOSE VICINITY OF LINE 131 PIPELINE EASMENT. USA TIDNET 327017. HOUSE ADDRESS 41892 COVINGTON DR. FREMONT.
|  | 131 | 52.75 | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7049025; TIE-IN LOCATION FOR THE REPLACEMTN OF LINE 131 MP 52.75. ORDER NUMBER 7036396.
|  | 131N | 53.27 | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#7049025. TIE-IN LOCATION FOR THE REPLACEMENT OF L-131N M.P. 53.27. ORDER NUMBER 7036396.
|  | 131 | 53.48 | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#7049003; THIS IS A TIE-IN LOCATION FOR THE REPLACEMENT OF L131, M.P. 53.48, ORDER #7036396.
|  | 131 | 53.81 | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7049008. THIS IS A TIE-IN LOCATION FOR THE REPLACEMENT OF L-131 M.P. 5381, ORDER NUMBER 7036396.
|  | 131 | 55.85 | [12 empty] | Steel/Wrought Iron | DSIAW | FREMONT | HAVE A FLANGED 3" GATE TAP VALVE, WILL NOT SHUT IN.
|  | 131 | [16 empty] | 5 LOCATIONS POTHOLED. GPS FILE # MCCARTHY.
|  | 132 | [15 empty] | MILPITAS | R050306A.
|  | 132 | [15 empty] | MILPITAS | R050306A
|  | 132 | 0.7229 | 24 | [11 empty] | Steel/Wrought Iron |  |  | INSPECTION ONLY; DIVISION SAN JOSE. SO 7064905-07. SEE ATTACHED JOB PMNT FOR MORE DETAIL.
|  | 132 | 0.8115 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | SUNNYVALE | LINE 132 STA. 43+25 ROUGHT GCUST 5813. MP. 0.8113. LAT. 22 57.23081. LONG -122 00 52.66880. S. BRITTON ABE, AND TAYLOR AVE. SUNNVALE.
|  | 132 | 0.9182 | 24 | [11 empty] | Steel/Wrought Iron |  |  | INSPECTION ONLY; DIVISION: SAN JOSE. SO# 7064905-07. SEE ATTACHED JOB PRINT FOR MORE DETAIL.
|  | 132 | 3.46 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | S.C. | SO# 8055700.
|  | 132 | 3.524 | 24 | Transmission | [6 empty] | 2003-05-12 | 2003-05-13 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SANTA CLARA | SO#7046265. GREAT AMERICA PARK NEAR EAST P/L. REPAIR BY INSTALLING DRESSER 200 SLEEVE.
|  | 132 | 3.78 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | S.C. | SO# 8055700; POOR WRAP.
|  | 132 | 1 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | SUNNYVALE | SUNNYVALE LAKEHAVEN DR. LINE 132. MP 1.00 LATIT 37 23 45.27890 , LONG -122 00 19.09294.
|  | 132 | 13.3 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PALO ALTO | SO# 7041177. PIPE REPLACEMENT; TIE-IN POINTS FOR CONTRACTOR INSTALLED PIPE REPLACEMENT.
|  | 132 | 13.3027 & 13.5278 | [15 empty] | SO# 7041177.
|  | 132 | 13.6 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PALO ALTO | SO# 7041177. PIPE REPLACEMENT; TIE-IN POINTS FOR CONTRACTOR. INSTALLED PIPE REPLACEMENT.
|  | 132 | 23.42 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | REDWOOD CITY | SO# 7055152-05. DIV: PENINSULA; EXPOSED CRETE COATING.
58 | 88-20370-1 | 132 | 30.44 | 30 | Transmission |  | Longitudinal Weld |  |  | Material Failure |  | 1988-10-27 | 1988-10-28 | Replace Pipe |  | Steel/Wrought Iron |  | SAN MATEO | INSTALLED 1 - 4 BOLT CLAMP TO STOP LEAK. 11-4-88 GC. REPLACED 30" PIPE; PROBED AND VENTED.
| 88-20370-1 | 132 | 30.4 | 30 | Transmission |  | Longitudinal Weld |  |  | Material Failure |  | 1988-10-27 | 1988-10-28 | Replace Pipe |  | Steel/Wrought Iron |  | SAN MATEO | INSTALLED 1 - 4 BOLT CLAMP TO STOP LEAK. 11-4-88 G.C. REPLACED 30" PIPE; PROBED AND VENTED.
|  | 132 | 38.4096 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN BRUNO | PM 36151-10. SAN ANDREAS CROSSTOE STA; APPROX 10' PF 24" PIPE WAS REMOVED.
|  | 132 | 39.1475 | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN BRUNO | DIVISION: PENINSULA. PM 41363151-10. CUT OUT 7' OF 30" STL ON LINE 132 44' TO CENTER OF 7' CUT OUT SECTION S/S OF ESTATES DR.
|  | 132 | 39.278 | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN BRUNO | DIVISION: PENINSULA. PM 41363151-10; L132 WESTSIDE GLENVIEW DR, 27' N/O EARL AVE. SAN BRUNO, SAN MATEO COUNTY. INSPECTION AREA IN STREET AREA +- 42" COVER COULD NOT MEASURE. 2" MUELLER SAVE-A-VALVE.
|  | 132 | 39.2917 | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN BRUNO | DIVISION: PENINSULA. PM 41363151-10; L132 WESTSIDE GLENVIEW DR, 27' N/O EARL AVE. SAN BRUNO, SAN MATEO COUNTY. +- 42" COVER COULD NOT MEASURE. 2" MUELLER SAVE-A-VALVE.;
|  | 132 | 39.637 | 30 | Transmission | [7 empty] | 2010-10-07 | Replace TP Main |  | Steel/Wrought Iron |  | SAN BRUNO | DIVISION: PENINSULA. PM 41363151-10; 10' X 30" SECTION WAS REMOVED + REPLACED FROM THIS LOCATION.
|  | 132 | 39.6387 | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN BRUNO | DIVISION: PENINSULA. PM 41363151-10; NO WELDING WAS DONE. CUT PIECE WITH SAW MACHINE.
|  | 132 | 39.9375 | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN BRUNO | DIVISION: PENINSULA. PM 41363151-10; APPROXIMATE LOCATION OF PIPELINE INSPECTION + PIPE WRAP SAMPLE.
|  | 132 | 40.05 | 30.00 & 24.00 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN BRUNO | DIVISION: PENINSULA. PM 41363151-10; 24" X 30" REVIEW + APPROX 10' OF 30" PIPE REMOVED.
|  | 132 | 40.9 | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  | SO SAN FRANCISCO | PIPE WAS STRUCK BY GROUND ROD 5' FRM NORTH-EASTERN PROPERTY LINE FENCE AT SOME TIME IN PAST. FOUND AS A CP CONTACT BY MARK AND LOCATE PERSONNEL. PIPELINE EXPOSED TO VERIFY THAT SIGNIFICANT PIPELINE DAMAGE WASN'T DONE. SEE ATTACHED ATS INSPECTION SHEET. DMK6.
|  | 132 | 41.1164 | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  | SOUTH SAN FRANCISCO | SOUTH SAN FRANCISCO. LINE 132 ,P 41.1164. LATIT37 38 37.08835, LONG 122 26 20.89636.
|  | 132 | 42.25 | 30 | Transmission |  |  |  |  | Other | NONE |  | 2001-11-20 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | S.S.F. | GC. CREWS WELDED 30"X18" SLEEVE.
|  | 132 | 45.08 | 30 | [7 empty] | 2005-05-16 | 2005-08-16 | Other | GRINDING |  |  | BRISBANE | GRIND OUT DAMAGE ON TP MAIN.
| 01-20641-1 | 132 | 48.18 | 6 | Transmission |  | Other |  | FLANGES | Other | BAD GASKET | 2001-04-03 | 2002-01-11 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | VALVE #851 B-PASSING CAUSING LEAK @ 6" BLOW-OFF FLANGE; AND 1 1/2" PLUG IN FLANGE. HAD VALVE #851 GREASED. REPLACED GASKET AND 1 1/2" PLUG ON 6" BLOW OFF.
| 03-20491- | 132 | 48.18 | 6 | Transmission |  | Valves |  |  | Other | DRY GREASE | 2003-03-26 | 2003-03-27 | Other | GREASE VALVE | Steel/Wrought Iron |  | SAN FRANCISCO | GREASED TP MAIN VALVE #851.
|  | 132 | 51.44 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN FRANCISCO | SAN FRANCISCO, ILLINOIS ST. LINE 132. MP 51.4468. LATIT 37045 16082461 , LONG-122 23 12.83504.
|  | 132 | 51.4461 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN FRANCISCO | SAN FRANCISCO, ILLINOIS ST. LINE 132. MP 51.4468. LATIT 37045 16082461 , LONG-122 23 12.83504.
|  | 108 | 62.8531 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | ELK GROVE | ELK GROVE. LINE 108. MP 62.8531. LATIT 38 25 30.11845, LONG -121 27 24.34861. THROW WALL CORROSION. THERE IS VERY LITTLE ASPHALT COATING ON THE GAS PIPE.
| 01-20641-1 | 132 | 48.18 | 6 | Transmission |  | Other |  |  | Other |  | 2001-04-03 | 2002-01-11 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | GREASED VALVE #851. REPL GASKET & 1.5" PL.
|  | 134 | 0 | 6 | Gathering | [10 empty] | Steel/Wrought Iron |  | MADERA | SO# 7044028; 6" PIPE CUT OFF 18" OUTSIDE OF BOX. 2" BLOW OFF VALVE.
|  | 134A | 19.0161 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | FIREBAUGH
|  | 134A | 18.763 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | FIREBAUGH
|  | 134A | 18.7536 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | FIREBAUGH
|  | 134A | 18.5112 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | FIREBAUGH
|  | 134A | 18.5102 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | FIREBAUGH
|  | 134A | 18.2753 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | FIREBAUGH
|  | 134A | 18.2677 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | FIREBAUGH
|  | 134A | 18.0353 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | FIREBAUGH
|  | 134A |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | FIREBAUGH
|  | 134A | 17.1968 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | FIREBAUGH
|  | 134A | 17.9558 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | FIREBAUGH
|  | 134A | 17.7225 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | FIREBAUGH
|  | 134A | 27.5 | 3 | Transmission | [6 empty] | 2008-05-07 | 2008-05-08 | Replace TP Main |  | Steel/Wrought Iron |  | MENDOLA | INSTALLED 43.5 INCHES OF 3" GRADE B SMLS .216 K/ALL. INSTALLED (1) 3" ANSI 300 MUELLER P.C.F. INSTALLED (2) 3/4" SAV-A-VALVE. WELDED BY M. WALL AND G. GRANT. INSTALLED (1) BIG FINK WELD LEADS ON 3" AND 6' MAINS. "NOTE" 3" ANSI 300 PCF GPS COORDINATES 30 DEGREES 47.137 MINUNTES NORTH. 120 DEGREES 24.726 MINUTES. WEST ELEVATION 168 FEET.
|  |  |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 134A | 33.7904 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | FIREBAUGH | LINE 134 STA. 11+35. ROUGHT 134A. MP 33.7904. LATIT 36 51 12.05842, LONG -120 26 48.96106. QST. AND 6TH ST. FIREBAUGH.
|  | 134 | 33.7904 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | FIREBAUGH | LINE 134 STA. 11+35. ROUGHT 134A. MP 33.7904. LATIT 36 51 12.05842, LONG -120 26 48.96106. QST. AND 6TH ST. FIREBAUGH.
| 01-75022-1 | 134 | 33.81 | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2001-09-14 | 2001-12-11 | Replace TP Main |  | Steel/Wrought Iron |  | FIREBAUGH
|  | 134A | 34.33 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | FIREBAUGH | PM#30717098; NEW FIRE VALVE.
| 08-30039-1 | 137D | 0.1419 | 10 | Transmission |  | Girth Weld |  |  | Weld Failure |  | 2008-09-17 | 2009-03-18 | Mechanical Repair Fitting - Fitting | FILL WELD DMB; OTHER-PLIDCO CLAMP | Steel/Wrought Iron |  | ARCATA | #41053281; PLIDCO CLAMP WELDED; SEE ATTACHED SKETCH.
|  | 137B | 0.638 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | #30603493
|  | 137B | 0.8928 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 30603493
|  | 137B | 2.74 | 8 | [11 empty] | Steel/Wrought Iron |  |  | INSTALLED ETS STA "SMALL FINK" AT GATE TO 5100 RANCH. JOB 6041269.
|  | 137B | 3.62 | 8 | [11 empty] | Steel/Wrought Iron |  |  | INSTALLED ETS STATION - G5 BOX & 2 WIRES ON CASING 2 WIRES FROM 8" L 137-B. JOB#6041269.
|  | 137B | 5.83 | [12 empty] | Steel/Wrought Iron |  |  | INSTALLED ETS LITTLE FINK L 137B ARCATA. JOB 6041269.
| 08-30038-1 | 137B | 7.22 | 8.625 | Transmission |  | Girth Weld |  |  | Weld Failure |  | 2008-09-17 | 2009-02-15 | Patch Weld - Weld |  | Steel/Wrought Iron |  | ARCATA | PM# 40950067; PREFORMED BY LEE HAYNES CORR. ENG. GROUP (ON VACATION AT THIS TIME); INSPECTION LOCATION AND WELD REPAIRED ARE ON THE EAST SIDE OF RR TRACKS JUST EAST OF CASING (18" TO WELD LOC.);
|  | 137B | 7.2006 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | ARCATA | NORTH COAST. PM# 30709870; ATTACHED 2 WHITE #10 WIRE ON CASING. ATTACHED 2 BLACK #10 WIRE TO TP MAIN.
|  | 137D | 6.89 | 10 | [11 empty] | Steel/Wrought Iron |  | ARCATA | INSTALLED ETS STATION G-5 BOX 2 WIRES FROM 10" L 137D JANES RD & VASSAIDE RD ARCATA.
|  | 137D | 3.09 | [12 empty] | Steel/Wrought Iron |  | ARCATA | INSTALLED ETS "LITTLE FINK" JANES RD ARCATA. JOB 6041269.
| 09-30015-1 | 137D | 0.1269 | 10 | Transmission |  | Girth Weld |  |  | Weld Failure |  | 2009-03-26 | 2009-03-27 | Other | GROUND OUT ENTIRE GIRTH WELD AND REWELDED | Steel/Wrought Iron |  | ARCATA | #41083281. REPAIRED GIRTH WELD; SEE ATTACHED SKETCH.
|  | 127C | 0.29 | [12 empty] | Steel/Wrought Iron |  |  | INSTALLED ETS STA WITH "LITTLE FINK" 20' SPAN. 19-10-00. JOB# 6041269.
|  | 137C | 0.35 | [12 empty] | Steel/Wrought Iron |  |  | INSTALLED ETS STA. @ T-49 MYRTLE AVE. JOB #6041269
| 01-30008-1 | 137C | 1.67 | 4.5 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2001-02-13 | 2001-02-13 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | EUREKA | FINAL REPAIR WELDED 4" CAN (SLEEVE?)
| 08-40012-1 | 137C | 3.12 | 4 | Transmission |  | Body of Pipe |  |  |  |  | 2008-07-21 | 2008-07-22 | Replace TP Main |  | Steel/Wrought Iron |  | ARCATA | DIVISION: NORTH COAST 40927951-08; WHILE DIGGING A CULVERT LOCATION - CONTRACTORS EXCAVATOR SANK AND STRUCK SIDE OF 4" TP L137 WHILE TRYING TO FREE HIMSELF THE TRACKS ON EXCAVATOR STRUCK SIDE OF L137C AND CAUSED GAS LEAK. 3'6" LONG 4" PIPE; FOREMAN TOM HUBUER WAS CONTACTED AND TOLD ABOUT STANDBY REQUIREMENTS. NO STANDBY WAS REQUESTED.
|  | 137C | 3.7 | [12 empty] | Steel/Wrought Iron |  |  | INSTALLED 3 ETS STA L-137 WITH G-5 BOX ON JOB #6041269.
|  | 137C | 3.8891 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM# 30604382.
|  | 137C | 4.0774 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIVISION: NORTH COAST. SO# 808798-07.
|  | 137C | 4.1291 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DM# 30604382
| 04-30042- | 137 | 4.92 | 4 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 2004-12-09 | 2004-12-10 | Other | PLETCO BAND. | Steel/Wrought Iron |  | EUREKA | FLAMEPACKED AREA, FOUND LEAK OUTSIDE T.P. CALLED ... FOUND LEAK & CLAMPED LEAK. REPAIRS MADE W/ 4" PLETCO BAND.
|  | 137C | 7.2031 | [12 empty] | Steel/Wrought Iron |  | ARCATA | SO# 70045451-03. CITY OF ARCATA REMOVED 4" INOPERABLE VALVE.
|  | 137C | 8.04 | [12 empty] | Steel/Wrought Iron |  |  | INSTALLED ETS STA ARCATA (BEHIND SAFEWAY BLDG 7TH AND F ST ARCATA) JOB 6041260
|  | 137C | 8.44 | [12 empty] | Steel/Wrought Iron |  | ARCATA | INSTALLED ETS STA G5 BOXES ON 7TH ST L137C. JOB 6041269.
|  | 137 | [13 empty] | Steel/Wrought Iron |  |  | INSTALLED 1 - G5 BOX ON LINES L137C 4" STL &L137A 8" STL. ON ETS PHASE iii. JOB# 6041269.
| 02-50085-1 | 138 | 35.74 |  | Transmission |  | Body of Pipe |  |  | Digin |  | 2002-06-11 | 2002-06-11 | Other | REPLACE PIPE | Steel/Wrought Iron |  |  | WELDED IN NEW PIECE OF PIPE
|  | 141 | 0.07 | 6.62 | [11 empty] | Steel/Wrought Iron |  |  | AT CASING CROSSING RR ROW
|  |  | 2.7083 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#7047568. DEACTIVATE LINE.
|  |  | 0.3896 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | INSTALLED 4" LINE STOPPER & WELD CAP.
|  |  | 5.3092 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | INSTALL 6" MUELLER LINE STOPPER.
|  |  | 5.3082 | 6 | Gathering | [10 empty] | Steel/Wrought Iron |  | THORNTON
[5 empty] | Transmission | SERVICE | [12 empty] | SO# 7061707; 16" WAS CUT OFF & LEFT OPEN.
|  |  | 0.0095 | 2 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | THORNTON | REMOVE HPR AND REPLACE WITH 2" STL.
|  |  | 0.0023 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | BAKERSFIELD TAP; PM 30603599 NEW REG STA.
|  |  | 0 | 12 | [11 empty] | Steel/Wrought Iron |  |  | BAKERSFIELD TAP. PM 30603599 NEW REG. STA.
| 03-40096-1 | 1142N | 6.5323 | 12 | Transmission |  |  |  |  | Damage by 3rd Party |  | 2003-12-08 |  |  |  | Steel/Wrought Iron |  | BAKERSFIELD | OVER TRANS MAIN. NO LEAK.
|  | 142S | 2.22 | 10 | Transmission | [7 empty] | 2001-10-03 | Other |  | Steel/Wrought Iron |  | BAKERSFIELD | KERN DIVISION. SO#7037309-. INSTALLED NEW ETS; INSTALLED (2) LOCATING WIRED OFF OF L-142. INSTALLED ABOVE GROUND FINK STATION.
|  | 142S | 1.26 | [14 empty] | BAKERSFIELD | NEED TO MAP E.T.S. ALREADY INSTALLED.
|  | 142S | 5.28 | 4 | Transmission | [7 empty] | 2001-09-24 |  |  | Steel/Wrought Iron |  | BAKERSFIELD | INSTALLED LOCATING WIRES TO DIST & TRANS MAINS; INSTALLED E.T.S (FINK) CONNECTED TO DIST. AND TRANS. MAINS IN SOUTH PIT.
|  | 142S | 6.35 |  | Transmission | [7 empty] | 2001-09-25 | Other | INSTALLED LOCATING WIRES | Steel/Wrought Iron |  | BAKERSFIELD | INSTALLED (2) LOCATING WIRES OFF AT L-142 INTO G-5 BOX.
|  | 142S | 7.36 | [9 empty] | 2001-09-29 |  |  |  |  | BAKERSFIELD | EXISTING ETS MAPPING ONLY. PLEASE MAP EXISTING E.T.S STATION.
|  | 142N | 3.17 | 16 | Transmission | [7 empty] | 2001-08-30 |  |  | Steel/Wrought Iron |  |  | INSTALLED ETS OFF OF L-142; INSTALLED NEW E.T.S ON 142N FOR LOCATING PURPOSES.
|  | 142N | 5.16 | 16 | Transmission | [7 empty] | 2001-09-04 |  |  | Steel/Wrought Iron |  | BAKERSFIELD | INSTALLED ETS OFF OF L-142; CAD WELD (2) WIRES OFF OF L-142. INSTALLED FINK E.T.S NEXT TO LINE MARKER.
|  | 142N | 2.66 | 20 | Transmission | [7 empty] | 2001-08-31 |  |  | Steel/Wrought Iron |  | BAKERSFIELD | INSTALLED E.T.S. OFF OF L-142
|  |  | 0.0019 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | INSPECTION OF NEW BAKER TAP REG-pm30603599
|  | 142 | 3.42-3.67
|  |  | 3.1586 & 3.43 |  | Transmission | [10 empty] | Steel/Wrought Iron |  | BAKERSFIELD
| 99-00004-1 |  |  | 6 | Gathering |  |  |  |  | Damage by 3rd Party | DIGIN | 1999-12-01 | [5 empty] | DIXON | LINE WAS ISOLATED FOR REPAIRS
|  | 143 |  | 6 | Gathering | [12 empty] | DIXON
| 99-00004-1 | 143 |  | 6 | Gathering |  |  |  |  | Damage by 3rd Party | DIGIN | 1999-12-01 | [5 empty] | DIXON | LINE WAS ISOLATED FOR REPAIRS: INSTALLED 50" OF 6" .X42 ERW .156 WALL & 2" SAVE VALVE ROLLED 4 DEGREES TOWARD SIKES ROAD GPS READING
|  | 143 | [13 empty] | Steel/Wrought Iron |  |  | L-143 RETIREMENT, INSPECT FORMS
Steel/Wrought Iron
Steel/Wrought Iron
Steel/Wrought Iron
Steel/Wrought Iron
Steel/Wrought Iron
Steel/Wrought Iron
Steel/Wrought Iron
|  | 143 |  | 6.625 | [11 empty] | Steel/Wrought Iron
|  | 143 |  | 4.5 | [11 empty] | Steel/Wrought Iron
|  | 143 |  | 6.625 | [11 empty] | Steel/Wrought Iron
|  | 143 |  | 3.5 | [11 empty] | Steel/Wrought Iron
|  | 143 |  | 4.5 | [11 empty] | Steel/Wrought Iron
|  |  |  | 6.62 | [11 empty] | Steel/Wrought Iron
|  |  |  | 4.5 | [11 empty] | Steel/Wrought Iron
|  |  |  | 4.5 | [11 empty] | Steel/Wrought Iron
|  |  |  | 4.5 | [11 empty] | Steel/Wrought Iron
|  |  |  | 3.5 | [11 empty] | Steel/Wrought Iron
|  |  |  | 6.25 | [11 empty] | Steel/Wrought Iron
|  |  |  | 06.00 & 04.00 | [11 empty] | Steel/Wrought Iron |  |  | C/O TO PLAT AND RETIRE: SEE DETAIL 4 OF SHEET 3 6" & 4" C/O AND RETIRE
|  |  |  | 02.00 & 03.00 | [14 empty] | SEE DETAIL 5 OF SHEET 2 C/O AT 6' MAIN: C/O 2" AT 6" MAIN THREADED AND CAPPED C/O 3" RISER 48" COVER TO C/O
|  |  |  | 6 | [11 empty] | Steel/Wrought Iron |  |  | C/O 637 AND REMOVED SECTION OF 6" TO PIPE & RETIRE: SEE DETAIL 3 OF SHEET 3
|  |  | 10.7366 | 6.5 | [14 empty] | MILLAR STATION
|  |  |  | 6 | [14 empty] | 2 1/2' OF 6" STL MAIN WAS REMOVED @ THIS LOCATION
|  |  |  | 6.5 | [14 empty] | 2' OF 6" MAIN REMOVED @ THIS LOCATION
|  |  |  | 6.5 | [14 empty] | ABANDONED G/W REMOVED RISER
|  | 144 |  | 6.625 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 6028283 LOC AT VALVE 27 DETAIL #1 L-44
|  | 144 |  | 6.625 | [11 empty] | Steel/Wrought Iron |  |  | JOB#6028283 LOC AT 10 X 6 REDUCER F.S. G.C. 124+74 L-44
|  | 144 | 10.5 | [12 empty] | Steel/Wrought Iron |  |  | JOB# 6028283 LOC AT 10 X 6 REDUCER F.S. G.C. 124+74 L-144
|  | 144 |  | 10.5 | [11 empty] | Steel/Wrought Iron |  |  | JOB #6028283 LOC AT VALVE #6 AT 10 X 6 REDUCER F.S. HO+00 F.S. 205+10 L-144
|  | 144 |  | 6.625 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 602828 LOC AT VALVE A EAST OF VALVE #6 L-144
|  |  |  | 6.625 | [11 empty] | Steel/Wrought Iron |  |  | JOB #7042389 LOC AT MILLAR STA. RT =144; PIPE LINE HAD CRYSTAL LIKE FORMATION INSIDE OF PIPE. NOTIFIED JERRY P... ON LOC SITE AT TIME ...WAS TAKEN AND SENT TO TES FOR TESTING
|  | 144 | 2.38 & 3.54 | 10.75 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | REMOVED 38' OF RETIRED 10" LINE 144 TREEFOIL & ETZEL RD. FOR NEW CULVERT AT CANAL. SO 6028283, ROUTE 144 M.P. BET 2.38 & 3.54; SOLANO CO. RD. CREW REMOVED 38' OF 10" PIPE TO INSTALL NEW CULVERT AFTER CUT OFF (INSTALLED REDWOOD PLUGS) PIPELINE RETIRED ON SO 6028283
|  | 145 |  | 4 | Gathering | [6 empty] | 2000-10-13 | 2000-10-18 | Welded Sleeve/Can - Weld |  |  |  | DIXON | CONTRACTOR HIT LINE NO GAS LEAKING; REPLACED 48" OF 4" LINE
|  | 145 | 0.29 | 4 | Gathering | [6 empty] | 2000-10-13 | 2000-10-18 | Weld Over Sleeve or Can |  |  |  | DIXON | ROUTE 145-1-10 M.P. 0.29 MAINT. ORG- GRV1 RIO VISTA; CONTRACTOR HIT LINE NO GAS LEAKING; REPLACED 48' OF 4" LINE
|  |  | 0 | 4 | [11 empty] | Steel/Wrought Iron |  |  | JOB # 7042389 LOC AT VALVE #1 RT = 145-1-10, M.P. 0.00; SEE DETAIL (1) SHEET 2 OF 3 7042389
|  | 146 | 5.79 | 8 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | L-146 MAINE PRAIRIE JOB# 7046906 (BARKER SLOUGH X-ING SOUTH END); M.P. 5.78 SACRAMENTO DIV; L-146 MAINE PRAIRIE JOB# 7046906 BARKER SLOUGH X-ING SOUTH SIDE; DUG UP AND EXPOSED 8" GAS MAIN (L146 ABANDONED) 100' FROM EDGE OF BARKER SLOUGH. CUT OUT AND REMOVED 3' CAN. WELDED 8" STEEL CAP ON SOUTH SIDE OF SC# SLOUGH CROSSING. MADE READY FOR FILLING 400' OF PIPELINE W/ CONCRETE. 42" COVER ON 8" LINE AT BELL HOLE LOC.
|  | 146 | 4.1 | 8 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | L-146 8" MAIN PRAIRIE JOB # 7046906 (ULATIS CREEK X-ING); M.P. 4.10 SACRAMENTO DIV.; L-146 8" MAIN PRAIRIE JOB# 7046906 (ULATIS CREEK X-ING EAST SIDE; DUG UP 8" STEEL L-146 AT EAST SIDE ULATIS CREEK 100' OFF TOE OF LEVEE. 54" COVER ON ABANDONED 8" GAS MAIN. CUT OUT 4' SECTION OF PIPE. CAPPED OFF ENDS & MADE READY FOR CONCRETE SLURRY OF CREEK X-ING. NOTE: COULD NOT SLURRY X-ING DUE TO HOLE IN PIPELINE. SLURRIED BOTH ENDS, BUT NOT DOG LED UNDER CREEK DUE TO THE HOLE IN PIPE.
|  | 146 | 4.1 | 8 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | L -143 8" MAIN PRAIRIE JOB# 7046906 )ULATIS CREEK X-ING); L-146 8" MAIN PRAIRIE JOB# 7046906 (ULATIS CREEK X-ING EAST SIDE. DUG UP 8" STEEL L-146 AT EAST SIDE ULATIS CREEK 100' OFF TOE OF LEVEE. 54" COVER ON ABANDONED 8" GAS MAIN. CUT OUT 4' SECTION OF PIPE. CAPPED OFF ENDS & MADE READY FOR CONCRETE SLURRY OF CREEK X-ING. NOTE: COULD NOT SLURRY X-ING DUE TO HOLE IN PIPLINE. SLURRIED BOTH ENDS, BUT NOT DOG LEG UNDER CREEK DUE TO THE HOLE IN PIPE.
|  | 146 | 4.45 | 8 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | ALAMO CREEK (MAINE PRAIRE) #7046906- NORTH SIDE; L146 M.P. 4.45 SACRAMENTO DIV; (ALAMO CREEK) MAINE PRAIRE # 7046906 (NORTH SIDE).; DUG UP 8" PIPE LINE AT NORTH SIDE ALAMO CREEK LEVEE.. MADE READY FOR INJECTING CONCRETE INTO ABANDONDED PIPE LINE, FOR CREEK X-ING OLF L-146 ABANDONMENT JOB MAIN PRAIRIE
|  | 146 | 4.48 | 8 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | ALAMO CREEK MAINE PRAIRIE #7046906- SOUTH SIDE-; L 146 M.P. 4.48, SACRAMENTO DIV; (ALAMO CREEK MAINE PRAIRIE # 7046906 (SOUTH SIDE); DUG UP 8" PIPE LINE AT SOUTH SIDE ALAMO CREEK LEVEE MADE READY FOR INJECTING CONCRETE INTO ABANDONED PIPE LINE FOR CREEK X-ING OLD LINE 146 ABANDONMENT JOB MAINE PRAIRIE
|  | 148 | 13.59 | [8 empty] | 2002-07-24 |  |  |  | Steel/Wrought Iron |  | MODESTO | SO# 7044185-02, RT = 148, M.P. 13.59; LINE 148 (8")
|  | 146 | 13.6 | [12 empty] | Steel/Wrought Iron |  | MODESTO | SO # 7044185-02. RT = 148, M.P. 13.60
|  | 144-1-2 |  | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | JOB # 6088685 AT RISER LOCATION WINTERS 4-1 WELL; L-144-1-2
|  | 149-1-2 | 0 | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 6088685 AT CUT OFF LOCATION L-149-1-2, M.P. 0.00
|  | 150 |  | 6 | Transmission | [6 empty] | 1999-08-31 |  |  |  | Steel/Wrought Iron |  |  | L-150 SO #2016646; L-150, M.P. 10.02, 10.32, 10.62, 10.88; LINE #150 2016646
|  | 150 | 17.22 | 1.5 | Service | [10 empty] | Steel/Wrought Iron |  |  | JOB 70451.45 SERVICE ORDER 98268 SERVICE TAP LOC ON LINE 150, MAP NO. 2582; DCUST = 1574, SCR RT= 150, MP= 17.22
|  |  | 15.171 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM 30605995, ROUTE 150, M.P. 15.1710; REMOVED 6" MLV 15.18 AND DRESSER FITTING C/O...; L-150 V-15.18 REMOVED
|  | 151 |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM #30676701, 6" TIE IN ON L-151; SEE STPR; JOB # 30676701
|  | 153 | 10.0137 | [15 empty] | L153 M.P. 10.0137 JOB 7055689
|  | 153 | 9.79 | 30 | [11 empty] | Steel-Other |  |  | 7022907 L-153 MP 9.79
|  | 153 | 10.03 | 30 | [11 empty] | Steel-Other |  |  | 7022907 L-153 M.P. 10.03
|  | 153 | 10.2847 | [15 empty] | L-153 M.P. 10.2847, JOB 7055689
|  | 153 | 17.6281 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN LEANDRO | LT 153, M.P. 176295;; RUN 3 STA. 3+10; M.P. 17.6281; LATIT 37 42 04.83541, LONG -122 10 26.72379; FAIRWAY ST. VALVE STATION SAN LEANDRO; ; COMMENTS/INFORMATION: THIS SITE IS LOCATED AT THE FAIRWAY AVE. CORSSOVER STATION AT 1995 FAIRWAY DR. IN SAN LEANDRO, CA. IT IS IN THE PG&E VALVE YARD. THE DIG WAS HAND DUG DUE TO BEING IN THE VALVE YARD. IT IS ON RUN#3 A 20" WITH A TEE INTO A 30" LINE WAS EXPOSED. THE VALVE YARD IS FENCED IN WITH A RAILROAD TRACKT TO THE SOUTH. THREE COATING TYPES WERE ON THE EXPOSED PIPE. FBE, HAA, AND PROTAL 7200. DITCH WAS EXTENDED TO EXPOSE DISABLED SHUT OFF VALVES WERE PERMANENTLY REMOVED DURING EXCAVATION. AT VALVE, MANUGACTURE COATING WAS FOUND. THE HAA COATING WAS REMOVED FOR INSPECTION. THE PIPE WAS MEDIA BLASTED AND INSPECTED. GENERAL CORROSION AND PITTING FOUND LESS THAN 20%. NOMINAL WALL THICKNESS TAKEN ON 20" PIPE. ATS FOUND LINER INDICATIONS ON THE TWO GW'S NEAR THE D/S EDGE. ENGINEER DAVID AUGIER WAS CONTACTED, PICTURES WERE EMAILED TO HIM FOR REVIEW. DAVID CAME TO THE SITE AND DETERMINED ATS WAS TO BUFF OUT INDICATIONS. PROCESS WAS COMPLETED BY ROBERT MILLER OF ATS. THE PIPE WAS REBLASTED. NEW WIRES WERE CAD WELDED ON. THE PIPE WAS RE-COATED WITH WAX TAPE. NATIVE SOIL WAS USED TO BACK FILL DITCH.
|  | 153 | 17.65 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-153 PM #307079338, M.P. 17.65; INPECTION DONE IN CONNECTION W/ PM 30707938 UPGRADE FAIRWAY STATION CORSSOVER STATION
|  | 153 | 17.65 | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN LEANDRO | LT 153 M.P. 17.6425;; FAIRWAY VALVE STATION ; RUN #1 STA 4+90MP 17.6499; LATIT 37 42 05.36109, LONG -122 10 25.91750; PIPE LINE SIZE VARIES FORM 30" TO 26" & 24"; ; MISC COMMENTS/INFORMATION: THIS SITE IS LOCATED AT THE FAIRWAY AVE. CROSSOVER STATION AT 1995 FAIRWAY DR. IN SAN LEANDRO, CA. IT IS IN THE PG&E VALVE YARD. THIS PIPE IS A 30" WITH A REDUCER TO A 26" DOWN TO A 24". THERE WAS NO CORROSION FOUND. THE PIPE WAS MEDIA BLASTED TWICE. NEW PIPE E.T.S. WIRES WERE CAD WELDED AT THE D/S/ EDGE. THE PIPE WAS RECOATED WITH PROTAL 7200. A COUPON E.T.S. WAS INSTALLED AND THE DITCH WAS FILLED WITH NATIVE SOIL. A LAYER OF ROCK WAS SPREAD OVER SITE AFTER BACKFILL WAS COMPLETED.
|  |  | 23.1287 & 23.2577 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | FORM A 7055945 ROUTE 153 MP 23 1287, MP 23.2577; COLISEUM WY FROM 880 NB HIGH ST OFF RAMP TO HIGH ST.
|  |  | 23.3165 & 23.3391 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | FORM A 7055945 ROUTE 153 M.P. 23.3165, MP 23.3391. LOCATION : HIGH ST (NORTH SIDE_ BETWEEN COLISEUM WY AND OAKPORT
|  |  | 3.7682 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | FORM A SEE ATTACHED ORIGINAL LEAK REPORT (LLEAK #05-21124-1). 7055945, ROUTE 153, MP. 23.7682. LOCATION ALAMEDA AVE NEAR FRUITVALE CROSS STREET
|  |  | 0.0005 | 2 | Transmission | [12 empty] | OAKLAND | SOURCE R-153, M.P. 25.09. DFPS 10651. MP 0.0005. PM# 30631288
|  | 156 | 3.65 | 6.625 | [8 empty] | 2000-09-11 |  |  | Steel-Other |  |  | L-156, M.P. 3.65, SO# 6034483-00; REMOVE RISERS INSTALLED 21' OF PRETESTED 6" .219 TO CONNECT PIPE LINE; SEE AS BUILT
|  | 156 | 3.16 | 6.625 | [8 empty] | 2000-09-08 |  |  | Steel-Other |  |  | L-156, MP. 3.16, SO# 6034483.00; CUT & REMOVED VALVE AND TEE INSTALL 20" OF PRETESTED 6" .219; SEE AS BUILTS
|  | 156 | 2.49 | 6.625 | [8 empty] | 2000-09-08 |  |  | Steel-Other |  |  | L-156, M.P. 2.49, SO# 6034483-00; CUT AND REMOVE VALVE AND TEE INSTALL 21" PRETESTED 6" .219 TO RECONNECT PIPE LINE; SEE AS BUILTS
|  | 156 | 2.42 | 6.625 | [8 empty] | 2000-09-08 |  |  | Steel-Other |  |  | L-156, M.P. 2.42, SO# 6034483-00; CUT AND REMOVE VALVE AND TEE. INSTALL 36" PRETESTED 6" .219 TO CONNECT PIPE LINE; SEE AS BUILTS
|  | 156 | 2.11 | 6.625 | [8 empty] | 2000-09-08 |  |  | Steel-Other |  |  | L -156, M.P. 2.11, SO# 6034483-00; CUT AND REMOVE VALVE AND TEE. INSTALL 36" PRETESTED 6" .219 TO CONNECT PIPE LINE; SEE AS BUILT
|  | 156 | 1.13 | 6.625 | [8 empty] | 2000-09-08 |  |  | Steel-Other |  |  | L-156, M.P. 1.13, SO# 6034483-00; CUT AND REMOVE DRIP INSTALLED 6" CAP; SEE AS BUILT
| 08-35071-1 | 158 | 0 | 0.75 | Distribution Main |  | Other |  |  | Other |  | 2008-05-26 | 2008-07-30 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | YOLO | VALVE #2; VALE #2; TIGHTENED CAP; SOAP TESTED
|  | 159 & 206 |  |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7045145 ROUTE X7739 X-TIE L-159$ C-206; INSTALL 4" VALVE
|  | 162A | 0 | 10 | Transmission | [13 empty] | SO #7048515, STA 5987 (L162A) MP. 0
|  | 162 | 0.17 | 10 | Transmission | [12 empty] | TRACY | ROUTE 162A, M.P. 0.17
|  | 162A | 0.25 | 10 | Transmission | [7 empty] | 2005-10-15 |  |  | Steel/Wrought Iron |  |  | L162A, M.P. 0.2811, JOB 7052169; TIE IN PIPE; ALL PIPE HAD AN 8 HR HYDRO TEST. TIE IN PIECES WERE BUILT AND INSTALLED BY G.C. GAS STOCKTON.
|  | 162A | 0.3085 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 704.... L-162A M.P. 0.3085
|  | 1621-01 | 0.427 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | STOCKTON | ORIG R. BAUTISTA COPY.... GIS L-1621-01, M.P. 0.4274
|  | 162 | 0.76 | 10 | [11 empty] | Steel-Other |  |  | L-162 M.P. 0.76 SO# 7031307-00; LOC L-162, M.P. 0.76
|  | 162A | 0.5 | 10 | Transmission | [7 empty] | 2005-10-15 |  |  | Steel/Wrought Iron |  |  | L-162A M.P. 0.7969 JOB 7050285; TIE IN POINT, WE USED T.D. WILLAMSEN PCF FOR TIE; ALL PIPE HAD AN 8 HR. HYDRO TES6T. WE USED A 10" (600#) TDW/PCF WITH SIDE OUT. ALL TIE IN PEICES WERE BUILT AND INSTALLED BY G.C. GAS STOCKTON
|  | 162B | 1.67 | 6 | [11 empty] | Plastic |  |  | LINE/ROUTE 162B MP 1.67, STOCKTON DIV.
|  |  | 3.64 | 2 | [8 empty] | 2001-10-17 |  |  | Steel-Other |  |  | DREG SOURCE 162A ST. TY HP-05, M.P. 3.64, SO# 6074225, STOCKTON DIV; TIE-IN ROAD CROSSING TO EXSITING 2" GAS MAIN.
|  | 162A | 3.64 | [12 empty] | Steel/Wrought Iron |  | TRACY | INSPECTION REPORT; L-162A M.P. 3.64, SO# 6074225-01
|  | 162A | 4.28 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | 162A M.P. 4.28
|  | 162A | 4.28 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | 162A M.P. 4.28; EXPOSED BY ....
|  | 162 | 4.9677 | [14 empty] | TRACY | ROUTE 162A. M.P 4.9677
|  |  |  | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | STOCKTON 162A 5.157
|  | 162 |  | 10 | [13 empty] | TRACY | 162A M.P. 5.66
|  |  | 6.0365 | 10 | Transmission | [12 empty] | TRACY | RT = 162A, M.P. 6.0365
|  | 162A | 6.184 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | GIS L-162A M.P. 6.1864
|  | 162A | 6.1842 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | TO RAY B. COPY TO ROBERY MACDONALDO. GIS. L-162A, M.P. 6.1842
|  | 162A | 6.2129 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | GAS. L-162A. M.P. 6.2129
|  | 162A | 6.2019 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | GIS L-162A M.P 6.2019
|  | 162A | 6.2486 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | GIS L-162A M.P. 6.2486; TRENCH IS 72" DEEP GAS MAIN IS 54" DEEP PLENTY OF CLEARANCE (16) TAPE 10-5-10; AT 404 GRANT LINE RD. AT E/SIDE OF DRIVEWAY.
|  | 162A | 6.2501 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | GIS L-162A, M.P. 6.2501; TRENCH IS 72" DEEP, GAS MAIN IS 56" DEEP. CLEARANCE IS 17" TAPF 10-5-10; TRENCH IS E/OF DRIVEWAY (45') FROM TRENCH
|  | 162A | 6.26 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | GIS L-162A M.P. 6.26
|  | 162A | 6.3239 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | ORIG TO RAY BAUTISTA, COPY TO ROBERT. GIS L-162A M.P. 6.3239
|  | 162A | 6.3571 | 10 | [11 empty] | Steel/Wrought Iron |  | TRACY | DIV: STOCKTON. ORIG - TO RAY BAUTISTA COPT TO ROBERT. LO 162A, M.P. 6.3571
|  | 162A | 6.491 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | ORIG TO RAY B., COPY TO ROBERT M., GIS L-162A MP 6.4910
|  | 162A | 6.4912 | 8 | [11 empty] | Steel-Other |  | TRACY | L-162A MP. 6.4912
|  | 162A | 6.5039 | [12 empty] | Steel-Other |  | TRACY | L 162A, M.P. 6.5039
|  | 162A | 6.5177 | 8 | [11 empty] | Steel-Other |  | TRACY | L-162A, M.P. 6.5177
|  | 162A | 6.5313 | 10 | [11 empty] | Steel-Other |  | TRACY | L-162A MP6.5313
|  | 162A | 6.5345 | 10 | Transmission | [12 empty] | TRACY | GIS L-162A MP 6.5345
|  |  | 6.5933 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | SO #7038133, ROUTE 162A, MP 6.5953; 10" TDW FITTING WELDED IN AREA CHECKED
|  | 162A | 6.5345 | 10 | Transmission | [12 empty] | TRACY | GIS L162A MP 6.5345
|  | 162A | 6.5886 | 10 | [11 empty] | Steel/Wrought Iron |  | TRACY | DIV: STOCKTON. ORIG TO BAUTISTA, COPY TO MACLDONALOD. LT 162A, M.P.6.5886; 10" MAIN IS 53" DEEP .20" CLEARANCE BETWEEN MAIN AND THEIR PIPE AT S/W CORNER OF GRANT LINER RD. AND HOLLY DR.
|  |  | 6.5962 | 8 | [13 empty] | TRACY | ROUTE 162A, M.P. 6.5962
|  | 162A | 6.5996 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | SO #7038133, ROUTE 162A, MP. 6.5996; MUELLER LOCATION EAST SIDE OF 162 MLV GRANT LINE
|  | 162 | 06.60 & 06.61 | 08.00 & 10.00 | Transmission |  |  |  |  | Other | NO LEAK OR DAMAGE |  |  |  |  | Steel/Wrought Iron |  |  | RT = 1617-01, M.P. 0.0048; RT = 162A, M.P. 6.60 & M.P. 6.61
|  | 162 | 6.61 | 8 | [13 empty] | TRACY | ROUTE 162A, M.P. 6.6100
|  | 162 | 6.6115 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | L-162, M.P. 6.6115. ORIG TO RAY BAUTISTA/ COPY TO ROBERT; ROUTE: 162A, LOCATION:...4-13-09
|  | 162A | 6.623 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | GIS L-162A, M.P. 6.6230
|  |  | 6.723 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | MAIN INSPECTION REPORT. ROUTE 162A, M.P. 6.7238; NO LEAK; PIPE EXPOSED TO REPLACE STORM DRAIN IN CLOSURE
|  | 162 | 06.8682 & 06.8480 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIVISION: STOCKTON. POT HOLE #1, L-162A, M.P. 6.8682; POT HOLE #2 L-162A, M.P. 6.8480
|  |  | 6.853 | 8 | Transmission | [12 empty] | TRACY | TRACY DIST. ROUTE 162A & M.P. 6.8530
|  |  |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT 162A...; POT HOLE ONLY
|  | 162 | 6.9607 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | NO LEAK; DIVISION: STOCKTON; L-162A, M.P. 6.9607
|  |  | 7.0211 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | TO RAY BAUTISTA, COPY TO ROBERT. RT 162A, M.P. 7.0211
|  |  | 7.0218 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | RT 162A, MP 7.0218
|  |  | 7.0491 |  | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | RT 162A, M.P. 7.0491
|  |  | 7.1233 | 8 |  | DFM | [9 empty] | Steel/Wrought Iron |  | TRACY | ROUTE: 162A, M.P. 7.1233
|  |  |  | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | TRACY
|  |  | 7.2076 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | RT: 162A, M.P. 7.2076
|  |  | 7.2095 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | RT: 162A, M.P. 7.2095
|  |  | 7.219 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | RT = 162A, M.P.= 7.2190
|  |  | 8.1133 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | ORIG TO RAY BAUTISTA, COPY TO ROBERT MACDONALD. RT = 162A, M.P. 8.113
|  |  | 8.6316 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | RT = 162A, M.P. = 8.6316
|  |  | 8.6684 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | TRACY | RT = 162A, M.P. = 8.6684
|  |  | 8.6788 | 6 | Transmission | [12 empty] | TRACY | RT = 162A, M.P. 8.6778
|  |  | 8.6875 | 6 | Transmission | [12 empty] | TRACY | RT = 162A, M.P.= 8.6875
|  |  | 6.08 | 8 | Transmission | [10 empty] | Steel/Wrought Iron | PE 2408( YELLOW OR ORANGE) | TRACY | 162A 6.0800 DONECROSSED TWO 8" GAS LINES. THEY WENT UNDER BOTH OF THEM. CLEARANCE WAS 12" BOTH 8" MAINS RUNNING N/TO SOUTH, WERE 53" DEEP. TAPF 8-4-10
68 | 98-70112-1 | 164 |  | 8.625 | Transmission |  | Body of Pipe |  |  | Digin |  | 1998-08-17 | 1998-08-17 | Replace Pipe |  | Steel/Wrought Iron |  | COALINGA | ISOLATED 3 MILES OF TRANSMISSION MAIN TO THE END OF LINE #164 USING VALVE AT AMADOR STA. CUT OUE 6' SECTION OF DAMAGED 8" PIPE, WELDED IN PRETESTED 6' SECTION OF 8" PIPE FOR REPAIRS
|  | 164 | 0.64
|  | 164 | 1.04 | [15 empty] | LOCATION #2; JOB # SP802117; WELD DRESSOR STYLE 220 ENFORCING SLEEVE OVER STYLE 63-2 EXPANSION JOINT
|  | 164 | 1.74 | [15 empty] | LOCATION #3: JOB # SP802117; WELD DRESSOR STYLE 220 REINFORCING SLEEVE OVER STYLE 63-3 EXPANSION JOINTS
|  | 164 | 2.1 | [15 empty] | LOCATION #4; JOB# SP802117; WELD DRESSOR STYLE 220 REINFORCING SLEEVE OVER STYLE 63-0 EXPANSION JOINT
| 10-16401-1 | 164 | 0.34 | 10 | Transmission |  | Mechanical Joint |  |  | Material Failure |  | 2010-04-07 | 2010-04-09 | Bell Joint Clamp | REPLACE DIST MAIN < 100 FT | Steel/Wrought Iron |  | COALINGA | PM# 30768518; ROUTE 164; M.P. 0.334; FOUND A 10" DRESSOR COULING LEAKING AT BOTTOM. CUT A 82" SECTION TO REMOVE COUPLING AND REPLACE IT WITH A 82" OF TESTED 10" PIPE
| 00-16703-1 | 167 | 1.12 | 12 | Gathering | ONLY TO DISTRIBUTION | Body of Pipe |  |  | Internal Corrosion |  | 2000-08-08 | 2001-02-28 | Other | REPLACE |  |  | PRINCETON | POSTED 3/21/2001 RABH 072A S/P; SECTION OF LINE AT 100PSI; AWAITING PERMANENT REG; INSTALLATION & REPAIR CB.; (ALL GATHERING REMOVED); COULD NOT DETECT LEAK AT REDUCED PRESSURE CB 12/19/00; NONE REPLACED WITH TESTED PIPE...12-15-99 R.BOOTH; REPLACED 25' 8" OF 12" PIPE SOUTH TIED TO PREVIOUS LEAK REPLACEMENT OF .281 Y42 ERW
|  | 167 | 1.13 | 12 | Distribution Main |  | Other |  | PIT | Internal Corrosion | [5 empty] | Steel/Wrought Iron |  |  | L-167; MP. 1.13; SO# 6033443-01; 2 LEAKS CUT IN 25' 8"
|  | 167 | 1.32 | [12 empty] | Steel/Wrought Iron |  |  | L-167/DREG; M.P. 1.32; SO#6033943-01; PURGED SOAP TESTED @ 95PSI
|  | 167 | 01.40 & 01.33 | [12 empty] | Steel/Wrought Iron |  |  | SO#6033993-01; L-167; M.P. 1.40 & 1.33; ORCHARD NO LEAKS DETECTED
|  |  | 1.62 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM# 30004367-00 STUB 9181 M.P. 1.62; RT = 167-30; CUT AND CAP 6"
|  | 167 | 2.34 | [12 empty] | Steel/Wrought Iron |  |  | L-167/DREG; M.P. 2.34; SO#6033943-01
|  | 167 | 2.6 | [12 empty] | Steel/Wrought Iron |  |  | L-167; M.P. 2.62; SO# 6033943-01
|  | 167 | 3.53 | [12 empty] | Steel/Wrought Iron |  |  | L-167; M.P. 3.53; SO# 6033943-01
|  | 167 | 3.54 | [12 empty] | Steel/Wrought Iron |  |  | L-167; M.P. 3.54; SO# 6033943-01
|  | 167 | 4.3893 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | JOB 30638082 L-167, M.P. 4.3893
|  | 167 | 5.97 | [12 empty] | Steel/Wrought Iron |  |  | CG - L-167, M.P. .597; CONVERTED DSB; SO #6022605-01
|  | 172A | 7.72 | [15 empty] | SRCMP L-172A, M.P. 7.72; RT 167-68; SO# 7041087-02; RETIRE COMPTON 97-1 WELL
|  | 167 | 18.3 | [8 empty] | 2002-01-25 | [5 empty] | NEAR GRIDLEY | L-167, M.P.18.30 *PIPE AND WRAP INSPECTION ONLY; RAY, THIS IS FOR DU PROJECT PUT GEORGE KARHAGIS WAS WORKING ON. I LOGGED THE DATA AS 01-25-02, THAT IS WHEN THE FIRST ONE THAT WAS ...WAS COMPLETED THANKS, JANE; * SEE ATTACHED SHEETS- * EXCAVATION DUE TO DUCKS UNLIMITED WATER DELIVERY PROJECT- CONCRETE CAP ALSO INSTALLED BY DUCKS UNLIMITED, OK'D BY GERORF KARHAGIS
|  | 167 | 18.3 | [8 empty] | 2002-01-25 | [5 empty] | NEAR GRIDLEY | SO# 8049809-02; L-167 M.P. 18.30 *PIPE AND WRAP INSPECTION ONLY; 1) PAT HARTMAN, NORTH VALLEY, CHICO 2). CARL BISH, MERDIAN DIST. GAH 06/13/02; * SEE ATTACHED SHEETS- * EXCAVATION DUE TO DUCKS UNLIMITED WATER DELIVERY PROJECT- CONCRETE CAP ALSO INSTALLED BY DUCKS UNLIMITED, OK'D BY GEORGE KARHAGIS
|  | 167 | 18.32 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | GRIDLEY | NO LEAK- EXCAVATION DATA FOR CANAL CROSSING; RT = 167, M.P. 18.32; GPS FILE R012322A; PROVIDED DUCKS UNLIMITED DRAWING FOR CONCRETE CAP AND WAX TAPED PIPE PRROR TO CONCRETE POUR; AREA WAS GPS'D - FILE R012322A; 200 YDS S/O WEST EVANS REIMER RD.
|  |  | 33.3247 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | #40965738; rt =167, m.p. 33.3247; REMOVE SECTIOIN OF LINE 167 FOR HYDRO TEST AND PITTING APPROX 83" WAS REMOVED
|  |  | 34.5247 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 40965738; RT = 167 M.P.34.5297; DUG BELL-HOLE TO EXPOSE 16" TRANS MISSION LINE FOR HYDRO TEST. REMOVED SECTION OF LINE 167 APPROX 114" FOR HYDRO TEST PITTING
|  | 167 | [13 empty] | Steel/Wrought Iron |  |  | L-167/DSSN; SO# 6033943-01
|  | 167 |  | 3 | [11 empty] | Steel-Other |  |  | L-167; ROUTE 167-66; GOODMAN I WELL; SO# 6077244-01
|  | 167 | [16 empty] | L-167/DSBN; SO# 6033943-0
|  | 167 | [13 empty] | Steel/Wrought Iron |  |  | L-167/DSBN; SO# 6033943-01
|  | 167 | [13 empty] | Steel/Wrought Iron |  |  | L-167/DREG; SO# 6033943-01; PURGED SOAP TESTED WELDS AT 95PSI
[16 empty] | Steel/Wrought Iron |  |  | GG L-167; CONVERTED DSBN; SO# 6022605-01
GG L-167; CONVERTED DSBN; SO# 6022605-01
VALVE 133 LINE 172 MAIN NOT EXPOSED; TIED IN TO V-97 FOR TERM RP; 3" RISER 3X2 REDUCER TO 2" 600 ANSI FLANGE
| 00-16701-1 | 167 |  | 12 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2000-02-25 | 2000-08-03 | Replace TP Main |  | Steel/Wrought Iron |  | PRINCETON | INSTALED 3' OF 12" PRETESTED PIPE; OD# 082284 WEST LIBERTY
|  | 167 | [16 empty] | SO# 7046905-04; RT STUB7527; L-167; FLANGED VALVE FOR C/O
[5 empty] | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM# 3060... ROUTE 167-62; STUB9204; INSTALLED ED 4" BLIND FLANGE ON VALVE -4
| 99-167-2 |  |  | 12 | Transmission >= 20% SMYS |  | Body of Pipe | Other | DIG-IN PIPE SEVERED | Damage by 3rd Party | OTHER- DIG-IN | 1999-11-11 | 1999-11-12 | Other | INST. 44' PIPE | Steel/Wrought Iron |  | S/E PRINCETON | REPLACED BAD PIPE 44' OF .281 WT. X 42 12" PIPE
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | STUB 9186 OR RE 167-24; PM# 30604367-08; PUT BLIND FLANGE ON 4" VALVE DIDN'T UNCOVER 12" MAIN
|  |  |  | 12 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | PRINCETON | COUNTY LINE REG. STATION; TESTED FOR 8 HOURS/15 MINUTES AT 1225 PSIG- LOW. SEE STPR FOR DETAILS
|  | 167 |  | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | JOB #40755124. R-063; L-167 CONVERTED + DSBN; COPY
|  |  |  | 12 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | COPY
|  |  |  | 12 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | BUTTE CITY | COPY; REMOVED 2" BALL VALVE FROM 2" SAV-A-VALVE. REMOVED DRIP LINE. DID NOT REMOVE WRAP FROM 12" NO WELDING.
|  |  | 0 | 6.62 | [11 empty] | Steel/Wrought Iron |  |  | SHEET 1 OF 2. DETAIL #2 ROUTE# 168-1-1, M.P. 0.00; CUT OFF LOCATION AT VALVE 15 PIT AREA, JOB# 7042489
|  |  | 0.0002 | 2.375 | Gathering | [10 empty] | Steel/Wrought Iron | ; |  | JOB #7051968 ROUTE 168-4-2, M.P. 0.0002
|  |  | 0.54 | 8.62 | [11 empty] | Steel/Wrought Iron |  |  | ROUTE 168-1-1, M.P. 0.54; LOCATION AT VALVE 21 SHEET 2 OF 2 DETAIL 2 JOB# 7042489
|  |  | 2.45 | 6.62 | [11 empty] | Steel/Wrought Iron |  |  | 15' EAST OF VALVE 31 PIT. SHEET 1 OF 2 DETAIL #1 JOB# 7042489; ROUTE 168-1-1, M.P. 2.45
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | RYDE | SO# 7048315; ROUTE 168-2-10
|  | 168-1-1 |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | RYDE | SO# 7042996; ROUTE L-168-1-1 NORTH OF PUCCI METER III CTER. ; CUT & CAP 6" STL & ABAND 6" STL
|  |  | 0.0122 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | #3 ...46 L-167... M.P. 0.0122; PM# 30693862...PM# 3060676-09; JOB# 30610676 & 30693862; REMOVED SECTION OF PIPE W/ TEE & INSTALLED 73" CAN OF 12" 0.281 X 52 ERW
|  |  | 0 | 2 | [11 empty] | Steel-Other |  |  | SO# 6033944-01; ROUTE 169-18-2; M.P. 0.00
|  | 167 & 169 | 0 | [15 empty] | L-167, 169; M.P. 0.00, SO# 60339433-01
|  | 169 | 4.27 | 4 | [8 empty] | 2000-08-03 |  |  | Steel-Other |  |  | MAINT. ORG.... ROUTE 169-1A-5, M.P. 0.00; TIED TO LINE 169 M.P. 4.27; JOB# 6035404-00; CUT & CAP V 76 TO RETIRE ...#1 GAS WELL; SEEE AS BUILT; JOB 6035404 10-16-00
|  | 169-6D-4 | 0.0453 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIST: MERDIAN 7059887; SO# 7059887-06; L-169-6D-4, M.P. 0.0453
|  |  | 0.0021 | 4.5 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | SO#7058131-06; 7058131; DSBN 8658; M.P. 0.0021; DIV: NORTH VALLEY/SOUT (PREVIOUS L-169-15)
|  | 169A | 0.004 | 4 | [8 empty] | 2004-11-04 |  |  |  | G.R.B. SMLS | GLENN | SO# 7047126-04 RT = STUB 7835 (169A) MP 0.004; CUT AND CAP @ V-201 TO ABANDON 70.4; SOAP TESTED @ 150PSI; SEE DRAWING
|  |  | 0.01 | 4 | Gathering | [7 empty] | 2002-04-29 |  |  | Other | GRR SLMS |  | SO# 7032725-02; RT 169-022; M.P. 0.01; CUT AND CAP L-169; SOAP CAP SAVE-A- VALVE @ 100PSI
|  | 169 | 0.11 | [12 empty] | Steel/Wrought Iron |  |  | SO# 7042685 L-169 (GATHERING) RT 169-6D-5, M.P. 0.11
|  |  | 0.9075 | [12 empty] | Steel/Wrought Iron |  |  | DISTRICT MERIDAN; # 7048332-05; ... 169B, M.O. 0.9075; RTE :STUB8281
|  | 169 | 1.0851 | [12 empty] | Steel/Wrought Iron |  |  | DIV: NORTH VALLEY/SOUTH; # 7058131-06; L-169-16, M.P. 1.0851
|  | 169 | 1.15 | [12 empty] | Steel/Wrought Iron |  |  | L-169C, M.P. 1.15, SO# 6033943-01; ABANDON 12" MAIN 169 FROM V105-104
|  |  | 1.7702 | [12 empty] | Steel/Wrought Iron |  |  | SO# 7047005-06 ABANDON MCBURNEY STUBB 660, M.P. 1.7702 DIST MERIDIAN (169-16 = PREVIOUSLY); SEE AS BUILT FOR C/O INFORMATION
|  |  | 1.9349 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | #1 12" PIPE @ ALFALFA FIELD....M.P. 1.9349; PM#3061067...
|  | 196C | 1.96 | [12 empty] | Steel/Wrought Iron |  |  | L-169C, M.P. 1.96, SO# 6033943-01; ABANDON MAIN FROM V-105-104
|  | 169 | 1.9991 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | #5...46 L-169-14 M.P. 1.9991; PM# 30693862; JOB # 30610676 & 30693862; REMOVED SECTION OF PIPE W/ TEE & INSTD 73" CAN OF 12" 0.281" X52 ERW
|  |  |  | 4 | Transmission | GATHERING | [9 empty] | Steel/Wrought Iron |  |  | SRCRE 169-14GG; SRC MP 2.0102; DIST: MERIDIAN/STUB 8572; 7045885; C/O @ VESTNEA #1; SO# 7045885-06
|  |  | 2.4557 | [12 empty] | Steel/Wrought Iron |  |  | DIV: NORTH VALLEY/SOUT; SO# 7058151-06; DSBN8658, M.P.2.4557
;
|  | 169A | 5.0751 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIST: MERIDIAN #7056506 LOCATION #2; L-169A, M.P. 5.0751; SO#7056506-06 LOC#1
| 03-16901-1 | 169 | 5.1337 | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion | OTHER- SUSPECT INT. CORROSION | 2003-12-01 | 2003-12-03 | Welded Sleeve/Can - Weld |  |  |  | WILLOWS
| 98-16902-1 |  | 5.1914 | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-06-07 | 1998-06-18 | Replace Pipe |  | Steel/Wrought Iron |  | WILLOWS | REPAIRED LEAK 163" TESTED PIPE X82 .312 W.T.
| 98-169-3-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-07-01 | 1998-11-06 | Replace Pipe |  | Steel/Wrought Iron |  | WILLOWS | INSTALL 4' PIECE TO REPAIR LEAK
|  | 169A | 6.8701 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIST: MERDIAN; #7056506 LOCATION #2; L-169A, M.P. 6.8701; SO#7056506-02; LOC #2
|  | 169A | 7.7117 | 18 | [7 empty] | 2002-10-31 | [5 empty] | WILLOWS | SO #6091983, ROUTE 169A; M.P. 7.7117 #14; APPLIED TWO WIRES FOR E.T.S.; PUT ON WIRES FOR E.T.S.
|  | 169A | 9.7234 | 18 | [7 empty] | 2002-10-31 | [5 empty] | WILLOWS | SO# 6091983, ROUTE 169A, M.P. 9.7234 #13; PUT WIRES ON PIPE FOR E.T.S. ONLY EXCAVATED TOP OF PIPE BY SOFT DIG; INSTALLED WIRES FOR E.T.S.
PIPE HAD GROVE FROM MANDRILL
|  | 169 |  | 3 | [7 empty] | 2001-11-14 | 2001-11-15 | Welded Sleeve/Can - Weld |  |  |  | PRINCETON | SOIL PIPE DATA ONL NO LEAK RAY BAUTISTA; ROUTE 169-7A-2; (NO LEAK); REPALCED BAD SECTION WITH PRETESTED PIPE; REPLACED WITH 81/2" OF 3.5" OD X .300WT GRB SMLS
|  | 169 | [13 empty] | Steel/Wrought Iron |  |  | L-169-10A-3; SO#7040985-02
SO# 6033945-01 ROUTE 169-1B-5; RETIRE WHYLER 18-1 WELL
|  | 169 | [13 empty] | Steel/Wrought Iron |  |  | L-169 SO# 7040985-02; RICE FIELD;; 18" CAN & SAV-A-VALVE CUT & CAP
|  | 169 | [13 empty] | Steel/Wrought Iron |  |  | L-169-14C-1; SO# 7040985-02
|  | 169 | [13 empty] | Steel/Wrought Iron |  |  | L-169-6B-4; SO# 7040985-02; CUT OFF AT SPRACUR 1-A
|  | 169 |  | 04.00 & 06.00 | [11 empty] | Other | GRB SMLS |  | L-169 MERIDIAN DISTRICT ABANDON PIPE ROUTE 169-008 SEGMENTS 009.1X 008.1X
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 32 AT CHEVERON COMPRESSOR STATION 14081; PM# 30610676-09
|  |  |  | 6 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | #4 6 PIPE @ ALFALFA FIELD
|  | 169 |  | 6 | [11 empty] | Other | GEB SMLS |  | L-169 ROUTE 169-003; SO# 6044143-00
| 99-169-1 | 169 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-05-10 | 1999-06-23 | Other | 9' ... | Steel/Wrought Iron |  | GLENN | SO# 8024070; BUBLES IN FLOODED RICE FIELD; BUBBLES SAME IN FLOODED FIELD; REPLACED.... STET #A-0020-01 FOUND PIN HOLE AT BOTTOM; FOUND PIN HOLE AT 6 O'CLOCK BOTTOM
| 99-169- |  |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-11-26 | 1999-11-27 | Other | 6' 8 1/4" TESTED PIPE | Steel/Wrought Iron |  | GLENN | SO# 8030256; FIRE IN FIELD; FIRE IN FIELD; REPALCE 6' 81/4" .250W.T. PIPE
| 99-169-1 | 169 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-05-10 | 1999-06-25 | Other |  | Steel/Wrought Iron |  | GLENN | BUBLLES IN FLOODED RICE FIELD; REPLACED...SER# A-0020-01
| 98-169-1-1 | 169 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-05-07 | 1998-06-04 | Replace Pipe |  | Steel/Wrought Iron |  | WILLOWS | PRODUCE DECIDED TO SEEM THEIR OWN PIPE AROUND THIS LEAK SECTION. THEREFORE THIS WAS NOT REPAIRD. REQUESTED RETIREMENT JOB FOR THIS PIPE.
| 99-169- |  |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-11-26 | 1999-11-27 | Other | 6'81/4" TESTED PIPE | Steel/Wrought Iron |  | GLENN | SO# 8030256; FIRE IN FIELD' FIRE IN FIELD; REPLACE 6' 81/4" .250 WT. PIPE; WENDY PLEASE ADD THESE...
|  |  |  | 3 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM# 30674584; L-167-8-7 M.P. 0.0004; CL-172A M. 3.586
|  | 172A | 32.0472 | [12 empty] | Steel/Wrought Iron |  |  | DOST: MERDIAN SO#7062486-06, STUB8779, M.P. 0.0006; SRCRTE L-172A, M.P. 32.0472; 7062486 RETIRE MAYFAIR 1-2 GAS WELL
|  |  | 0.01 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | TIE IN 12" N/O VALVE #3 TWEDT STATION; 70383302-02 M.P. 0.01
|  |  |  | 0.01 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | TWEDT STATION TIE-ON OF VA;VE #3; 172C DREG MP0.01; 7038330-02
|  |  | 0.25 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 12" TIE-IN S/O MLV# 9.68 ROADWAY YARD; 172C M.P. 0.25; 7038330-02
|  | 172 | 5.4066 | [8 empty] | 2002-11-01 | [5 empty] | WILLOWS | SO# 6091983; ROUTE 172A; M.P. 5.4066 #12; INSTALLED W. RES ON PIPE FOR E.T.S. BY SODT DIG METHOD; INSTALLED E.T.S.
|  | 172 | 7.5662 | 18 | [7 empty] | 2002-11-01 | [5 empty] | COLUSA | SO# 6091983; ROUTE 172A; M.P. 7.5662 #11; INSTALLED RES ON PIPE BY SOFT DIG METHOD; INSTALLED WIRES FOR E.T.S.
|  | 172A | 7.7209 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM# 30609902; L172A, M.P. 7.7209; BLIND FLANGE INSTALLED; INSTALLED 4" BLIND FLANGE ON V-133
|  | 172 | 8.7407 | 18 | [7 empty] | 2002-11-02 | [5 empty] | COLUSA | SO#6091983; ROUTE 172A M.P. 8.7407 #10; INSTALLED WIRES FOR E.T.S. USING DOFT PIG METHOD; INSTALLED WIRE ON PIPE
|  | 172 | 11.3209 | 18 | [7 empty] | 2002-11-05 | [5 empty] | WILLOWS | SO#6091983; ROUTE 172A; M.P. 11.3209 #6; INSTALLED WIRES ON PIPE FOR E.T.S USING SOFT DIG METHOD; INSTALLED WIRES FOR E.T.S.
|  | 172 | 12.4723 | 18 | [7 empty] | 2002-11-03 | [5 empty] | COLUSA | SO# 6091983, ROUTE 172A M.P.12.4723 #9; INSTALLED WIRES ON PIPE FOR E.T.S. USING SOFT DIG METHOD; INSTALLED WIRES ON PIPE FOR E.T.S
|  | 172 | 14.8572 | 18 | [7 empty] | 2002-11-04 | [5 empty] | COLUSA | SO#6091983; ROUTE 172A M.P. 14.8572 #8; INSTALLED WIRES ON PIPE FOR E.T.S. USING SOFT DIG METHOD; INSTALLED WIRES FOR E.T.S.
|  | 172 | 16.6887 | 18 | [7 empty] | 2002-11-05 | [5 empty] | COLUSA | SO# 6091983; ROUTE 172A M.P. 16.6887 #7; INSTALLED WIRES ON PIPE FOR E.T.S. USING SOFT DIG METHOD; INSTALLED WIRES FOR E.T.S.
|  |  | 22.3391 | [14 empty] | WILLIAMS | SO# 6091983; ROUTE 172A M.P. 22.3391 #21
|  |  | 24.3504 | [14 empty] | WILLIAMS | SO#6091983 ROUTE 172A M.P. 24.3504 #22
|  |  | 25.3073 | [14 empty] | WILLIAMS | SO# 6091983 ROUTE 172A, M.P. 25.3073
[16 empty] | Steel/Wrought Iron |  |  | DIV: MERIDIAN SO# 7048568-05; TAP VALVE LOCATION SRC RTE 172A, SAC MP. 26.7112; STUB8282, M.P. 0.0004; SEE AS BUILT NOTES
|  | 172 | 26.8864 | 18 | [14 empty] | SO# 6091983 ROUTE 172A M.P. 26.8864 #17; PLACED WIRES ON PIPE FOR E.T.S. USING SOFT DIG METHOD; INSTALLED WIRES FOR E.T.S. USING SOFT DIG
|  | 172 | 28.6328 | 18 | [7 empty] | 2002-11-06 | [5 empty] | ARBUCKLE | SO# 6091983; ROUTE 172A; M.P. 28.6328 #5; INSTALLED WIRES FOR E.T.S USING SOFT DIG METHOD; INSTALLED WIRES FOR E.T.S
| 02-17201-1 | 172A | 29.26 | 18 | Transmission |  | Unknown |  |  | Unknown |  | 2002-05-29 | [5 empty] | ARBUCKLE | L-172, M.P. 29.26; POSTED GSAVE; LEAK LOCATED IN TOMATOE FIELD- AREA WAS BARRICADED OFF; REPAIR # 8053217; CRACK 3:00 W/S PIPE LONGITUDINAL; PIPE APPEARS TO BE ERW PIPE NOT DSAW
|  | 172 | 30.8914 | 18 | [7 empty] | 2002-11-06 | [5 empty] | ARBUCKLE | ISNTALLED WIRES ON PIPE FOR E.T.S. USING SOFT DIG METHOD; INSTALLED WIRES FOR E.T.S.
|  |  | 33.4259 | 18 | [7 empty] | 2002-11-06 | [5 empty] | COLLEGE CITY | SO# 6091983 ROUTE 172A M.P. 33.4259; INSTALLED WIRES FOR E.T.S. USING SOFT DIG METHOD; INSTALLED WIRES FOR E.T.S.
|  | 172 | 34.198 | 18 | [7 empty] | 2002-11-07 | [5 empty] | COLLEGE CITY | SO# 6091983 ROUTE 172A M.P. 34.198; INSTALLED WIRES FOR E.T.S. USING SOFT DIG METHOD; INSTALLED WIRES FOR E.T.S.
|  | 172 | 35.57 | 20 | Transmission |  |  |  | N/A |  | N/A | [7 empty] | A-FORM DATA FOR EXPOSED PIPE; PM# 30318088 RT = 172A M.P. 35.5547 (GAS MAP); JOB PM 30318088; INSTALLED SERVICE TAP FOR CONTAD FOREST PRODUCTS LOCATED AT 7085 EDDY ROAD (SIERRA DIVISION CUSTOMER)
|  | 172 | 35.57 | 20 | Transmission |  |  |  | N/A |  | N/A | [7 empty] | A- FORM DATA FOR EXPOSED PIPE; PM# 30318088 RT = 172A, M.P. 35.5606(GAS MAP); JOB PM 30318088 INSTALLED SERVICE TAP FOR CONTAD FOREST PRODUCTS LOCATED AT 7085 EDDY ROAD ( SIERRA DIVISION CUSTOMERS)
|  | 172 | 35.5965 | 18 | [7 empty] | 2002-11-07 | [5 empty] | COLLEGE CITY | SO# 6091983 ROUTE 172A, M.P. 35.5965; INSTALLED WIRES FOR E.T.S USING SOFT DIG METHOD
|  | 172 | 40.07 | 20 | [11 empty] | Steel/Wrought Iron |  |  | SACRAMENTO DIV; SO#7046013-05 L-172A MP 40.07 HERSHEY STA.; L172-HERSHEY LAUNCHER TIE-IN 7046013
[13 empty] | 2004-06-03 |  |  | Steel/Wrought Iron |  | DUNNIGAN | INSTALL 101" OF 20" W.8" BALL VALVE FOR KICKER GAS L-172A; SACRAMENTO DIV; SO#7046013-05, M.P. 40.07 HERSHEY L-172A 7046013; HERSHEY KICKER GAS JOB 7046013
|  | 172 | 41.68 & 41.69 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SACRAMENTO, SO 7046013-05, M.P. 41.68+MP 41.69 L-172A DUNNIGAN; L172 REPALCE VALVES- RD 5-DUNNIGAN 7046013
|  | 172A | 43.4 | [14 empty] | ARBUCKLE | SO#6091983 ROUTE 172A M.P.43.40 #20
|  | 172 | 45.77 | 18 | [14 empty] | SO #6091983 ROUTE 172A M.P. 45.77 #19; INSTALLED WIRES FOR E.T.S. USING SOFT DIG METHOD; ISNTALLED WIRES FOR E.T.S.
|  | 172A | 47.07 | 18 | [14 empty] | SO #6091983 ROUTE 172A M.P. 47.07; INSTALLED WIRES ON PIPE FOR E.T.S. USING SOFT DIG METHOD; ISNTALLED WIRES FOR E.T.S.
|  | 172A | 49.25 & 49.26 | [12 empty] | Steel/Wrought Iron |  |  | SACRAMENTO DIV, 7046018-05, M.P. 49.25 & 49.26 L-172A; ZAMORA VALVE REPLACEMENT INSTALLED NEW VALVES
|  | 172A | 52.17 | [14 empty] | WILLIAMS | SO# 6091983 ROUTE 172A M.P. 52.17 #15
|  | 172A | 55.38 & 55.39 | [12 empty] | Steel/Wrought Iron |  |  | SACRAMENTO DIV, SO# 7046013-05, M.P. 55.38 & 55.34 L-172A YOLO TAP; INSTALLED NEW VALVES - YOLO TAP
|  | 172a | 61.9 | [12 empty] | Steel/Wrought Iron |  |  | SACRAMENTO DIV., 7046013-05, M.P. 61.90 L-172A; #7046013 FORM HAM AVE & HUSTON CIRC. WOODLAND
|  | 172 | 61.96 | [12 empty] | Steel/Wrought Iron |  |  | SACRAMENT DIV; 7046013-05, M.P. 61.96 L-172A; # 7046013; S/S. E. GIBSON RD. 426" W/O RD 102 WOODLAND
|  | 172a | 62.6757 | [12 empty] | Steel/Wrought Iron |  |  | ROUTE 172A M.P. 62.6757, SACRAMENTO DIV., WOODLAND- NORTH LOWERIN... JOB #7047528 M.P. 62.68 2200' N/O RD. 25
|  | 172a | 63.4186 | [12 empty] | Steel/Wrought Iron |  |  | ROUTE 172A M.P. 63.4136 (SACRAMENTO DIV) WOODLAND LOWERING SOUTH DOG LEGS; JOB# 7047528 M.P. 63.47 1640' S/O RD. 25
|  | 172a | 64.26 & 64.26 | [12 empty] | Steel/Wrought Iron |  |  | SACRAMENTO DIV., SO#7046013-05 CONWAY STATION 7046013 M.P. 64.26, M.P. 64.26, M.P. 64.27, L-172A
|  | 172A | 65.30 & 65.31 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SACRAMENTO DIV.. SO 7046013-05; RD .27-REMOVE VALVE L-172A MP65.30, M.P. 65.31; L172 REMOVE VALVE RD .27., 7046013
|  | 172A | 67.48 | 20 | Transmission | [6 empty] | 2006-09-06 | 2006-09-07 | Other | BUFF GOUGES W/ 60 ERT WHEEL | Steel/Wrought Iron |  | DAVIS | SO# 8079899;; ROUTE 172A M.P. 67.50 ORIGINAL A1 FORM MISSING; (5) SLIGHT GOUGES CAUSED BY CONTRACTOR BACK HOE .013" MAX DEPTH BUFF OUT GOUGES RECAP
|  | 172 | 68.62 | 18 | [13 empty] | DAVIS | SO#6091983 ROUTE 172A M.P. 68.62; INSTALLED WIRES ON PIPE FOR E.T.S USING SOFT DIG; INSTALLED WIRES FOR E.T.S.
|  | 172A | 69.79 & 69.80 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SACRAMENTO DIV., SO 7046013-05; SWINGLE STA. L-172A; LINE 172 RECIEVER TIE-IN 7046013
| 01-35018-1 | 172 | 70.1797 | 18 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2001-10-18 | 2001-10-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | DAVIS | RT= 172A M.P. 70.1797; NORTH SIDE OF DIRT RD; WELD SLEEVE OVER 1 LEAK & 2 SAV-A-VALVE OV.; 1 SLEEVE & 2 SAV-A-VALVE OVER SERIES
| 01-35018- | 172 | 70.18 | 18 | Transmission | [6 empty] | 2001-10-18 | 2001-10-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | DAVIS | LINE #116 & LINE #119 UPRATE 1 OF 4 SURVEY (2ND STOP); L-172 FM.P. 70.18; WELD 1-18" O.D. X 18" LONG SLEEVE OVER 1 LEAK EXT OVER. WELD 2" SAV-A-VALVE OVER 2 OTHER LEAKS; 1 SLEEVE & 2EA 2" SAVE A VALVE OVER SERIES
| 01-35018- | 172 | 70.18 | 18 | Transmission | [6 empty] | 2001-10-18 | 2001-10-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | DAVIS | LINE #116 & #117 UPRATE SURVEY (2ND STOP) L-172A M.P. 70.18 2 OF 4; 7038330-02; WELD 1-18" O.D. X 18" LONG SLEEVE OVER 1 LEAK EXT. CORR. WELD= -2" SAVE A VALVE OVER 2 ...LEAK; 1 SLEEVE & 2 SAVE A VALVE OVER SERIES
|  | 172A | 70.18 | 18 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 1 SLEEVE PLUS 2EA 2" SAVE A VALVE OVER SERIES OF PITS
|  | 172 | 70.18 |  | Transmission |  | Body of Pipe |  |  | External Corrosion |  |  | 2001-10-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  |  | L-172A M.P. 70.18 4 OF 4; 7038330-02; WELDED 1-18" O.D. 18" LONG SLEEVE OVER 1 LEAKING EXT CORR PIT., 2 SAVE VALVES OVER 2 OTHERS
| 01-35018- | [16 empty] | DAVIS | LINE #116 &119 UPRATE SURVEY (2ND STOP); NORTH SIDE OF DIRT ROAD
|  | 172A | 76.8 | 16 | Transmission | [7 empty] | 2009-05-15 | Grinding - Other |  | Steel/Wrought Iron |  |  | EVERGREEN AVE WEST SACRAMENTO; CONTRACTOR NICKED 16" GAS TRANSMISSION MAIN I FOUR LOCATIONS WITHIN A LENDTH OF 12". THREE AT .030 DEPTH AND ONE AT .090 WALL THICKNESS WAS MEASURED AT .281 ALL DEFECTS REMOVED WITH SANDING DISK. REPAIR LOCATION IS ON EVERGREEN AVE. WEST SACRAMENTO
|  |  | 0.0002 | 8 | Transmission | [13 empty] | ROUTE: 173-15, MP. 0.0002, PM#30633341, 05/15/09 ...; 54' TO TOP OF PCA, 59" TO TOP OF PIPE.
|  |  | 0.0002 | 8 | Transmission | [13 empty] | ROUT: 173-15, M.P. 0.0002, PM# 30633341, 5/15/09
|  | 137-1 | 0.0727 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SIERRA DIV, L-173-1, M.P. 0.0727, SO# 7051967-05
|  | 173 | 0.56 | 8.625 | Transmission |  |  |  |  | Digin |  | 2000-12-15 | 2000-12-16 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | ROSEVILLE | INSTALLED REPAIR WELDING SLEEVES 8 3/4" ID X 3/8" WT, SMYS 50,000 PSI
|  |  | 3.0976 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#7055735, ROUTE L-173, M.P. 3.0976
|  |  | 3.2171 | 8.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7055735, ROUTE L-173, M.P. 3.2171
|  |  | 4.809 | 8.5 | [11 empty] | Steel/Wrought Iron |  |  | SO# 7055735, ROUTE L-173, M.P. 4.8090
|  | 173 | 5.5001 | 8.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIVE SIERRA, L-173, M.P. 5.5001, SO#7054566-05 (NORTH TIE-IN FOR 12" DFM 1519-04)
|  | 173 | 5.5032 | [15 empty] | ROUTE 173, M.P. 5.5032, M.P. 5.5133; LINE 173, M.P. 5.5032 & 5.5133, JOB# 30604316
|  | 173 | 5.5032 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE 173, M.P. 5.5032 & 5.5133, JOB # 30604316; EXPOSED 8" LINE 173 FOR THE PURPOSE OF BYPASS
|  |  | 10.8376 | 6.375 | Transmission | [13 empty] | SO# 7046907, RT = 173, M.P. 10.8376
|  | 173 | 11.45 | [12 empty] | Steel/Wrought Iron |  | NEW CASTLE | L173, M.P. 11.53
|  | 173 | 15.2572 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | OPHIR | DIVISION: SIERRA, SO# 7060911-07, L-173, M.P. 15.2572 (FOR DREG5022, M.P 5.2574 R230)
|  | 173 | 16.03 | [12 empty] | Steel/Wrought Iron |  | NEWCASTLE | L-173, M.P. 16.03
|  | 173 | 16.58 | 6.625 | Transmission | [13 empty] | SO# 7048206, RT= 173-5, M.P. 16.58; SEE ATTACHED
|  | 173 | 9.7881 | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L173, M.P.9.7881, JOB# 7044649
| 01-00152-1 | 173 |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2001-06-27 | 2001-06-27 | Other |  | Steel/Wrought Iron |  | PENRYN | EXTENDED GREASE PLUG, GREASED VALVE & INS.
|  |  | 13.23 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LOC #3 RT ATUB 10694, (~173) M.P. 13.23; CUT OFF EXSISTING PIPE VALVE AND CAPPED INSTALLED NEW PIN-OFF AND FIRE VALVE. ALSO, 3/4" PIPE BACK TO HPR V-R224
|  |  | 13.2339 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | #41132104, OLD FILE, LOC# 3 RT 173, M.P. 13-2399; EXPOSED PIPE TO INSTALL NEW FIRE VALVE 20FT. FROM HPR
|  | 173 | 13.3016 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | NEWCASTLE | #41132104. LOC #1. RT: 173, M.P. 13.3016; INSTALLED 1" PIN-OFF TEE, 24' OF 3/4" STEEL PIPE AND NEW FIRE VALVE REMOVED 3/4" FIRE VALVE
|  |  | 15.6676 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | #41132104. NEW PIPE. LOC#...RT:173, M.P. 17.6676; MOVED HPR 20 + FT. AWAY FROM FIRE VALVE, PER NEW REGULATION UP TH HILL.
|  |  | 15.66 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | #41132104. OLD PIPE, LOC#2, RT DREG5023, M.P. 000, (173), M.P. 15.66; DUG UP L-173 ON WISE RD. AT V-231. EXPOSED LINE TO UTILIZE PIN-OFF TEE AFTER VALVE BROK REPLACED FIRE VALVE.
|  | 174 | [13 empty] | Steel/Wrought Iron |  |  | L-174-4-7. SO# 7040927-02
|  | 174 | [13 empty] | Steel/Wrought Iron |  |  | L-147-4-3. SO#7040927-02
|  | 174 | [16 empty] | 7043096-02, L174GG
|  | 174 | [16 empty] | INSPECTION ON 4" REACTIVATED 5 VALVES.
| 03-17401-1 | 174 | [9 empty] | 2003-05-16 | 2003-06-04 | Other | REPLACED NEW | Steel/Wrought Iron |  | GRIMES | PIPE CAN AT V-1L GOOD C-13 CUT. TO VALVE FACE- REPLACE 80'; REPLACE 10" W.90' .365 GR.B ...
|  | 176 | 0.08 | 10 | Distribution Main | [10 empty] | Steel/Wrought Iron |  | HOLT | L-176, M.P. 0.08; SHOWN AS 8" G-SAVE PMN.
|  | 176 | 14.7 | 8 | [11 empty] | Steel/Wrought Iron |  | TRACY | 176, M.P. 14.70; EXPOSED ON STAND BY (TEICHER & CON.); 3112 C-1
|  | 176 | 15.24 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 176, M.P. 15.24; SEE ATT'D PLAT
|  | 176 | 16.39 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-176. M.P.16.34
|  | 176 | 16.5 | 6 | Transmission | [12 empty] | MOUNTAIN HOUSE | ROUTE 176, M.P. 16.50
|  | 176 | 16.63 | 6 | Transmission | [12 empty] | MOUNTAIN HOUSE | ROUTE 176, M.P. 16.63
|  | 176 | 16.85 | 6 | Transmission | [12 empty] | MOUNTAIN HOUSE | ROUTE 176, M.P. 16.85
|  | 176 | 16.8798 | 6 | Transmission | [7 empty] | 2005-10-15 |  |  | Steel/Wrought Iron |  |  | L-176, M.P. 16.8798; L176 MP 16.8798, JOB 7053165; G.C. GAS TIE IN FOR L-176 USED TDW/PCF FOR TIE; ALL PIPE HAD AN 8HR. HYDRO TEST. TIE IN PIECES WERE BUILT & INSTALLED BY G.C. GAS, STOCKTON.
|  |  | 17.34 | 6 | Transmission | [12 empty] | MOUNTAIN HOUSE | ROUTE 176, M.P. 17.34
|  | 176 | 17.4 | 6 | Transmission | [12 empty] | MOUNTAIN HOUSE | ROUTE 176, M.P. 17.40
|  | 176 | 17.54 | 6 | Transmission | [12 empty] | MOUNTAIN HOUSE | ROUTE 176 M.P. 17.54
|  | 176 | 17.55 | 6 | Transmission | [12 empty] | MOUNTAIN HOUSE | ROUTE 176, M.P. 17.55
|  | 176 | 17.71 | 6 | Transmission | [12 empty] | MOUNTAIN HOUSE | ROUTE 176 MP 17.71
|  | 176 | 17.81 | 6 | Transmission | [12 empty] | MOUNTAIN HOUSE | ROUTE 176, M.P. 17.81
|  | 176 | 17.85 | 6 | [11 empty] | Steel-Other |  |  | L-176, M.P. 17.85. SO #7031307-00; LOC: L-176, M.P. 17.85 GSAVE 17.98
|  | 176 | 17.89 | 6 | Transmission | [12 empty] | MOUNTAIN HOUSE | ROUTE 176, M.P. 17.89
|  | 176 | 17.97 | 6 | Transmission | [12 empty] | MOUONTAIN HOUSE | ROUTE 176, M.P. 17.97
|  |  |  | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | OTTMAN. # 41137106. RT 177A, M.P. 38.8990; FOUND BARE SPOT ON PIPE WITH A PIT MEASURED AT .008, CLEANED & WRAPPED AS PER G. CAEKAZIS
|  |  | 39.5768 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | FLORES AVE. #411321206. RT 177A, M.P 39.5768; WHILE REMOVING WRAPP TO INST. NEW VALVE TEE & FIRE VALVE FOR REG 122, FOUND UGLY REPAIR, AT TIME OF THIS INSPECTION STILL UNDER ADVISEMENT OF GEORG KAZKAZIS
|  | 177 | 24.12 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 7030805-00, 177S, M.P. 1.24; NO MP# ON PRINT; RETIRE 36-1 CORNING GAS WELL
|  | 177 | [16 empty] | SO# 7042448-02, L177
|  | 177A |  | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron | ; | GERBER | L-177A, PM# 7062610, 36.51L INSTALLED 12" L.S. FITTING
|  | 177A |  | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | GERBER | L-177A. PM#7062610; TIE-INPOINT
|  | 177A | 36.64 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 177A, M.P. 36.64, SO#7054314-05
|  | 177 | [13 empty] | Steel/Wrought Iron |  |  | 8" TIE-IN #7051326 GERBER COMPR. STA. L-177; TUBE #2 TIE-IN 8"
|  | 177 | [13 empty] | Steel/Wrought Iron |  |  | 12" TIE-IN #7051326 GERBER COMPR. STA. L-177; 12" VAULT TIE-IN
|  | 177 | [13 empty] | Steel/Wrought Iron |  |  | 6" TIE-IN #7051326 GERBER COMPR. STA. L-177; TUBE#2 TIE-IN 6"
|  | 177A | 44.97 | 2.375 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-177A, M.P. 44.97 PM# 30610529 RT - STUB9301, MP-0; SAVE-A- VALVE; WILDER RD.
|  | 177 | 44.98 | [12 empty] | Steel/Wrought Iron |  |  | L-177, M.P 44.95, SO#6056971
|  | 177A | 85.66 | 12.75 | Transmission | [13 empty] | L-177A, M.P. 85.6155; DIG TO INSPECT CASING- CASING IS CORRUGATED NESTABLE- END SEAL IS COMPROMISED
|  | 177A | 85.66 | 12 | [13 empty] | PLATINA | NORTH VALVE/ NORTH DIV. ROUTHE = L-177A., M.P. 85.6604; NO LEAK. INSTALLED E.T.S.
|  | 177A | 86.76 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM# 30659072, RT = 177A, M.P. 86.76; SOAP TESTED WELDS @ LINE PR.; @V88.77
|  | 177 | 86.78 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7027826-00, L-177; M.P. 86.78
|  |  | 86.85 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM# 30659072, RT = 177A, M.P. 86.85; SOAP TESTED WELDS @ LINE PRESSURE; L177 @ M.P. 86.84
|  | 177 | 12.5 | [12 empty] | Steel/Wrought Iron |  | MADD RIVER | JOB #7063025; 177A 124.8608, JOB 7063025; L-177 MP 125. 17 MI W/O HAYFORK TRINITY CO. (MADD RIVER) JOB #7063025; A-GPS TIE-IN LOC WEST SIDE 40 27 17.571"N, 123 29 14.601" W; B- GPS TIE IN LOC EAST SIDE 40 27 17.045"N 123 29 12.132"W
| 06-30029-1 | 177 | 124 | 12 | Transmission |  | Body of Pipe |  |  | Construction Defect |  | 2006-08-19 | 2006-08-19 | Other |  | Steel/Wrought Iron |  | MAD RIVER | 177A,...; L177 M.P. 124.9 JOB 8079616; SHUT DOWN LINE (REPLACED 16' 12" ON 08/2; SOAP @ VISUAL G.C. AREA 7 WELDED PIPE.
|  | 177 | 168.8601 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | ALTON | 12" LINE 177, M.P. 168.8601. ALTON, CA.; L177 M.P. 168.8601, JOB 7048668
|  |  | 170.45 | [12 empty] | Steel/Wrought Iron |  |  | SO# 7045274-03, RT 177A, M.P. 170.45
| 01-50044-1 | 177 | 173.89 | 12 | Transmission |  | Valves |  |  | Other |  | 2001-07-09 | 2001-07-23 | Other |  | Steel/Wrought Iron |  | FORUNA | RT 177A, M.P 173.89; GREASED VALVE
|  | 177 | 182.9382 | 12 | Transmission | [6 empty] | 2005-09-27 |  |  |  | Steel/Wrought Iron |  | EUREKA | 12" LINE 177 EUREKA ERCOH REPAIR; 177 M.P. 182.9382 JOB 7048668
|  | 177A | 192.23 | [12 empty] | Steel/Wrought Iron |  |  | ;-177A ~MP. 192.23; INSTALLED I-G5 BOX ON LINES L137 4" STL & L137 A 8" STL ON E.T.S. PHASE III JOB#6041269
|  | 182 | 1.0751 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | #7061267, ROUTE 182, M.P. 1.0751; #7061267 L-182
|  |  | 1.88 | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | 4/3/05 #30606773. RT = 182B, M.P. 1.88; PINNED OF 2" SPIN-OFF TEE, CUT & INSTALLED 2: SOCKET WELD CAP. REMOVED 3" VALVE @ MAIN. PIGGED LINE, REMOVED RISER, METER SHED & LINE MARKERS.; LOCATION IS APX.14 MILES S/SW OF HWY 12 LOCATED IN GRIZZLY ISLAND RD. LEFT HAND SIDE OF ROAD ACROSS FROM STATE EQUIPMENT YARD & WELL LOCATION.
|  |  | 1.8842 | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB 7047307, ROUTE 182B, M.P 1.8842
|  | 182 | 3.2307 | 10 | Gathering | [7 empty] | 2002-10-16 | Other | REPAIR WRAP |  |  | SUISUN | RT = 182B, M.P. 3.2307; 40' OF L-182 RE-COATED WITH POWERCRETE "I"; GPS FILE #R100918A
|  |  | 4.2646 | [12 empty] | Steel/Wrought Iron |  |  | #7059085 ROUTE 182B, M.P. 4.2646
|  |  | 4.73 | 6.25 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | RT 182B, M.P. 4.73, SO# 6088103; CANAL X-ING
|  |  | 12.4 | 10.75 | Transmission | [7 empty] | 2008-08-20 |  |  | Steel/Wrought Iron |  | SUISUN CITY | RT= 182, M.P. = 12.40; NO LEAK; NO LEAK SPAN INSPECTION. THE SPAN WAS SANDBLASTED PITTING MEASURED AND A RSTRENG COMPLETED (SEE ATTACHED SHEET). THE SPAN WAS RECOATED WITH PROTAL 7200 AND 2 COATS OF ENAMEL PAINT
|  |  | 12.41 | 10.75 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | SO# 6088103, RT 182, M.P. 12.41
| 07-95047 | 186 |  | 4 | Transmission |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2007-11-21 | 2007-12-11 | Deactivate #TP Main |  | Steel/Wrought Iron |  | DOS PALOS | 275' OF NEW 4" STL BORED IN UNDER FARMERS WATER DITCH
|  |  | 6.66 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | DOS PALOS | SO# 7045867-03, RT 186, M.P. 6.660; VALVE 6.66
| 04-75024-1 | 186 | 19.31 | 6 | Transmission |  | Physical/Mechanical Joint |  | FLANGE GASKETS | Other | GRASS FIRE | 2004-09-06 | 2004-09-06 | Replace TP Main |  | Steel/Wrought Iron |  | DOS PALOS | SO# 7053345-04, RT = 186, M.P. 19.303, 7 OF 22; REPLACED MLVALVE 19.31 AND BLOW OFFS WITH 6" STEEL PIPE
|  | 187 | 8.11 | [8 empty] | 2008-04-29 | [5 empty] | SAN ARDO | L-187, MP 8.11
|  | 187 | 14.25 | 6 | Transmission | [6 empty] | 2008-04-28 |  |  |  | Steel/Wrought Iron |  | KING CITY | L-187, M.P. 14.25
| 97-40006-1 | 187 | 20.85 | 6.62 | Transmission |  | Body of Pipe |  |  | Digin |  | 1997-06-13 | 1997-06-14 | Replace Pipe |  | Steel/Wrought Iron |  | KING CITY | REPLACED 28' SECTION OF TRANSMISSION MAIN
|  | 187 | 22.57 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | KNG CITY | EXPOSED L-187, M.P. 22...;
|  | 187 | 45.31 | 8 | Transmission | [7 empty] | 2002-12-09 |  |  | Steel/Wrought Iron |  |  | SO#8051456, ROUTE 187,MP. 45.0560; WE WERE CHECKING THE COATING FOR POSSIBLE FAILURE; TAR COATING WAS GOOD- WE DID FMD SOME WATER UNDER. THE TAR COATING AT A FIELD WLED. PIPE LOOKS GOOD. WE RECOATED THE EXPOSED AREA WITH TRENTON WAX TAP. SOIL WAS SANDY WE ALSO ATTACHED LOCATING WIRES "E.T.S. STEVE JAMESON 12-9-02
|  | 187 | 50.67 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  | GONZALES | NO LEAK/INSPECTION ; DIV: CENTRAL COAST. L-187, M.P. 50.5316. SO# 7058725-06; REMOVED CASING PIPE. DID NOT WORK ON CARRIER PIPE; L-187, M.P. 50.67
|  | 187 | 56.1734 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIV: CENTRAL COAST. SO 7059765-06, L187, M.P. 56.1734
|  | 187 | 56.57 | 8 | Transmission | [7 empty] | 2002-12-10 |  |  | Steel/Wrought Iron |  |  | SO# 8051456, ROUTE 187, M.P. 56.5038; WE WERE CHECKING COATING FOR POSSIBLE FAILURE; ORIGINAL COATIG GOOD, PIPE LOOKS LIKE NEW. NO CORROSION, NO WATER UNDER COATING. WE RECOATED WITH TRENTON WAX TAPE AND BACK FILLED WITH SAND. WE ALSO ATTACHED TEST LEAKS. S. JAMESON 12-10-02
| 98-00059 | 187 | 58.48 | 8 | Transmission |  | Body of Pipe |  |  | Digin |  | 1998-09-05 | 1998-09-06 |  |  | Steel/Wrought Iron |  | CHUALAN | REPLACE 80FT OF 8" MAIN;
|  | 187 | 59.1 | 8 | Transmission | [6 empty] | 2005-06-10 | 2005-06-15 | Other | GRINDING AQUA- WRAP (FIBER-REINFORCED POLYMER COMPOSITE SYSTEM) | Steel/Wrought Iron |  | SALINAS | NON-LEAK DIG IN. L-187, M.P. 59.0990. DAMAGE ONLY; INSTALL 4 FT. OF AQUA-WRAP, GRIND OUT ~3 SMALLER SCRATCHES (<10% OF WT); MECHANICAL REPAIRS MADE DUE TO SCRATCHED PIPE, NO WELDING, NO FITTINGS WERE USED
| 01-50110-1 | 187 | 61.2 | 8 | Transmission |  | Body of Pipe |  |  | Digin |  | 2001-08-31 | 2001-08-31 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | OH H.P. GAS LINE
| 01-00110-1 | 187 | 61.45 | 8 | Transmission |  |  |  |  | Digin |  | 2001-08-31 | 2001-08-31 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | WHILE REPAIRING DIGIN @ MP 61.35, G.C. GAS DAMAGED PIPE # MP 61.25
|  | 187 | 61.1231 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-187, M.P. 61.1231;; LINE 187 STA 7+95; M.P. 61.1231; LATIT 36.614585150, LONG -121.570433258; ; MISC. COMMENTS/INFORMATION: SMALL PLANT ROOTS PRESENT, MINOR CALCEREOUS DEPOSITS & SURFACE RUST ON PIPE. FOUND AVERAGE PIPE WALL THICKNESS TO BE 0.192". MINOR SCRATCHES FOUND DURING MAG. PARTICLE TESTING, NO INDICATIONS FOUND. NO COUPON, CAD WELDS OR WET REFERENCE CELL INSTALLED PER MIKE WEST BECAUSE FARMLAND. PIPE RECOATED WITH PROTAL 7200 & WAX TAPED TRANSITIONS INTO OLD COATING.
| 01-00109-1 | 187 | 61.35 | 8 | Transmission |  | Body of Pipe |  |  | Digin |  | 2001-08-30 | 2001-08-31 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | INSTALLED 3 FT. OF 8" GRB SEAMLESS .322 W.T.
| 01-50109-1 | 187 | 61.35 | 8 | Transmission |  | Body of Pipe |  |  | Digin |  | 2001-08-30 | 2001-08-30 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | L-187, M.P. 61.50; INSTALLED 3' OF 8" GRB SEAMLESS .322"
| 09-50072-1 | 187 | 62 | 8 | Transmission |  | Body of Pipe |  |  |  |  | 2009-04-03 | 2009-04-04 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | DO. RT = 187, M.P. 62.00; SHUT VALVES AT 2 LOCATIONS- CUT-OUT DAMAGED PIPE.; TEST QUALIFIES FOR 2105- INSPECTED BY TCI INSPECTIONS -CLARK 21' OF PIPE I
|  |  | 62.2186 | [12 empty] | Steel/Wrought Iron |  |  | RT = 187, M.P. 62.2186, PM# 30704063; PGE LINE 187 MP. 62-8" PIPELINE REPLACEMENT PROJECT. L-187 RELOCATION @ APPROX MP. 62.25 SALINAS , CA.
|  | 187 | 62.31 | [15 empty] | ROUTE 187, LOCATION 62.3100; CASING SHORTED TO PIPE. SOUTH END OF CASING LOCATED 123' NORTH OF CENTERLINE OF RR SPUR. CASING VENT & TEST LEADS INSTALLED AND EXTENDED TO ELECTRIC POLE. MARKER BALL INSTALLED OVER CASING END. DREW KELLY
|  | 187 | 63.57 | 8 | Transmission | [7 empty] | 2003-12-13 | Other | GRINDING PER 54134 | Steel/Wrought Iron |  |  | SO# 8051456, ROUTE 187, MP. 63.1974; CHECKING COATING FOR POSSIBLE FAILURE. GAUGE FOUND, REPAIRED BY GRINDING; L-187 @MP 63.57 3-12-03. TAR COATING WAS IN GOOD SHAPE, OTHER THAN SPOTS WITH MECHANICAL DAMAGE NO WATER UNDER COATING PIPE LOOKS GOOD. 2 LIGHT GOUGES WORST ONE WAS 4 1/2" LONG, 3/8" WIDE .001" DDEP. THE MECHANICAL DAMAGE CAUSED DAMAGE TAR COATING TO DEBOND AND ALLOW PITTING TO OCCUR. REPAIRED BY GRINDING. WE ALSO ATTACHED 3 BLACK WIRES TO THE MAIN AND INSTALLED AN E.T.S. STATION.
|  | 191 | 0+24 | [12 empty] | Steel/Wrought Iron |  | ANTIOCH | REMOVED 24" OF WRAP AND REWRAPPED AND INSTALLED REINFORCE COMPOSITE E.T.S. STATION WITH WARNING STICKERS.
|  |  |  | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | INSTALL TEST LEADS ON LINE 191 APPROX M.P. .23 REMOVED 24" OF WRAP FOR INSPECTION OF L191 LIGHT SURGACE RUST NO PIPE DAMAGE
|  | 191 | 4.57 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | ANTIOCH | M.P. 4.57, L-191; INSTALLED E.T.S. LINE 191 ANTIOCH
|  | 191 | 4.54 | [15 empty] | L-191 EXPOSED TO INSTALL E.T.S. LEADS APP 75 WEST OF INTERLINE OF L TREAT ...FOR LEAD ...TO CANAL FENCE APP 85 WEST OF CENTER LINE OF L IT.
|  | 191 | 4.78 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | ANTIOCH | L-191, M.P. 4.78; INSTALLED E.T.S. LINE 191 ANTIOCH
|  | 191 | 4.78 | [15 empty] | RUSTED 6-20-01. L-191, M.P. 4.78; L-191 EXPOSED TO INSTALL E.T.S. LEADS NEXT TO 3RD POWER TOWER EST OF L STREET
|  |  | 5.2002 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT= 191, M.P. 5.2002; #15 ON MAP L-191, KINDER CARE PARKING LOT
|  |  | 5.2097 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT = 191 M.P. 5.2097; #14 ON MAP EMPTY LOT W/O KINDER CARE L~191
|  |  | 5.24 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-191, M.P. 5.30 .24; LINE 191 APPROX M.P. 5.3, INSTALL C.P. E.T.S.
|  | 191 | 5.24 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | ANTIOCH | L-191 MP 5.24; INSTALLED E.T.S. LINE 191 ANTIOCH
|  |  | 5.3728 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT = 191, M.P. 5.3725; #13 ON MAP IN FRONT OF RAMADA INN. L-191
|  | 191 | 5.4 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L191, M.P. 5.40, JOB 8075984 (WBS TO 2084); MEARS JOB # 8075984, IN FRONT OF RAMADA INN ANTIOCH. L-191 APPROX M.P. 5.40, INSPECT PIPE DUE TO CLOSE INTERNAL SURVEY. WBS P02084
|  | 191 | 5.4 | [15 empty] | L-191; M.P. 5.40; L-191 EXPOSED TO INSTALL E.T.S. LEADS NEXT TO 3RD POWER TOWER WEST OF L. STREET. L STREET ...ANTIOCH. MP 5.40...AT THE ANTIOCH & PITTSBURG BORDER, ...3/4 MILES AWAY.
|  |  | 5.4202 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT = 191 MP. 5.4202; #12 ON MAP BUGER KING PARKING LOT APPROX 30' FT. EAST OF MLV 5.42 L-191
|  | 191 | 5.48 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | PM# 30604241 ROUTE 191, M.P. 5.4548; PITTSBURG CONTRA COSTA COUNTY
|  | 191 | 5.47 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | PM# 30604241, ROUTE 191, M.P. 5.47; PITTSBURG CONTRA COSTA COUNTY
|  | 191 | 5.47 | 24 | Transmission | [13 empty] | APPROX M.P. 5.47 W/S OF SOMERSVILLE RD. ANTIOCH, CA. L-191
|  | 191 | 5.48 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | SO# 8037096-02, RT = 191, M.P. 5.47; LINE 191 SOMERSVILLE RD. PITTSBURG. BETWEEN V 5.43 * MP 5.48. ANOMALIE AT N=4207019.368M E= 602156.992M; HWY 4 ON RAMP NOTE: COORDINATE SYSTEM 4TM ZONE; 10 NORTH DATUML NAD 1983 (CONUS) METERS; 2' OF WRAP SEPARATED FORM PIPE. VERY LITTLE WATER BETWEEN WRAPED PIPE. NO RUST OR PITTING. WRAP 1/2" TO 3/4" THICK (TAR) REWRAPPED WITH STAC WRAP * PLASTIC PROTECTION TAPE.
|  | 191 | 5.48 | 24 | Transmission | [13 empty] | APPROX M.P 5.48 W/S OF SOMERSVILLE RD. ANTIOCH, CA L-191
|  | 191 | 5.48 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | SO# 8037096-02, RT = 191, M.P 5.48; LINE 119 SOMERVILLE RD., PITTSBURG BEWEEN V 5.43 & MP 5.48; ANOMALIE AT N= 4207013.056M E= 602145.572M; NOTE: COORDINATE SYSTEM UTM ZONE; 10 NORTH DATUM; NAD 1983 (CONUS) METERS; 5' OF WRAP REAL FLAKEY SEPARATING FROM PIPE WATER TRAPPED BETWEEN WRAP & PIPE. NO RUST OF PTTING WRAP 1/4" THICK (TAR). REWRAPP WITH STAC WRAP & PLASTIC PROTECTION TAPE KNOCKED OFF ALL WRAP & REWRAPPED ENTIRE PIPE.
|  | 191 | 5.48 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | LINE 119 SOMERSVILLE RD. PITTSBURG BETWEEN V 5.43 & M.P. 5.48.; ANOMALIE AT =4207010.572M, =602135.425M; NOTE CORRDINATE SYSTEM UTM ZONE 10 NORTH DATUM, NAD 1983 (CONUS) METERS; 15 OF WRAP SEPARATING FORM PIPE. NO RUST OR PITTING "WRAP 1/4" TO 3/8" THICK (TAR) REWRAPPED WITH STAC WRAP & PLASTIC PROTECTION TAPE. KNOCKED OFF ALL WRAP & REWRAPPED PIPE. PIPE COVER VARIES FROM 5' TO ....
|  | 191 | 5.49 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-191 M.P. 5....; APPROX M.P. 5.49 W/S OF SOMERSVILLE RD. ANTIOCH. L-191
|  | 191 | 5.48 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | SO# 8037096-02, RT = 191, M.P. 5.49; LINE 191 SOMERSVILLE RD. PITTSBURG BETWEEN V5.43 & MP 5.48; NOTE COORDINATE SYSTEM UTM ZONE, 10 NORTH DATUM, NAD 1983 (CONUS) METERS; PIPE IN GOOD SHAPE LITTLE RUST WRAP WAS HIT PRIOR; WRAP HAD BEEN KNOCKED OFF. REWRAPPED WITH STAC WRAP & PLASTIC PROTECTION TAPE. KNOCKED OFF ALL WRAP & REWRAPPED PIPE.
|  | 191 | 5.48 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | LINE 191 SOMERSVILLE RD. PITTSBURG, CA. BETWEEN V5.43 & MP. 5.48; NOTE: COORDINATE SYSTEM UTM ZONE 10NORTH DATUM, NAD 1983(CONUS) METERS; WRAP HAD 1" SPERARATIONON TOP FOR 18" WRAP IS SEPARATING FROM ITSELF. LITE RUST. REWRAPPED WITH STAC WRAP * PLASTIC PROTECTIVE TAPE. KNOWCKED OFF ALL WRAP & REWRAPPED PIPE
|  | 191 | 5.16 | [15 empty] | L-191 EXPOSED TO INSTALL E.T.S. LEADS APP 75 WEST OF ...OF L STREET ...FOR LEAD ...TO CANAL FENCE APP 85' WEST OF CENTERLINE OF L ST.
|  | 191 | 5.75 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT= 191 M.P. 5.75; NEW CIRCUIT CITY IN PITTSBURG JOB SITE. L-191 WAS NOT EXPOSED, DEPTH CHECKED BY PROBING, COVER OVER PIPE IN FUTURE WILL BE ASPHALT
|  | 191 | 5.59 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | PM# 30604241, ROUTE 191, M.P. 5.59; PITTSBURG CONTRA COSTA COUNTY
|  | 191 | 6.58 | 24 | Transmission | [10 empty] | Steel/Wrought Iron | ; | PITTSBURG | L-191, M.P. 6.58; LINE 191 INSTALLED E.T.S.
|  | 191 | 6.75 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | ROUTE = 191, M.P.6.7119, PM# 30603900; PITTSBURG CONTRA COSTA COUNTY
|  | 191 | 6.82 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE 191 APPROX M.P. 6.4 INSTALLED C.P. E.T.S.
|  | 191 | 6.82 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | L-191, M.P. 6.82; INSTALLED E.T.S. LINE 191
|  | 191 | 7.38 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | AFORM/ET...6-20-01; L191, MP 7.24; INSTALL C.P. E.T.S., M.P. 7.38 L-191; 7.38 PER...NUTT POINT IN MIDDLE OF CASING L-191 INSERTED INTO ...
|  | 191 | 7.24 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | L-191, M.P. 7.24; INSTALLED E.T.S. LINE 191
|  | 191 | 07.52 TO 07.45 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIST. LOS MEDANOS L-191 (CALIFORNIA AVE) M.P. 7.52 (DIANE AVE) TO M.P. 7.45 (CARION CT)
|  | 191 | 7.591 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | 191 M.P. 7.591, PM# 30603900; PITTSBURG, CONTRA COSTA COUNTY
|  | 191 | 7.5337 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | ROUTE 191, M.P. 7.5337, PN# 30603900; PITTSBURG CONTRA COSTA COUNTY
|  | 191 | 7.74 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | 191, M.P. 7.73, PM# 30603900
|  | 191 | 9.73 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-191 ROUTE 191-1, M.P 9.73; INSTALL C.P. E.T.S. N/S W. LELAND RD.; NO LINE #....
|  |  |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | THIS WORK IS FOR NEW AUTO ROW AT CENTRY BLVS PITTSBURG WINTER CHEVEROLET HONDA, M.P. APPROX 6.2
|  | 191 | 8.47 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | L-191, M.P. 8.47; INSTALLED E.T.S. LINE 191
|  | 191 | 8.46 | [15 empty] | LINE 191 EXPOSED TO INSTALL E.T.S. LEAK 30 FT. EAST OF RAILROAD AVE. ON CALIFORNIA ST. RISER FOR LEAK INSTALLED NEZT TO ...OF POWER TOWER ON EAST SIDE OF RAILROAD.
|  | 191 | 8.7041 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | SO# 7007103, ROUTE 191, M.P. 8.704; S.O. 7007103, PITTSBURG CONTRA COSTA COUNTY
|  | 191 | 9.1995 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | SO# 7007013, ROUTE 191, M.P. 9.1995; S.O. 7007103 PITTSBURG, CONTRA COSTA COUNTY
|  | 191 | 9.3228 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | SO# 7007103, ROUTE 191, M.P. 9.3228; S.O. 7007103, PITTSBURG CONTRA COSTA COUNTY
|  | 191 | 9.4767 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | SO# 7007103, ROUTE 191, M.P. 9.4767; SO. 7007103, PITTSBURG CONTRA COSTA COUNTY
|  | 191 | 9.5219 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | SO#7007103, ROUTE 191, M.P. 9.5219; S.O. 7007103, PITTSBURG CONTRA COSTA COUTNY
|  | 191 | 9.54 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-191 (191-1), M.P. 9.54; INSTALL C.P. E.T.S. 20" L-191 S/S HWY 4
|  | 191 | 9.54 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | L-191 M.P 9.54; INSTALLED E.T.S. LINE 191
|  | 191 | 9.6491 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | SO# 7049288, ROUTE 191-1, M.P. 9.6491; SO# 7049288, PITTSBURG CONTRA COSTA COUNTY
|  | 191 | 9.82 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L 191 MP 9.82; LINE 191 S/O N. PARKSIDE DR. PITTSBURG APPROX M.P. 9.4. INSTALL C.P. E.T.S.
|  | 191 | 9.82 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | L-191 M.P. 9.82; INSTALLED E.T.S. LINE 191
|  | 191 | 9.73 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | L-191 M.P. 9.73; INSTALLED E.T.S. LINE 191
|  | 191 | 27.18 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | LAFAYETTE | L-191, M.P. 27.18; REPAIR LINE 191 WHERE EBMUD INSTALL HOT TAP
|  | 191 | 9.5882 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  | PITTSBURG | SO# 70492088, ROUTE 191-1, M.P. 9.5862; SO. 7049288 PITTSBURG CONTRA COSTA COUNTY
|  |  |  | 24 | [11 empty] | Steel-Other
|  |  | 00.0088 & 00.0115 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | MARTINEZ | PM# 30631287 DF 3450, M.P 0.0088, M.P. 0.0115; 191-1 MLV 34.08; SIDEWALK AREA IN FRONT OF 4811 ALHAMBRA AVE.
|  | 131 | 33.87 | [15 empty] | MP 33.85 9' TOP 131
[16 empty] | Steel/Wrought Iron |  | ANTIOCH | TREE ROOTS INDENTATION IN 2 LOCATIONS ON WRAP ABOUT 10" APART. ALSO WRAP DIDN'T ADHEIR TO PIPING IN THIS LOCATION
[16 empty] | Steel/Wrought Iron |  | ANTIOCH | REMOVED 24" OF WRAP & REWRAPPED & INSTALLED REINFORCED COMPOSITE E.T.S. STATION WITH WARNING STICKERS
|  |  |  | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | REMOVED WRAP SP5 APPROX MP .25 TO INSPECT
|  |  | 0.22 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | REMOVED 24" OF WRAP, INSTALLED TEST LEAK APPROX M.P. .22 SP5
|  | 191 | 0.25 | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | REMOVED WRAP TO INSPECT L-191 APPROX MO. .25 NO DAMAGE TO PIPE
|  | 191 | 0.25 | [12 empty] | Steel/Wrought Iron |  | ANTIOCH | REWRAPPED 6' 2" OF LINE 191. LOOKS LIKE REPAIR HAS BEED MADE ON PIPE. DUE TO TAPE WRAP AT THIS LOCATION NEXT TO HPR COATING
|  | 191 | 0.0004 | 1.05 | Transmission | [10 empty] | Steel/Wrought Iron |  | MARTINEZ | SOURE VTE = 191- DREG 5211, M.P. 0.0004, PM# 41346871; L-191 1:3/4" TAP LINE FROM L 191 TO RC- 26 ALHAMBRA VALLEY RD & MILTHWAIT DRIVE MARTINEZ; CONTRA COSTA COUNTY
| 08-40102-1 | 401 | 233.88 | 1 | Transmission |  | Valves |  |  |  |  | 2008-06-04 | [5 empty] | DUNNIGAN
| 08-40102-1 | 401 | 233.88 | 1 | Transmission |  | Valves |  |  |  |  | 2008-06-04 | [5 empty] | DUNNIGAN
| 08-40102-1 | 401 | 233.88 | 1 |  |  | Valves |  |  |  |  | 2008-06-04 | [5 empty] | DUNNIGAN | SMALL VALVES IN BOTH VALVE COVERS
| 08-40008-1 | 400 | 269.48 | 36 | Transmission |  | Mechanical Joint | Valves |  |  |  | 2008-02-25 |  |  |  | Steel/Wrought Iron |  | VACAVILLE
| 08-40003-1 | 400 | 269.48 | 34 | Transmission |  | Mechanical Joint | Valves |  |  |  | 2008-02-25 |  |  |  | Steel/Wrought Iron |  | VACAVILLE
| 06-33100-1 | [10 empty] | 2006-09-06 | [5 empty] | VACAVILLE | ... 269.5 AT THE MERIDIAN VACA DIXO...; SAME; SAME; RECHECK
| 08-40001-1 | 400 | 82.33 | 30 | Transmission |  | Other |  | FLANGE BOLT | Equipment Malfunction |  | 2008-05-29 | 2009-09-17 | Other | TRP-3117 | Steel/Wrought Iron |  | BURNEY | GPS READ N. 40 53.591' W 121 38.008'
|  |  |  | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | GPS READ N 40 53.591', W 121 38.008
| 08-40001-1 | 400 | 82.33 | 30 | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2008-05-29 |  |  |  | Steel/Wrought Iron |  | BURNEY
| 08-40001-1 | 400 | 82.33 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2008-05-29 |  |  |  | Steel/Wrought Iron |  | BURNEY
| 08-20006-1 | 200 |  | 10 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-08-21 | 2008-08-22 | Other | PLIDCO CLAMP | Steel/Wrought Iron |  | RIO VISTA | L-200 CL RV29-08, GPS N38 10.340', W 121 42.409', FAXED @ 12:26; CONTACTED N. JENEST
| 08-40002-1 | 210 |  |  | Transmission |  | Other |  | ORIFACE FITTING IN VAULT |  |  | 2008-08-29 | 2009-01-07 | Other | TIGHTEN FITTING | Steel/Wrought Iron |  | DIXON | TIGHTENED MISC. FITTING ON METER
| 08-40002-1 | 210A | 1.42 |  | Transmission |  | Other |  | ORIFACE FITTING IN VAULT |  |  | 2008-08-29 |  |  |  | Steel/Wrought Iron |  | DIXON
| 08-40001-1 | 400 | 82.33 | [8 empty] | 2008-05-29 | [5 empty] | BURNEY
| 08-40001-1 | [10 empty] | 2008-05-29 | [5 empty] | BURNEY
| 08-40001-1 | 400 | 82.33 | [8 empty] | 2008-05-29 | [5 empty] | BURNEY
| 08-40001-1 | 400 | 82.33 | [8 empty] | 2008-05-29 | [5 empty] | BURNEY
| 08-31804-1 |  |  | 6.25 |  |  | Unknown |  |  | Unknown | SUSPECT INTERNAL CORROSION | 2008-06-09 |  |  | SEE GAS OPERATIONAL CHANGE NOTICE | Steel/Wrought Iron |  | ORLAND | SEE GAS OPERATIONAL CHANGE NOTICE ATTACHED
| 08-31803-1 |  | 0.626 | 6.25 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-04-30 | 2008-06-03 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | ORLAND | INSTALLED 6" PLIDCO SPLIT & SLEEVE OVER PIN HOLE 6" STEEL L-318 36'6" E/O V-6 SOAP @ 100PSI
| 08-31802-1 |  | 2.2785 | 6.25 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-04-30 | 2008-06-04 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | ORLAND | INSTALL 6" PLIDCO SPLIT SLEEVE OVER PINHOLE 6" STEEL L-318 SOAP @ 100 PSI
| 08-31801-1 | 318 | 2.044 | 6.5 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-02-08 | 2008-02-09 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | ORLAND | FOUND PIN HOLE IN BOTTOM OF PIPE. REPAIRED BY INSTALLING 24" CAN OF PRETESTED EMERGENCY STOCK
| 08-31403-1 | 314 | 23 | [8 empty] | 2008-10-20 | [5 empty] | ORE GRANDE
| 08-31401-1 | 314 | 24.72 | [8 empty] | 2008-10-17 | [5 empty] | ORE GRANDE
| 08-30205-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-12-03 | 2008-12-10 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | DUNNIGAN
| 08-30204-1 |  | 0.0069 | 6.25 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-06-03 | 2008-06-11 | Other | CUT/CAP | Steel/Wrought Iron |  | MERIDIAN | GHS WELL JOB#30634757, RT = 302-150, M.P. 0.0069; CUT & CAP @ V55 TO ABANDOON 52 GAS WELL DUE TO LEAK
| 08-30203-1 |  | 0.5433 | 12 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-07-02 | 2008-07-16 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | GRIMES | INSTALL 70" CAN WITH SAV-A-VALVE
| 08-30202-1 | 302 | 5.5682 | 3 | Gathering |  | Body of Pipe |  |  |  |  | 2008-05-27 | 2008-05-30 | Deactivate #TP Main | OTHER= CUT AND CAP 3" | Steel/Wrought Iron |  | GRIMES | JOB#30633279; CAP WITH SAV-A-VALVE AT 20" AND CUT OFF RISER 24' BELOW GROUND. CUT OFF AND ABANDONED APPROX 2,420' OF 3" T.P. STL MAIN
| 08-30201-1 | 302 | 22.5 | 6.625 | Transmission |  | Body of Pipe | Other | DIG IN 3RD PARTY |  |  | 2008-02-29 | 2008-03-01 | Replace TP Main |  | Steel/Wrought Iron |  | SUTTER | SEE ATTACHED; CONTRACTOR DUG INTO PIPE. AREA NOT LOCATED BY LOCATOR. ; LOCATOR DID NOT MARK OR LOCATE PIPELINE
| 08-30014-1 |  |  | 0.75 | Gathering |  | Fitting |  |  | Unknown |  | 2008-08-26 | 2008-12-17 | Other | SERVICE VALVE |  |  | AVENAL | LEAK WAS COMING FROM GREASE FITTING RISER ON L-306 VALVE -57, SERVICE MLV WITH 1040 GREASE STOPPED LEAK
| 08-30014-1 | [10 empty] | 2008-08-26 | [5 empty] | AVENAL
| 08-30013-1 | [10 empty] | 2008-08-26 | [5 empty] | AVENAL
| 08-30013-1 | [10 empty] | 2008-08-26 | 2008-12-08 | Tighten Cap or Bolt |  |  |  | AVENAL | FOUND LEAK AT FIRE VALVE NEXT TO MLV 354.13 FIXED LEAK BY FULLY OPENING FIRE VALVE CHECKED REPAIR BY DOING SOAP TEST. LEAK REPAIRED
| 08-30013-1 | [10 empty] | 2008-10-17 | [5 empty] | AVENAL
| 08-30012-1 |  |  | 0.5 | Transmission |  | Fitting |  |  | Unknown |  | 2008-08-26 | 2008-12-17 | Soap and/or Tape - Other |  | Steel/Wrought Iron |  | AVENAL | LEAK AT 1/2" CLOSE NIPPLE ON BODY BLEED FOR 3" BALL VALVE. CLEANED THREADS, TAPED, RE-TIGHTENED FITTINGS
| 08-30012-1 | [10 empty] | 2008-10-17 | [5 empty] | AVENAL
| 08-30011-1 | [10 empty] | 2008-08-26 | [5 empty] | AVENAL
| 08-30011-1 | [10 empty] | 2008-08-26 | 2008-12-08 | Tighten Cap or Bolt |  |  |  | AVENAL | FOUND LEAK ON THE L-190 METER RUN IN KETT. COM P. STA. I TIGHTEN THERMOWELD AND CHECKED REPAIR DOING SOAP TEST. LEAK REPAIRED
| 08-30011-1 | [10 empty] | 2008-10-17 | [5 empty] | AVENAL
| 08-30010-1 |  |  | 34 | Transmission |  | Unknown |  |  | Unknown |  | 2008-10-28 |  |  |  | Steel/Wrought Iron |  | HINKLLEY | ON 1/2" STATION PIPE; INSIDE STATION TRYING OT LOCATE
| 08-30010-1 | 300B | 0.45 | 34 |  |  | Unknown |  |  | Unknown |  | 2008-10-28 |  |  |  | Steel/Wrought Iron
| 08-30009-1 | 300A | 31 | 34 |  |  | Unknown |  |  | Unknown |  | 2008-10-28 |  |  |  | Steel/Wrought Iron |  | TOPOCK DISTRICT | RT 300A M.P. 31.00
| 08-30009-1 | 300A | 31 | 34 |  |  | Unknown |  |  | Unknown |  | 2008-10-28 |  |  |  | Steel/Wrought Iron
| 08-30009-1 | 300A | 31 | 34 |  |  | Unknown |  |  | Unknown |  | 2008-10-28 |  |  |  | Steel/Wrought Iron
| 08-30008-1 | 300A | 29 | 34 |  |  | Unknown |  |  | Unknown |  | 10/28/0200 |  |  |  | Steel/Wrought Iron |  | TOPOCK DISTRICT
| 08-30009-1 | 300A | 31 | 34 | Transmission |  | Longitudinal Weld |  |  | Weld Failure |  | 2008-10-28 | 2010-10-15 | Welded Sav-A-Valve - Weld |  | Steel/Wrought Iron |  | NEEDLES | MADE REPAIR FOLLOWING NO STANDARD 54134. AS PER MIKE TEAR INSTRUCTION
| 08-30008-1 | 300A | 29 | 34 | Transmission |  | Longitudinal Weld |  |  | Material Failure |  | 2008-10-28 | 2010-10-15 | Welded Sav-A-Valve - Weld |  | Steel/Wrought Iron |  | NEEDLES | MADE REPAIR FOLLOGIN 54134. AS PER TO MIKE TEARE INSTRUCTIONS
| 08-30008-1 | 300A | 29 | 34 |  |  | Unknown |  |  | Unknown |  | 2008-10-28 |  |  |  | Steel/Wrought Iron
| 08-30008-1 | 300A | 29 | 34 |  |  | Unknown |  |  | Unknown |  | 2008-10-28 |  |  |  | Steel/Wrought Iron
| 08-30007-1 | 300B | 20.44 | 34 |  |  | Unknown |  |  | Unknown |  | 2008-10-28 |  |  |  | Steel/Wrought Iron
| 08-30006-1 | [10 empty] | 2008-10-21 | [5 empty] | KETTLEMAN CITY
| 08-30006-1 | [10 empty] | 2008-10-21 | [5 empty] | KETTLEMAN CITY
| 08-30006-1 | [10 empty] | 2008-10-21 | [5 empty] | KETTLEMAN CITY
| 08-30004-1 | 300A | 354 | [8 empty] | 2008-10-17 | [5 empty] | AVENAL
| 08-30004-1 | [10 empty] | 2008-10-17 | [5 empty] | AVENAL
| 08-30003-1 | 300B | 137.55 | [8 empty] | 2008-10-18 | [5 empty] | ORE GRANDE
| 08-30002-1 | 300B | 203.07 | [8 empty] | 2008-10-19 | [5 empty] | NORTH EDWARDS | X-6521, MP. 0.0079
| 08-30001-1 | 300A | 304.34 | 12 |  |  | Fitting |  |  | Other | FITTING | 2008-09-09 | 2008-09-09 | Tighten Cap or Bolt | SOAP AND/OR TAPE | Steel/Wrought Iron |  |  | SURVIED VALVE & TIGHTEN UNIBOLT CAP AND PLUG ON 1" VENT
| 08-30001-1 | 300A | 304.34 | 12 |  |  | Fitting |  |  | Other | FITTING | 2008-09-09 | 2008-09-09 | Tighten Cap or Bolt | SOAP AND/OR TAPE | Steel/Wrought Iron |  |  | SURVIED VALVE & TIGHTEN UNIBOLT CAP & PLUG ON 1" VENT
| 08-20008-1 | 200 | STATION | 24 | Transmission |  | Fitting | Physical/Mechanical Joint |  |  |  | 2008-08-27 | 06/00/2009 | Deactivate #TP Main |  |  |  | RIO VISTA | NO REPAIR- LINE WAS ISOLATED BLOWN DOWN AND REMOVED; SERPA COMPRESSOR STA. NOTIFIED SUPERVISOR OFLEAK LOCATION IN ORIFACE VAULT. CL RV39-08 BYPASSED SECTION OF LINE. VALVES OFF ...TAKEN OUT-OF-SERVICE 10/23/2008. LINE REMOVED 06/09 ON 3066519
| 08-20008-1 | 200 | STATION | 24 | Transmission |  | Fitting | Physical/Mechanical Joint |  |  |  | 2008-08-27 | [5 empty] | RIO VISTA | NO REPAIR- LINE WAS ISOLATED BLOWN DOWN AND REMOVED; SERPA COMPRESSOR STA. NOTIFIED SUPERVIOSR OF LEAK LOCATION IN ORIFACE VAULT. CL RV39-08 BYPASSED SECTION OF LINE. VALVED OFF A TAKEN OUT-OF-SERVICE 10/23/08. LINE REMOVED 06/09 ON 3066519
| 08-20008-1 | 200 | STATION | 24 | Transmission |  | Fitting | Physical/Mechanical Joint |  |  |  | 2008-08-27 | [5 empty] | RIO VISTA | SER[A COMPRSSOR STA. NOTIFIED SUPERVISOR OF LEAK LOCATION IN ORIFACE VAULT
| 08-20007-1 | 200A | 5.07 | 24.00 & 16.00 | Transmission |  | Fitting | Physical/Mechanical Joint |  |  |  | 2008-08-27 | [5 empty] | RIO VISTA | NOTIFIED SUPERVISOR OF LEAK LOCATION IN ORIFACE VAULT
| 08-20006-1 | 200 |  | 10 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-08-21 | 2008-08-22 | Other | PLIDCO CLAMP | Steel/Wrought Iron |  | RIO VISTA | CONTACTED N JENEST
| 08-20005-1 | 200 |  | 8 | Transmission | GATHERING | Body of Pipe |  |  | Internal Corrosion |  | 2008-07-01 |  |  |  | Steel/Wrought Iron |  | RIO VISTA
| 08-20004-1 | 200 | 0.38 | 8 | Gathering |  |  |  |  | Internal Corrosion |  | 2008-04-30 |  |  |  | Steel/Wrought Iron |  | RIO VISTA
| 08-20004-1 | 200 | 0.3847 | 8 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB # 40760358, ROUTE L-200 C1-2, M.P 0.3847 & 0.3834; JOB# 40760358; NO WELDING NEEDED AT LEAK LOCATION. INSTALLED (2EA) 8" HIGH PRESSURE PLIDCO REPAIR LEAK CLAMP. SER # SN2771023B & WP 1000F 6 FEET APART. FIRST CLAMP 123' SOUTH OF VALVE #228 2ND REPAIR CLAMP 129' SOUTH OF VALVE #228
| 08-20003-1 | 200 | 0.387 | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-04-21 |  |  |  | Steel/Wrought Iron |  | RIO VISTA
| 08-20003-1 | 200 | 00.3847 & 00.3834 | 8 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 40760358 ROUTE L-200C1-2; 1. M.P. 0.3847 2. M.P. 0.3834; JOB # 40760358; JOB# 40760358; NO WELDING NEEDED AT LEAK LOCATION. INSTALLED (2EA) 8" HIGH PRESSURE PLIDCO REPAIR LEAK CLAMP. SER #SN2771023B& WP 1000F 6 FEET APART. FIRST CLAMP 123' SOUTH OF VALVE #228. 2ND REPAIR CLAMP 129' SOUTH OF VALVE #228
| 08-20002-1 | 200 | 0.33 | 8 | Gathering | [6 empty] | 2008-04-21 |  |  |  | Steel/Wrought Iron |  | RIO VISTA
| 08-20002-1 |  | 0.3312 | 8 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | ROUTE L-200 C7-1, M.P. 0.3312, JOB# 40760358; JOB # 40760358; JOB# 40760358; DUG UP LEAK LOCATION & IDENTIFIED PROBLEM. CUT OUT 3' OF 8" STEEL PIPE AND INSTALLED NEW 8" PIPE. (3' OF .188 WALL TESTED GRADE B SEAMLESS). LEAK LOCATION WAS 405' SOUTH OF V-228. GPS COORD BY JERRY PENICK CGT SUPERVISOR N38 14.925 MINUTES W 121 45.157 MINUTES (LEAK WAS CAUSED BY INTERNALL CORROSION)
| 08-20001-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-01-26 | 2008-02-05 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | RIO VISTA | BACK GROUND .280 CAN 3' LONG
| 08-19601-1 | 196 |  | 2 | Transmission |  | Valves |  |  |  |  | 2008-08-28 | [5 empty] | RIO VISTA | FRAME AND COVER INSIDE OF YARD V-4 (VAULT); CAN RECHECK, AFTER GREASE AND OPERATE. SMALL LEAK
| 08-19503-1 | 195-0151 |  | 8 | Gathering |  | Unknown |  | AT THIS TIME |  |  | 2008-11-03 |  |  |  | Steel/Wrought Iron |  | RIO VISTA | GPS.... N 38 9.412, W 121 40.392. CL RV 37-08
| 08-19502-1 | 196 |  | 2 | Transmission |  | Valves |  |  |  |  | 2008-08-28 | [5 empty] | RIO VISTA | FRAME AND COVER INSIDE OF YARD; CAN RECHECK, AFTER GREASE AND OPERATE
| 08-19101-1 | 191 | 8.7 | 24 | Transmission |  | Unknown |  |  | Unknown |  | 2008-11-24 | 2008-12-23 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | PITTSBURG | TIGHTENED FLANGE FITTING
| 08-19101-1 | 191 | 8.7 | 24 | Transmission |  | Unknown |  |  | Unknown |  | 2008-11-24 |  |  |  | Steel/Wrought Iron |  | PITTSBURG
| 08-17701-1 | 177 |  | 0.25 | Transmission |  | Fitting | Valves |  | Other |  | 2008-06-05 | 2009-09-16 | Other | TIGHTENED FITTING EXCERCISED VALVE | Steel/Wrought Iron |  | CHICO | EXERCISED VALVE AND TIGHTENED 1/4" TUBE FITTING SOAP TEST- NO LEAKS
| 08-17202-1 | 172 | [9 empty] | 2008-05-20 | [5 empty] | DUNNIGAN
| 08-17201-1 | 172 | [9 empty] | 2008-05-20
| 08-17202-1 | 172 | [9 empty] | 2008-05-20 | [5 empty] | DUNNIGAN
| 08-17201-1 | 172 | [9 empty] | 2008-05-20
| 08-16902-1 | 169 |  | 1 | Transmission |  | Valves |  |  | Other | VALVE | 2008-06-05 | 2009-09-23 | Other | SEALED CONDUITS IN SPLICE BOX FOR V-20 | Steel/Wrought Iron |  | CHICO | SEALED CONDUITS FOR V-20 SPLICE BOX
| 08-16901-1 | 169 | 2.08 | 12.75 | Transmission |  | Body of Pipe |  |  |  |  | 2008-03-31 | 2008-04-01 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | GLENN | INSTALLED SLEEVE OVER PUNCTURE HOLE IN PIPE; FARMER WAS DIGGING OUT BOTTOM OF DIFER WITH A V-DITCHER PLOW WHEN HE STRUCK STEEL MAIN CAUSING THE LEAK; FARMER DID NOT CALL IN USA FOR AREA HE WAS WORKING
| 08-13102-1 | 131 | 26.98 | 24 | Transmission |  | Valves |  |  | External Corrosion |  | 2008-11-05 | 2008-11-08 | Other | INSTALLED NEW PLUG | Steel/Wrought Iron |  | LIVERMORE
| 08-13102-1 | 131 | 26.63 | 24 | Transmission |  | Valves |  |  | External Corrosion |  | 2008-11-05 |  |  |  | Steel/Wrought Iron |  | LIVERMORE
96 | 08-13101-1 | 131 | 33.95 | 1 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2008-06-12 | 2010-10-28 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | LIVERMORE | AT BASE OF VALVE; MUELLER VALVE TEE FOR GAGE TAP CAP LEAKING
| 08-13101-1 | 131 | 33.95 | 24 | Transmission |  | Fitting | Valves |  |  |  | 2008-06-12 | [5 empty] | LIVERMORE | 06-12-08 NOTIFIED SUPERVISORS OF LEAK AT LOCATION IN VALVE YARD. GRADE 3 AT THIS TIME. TO SET UP FOR RECHECK DJMR/DFK1
| 08-10701-1 | 107 | 15.27 | 22 | Transmission |  | Other |  | LEAKING DRESSER COUPLING | Material Failure |  | 2008-03-10 | 2008-11-07 | Replace TP Main |  | Steel/Wrought Iron |  | LIVERMORE | REMOVED MLV BRIDLE INPIT W/ DRESSER COUPLINGS
| 08-10701-1 | 107 | 15.27 | 22 | Transmission |  | Other |  | DRESSER COUPLING IN PIT | Material Failure |  | 2008-03-10 | [5 empty] | LIVERMORE
| 08-10701-1 | 107 | 15.27 | 22 | Transmission |  | Other |  | DRESSER COUPLING | Material Failure |  | 2008-03-10 | [5 empty] | LIVERMORE | L-107 M.P 15.27 ARROYO RD LIVERMORE
| 08-00501-1 | STANPAC5 | 3.17 | 34 | Transmission |  | Other | Unknown | NOT PIPELINE GAS TESTED AND CONFIRMED NOT TO BE PIPELINE GAS RESULTS 9-22-08 | Unknown |  | 2008-05-30 |  | Other | CASING VENT MODIFICATION | Steel/Wrought Iron |  | ANTIOCH | NO REPAIR NEEDED TO PIPELINE
| 08-00501-1 | STANPAC5 | 3.17 | 24 | Transmission |  | Unknown |  |  | Unknown |  | 2008-05-30 |  |  |  | Steel/Wrought Iron |  | ANTIOCH
| 08-00501-1 | STANPACK5 | 3.17 | 24 | Transmission |  | Unknown |  |  | Unknown |  | 2008-05-30 |  |  |  | Steel/Wrought Iron |  | ANITOCH
| 08-00201-1 | [10 empty] | 2008-08-26 | 2008-09-15 | Tighten Cap or Bolt |  |  |  | TRACY
| 08-00201-1 | [10 empty] | 2008-08-26 | [5 empty] | TRACY
| 08-00202-1 | [10 empty] | 2008-08-26 | 2008-09-15 | Tighten Cap or Bolt |  |  |  | TRACY
| 08-00202-1 | [10 empty] | 2008-08-26 | [5 empty] | TRACY
| 08-00203-1 | 2 |  | 6 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2008-08-26 | 2008-09-15 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | TRACY
| 08-00203-1 | [10 empty] | 2008-08-26 | [5 empty] | TRACY
| 08-00203-1 | [10 empty] | 2008-08-26 | 2008-09-15 | Tighten Cap or Bolt |  |  |  | TRACY
| 08-00204-1 | 2 |  | 6 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2008-08-26 | 2008-09-15 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | TRACY
| 08-00204-1 | [16 empty] | TRACY
| 08-00204-1 | [11 empty] | 2008-09-15 | Tighten Cap or Bolt |  |  |  | TRACY
| 08-00205-1 | 2 |  | 6 | Transmission |  | Unknown |  |  | Unknown |  | 2008-08-26 | 2009-03-02 | Tighten Cap or Bolt | Other | Other |  | THORNTON
| 08-00205-1 | 162 | [9 empty] | 2008-08-26 | 2009-03-02 | Other | MOONEY SPRING CASE |  |  | TRACY
| 08-00205-1 | [10 empty] | 2008-08-26 | [5 empty] | TRACY
| 08-00206-1 | 2 | [9 empty] | 2008-08-26 | 2008-11-19 | Other | TIGHTEN STEM PACKING |  |  | TRACY
| 08-00206-1 | [10 empty] | 2008-08-26 | [5 empty] | TRACY
| 08-19601-1 | 196 | [15 empty] | ISLETON | DIVISION LEAK REMOVE DISTRICT #
| 07-31801-1 | 318 | 4.12 | 4 | Transmission | Gathering |  |  |  | Internal Corrosion |  | 2007-01-30 | 2007-02-07 | Other | REPLACED PIPE |  |  | ORLAND
| 07-30011-1 | 300A | 60.92 | 12 | Transmission |  | Other |  | UNIBOLT CAP | Other | LOSE CAP | 2007-09-28 | 2010-09-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | NEEDLES | DURING ANNUAL LEAK SURVEY, CHECKED STACK AND NO LEAK
| 07-30011-1 | 300A | 80.92 | 34 | Transmission |  | Valves |  |  |  |  | 2007-09-28 | [5 empty] | NEEDLES
| 07-30011-1 | 300 A | 60.92 | 34 | Transmission |  | Valves
| 07-30010-1 | 300A | 55.89 | 12 | Transmission |  | Other |  | UNIBOLT CAP | Other | LOSE CAP | 2007-09-28 | 2010-10-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | NEEDLES | REMOVED LID, INSTALLED WITH TIGHT-SEAL, NO LEAKS.
| 07-30010-1 | 300A | 55.9 | 34 | [7 empty] | 2010-09-14
| 07-30010-1 | 300A | 55.89 | 34 | Transmission |  | Valves | [11 empty] | UNI-BOLT FITTING TO BLOW DOWN STACK
| 07-30005-1 | 300A | 87.1 | 12 | Transmission |  | Other |  | UNIBOLT CAP | Other | LOSE CAP | 2007-09-26 | 2010-10-11 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | NEEDLES | REMOVE UNIBOLT CAP AND CLEANED GASKET SURFACE, APLIED TIGHT SEAL TO GASKET AND REINSTALLED. CHECKED FOR LEAKS AT 100 PSI
| 07-30005-1 | 300A | 87.1 | 34 |  |  | Valves |  |  |  |  | 2007-09-26 | 2010-10-11 |  |  |  |  | NEEDLES | REMOVE UNIBOLT CAP AND CLEANED GASKET SURFACE, APLIED TIGHT SEAL TO GASKET AND REINSTALLED. CHECKED FOR LEAKS AT 100 PSI
| 07-30005-1 | 300 A | 87.1 | 34 | Transmission |  | Valves | [11 empty] | UNIBOLT FITTING TO BLOW DOWN STACK
| 07-30005-1 | 300A | 87.1 | 34 | Branch Service |  | Fitting |  |  |  |  | 2010-09-16 |  |  |  | Steel/Wrought Iron |  | NEEDLES
| 07-30002-1 | 300A | 108.39 | [8 empty] | 2010-09-17 | [5 empty] | LUDLOW
| 07-30002-1 | 300 A | 108.39 | 34 | Transmission |  | Valves
| 07-30001-1 | 300B | 354.2 | 34 | Transmission |  | Other |  | DRILL HOLE | Other | DRILLED WRONG LINE | 2007-08-13 | 2007-08-16 | Other | WELD 1" SAVE-A-VALVE | Steel/Wrought Iron |  | AVENEL | DRILL 15/64 HOLE ON 300-B WHEN IT SHOULD OF BEEN DRILLED ON 300-A FOR A SNIFF HOLE TO REPLACE V-56 AT KETT. COMP. STA.
| 07-20002-1 | 200 | 0.1415 | 10 | Gathering |  |  |  |  | Internal Corrosion |  | 2007-05-07 | 2007-05-08 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | RIO VISTA
| 07-20002-1 | 200 | 0.1415 | 10 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2007-05-07 |  |  |  | Steel/Wrought Iron |  | RIO VISTA
| 07-20002-1 | 200 |  | 10 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2007-05-07 |  |  |  | Steel/Wrought Iron |  | RIO VISTA
| 07-20001-1 | 200 | 0.1774 | 8 | Gathering |  |  |  |  | Internal Corrosion |  | 2007-01-24 |  |  |  | Steel/Wrought Iron |  | RIO VISTA | N/A - RETIRED IN PLACE JOB#6102223 3-28-07; RETIRED IN PLACE ON JOB#6102223
| 07-20001-1 | 200 |  | 8 | Gathering |  |  |  |  | Internal Corrosion |  | 2007-01-24 |  |  |  | Steel/Wrought Iron |  | RIO VISTA | N/A - RETIRED IN PLACE JOB#6102223 3-28-07; RETIRED IN PLACE ON JOB#6102223
| 07-19601-1 | 196 | 0.0024 | 6 | [7 empty] | 2007-08-23 | [5 empty] | THORNTON
| 07-19601-1 | 196 | 0.0024 | [8 empty] | 2007-09-10 | [5 empty] | THORNTON | OLD GAMBLE 1 WALL 5500' S/O PELTIER RD & 8500' W/O BLOSSOM RD.
| 07-19601-1 | 196 |  | 6 | [7 empty] | 2007-08-23 |  | Deactivate #TP Main |  |  |  | THORNTON | OLD GAMBLE 1 WALL 5500' S/O PELTIER RD & 8500' W/O BLOSSOM RD.; N/A RETIRED IN-PLACE
| 07-19601-1 | 196 |  | 6 | Gathering | [6 empty] | 2007-08-23 |  | Deactivate #TP Main |  | Steel/Wrought Iron |  | THORNTON | OLD GAMBLE 1 WALL 5500' S/O PELTIER RD & 8500' W/O BLOSSOM RD.; N/A RETIRED IN-PLACE; PIPELINE RETIRED IN PLACE AFTER CUT OFF AT WOODBRIDGE RD.
| 07-19505-1 | 195 |  |  |  |  | Fitting |  |  |  |  | 2007-11-29 | 2007-11-29 | Other | REMOVED BROKEN FITTING |  |  | ISLETON
| 07-19505-1 | 195 |  |  | Gathering |  | Fitting |  |  | Material Failure |  | 2007-11-29 | 2007-11-29 | Other | REMOVED BROKEN FITTING | Steel/Wrought Iron |  | ISLETON
| 07-19504-1 | 195 | 0.4518 | 12 | [7 empty] | 2007-11-05 | [5 empty] | ISLETON
| 07-19504-1 | 195 |  | 12 | Gathering |  |  |  |  | Internal Corrosion |  | 2007-11-05 |  |  |  | Steel/Wrought Iron |  | ISLETON | DEACTIVATED PIPELINE FOR 3RD PARTY SALE
| 07-19504-1 | 195 |  | 12 | Gathering |  |  |  |  | Internal Corrosion |  | 2007-11-05 |  |  |  | Steel/Wrought Iron |  | ISLETON | DEACTIVATED PIPELINE FOR 3RD PARTY SALE
| 07-19503-1 | 195 | 0.0924 | 10 | [13 empty] | ISLETON
| 07-19503-1 | 195 | 79A | 10 | Gathering |  |  |  |  | Internal Corrosion |  | 2007-11-05 | 2007-11-29 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | ISLETON | INSTALLED 20' CAN LEFT. DEACTIVATED FOR 3RD PARTY SALE
| 07-19503-1 | 195 | 79A | 10 | Gathering |  |  |  |  | Internal Corrosion |  | 2007-11-05 | 2007-11-29 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | ISLETON | INSTALLED 20' CAN LEFT. DEACTIVATED FOR 3RD PARTY SALE; LEFT DEACTIVATED FOR 3RD PARTY SALE
| 07-19502-1 | 195 | 0 | [8 empty] | 2007-10-25 | [5 empty] | ISLETON
| 07-19502-1 |  |  | 12 | Gathering |  |  |  |  | Internal Corrosion |  | 2007-10-25 | 2007-10-25 | SS Clamp w/Anode - Clamp |  |  |  | ISLETON | INSTALLED SS CLAMP
| 07-19503-1 | 195 | 79A | 10 | Gathering |  |  |  |  | Internal Corrosion |  | 2007-11-05 | 2007-11-29 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | ISLETON | INSTALLED 20' CAN. LEFT DEACTIVATED FOR 3RD PARTY SALE
| 07-19502-1 | 195 |  | 12 | Gathering |  |  |  |  | Internal Corrosion |  | 2007-10-25 | 2007-10-25 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | ISLETON | INSTALLED SS CLAMP AND WRAPPED
| 07-19501-1 | 195 | 0.0907 | 10 | [7 empty] | 2007-10-18 | [5 empty] | ISLETON
| 07-19501-1 | 195 |  | 10 | [5 empty] | Internal Corrosion |  | 2007-10-18 | 2007-10-19 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | ISLETON | INSTALLED WELDED SLEEVE
| 07-19501-1 | 195 |  | 10 | Gathering |  |  |  |  | Internal Corrosion |  | 2007-10-18 | 2007-10-19 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | ISLETON | INSTALLED WELDED SLEEVE
| 07-30035-1 | 125 | 0 | 2 | Gathering |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2007-12-14 | 2008-01-15 | Replace Dist Main < 100 ft |  | Steel/Wrought Iron |  | FORTUNA | BODY OF PIPE-INSTALLED CLAMP; REPLACED 1'-2" STL PIPE; SOAP TESTED (MAPPING REC. LEAK ON 03-04-08)
| 07-12001-1 | 120 | 0 | 6 | Transmission |  | Unknown |  |  | Unknown |  | 2007-08-01 | 2007-08-01 | Deactivate #TP Main |  | Steel/Wrought Iron |  | SUTTER | DEACTIVATED APROX. 105' OF 6", 4", 2" STL ON LINE 120 FROM T-2.03 TO VALVE #5 IN SUTTER CREEK VALVE LOT
| 07-00129-1 | 121 | 2.03 | 6 | Transmission |  | Unknown |  |  | Unknown |  | 2007-08-01 | 2007-08-01 | Deactivate #TP Main |  | Steel/Wrought Iron |  | SUTTER | DEACTIVATED APPROX. 105' STL. @T-2.03 TO
| 09-40104-1 |  | 197.8 |  | Transmission |  | Valves |  |  | Other | VALVES | 2009-06-02 |  |  |  | Steel/Wrought Iron |  | MAXWELL
| 09-40104-1 |  | 197.8 |  | Transmission |  | Valves |  |  | Other | VALVES | 2009-06-02 |  |  |  | Steel/Wrought Iron |  | MAXWELL
| 09-40104-1 |  | 197.8 |  | Transmission |  | Valves |  |  | Other | VALVES | 2009-06-02 |  |  |  | Steel/Wrought Iron |  | MAXWELL
| 09-40103-1 | 401 | 197.8 |  | Transmission |  | Valves |  |  | Other | VALVES | 2009-06-02 |  |  |  | Steel/Wrought Iron |  | MAXWELL
| 09-40103-1 | 401 | 197.8 |  | Transmission |  | Valves |  |  | Other | VALVES | 2009-06-02 |  |  |  | Steel/Wrought Iron |  | MAXWELL
| 09-40103-1 | 401 | 197.8 |  | Transmission |  | Valves |  |  | Other | VALVES | 2009-06-02 |  |  |  | Steel/Wrought Iron |  | MAXWELL
| 09-40102-1 |  | 269.2658 | [8 empty] | 2009-10-26 | [5 empty] | VACAVILLE
| 09-40007-1 | 400 | 24.6 | 34 | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-07-28 | 2009-09-14 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | TIANASTA | TOUCH UP PAINT & TRANSITION COATING NEEDED
| 09-40007-1 | 400 | 24.6 | [8 empty] | 2009-07-28 | [5 empty] | TIANASTA
| 09-40006-1 | [5 empty] | Valves |  | PACKING |  |  | 2009-07-27 | [5 empty] | ANTIOCH
| 09-40006-1 | 400 | 297.86 |  |  |  | Valves |  | PACKING | Equipment Malfunction | Unknown | 2010-10-02 |  |  |  | Steel/Wrought Iron |  | ANITOCH
| 09-40005-1 | 400 | 97.66 | [8 empty] | 2009-05-26
| 09-40005-1 | 400 | 97.66 | [8 empty] | 2009-05-26
| 09-40005-1 | 400 | 97.66 | [8 empty] | 2006-05-26
| 09-40003-1 | 400 | 82.33 | [8 empty] | 2009-05-13 | [5 empty] | BURNEY
| 09-40003-1 | 400 | 82.33 | [8 empty] | 2009-05-13 | [5 empty] | BURNEY
| 09-40002-1 | 400 | 298.29 | 1.5 | Single Service |  | Fitting |  |  | Unknown |  | 2009-01-30 | 2009-02-11 | Other | TIGHTEN FITTING | Steel/Wrought Iron |  | ANITOCH | TIGHTENED FITTING TO STOP LEAK
| 09-40001-1 |  |  | 1 | Single Service |  | Fitting |  |  | Unknown |  | 2009-01-30 | 2009-02-11 | Other | TIGHTEN FITTING | Steel/Wrought Iron |  | ANITOCH | TIGHTENED SEALANT FITTING ON STOP LEAK.
| 09-31601-1 | 316A | 1.02 | 4 | Gathering |  | Tap Connection | Valves |  | Unknown |  | 2009-11-10 |  |  |  | Steel/Wrought Iron |  | OAKLEY
| 09-31406-1 | [10 empty] | 2009-10-28 | [5 empty] | ORO GRANDE
| 09-31407-1 | [10 empty] | 2009-10-28 | [5 empty] | ORO GRANDE
| 09-31408-1 | 314 | 27.46 | [8 empty] | 2009-10-28 | [5 empty] | VICTORVILLE
| 09-31404-1 | 314 | 24.19 | [8 empty] | 2009-10-03 | [5 empty] | ORO GRANDE
| 08-31404-1 | 314 | 22.31 | [8 empty] | 2008-10-21 | [5 empty] | ORE GRANDE
| 09-31403-1 | 314 | 24.72 | [8 empty] | 2009-10-02 | [5 empty] | ORE GRANDE
| 09-31402-1 | 314 | 38.57 | 8 | Transmission |  | Valves |  | LEAK IS FROM VALVE PIT. THERE IS A VALVE AND CHECK VALVE IN THE PIT. | Material Failure |  | 2009-09-21 | 2010-10-14 | Other | REPLACED STEM O-RINGS AND BUSHING | Steel/Wrought Iron |  | APPLY VALLEY | LEAK IS FROM VALVE PIT. THERE IS A VALVE AND CHECK VALVE IN THE PIT; I BACK SEATED GATE VALVE AND REMOVED FAILED BUSHINGS AND O-RINGS. REPLACED WITH NEW BUSHINGS AND O-RINGS.
| 09-31402-1 |  |  | 10 |  |  |  |  | LEAK IS FROM VALVE PIT. THERE IS A VALVE AND CHECK VALVE IN THE PIT. |  |  | 2009-09-21 | [5 empty] | APPLY VALLEY | LEAK IS FROM VALVE PIT. THERE IS A VALVE AND CHECK VALVE IN THE PIT
| 09-31402-1 |  |  | 10 |  |  |  |  | LEAK IS FROM VALVE PIT. THERE IS A VALVE AND CHECK VALVE IN THE PIT |  |  | 2009-09-21 | [5 empty] | APPLY VALLEY | LEAK IS FROM VALVE PIT. THERE IS A VALVE AND CHECK VALVE IN THE PIT.
| 09-31401-1 | [10 empty] | 2009-01-28 | [5 empty] | HODGE
| 09-31303-1 | 313 | 34.34 | [8 empty] | 2009-11-23 | [5 empty] | LUCERNA VALLEY
| 09-31303-1 | 313 | 34.34 |  |  |  | Valves |  |  | Equipment Malfunction |  | 2009-11-23 | [5 empty] | LUCERNA VALLEY
| 09-31302-1 | 313 | 27.26 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-23 | [5 empty] | LUCERNA VALLEY
| 09-31303-1 | 313 | 28.26 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-23 | [5 empty] | LUCERNA VALLEY
| 09-31101-1 | 300A | 180.64 |  | Transmission |  | Fitting | Valves |  | Equipment Malfunction |  | 2009-11-16 | [5 empty] | HINKLEY
| 09-30606-1 | 306 | 43.3 | 20 | Transmission |  | Valves |  |  |  |  | 2009-10-08 |  |  |  | Steel/Wrought Iron |  | PASO ROBLES
| 09-31405-1 | 314 | 8.76 | 12 | Transmission |  | Valves |  |  | Other | LOW ON STEM LACKING | 2009-10-07 | 2010-06-22 | Other | INSTALL STEM PACKING IN PLUG VALVE (BYPASS VALVE) | Steel/Wrought Iron |  | HELENDALE
| 09-30604-1 | 306 | 70 | 1 | Transmission | [6 empty] | 2009-08-05 | 2010-01-28 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | MORRO BAY
| 09-30605-1 | 306 | 70 |  | Transmission | [6 empty] | 2009-08-05 | 2010-01-27 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | MORRO BAY
| 09-30604-1 | 306 | 70 | [8 empty] | 2009-08-05 | 2010-01-28 | Replace Valve < 2 inch |  |  |  | MORRO BAY
| 09-30605-1 | 306 | 70 | [8 empty] | 2009-08-05 | 2010-01-27 | Replace Valve < 2 inch |  |  |  | MORROW BAY
| 09-30605-1 | 306 | 70 | [8 empty] | 2009-08-05 | [5 empty] | MORRO BAY
| 09-30604-1 | 306 | 70 | [8 empty] | 2009-08-05 | [5 empty] | MORRO BAY
| 09-30010-1 | 300A | 51.5 | 34 | Transmission |  | Unknown |  |  | Unknown |  | 2009-09-02 | 2010-09-03 |  |  | Steel/Wrought Iron |  | NEEDLES | SURVEYED AREA DURING ANNUAL SURVEY WITH AN HFI UNIT. UNABLE TO FIND LEAK. HAD KBS8 RE-SURVEY AREA TO VERIFY THERE WAS NO LEAK
| 09-40101-1 | 400 | 24.6 | 34 | Transmission |  | Fitting |  | BODY BLEED FITTINGS | Equipment Malfunction |  | 2009-10-15 | 2010-09-21 | Other | PIPE DOPE & REINSTALL FITTINGS | Steel/Wrought Iron |  | TIANESTA | COATED AREAS OF NEED
| 09-40101-1 | 400 | 24.6 | [8 empty] | 2009-10-15 | [5 empty] | TIANESTA
| 09-40101-1 | 400 | 24.6 | [8 empty] | 2009-10-15 | [5 empty] | TIANESTA
| 09-30602-1 | 306 | 0 | 20 |  |  | Valves |  | STAINLESS STEEL TUBING |  |  | 2009-04-02 | 2009-06-08 | Mechanical Repair Fitting - Fitting |  |  |  | AVENAL
| 09-30602-1 | 306 | 0 | 20 |  |  | Other |  | STAINLESS STEEL TUBING |  |  | 2009-04-02 | 2009-06-08 | Mechanical Repair Fitting - Fitting |  |  |  | AVENAL
| 09-30602-1 | 306 | 0 | 20 |  |  | Other |  | STAINLESS STEEL TUBING |  |  | 2009-04-02 | [5 empty] | AVENAL
| 09-30601-1 | 306 | 0 | 20 |  |  | Valves |  |  |  |  | 2009-04-02 | 2009-06-08 | Mechanical Repair Fitting - Fitting |  |  |  | AVENAL
| 09-30601-1 | 306 | 0 | 20 |  |  | Valves |  |  |  |  | 2009-04-02 | 2009-06-08 | Mechanical Repair Fitting - Fitting |  |  |  | AVENAL
| 09-30601-1 | 306 | 0 | 20 |  |  | Valves |  |  |  |  | 2009-04-02 | 2009-06-08 | Mechanical Repair Fitting - Fitting |  |  |  | AVENAL
| 09-30601-1 | 306 | 0 | 20 |  |  | Valves |  |  |  |  | 2009-04-02 | [5 empty] | AVENAL
| 09-30203-1 | 302 |  | 0.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2009-04-20 | 2009-05-29 | Replace TP Main |  | Steel/Wrought Iron |  | GRIMES | RAPID 20" DRIP PIPE. POST REPAIR COMPLET; TEST QUALITIES PIPE FOR 1000 PSIG MAOP. REPLACED ENTIRE POUNDSTONE DRIP STA ON PM# 30709311. SEE AS-BUILT FOR DETAILS
| 09-30203-1 | 302 |  | 20 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2009-04-20 | 2009-05-29 | Replace TP Main |  | Steel/Wrought Iron |  | GRIMES | REPLACED 20" DRIP PIPE; REPLACED ENTIRE POUNDSTONE DRIP STATION ON PM # 30709311. SEE AS BUILT FOR DETAILS.
| 09-30203-1 | 302 |  | 20 | Gathering |  | Body of Pipe | Other | INTERNAL CORROSION | Internal Corrosion |  | 2009-04-20 | 2009-05-29 | Replace TP Main | OTHER- INSTALL NEW DRIP | Steel/Wrought Iron |  | GRIMES | REPLACED 20" DRIP PIPE; REPLACED ENTIRE POUNDSTONE DRIP STATION ON PM # 30709311. SEE AS BUILT FOR DETAILS.
| 09-30203-1 | 302 |  | 20 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2009-04-20 | 2009-05-29 | Replace TP Main |  | Steel/Wrought Iron |  | GRIMES | REPLACED 20" DRIP PIPE; REPLACED ENTIRE POUNDSTONE DRIP STATION ON PM # 30709311. SEE AS BUILT FOR DETAILS.
| 09-30203-1 | [10 empty] | 2009-04-20 | [5 empty] | GRIMES
| 09-30603-1 | 306 | 69.8 | 8 | Transmission |  | Valves |  |  | Atmospheric Corrosion |  | 2009-06-17 | 2009-09-23 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | MORRO BAY
| 09-30603-1 | 306 | 69.8 | 8 | Transmission |  | Valves |  |  |  |  | 2009-06-17 |  |  |  | Steel/Wrought Iron |  | MORRO BAY
| 09-30604-1 | 306 | 70 | 1 | Transmission | [6 empty] | 2009-08-05 | 2010-01-28 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | MORRO BAY
| 09-30605-1 | 306 | 70 |  | Transmission | [6 empty] | 2009-08-05 | 2010-01-27 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | MORRO BAY
| 09-30202-1 | 302 |  | 8 | Gathering |  | Valves |  |  | Other | O-RINGS | 2009-03-31 |  |  |  | Steel/Wrought Iron |  | GRIMES
| 09-30202-1 | 302 | 0.15 | 8 | Gathering |  | Valves |  |  | Other | O-RINGS | 2009-03-31 | 2009-04-03 | Other | REPLACE SHAFT O-RING (STEM) | Steel/Wrought Iron |  | GRIMES | V-82 LEAK REPAIRED BY INSTALLING NEW O-RINGS ON GLAND PLATE AT THE STEM. REPAIRED AND LUBED STEM. ALL OK AT THIS TIME. REPAIRED BY DFA2/RJWG, 4-3--09 FIELD CHECKED
| 09-30201-1 | 302 |  | 6 | Gathering | PRODUCER LINE |  |  |  | Internal Corrosion |  | 2009-03-08 |  |  |  | Steel/Wrought Iron |  | MERIDIAN
| 09-30201-1 | 302 |  | 6 | Gathering | PRODUCER LINE |  |  |  | Internal Corrosion |  | 2009-03-08 | 2009-03-27 | Other | PLIDCO CLAMP | Steel/Wrought Iron |  | MERIDIAN | THIS PIECE OF PIPE IS STRANDED AND IS USED BY ATLANTIC OIL AS A SUCTION LINE (20 PSIG). THIS WAS A GRADE 1 LEAK IN THE MIDDLE OF A BEAN FIELD. PRODUCER ISOLATED PIPE TO MAKE SAFE, REPAIR DATE IS 3-27-09 TO INSTALL PLIDCO CLAMP. PIPELINE IS ON GATHERING LIST FOR SALE TO ATLANTIC OIL.
| 09-30033 | 300A | 141.03 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-23 |  |  |  | Steel/Wrought Iron |  | LUCERNE
| 09-30033-1 | 300A | 141.03 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-23 | [5 empty] | LUCERNE
| 09-30032-1 | 300B | 180.11 |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-11-16 | [5 empty] | HINKLEY
| 09-30031-1 | 300A | 203.02 |  |  |  | Fitting |  |  | Other | STEM PACKING | 2009-11-06 |  |  |  | Steel/Wrought Iron |  | HINKLEY
| 09-30031-1 | 300A | 203.02 |  | Transmission |  | Fitting |  |  | Unknown |  | 2009-11-16 | [5 empty] | HINKLEY
| 09-30031-1 | 300A | 203.02 |  | Transmission |  | Fitting | Valves |  | Unknown |  | 2009-11-16 | [5 empty] | HINKLEY
98 | 09-30030-1 | 300A | 218.73 | 4 | [7 empty] | 2009-11-16 |  |  |  | Steel/Wrought Iron |  | MOJAVE
| 09-30030-1 | 300A | 218.73 | 4 | Transmission |  | Fitting | Valves |  | Equipment Malfunction |  | 2009-11-16 | 2010-10-11 | Other | RESEAL THREADED FITTING | Steel/Wrought Iron |  | MOJAVE
| 09-30030-1 | 300A | 218.73 |  | Transmission |  | Fitting | Valves |  | Equipment Malfunction |  | 2009-11-16 | [5 empty] | MOJAVE
| 09-30029-1 | 300A | 218.69 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-16 | [5 empty] | MOJAVE
| 09-30028-1 | 300B | 168.39 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-16 | [5 empty] | HINKLEY
| 09-30028-1 | 300B | 168.39 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-16 | [5 empty] | HINKLEY
| 09-30027-1 | 300 | 149.64 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-09 | [5 empty] | BARSTOW
| 09-30026-1 | 300A | 154.74 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-09 | 2010-10-12 | Other | RESEAL FITTINGS | Steel/Wrought Iron |  | BARSTOW | REMOVED THREADED FITTINGS AND INSTALLED PIPE TAPE & THREAD SEALANT
| 09-30026-1 | 300 | 154.74 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-09 | [5 empty] | BARSTOW
| 09-30025-1 | 300A | 147.91 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-09 | 2010-10-12 | Other | RESEAL FITTINGS | Steel/Wrought Iron |  | BARSTOW | REMOVED FITTING AND APPLIED THREAD TOP & SEALANT
| 09-30025-1 | 300 | 147.91 |  | Transmission |  | Fitting |  |  | Equipment Malfunction |  | 2009-11-09 | [5 empty] | BARSTOW
| 09-30024-1 | 300 | 151.06 |  | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2009-11-09 | 2010-10-10 | Other | RESEAL FITTING | Steel/Wrought Iron |  | HINKLEY | EE REPAIRED LEAKING FITTINGS BY REMOVING AND APPLY PIPE DOPE AND SEALANT TAPE.
| 09-30024-1 | 300 | 151.06 |  | Transmission |  | Fitting |  | THREADED FITTING | Equipment Malfunction |  | 2009-11-09 | [5 empty] | HINKLEY
| 09-30023-1 | [10 empty] | 2009-10-28 | [5 empty] | DAGGET
| 09-30023-1 |  | 140.51 | [8 empty] | 2009-10-28 | [5 empty] | DAGGET
| 09-30022-1 | 300B | 148.19 |  | Transmission |  | Fitting | Valves | OTHER-SENSING LINES | Equipment Malfunction |  | 2009-10-28 |  |  |  | Steel/Wrought Iron |  | BARSTOW
| 09-30022-1 | 300B | 148.91 | [8 empty] | 2009-10-28 | [5 empty] | BARSTOW
| 09-30022-1 | 300B | 148.91 | [8 empty] | 2009-10-28 | [5 empty] | BARSTOW
| 09-30021-1 | [10 empty] | 2009-10-28 | [5 empty] | CALIFORNIA CITY
| 09-30021-1 |  | 203.05 | [8 empty] | 2009-10-28 | [5 empty] | CALIFORNIA CITY
| 09-30020-1 | 300B | [9 empty] | 2009-10-28 | [5 empty] | DAGGET
| 09-30020-1 | 300B | [9 empty] | 2009-10-28 | [5 empty] | DAGGET
| 09-30019-1 | 300B | 140.91 | [8 empty] | 2009-10-28 | [5 empty] | DAGGET
| 09-30019-1 | 300B | 140.91 | [8 empty] | 2009-10-28 | [5 empty] | DAGGET
| 09-30018-1 | 300B | 152.46 |  |  |  | Fitting | Mechanical Joint |  | Equipment Malfunction |  | 2009-10-28 |  |  |  | Steel/Wrought Iron |  | BARSTOW
| 09-30018-1 | 300B | [9 empty] | 2009-10-28 | [5 empty] | BARSTOW
| 09-30018-1 | 300B | 152.46 | [8 empty] | 2009-10-28 | [5 empty] | BARSTOW
| 09-30017-1 | 300A | 103.72 | [8 empty] | 2010-09-17
| 09-30017-1 | 300A | 103.72 | [8 empty] | 2009-09-01
| 09-30016-1 | 300A | 106.39 | 34 | Transmission |  | Fitting |  |  | Other | LOOSE CAP | 2009-09-01 | 2010-10-11 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | NEEDLES | LEAK IS APPROXIMATELY 200 YARDS SOUTH OF RAILROAD TRACKS ON WEST SIDE OF WASH BED, RESEALED COMPLETION PLUG AND CAP WITH TEFLOW TAPE. SOAP TESTED TO VERIFY REPAIR
| 09-30016-1 | 300A | 106.39 | [14 empty] | TOPOCK
| 09-30016-1 | 300A | 106.39 | 34 |  |  | Unknown |  |  | Unknown |  | 2009-09-01 |  |  |  | Steel/Wrought Iron |  | TOPOCK | LEAK IS APPROXIMATELY 200 YARDS SOUTH OF RAILROAD TRACKS ON WEST SIDE OF WASH BED, RESEALED COMPLETION PLUG & CAP WITH TAPE; SOAP TESTED TO VERIFY REPAIR.
| 09-30016-1 | 300A | 106.39 | [8 empty] | 2009-09-01 | [5 empty] | TOPOCK
| 09-30016-1 | 300A | 106.39 | [8 empty] | 2009-09-01
| 09-30015-1 | 300A | 72.4 | [8 empty] | 2009-09-04 | [5 empty] | TOPOCK
| 09-30015-1 | 300A | 72.4 | [8 empty] | 2009-09-04
| 09-30014-1 | 300A | 68.36 | [8 empty] | 2009-09-03 | [5 empty] | TOPOCK
| 09-30014-1 | 300A | 68.36 | [8 empty] | 2009-09-03
| 09-30013-1 | 300A | 59.29 | [8 empty] | 2009-09-03 | [5 empty] | TOPOCK
| 09-30013-1 | 300A | 59.29 | [8 empty] | 2009-09-03
| 09-30012-1 | 300A | 40.87 | 34 |  |  | Fitting |  |  | Unknown |  | 2010-09-02 |  |  |  | Steel/Wrought Iron |  | NEEDLES
| 09-30012-1 |  | 300A | 40.87 | [7 empty] | 2010-09-02
| 09-30012-1 | 300A | 40.87 | [8 empty] | 2009-09-01 | [5 empty] | TOPOCK
| 09-30012-1 | 300A | 40.87 | [8 empty] | 2009-09-01
| 09-30011-1 | 300A | 40.87 | [8 empty] | 2009-09-01 | [5 empty] | TOPOCK
| 09-30011-1 | 300A | 40.87 | [8 empty] | 2009-09-01
| 09-30010-1 | 300A | 51.5 | [9 empty] | 2010-09-03 |  |  |  |  | TOPOCK | SURVEYED STEM DURINGANNUAL SURVEY WITH AN HFI UNIT. UNABLE TO FIND LEAK. HEAD K058 RESURVEY AREA TO VERIFY THERE WAS NO LEAK
| 09-30010-1 | 300A | 51.5 | [8 empty] | 2009-09-02
| 09-30009-1 | 300A | 31.69 | 4 | Transmission |  | Longitudinal Weld |  |  | Weld Failure |  | 2009-09-02 | 2010-10-15 | Welded Sav-A-Valve - Weld |  | Steel/Wrought Iron |  | NEEDLES | REPAIR MADE BY FOLLOWING GAS STANARD A-53. USING 2" SAV-A-VALVE AS PER MIKE TEARE ISTRUCTIONS. ALSO FOLLOWED JO STANDARD 54134
| 09-30009-1 | 300A | 31.69 | [8 empty] | 2009-09-02 | [5 empty] | TOPOCK
| 09-30009-1 | 300A | 31.69 | [8 empty] | 2009-09-02
| 09-30008-1 | 300A | 2.04 | [8 empty] | 2009-08-31 | [5 empty] | TOPOCK
| 09-30008-1 | 300A | 2.04 | [8 empty] | 2009-08-31
98 | 09-30007-1 | 300A | 3.25 | 0.75 | Transmission >= 20% SMYS |  | Curb Valve |  |  | No/Deteriorated Pipe Dope |  | 2009-08-31 | 2011-04-28 | Mechanical Repair Fitting - Fitting |  | Steel-Other |  | NEEDLES | FIRE VALVE MARKED WITH YELLOW PAINT; REPLACED O-RINGS IN CAP
| 09-30007-1 | 300A | 3.25 | [8 empty] | 2009-08-31 | [5 empty] | TOPOCK | FIRE VALVE MARKED WITH YELLOW PAINT
| 09-30007-1 | 300A | 3.25 | [8 empty] | 2009-08-31
| 09-30006-1 | 300B | 284.62 | 34 | Transmission |  | Fitting | Other | FIRE VALVE |  |  | 2009-04-28 | 2009-07-24 |  |  | Steel/Wrought Iron |  | BAKERSFIELD | REPLACE CURB VALVE CAP; ATTENDED TO REPAIR FIRE VALVE. TIGHEN CAP, BUT IT SLILL LEAK. WOULD HAVE TO EXCAVATE TO MAIN AND CLOSE SERVICE TAP TO REPLACE FIRE VALVE CAP. 6/17/09
| 09-30006-1 | 300B | 284.62 | 34 | Transmission |  | Other |  | THE VALVE |  |  | 2009-04-28 | 2009-07-24 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | BAKERSFIELD | ATTENDED TO REPAIR FIRE VALVE. TIGHEN CAP, BUT IT SLILL LEAK. WOULD HAVE TO EXCAVATE TO MAIN AND CLOSE SERVICE TAP TO REPLACE FIRE VALVE CAP. 6/17/09
| 09-30005-1 | 300A | 284.69 | 34 | Transmission |  | Other |  | BLOW DOWN STACK | Material Failure |  | 2009-04-28 | 2009-07-23 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | BAKERSFIELD | REMOVED UNIBOLT CAP, CLEANED AND REPLACED CAP TO BLOW-DOWN STACK. STILL LEAKS. NEED TO REPLACE UNIBOLT CAP WITH A BLIND FLANGE. WORK REG # 152313
| 09-30005-1 | 300A | 284.69 | 34 | Transmission |  | Other |  | BLOW DOWN STACK |  |  | 2009-04-28 | 2009-07-23 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | BAKERSFIELD | REMOVED UNIBOLT CAP, CLEANED AND REPLACED CAP TO BLOW-DOWN STACK. STILL LEAKS. NEED TO REPLACE UNIBOLT CAP WITH A BLIND FLANGE. WORK REG # 152313
| 09-30004-1 | 300A | 256.21 | 34 | Transmission |  | Fitting |  |  | Material Failure |  | 2009-05-14 | 2009-06-26 | Other | REPLACE INSERTION METER WITH A BLIND FLANGE | Steel/Wrought Iron |  | ARVIN | M.P. 256.21 - A, THE INSERTION METER WAS REMOVED AND REPLACE WITH A 3" BLIND FLANGE. STOPPED GAS LEAK.
| 09-30004-1 | 300A | 256.21 | 34 | [7 empty] | 2009-05-14 | [5 empty] | ARVIN
| 09-30003-1 | 300B | 256.64 | 34 | Transmission |  | Fitting |  |  | Material Failure |  | 2009-05-14 | 2009-06-26 | Tighten Cap or Bolt | Soap and/or Tape | Steel/Wrought Iron |  | ARVIN | REMOVE INSERTION METERS AND REPLACED WITH 3" BLIND FLANGE. NO MORE LEAKS.
| 09-30003-1 | 300B | 256.64 | 34 | [7 empty] | 2009-05-14 | [5 empty] | ARVIN
| 09-30002-1 | 300 B | 354.01 | 34 |  |  | Valves |  |  |  |  | 2009-04-02 | 2009-08-12 | Mechanical Repair Fitting - Fitting |  |  |  | AVENAL | INSTALLED NEW CAP
| 09-30002-1 | 300 B | 354.01 | 34 |  |  | Valves |  |  |  |  | 2009-04-02 | 2009-08-12 | Mechanical Repair Fitting - Fitting |  |  |  | AVENAL | INSTALLED NEW CAP
| 09-30002-1 | 300 B | 354.01 | 34 |  |  | Valves |  |  |  |  | 2009-04-02 | [5 empty] | AVENAL
| 09-30001-1 | 300 B | 354.01 | 34 |  |  | Other |  | BLONDOWN STACK |  |  | 2009-04-02 | [5 empty] | AVENAL | LEAK DOWNGRADED FROM 2+ TO 3. WR#159.293 WILL ADDRESS WTHIS LEAK FOR CORRECTIVE MEASURES. THIS LEAK RESIDES WITHIN THE GATES OF KETTLEMAN COMPRESSOR STATION, THERE ARE BALLARDS AND NO SMOKING SIGNS AROUND LEAK.
| 09-30001-1 | 300 B | 354.01 | 34 |  |  | Other |  | BLOWDOWN STACK |  |  | 2009-04-02 | [5 empty] | AVENAL
| 09-22003-1 | 220 | 3.021 | [8 empty] | 2009-10-05 | [5 empty] | DIXON
| 09-22002-1 | 0600-06 | 0.6102 | 3 |  |  | Valves |  |  |  |  | 2009-10-02 | [5 empty] | DIXON | NO LEAK FOUND @ VALVE 2. SOAPED VALVE, BODY BLEED, & GREASE FITTINGS, NO LEAKS FOUND. 1-10-11 IXG4
| 09-22002-1 |  | 0.6102 | 3 |  |  | Valves |  |  |  |  | 2009-10-02 | [5 empty] | DIXON
| 09-22002-1 |  | 0.6102 | 3 |  |  | Valves |  |  |  |  | 2009-10-02 | [5 empty] | DIXON
| 09-22001-1 | 220 | 12.22 | 0.75 | Transmission |  | Valves |  |  | Other | SEE COMMENTS | 2009-10-02 | 2011-01-10 | Other | SEE COMMENTS | Steel/Wrought Iron |  | DIXON | INLET VALVE OFF, BLEEDING BY TO GUAGE TAP FITTING W/ LOOSE PLUG. GREASED VALVE IN OFF POSITION. TIGHTENED PLUG ON GAUGE TAP FITTING. ABANDONED SERVICE, NO UTR & LOCATION. VALVE REMAINS OFF W/ CAUTION TAG. IXG4 1-10-11
| 09-22001-1 |  |  | 3 |  |  | Valves |  |  |  |  | 2009-10-02 | [5 empty] | DIXON
| 09-22001-1 | [10 empty] | 2009-10-02 | [5 empty] | DIXON
96 | 09-20009-1 | 200C-6 | [9 empty] | 2009-10-12 | [5 empty] | RIO VISTA
| 09-20009-1 | 200C-6 | 1.3784 | 26 | Gathering |  | Valves |  |  | Other |  | 2009-10-12 | 2010-10-13 |  |  | Steel/Wrought Iron |  | RIO VISTA | WELL CUT-OFF AT CHURCH 1, RETIRED PIPE FROM CHURCH 1 TO CHURCH . SEE LEAK 09-20008-1 FOR SKETCH OF CUT-OFF
| 09-20009-1 | 200C-6 | 1.3784 |  |  |  | Valves |  |  |  |  | 2009-10-12 | [5 empty] | RIO VISTA | WELL CUT-OFF AT CHURCH 1, RETIRED PIPE FROM CHURCH 1 TO CHURCH . SEE LEAK 09-20008-1 FOR SKETCH OF CUT-OFF
| 09-20008-1 |  |  | 6 | Gathering | [6 empty] | 2009-10-12 | 2010-10-12 | Other | SEE COMMENTS LAST PAGE OF REPORT PAGE 3 OF 3 |  |  | RIO VISTA | GAS LEAK REPORTED, LEAK REPAIR CHANGED TO % L-200 @ CHUCH 1. BELL HOLE BACK FILLED PER JOE C REQUEST
| 09-20008-1 |  |  | 6 | Gathering | [6 empty] | 2009-10-12 |  | Other | SEE COMMENTS LAST PAGE OF REPORT PAGE 3 OF 3 |  |  | RIO VISTA | GAS LEAK REPORTED, LEAK REPAIR CHANGED TO % L-200 @ CHUCH 1. BELL HOLE BACK FILLED PER JOE C REQUEST
| 09-20007-1 |  |  | 4 | Gathering |  | Fitting |  |  | Other |  | 2009-10-12 | 2010-10-06 | Other | GREASED | Steel/Wrought Iron |  | RIO VISTA | TIGHTED, CLEANED, GREASED FITTING - CHECKED FROM LEAK, CHECK GAS & THIS IS V-B A BLOW DOWN VALVE 10-6-10
| 09-20007-1 | [5 empty] | Fitting |  |  |  |  | 2009-10-12 | 2010-10-06 | Other | GREASED |  |  | RIO VISTA | TIGHTED, CLEANED, GREASED FITTING - CHECKED FROM LEAK, CHECK GAS & THIS IS V-B A BLOW DOWN VALVE 10-6-10
| 09-20006-1 | 200 |  | 8 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2009-10-10 | 2010-10-09 | Other | 8" PLIDCO CLAMP | Steel/Wrought Iron |  | RIO VISTA | LEAK WAS LOCATED AND REPAIRED. CREW INSTALLED A 8" PLIDCO CLAMP. REPAIR WAS WRAPED AND BACK FILLED. SOAP TESTED @ LINE PRESSURE
| 09-20006-1 | 200 | [9 empty] | 2009-10-10 | 2010-10-09 | Other | 8" PLIDCO CLAMP |  |  | RIO VISTA | LEAK WAS LOCATED AND REPAIRED. CREW INSTALLED A 8" PLIDCO CLAMP. REPAIR WAS WRAPED AND BACK FILLED. SOAP TESTED @ LINE PRESSURE
| 09-20005-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2009-10-10 | 2010-10-09 | Other | 8" PLIDCO CLAMP SER# 3062926 | Steel/Wrought Iron |  | RIO VISTA | TESTED @ LINE PRESSURE
| 09-20005-1 | [10 empty] | 2009-10-10 | 2010-10-09 | Other | 8" PLIDCO CLAMP SER#3062926 |  |  | RIO VISTA | TESTED @ LINE PRESSURE
| 09-20004-1 |  |  | 3 | Gathering |  | Fitting |  |  | Equipment Malfunction |  | 2009-10-09 | 2009-10-10 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | RIO VISTA
| 09-20004-1 |  |  | 3 |  |  | Fitting |  |  | Equipment Malfunction |  | 2009-10-09 | 2009-10-10 | Mechanical Repair Fitting - Fitting |  |  |  | RIO VISTA
| 09-20002-1 | 200 | [9 empty] | 2009-08-25 | [5 empty] | RIO VISTA
| 09-20001-1 | 200 |  | 2 |  |  | Valves |  | 2" MUELLER VALVE FOR FEEDER LINE TO SUMMERSET REGS. |  |  | 2009-04-24 | [5 empty] | RIO VISTA | 2" MUELLER VALVE FOR FEEDER LINE TO SUMMERSET REGS.
| 09-19601-1 | 196 | 0.9527 | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2009-03-17 | 2009-05-14 | Other | RETIRE LINE 196 | Steel/Wrought Iron |  | LODI | REFER TO STOCKTON DIV. LEAK NO. 09-02038-1, 3/17/09
|  |  |  | 6 | Gathering | [7 empty] | 2009-05-14 | Other | RETIRE LINE 196 | Steel/Wrought Iron |  |  | REFER TO STOCKTON DIV. LEAK NO. 09-02038-1, 3/17/09
|  |  |  | 6 | Gathering | [7 empty] | 2009-05-14 | Other | RETIRE LINE 196 | Steel/Wrought Iron |  |  | REFER TO STOCKTON DIV. LEAK NO. 09-02038-1, 3/17/09
| 09-19607-1 | 196A | 9.92 | [8 empty] | 10/80/2009 | [5 empty] | ISLETON
| 09-19606-1 | 196A | 9.92 | [8 empty] | 2009-10-30 | [5 empty] | ISLETON
| 09-19605-1 | 196 | 0.0189 | [8 empty] | 2009-11-08 | [5 empty] | STOCKTON
| 09-19604 | 196A | 4.2489 | [8 empty] | 2010-11-03 | [5 empty] | RIO VISTA
| 09-19604-1 | 196 | [9 empty] | 2009-11-04 | [5 empty] | LODI
| 09-19603-6 | 196A | [9 empty] | 2010-11-03 | [5 empty] | RIO VISTA
| 09-19603-1 | 196 | 6.61 | [8 empty] | 2009-11-04 | [5 empty] | LODI
| 09-19601-1 | 196 | [9 empty] | 2009-04-08 | [5 empty] | LODI | REFER TO STOCKTON DIV. LEAK NO. 09-02038-1, 3/17/09 L196 PIPELINE SHUT-IN ON 4/9/09 (KING ISLAND)
| 09-02038-1 | [10 empty] | 2009-03-17 | [5 empty] | LODI
| 09-19101-1 | 191 | 5.43 | [8 empty] | 2009-05-29 | 2009-10-23 | Other | REPLACED BLOWDOWN STACK "O" RING |  |  | ANITOCH
| 09-19101-1 | 191 | 5.43 | [8 empty] | 2009-05-29 | [5 empty] | ANTIOCH
| 09-19001-1 | 190 | 0 | 12.75 |  |  | Other |  | GAUGE TAP |  |  | 2009-04-02 | 2009-06-08 | Mechanical Repair Fitting - Fitting |  |  |  | AVENAL
| 09-19001-1 | 190 | 0 | 12.75 |  |  | Other |  | GAUGE TAP |  |  | 2009-04-02 | 2009-06-08 | Mechanical Repair Fitting - Fitting |  |  |  | AVENAL
| 09-19001-1 | 190 | 0 | 12.75 |  |  | Other |  | GAUGE TAP |  |  | 2009-04-02 | [5 empty] | AVENAL
| 09-17703-1 | 177 |  | 10 | [7 empty] | 2009-09-03 | [5 empty] | CORNING
| 09-17702-1 | [10 empty] | 2009-06-22 | [5 empty] | CHICO
| 09-17702-1 | 177 |  | 0.25 | Transmission |  | Fitting | Valves |  | Other |  | 2009-06-22 | 2009-09-16 | Other | TIGHTENED FITTING - EXERCISED VALVE | Steel/Wrought Iron |  | CHICO | EXERCISED VALVE AND TIGHTENED 1/4" TUBE FITTING, SOAP TEST - NO LEAKS
| 09-11402-1 | [5 empty] | Other |  | THREADED CAP |  |  | 2009-07-08 | 2009-11-03 | Tighten Cap or Bolt |  |  |  | OAKLEY
| 09-11402-1 | [5 empty] | Other |  | THREADED CAP |  |  | 2009-07-08 | [5 empty] | OAKLEY
| 09-17701-1 | 177 |  | 1 | Transmission |  | Valves |  |  | Unknown |  | 2009-06-22 | 2009-09-16 | Other | OPERATED VALVE - STEM LEAK STOPPED | Steel/Wrought Iron |  | CHICO | EXERCISED TWO MOST NORTH VALVES IN FRAME AND COVERS ON THE NORTH EAST CORNER OF FELL STATION. LEAKS STOPPED 9-16-04 MWR4
| 09-16901-1 | 169 |  | 0.5 | Transmission |  | Fitting |  |  | Construction Defect |  | 2009-06-22 | 2009-11-06 | Other | INSTALLED NEW SEALANT TAPE ON BUSHING SOAP TEST "NO LEAKS" | Steel/Wrought Iron |  | CHICO | INSTALLED NEW SEALANT TAPE ON BUSHING - SOAP TEST "NO LEAKS"
| 09-16901-1 | [10 empty] | 2009-06-22 | [5 empty] | CHICO
| 09-13601-1 | 136 |  | 0.5 | Transmission |  | Fitting |  |  | Unknown |  | 2009-06-22 | 2009-11-06 | Other | TIGHTENED FITTING SOAP TESTED "NO LEAKS" | Steel/Wrought Iron |  | CHICO | TIGHTENED FITTINGS. SOAP TEST - NO LEAKS
| 09-13601-1 | [10 empty] | 2009-06-22 | [5 empty] | CHICO
| 09-13102-1 | 1312 | 0.54 | [8 empty] | 2009-10-30 | [5 empty] | RIO VISTA
| 09-06505-1 | [5 empty] | Valves | Other | 4 ABOVE GRADE |  |  | 2009-06-05 | [5 empty] | CONCORD
09-06505-1
| 09-06504-1 | [5 empty] | Mechanical Joint | Valves | 7 ABOVE GRADE |  |  | 2009-06-05 | [5 empty] | CONCORD
09-06504-1
| 09-06503-1 | [5 empty] | Valves | Other | 1 ABOVE GRADE |  |  | 2009-06-04 | [5 empty] | CONCORD
09-06502-1
| 09-06502-1 | [5 empty] | Mechanical Joint | Valves | 4 ABOVE GRADE |  |  | 2009-06-04 | [5 empty] | CONCORD
| 09-06501-1 | [5 empty] | Mechanical Joint | Valves | 8 ABOVE GRADE |  |  | 2009-06-10 | [5 empty] | CONCORD
09-06501-1
| 09-06501-1 | [5 empty] | Valves | Mechanical Joint | 8 ABOVE GRADE |  |  | 2009-06-10 | [5 empty] | CONCORD
| 09-06502-1 | [5 empty] | Valves | Mechanical Joint | 4 ABOVE GRADE |  |  | 2009-06-04 | [5 empty] | CONCORD
| 09-06503-1 | [5 empty] | Valves | Mechanical Joint | 1 ABOVE GRADE |  |  | 2009-06-04 | [5 empty] | CONCORD
| 09-06504-1 | [5 empty] | Valves | Mechanical Joint | 7 ABOVE GRADE |  |  | 2009-06-05 | [5 empty] | CONCORD
| 09-06505-1 | [16 empty] | CONCORD
98 | 09-05704-1 | 57A | 16.64 | 16 | Transmission >= 20% SMYS |  | Unknown |  |  | Material Failure |  | 2009-04-20 | 2010-12-03 | Mechanical Repair Fitting - Fitting |  | Cast Iron |  | BRENTWOOD | REPLACED UPPER HOSING OF MTR TUBE
98 | 09-05704-B | 57A | 16.64 | 16 | Transmission >= 20% SMYS |  | Unknown |  |  | Material Failure |  | 2009-04-20 | 2010-12-23 | Mechanical Repair Fitting - Fitting |  | Cast Iron |  | BRENTWOOD | REPLACED UPPER HOUSING OF METER TUBE
| 09-05704-1 | [5 empty] | Unknown | Other | LEAK ON SR. FITTING |  |  | 2009-04-20 | [5 empty] | BRENTWOOD
98 | 09-05704-B | 57A | 16.64 | 16 | Transmission >= 20% SMYS |  | Unknown |  |  | Material Failure |  | 2009-04-20 | 2010-12-23 | Mechanical Repair Fitting - Fitting | REPLACED UPPER HOUSING OF METER TUBE | Cast Iron |  | BRENTWOOD
| 09-05703-1 | 57B | 16.57 | 0.75 |  |  | Fitting |  | REPAIRED 7/22/09 | Other | LOOSE THREADED FITTING | 2009-04-20 | 2009-07-22 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | BRENTWOOD | DIASEMBLE & REDOPED FITTINGS
| 09-05702-1 | 114 |  |  |  |  | Unknown |  |  | Other | LEAKY FITTINGS | 2009-04-20 | 2009-07-08 | Tighten Cap or Bolt |  |  |  | BRENTWOOD | VALVE 70 AT BRENTWOOD TERMINAL; DISASSEMBLED POWER GAS PIPE FITTINGS AND CLEANED THREADS AND REASSEMBLED WITH TEFLON TAPE AND PIPE DOPE
| 03-11401-1 | 114 | 20.68 |  | Transmission |  | Physical/Mechanical Joint |  |  | Atmospheric Corrosion |  | 2003-09-19 | 2005-05-07 | Weld Over Sleeve or Can | REMOVED VALVE |  |  | N. OF LIVERMORE | REPAIRED BY REPLACING VALVE W/ SECTION OF PIPE OFFER #7054807
| 09-05607-1 | [5 empty] | Valves | Mechanical Joint | 4 ABOVE GRADE UPDATED 11-9-10 |  |  | 2009-06-17 | [5 empty] | WINTERS
| 09-05608-1 | [5 empty] | Mechanical Joint | Valves | 2 ABOVE GRADE |  |  | 2009-06-17 | [5 empty] | WINTERS
| 09-05606-1 | 56A | 0.004 |  |  |  | Mechanical Joint | Valves | 2 ABOVE GROUND |  |  | 2009-06-15 | 2010-04-22 | Deactivated Entire Service | REPLACE ENTIRE SERVICE |  |  | WINTERS
| 09-05605-1 | [5 empty] | Mechanical Joint | Valves | 2 ABOVE GRADE |  |  | 2009-06-16 | [5 empty] | WINTERS
| 09-05604-1 | [5 empty] | Mechanical Joint | Valves | 2 ABOVE GRADE |  |  | 2009-06-16 | [5 empty] | WINTERS
| 09-05603-1 | [5 empty] | Mechanical Joint | Valves | 6 ABOVE GRADE UPDATED 11-9-2010 |  |  | 2009-06-16 | [5 empty] | WINTERS
| 09-05604-1 | [5 empty] | Mechanical Joint | Valves | 2 ABOVE GRADE UPDATED 11-9-10 |  |  | 2009-06-16 | [5 empty] | WINTERS
| 09-05605-1 | [5 empty] | Mechanical Joint | Valves | 2 ABOVE GRADE |  |  | 2009-06-16 | [5 empty] | WINTERS
| 09-05607-1 | [5 empty] | Mechanical Joint | Valves | 4 ABOVE GRADE |  |  | 2009-06-17 | [5 empty] | WINTERS
| 09-05608-1 | [5 empty] | Mechanical Joint | Valves | 2 ABOVE GRADE |  |  | 2009-06-17 | [5 empty] | WINTERS
| 09-05603-1 | [5 empty] | Mechanical Joint | Valves | 6 ABOVE GRADE UPDATED 11-9-10 |  |  | 2009-06-16 | [5 empty] | WINTERS
| 09-05603-1 | [5 empty] | Mechanical Joint | Valves | 6 ABOVE GRADE |  |  | 2009-06-16 | [5 empty] | WINTERS
| 09-05604-1 | [5 empty] | Mechanical Joint | Valves | 2 ABOVE GRADE |  |  | 2009-06-16 | [5 empty] | WINTERS
| 09-05605-1 | [5 empty] | Mechanical Joint | Valves | 2 ABOVE GRADE |  |  | 2009-06-16 | [5 empty] | WINTERS
| 09-05606-1 | [5 empty] | Mechanical Joint | Valves | 2 ABOVE GROUND |  |  | 2009-06-15 | [5 empty] | WINTERS
| 09-05607-1 | [5 empty] | Mechanical Joint | Valves | 4 ABOVE GRADE |  |  | 2009-06-16 | [5 empty] | WINTERS
| 09-05608-1 | [5 empty] | Mechanical Joint | Valves | 2 ABOVE GRADE |  |  | 2009-06-17 | [5 empty] | WINTERS
| 09-05602-1 | 56A |  |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-04-30
| 09-05601-1 | 56A |  |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-04-30 |  |  |  | Steel/Wrought Iron
| 09-05601-1 | 56A |  |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-04-30 |  |  |  | Steel/Wrought Iron
| 09-05602-1 | 56A |  |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-04-30
| 09-05601-1 | 56A |  |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-04-30 |  |  |  | Steel/Wrought Iron
|  | 56A |  |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-04-30 |  |  |  | Steel/Wrought Iron
| 09-00503-1 | [5 empty] | Fitting | Valves |  | Equipment Malfunction |  | 2009-05-18 |  |  |  | Steel/Wrought Iron |  | ANTIOCH
| 09-00502-1 |  |  | 2 | Transmission |  | Fitting | Valves |  | Equipment Malfunction |  | 2009-05-18 | 2009-08-13 | Tighten Cap or Bolt | SOAP AND/OR TAPE | Steel/Wrought Iron |  | ANTIOCH
Steel/Wrought Iron
| 09-00502-1 |  |  |  | Transmission |  | Fitting | Valves |  | Equipment Malfunction |  | 2009-05-18 | 2009-08-13 | Tighten Cap or Bolt | SOAP AND/OR TAPE | Steel/Wrought Iron |  | ANTIOCH
| 09-00502-1 |  |  |  | Transmission |  | Fitting | Valves |  | Equipment Malfunction |  | 2009-05-18 |  |  |  | Steel/Wrought Iron |  | ANTIOCH
| 09-00501-1 | SP5 | 4.28 | 30 | Distribution Main | TRANSMISSION | Valves |  |  | Equipment Malfunction |  | 2009-05-12 |  |  |  | Steel/Wrought Iron |  | ANTIOCH
| 09-00501-1 | SP5 | 4.28 | 30 | Distribution Main | TRANSMISSION | Valves |  |  | Equipment Malfunction |  | 2009-05-12 |  |  |  | Steel/Wrought Iron |  | ANTIOCH
| 09-00401-1 | [10 empty] | 2009-01-13 | 2009-02-10 | Mechanical Repair Fitting - Fitting |  |  |  | OAKLEY
| 09-00401-1 | SP4Z | 8.18 | [8 empty] | 2009-01-13 | [5 empty] | OAKLEY
| 09-00302-1 | 191 |  |  | Transmission |  | Valves | Unknown | REFERENCE G.T. STATION LEAK SURVEY REPORT, @ LOS MEDANOS 15 LEAKS @ THIS LOCATION. ITEMIZED LIST. | Unknown |  | 2009-06-03 |  |  |  | Steel/Wrought Iron |  | PITTSBURG
| 09-00302-1 | 191 | [9 empty] | 2009-06-03 | [5 empty] | PITTSBURG
| 09-00301-1 | SP3 | 176.16 |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-05-28 |  |  |  | Steel/Wrought Iron |  | CONCORD
| 09-00301-1 | SP3 | 176.16 |  | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-05-28 |  |  |  | Steel/Wrought Iron |  | CONCORD
| 09-00204-1 | [7 empty] | REPAIRED 7/3/09 |  |  | 2009-04-06 | 2009-07-03 | Other | STEM PACKING |  |  |  | VALVE IS LEAKING AROUND STEM PACKING TIGHTENED PACKING AND GREASED VALVE STOPPED LEAK.
| 09-00204-1 | [10 empty] | 2009-04-06
| 09-00204-1 | [10 empty] | 2009-04-06 | 2009-07-03 | Other | STEM PACKING |  |  |  | VALVE IS LEAKING AROUND STEM PACKING TIGHTENED PACKING AND GREASED VALVE STOPPED LEAK.
| 09-00203-1 | [7 empty] | REPAIRED 7/3/09 |  |  | 2009-03-09 | 2009-07-03 | Other | SENIOR ORIFICE METER GREASE FITTING AND ORIFICE PLATE GASKET |  |  | TRACY
| 09-00203-1 | [7 empty] | REPAIRED 7/3/09 |  |  | 2009-03-09 | 2009-07-03 | Other | SENIOR ORIFICE METER GREASE FITTING AND ORIFICE PLATE GASKET |  |  | TRACY
| 09-00203-1 | [10 empty] | 2009-03-09 | [5 empty] | TRACY
| 09-00202-1 | 2 |  | 0.75 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2009-03-09 | 2009-04-20 | Tighten Cap or Bolt | SOAP AND/OR TAPE | Steel/Wrought Iron |  | TRACY
| 09-00202-1 | [10 empty] | 2009-03-09 | [5 empty] | TRACY
| 09-00201-1 | [7 empty] | REPAIRED 7/3/09 |  |  | 2009-03-09 | 2009-07-03 | Other | GAS SUPPLY REGULATOR GASKET AND TUBING FITTING |  |  | TRACY
| 09-00201-1 | [10 empty] | 2009-03-09 | [5 empty] | TRACY
| 10-40102-1 | 401 | 197.8 |  | Transmission |  | Valves |  |  | Other | VLV STEM | 2010-10-27 |  |  |  | Steel/Wrought Iron |  | MAXWELL | WORK REQUEST MADE OUT EACH TIME TO GREASE TO STOP LEAK; WORK REQUEST MADE OUT EACH TIME TO GREASE TO STOP LEAK.
| 10-40101-1 | 401 | 197.8 |  | Transmission |  | Valves |  |  | Other | VLV STEM | 2010-06-28 |  |  |  | Steel/Wrought Iron |  | MAXWELL
| 10-40101-1 | 401 | 197.8 |  | Transmission |  | Valves |  |  | Other | VLV STEM | 2010-06-28 |  |  |  | Steel/Wrought Iron |  | MAXWELL
| 10-40101-1 | 401 | 197.8 |  | Transmission |  | Valves |  |  | Other | VALVE STEM | 2009-06-02 | [5 empty] | MAXWELL
| 10-40001-1 | 400 | 4864 | [8 empty] | 2010-05-05 | [5 empty] | FALL RIVER
| 10-40002-1 | 400 | 164.4 | 36 | Transmission |  |  |  |  | Unknown |  | 2010-08-27 |  |  |  | Steel/Wrought Iron |  | SOUR GRASS ROAD ORLAND | THIS LEAK IS UNDER GROUND NEXT TO M.L. VALVE AND PIPING FOR BLOWING OUT DRIPS OF "P.L. FLUIDS." CAN'T FIND INFO ON NEAR VALVE WAS PUT INTO SERVICE.
| 10-30201-1 | 302 | 2.37 | 4 | Gathering |  | Unknown | Other | SUSPECT INTERNAL CORROSION | Internal Corrosion |  | 2010-05-13 | 2010-05-26 | Other | RETIRED | Steel/Wrought Iron |  | GRIMES CA | NEAR V-290 - LINE RETIRED
| 10-10801-1 | 108 | 43.4762 | [8 empty] | 2010-08-13 | [5 empty] | LODI
| 10-10801-1 |  |  |  | Transmission |  | Valves |  |  | Other | LOOSE FITTING TIGHTEN FITTING | 2010-08-12 | 2010-09-05 | Other | GREASE & TIGHTEN FITTINGS | Steel/Wrought Iron |  | LODI | GREASED VALVE TO STOP LEAK. REMOVED 2IN PLUG. PUT PIPE DOPE ON PLUG AND INSTALLED AND TIGHTENED.
| 10-19601-1 | 196 |  |  | Transmission |  | Regulator |  |  | Other | LOOSE RACK | 2010-08-13 | 2010-09-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron | GASKET | LODI | TIGHTEN BOLTS ON DIAPHRAGM OF REGULATOR TO STOP LEAK. W/R ATTACHED.
| 10-19601-1 | [10 empty] | 2010-08-13 | [5 empty] | LODI
| 10-20001-1 | 200 |  |  | Gathering |  | Unknown |  |  | Unknown |  | 2010-06-22 | 2010-10-08 | Other | 8" PLIDCO CLAMP SER. # 3092307 | Other |  | N/E OF RIO VISTA | PIN HOLE ON BOTTOM OF MAIN; SOAP TESTED @ LINE PRESSURE
96 | 10-20001-1 | 200C7-3 | 34 |  | Gathering |  | Unknown |  |  | Unknown |  | 2010-06-22 | 2010-10-06 | Other |  | Other |  | FAIRFIELD
| 10-20001-1 | 200 |  |  | Gathering |  | Unknown |  |  | Unknown |  | 2010-06-22 | 2010-10-08 | Other | 8" PLIDCO CLAMP SER. #3092307 | Other | STEEL | N/E OF RIO VISTA | SOAP TESTEED @ LINE PRESSURE
| 10-20001-1 | 200 |  |  | Gathering |  | Unknown |  |  | Unknown |  | 2010-06-22 |  |  |  | Other | STEEL | N/E OF RIO VISTA
| 10-20002-1 | 200B3-3 | 1.387 | [8 empty] | 2010-08-10 | [5 empty] | RIO VISTA
96 | 10-20003-1 |  |  | 4 | Transmission >= 20% SMYS |  | Other |  | BLOW DOWN STACK | Other | MECH. JOINT | 2010-08-10 | 2011-03-12 |  |  |  |  | RIO VISTA | BLOW DOWN STACK LEAKING AT CAP; CAN ON TOP OF BLOW DOWN STACK LEAKING AT O-RING; PULLED JOINT APART CLEANED O-RING GROVE AND FACE OF FLANGE, REINSTALLED O-RING WITH LITHIUM GREASE.
96 | 10-20003-1 |  |  |  | Transmission >= 20% SMYS |  | Other |  | BLOW DOWN STACK | Other | MECH. JOINT | 2010-08-10 | 2011-03-12 | Mechanical Repair Fitting - Fitting |  |  |  | RIO VISTA | CAP ON TOP OF BLOW DOWN STACK LEAKING AT O-RING; PULLED JOINT APART CLEANED O-RING GROVE AND FACE OF FLANGE, REINSTALLED O-RING WITH LITHIUM GREASE.
96 | 10-20003-1 |  |  | 4 | Transmission >= 20% SMYS |  | Other |  | BLOW DOWN STACK | Other | MECH. JOINT | 2010-08-10 | 2011-03-12 | Mechanical Repair Fitting - Fitting |  |  |  | RIO VISTA | CAP ON TOP OF BLOW DOWN STACK LEAKING AT O-RING; PULLED JOINT APART CLEANED O-RING GROVE AND FACE OF FLANGE, REINSTALLED O-RING WITH LITHIUM GREASE.
96 | 10-20003-1 | [10 empty] | 2010-06-10 | [5 empty] | RIO VISTA
| 10-20003-1 | 200 | 1.4832 | [8 empty] | 2010-08-10 | [5 empty] | RIO VISTA
| 10-20004-1 | 200 | 0.7827 | [8 empty] | 2010-08-10 | [5 empty] | RIO VISTA | GASKET + STEM PACKING ON ORIFICE METER
| 10-21001-1 |  |  | 12 | Transmission |  | Valves |  |  | Material Failure |  | 2010-08-13 | 2010-10-22 | Other | REPLACE STEM SEALS JACK | Steel/Wrought Iron |  | DIXON | REPAIRED IN IGTS 10/26/10; REMAINING STEM SEALS IN ... REPLACED STEM SEALS. CWF4
| 10-21001-1 |  |  | 12 | Transmission |  | Valves |  |  | Material Failure |  | 2010-08-13 | 2010-10-22 | Other | REPLACE STEM SEALS JACK | Steel/Wrought Iron |  | DIXON | REPAIRED IN IGIS 10/22/10; REMAINING STEM SEALS IN ... REPLACED STEM SEALS CWF4 10/22/10
| 10-21001-1 | 210W |  | 12 | Transmission |  | Valves |  |  | Material Failure |  | 2010-08-13 | 2010-10-22 | Other | REPLACE STEM SEALS JACK | Steel/Wrought Iron |  | DIXON | L-210 W; REMAINING STEM SEALS ...
96 | 10-21001-1 | 1 | [9 empty] | 2010-08-13 | [5 empty] | DIXON
96 | 10-21001-1 | 1 |  | 12 | Transmission >= 20% SMYS |  |  |  |  | Material Failure |  | 2010-08-13 | 2010-10-22 | Mechanical Repair Fitting - Fitting |  |  |  | DIXON
| 10-21001-1 |  |  | 12 | Transmission |  | Valves |  |  | Material Failure |  | 2010-08-13 | 2010-10-22 | Other | REPLACE STEM SEALS JACK |  |  | DIXON | L-210 W; REMAINING STEM SEALS ...
| 10-21001-1 | 210W |  | 12 | Transmission |  | Valves |  |  | Material Failure |  | 2010-08-13 | [5 empty] | DIXON
| 10-21001-1 | 210W | [9 empty] | 2010-08-13 | [5 empty] | DIXON | L - 210 W
| 10-21001-1 | 210 | 1.4103 | [8 empty] | 2010-08-13 | [5 empty] | DIXON | L210B MP 1.4163; L - 210 W
96 | 10-22001-1 |  |  | 6 | Transmission >= 20% SMYS |  | Other Mechanical Joint |  |  | Other |  | 2010-08-13 | 2011-03-19 | Other |  | Steel/Wrought Iron |  | DIXON | REMOVED SPOOL PIECE INSTALL NEW GASKETS; REMOVED SPOOL PIECE CLEANED GASKET FACES AND REINSTALLED SPOOL PIECE WITH NEW GASKETS. BLOW DOWN STACK FOR VALVE, A, L, J.
| 10-22001-1 | 220 | 0.0397 | [8 empty] | 2010-08-13 | [5 empty] | DIXON | L220 MP 0.0397
| 10-00202-1 | 2 | 59.5 | 26 | Transmission |  | Valves |  |  | Other | PLUG | 2010-04-19 | 2010-04-19 | Other | CLEAN AND RECAP PLUG | Steel/Wrought Iron |  | FIREBAUGH
| 10-00501-1 | SP5 |  |  |  |  | Other |  | BLOWDOWN STACK CLOSURE |  |  | 2010-05-05 | [5 empty] | ANTIOCH
| 10-05601-1 | 056B-2 | 0.02 |  | Gathering | TRANSMISSION; STORAGE | Mechanical Joint | Other | 2 ABOVE GRADE. SEE PIPELINE PATROL REPORT FOR DETAILS ABOUT LEAKS. READINGS ABOVE INDICATE THE LEAK OF HIGHEST CONCENTRATION! |  |  | 2010-04-21 |  |  |  | Steel/Wrought Iron |  | WINTERS | SEE PIPELINE PATROL REPORT FOR DETAILS ABOUT LEAKS. READINGS INDICATE THE HIGHEST CONCENTRATION!
| 10-05601-1 | 056B-2 | 0.02 |  | Gathering | TRANSMISSION; STORAGE | Mechanical Joint | Other | 2 ABOVE GRADE SEE PIPELINE PATROL REPORT FOR DETAILS ABOUT LEAKS. READINGS INDICATE THE HIGHEST CONCENTRATION! |  |  | 2010-04-21 |  |  |  | Steel/Wrought Iron |  | WINTERS | SEE PIPELINE PATROL REPORT FOR DETAILS ABOUT LEAKS. READINGS INDICATE THE HIGHEST CONCENTRATION!
| 10-11401-1 | [5 empty] | Unknown |  |  | Unknown |  | 2010-04-05 |  |  |  | Steel/Wrought Iron |  | BRENTWOOD | CALLED JEROD KUNLYA. HE DIDN'T KNOW WHAT THE INSTR. SHOULD BE. WILL CHECK ON THIS LEAK # AND WILL GET BACK TO NLE
96 | 10-11402-1 | 114 |  | 22 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | External Corrosion |  | 2010-06-25 | 2010-07-01 | Replace TP Main |  |  |  | LIVERMORE | REPLACE 11' OF 4" TP MAIN
| 10-11402-1 | 114 | 26.25 | 22 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2010-05-25 | 2010-07-01 | Replace TP Main |  | Steel/Wrought Iron |  | LIVERMORE | REPLACED 11' 4" TP MAIN
| 10-11402-1 | 114 | 26.25 | 22 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2010-05-25 | 2010-07-01 | Replace TP Main |  | Steel/Wrought Iron |  | LIVERMORE | REPLACED 11' 4" TP MAIN
| 10-22201-1 | 222 | 0 | [8 empty] | 2010-05-19 | [5 empty] | TRACY
| 10-22201-1 | 222 | 0 | [8 empty] | 2010-05-19 | 2010-05-25 | Other | GREASE FITTING LEAK.. GREASED FITTING STOPPED LEAK |  |  | TRACY | TRACY STATION GREASE FITTING LEAKING (GREASED VALVE)
96 | 10-30301-1 | 303 | 7.8 | 0.75 | Transmission >= 20% SMYS |  | Line Valve |  |  | Equipment Malfunction |  | 2010-11-04 | 2010-11-24 | Deactivated Partial Service |  | Steel-Other |  | BRENTWOOD | RMVED CHROMATOGRAPH PROBE CLOSED VLV INS
98 | 10-30301-B | 303 | 7.8 | 0.75 | Transmission >= 20% SMYS |  | Line Valve |  |  | Equipment Malfunction |  | 2010-11-04 | 2010-11-24 | Deactivated Partial Service |  | Steel-Other |  | BRENTWOOD | REMOVED CHROMATOGRAPH PROBE & CLOSED VALVE & INSTALLED PLUG
| 10-31601-1 | 316-20 | 0.77 |  | Transmission | [6 empty] | 2010-05-03 | 2010-05-24 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | BRENTWOOD | L-316 VALVE PIT V-22 (TIGHTEN PIPE PLUG)
| 10-16401-1 | 164 | 0.34 | 10 | Transmission |  | Mechanical Joint |  |  | Material Failure |  | 2010-04-07 | 2010-04-09 | Bell Joint Clamp | REPLACE DIST. MAIN <100 FT. | Steel/Wrought Iron |  | COALINGA | RT 164 MP 0.34; FOUND A 10" DRESSER COUPLING LEAKING AT BOTTOM. CUT A 82" SECTION TO REMOVE COUPLING AND REPLACED IT WITH A 82" OF TESTED 10" PIPE.
| 10-16401-1 | 104 | 0.34 | 10 | Transmission |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2010-04-07 | 2010-04-08 | Replace Dist Main < 100 ft |  | Steel/Wrought Iron |  |  | FOUND A 10" DRESSER COUPLING LEAKING AT BOTTOM. CUT A 82" SECTION TO REMOVE COUPLING AND REPLACED IT WITH A 82" OF TESTED 10" PIPE.
| 10-30001-1 | 300B | 10.5 | 0.5 | Transmission |  | Other Welds |  |  | Unknown |  | 2010-04-06 |  |  |  | Cast/Ductile Iron
98 | 10-30001-2 | 300B | 10.5 | 0.75 | Transmission >= 20% SMYS |  | Curb Valve |  |  | Other |  | 2010-10-25 | 2011-04-27 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | NEEDLES | POSTED IN IGIS 4-28-11; ULS GAUGE TOP VALVE TIGHTEN FITTING; TIGHTEN
| 10-30001-2 | 300B | 10.5 | 0.75 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2010-10-25 |  |  |  | Steel/Wrought Iron |  | NEEDLES TOPOCK DISTRICT PIPELINE | DUPLICATE RE'D 11/10/10
| 10-30001-3 | 300B | 10.47 | 0.25 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2010-10-25 |  |  |  | Steel/Wrought Iron |  | NEEDLES TOPOCK DISTRICT PIPELINE
| 10-30001-4 | 300B | 10.47 | 6 | Transmission |  | Other |  | BOLTED FLANGE | Other | GASKET | 2010-10-25 |  |  |  | Steel/Wrought Iron |  | NEEDLES TOPOCK DISTRICT PIPELINE
| 10-30001-2 | 300B | 10.5 | 0.75 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2010-10-25 |  |  |  | Steel/Wrought Iron |  | NEEDLES TOPOCK DISTRICT PIPELINE
98 | 10-30001-3 | 300B | 10.47 | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-10-25 | 2011-04-27 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | NEEDLES | TIGHTEN VALVE
98 | 10-30001-2 | 300B | 10.5 | 0.75 | Transmission >= 20% SMYS |  | Curb Valve |  |  | Other |  | 2010-10-25 | 2011-04-27 | Tee Fused Over Defect - Plastic |  | Steel/Wrought Iron |  | NEEDLES | U/S GAUGE TAP VALVE TIGHTEN FITTING
98 | 10-30001-3 | 300B | 10.47 | 0.75 | Transmission >= 20% SMYS |  | Fitting |  |  | Other | TIGHTEN CAP | 2010-10-25 | 2011-04-27 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | NEEDLES | TIGHTEN VALVE; TIGHTEN VALVE
| 10-30001-3 | 300B | 10.47 | 0.25 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2010-10-25 |  |  |  | Steel/Wrought Iron |  | NEEDLES TOPOCK DISTRICT PIPELINE
| 10-30001-4 | 300B | 10.47 | 6 | Transmission |  | Other |  | BOLTED FLANGE | Other | GASKET | 2010-10-25 |  |  |  | Steel/Wrought Iron |  | NEEDLES TOPOCK DISTRICT PIPELINE
98 | 10-30017-1 | 300A | 0.64 | 16 | Transmission |  | Mechanical Joint |  |  | Other | MISALIGNED FLANGE | 2010-09-20 | 2010-10-09 | Other | INSTALLED NEW GASKET | Steel/Wrought Iron |  | NEEDLES TOPOCK DISTRICT PIPELINE
| 10-30017-1 | 300A | [9 empty] | 2010-09-20 | 2010-10-11 | [5 empty] | REPAIRED VARIOUS FITTINGS AROUND STATION - SEE STATION LEAK SURVEY REPORT
| 10-30017-1 | 300A |  | 34 | Branch Service |  | Fitting | Valves |  | Unknown |  | 2010-09-20 |  |  |  | Steel/Wrought Iron |  | TOPOCK
96 | 10-30018-1 | 300B | 71.96 | [8 empty] | 2010-10-18 | [5 empty] | NEEDLES
| 10-30018-1 | 300B | 71.96 | 0.75 | Transmission |  | Valves |  |  | Unknown |  | 2010-10-18 |  |  |  | Steel/Wrought Iron |  | TOPOCK DISTRICT
98 | 10-30019-7 | 300A | 40.87 | 1 | Transmission |  |  |  |  | Other |  | 2010-09-02 | [5 empty] | NEEDLES
| 10-30019-1 | 300A | 40.87 | 0.75 | Transmission |  | Valves |  |  | Other | STEM PACKING | 2010-09-02 |  |  |  | Steel/Wrought Iron |  | NEEDLES TOPOCK DISTRICT PIPELINE
| 10-30019-2 | 300A | 40.87 | 0.75 | Transmission |  | Valves |  |  | Other | STEAM LEAKING | 2010-09-02 |  |  |  | Steel/Wrought Iron |  | NEEDLES TOPOCK DISTRICT PIPELINE
| 10-30019-3 | 300A | 40.87 | 0.75 | Transmission |  | Valves |  |  | Other | STEM PACKING | 2010-09-02 |  |  |  | Steel/Wrought Iron |  | NEEDLES - TOPOCK DISTRICT PIPELINE
| 10-30019-4 | 300A | 40.87 | 0.75 | Transmission |  | Valves |  |  | Other | STEM PACKING | 2010-09-02 |  |  |  | Steel/Wrought Iron |  | NEEDLES TOPOCK DISTRICT PIPELINE
| 10-30019-5 | 300A | 40.87 | 0.75 | Transmission |  | Valves |  |  | Other | STEM PACKING | 2010-09-02 |  |  |  | Steel/Wrought Iron |  | NEEDLES TOPOCK DISTRICT PIPELINE
| 10-30019-6 | 300A | 40.97 | 34 | Transmission |  | Other |  | METER | Other | STEM PACKING | 2010-09-02 |  |  |  | Steel/Wrought Iron |  | NEEDLE TOPOCK DISTRICT PIPELINE
| 10-30019-7 | 300A | 40.87 | 1 | Transmission |  | Valves |  |  | Other | LOOSE FITTING | 2010-09-02 |  |  |  | Steel/Wrought Iron |  | NEEDLES - TOPOCK DISTRICT PIPELINE
| 10-31402-1 | 314 | 24.78 | 10 | Transmission |  | Unknown |  |  | Unknown |  | 2010-08-26 |  |  |  | Steel/Wrought Iron |  | ORO GRANDE
| 10-31403-1 | 314 | 24.72 | 10 | Transmission |  | Other |  | FITTINGS | Equipment Malfunction |  | 2010-08-26 | [5 empty] | ORO GRANDE
| 10-20601-1 | 101 | 0.12 | 6 |  |  | Fitting | Other | GREASE FITTING |  |  | 2010-04-29 | [5 empty] | MILPITAS
[5 empty] | Transmission | [7 empty] | 2010-05-24 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  |  | PUMPED GREASE FITTING WITH GREASE. THIS WAS A GREASE FITTING ISSUE.
96 | 11-21002-1 | 400 | 242.85 | 0.75 | Transmission |  | Line Valve |  |  | Material Failure |  | 2011-02-03 | 2011-02-04 | Other | SENSING LINE VALVE | Steel-Other |  | CAPAY | CLOSED PIN-OFF TEE ON MAIN. INSTALLED NEW 3/4" VALVE.
96 | 11-21002-1 | 400 | 242.85 | [8 empty] | 2011-02-03 |  |  |  | Steel-Other |  | CAPAY | LEAK AT VALVE PLUG ON 3/4" UPSTREAM SENSING LINE
96 | 11-21001-1 | 400 | 197.83 | 12 | Transmission >= 20% SMYS |  | Other Mechanical Joint |  |  | Equipment Malfunction |  | 2011-01-25 | 2011-01-26 | Mechanical Repair Fitting - Fitting |  | Steel-Other |  | MAXWELL | V-152 WAS INJECTED WITH SEALANT BY TEAM INDUSTRIAL SERVICES; HOV-152 E-1 GAS COOLER DISCH. VALVE; LEAK WAS MACHINED FLANGE FACE OF VALVE; SEALANT WAS INJECTED INTO FLANGE BOLT HOLES AT EVERY BOLT. INJECTION VALVES WERE INSTALLED FOR INJECTION & LATER REMOVED & HOLES PLUGGED.
|  |  |  | 0.75 | Transmission >= 20% SMYS |  | Line Valve |  |  | Material Failure |  |  |  | Other | SENSING LINE VALVE | Steel-Other |  |  | REPLACED 3/4" U/S/ SENSING LINE VALVE ON TAP TO CACHE CREEK CASINO.
242.85
242.85
96 | 11-22001-1 | 302 | [9 empty] | 2011-05-04 | [5 empty] | COLUSA
96 | 11-22002-B | 302 | [9 empty] | 2011-04-04 | [5 empty] | MERIDIAN
96 | 11-22003-B | [10 empty] | 2011-04-06 | [5 empty] | ARBUCKLE
96 | 11-22003-B | [10 empty] | 2011-04-06 | [5 empty] | ARBUCKLE
96 | 11-23001-1 | [10 empty] | 2011-01-03 | [5 empty] | LODI | REGULATOR ON GAS SAVER CIRCUIT ON VALVE #76
[5 empty] | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Material Failure
96 | 11-23002-1 | 114 | [16 empty] | KNIFE RIVER CONSTRUCTION EMPLOYEE OPERATING A D-8 CAT PUNCTURED 16" LINE 114 OPERATING AT APPROC 350PSI. KNIFE RIVER CONSTRUCTION DID NOT REQUEST A STAND BY
96 | 11-23002-B | 114 | 3.18 | 16 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | Digin |  | 2011-06-13 | 2011-06-14 | Replace #TP Main < 50 ft |  | Steel-Other |  | RIO VISTA | CUTT IN NEW PIECE 16" PIPE; EXITING PIPE GB SIMS X35
98 | 11-51002-B |  | 242.4BA | 2 | Transmission >= 20% SMYS |  | Line Valve |  |  |  |  | 2011-04-21 | 2011-05-06 | Tighten Cap/Bolt - Fitting | GREASED-OTHER | Steel-Other |  | TEHACHAPI | GREASED, TIGHTENED BUTTON HEAD
98 | 11-51002-B |  | 242.4BA | 2 | Transmission >= 20% SMYS |  | Line Valve |  |  |  |  | 2011-04-21 |  |  |  | Steel-Other |  | TEHACHAPI
300A
98 | 11-52001-1 |  |  |  | Transmission >= 20% SMYS |  | Other |  | VOLUME BOOSTER BAD | Material Failure |  | 2011-01-15 | 2011-01-15 | Other | REBUILD VOLUME BOOSTER | Steel-Other |  | COLMA | REPAIRED VOLUME BOOSTER; REBUILD VOLUME BOOSTER SOAP TEST ON VALVE 14 ACTUATOR
98 | 11-53001-1 | 300A | 462.19 | 2 | Transmission |  | Other |  |  | Inspection Only |  | 2011-01-13 |  |  |  | Steel-Other |  | GILROY
98 | 11-53001-1 | 300A | 462.19 | 2 | Transmission |  | Other |  |  | Inspection Only |  | 2011-01-13 |  |  |  | Steel-Other |  | GILROY
|  | 300A | 462.19 | 2 | Transmission |  | Other |  |  | Inspection Only |  | 2011-01-13 |  |  |  | Steel-Other |  | GILROY
96 | 11-55001-1 | 300A | 0.64 | 0.75 | Transmission >= 20% SMYS |  | Curb Valve |  |  | Other |  | 2011-02-04 | 2011-02-07 | Other |  | Steel-Other |  | NEEDLES
98 | 11-55001-1 | 300A | 0.64 | 0.75 | Transmission >= 20% SMYS |  | Curb Valve |  |  | Other | HARDENED O-RINGS | 2011-02-04 | 2011-02-07 | Other | INSTALLED NEW STEM, CAP BORINGS ON CURB STOP VALVE | Steel-Other |  | NEEDLES | CLOSED CURB STOP VALVE, VENTED DOWN STREAM PRESSURE, REMOVED & INSTALLED NEW STEM CAP & O-RINGS FOR CURB STOP VALVE; SKETCH SHOWS AERIAL VIEW OF LEAK LOCATION AND SIDE VIEW OF VALVE POSITION. VALVE BOX COVER WAS ABOUT 6" BELOW GROUND LEVEL.
98 | 11-55001-B | 300A | 0.64 | [8 empty] | 2011-02-04 | [5 empty] | NEEDLES
98 | 11-55002-A | 300A | 10.85 | 0.5 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2011-04-18 |  |  |  | Steel/Wrought Iron |  | NEEDLES DISTRICT
|  | 197B | 4.3825 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | WOODBRIDGE | NO LEAK DIG TO INSTALL WATER SRV. (STANDBY); DIG FOR WATER SRV. ONLY (STANDBY).
|  | 197A | 39.1915 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN ANDREAS
|  | 197B | 4.1652 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | LODI
|  | 197 | 16.34 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 8057736
197B
|  | 197C | 5.1187 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | M/O CLEMENTS
|  | 197C | 15.7465 | 0.1 | Transmission | [13 empty] | 2" VENT LINE IS 44" DEEP.
|  | 197C | 15.4375 | 10 | Transmission | [12 empty] | IONE | STOCKTON DIV; NO ASBESTOS DETECTED IN WRAP.
|  | 197C | 16.7328 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | IONE
|  | 197A | 39.9323 | [12 empty] | Steel/Wrought Iron |  |  | DIVISION: STOCKTON. SO #7053706-07. CUT & CAP TP MAIN AT 39.98 TRANSFER TP PIPE SOUTH TO MP 40.78 INTO DIST. MAIN.
|  | 197 | 4.9985 | 10 | [14 empty] | DIVISION: STOCKTON
|  | 197C | 14.7 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | IONE | DIVISION: STOCKTON; POTHOLE LOCATION 12' 5 W OF MILE MARKER 14.7.
|  | 197 | 14.7 | 6 | [11 empty] | Steel/Wrought Iron |  | IONE | POTHOLE 6" ON N/E CORNER OF HWY 88 AND BUENAVISTA RD.
|  | 197C | 14.7 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | IONE | POTHOLE LOCATION 23' NORTH OF MILE MARKER 14.7
|  | 197C | 14.7 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | IONE | POTHOLE 4 FEET SOUTH OF ARIAI MILE MARKER 14.7.
|  | 197B |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  | WOODBRIDGE | MAIL TO KEVIN ARMATO WHO CAN FORWARD TO RAY BAUTISTA.
|  | 197C | 11.4199 | 10 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 197C | 11.5003 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | IONE
|  | 197C | 11.827 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | IONE
|  | 197C | 13.9593 | 10 | Transmission | [10 empty] | Steel/Wrought Iron |  | IONE
|  |  |  | 8.625 | [11 empty] | Steel/Wrought Iron |  |  | JOB #6050086; EXPOSED WHERE 4" X-TIE WAS CUT OUT.
|  | 200 |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIO VISTA | PM 41294206; LINE 200 16"
[16 empty] | Steel/Wrought Iron |  |  | TRIGUIERO JUNCTION #7065907.
|  | 200-37 |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | SACRAMENTO DIV. JOB 7047686. 6" MUELLER NEAR MARKS 4 DETAIL #1.
|  | 200-18 |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 7047686 DETAIL 2. SACRAMENTO DIV.
|  | 200-462 |  | 6.625 | Gathering | [13 empty] | JOB# 7047686 DETAIL 2. SACRAMENTO DIV.
|  | 200-37 |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB 7047686 48' NORTH OF VALVE 30. SACRAMENTO DIVISION;
|  | 200-37 |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB #7047686 AT VALVE 30. SACRAMENTO DIV.
|  | 200-13 |  | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 7047686 AT 8" MUELLER DETAIL 3. SACRAMENTO DIV.
|  | 200-53 |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB 7047686 6" TOW AT TRIGUEIRO JET DETAIL 4. SACRAMENTO DIV.
|  | 200A-2 | 1.7256 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | JOB 7047686 8" MUELLER TRIGEUIRO JET DETAIL 4. SACRAMENTO DIV.
|  | 200-13 |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB 7047686 AT 4" X 8" TIE, DETAIL 5.
|  | 200-13 |  | 8.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB 7047686 AT 4" X 8" TIE, DETAIL 5. SACRAMENTO DIV.
|  | 200A11 | 4.4718 |  | Transmission | [12 empty] | RIO VISTA | SO #7047613. C/O 3/4 SERVICE.
|  | 200-388 |  | 0.03 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIO VISTA | INSTALL RISER. C/O RISER AT WELL SHADE. #7048366.
|  | 200A | 1.1647 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | JOB #7047445. SO SIDE HIWAY 12.
|  | 200A-2 | 8.4 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | JOB# 7047445. NO SIDE HIWAY 2.
|  |  |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron
|  | 200C9-1 | 0.0004 | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB #7045171. FSE 46+63 AT VALVE 242.
|  | 200C9-2 | 0.2489 | 6.625 | Gathering | [13 empty] | F.S.E 4+95
|  | 200C9.3 | 0 | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron
|  | 200C9-2 | 24.9994 | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron
|  | 200C9.3 | 0.45 | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB #7645171. F.S. 26 + 63.
|  | 200C9.5 | 0 | 3.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | F.S. 23+68
|  | 200C9.4 | 0 |  | Gathering | [10 empty] | Steel/Wrought Iron |  |  | FSA 22+26
|  | 200C9.5 | 0.45 | 3.5 | Gathering | [10 empty] | Steel/Wrought Iron
|  | 200C9.6 | 0.18 | 3.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | KROUTH 16-1 RISER LOC.
|  | 200C9.4 | 0.42 | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | F.S. 39+45
|  | 200C9.6 | 0 | 3.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | F.S. 39+45
|  | STUB 7611 | 0.0504 | 0.08 | Transmission | [10 empty] | Steel/Wrought Iron |  | RIO VISTA | SO #7045290; CUT + CAP 6" STL MAIN, HP.
|  |  | 1.0715 | 0.08 | [13 empty] | RIO VISTA | SO# 7045290; CUT + CAP 8" STL MAIN HP.
|  | 200C7-3 | 0.2902 |  | Transmission | [10 empty] | Steel/Wrought Iron |  | RIO VISTA | SO# 7045290. VALVE LOCATION - 241; C/O AND CAP 8" STL.
|  | 200A15-3 | 0.1457 | 4.5 | [14 empty] | JOB# 7045130. FS 8+35 CUT OFF POINT CHURCH 11; INSTALLED 4" CAP WITH 1" SAV-A-VALVE LEFT IN PLACE AFTER PIGGING. REMOVED 4X4X4 TEE FS 8+35.
|  | 200A-15 | 0 | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 7045130. F.S. 0+05 RISER LOCATION. CHURCH 11.
|  | 200A15-3 | 0.0114 | [12 empty] | Steel/Wrought Iron |  |  | SO#7045130.
|  | 200A15-1 | [16 empty] | SO# 7045130.
|  |  | 0.38 | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | JOB 7045130. FS 0+05 RISER LOCATION. CHURCH 1-12. ROUTE: 200A15-3
|  | 200A15-3 | 0.1234 | [12 empty] | Steel/Wrought Iron |  |  | SO# 7045130
|  |  |  | 8.62 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 6067864. LOCATION AT 8" TIE POINT. 6' HOT TAP LOCATION.
|  |  | 0.47 | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | RT: 200B2-2
|  | 200B3-3 | 0.88 | 12.75 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 6067864. 6" HOT TAP LOCATION; INFORMATION X-RAY. NO PITTING.
|  | 200-405 | 0 | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 6067864. LOCATION AT 4" TIE POINT.
|  | 200 |  | 8.62 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 6067864 AT 8" TIE-IN LOCATION.
|  | 200A7-1 |  | 8.62 | [14 empty] | JOB#7042806. CUT-OFF POINT AT TEE FOR HIGHLAND WILLOWS SPRINGS 3-12 GAS WELL.
|  | 200 |  | 2 | [11 empty] | Steel/Wrought Iron |  | RIO VISTA | SO#6083624. RETIRED HANSON 7 WELL. CUT-OFF LOCATION RIO VISTA.
|  | 200B3-7 |  | 16 | [11 empty] | Steel/Wrought Iron |  |  | HT 3" HOT TAP TEE LOCATION. 85' NORTH OF VALVE 101 & 102. PIT WALL. JOB # 6059584
|  | 200 |  | 3.5 | [14 empty] | JOB#6021544. DOLIER PRESSLEY VALVE 111.
|  | 200 |  | 3.5 | [14 empty] | JOB#6021544. DOLIER PRESSLEY #5 GAS WELL RISER.
|  | 200A |  | 6.62 | [11 empty] | Steel/Wrought Iron |  |  | JOB#6021544. LOC EHIGH #10 GAS WELL. RISER LOC F.S. A 8+50.
|  | 200A |  | 6.62 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 6021544. LOC EHIGH #10 CUTOFF. F.S. 29+70 A 0+02.
|  | 200 |  |  | Gathering | [6 empty] | 2001-04-11 | 2001-04-11 |  | WRAP PIPE |  |  | RIO VISTA | WRAPPED 3 FEET OF 6" LINE ZOO.
| 01-20001-1 | 200 | 0.42 | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2001-03-02 | 2001-03-14 | Other | LEAK CLAMP |  |  | RIO VISTA | 6" LINE 200 EAST OF AKER 1-12. INSTALL 6" PLIDCO LEAK CLAMP; INSTALLED LEAK CLAMP. WRAPPED 30' OF PIPE.
|  | 200 |  | 6 | Gathering | [6 empty] | 2000-08-14 | 2000-08-14 | Other | WRAP REPAIR |  |  | RIO VISTA | VALVE 60 6" LINE 200; NO PIPE DAMAGE. JUST PIPE WRAP REMOVED.
|  | 200 |  | 3 | Gathering | [6 empty] | 2000-08-14 | 2000-08-14 |  |  |  |  | RIO VISTA | 3" LINE 200. NO REPAIRS. INSPECTION ONLY; NO DAMAGE PIPE LINE UNCOVERED
|  | 200 |  | 6 | [7 empty] | 2000-08-14 | 2000-08-14 |  |  |  |  | RIO VISTA | 6" LINE 200. NO REPAIRS. INSPECTION ONLY; NO DAMAGE - PIPE LINE UNCOVERED.
|  |  | 1.4189 | 12.75 | [11 empty] | Steel/Wrought Iron |  |  | ROUTE: 200A9-2; JOB#7046069. LOC#1.
[5 empty] | Gathering | [10 empty] | Steel/Wrought Iron |  |  | ROUTE: 200-45; JOB# 7046069. LOC#2.
|  |  |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 7046069. LOC#3; ROUTE STUB8039
|  |  |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB #7046069. LOC#4; ROUTE: STUB8027
|  |  |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB#7046069. LOC#5; ROUTE STUB8035
|  |  |  | 6.625 | [11 empty] | Steel/Wrought Iron |  |  | JOB#7046069. 6" LINE FROM VALVE 39 TRIGUERO JET.; ROUTE- 200-53-1
|  | STUB8043 |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB#7046069. LOC#7.
|  | STUB8046 | 0.52 | 6.625 | [11 empty] | Steel/Wrought Iron |  |  | 6" LINE FROM VALVE 51 TRIGUERO JET. LOC #6 #8 #9.
|  | STUB8047 | 0.0065 | 12.75 | [14 empty] | 12" LINE FROM VALVE 50 TRIGUERO JET.
|  | 200B4-1 | 0.9645 | 10.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 7046069. LOC#10.
|  | STUB050 | 0.6887 | 8.625 | Gathering | [13 empty] | JOB 7046069. LOC #11. VALVE 66 SIDE.
|  |  |  | 6.625 | [11 empty] | Steel/Wrought Iron |  |  | LOC#12.
|  |  |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 7046063. LOC#13 AT VALVE 71.
|  | STUB8057 | 0.0008 | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB #7040059
|  | 200.39 |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 7046067. LOC#14.
|  | STUB8061 |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 7046069. LOC#15; INSTALLED BLIND FLANGE. ROMVED 4" 400 FLANGE... AND 54" OF 188 ... PIPE.
|  |  |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 7046069. LOC#17.
|  |  |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron
|  |  |  | 6.625 | [11 empty] | Steel/Wrought Iron
|  | STUB8067 |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB 7046069. LOC#19.
|  | STUB8070 |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB 7046069. LOC#20.
|  |  |  | 2.375 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | LOC #21. JOB# 7046069. VALVE 57 & 57 AT RIO VISTA TOWN REG. STA; INSTALLED 2" SOCKET WELD CAP. REMOVED 35' OF 2" PIPE. INSTALLED 2" STEEL PLUG SA.
|  | STUB8071 | 1.3453 | 10.75 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 70046069. LOC#22.
|  | STUB8072. |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | LOB# 7046069. LOC#23.
|  | 200A14-3 | 0.2791 | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 7046069. LOC#25.
|  | 200-71 |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 7046069. LOC 26.
|  | 200-208 |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 7046069. LOC 27. 3" HOT TAP FOR RELIEF DROWN COMP STA.
|  | 200B1-8 | 0.0149 | 10.75 | [11 empty] | Steel/Wrought Iron |  |  | JOB#7046069. LOC 28. 10" HOT TAP; XRAY INFO SHOTS SHOWN. NO VARIATION IN WALL THICKNESS.
| 05-20002-1 |  |  | 6.625 | Gathering |  |  |  |  | Internal Corrosion | [5 empty] | Steel/Wrought Iron |  | RIO VISTA | JOB# 7055530-05. BUBBLES IN FIELD; RETIRED 396 FEET 6" MAIN TO NEIL HAMILTON #4 GAS WELL. POSSIBLE DRIP LINE FARMER SAID IT WAS OLD SERVICE LINE.
|  | 200A14-7 | [16 empty] | JOB 6098643. RGVU189 RISER LOCATION; RETIRED RGVU 189.
JOB 6098643 AT LOC OF V221. STUB8225; RETIRED RVGU #184. INSTALLED 3" 600# BLIND FLANGE.
|  | 200C4-5 | 0.553 | 6.625 | [8 empty] | 2005-07-27 | Other | INSTALL NEW PIPE & ANGLE |  |  | RIO VISTA | S.O. 8072235 PSRS 16925. DENTED PIPE AT DITCH OVER-CROSSING. REPLACED SECTION WITH NEW PIPE; REPLACED ANGLE & SECTION OF PIPE DUE TO DENT IN PIPE BELOW ANDLE NORTH SIDE OF DITCH. CPS FILE #R080113A.
|  | 200-389 | [16 empty] | SO# 7052765.
|  |  | 1.5604 | [12 empty] | Steel/Wrought Iron |  |  | SO# 7062485; DIST RIO VISTA #20 7062485-07. STUB8831.
|  | 2000-6 | 0.0002 | [15 empty] | SO#7062485; DIST RIO VISTA SO #7062485-07, STUB8830
|  | 200-13 |  | 8 | [11 empty] | Steel/Wrought Iron |  |  | DISTRICT: RIO VISTA. SO#8079859-07.
|  | 200A15-2 | 0.4104 | 6 | Transmission | [8 empty] | Deactivate #TP Main |  | Steel/Wrought Iron |  |  | #SO 30610398; REOVED 4' SECTION OF 6" ON T.P. FOR ISOLATION & ABANDONMENT. SEALED OPEN ENDS OF PIPE W/ 6" STP PIPE CAP (STEEL) HOT TIE IN, X-RAY WELD, & RE-WRAP MAIN W/ STACK WRAP. (LAX STYLE) - 5' COVER ON MAIN.
|  | 200A15-2 | 0.0567 | 6 | Gathering | [7 empty] | 2008-02-05 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  |  | PM 30610398; BACK GROUND .280 CAN 3' LONG.
|  | 200 | 0.0017 | [15 empty] | PM 30604263. 10% MASTER METER. RP DEEP "A".
|  |  |  | 10 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | 10", 450# LINE USED FOR ROSETTO MASTER METER. "DEEP A". AS BUILT ON JOB# 30604263.
|  |  | 0.1617 | [15 empty] | SO# 30610498. ROUTE: 200C5-4
|  | 200 | 0 | 2 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | STUB10702. JOB#30608863; GATHERING LINE RETIRED AT V-109 @ LINE 114.
|  | 200 | 0.75 | 2 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB#30608863 MCCORMACK; GATHERING LINE RETIRED AT MCCORMACK3.
|  |  |  | 4 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB 30608863. MCCORMACK 5; GATHERING LINE RETIRED AT MCCORMACK 5. RISER REMOVED.
|  | 200 |  | 2 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB 30608863. ANDERSON 29; GATHERING LINE RETIRED AT ANDERSON 29.
|  | 200B4-1 | 0.0138 | 10 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 3061968; RECONNECTED L-200 12" WITH L-200 10" BY CROSS TIE WITH 2" STEEL. BOTH LINES PRIOR WERE TEMPORARILY ISOLATED, RE-CONNECTED FOR GAS FLOW. NOTES SEE AS- BUILT ON 2" TIE-IN PIECE FOR CORRECT DIMENSIONS.
|  | 200A-1 | 1.2963 | 1 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | DISTRICT RIO VISTA. JOB# 30619687-10; CREW C/O REMOVED 11' OF 1" LINE FROM L-200 THAT WAS NOT IN USE IN MARKS STA.
|  | 200A9-2 | 0.304 |  | Single Service | [13 empty] | DISTRICT: RIO VISTA. MARKS JOB # 30619687-10; CREW C/O AND REMOVED 10" PIPE AND V-25 CREW ALSO REMOVED BLOW DOWN.
|  | 200B4-1 | 0.32 | 10 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | DISTRICT: RIO VISTA. MARKS JOB# 30619687 (ABANDONED). DEACTIVATED; C/O PIPE, V-19, V-51 AND V-24.
|  | 200-53 | 0.0009 | 4 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | DISTRICT: RIO VISTA. MARKS JOB# 30619687 DEACTIVATED; CREW C/O 13'+/- PIPE AND REMOVED V-22 AND V-31.
|  |  | 0.016 | 3 | Gathering | [10 empty] | Steel/Wrought Iron |  | RIO VISTA | PM 30610001; RT: 200 66-LT; CUT OFF RISER.
|  |  | 0.8695 | 3 | Gathering | [10 empty] | Steel/Wrought Iron |  | RIO VISTA | PM 30610001; RT: 200 66-LT MP 0.8693; STUB10719 MP 0.4796; CUT OFF 2500 ' OF 3" PIPE GOING FROM MCCORMACK #1 TO WELL PAD #4. WIRE FOR CATHOTIC PROTECTION IN ABANDON PIPE. RISER CUT-OFF. CUT OFF 3" CAP. 4'6" COVER ON PIPE.
|  | 209 | 0.0022 | 4.5 | Transmission | [13 empty] | JOHNS MANSVILLE MTR & REG STA. SO#7050514. PSRS#14755
|  | 210D | 0 | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | DIXON AREA SOLANO COUNTY | LAMBIC POWER PLANT PIPELINE U-3 LINE 210B TIE IN POINT.
|  | 210D | 0 | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | DIXON AREA SOLANO COUNTY | LAMBIC POWER PLANT PIPE LINE 6" TIE TO EXISTING REACTIVATE PIPELINE. SO 7042717.
|  | 210D | 0.02 | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | DIXON AREA SOLANO COUNTY. | LAMBIC POWER PLANT PIPELINE. TIE-IN REACTIVATED 6" PIPE NORTH OF DAN VERTON VALVE LOT. SO 7042717; COORDINATE SYSTEM UTM ZONE 10 NORTH DATUM NAD 1983 (CONUS) FEET.
|  | 210D | 0.02 | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | DIXON AREA SOLANO COUNTY | SO 7042717. LAMBIC POWER PLANT PIPELINE. TIE IN REACTIVATED 6" PIPE IN DENWERTON VALVE LOT SOUTH OF NORTH FENCE LINE.
|  | 210D | 0.04 | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | DIXON AREA SOLANO COUNTY | SO 7042717. LAMBIC POWER PLANT PIPELINE. TIE IN REACTIVATED 6" PIPE IN DENWERTON VALVE LOT NORTH OF SOUTH FENCE LINE
|  | 210D | 0.66 | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | DIXON AREA SOLANO COUNTY
|  | 210D | 0.9 | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | DIXON AREA SOLANO COUNTY | SO 7042717. LAMBIC POWER PLANT PIPELINE. 6" TIE IN TO REACTIVATED PIPELINE NORTH AT RAILROAD TRACKS.
|  | 210D | 0.9 | 3.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO 7042717. LAMBIC POWER PLANT PIPELINE. 3" TO 6" TIE IN NORTH OF RAILROAD TRACKS. REACTIVATED PIPELINES.
|  | 210D | 0.92 | 3.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | DIXON AREA SOLANO COUNTY | SO 7042717. LAMBIC POWER PLANT PIPELINE. 3" TO 6" TIE IN SOUTH OF RAILROAD TRACKS. REACTIVATED PIPELINES.
|  | 210D | 0.92 | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | DIXON AREA SOLANO COUNTY | SO 7042717. LAMBIC POWER PLANT PIPELINE. 6" TIE-IN TO REACTIVATED PIPELINE SOUTH OF RAILROAD TRACKS.
|  | 210D | 1.41 | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | DIXON AREA SOLANO COUNTY | SO 7042717. LAMBIC POWER PLANT PIPELINE. 6" REACTIVATED PIPELINE NORTH CONNECTION TO V-1 SOUTH OF CAL PINE'S NORTH FENCE LINE.
|  | 210D | 1.41 | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | DIXON AREA SOLANO COUNTY | SO 7042717. LAMBIC POWER PLANT PIPELINE. 6" REACTIVATED PIPELINE SOUTH CONNECTION TO U-1 SOUTH OF CALPINE'S NORTH FENCELINE.
|  | 210D | 1.4 | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | DIXON AREA SOLANO COUNTY | SO 7042717. LAMBIC POWER PLANT PIPELINE. 6" REACTIVATED PIPELINE SEGMENT RECONNECTION SOUTH OF CALPINE'S NORTH FENCELINE.
|  | 210D | 1.41 | 6.25 | Transmission | [10 empty] | Steel/Wrought Iron |  | DIXON AREA SOLANO COUNTY | SO 7042717. LAMBIC POWER PLANT PIPELINE. 6" REACTIVATED PIPELINE SEGMENT RECONNECTION SOUTH OF CALPINE'S NORTH FENCELINE.
|  | 210D | 1.43 | 6.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | DIXON AREA SOLANO COUNTY | SO 7042717. LAMBIC POWER PLANT PIPELINE. 6" REACTIVATED PIPELINE CONNECTION TO NEW PIPE TO METER SET SOUTH OF CALPINE'S NORTH FENCELINE.
|  | 210A | 2.03 | 32 | Transmission | [10 empty] | Steel/Wrought Iron |  | DIXON AREA SOLANO COUNTY | GOOSE HAVEN POWER PLANT HOT TAP LOCATION
|  | 210A | 8.08 | 32 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 6088663
|  | 210A |  | 32 | Transmission | [10 empty] | Steel/Wrought Iron |  | 7 MILES S/E VACAVILLE | S.O. 7043312. CREED POWER PLANT HOT TAP LOCATION.
|  | 210A |  | 32 | Transmission | [10 empty] | Steel/Wrought Iron |  | 7 MILES S/E VACAVILLE | S.O. 7043312. CREED POWER PLANT HOT TAP LOCATION.
|  | 210A | 20.22 | 10 | Transmission | [6 empty] | 2003-10-28 |  | Replaced TP Main |  | Steel/Wrought Iron |  | CORDELIA | INSTALLED 10" TDW BOTTOW TAP TO FEED NEW 2" MAIN.
|  | 210A | 15 | 32 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | JOB 8067236 WEST OF BECK AVE. SOUTH SIDE OF RR TRACK CROSSING. INCLUDE W/ POST ESTIMATE PAPERWORK. INSTALLED ETS IN LITTLE FINK ON 32" MAIN LOCATED LITTLE FINK AT VENT STACK AND LINE MARKER AT RR RIGHT OF WAY FENCE. GOUGE AREAS REPAIRED BY GRINDING & MAG PARTICLE TESTING. GOUGED CIRCUMFERENTIAL WELD X-RAYS AND FOUND GOOD. 27" COVER FROM FENCE TO 90 DEGREE ELL THEN WEST FOR 50'. ORIGINAL COVER WAS 60".
| 00-53133-1 | 210A | 18.08 | 32 | Transmission |  | Body of Pipe |  |  | Digin |  | 2000-12-26 | 2000-12-26 | Other | REPLACE 30' OF PIPE | Steel/Wrought Iron |  | CORDELIA | 30' OF 32" A-1333-01 EMER STOCK X-60 HYP ROD USED IN REPAIR & PRE-HEAT; 30' OF PRE-TEST EMER. STOCK 32" A 1333/01. X-RAY TIE-IN WELD #: 2 GOOD CMT.
|  | 210A | 21.89 | 10 | Transmission | [6 empty] | 2003-10-28 |  | Replace TP Main |  | Steel/Wrought Iron |  |  | INSTALLED TDW BOTTOM TAP FITTING FOR TIE IN TO NEW 24" MAIN.
|  | 210 | 0 | 3.5 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 7040907. DETAIL #2 VALVE #1.
|  | 210D | 0.9 | 23.5 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 7040907. LOC#1 NORTH SIDE SNRR.
|  | 210D | 0.92 | 3.5 | [11 empty] | Steel/Wrought Iron |  |  | JOB 7040907. LOC#1 SOUTH SIDE SNRR.
|  | 210B | 20.3 | 16 | [11 empty] | Steel/Wrought Iron |  |  | DIVISION: SACRAMENTO. #7058608-07. TIE-IN POINT AT 16". STA. 12A00 TIE IN AT 16".
|  | 210 |  | 3.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | RTESTUB8482, MP 0.0007. RTE STUB8483, MP 0.0007. SRC RTE 210A, MP 8.0848. SRCRTE 210B, MP 7.5119. SO 6098883-06. DIV SACRAMENTO; INSTALLED (2) 3" BLIND FLANGE.
|  | 210B | 21.89 | 16 | Transmission | [6 empty] | 2003-11-01 |  | Replace TP Main |  | Steel/Wrought Iron |  | CORDELIA | SO# 7033657-04; CUT IN 16" TEE AND M.L. VALVE FOR CROSS TIE TO NEW 24" LINE 210A
|  | 210B | 20.22 | 16 | Transmission | [6 empty] | 2003-11-01 |  | Replace TP Main |  | Steel/Wrought Iron |  | CORDELIA | SO# 7033657-04; CUT IN 16" TEE AND M.L. VALVE FOR CROSS TIE TO NEW 24" LINE 210A.
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  | 0.0411 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7056387. HWY 113 CROSSING.
|  | 210B | 7.51 | 16 | [11 empty] | TR 418 |  |  | JOB# 6088663
|  | 210C | 3.62 | 18 | [8 empty] | 2000-09-29 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  |  | NORTH BAY DIV.
|  | 210A | 23 | 10 | Transmission | [6 empty] | 2007-10-05 | 2007-10-05 | Other | PROTOL | Steel/Wrought Iron |  | AMERICAN CANYON | CONTRACTOR DIGGING TO EXPOSE 10" TRANS. MAIN GOUGED 10" TRANS GAS LINE WITH PICK (HAND); DID NOT SEE CONTRACTOR HIT MAIN. CONTRACTOR IS NOT ADMITTING TO IT BUT IT WAS DONE WHILE EXPOSING MAIN. ERCON (PG+E CONTRACTOR) WAS BILLED/PAID FOR DAMAGE REPAIRS. ACTUAL COSTS WERE DEDUCTED FROM FINAL INVOICE FROM ERCON. 2ND DAY OF JOB DID NOT SEE EVIDENCE OF MARKS; DIGGING TO EXPOSE MAIN.
|  |  | 0.0001 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DF10031. PM#30664024; INSTALLED NEW V-A, V-B, V-1 & V-2 @ CORNER OF TODD RD & STONY POINT RD. SANTA ROSA PM 30664024 L-210 MP 47.39.
|  | 21H | 8.4 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PIPE DOES NOT HAVE ANY WRAP LEFT ON IT.
|  | 021A | 14.7051 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  | NAPA | DIVISION: NORTH BAY. SO#7053647-07
| 98-05017-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1998-06-19 | 1998-07-07 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | SAN RAFAEL | DRILLED & VENTED-INSTALLED 8" SKINNER LE
|  |  |  | 10 | Distribution Feeder Main | [6 empty] | 1987-03-26 |  |  |  | Steel/Wrought Iron |  | SAN RAFAEL | JOB IN PROGRESS - GM 4432688.
| 95-03638-1 |  |  | 10 | Transmission |  | Other Welds |  |  | Unknown |  | 1995-11-03 | 2001-04-27 | Other |  | Steel/Wrought Iron |  | CORTE MADERA | CRACKS IN STREET.
|  | 21 |  | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL
|  |  |  | 6 | [11 empty] | Steel-Other |  | SAN RAFAEL | DREG3895; 0.0624; W.O. 44885
|  | 21-B | 1.1412 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | API SL X42 .281 W.T. SO- 7035594. BEING REPLACED AND LOWERED TO CLEAR NEW CREEK.
|  | 021B-1 | 2.2 | 12 | Transmission | [7 empty] | 2002-10-29 |  |  | Steel/Wrought Iron |  |  | SO# 7045425. WELDED 2 - 2" CAPS OVER SERVICE TEE LOCATIONS; WHEN LINE WAS BLOWN DOWN FOR HVHIC ROAD WELDER CUT TWO 3/4 TEE OFF AND WELDED 2 - 2" GRADE B SMLS CAPS TO WALL. THIS WAS DONE BECAUSE 2 - 3/4" VALVES WERE LEAKING.
|  | 021-B | 0.98 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7046425
|  | 021-B | 6.05 | 8.625 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7045425
|  | 21C | 39.52 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT # 021C MP 39.52
|  | 21C | 39.52 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT 021C MP 39.52
|  |  |  | 0.04 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 021C | 50.65 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 30237082
|  | 021C | 50.74 | 12.75 | Transmission | [13 empty] | SO# 30237082
|  | 021E | 55.4172 | [15 empty] | SO# 7046002. INSPECTED 12" MAIN.
| 01-40244-1 | 21 | 57.67 | 12 | Transmission |  |  |  |  | Digin |  | 2001-12-16 | 2001-12-16 | Replace TP Main |  | Steel/Wrought Iron |  | WINDSOR | ROUTE 21E; MP. 57.73; SO# 8080456-02
|  | 021E | 57.73 | 12.75 | Transmission |  | Body of Pipe |  |  | Digin |  |  | 2002-04-29 | Other | INST. NEW SECTION | Steel/Wrought Iron |  |  | SO# 8050456-02. INSTALL NEW SECTION WITH MLV BRIDAL ASSY.
|  | 021E | 57.73 |  | Transmission |  | Body of Pipe |  |  | Digin |  |  | 2002-04-29 | Other | INST. NEW SECTION | Steel/Wrought Iron
|  |  |  | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL
| 00-00553-1 | LINCOLN |  | 16 | Transmission |  | Body of Pipe |  |  | Digin |  | 2000-08-17 | 2000-08-17 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SAN RAFAEL
| 00-00553-1 | LINCOLN |  | 16 | Transmission |  | Body of Pipe |  |  | Digin |  | 2000-08-17 | 2000-08-17 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SAN RAFAEL | DIG-IN REPAIR SLEEVE. ON 16" TRANS MAIN. PEDRO RD, 23' OFF P/L - INSTALLED 18" LONG SLEEVE.
[16 empty] | Steel/Wrought Iron |  | SAN RAFAEL | DIG IN - NO DAMAGE
| 90-00076-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  |  |  | 1990-01-22 | 1990-01-29 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SR | INST'D 2" SAV-A-VALVE OVER CORROSION LEAK ON 12" DFM MAIN INST'D ETS.
INST'D 2" SAVE-A-VALVE OVER LARGE CORROSION LEAK ON BOTTOM OF MAIN. INST'D ETS ON 2"
|  | 21D | 0.14 | 16 | [11 empty] | Steel-Other |  | SANTA ROSA
|  | 21D | 0.44 | 16 | [11 empty] | Steel-Other |  | SANTA ROSA
| 78-00316-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-06-27 | 1978-07-05 | Patch Welded |  | Steel/Wrought Iron |  | SAN RAFAEL | VENTED PATCH WELDED ON BY G.C WELDER 44' N/E OF HPR. TIGHTENED LEAKING SERVICE TEE CAP OF AN ABANDONED SERVICE. LARGE ROCKS ARE WEDGED AROUND THE MAIN. THESE ROCKS ARE LIKELY TO CAUSE FURTHER PROBLEMS.
|  |  |  | 16 | [7 empty] | 1989-05-03 |  |  |  | Steel-Other
SO. TIE-IN ON GM4529442.
|  |  |  | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL | INSTALLED 6-5 BOC FOR ETS AND (2) 32# MCG ANODES.
|  |  |  | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL
|  |  |  | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL
|  |  |  | 16 | Distribution Feeder Main | [6 empty] | 1987-03-26 |  |  |  | Steel-Other |  | SAN RAFAEL | JOB IN PROGRESS - GM 4432688.
|  |  |  | 12 | [11 empty] | Steel-Other |  | SAN RAFAEL
|  |  |  | 12 | [11 empty] | Steel-Other |  | SAN RAFAEL | 0401-01 1.7902; EXPOSED 12" MAIN IN ORDER TO RAISE GAS MAIN AND CLEAR CONTACT WITH 8" CI WATER MAIN FOR CORROSION DEPT.
|  |  |  | 20 | Distribution Feeder Main | [6 empty] | 1987-03-26 |  |  |  | Steel-Other |  | SAN RAFAEL | JOB IN PROGRESS - GM 4432688.
|  |  |  | 12 | [13 empty] | SAN RAFAEL
|  |  |  | 20 | [11 empty] | Steel-Other |  | SAN RAFAEL | S/W CORNER AT CROSSWALK
|  |  |  | 12 | [11 empty] | Steel-Other |  | SAN RAFAEL | INST'D ETS.
|  |  |  | 16 | Transmission | [10 empty] | Steel-Other |  | SAN RAFAEL | INSTALLED ETS ON 16" LINCOLN AVE. LINE AT 3RD + LINCOLN AVE. CITY POURED A 2'X2'X3' SLAB FOR SIGNAL LIGHTS ADJACENT TO 16" MAIN AT ETS LOCATION.
|  |  |  | 12 | [11 empty] | Steel-Other |  | SAN RAFAEL | INST'D E.T.S.
|  |  |  | 10 | [11 empty] | Steel-Other |  | SAN RAFAEL | NORTH BAY 0402-01 0.3144
|  | 21 |  | 16 | [13 empty] | SAN RAFAEL | NORTH BAY 0402-01 2.3421; PUT CORRUGATED PIPE AROUND GAS MAIN.
|  |  |  | 10 | [11 empty] | Steel-Other |  | SAN RAFAEL | PUT CORRUGATED PIPE AROUND PIPE.
|  |  |  | 12 | [11 empty] | Steel-Other |  | SAN RAFAEL | INSTALLED 1/2" STL. SERVICE TO LOAD CENTER.
|  |  |  | 12 | [11 empty] | Steel/Wrought Iron |  | SAN RAFAEL
|  |  |  | 12 | [11 empty] | Steel-Other |  | SAN RAFAEL | INSTALL ETS.
|  |  |  | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL | 0401-01 2.3971; MAIN INST'D ON GM 124863- IN 1954. WATER CO. DUG INTO MAIN WHILE INSTALLING WATER MAIN. BACKHOE TOOTHHIT 16" GAS MAIN. TOOTH SCRAPED OFF MAIN. NO DAMAGE TO MAIN.
|  |  |  | 16 | [13 empty] | SAN RAFAEL
|  |  |  | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL | DEPTH CHECK.
|  | 21 |  | 16 | [11 empty] | Steel/Wrought Iron |  | SAN RAFAEL | PUT CORRUGATED PIPE AROUND MAIN.
| 99-80156-1 | DFM |  | 12 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1999-10-20 | 1999-11-24 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SAN RAFAEL | INSPECT ALREADY HERE - ADDED LEAK INFO.
| 99-80156-1 | DFM |  | 12 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1999-10-20 | 1999-11-24 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SAN RAFAEL | ODER IN AIR. R/GATE TO SUBSTATION. GC INSTALLED + WELDED 2 - 12" PLIDCO CLAMPS ON MAIN.
|  |  |  | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL | CADWELDED 2 #10 WIRES ON 16" MAIN FOR RECTIFIER.
| 98-00162-1 |  |  | 16 | Distribution Feeder Main |  | Longitudinal Weld |  |  | Corrosion |  | 1998-04-22 | 1998-06-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SAN RAFAEL | WELDED CAN OVER PIPE.
|  |  |  | 10 | [11 empty] | Steel-Other |  | SAN RAFAEL | DEPTH CHECK.
|  |  |  | 10 | [13 empty] | SAN RAFAEL | 0401-01 2.5521 ALREADY DONE
|  |  |  | 10.75 | [11 empty] | Steel-Other |  |  | 0402-01 2.6342; REMOVED VALVE.
|  |  |  | 10 | [11 empty] | Steel-Other |  | SAN RAFAEL | NORTH BAY 0401-01 2.6398
40 | 97-05006-1 |  |  | 10 | Distribution Feeder Main |  | Girth Weld |  |  | Construction Defect |  | 1997-06-16 | 1998-06-10 | Patch Welded |  | Steel/Wrought Iron |  | SAN RAFAEL | WELD AT BASE OF SUC TEE LEAKING. PINNED SUC AND REWELDED SUC TEE. NORTH BAY 0401-01 2.6805
|  |  |  | 10 | [11 empty] | Steel-Other |  | SAN RAFAEL | INSTALLED ETS. 0401-01 3.3309
|  |  |  | 10 | [11 empty] | Steel-Other |  | SAN RAFAEL | INSTALLED ETS. 0401-01 3.3545
|  |  |  | 10 | [11 empty] | Steel-Other |  | SAN RAFAEL | NORTH BAY 0401-01 3.8332; (INSTALLED ETS) WHERE 10" TURNS UP MEADOW FROM IRWIN (RIGHT AT BEND).
|  |  |  | 16 | [11 empty] | Steel-Other |  | GREENBRAE | 0402-01 4.3534. INSTALLED G-5 BOX FOR ETS. SEE PLAT FOR LOCATION OF NEW ETS.
|  |  |  | 16 | [11 empty] | Steel-Other |  | GREENBRAE | INSTALLED G-5 BOX FOR ETS. SEE PLAT FOR LOCATION OF NEW ETS. 4.3534.
| 90-00110-1 |  |  | 0.75 | Distribution Feeder Main |  | Body of Pipe |  |  | Digin |  | 1990-03-07 | 1990-03-07 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | LARKSPUR | WELDED 2" SAV-A-VALVE OVER 1/2" TAP.
| 78-00231-1 |  |  | 16 | Distribution Feeder Main |  | Physical/Mechanical Joint |  |  | Material Failure |  | 1978-04-20 | 1978-07-06 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | REMOVED PART THAT WAS LEAKING AND REPLACED WITH NEW PIECE OF PIPE. (64"...)
|  |  |  | 16 | Distribution Feeder Main |  | Other | [10 empty] | LARKSPUR | 0402-01 3.028 2485 DT; NOTE: PIPE DID NOT SHIFT OR PULL APART WHEN PIPE WAS CUT. 16" GASKET WAS REMOVED FOR INSPECTION. INDICATED NO DAMAGE TO GASKET.
|  |  |  | 16 | [11 empty] | Steel-Other |  | CORTE MADERA | 0402-01 3.211...; C/O 3/4" STL. SERVICE.
|  |  |  | 16 | [11 empty] | Steel-Other |  | LARKSPUR | 0402-01
|  |  |  | 20 | [11 empty] | Steel-Other |  | GREENBRAE | INSTALLED ETS.
|  |  |  | 16 | [11 empty] | Steel-Other |  | GREENBRAE | INSTALLED ETS. INSTALLED NEW MAIN MARKER.
|  | 21 | [13 empty] | Steel-Other |  |  | 16" TRANS. MAIN AT ANGLE POINT OF ROAD CROSSING INTERSECTION OF OLD REDWOOD HIGHWAY AND SAN MARIN DR.. EAST SIDE OF CASING.
|  |  |  | 20 | [11 empty] | Steel-Other |  |  | NORTH BAY 0216 10.5502
|  | 21 |  | 12.75 | [11 empty] | Steel-Other |  |  | 10.84
| 05-50- | 021G | 10.8547 | 20 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party |  | 2005-10-24 | 2005-10-26 | Other | WELD SLEEVE | Steel/Wrought Iron |  | NOVATO | GOUGE TO 20" GAS MAIN. WELDED 20" DIA X 36" REPAIR SLEEVE. 20" BY 36" SLEEVE INSTALLED BY GC GAS.
|  |  |  | 12 | [11 empty] | Steel/Wrought Iron
|  |  |  | 20 | [11 empty] | Steel/Wrought Iron |  | NOVATO
|  |  |  | 20 | [11 empty] | Steel/Wrought Iron |  | NOVATO | DID NOT BREAK WRAP; LINE 21 12 2' DEEP AT CROSSING DF NEW 2" STUB. DUG UP MAIN AT NEW GAS CROSSING & PUSHED AHEAD NEW GAS SERV. BOH DIRECTIONS FROM BELL HOLE.
|  |  |  | 12 | [11 empty] | Steel/Wrought Iron |  | NOVATO | INST. ETS.
|  |  |  | 12 | [11 empty] | Steel-Other |  | NOVATO | CROSSED AND EXPOSED 12" MAIN WHILE TRENCHING FOR SERVICE TO #1559 SO NOVATO BLVD. NOV.
|  | 21 | [13 empty] | Steel-Other |  | NOVATO | NORTH BAY 21F 12.1316; GROUND OUT SCRATCHES IN MAIN AND RE-WRAPPED.
|  |  |  | 12 | [11 empty] | Steel-Other |  | NOVATO | NORTH BAY 021F 12.3957
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | NOVATO | DEPTH CHECKED FOR SEWER. NORTH BAY 021F 12.9231
|  | 21 |  | 20 | [11 empty] | Steel/Wrought Iron |  | NOVATO | INST. ETS.
|  | 21 | [10 empty] | 2000-04-05 | Other | WRAPPED MAIN | Steel/Wrought Iron |  | NOVATO | NO LEAK/ WRAP DAMAGED. WRAPPED MAIN TOOK PIPE TO SOIL.
|  | 21 |  | 20 | [11 empty] | Steel/Wrought Iron |  |  | ETS INSTALL.
|  | 21 | [13 empty] | Steel/Wrought Iron |  | NOVATO | PATCHED 5' SECTION OF LINE 21 S/ ROWLAND BLVD.
|  |  |  | 20 | [11 empty] | Steel-Other |  | NOVATO
|  |  |  | 12 | [11 empty] | Steel-Other |  | NOVATO
|  |  |  | 12 | [11 empty] | Steel-Other |  | NOVATO
|  |  |  | 12 | [11 empty] | Steel-Other |  | NOVATO
|  |  |  | 12 | [11 empty] | Steel-Other |  | NOVATO
|  |  |  | 12 | [11 empty] | Steel-Other |  | NOVATO
|  |  |  | 20 | [11 empty] | Steel-Other |  | NOVATO
|  |  |  | 12 | [11 empty] | Steel-Other |  | NOVATO
|  | 21 |  | 12 | [11 empty] | Steel/Wrought Iron |  | NOVATO | INST. ETS.
|  |  |  | 12 | [11 empty] | Steel-Other |  | NOVATO
|  | 21 |  | 12.75 | [11 empty] | Steel-Other
|  |  |  | 12.75 | [11 empty] | Steel-Other |  | NOVATO
|  | 21 |  | 16 | [11 empty] | Steel-Other |  | NOVATO | 16" TRANSMISSION MAIN S/O SOUTH NOVATO BLVD. IN HILLSIDE PARK CONDO'S
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | NOVATO | MAIN INSPECTION 16"; NEW STREET NO ADDRESS YET
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | NOVATO | TWO PIPES ON FORM
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | NOVATO | 12" TRANSMISSION MAIN S/O SOUTH NOVATO BLVD IN HILLSIDE PARK CONDOS
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | NOVATO | MAIN INSPECTION 12"; NEW STREET NO ADDRESS YET
|  | 21 |  | 16 | [11 empty] | Steel-Other |  | IGNACIO | INST. ETS # PLASTIC MAIN MARKER
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | IGNACIO | INSTALLED PLASTIC MAIN MARKER
|  |  |  | 16 | [11 empty] | Steel-Other |  | IGNACIO | INSTALLED PLASIC MAIN MARKER
|  |  |  | 12 | [11 empty] | Steel-Other |  | NOVATO
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | IGNACIO | INST ETS & PLASTIC MAIN MARKER
|  |  |  | 16 | [11 empty] | Steel-Other |  | NOVATO | CONTRACTOR POTHOLING MARKER
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | NOVATO | LINE 21 DEPTH CHECK
|  | 21 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | NOVATO | WRAP IS IN VERY POOR CONDITION CAN PEAL OFF BY HAND; SAME MOISTURE UNDER WRAP - SPOT WRAPPED.
|  |  |  | 12 | [11 empty] | Steel/Wrought Iron |  | NOVATO | WRAP IS IN VERY POOR CONDITION CAN PEAL OFF BY HAND; SAME MOISTURE UNDER WRAP - SPOT WRAPPED.
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | NOVATO | DEPTH CHECK WITH PROBE BAR
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | NOVATO | DEPTH CHECK WITH PROBE BAR
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | NOVATO | DEPTH CHECK WITH PROBE BAR
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | NOVATO | DEPTH CHECK WITH PROBE BAR
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | NOVATO | DEPTH CHECK WITH PROBE BAR
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | NOVATO | DEPTH CHECK WITH PROBE BAR
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | NOVATO | DEPTH CHECK WITH PROBE BAR
|  | 21 |  | 16 | [11 empty] | Steel-Other |  | NOVATO | ALL READY MARKED ON PLAT SHEET.
|  | 21 |  | 12 | Transmission | [10 empty] | Steel-Other |  | NOVATO | DEPTH CHECK ON 12' ... INSTALLED E.T.S. BOX AT THIS LOCATION
|  | 21 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | NOVATO | DEPTH CHECK ON 12" LINE 21
|  | 21 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | NOVATO | DEPTH CHECK ON 12" LINE 21. INSTALLED E.T.S. BOX AT THIS LOCATION
|  | 21 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | NOVATO | DEPTH CHECK ON ...
|  | 21 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | NOVATO | DEPTH CHECK ON 12" LINE 21. INSTALLED E.T.S. AT THIS LOCATION.
|  | 21 |  | 12 | [11 empty] | Steel/Wrought Iron |  | NOVATO | PLAT 2927-C5 SEE PLAT SHEET FOR LOCATION. ALL WRAP WAS REMOVED FROM TOP OF MAIN. BACKFILL INST'D BY DEVELOPER. REGARDING BACKFILL REMOVAL - NOTIFIED LARRY KIRBS 4/17/78 NOT TO WORK OVER OUR MAIN WITHOUT SPECIFICALLY CLEARING THROUGH ME - HE AGREED; WRAP HAS BEEN SCRAPED OFF TOP OF MAIN & PIPE SHOWED EVIDENCE OF CORROSION. HEAVY EQUIPMENT HAD BEEN DRIVING OVER MAIN.
|  |  |  | 12 | [8 empty] | 1985-07-07 |  |  | Steel/Wrought Iron |  | NOVATO | DEPTH CHECKED MAIN
|  |  |  | 12 | Transmission | [7 empty] | 1985-07-07 |  |  | Steel/Wrought Iron |  | NOVATO | INSTALLED 2 WIRES #10 CU & ETS BOX.
|  |  |  | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL | INSTALLED WIRES ON EXPOSED 16" IN WASHOUT FOR E.T.S.
[18 empty] | SAN RAFAEL | 4' OF PIPE EXPOSED DUE TO E...
|  | 21 |  | 16 | [11 empty] | Steel/Wrought Iron |  |  | GHILOTTI DEPTH CHECK MAIN FOR CONSTRUCTION
|  | 21 |  | 16 | [11 empty] | Steel-Other |  |  | GHILOTTI DEPTH CHECK MAIN FOR CONSTRUCTION.
|  | 21 |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | GHILOTTI DEPTH CHECK MAIN FOR CONST.
|  | 21 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN RAFAEL | DUG UP MAIN AT EDGE OF CYCLONE FENCE BY MAIN MARKER FOR DEPTH CHECK FOR STATE.
|  | 21 |  | 16 | [11 empty] | Steel-Other |  | TERA LINDA
40 | 98-05009-1 |  |  | 16 | Transmission |  | Fitting |  |  | Construction Defect |  | 1998-06-10 | 1999-05-28 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN RAFAEL | TEFLON TAPE THREADS & TIGHTEN CAP; TEFLON TAPE THREADS & TIGHTEN CAP ON 2 1/2" HO SAVE-A-VALVE PER M. AUILLA R. KOHL MADE REPAIRS
|  | 21 |  | 16 | [11 empty] | Steel-Other |  | SAN RAFEL | EXPOSED 16" TRANS G. MAIN (LINE #21) AND INSTALLED A G-5 BOX FOR E.T.S.
|  | 21 |  | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL | DEPTH CHECK ONLY
|  | 21 |  | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL
| 91--1 | 21 | 21.8 | 16 | Transmission |  |  |  | N/A |  | N/A |  | 1991-12-20 |  | N/A | Steel/Wrought Iron |  | PETALUMA
|  | 21 | 24.25 | 16 | [11 empty] | Steel-Other |  | PETALUMA | PLEASE MAP! INSTALL E.T.S. ON LINE 21; INSTALL E.T.S.
|  | 21C | 36.94 | 12 | [11 empty] | Steel-Other |  | PETALUMA
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | PETALUMA | PLEASE MAP! INSTALL E.T.S. ON LINE 21; INSTALL ETS
4 |  | 21C | 48.83 | 12 | [11 empty] | Steel-Other |  | SANTA ROSA
|  |  |  | 12 | [11 empty] | Steel/Wrought Iron |  |  | NORTH COAST 21C 50.1415
|  | 21C | 50.17 | 16 | [11 empty] | Steel-Other
|  |  |  | 12 | [11 empty] | Steel-Other |  |  | NORTH COAST 221C 50.1717
|  | 21C | 50.34 | 12
|  | 21C | 50.35 | 12 | [11 empty] | Steel-Other
|  | 21C | 50.96 | 12 | [11 empty] | Steel/Wrought Iron |  | SANTA ROSA
|  | 21C | 51.18 | 12 | [11 empty] | Steel-Other |  | SANTA ROSA
Steel/Wrought Iron
|  |  |  | 12 | [11 empty] | Steel-Other |  | HOPLAND | NORTHCOAST 021E 98.9141
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | HENDOCINA COUNTY | JACKED UP MAIN TO CLEAR CASING ON BOTH ENDS OF CASING. USED NYLON WEDGES TO MAINTAIN CLEARENCE. INSTALLED E.T.S. ON BOTH ENDS.
|  | 21 |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | UKIAH | INSPECTION LOC. AT TIE-IN POINT OF HPR'S TO L-21
|  |  |  | 12 | [11 empty] | Steel-Other |  |  | 12" SEPARATION FROM WATER & GAS. WATER CROSSED...
|  | 21 |  | 12 | [11 empty] | Steel-Other
| 99-00035- | 21 |  | 12 | Transmission |  |  |  |  | Damage by 3rd Party |  | 1999-11-29 | 1999-12-01 | Patch Weld - Weld |  | Steel/Wrought Iron |  | UKIAH | NO LEAKAGE DAMAGE 12" L-21 - 3/32 NICK IN PIPE; DAMAGE AREA TO BE PATCH WELD.
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | UKIAH | INSTALLED E.T.S. 79' SOUTH OF 90 DEGREE TURN TO WEST ON LINE 21
|  | 21 |  | 8 | [11 empty] | Steel-Other |  |  | FOUND 3/4" MULLER TEE & 8" - 3/4" STUB CAPPED OFF 8" STEEL MAIN
|  |  |  | 8 | Transmission | [10 empty] | Steel-Other |  | UKIAH
|  |  |  | 8 | [11 empty] | Steel/Wrought Iron
|  | 21 |  | 8 | [11 empty] | Steel/Wrought Iron |  | WILLITS | NO SAND AROUND PIPE AT TIE-IN L-21
|  |  |  | 8 | [11 empty] | Steel-Other |  | WILLITS
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | NOVATO | DEPTH CHECK WITH PROBE BAR
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | NOVATO | DEPTH CHECK WITH PROBE BAR
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | NOVATO | 12" LINE - N/O ALAMEDA DEL PRADO VALVE CLUSTER
|  |  |  | 16 | [11 empty] | Steel-Other |  | NOVATO | 16" LINE - N/O ALAMEDA PRADO VALVE CLUSTER
|  |  |  | 16 | [11 empty] | Steel-Other |  | NOVATO | 16" LINE - N/O ALAMEDA DEL PRADO VALVE CLUSTER; CLAY
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | NOVATO | LINE 21 - N/O ALAMEDA DEL PRADO VALVE CLUSTER
|  |  |  | 12 | [11 empty] | Steel-Other |  | SAN RAFAEL INC
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | NOVATO | DEPTH CHECK WITH PROBE BAR.
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | NOVATO | DEPTH CHECK WITH PROBE BAR
|  |  |  | 12.75 | [11 empty] | Steel-Other
|  |  | 79.1587 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LOWERED MAIN IN CREEK.
| 96-40047-1 |  | 79.7569 | 12 | Transmission |  | Longitudinal Weld |  |  | Construction Defect |  | 1996-01-04 | 1996-02-07 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | CLOVERDALE | WELDED FULL CIRCLE SLEEVE
|  | 021E | 116.7316 | 8 | [13 empty] | UKIAH
|  | 021E | 122.07 | 8 | [13 empty] | REDWOOD VALLEY
|  | 21E |  | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 807' 6" OF NEW PINE INSTALLED JOB # 7060186 LINE 21E 6 MILES
|  | 21 | 0.2832 | 16 | [11 empty] | Steel/Wrought Iron |  | SAN RAFAEL INC
|  | 21 | 10.84 | 12.75 | [11 empty] | Steel-Other
|  |  | 11.0769 | 12
|  |  | 11.4519 | 12 | [13 empty] | NOVATO | RT = 021F; MP = 11.4519
|  |  | 12.0217 | 12 | [11 empty] | Steel-Other |  | NOVATO | CROSSED AND EXPOSED 12" MAIN WHILE TRENCHING FOR SERVICE TO # 1559 SO NOVATO BLVD, NOV.
|  | 21 | 12.1257 | 12 | [11 empty] | Steel-Other |  | NOVATO | GROUND OUT SCRATCHES IN MAIN AND RE-WRAPPED.
|  |  | 12.3897 | [12 empty] | Steel-Other |  | NOVATO INC | RT = 021F
|  | 21 | 12.9231 | 12 | [13 empty] | NOVATO | RT= 021F; DEPTH CHECKED FOR SEWER
|  | 21 | 13.1472 | [9 empty] | 2000-04-05 | Other | WRAPPED MAIN | Steel/Wrought Iron |  | NOVATO | NO LEAK/WRAP DAMAGED, WRAPPED MAIN TOOK PIPE TO SOIL
|  | 21 | 13.2048 | [12 empty] | Steel/Wrought Iron |  | NOVATO | PATCHED 5' SECTION OF LINE 21 S/ ROWLAND BLVD
|  |  | 13.5888 | 12 | [11 empty] | Steel-Other |  | NOVATO
|  |  | 13.613 | 12 | [11 empty] | Steel-Other |  | NOVATO
|  |  | 13.6363 | 12 | [11 empty] | Steel-Other |  | NOVATO
|  |  | 13.6564 | 12 | [11 empty] | Steel-Other |  | NOVATO
|  |  | 13.6635 | 12 | [11 empty] | Steel-Other |  | NOVATO
|  |  | 13.6676 | 12 | [11 empty] | Steel-Other |  | NOVATO
|  |  | 13.6814 | 12 | [11 empty] | Steel-Other |  | NOVATO
|  |  | 13.8213 | 12 | [11 empty] | Steel-Other |  | NOVATO
|  | 21 | 14.1416 & 14.1388 | 12 | [11 empty] | Steel-Other |  | NOVATO | 12" TRANSMISSION MAIN S/O WOUTH NOVATO BL. IN HILLSIDE PARK CONDOS
|  | 21 | 13.9 | 12.75 | [11 empty] | Steel-Other
|  |  | 13.9131 | 12.75 | [11 empty] | Steel-Other |  | NOVATO
|  |  | 14.1595 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | NOVATO | NEW STREET NO ADDRESS YET
|  | 21 | 14.5012 | 12 | [11 empty] | Steel/Wrought Iron |  | IGNACIO | INSTALLED PLASTIC MAIN MARKER
|  | 21F | 14.53 | 12 | Transmission
|  | 21F | 15 |  | Transmission | [10 empty] | Steel/Wrought Iron
|  | 21 |  | 12 | [11 empty] | Steel-Other |  | NOVATO | LINE 21 DEPTH CHECK
|  | 21 | 15.95 | 12.75 | [11 empty] | Steel-Other
|  | 21 | 15.15 | 12 | [11 empty] | Steel-Other |  | NOVATO | DEPTH CHECK WITH PROBE BAR
|  | 21 | 15.9534 | 12 | [11 empty] | Steel-Other |  | NOVATO | DEPTH CHECK WITH PROBE BAR
|  |  | 15.956 | 12 | [11 empty] | Steel-Other |  | NOVATO | WRAP IS IN VERY POOR CONDITION CAN PEAL OFF BY HAND; SOME MOISTURE UNDER WRAP - SPOT WRAPPED.
|  | 21 | 15.9618 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | NOVATO | DEPTH CHECK WITH PROBE BAR
|  | 21 | 15.9568 | 12 | [11 empty] | Steel-Other |  | NOVATO | DEPTH CHECK WITH PROBE BAR
|  | 21 | 15.9658 | 12 | [11 empty] | Steel-Other |  | NOVATO | DEPTH CHECK WITH PROBE BAR
|  | 21 | 15.9759 | 12 | [11 empty] | Steel-Other |  | NOVATO | DEPTH CHECK WITH PROBE BAR
|  | 21 | 15.9791 | 12 | [11 empty] | Steel-Other |  | NOVATO | DEPTH CHECK WITH PROBE BAR
|  | 21 | 15.9796 | 12 | [11 empty] | Steel-Other |  | NOVATO | DEPTH CHECK WITH PROBE BAR
|  | 21 | 15.9821 | 12 | [11 empty] | Steel-Other |  | NOVATO | DEPTH CHECK WITH PROBE BAR
|  | 21 | 16.6013 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | NOVATO | DEPTH CHECK ON 12" LINE 21 INSTALLED E.T.S. BOX AT THIS LOCATION.
|  | 21 | 16.6205 | 12 | [11 empty] | Steel-Other |  | NOVATO | 12" LINE - N/O ALAMEDA DEL PRADO VALVE CLUSTER
|  | 21 | 16.6374 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | NOVATO | DEPTH CHECK ON 12" LINE 21
|  | 21 | 16.6491 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | NOVATO | DEPTH CHECK ON 12" LINE 21. INSTALLED E.T.S. BOX AT THIS LOCATION
|  | 21 | 16.65 | 12 | [11 empty] | Steel-Other |  | NOVATO | NONE
|  | 21 | 16.6638 | 12.75 | [11 empty] | Steel-Other |  |  | HYDRO FOR WHAT?
|  | 21 |  | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL | DEPTH CHECK L-21
|  | 21 | 16.6646 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | NOVATO | DEPTH CHECK ON 12" LINE 21.
|  | 21 | 16.6906 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | NOVATO | DEPTH CHECK ON 12" LINE 21. INSTALLED E.T.S. AT THIS LOCATION.
|  | 21 | 17.0083 | 12 | [11 empty] | Steel/Wrought Iron |  | NOVATO | WRAP HAS BEEN SCRAPED OFF TOP OF MAIN & PIPE SHOWED EVIDENCE OF CORROSION. HEAVY EQUIPMENT HAS BEEN DRIVING OVER MAIN.
|  |  | 17.0092 | 12 | [8 empty] | 1985-07-07 |  |  | Steel/Wrought Iron |  | NOVATO | DEPTH CHECKED MAIN.
|  |  | 17.016 | 12 | Transmission | [7 empty] | 1985-07-07 |  |  | Steel/Wrought Iron |  | NOVATO | INSTALL ETS; INSTALLED 2 WIRES #10 CU ETS BOX
|  |  | 18.4721 | 16 | [11 empty] | TR 418 |  | SAN RAFAEL | INSTALLED WIRES ON EXPOSED 16" IN WASHOUT FOR E.T.S.
|  | 21 | 18.8 | [14 empty] | SAN RAFAEL
|  | 21 | 19.2567 | 16 | [11 empty] | Steel-Other |  |  | GHILOTTI DEPTH CHECK MAIN FOR CONSTRUCTION
|  | 21 | 19.2598 | 16 | [11 empty] | Steel-Other |  |  | GHILOTTO DEPTH CHECK MAIN FOR CONSTRUCTION.
|  | 21 | 19.3042 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | GHILOTTI DEPTH CHECK MAIN FOR CONST.
|  | 21 | 19.6409 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN RAFAEL | DUG UP MAIN AT EDGE OF CYCLONE FENCE BY MAIN MARKER FOR DEPTH CHECK FOR STATE.
|  |  | 20.6765 | 16 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  | 19.93 | [14 empty] | SAN RAFAEL
|  | 21 | 19.9451 | 16 | [11 empty] | Steel/Wrought Iron |  | TERA LINDA
40 | 98-05009-1 | 21 | 20.0545 | 16 | Transmission |  | Fitting |  |  | Construction Defect |  | 1998-06-10 | 1999-05-28 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN RAFAEL | TEFLON TAPE THREADS & TIGHTEN CAP; TEFLON TAPE TREADS & TIGHTEN CAP ON 2 1/2" HP SAVE-A-VALVE PER M. AUILLA R. KOHL MADE REPAIRS
|  | 21 | 20.6018 | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL | DEPTH CHECK ONLY
|  | 21 | 1.05 | 16 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 21 | 10.3073 | 16 | [11 empty] | Steel-Other |  |  | LINE 21 16" TRANS. MAIN AT ANGLE POINT OF ROAD CROSSING INTERSECTION OF OLD REDWOOD HWY & SAN MARIN DR. EAST SIDE OF CASING
|  |  | 10.7143 | 20 | [11 empty] | Steel-Other
|  |  | 11.0719 | 20 | [11 empty] | Steel-Other |  | NOVATO
|  | 21 | 11.3644 | 20 | [11 empty] | Steel-Other |  | NOVATO | LINE 21 IS 5' DEEP AT CROSSING OF NEW 2" STUD, DUG UP MAIN AT NEW GAS CROSSING & PUSHED PULLED NEW GAS SERV. BOTH DIRECTIONS FROM BELL HOLE
|  | 21 | 13.1301 | 20 | [11 empty] | Steel-Other |  | NOVATO
|  | 21 | 13.1945 | 20 | [11 empty] | Steel-Other
|  |  | 13.4992 | 20 | [11 empty] | Steel-Other |  | NOVATO
|  |  | 13.5066 | 20 | [11 empty] | Steel-Other |  | NOVATO | NORTH OF REQUESTED AREA BUT GOOD DATA
|  | 21 | 13.7806 & 13.9697 | 12 | [11 empty] | Steel-Other |  | NOVATO | TWO PIPES ON FORM
|  |  | 13.9385 & 14.1294 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | NOVATO | TWO PIPES ON FORM
|  | 21 | 13.9500 & 13.9474 | 16 | [11 empty] | Steel-Other |  | NOVATO | 16" TRANSMISSION MAIN S/O SOUTH NOVATO BLVD, IN HILLSIDE PARK CONDO
|  |  | 13.9661 | 16 | Transmission | [10 empty] | Steel-Other |  | NOVATO | NEW STREET NO ADDRESS YET.
|  | 21 | 14.2925 | 16 | [11 empty] | Steel-Other |  | IGNACIO | INSTALLED PLASTIC MAIN MARKER
|  | 21 | 14.303 | 16 | [11 empty] | Steel-Other |  | IGNACIO | INST. ETS & PLASTIC MAIN MARKER
|  | 21 | 14.49 | 16 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 21 | 14.66 | 16 | Transmission | [10 empty] | Steel/Wrought Iron
|  |  | 16.0544 | 16 | [11 empty] | Steel-Other |  | NOVATO | 16" LINE - N/O ALAMEDA PRADO VALVE CLUSTER
|  |  | 16.0791 | 16 | [11 empty] | Steel-Other |  | NOVATO | 16" LINE - N/O ALAMEDA DEL PRADO VALVE CLUSTER; CLAY
|  | 21 | 16.3251 | 16 | [11 empty] | Steel-Other |  | NOVATO | ALL READY MARKED ON PLAT SHEET
|  | 21 | 20.4579 | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL | EXPOSED 16" TRAN. G. MAIN (LINE #21) AND INSTALLED A G-5 BOX FOR E.T.S.
|  | 21 |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 21 | 20.53 | 16 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 21 | 20.531 | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL | EXPOSED 16" TRAN. G. MAIN (LINE#21) AND INSTALLED A G-5 BOX FOR E.T.S.
| 08-02641- | 21C |  | 12 | Transmission |  | Valves |  |  | Other | FITTING ST 90 DEGREE ELL | 2008-09-25 | 2009-06-11 | Other | REPLACED BODY BLEED 1/2" PIPE | Steel/Wrought Iron |  | SEBASTOPOL | MADRONE REGULATOR STATION; REGULATOR STATION, VALVE #3
|  | 021D | 21.6771 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | PETALUMA | LINE 021D STA 70+05 ROUGHT 021 D MP 20.37 LATI 38 15 12.26185 LONG - 122 37 36.96411 276 FT. EAST OF NOVAK DR. PETALUMA
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PLS SEE NAPA Y MTR. STATION PHASE 2 DIAGRAM LETTER "A" FOR EXACT LOCATION OF INSPECTION.
|  |  | 12.0528 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SEE PHASE 2 DIAGRAM LTR. "B" SO# 7045965 STUB 8102 M.P. 12.0528
|  |  | 12.0558 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SEE PHASE 2 DIAGRAM LTR. "C" SO # 7045965 ROUTE: 021A MP 12.0558
|  |  |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SEE PHASE PHASE 2 DIAGRAM LTR. "D". SI # 7045965 ROUTE STAPIPE @ NAPA "Y" METER STA
|  | 21H |  | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 30708685-08
|  | 2 | 147.7343 | 26 | Single Service | Transmission | [9 empty] | Steel/Wrought Iron |  | TRACY | LOCATED VALVE AND FLANGE: DISCONNECTED SERVICE AND REMOVED 5' 3" OF 2" PIPE. INSTALLED BLIND FLANGE & WRAPPED
|  |  | 43.46 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 7030745-00 L-... MP = 43.46
|  | 2 | 43.68 | [12 empty] | Steel/Wrought Iron |  |  | L-2 M.P. 43.68 EXPOSED 12' W/ 80" COVER REMOVED 10' OF WRAP. 26" O.D. PIPE
|  | 2 | 43.68 | [12 empty] | Steel/Wrought Iron |  |  | L-2 M.P. 43.68 EXPOSED 12' W/ 80" COVER REMOVED 10' OF WRAP. 26" O.D. PIPE
|  | 2 | 44.4 | [15 empty] | CALD WELD COUPONS ON GAS MAIN
|  | 2 | 46.35 | [15 empty] | CALD WELD COUPONS ON GAS MAIN
|  | 2 | 47.05
|  | 2 | 47.3
|  | 2 | 47.85
|  | 2 | 48.5 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | EXCAVATED L-2 TO INSPECT GAS MAIN BECAUSE OF TRENCHER. CHECKED OK
|  | 2 | 48.8178 | 26 | [11 empty] | Steel/Wrought Iron
|  | 2 | 48.93 | 26 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 2 | 48.94 | 26 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 2 | 49.6 | [12 empty] | Steel/Wrought Iron |  |  | L-2 M.P 49.6 EXPOSED 12' REMOVED 10' OF WRAP 48' COVER 26" O.D. PIPE
|  | 2 | 49.6 | [12 empty] | Steel/Wrought Iron |  |  | L-2 M.P 49.6 EXPOSED 12' REMOVED 10' OF WRAP 48' COVER 26" O.D. PIPE
|  | 2 | 49.85 | [12 empty] | Steel/Wrought Iron |  |  | EXPOSED 12' REMOVED 10' OF WRAP 50" COVER 26" O.D. PIPE
|  | 2 | 49.85 | [12 empty] | Steel/Wrought Iron |  |  | EXPOSED 12' REMOVED 10' OF WRAP 50" COVER 26" O.D. PIPE 7-20-99
|  | 2 | 54.52 | [15 empty] | JOB 7030927
|  | 2 | 59.95/ 59.96 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-2 M.P. 59.96 IN HOLE #2 CLUSTER OF PITS. SHOWN ON ATTACHED PICTURE. DEEPEST PIT WAS .224 THOUSANDS OF AN INCH. PITS WERE FOUND BY THE SMART PIG DATA.
|  | 2 | 59.96 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | M.P. 59.96 IN HOLE #1. THE DEEPEST PIT WAS .224 THOUSANDS OF AN INCH. PIT WERE FOUND BY THE SMART PIG DATA.
|  | 2 | 61.3
|  | 2 | 63
|  | 2 | 63.38 | [12 empty] | Steel/Wrought Iron
|  | 2 | 63.38
|  | 2 | 63.38 | [12 empty] | Steel/Wrought Iron
|  | 2 | 64.65
|  | 2 | 72.86 | 26 | Transmission
|  | 2 | 72.86 | 26 | Transmission
|  | 2 | 75.33 | [12 empty] | Steel/Wrought Iron |  | LOS BANOS | COATING IS DISBONDED WITH MOISTURE UNDER WRAP ON THE BOTTOM AND UP SOME ON THE SIDES OF THE PIPE PRIMER COMES OFF WITH THE WRAP REMOVED IN MOST CASES AT THIS LOCATION. PRIVER LEFT ON PIPE WAS 1 MIL OVERALL THIS COATING IS IN FAIR CONDITION GC PAINT CREW USED POWER CRETE J TO REPAIR COATING
|  | 2 | 87.35 | 26 | [14 empty] | SEE BACK - WE HAVE 3 CROSSINGS, ONE STORM DRAIN, ONE WATER, AND ONE NON-POTABLE WATER. THE STOM DRAIN IS 30" CONCRETE PIPE THE WATER LINES ARE 12" PLASTIC. THE BOTTOM OF DITCH FOR THE 30" CONCRETE PIPE WAS 13'16" THE BOTTOM OF DITCH FOR THE 12" WATER LINE WAS 10'6" THE BOTTOM OF DITCH FOR THE 12" NON-POTABLE LINE WAS 11". ALL THESE DEPTHS WILL CHANGE A PAVED ROAD WILL GO OVER ALL THREE LINES
|  | 2 | 88.4 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  | SANTA NELLO
|  | 2 | 88.3 | [15 empty] | 6" FEED TO L-331 FROM L-2 @ BAYVIEW STATION JOB # 7026205
|  | 2 | 100.34 | [12 empty] | TR 418
|  | 2 | 106.84 | [12 empty] | Steel/Wrought Iron |  | NEWMAN | BLISTERS WITH MOISTURE UNDER COATING @ 3 O'CLOCK THEY WERE SCRAPED BACK TO GOOD CONDITION NOT COUNTING THE BLISTERS GC PAINT CREW PATCHED COATING WITH POWER CRETE J TWO COUPONS AND ONE BOND AND TWO TEST WIRES WERE INSTALLED @ THIS LOCATION
|  | 2 | 107.13 | [12 empty] | Steel/Wrought Iron |  | NEWMAN | FOUND ONE BLISTER @ 1 O'CLOCK 21" NORTH OF WELD. THIS SMALL BLISTER HAD A SMALL STONE EMBEDDED THERE REMOVED TAPE WRAP FROM WELD AREA TO INSPECT LOOKED GOOD UNDER TAPE WRAP G.C. PAINT UNDER POWER CRETE J TO REPAIR COATING INSTALLED 2 COUPONS AND ONE BOND AND TWO TEST WIRES @ THIS LOCATION.
|  | 2 | 11.9 | 26 | Transmission | [12 empty] | PATTERSON
|  | 2 |  | 26 | Transmission
|  | 2 | 111.86 | 26 | [14 empty] | SEE ATTACHMENT FOR SKETCH
|  | 2 | 111.88 | 26 | [14 empty] | SEE ATTACHMENT FOR SKETCH
|  | 2 | 111.92 | 26 | [14 empty] | SEE ATTACHMENT FOR SKETCH
|  | 2 | 118.02 | 24 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 2 | 122.06 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  | WESTLEY | TIE-IN MODIFICATION FOR PIG RECEIVER AT WESTLEY ST. SOUTH END OF TRENCH
|  | 2 | 122.06 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  | WESTLEY | TIE-IN MODIFICATION FOR PIG RECEIVING STA. @ WESTLEY NORTH END OF TRENCH
|  | 2 | 129.64 | 26 | [14 empty] | SEE BACK OF PAGE
|  | 2 | 135 |  | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party |  | 1999-12-04 | 1999-12-04 | Other | WELD 2" SAVE-A-VALVE & PAD |  |  | TRACY
|  | 2 | 139.49 | [12 empty] | Steel/Wrought Iron
|  | 2 | 139.76 | [15 empty] | LINE 2 AT GRAVEL RD IS 5'8' T.O.P.
|  | 2 | 140.6 | 26 | Transmission | [12 empty] | TRACY | ON BACK
|  | 2 | 144 | 26 | Transmission
|  | 2 | 144.26 | 26 | [14 empty] | DRAWING ON BACK
|  | 2 | 144.25 | 26 | [14 empty] | ALL DEPTHS WILL CHANGE PAVED ROAD TO BE INSTALLED OVER THIS SECTION
|  |  |  | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | CUT IN A BAR TEE
|  | 2 | 158 | 18 | [14 empty] | BRENTWOOD COMPRESSOR STATION
|  | 2 | 158 | 24 | [14 empty] | BRENTWOOD COMPRESSOR STATION
|  | 2 | 158 | 26.16 | Transmission | [13 empty] | BRENTWOOD COMPRESSOR STATION
|  | 300A | 0.56 | 34 | Transmission
|  | 300A | 0.64 | 4 | Branch Service | Transmission | [9 empty] | Steel/Wrought Iron |  | NEEDLES
|  | 300A | 0.64 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | NEEDLES
|  | 300 A | 0.74 | 34
|  | 300A+B | 2.50B 3.90A 4.08A
|  | 300A | 4.34 | [15 empty] | INSTALLED COUPONS FOR CPS STATIONS @ MILE 4.34 ON 300A
|  | 300A | 6 | [15 empty] | INSTALLED COUPONS FOR CP STATION @ MILE 6.00 ON 300 A
|  | 300A | 11.7 | [15 empty] | C.P. ACTION 300 A&B
|  | 300A | 12.69A | [15 empty] | EXPOSING FOR MAIN TO ... COUPONS FOR CP ... 3-31-03
|  | 300A | 23.05 | 31 | Transmission
|  | 300A | 25.21 | [15 empty] | C.P. ACTION LINE 300 A&B
|  | 300A | [16 empty] | 40.85
|  | 300A | 40.87 | 24 | [11 empty] | Steel/Wrought Iron
|  | 300A | 62.30A
|  | 300A | 103.2302 | 34 | Transmission | [10 empty] | Steel/Wrought Iron
|  | 300A | 116.5 | [15 empty] | DIG 4 - FOUND ABOUT 26' OF HAA WRAP HAD BEEN KNOCKED OFF IN PAST. MANY SCRAPS & COUGES. DEEPEST GOUGE FOUND TO BE .055" DEEP. LINE PRESSURED LOWERED 10%. REPAIRS MADE BY GRINDING ... UNTIL GOUGES WERE ... MINIMUM WALL THICKNESS OF PIPE W.T. @ .270 AT DEEPEST GOUGE AFTER .. VALLEY X-RAY CALLED TO CHECK AREA BY MAG. PARTICAL INSPECTION. NO SURFACE FLAWS FOUND. PIPE SAND BLASTED & COATED WITH POWER CRETE J. DAMAGE AND REPAIR AREA DRAWING ATTACHED. MEARS ALSO COMPLETED "H-FORM"
|  | 300A | 116 | [15 empty] | SEE DRAWINGS STAND BY FOR HOOD CONSTRUCTION
|  | 300A | 122.11 | [15 empty] | MEARS DIG #1 REST STOP ... ROAD MEARS MAKING "H-FORM' FOR PITT & WRAP INSPECTION 11' PIPE EXPOSED INSPECTED & RECOATED W/ POWER CRETE J
|  | 300A | 122.03 | [15 empty] | DIG 2 - WRAP FELL OFF AS DIGGING TOOK PLACE. WRAP IS DISBONDED MOST OF THE WAY AROUND THE PIPE. ONE INCH OR MORE DIRT HAS MIGRATED BETWEEN PIPE & WRAP. WATER BETWEEN WRAP & PIPE PH12. ...
|  | 300A | 125.2 | [15 empty] | DIG 3 - WRAP PIPE GOOD ...
|  | 300A | 131.28 | [15 empty] | MEARS CSI INVESTIGATION OF LINE. DUG UP ABOUT 20' OF LINE. WRAP IN BAD CONDITION. LARGE CALCARBUS DEPOSITS ON TOP OF LINE. DAVE AGUIR INVESTIGATED. NO PITS OR CORROSION ON LINE LOCATION. SAND BLASTED & COATED WITH POWER CRETE OR DEVTAR MEARS M.P. 131.29A.
|  | 300A | 131.37A | [15 empty] | INSTALLED 1 1/4" MULLER TEE AT THIS LOCATION AS AN ALT. FEED TO REG STATION
|  | 300A | 135.98A | [15 empty] | TAP
|  | 300A | 137 | [15 empty] | 300 SOUTH DISTRICT 300A; TAP
|  | 300A | 142.78A | [15 empty] | LAT: 34 511 12.02723 N; LONG 166 52 37.49155 W; ALT 2116; ; POT HOLE BY VAC TRUCK. FOR FUTRE CROSSING BY KERN RIVER P.L. CO. WITH 46" STEEL PIPE LINE
|  | 300A | 143.0413 | [15 empty] | DISTRICT G300S; L-300A; M.P. 143.0413; SO# 7056786-06
|  | 300A | 145.05A | [15 empty] | COVER ON LINE WASHED A WAY DUE TO LOCAL....
|  | 300A | 145.16A | [15 empty] | COVER ON LINE WASHED AWAY DUE TO LOCAL STORMS
|  | 300A | 145.19A | [12 empty] | Steel/Wrought Iron |  |  | SAMPLE TAKEN TO TEST FOR ASBESTOS
|  | 300A | 145.27 | [15 empty] | 300A M.P. 145.24; COVER ON LINE WASHED AWAY DUE TO LOCAL STORMS. THIS LOCATION HAS ... WRAP (...) HHA
|  | 300A | 147.25A | [15 empty] | SO#8056601-03, 300A M.P. 147.27A, 147.28 PIT, GAS GAUGE 4/8/03; LAT: 34 51 42.368N, LONG 116 57 21.72W; ALT 2231; ; 30' U/S +30% TO BE REPLACED WITH NEW PIPE AS PART OF HYDRO TEST OF LINE 300A. MEARS MILE POINT 146.83A WRAP FAIR. NO CORROSION OR PITTING. NO INTERNAL CORROSION ON PIPE. REPLACED, SAND BLASTED AND COATED WITH DEVTAR ON POWER CRETE
|  | 300A | 147.91A | [15 empty] | TAP
|  | 300A | 149.65A | [15 empty] | ABOUT 100' FEET TO BE REMOVED TO INSTALL NEW PLS STATION
|  | 300A | 150.469 |  | Transmission | [10 empty] | Steel-Other |  |  | LINE 300A MILE POINT 150.469 GPS NAD83 -117.0113; 34.87112; ; EXPOSED TOP OF PIPE BY THIRD PARTY TO SURVEY LOCATION AND ELEVATION FOR DECELOPMENT OF TRACT HOUSING AND PAVED ROADWAY IN RIGHT OF WAY. THERE USA #70960098
|  | 300A | 150.559 |  | Transmission | [10 empty] | Steel-Other |  |  | LINE 300A MILE POINT 150.559 GPS NAD83 -117.01268; 34.87142; EXPOSED TOP OF PIPE BY THIRD PARTY TO SURVEY LOCATION AND ELEVATION FOR DEVELOPMENT OF TRACT HOUSING AND PAVED ROADWAY IN RIGHT OF WAY. THERE USA #A70960098; ;
|  | 300A | 150.626 | [15 empty] | LINE 300A MILEPOINT 150.626 GPS NAD83 -117.01380; 34.87163; EXPOSED TOP OF PIPE BY THIRD PARTY TO SURVEY LOCATION AND ELEVATION FOR DEVELOPMENT OF TRACT HOUSING AND PAVED ROADWAY IN RIGHT OF WAY. THERE USA #A70960098; ; EXPOSED TOP OF PIPE BY THIRD PARTY TO SURVEY LOCATION AND ELEVATION FOR DEVELOPMENT OF TRACT HOUSING AND PAVED ROADWAY IN RIGHT OF WAY. THERE USA #70960098
|  | 300A | 150.68 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE 300A MILEPOINT 150.680 GPS NAD83 -117.01469; 34.87180; EXPOSED TOP OF PIPE BY THIRD PARTY TO SURVEY LOCATION AND ELEVATION FOR DEVELOPMENT OF TRACT HOUSING AND PAVED ROADWAY IN RIGHT OF WAY. THERE USA #A70960098; ; ; EXPOSED TOP OF PIPE BY THIRD PARY TO SURVEY LOCATION AND ELEVATION FOR DEVELOPMENT OF TRACT HOUSING AND PAVED ROADWAY IN RIGHT OF WAY. THERE USA #A70960098
|  | 300A | 150.718 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE 300A MILE POINT 150.718 GPS NAD83 -117.01535; 34.87193; EXPOSED TOP OF PIPE BY THIRD PARTY TO SURVEY LOCATION AND ELEVATION FOR DEVELOPMENT OF TRACT HOUSING AND PAVED ROADWAY IN RIGHT OF WAY. THERE USA #A70960098; ; ; EXPOSED TOP OF PIPE BY THIRD PARTY TO SURVEY LOCATION AND ELEVATION FOR DEVELOPMENT OF TRACT HOUSING AND PAVED ROADWAY IN RIGHT OF WAY. THERE USA #A70960098
|  |  |  | 34 | [11 empty] | Steel-Other
|  | 300A | 151.5 | [15 empty] | L-300A MP151.5; CONTRACTORS POT HOLE PIPE TO FIND DEPTH.
|  | 300 | 151.606 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE 300A MILE POINT 151.606 GPS NAD83 -117.03045; 34.87485l; EXPOSED PIPE BY THIRD PARTY TO CROSS UNDER THE LINE WITH AN 8" SEWER MAIN FOR NEW TRACT HOUSING AND THERE USA #A71011571; ; EXPOSED PIPE BY THIRD PARY TO CROSS UNDER THE LINE WITH AN 8" SEWER MAIN FOR NEW TRACT HOUSING AND THERE USA #A71011571
|  | 300A | 151.652 | [15 empty] | L-300A, MP. 151.6124; ; GPS NAD83 -117.03055; 34.87486
|  | 300A | 151.64 | [15 empty] | 300A M.P. 151.65; GPS N34 52 30.2; W 117 01 52.8; SEWER LINE CROSSING
|  | 300A | 151.70A | [15 empty] | WATER LINE TO BE INSTALLED UNDER 300A (AND FULL R/W) FOR NEW HOUSING TRACY
|  | 300A | 152.28A | [12 empty] | Steel/Wrought Iron |  |  | FIBEROPTIC TO BE INSTALLED UNDER LINE N 34.87712; W 117.04206
|  | 300A | 152.28A | [12 empty] | Steel/Wrought Iron
|  | 300A | 152.6 | [15 empty] | RT= 300A; MP= 152.6093; DISTRICTS 300S;; GPS NAD83 -117.04755; 34.87818; SEE WATER COMPANY DRAWING
|  | 300A | 153.56
|  | 300A | 156.32 | [15 empty] | LAT: 34 53 32.112 N'; LONG 117 06 35.257 W; ALT 2177; POT HOLES L-300A W/VAC. TRUCK EAST SIDE OF MAPLE STREET.
|  | 300A | 156.39 | [15 empty] | LAT 34 53 32.758N; LONG 117 06 38.682W; ALT 2177; POT HOLE L-300A W/ VAC. TRUCK EAST SIDE OF WALNUT STREET;
|  | 300A SOUTH | 156.41 | [15 empty] | LAT: 34 53 33.158N LONG 117 06 40.619W; ALT 2177; ; POT HOLE OF LINE W/VAC TRUCK BORED 4" PLASTIC GAS LINE UNDER 26" LINE.
|  | 300A NORTH | 156.41 | [15 empty] | LAT 34 53 33.157N; LONG 117 06 40.040W; ; POT HOLE OF LINE W/VAC TRUCK BORED 4" PLASTIC GAS LINE 26" LINE
|  | 300A SOUTH | 156.425 | [15 empty] | LAT: 34 53 33.26641N; LONG: 117 06 41.07092 W; ALT 2186; ; POTHOLE LINE FOR CROSSING W 1/2" HOPE SERVICE LINE
|  | 300A NORTH | 156.425 | [15 empty] | LAT 34 53 33.35841N; LONG 117 06 41.05547W; ALT 2187; ; POT HOLE LINE FOR CROSSING W 1/2" HOPE SERVICE LINE
|  | 300A | 156.43
|  | 300A | 156.43
|  | 300A NORTH | 156.46 | [15 empty] | LAT 34 53 33.77816N; LONG 117 06 43.08441; ALT 2184; ; POT HOLE LINE FOR CROSSING W/ 1/2" HOPE SERVICE LINE
|  | 300A NORTH | 156.46 | [15 empty] | LAT 34 53 33.68822N; LONG 117 06 43.09580W; ALT 2187; ; POT HOLE LINE FOR CROSSING W 1/2" HOPE SERVICE LINE
|  | 300A | 156.6 | [15 empty] | SOUTH LINE; LAT 34 53 35.495N LONG 117 06 51.871W; ; POT HOLE WITH VAC TRUCK FOR DEPTH & 2" PLASTIC SW. GAS CORP. 8 ORDERED UNDER 26" PGE LINE
|  | L300A | 156.6 | [15 empty] | NORTH LINE; LAT 34 53 35.589N LONG 117 06 51.884W; ; POT HOLE WITH VAC. TRUCK FOR DEPTH & 2" PLASTIC SW. GAS CORP. BORED UNDER 26" PGE LINE
|  | 300A | 156.75A | [15 empty] | SO# 8056601-03; 300A; M.P. 156.75A & 156.73;; ; ALT 2173; LAT 34 53 37.120 ; LONG -117 06 59.532; MEARS MILE POINT 156.74; 26" PIPE DUG UP TO INSPECT PIPE WRAP. NO CRACKS OR DISBONDING COULD BE FOUND. ;
|  | 300A | 157.87 | [15 empty] | INSPECTION OF LINE/WRAP BECAUSE OF 48" STEEL & CONCRETE WATER LINE INSTALLED 29" UNDER L-300A. TOOK SAMPLE OF WATER AND FOUND WATER BETWEEN WRAP AND PIPE. ADDED CAP TEST STATION AT ...
|  | L 300 A | 158.55 | [15 empty] | LAT 34 53 56.145"N; LONG 117 08 52.916"W; ALT 2184; TOPPED THE PIPE ONLY. NOTE R & R GAS LINE IN EXISTING DITCH.
|  | 300A | 152.62 | [15 empty] | LONG & lAT: 117 02 5125; 34 52 41.44
|  | L300A | 152.64 | [15 empty] | LAT 34 52 41.839 ; LONG 117 02 57.482; ALT 2421; ; LINE POT HOLED BY VAC TRUCK. TOP OF PIPE ONLY SEEN
|  | 300A | 152.33A | [15 empty] | LAT 34 52 44.527"N; LONG 117 03. 07.40"W; ALT 2355; ; POT HOLE TO TOP OF PIOPE BY APL. FOR SW GAS CORP
|  | 300A | 159.4 | [15 empty] | ROUTE= 300A M.P. 159.40; GPS 117.16290; 34.90124 (NAD83); ; INSPECTION OF WRAP AND PIPE BY MEARS
|  | 300A | 160 | 34 | Transmission | SERVICE | [9 empty] | Steel/Wrought Iron |  | HINKLEY | ABANDONDED TAP 160.00A TO SOUTH WEST GAS CORP.
|  | 300A | 180.64A | [12 empty] | Steel/Wrought Iron
|  | 300A | 180.94 | [15 empty] | SO # 7042906; RT = 300A; M.P. 180.95; KRAMER SCT INTERTIE;; POSTION; lAT 34 59 12.4"N; lONG 117 31 31.0" W; ; NEW 12" TAP TO BE INSTALLED
|  | 300A | 205.57A | [12 empty] | Steel/Wrought Iron |  |  | E.T.S. INSTALLED AT THIS SITE, SAMPLE OF WRAP TAKEN
|  | 300A | 209.97A | [12 empty] | Steel/Wrought Iron |  |  | WRAP REPAIRED WITH TAP. WRAP SAMPLE TAKED. SEE ATTACHED SKETCH. GPS DATA AVALIABLE FROM GEAN MUSE CO. 5834146
|  | 300A | 217.639 | [15 empty] | N 35.03342; W 118.16825; ; 12- 1 1/4" HOPE CONDUIT BORED UNDER L- 300A 10' & BELOW BOTTOM OF LINE 300A
|  | 300B | 217.688 | [15 empty] | N35.03340; W118.16825; ; 12-11/4" HOPE CONDUIT BORED UNDER LINE 300B 10' BELOW BOTTOM OF LINE 300B
|  | 300A | 218.67 | [15 empty] | LONG 116.18532; LAT 19.03452; ; SOME WATER BETWEEN PIPE & WRAP. BROWN "PAINT" BETWEEN PIPE & WRAP- MAY BE SAME TYPE OF COATING OR PRIMER FOR WRAP. 385' UPSTREAM...MLV 21873A
|  | 300A | 218.7 | [15 empty] | LONG 116.03464; LAT 116.18621; ; SOME WATER BETWEEN PIPE & WRAP; BROWN "PAINT" BETWEEN PIPE & WRAP MAYBE SOME TYPE OF COATING OR PRIMER FOR WRAP. 231 UPSTREAM OF MLV 218.73A
|  | 300A | 226.09 | 34 | Transmission | [7 empty] | 2009-10-05 | Other | GRIND | Steel/Wrought Iron |  |  | GRIND OUT GOUGES; MAG PARTICLE TEST PERFORMED= VALLEY INDUSTRIAL
|  | 300A | 238.48 | [12 empty] | Steel/Wrought Iron |  |  | iNSTALL TEST LEADS AT M.P. 238.5A. PICTURE NEXT PAGE
|  | 300A | 246.16 | 34 | [11 empty] | Steel/Wrought Iron |  |  | INSTALL TEST LEADS L-300A M.P. 246.16
|  | 300A | 246.81A | 34 | [11 empty] | Steel/Wrought Iron |  |  | INSTALL TEST LEADS L-300A M.P. 246.81A;
|  | 300A | 249.03-A |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 300A; 249.03; 30604260; ; ; INSTALL E.T.S. STATION M.P. 249.03A;
|  | 300A | 258.14-A |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | INSTALL E.T.S. STATION M.P. 258.14-A
|  | 300A | 259.94-A |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | INSTALL E.T.S. STATION M.P.259.94A
|  | 300A |  | 0.34 | Transmission | [13 empty] | SO#6083863-01; RT+300A; M.P. 261.04; JOB#6083863
|  | 300A | 261.08 | 0.34 | Transmission | [13 empty] | JOB#6083863
|  | 300A | 261.65 | 34 | Transmission | [13 empty] | INSTALL E.T.S. TEST STATION
|  | 300A | 263.09-A |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ISNTALL E.T.S. STATION M.P.263.09-A
|  | 300-A | 269.86 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 300A; 269.86; 3064260;; ; INSTALL E.T.S. STATION 269.86 LINE 300A
|  | 3001A | 270.85 | 34 | Transmission
|  | L-300A | 270.85 | 34 | [11 empty] | Steel/Wrought Iron |  |  | L300A MP 270.85
|  | 300A | 271.91A | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | M.P. 271.91A
|  | 300A | 271.9824 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | EXPOSED 40 FEET ... WITH NEW PIPE, CLASS ...LONG STEM DSAW WELL T .375
|  | L-300-A | 372.11
|  | 300A | 275.0071 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | EXPOSED FOR FUTURE TIE-IN POINT, CLASS CHANGE
|  | 300A | 275.02 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | M.P. 275.02
|  | L-300 A | 275.46
|  | 300A | 276 |  | Transmission | [10 empty] | Steel/Wrought Iron |  | BAKERFIELD
|  | L300A | 275.6149 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L300A M.P. 275.6149 JOB 7051316
|  | L300A | 276.5302 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-300A, M.P. 276.5302, JOB 7051316
|  | 300 | 277.6 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-300-A, M.P. 277.6 STAND BY FOR RUBENS PIPELING SERVICE, POT HOLEING GAS MAIN TO FIND ANGLE POINT ON PIPELINE BEFORE HEADING DOWN UNDER A CANAL (FOR SURVEY_. APPROX 50 FEET SOUTH OF CANAL GAS LINE STATS TO ANGLE DOWN.
|  | L-300A | 277.84A | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | USA TICKET#116528, L-300A, M.P. 277.84A
|  | 300A | 273 | 0.36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 3049337, 300A, M.P. 273.81
|  | 300A | 278.1 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  | BAKERSFIELD | SO # 7062246, RT= 300A, M.P. 278.09; NEW INSTALLATION NO LEAKS; L-300A BUENA VISTA RD. BAKERSFIELD MP. 278.10. EXISITING 36" PIPE X-60, DSAW 0.580"WT; NEW 36" PIPE- X60/X65 DSAW 0.500"WT
|  | 300A | 278.09 |  | Transmission | [10 empty] | Steel/Wrought Iron
|  | L-300-A | 278.09 | [9 empty] | 2001-05-18 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | WELD REPAIR BAND OVER GOUGE; CONTRACTOR INSTALLING A 60' CEMENT SEWER LINE 20" DEPTH GOUGED OVER GAS MAIN WELD A 36" REPAIR BAND OVER GOUGE; CHURCH
|  | 300A | 280.58 | 34 | [11 empty] | Steel/Wrought Iron |  | BAKERSFIELD | SO# 7062246, RT 300A, MP 280.02; NEW INSTALLATION NO LEAKS; L300A KKERN STATION MP. 280 EXISTING 34" PIPE -X60 DSAW, 0.460"WT. NEW 34" PIPE X-60 DSAW, 0.505" WT
REQUEST PER ENG. PIPELINE
|  | LINE 300-A | MP 280.54 | [15 empty] | G.C. CREW POT FOR FUTURE INSTALLMENT OF FILTER S/ OPERATOR
|  | L-300 A |  | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | EXPOSED FOR INSERTION METER INSTALLATION
|  | L-300-A | 281.07 | [12 empty] | Steel/Wrought Iron |  |  | INSTALL E.T.S. STATION M.P. 281.07 L-300A
|  | 300A | MP 281.6 |  | Transmission | [13 empty] | INSTALL E.T.S. STATION .L-300A M.P. 281.6
|  | L-300 A | 282.8 | [15 empty] | NEW WATER LINE BEING INSTALLED
|  | L-300 A | 284 | 34 | Transmission | [13 empty] | L-300A M.P. 254.; NEW GAS SAMPLE BEING INSTALLED
|  | 300-A | 292.15-B |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 300A; 292.15; PM 30604260; ; INSTALL E.T.S. STATION L-300A, M.P. 292.15B
|  | 300A | 299 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-300A 299.00
|  | L-300 A | 299.5 | [15 empty] | STND BY WHILE WATER LINE CROSSING
|  | 300A | 299.76 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | INSTALL TEST LEADS, L-300A MP 299.76
|  | 300A | 305.13A | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  | LOST HILLS | EXPOSED LINE TO INSTALL NEW E.T.S. @ MP 305.13A; MAP IS ATTACHED
|  | L300A | 337 | [15 empty] | GOUGE ...12 O'CLOCK PORTION...LINE...ABOUT 5 INCHES. IT STARTED AT 002 DEPTH AND WENT TO .016 DEPTH. THE METAL WAS RUBBED OFF WITH THTE LEAK SIDE OF BUCKET. ABOUT A 1/3 OF INCH WIDE. NO SHARP EDGES
|  | 300A | 339.50A | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  | KETTLEMAN CITY | EXPOSED LINE TO INSTALL NEW E.T.S. @ MP. 339.50A MAP ATTACHED
|  | 300A | 340.58 | 0.34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | INSTALL E.T.S. STATION M.P.340.58 LINE 300A
|  | 300A | 341.2 | 0.34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 300A; 341.20; PM 30604260;; ; INSTALL E.T.S. STATION 341.20 LINE 300A;
|  | 300A | 343.31A | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  | KETTLEMAN CITY | INSTALLED NEW COUPON @ M.P. 343.31A MAP ATTACHED
|  | 300A | 346.56A | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-300A, M.P. 346.5576, DIST L-300N; COMPLETED BY DON OLIVEIRA. INSTALLED TEST LEAD @ M.P. 346.56A MAP ATTACHED
|  | 300 A | 353.85 | [15 empty] | THE FORM MADE OUT FOR SITE 3 ON THE 12" PIPING
|  | 300A | 353.85 | [15 empty] | THIS FORM IS MADE OUT FOR SITE 1 ON THE 12" PIPING
|  | 300A | 353.9 | 34 | [13 empty] | AVENAL | NG LIQUIDS, LINE LOOKED VERY GOOD, COATING APPEARED TO BE IN GOOD CONDITION WE INSTALLED A NEW VALVE 3539"A" (24" VALVE) PIPE AND VALVE MEASURED 35'
|  |  |  | 0.34 | [11 empty] | Steel/Wrought Iron |  |  | CONTRACTORS WILL INSTALL 34" PIPE TO CONNECT NEW PLANT TO 300
|  |  | 354-A | 34 | Transmission | [13 empty] | PIPE TO SOIL .916 READING. FOUND, SMALL AMOUNT OF MOISTURE. INSPECTION TOP AND BOTTOM OF PIPE AND FOUND A SMALL AMOUNT OF RUST AT THE BOTTOM WIRE BRUSED AND REWRAPPED PIPE. CHECK OK. NOTE: SEE MAP FOR LOCATION (NEXT PAGE)
|  | 300A | 354.1401 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT= 300A, M.P. 354.1407; L-300A...INSTALL
|  |  | 355.78 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT= 300A; M.P. 355.78
|  | 300A | 362.6389 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 8071896-05, L-300A, M.P. 362.6389 (PASJARO CREEK CROSSING); PASAYARD CK.
|  | 300A | 368-A | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | INSTALL TEST LEAK M.P. 368-A
|  | 300A | 371-A | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | CONTRACTOR INSTALLED 8" PLASTIC LINE UNDER OUR ROW. WE HAVE 21" COVER PLASTIC WATER LINE WAS INSTALLED 78" DEEP, WITH 13" BETWEEN PIPES. MP. 371-A.
|  | 300A | 379.9706 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 8071896-05, L-300A M.P. 379.9706 (SALT CREEK CROSSING)
|  | L-300 A | 382.82 | [15 empty] | POT HOLE USA#379125
|  | L-300 A | 393.53 | [15 empty] | ROUTE 300A; MP 393.53; PROJECT TO INSTALL INSERSION MADE AT PANOCHE STA.
|  |  | 410.73A | 0.16 | Transmission | [13 empty] | RT= X, M.P. 0.20, SERT 300A, M.P. 410.73A SO#7043027
|  |  | 410.73A | 0.12 | Transmission | [13 empty] | RT= X; RT= 300A; M.P. 410.73; SO#7043027;
|  |  | 410.73 | 0.34 | Transmission | [13 empty] | RT=300A; M.P. 410.73; SO# 7043027
|  |  | 411.74A | 0.34 | Transmission | [13 empty] | RT = 300A; M.P. 411.74A; SO# 7043027; MP - 410.73
|  | 300A | 413.05 |  | Transmission | [10 empty] | Steel/Wrought Iron |  | PANOCHE | A FORM FILE SO#7042439-05 L-300A, MP 413.0441; MAIN WAS NOT UNCOVERED AT THIS LOCATION
|  |  | 418.86 | 0.24 | Transmission | [13 empty] | SO#7043027; RT+300A (X-TIE); M.P. 418.86
|  |  | 418.88 | 0.24 | Transmission | [13 empty] | SO#7043027 ; RT= 300A; M.P. 418.88
|  |  | 418.88 | 34 | Transmission | [13 empty] | SO#7043027; RT = 300A; M.P. 418.88
|  |  | 418.94 | 34 | Transmission | [13 empty] | SO#7043027; RT= 300A; M.P. 418.94
|  | 300A | 428.26 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  | PAICINES | SO# 7047705 ; RT= 300A; M.P. 428.26;; ; MAIN WAS NOT UNCOVERED. PROBE INDICATES 4' OF COVER UNDER MAT WHERE RD. CROSSES MAIN.
|  |  | 429.51A | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT= 300A; M.P. 429.51A; SO# 7043027
|  |  | 0.05 | 0.12 | [11 empty] | Steel/Wrought Iron |  |  | RT= 300A; M.L.V. 429.51A; RT = X, M.P. 0.05; SO#7043027
|  | 300A | 431.96 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  | PAICENES | 300A M.P. 431.96; SO# 8048742-01;; ; WRAP IN BETTER CONDITION THAN USUAL SEEN ON THIS MAIN.
|  | 300A | 432.92 | 34 | Transmission | [7 empty] | 2001-08-27 |  |  | Steel/Wrought Iron |  |  | RECOATING 300A
|  | 300 A | 432.92 | 34 | Transmission | [7 empty] | 2001-08-24 |  |  | Steel/Wrought Iron |  |  | RECOAT 300A
|  | 300 A | 433.04 | 34 | Transmission | [7 empty] | 2001-08-28 | Other |  | Steel/Wrought Iron |  |  | RECOATING 300A; OLD TAR COATING FAILED, SAND BLASTED AND RECOATED WITH POWER CRETE "2"
|  | 300 A | 434 | 34 | Transmission | [7 empty] | 2001-08-15 |  |  | Steel/Wrought Iron |  |  | RECOAT 300A
|  | 300A | 434 | 34 | [8 empty] | 2001-08-22 |  |  | Steel/Wrought Iron |  |  | RECOAT 300A
|  | 300 A | 435.75 | 34 | [8 empty] | 2001-08-17 |  |  | Steel/Wrought Iron |  |  | RECOAT 300A
|  | 300 A | 436 | 34 | Transmission | [7 empty] | 2001-07-23 |  |  | Steel/Wrought Iron |  |  | RECOATING 300A;
|  |  |  | 0.34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | M.L.V 436.74A; RT= 300A ; SO# 7043027;; PITS REMOVED DURING TIE-IN
|  | 300A | 437.74 | 34 | [8 empty] | 2001-07-05 |  |  | Steel/Wrought Iron |  |  | RECOAT 300 A
|  |  | 445.32 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO 7043027; RT = 300A (BD) ; M.P. 445.32
|  |  | 445.32 | 0.34 | [14 empty] | SO# 7043027 ; RT = 300A; M.P. 445.32
|  | 300A | 443.8 | [12 empty] | Steel-Other
|  | 300A | 453.6 | [12 empty] | Steel/Wrought Iron |  |  | 300A M.P. ....; NORTH SIDE AT... ROAD
|  |  | 458.32A | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT = 300A; M.P. 458.32; SO #7035589;; ; PIPE LOCATION IS 458.32 A HWY 156
|  | 300A | 460.98 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE 300A, M.P. 460.8361;; LINE L-300A, ILI #3; M.P. 460.98; LATIT 36 58 27.22345. LONG - 121 28 03.16980; ; mISC. COMMENTS/INFORMATION: THIS SITE IS LOCATED 2.7 MILES NORTHWEST OF INTERSECTION OF SHORE ROAD AND LAKE ROAD. 50' NORTH OF NORTH EDGE OF LAKE ROAD IN FIELD IN HOLLISTER, CA. ORIGINAL GPS LOCATION WAS 19' OFF LINE. FOOTAGE WAS TAKEN FROM AGM#51. FOOTAGE DIFFERENCE WAS 42'. ANOMALY WAS LOCATED WITH GW 18200.; THIS SIRE WAS REDUCED FROM 10' TO 2' INSPECTION AREA AROUND ANOMALY PER MIKE WEST. MIC TEST COMPLETED. INOCULATION ON 6/16/2010 AT 2:44 PM AND TURNED ATS FOR RESULT ANALIZATION. EXTERNAL CORROSION WAS LOCATED ON PIPE AT 10:33. TWO CELLS WERE MAPPED OUT AND INFOMATION WAS SENT TO PG&E'S TODD ARNETT ON 6/16/2010. NO OTHER CORROSION WAS FOUND ON INSPECTED AREA. MINOR SURFACE RUST NEAR ANOMALY. MT WAS PERFORMED BY ATS ON 6/16/2010 WITH NO INDICATIONS FOUND. ON 6/17/2010 TODD ARNETT'S REVICE (RSTRENG) OF THE EXTERNAL CORROSION DATA RESULTS WERE TO RE-COAT. THE PIPE WAS RE-COATED WITH PROTAL 7200. WAX TAPE WAS PUT ON TRANSITION ENDS. A LAYER OF TUFF-N-NUFF WAS PLACED OVER COATING. A COUPON E.T.S. AND REFERENCE CELL WERE INSTALLED. SITE WAS BACKFILLED WITH NATIVE SOIL
|  | 300A | 460.84 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE 300A, M.P. 460.9795;; LINE 300A ILI PRIORITY #2; M.P. 460.84; LATIT 36 58 33.67354, LONG - 121 28 07.94018; ; MISC. COMMENTS. INFORMATION: THIS ILI SITE CONTAINED AN ANOMALY 14.34' D/S FROM GW 18460. A 3' REGION AROUND THE ANAMOLY WAS INSPECTED PER MIKE WEST. ONLY THE ONE EXTERNAL CORROSION CELL WAS FOUND WITH A MAX PIT DEPTH OF 124 MILS (36% WALL LOSS), ALL REMAINING CORROSION WAS LESS THAN 10% WALL LOSS. THE PIT CONTAINED CORROSION PRODUCT AND IT WAS COLLECTED IN A VIAL AND A MIC TEST WAS INNOCULATEED ON 6/17/2010. THE MIC TEST WAS THEN GIVEN TO PG&E ATS FOR RESULT ANALYZATION. ALSO, ON 6/17/2010, ALL OF THE EC#1 DATA WAS EMAILED TO TODD ARNETT FOR ANALYSIS. HE RESPONDED THAT THE ANAMALY HAD PASSED RSTRENG AND NO REPAIRS WERE NEEDED VIA EMAIL ON 6/18/2010. THE INVESTIGATION OF GW 18460 AREAS WHERE COATING WAS REMAOVED, AS WELL AS THE INSPECTED 3' REGION OF PIPE, WERE RECOATED WITH PROTAL 7200 AND A COUPON WAS INSTALLED AT THE DOWNSTREAM EDGE PER MIKE WEST. OVERALL DITCH WAS SLOPED (61' X 30').
|  | 300A | 461.07A | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT= 300A; M.P. 461.07; SO # 7035589;; REMOVED GAS VALVE YARD AT MLV 461.07A PRESURE LIMITING STATION 6AX 34" LINE 300A
|  | 300A | 462.23 | [12 empty] | Steel/Wrought Iron |  |  | 300A, MP. 4...; SOUTH SIDE OF ... AVE
|  |  | 462.24A |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT = 300A; M.P. 462.24; SO# 7035589; M.P. 462.24A GILROY TAP
|  |  | 464.16A | 0.34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT = 300A ; MP 464.16A; SO# 7035589;; ; REPLACED 24" VALVE AT CROSS OVER TIE BETWEEN 300A & 300B LINE CANADA RD.
|  |  | 468.76 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT = 300A; MP 468.76; SO# 7035589;; ; 200 N/O DUTCHESS CT. ON BRIDLE PATH DR. GILROY
|  | 300A | 473.4 | 34 | Transmission | [6 empty] | 2006-12-29 | 2007-02-16 | Other | GROUND OUT SCRATCHES | Steel/Wrought Iron |  | MORGAN HILL | GROUND OUT SCRATCHES BACK FILLED, PLACED CONCRETE BAGS OVER LINE; KURT STRUMPH NOTICED EXPOSED AND DAMAGED PIPE DURING LEAK SURVEY WORK IN DEC 2006. TURNED IN PIPLING RISK REPORT. TODD ARNETT FOLLOWED UP ON REPORT AND ASSESSED DAMAGE 9/15/07. PRELIMINARY INSPECTION REVEALED GAUGES @ .020 DEPTH. L-300A WAS OPERATING @ 525 PSI. AND MAINTAINED AT THAT PRSSURE OVER NIGHT. LINE WAS EXPOSED AND GAUGES MEASURED UP TO .026" MAX
|  | 300A | 474.73 | [12 empty] | Steel/Wrought Iron
|  | 300A | 474.74 | [12 empty] | Steel/Wrought Iron
|  |  | 475.27 | 0.34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT= 300A; MP 475.27; SO# 7035589;; TRENCHED AT MILE MARKER 40. SHAFTER RD. MORGAN HILL. WELDED 3/4 SAVER ON LINE, THERE WAS NO TEE ON MAIN "SIDE TAP"
|  |  | 475.76A | 0.34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 300A; M.P. 475.76; SO # 7035589;; ; DIANA MP 475.76-A
|  | 300 A | 476.9 | 34 | Transmission | [12 empty] | MILPITAS | GPS FILE R0127HA LOC #1
|  |  | 476.26 | [15 empty] | RT = 300A; M.P. 476.26; SO# 7035589;; 159' E/O ESTATES DR. ON ROOP RD. GILROY
|  |  | 476.27 | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT= 300B; MP 476.27; SO# 7035589;; ; PIPE HAS A LOT OF BARE SPOTS
|  | 300A | 477.07 | [14 empty] | MORGAN HILL | RT = 300A; M.P 477.07;; GSAVE 477.07. PEET RD AT POWER POLE EXIT SIDE OR PEET RD.
|  | 300A | [16 empty] | LOCATION AT PEET RD. AND MISSION AVE. IN MORGAN HILL. CONTRACTOR HAD TO DIG UNDER LINE TO INSTALL SEWER LINE
|  |  | 477.15 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT = 300A; MP 477.15; SO# 7035589;; ; 738' S/O COCHRANE RD. ON PEET RD. MORGAN HILL
|  | 300A | [16 empty] | TRENCHING ACROSS 300A BY (TOM) TRI...CONST. FOR A STORM DRAIN GOING IN. LOCATION PEET RD & COCHRANE RD. FOR DIVIDERS ....PROJECT.
|  | 300A | 477.5 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  | MORGAN HILL | GPS FILE R090719A
|  | 300A | 477.6 | [15 empty] | ABANDON OF HIGH TO HIFH SET SHUR OFF TEE, CUT AND CAP 3/4" PIPE TO ISOLATE FROM 300A. 38" TO TOP OR TEE 33 FEET FROM EDGE OF PEET RD.
|  | 300A | 477 | 34 | [11 empty] | Steel/Wrought Iron
|  | 300A | 477.67 | 34 | [11 empty] | Steel/Wrought Iron |  | MORGAN HILL
|  | 300A | 477.61 | 34 | [11 empty] | Steel/Wrought Iron |  | MORGAN HILL
|  | 300A | 483.58 | 34 | [13 empty] | SAN JOSE | L-300 A 483.58
|  | 300A | 438.5 | 34 | [11 empty] | Steel/Wrought Iron |  | SAN JOSE | #1 LOCATION
|  | 300A |  | 34 | [11 empty] | Steel/Wrought Iron |  | SAN JOSE; | #2 LOCATION
|  | 300A |  | 34 | [13 empty] | SAN JOSE | # LOCATION 3
|  | 300A |  | 34 | [11 empty] | Steel/Wrought Iron |  | SAN JOSE | #4 LOCATION
|  | 300A |  | 34 | [11 empty] | Steel/Wrought Iron |  |  | #5 LOCATION
|  | 300A |  | 34 | [11 empty] | Steel/Wrought Iron |  | SAN JOSE | #6 LOCATION
|  | 300A | 486.7 | [14 empty] | SAN JOSE | RT = 300A; M.P. 486.8006;; ; TENNANT AVE & BASKINS RIDGE BY E.T.S. STATION
|  | 300A | 486.85 | 34 | [11 empty] | Steel/Wrought Iron |  | SAN JOSE | GPS FILE R010122A LOC#1
|  | 300 | 487.6217 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 469 PIERCY RD. SAN JOSE; LINE 300; M.P. 487.6217; LATITUDE 37 15 33.59046; LONGITUDE 121 46 50.44714
|  | 300A | 487.6217 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ROUTE 300A M.P. 487.62217; LAT= 37.259 33068; LONG 121.7806798;; ; 469 PIERCY RD. SAN JOSE; MP 487.6217; LATITUDE 37 15 33.59046; LONGITUDE 121 46 50.44714
|  |  | 487.6217 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT = 300A; M.P. 487.6217;; ; 469 PIERCY RD. SAN JOSE; MP 487.6217; LATITUDE 37 15 33.59046; LONGITUDE 121 46 50.44714; ;
|  | 300A | 487.64 | 34 | [13 empty] | SAN JOSE | GPS FILE R010122A LOC #2
|  |  | 487.78A | 0.34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7035589; RT = 300A; M.P. 487.78;; ; FONTANOSO MP 487.78A
|  |  | 487.78 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7035589; RT = 300A; M.P. 487.78;; ; REPLACED TWO 12" VALVES AND 34"
|  | 300A | 487.79 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN JOSE | GPS FILE R090719B
|  | 300A | 487.87 | 34 | Transmission |  | Girth Weld | [10 empty] | SAN JOSE
|  | 300A | 488 | 34 | Transmission | [12 empty] | SAN JOSE
|  | 300A | 488.25 | 34 | [13 empty] | SAN JOSE
|  | 300 A |  | 34 | [14 empty] | GPS FILE 062908A LOC1
|  | 300A | 489.14 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-300A, M.P. 489.14, CO# 803556-01 HYDRO TEST (CLASS CHANGED)
|  | 300A | 489.38 | [15 empty] | RT = 300A; M.P. 489.38
|  | 300A | 489.6 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO # 7008453-03 ; RT = 300A; MP 489.6613;; ; RECOAT SPAN @ M.P. 489.60 FOR BACKFILL BY APPLICANT;; SAND BLAST & RECOAT 20' SECTION OF L-300A, WITH POWERCRETE J FOR BACKFILL BY APPLICANT. ;
|  | 300A | 490.35 | 34 | Transmission |  | Girth Weld |  |  |  |  | 2000-01-13 | [5 empty] | SAN JOSE | G.P.S. FILE# LOCATION #6
|  | 300A | 497.36 | 34 | Transmission | [12 empty] | SAN JOSE
|  | 300A | 490.32 | 34 | Transmission
|  | 300A | 490.39 | 34 | Transmission |  | Girth Weld |  |  |  |  | 2000-01-13 | [5 empty] | SAN JOSE
|  | 300A | 490.42 | 34 | Transmission |  | Girth Weld |  |  |  |  | 2000-01-13 | [5 empty] | SAN JOSE | G.P.S FILE # LOCATION #8
|  | 300A | 490.46 | 34 | Transmission |  | Girth Weld |  |  |  |  | 2000-01-13 | [5 empty] | SAN JOSE | G.P.S. FILE # LOCATION #9
|  | 300A | 490.48 | 34 | Transmission |  | Girth Weld |  |  |  |  | 2000-01-13 | [5 empty] | SAN JOSE | G.P.S. FILE # LOCATION #10
|  | 300A | 498.48 | 34 | Transmission | [7 empty] | 2001-06-22 | Other |  |  |  | SAN JOSE | GOUGE & SCRATCHED WHERE LESS THAN 8% OF W.T. FREATHER OUT WILL GROUND; NOTIFY TODD ARNETT WENT OVER ON HOW TO REPAIR DO TEH REPAIR. FOLLWOING THE GAS STANDARDS A-65
|  | 300A | 490.49 | 34 | Transmission | [12 empty] | SAN JOSE
|  | 300A | 490.51 | 34 | Transmission | [12 empty] | SAN JOSE
|  | 300A | 490.52 | 34 | Transmission |  | Girth Weld |  |  |  |  | 2000-01-13 | [5 empty] | SAN JOSE | G.P.S. FILE # LOCATION # 11
|  |  | 490.6 | 0.34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT = 300A; APPROX MP 490.60; SO# 7035589;; ; FOUND PIPE HAD BEEN PATCHED WRAPPED DUE FROM BEING HIT BY SOMETHING
|  | 300A | 490.6 | 34 | Transmission |  | Girth Weld | [10 empty] | SAN JOSE | L-300A MP 490.60
|  | 300A | 490.63 | 34 | Transmission |  | Girth Weld |  |  |  |  | 2000-01-13 | [5 empty] | SAN JOSE | G.P.S FILE # LOCATION #12
|  | 300A | 490.63 | 34 | Transmission |  | Girth Weld |  |  |  |  | 2000-01-13 | [5 empty] | SAN JOSE | G.P.S. FILE # LOCATION #12
|  |  | 490.63 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7035589; RT = 300A; M.P. 490.63;; PLS-7 SOUTH END
|  |  | 490.67 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7035589; RT = 300A; MP 490.67;; ; PLS- 7 NORTH END
|  |  | 490.7 | 0.34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT = 300A APPROX MP 450.70 SO# 7035589
|  | 300A | 493.03 | [15 empty] | RT= 300A ; MP 493.03;; ; TULY & CAPITOL MP 493.03
|  | 300A | 493.08 | 34 | [13 empty] | SAN JOSE
|  | 300A | 493.38 | 34 | Transmission >= 20% SMYS | [7 empty] | 2002-01-14 | Other | REMOVED CASING | Steel/Wrought Iron |  | SAN JOSE | L-300AM M.P. 493.38; LINE 300A REMOVED CORRIGATED CASING (150') ON 300A CROSSING CAPITAL EXPRESSWAY. WORK COMPLETED ON JAN 14, 2002. EXCEPT FOR 4 LOCATIONS WHERE CASING WAS LAYING ON PIPE WATER TABLE HIGH IN THE .... COMPLETLY WRAP 150' OF PIPE. WUSED STAC WAX ....ON 300-A
|  | 300A | 493.9 | [15 empty] | DIV: SAN JOSE. BB 300A M.P. 493.9
|  | 300A | 495 | 34 | Transmission |  | Tap Connection |  |  | External Corrosion |  | 2001-06-06 | [5 empty] | SAN JOSE
|  |  | 495.45 | 0.34 | Transmission | [13 empty] | SO# 7035589; RT = 300A ; APPROX MP 495.45
|  |  | 495.50A | 0.34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO@ 7035589; RT = 300A; M.P. 495.50;; HOLISTER PIG LAUNCHER. ALUM ROCK MP 495.50A;
|  | 300A | 495.5 | [15 empty] | DIV: SAN JOSE 300A 495.61; MEARS PRJ. TO RECOAT AND INSPECT LINE AT ...APPROX 50' FROM GEBHART AND ...HWY
|  | 300A | 496.11 | 34 | Transmission | [12 empty] | SAN JOSE
|  | 300A | 496.15 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN JOSE | L-300A; MP 496.15; SO# 703661-02;; ; FROM 9-1-01 TO 12-15-01 WE REMOVED THE CORRIGATED, NESTABLE CASING & CENTRALIZERS. WE FOUND 4 LOCATIONS WHERE THE CASING HAD MADE METAL TO METAL CONTACT WITH LINE 300A. WE TESTED THE COATING AND REPAIRED ALL BAD SPOTS WITH "STACKWRAP" AS A OVER COAT TO THE EXISTING TAR COATING
|  | 300A | 497.22 | [14 empty] | SAN JOSE | RT 300A; MP 497.22;; ; L300A AT PEV TENCIA CREEK DRIP G.C. TO REMOVE DRIP HERE. BILL.... 408-505-3695
|  | 300A | 497.25 | [15 empty] | GIS L-300A MP 497.25; ...RIGHT OF WAY AT END OF DAHLIA CT. THRONG DOUBLE DIVERS ....FWY 680 LISA @0333270
|  | 300 A | 497.3 | [15 empty] | RT = 300A; MP 397.30;; ; NORTH OF ....CREEK DRIP BY ABOUT 500' SNIFF HOLE FOR ...DRIP OPERATION
|  | 300A | 498 | 34 | Transmission |  | Girth Weld | [10 empty] | MILPITAS | GPS FILE # R 112315A, LOC #4
|  | 300A | 498 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  | MILPITAS | LOC # 2 GPS FILE R 081315A
|  | 300A | 498.37 | 34 |  |  | Girth Weld | [10 empty] | SAN JOSE | I LINED THIS UP AS SHOWS ON L100 INSPEC REPT.
|  | 300A | 498.95 | 34 | [11 empty] | Steel/Wrought Iron |  | MILPITAS
|  | 300A | 499.66 | [12 empty] | Steel/Wrought Iron
|  | 300A | 499.9 | 34 | Transmission |  | Girth Weld | [10 empty] | MILPITAS | L 300A, MP 499.81; GPS FILE 072510A LOC#2
|  | 300A | 499.9127 | [14 empty] | MILPITAS | DISTRICT = MILPITAS L-300A MP 499.9127 (POT HOLED); PIT HOLED FUTURE UTA PROPOSED... LINE 300A USA TICKET # 0306021. IN THE PARK/INLOT OF ADDREES 760 E/ CAPITOL/ APPIAN AND ....
|  | 300A | 500 | 34 | [11 empty] | Steel/Wrought Iron |  | MILPITAS
|  | 300A | 500.01 | [15 empty] | RT 300A; MP 500.01; POT HOLE FOR UTILITES 300A ON CAPITOL AVE. APPROX AT CORNER OF LEFT FAST LAKE HEADING NORTH BOUND APPROX 300' SHOUTH OF ....STATION STREET
|  | 300A | 500.04 | [14 empty] | MILPITAS | L300A, 500.04; LOCATION
|  | 300A | 500.09 | [14 empty] | MILPITAS | L-300A, 500.09; LOCATION
|  | 300A | 500.12 | 34 | Transmission |  | Girth Weld | [10 empty] | MILPITAS | GPS FILE 021417A LOC #3
|  | 300A | 500.17 | [14 empty] | MILPITAS | L-3004, 500.17; LOCATION #6
|  | 300A | 500.4 | [14 empty] | MILPITAS | NEW 300A
|  | 300a |  | 34 | Transmission |  | Girth Weld | [10 empty] | MILPITAS | OLD LINE 300A
|  | 300A | 501 | 34 | [11 empty] | Steel/Wrought Iron |  | MILPITAS | LOC#2 GPS R081317A
|  | 300A | 500.57 | [14 empty] | MILPITAS
|  | 300A | 500.71 | 34 | Transmission |  | Girth Weld | [10 empty] | MILPITAS | R060615B LOC #2
|  | 300A | 500.71 | 36 | Transmission |  | Girth Weld | [10 empty] | MILPITAS | R060615B LOC #4
|  | 300A | 500.77 | 34 | Transmission |  | Girth Weld | [10 empty] | MILPITAS | GPS FILE R03....LOC #4
|  | 300A | 500.77 | 34 | Transmission |  | Girth Weld | [10 empty] | MILPITAS | GPS FILE R3...LOC #2
|  | 300A | 500.84 | [14 empty] | MILPITAS
|  | 300A | [16 empty] | SO# 7023881, 300A
|  | 300A | 500.87 | 34 | Transmission |  | Girth Weld | [10 empty] | MILPITAS | GPS FILE R032318A
|  | 300A | 500.92 | 34 | Transmission | [12 empty] | MILPITAS | L-300A MP 500.91; GPS FILE 072516A
|  | 300A | 501.46 | 34 | Transmission | [12 empty] | MILPITAS | LOCATION #1
|  | 300A | 501.65
|  | 300A | 501.69 | 34 | Transmission |  | Girth Weld | [10 empty] | MILPITAS | LOCATION #5;
|  | 300A | 501.67 | 34 | Transmission |  | Girth Weld | [10 empty] | MILPITAS | LOCATION #4
|  | 300A | 501.7 | [15 empty] | GPS FILE # PRESCHOOL
|  | 300A | 501
|  | 300B | [16 empty] | DIST: HOLLISTER SO#7049826-05, L-300B MLV 445.32B, BD 608, M.P. 0.0011; MLV 445.32B
|  | 300B | [16 empty] | DISTRICT: HOLLISTER, SO#7049826-05 (L300B, MLV 419.11B) X6509 , MP 0.0025; MLV 41911B
DIST: L300N, SO# 7049826-05; 1) X6508, MP 0.0015; 2) DF8923, MP0.0030
|  | 300B | 140.91B | [15 empty] | SO# 7064907-07, DAGGETT MTR. STA. L-300B, M.P. 14091B, DISTRICT G300S B0577, MP 0.0032 (SEG 611-612)
|  |  |  | 6 | Transmission | [8 empty] | Other | INSTALL SAV-A-VALVE | Steel/Wrought Iron |  | HOLLISTER
DISTRICT: HOLLISTER SO#7049826-05 (L-300B MLV 419.11B) X8929, MP 0.0057
DISTRICT: HOLLISTER SO#7049826-05 (L-300, MLV 419.11B) BD603 MP 0.0065
SO# 7046070; ROUTE 300B-1; MP 0.49; ; NEEVLES TAP 6" BERFORE VALVE #4
|  | 300B | 0.96 | 34 | [14 empty] | RT = 300B, MP 0.9604
|  | 300A & 300B | 3.90A & 2.50B | [15 empty] | 4.08A
|  | 300B | 4.10B & 4.97B
|  | 300B | 5.97 | [15 empty] | ISNTALLED COUPON @ E.T. STATION @ MILS 5.9713 ON 300B
|  | 300B | 7.87 | [15 empty] | C.P. ACTION 300 A & B EAST SIDE OF HWY 95
|  | 300 | 7.88 | 34 | Transmission | [13 empty] | PART OF C.P. ACTION FOR 300 A & B WEST SIDE OF HWY 95
|  | 300B | 7.94 | 34 | Transmission
|  | 300B | 40.49B | [15 empty] | EXPOSED...RO ISNTALL C.P.....EPR 3-31-03
|  | 300B | [16 empty] | L300B, 49.79
|  | 300B | 49.4698 | [15 empty] | DISTRICT G300S, L-300B, M.P. 59.4698 SO# 8071896-06
|  | 300B | [16 empty] | DISTRICT G300S, L-300B, M.P. 60.1398 (MP 60.15) SO# 8071896-06; DRY WASH
|  | 300B | 80
|  | 300B | 87.40B | [15 empty] | LOOKS GOOD
|  | 300B | 87.40B | [15 empty] | NORTH SIDE OF TRACKS
|  | 300B | 87.41B | [15 empty] | NORTH SIDE OF HWY
|  | 300B | 87.41B | [15 empty] | SOUTH SIDE OF HWY
|  | 300B | 99.77 | 34 | Transmission |  |  |  |  | Damage by 3rd Party |  | 2007-01-08 | 2007-01-09 | Welded Sleeve/Can - Weld |  |  |  |  | L-300A MP 99.7242 SO#8081877 DIST. G300S; L-300B, MP 99.77; L-300B SPAM... MP 99.77 LOSA GUN SHOT DAMAGE
|  | 300B | 116 | [15 empty] | ROUTES L-300B MP 117.9881; SEE DRAWINGS STAND BY FOR HOOD CONSTRUCTION OVER VIEW
|  |  | 300B | 131.378 | [14 empty] | CROSSED L-300B W/2" STL LINE FROM L/300A AS AN ALT FEED TO REG SET
|  | 300B | 137.55B | [15 empty] | TAP LOCATION
|  | 300B | 139.56 | [15 empty] | ONE ...AROUND LINE STARTING ...TOP OF PIPE
|  | 300B | 141.7498 | [15 empty] | ROUTE 300B MP 141.7498; GPS UTM NAD 1983 ZONE 10 -116.85309 34.85860 USA@A0580639. CROSSING BY SO. CAL DRISON WITH TWO 4" PVC SCM 80 CONDUITS FOR FIBER OPTIC LABLES
|  | 300B | 141.95B | [15 empty] | CROSSING OF 2" PLASTIC PIPE 24" SEPARATION MAINTAINED
|  | 300B | 142 | [15 empty] | COOL WATER GERNERATING STATION.
|  | 300B | 145.477 | [15 empty] | LAT 34 52 01.075 N; LONG 116 55 17.539 W; ALT 1486
|  | 300B | 146.71B | [15 empty] | SO# 8056601-03, 300B, MP 146.71B; LAT 34 52 24.837N, LONG 116 56 05.054W ALT 2014. GPS FILE 141.71 A FORMS. MLV 146.71B TO BE REMOVED AND REPLACED WITH IPE 2" TAP TO BE CAPPED W/A 1" MUELLER TEE TO BE INSTALLED EXPOSED OVER 20' FOR VALVE REPLACEMENT. WRAP FOUND MESS BONDED WITH OBSERVABLE PROBLEMS. SECTION REPLACED AS PORT OF HYDRO TEST, SITE VISITED BY DAVE AGUIR. THIS IS MEARS MILE POINT 145.06B
|  | 300B | 146.71B | [15 empty] | MLV 146.71B TO BE REMOVED AND REPLACED WITH PIPE 2" TAP TO BE CAPPED W/A 1" MUELLER TEE TO BE INSTALLED. RAY, JOB ...NOT IN ... MAY BE...BIG...IN ...MP 130.38 TO ...
|  | 300A | 147.25A | [15 empty] | 30' V/S & 30 D/S TO BE REPLACED WITH NEW PIPE AS PART OF HYDRO TEST OF LINE 300A...
|  | 300B | 147.95 | [15 empty] | L 300B MP 147.95; 3' BY 16" OF PIPE EXPOSED IN WASH
|  | 300B | 148.1988 | [15 empty] | DISTRICT G 300S, L-300B MP 148.1988 SO# 7056786-06
|  | 300B | 149.49 | 34 | Transmission | [12 empty] | BARSTOW
|  | 300B | 150.06 | [15 empty] | FS 7905+32.1; GPS 34 53 54.161N; 116 54 03.576W; EL 204538'; WOS1984
|  | 300B | 153.51 | [15 empty] | MOJAVE WATER AGENCE INSTALLED 42" CONCRETE AND STEEL WATER LINE 18" UNDER THE CASING CONTAINING L300B. L-300B PIPE WAS NOT EXPOSED JUST THEE CASING. PICTURES EMAILED TO GENE MUSE EEM6
|  | 300B | 159.24B | [15 empty] | 4-22-99; 48" STEEL WITH CONCRETE III COATING WATE LINE CROSSING 25" BETWEEN LINES
|  | 300B | 160.41 | [15 empty] | LAT 34 54 00.305N; LONG 117 08 53.052W; ALT 2180; FILE NAME APL XING955F; TOPPED THE PIPE ONLY; NOTE: R&R GAS LINE 1" EXISTING DITCH
|  | 300B | 181.645 | [15 empty] | FS 9697+95.5; N 34 59.892 W 117 22.446; N 34 59 53.52; W 117 32 38.76
|  |  |  | 34 | [13 empty] | BAKERSFIELD | X-RAY AND TESTING DATA COLLECTED BY G.C. GAS AREA 4 AND THE PROJECT INSPECTOR. THIS A-FORM IS FOR TIE-IN LOCATION OF THE PIPELINE REPLACEMENT JOB IN BAKERSDIELD THAT WAS COMPLETED ON 5/21/2010. THE INFORMATION PROVIDED IS FOR THE OLD SEGMENT OF PIPE AT THE TIE=IN LOCATION
|  |  | 283.1435 | [14 empty] | BAKERSFIELD | 300B, MP 283.1435; X-RAY AND TESTING DATA COLLECTED BY G.C. GAS AREA 4 AND THE PROJECT INSPECTOR. THIS A-FORM IS FOR TIE-IN LOCATION OF THE PIPELINE REPLACEMENT JOB IN BAKERSFIELD THAT WAS COMPLETED ON 5/21/2010. THE INFORMAITON PROVIDED IS FOR THE OLD SEGMENT OF PIPE AT THE TIE-IN LOCATION.
|  | 300B | 181.6 | [15 empty] | 300B WAS CROSSED @ A POINT APPROOX 258' WEST OF LINE MARKERS ON WEST SIDE OF HWY 395 N OF HWY 58. A 6" PLASTIC SEWER LINE WAS INSTALLED BENEATH 300B ON A DIAGNAL 37" PIPE COVER AT LOCATION.
|  | 300B | 191.18B | [15 empty] | LONG 117 42 12.82785N; LAT 35 00 03.65071 W; ALT 2394; GPS FILE NAME MOK19118.SSF; ; CROSSING UNDER L-300 BY ARB FOR RERN. RIVER PIPE LINE. BORED UNDER LINE. NO C.P. WIRES JUST TOP OF LINE EXPOSED
|  | 300B | 210.06B | [15 empty] | WRAP REPAIRED WITH TAP. SEE ATTACHED SKETCH. GPS DATA AVAILABLE FROM GENE MUSE CO 538-4146
|  | 300B | 219.47B | [15 empty] | LONG 116.18569; LAT 35.03460; ; COME WATER BETWEEN PIPE AND WRAP. BROWN "PAINT" BETWEED PIPE AND WRAP MAYBE SOME TYPE OF COATING OR PRIMER FOR WRAP
|  | 300B | 219.5 | [15 empty] | LONG 116.18611; LAT 35.03464; ; SOME WATER BETWEEN PIPE AND WRAP. BROWN "PAINT" BETWEEN PIPE AND WRAP MAYBE SOME TYPE OF COATING OR PRIMER FOR WRAP
|  |  | 240.89B | [15 empty] | ISNTALL TEST LEADS MP 240.89B; ; 300B; 240.89; 30604260
|  | 300B | 246.71 | [15 empty] | INSTALL TEST LEAD L-300B MP 346.71
|  | 300B | 2466.72 | [15 empty] | TRENCH FOR UTILITIES USA# 214856
|  |  | 249.09B | [15 empty] | 300B; 249.09 ; 30604260;; ; INSTALL E.T.S. STATION MP 249.09-B
|  |  | 260.31B | [15 empty] | 300B; 260.31; 30604260;; ; INSTALL E.T.S. STATION MP 260.31B;
|  | 300B | 261 | [15 empty] | NE CORNER OF ARVIN LAND FILL. NOTES: WRAP DISBOUNDED AT THE SIX FEET OF EXPOSED AREA. BOTTOM SECTION OF PIPE IS FILLED WITH MUD AND WATER. RUST AND SMALL PIT ARE PRESENT
|  | 300B | 261 | [15 empty] | NE CORNER OF ARVIN LAND FILL. NOTE: LOWER PART OF PIPE WAS FILL WITH WATER FROM APPROZ 3:00 CLOCK AND HIGHER. THE WRAP IS IN GOOD SHAPE. LOWER SECTION WAS DISBANDED
|  | 300B | 263 | [15 empty] | LINE 300B WRAP REPLACEMENT JOB# 7038925
|  |  | 268.05 | [15 empty] | 300B ; 268.05; 30604260;; ; INSTALL ETS STATION MP 268.05B
|  | 300B | 270.67 | [15 empty] | SEE ATTACHED MAP
|  | 300B | 272.38 | 34 | [13 empty] | BAKERSFIELD | DET. L300N, SO#7051317-05 RTE, L300B, MP 272.3998 (SOUTH TIE-IN)
|  | 300B | 272.39 | [15 empty] | CLASS CHANGE 312 WALL T0505WALL; DIST. , L300N, SO# 7051317-05, RTE L-300B, MP 272.4001
|  | 300B | 273.08
|  | 300B | 273.28 | [15 empty] | DIST, L300B, SO#7051317-05, RTE L300B, MP 273.2903
|  |  | 362.09B | [15 empty] | INSTALL 4" TAP FOR LOS GATOS TOMETO PLANT M.P. 362.09B
|  | 300B | 273.31 | [14 empty] | BAKERSFIELD | DIST. L300B, SO#7051317-05, RTE L-300B, M.P. 273.3100
|  | 300B | 273.4393 | [14 empty] | BAKERSFIELD | DIST L300N, SO# 7051317-05, RTE 300B, M.P. 273.4393
|  | 300B | 273.44 | [15 empty] | DIST L300N, SO#7051317-05, RTE L300B, M.P. 273.4598
|  | 300B | 274.11 | 34 | Transmission | [12 empty] | BAKERFIELD | DIST L300B, SO#7051317-05, RTEL-300B, M.P. 274.1204
|  | 300B | 244.11 | [15 empty] | DIST L300N, SO#7051317-05, RTE L300B, M.P. 274.1208 (NORTH TIE-IN)
|  | 300B | 276.15 | [15 empty] | NEW INDUSTRIAL PARK GOING IN
|  | 300B | 276.15B | [15 empty] | NEW INDUSTRIAL PARK GOING IN
|  | 300B | 276.15
[5 empty] | Transmission | [13 empty] | BAKERSFIELD AREA; U.T. DEVICE USED TO MEASURE WALL THICKNESS BELONGED TO ROB MC CORMACK. SER #V30893. MEASURED WALL THICNESS WAS .500
|  |  | 277.1589 | [15 empty] | RT 300B, MP 277.1589
|  | 300B | 277.5 | [15 empty] | USA TICKET #116528, l-300B, M.P. 277.5
|  | 300B | 277.54 | [15 empty] | NEW HOUSING TRACK GOING IN USA#377578
|  | 300B | 277.6 | [15 empty] | SURVEY FOR DEPTH USA#185907
|  | 300B | 277.63 | [15 empty] | SURVEY FOR DEPTH USA#185970
|  | 300B | 277.6 | [15 empty] | SURVEY FOR DEPTH USA#185907
|  | 300B | 277.68 | [15 empty] | SURVEY FOR DEPTH USA#185970
|  | 300B | 277.63 | [15 empty] | SURVEY FOR DEPTH USA#185970
|  | 300B | 277.68 | [15 empty] | SURVEY FOR DEPTH USA#185970
|  | 300B | 277.78 | [15 empty] | DUG TO VERIFY PIPELING WALL THICKNESS
|  | 300B | 277.9 | [15 empty] | DUG TO VERIFY PIPELINE WALL THICKNESS
|  | 300B | 277.8 | [15 empty] | L-300 M.P. 27780
PER REQUEST ENG. PIPE LINE
PER REQUEST ENG. PIEP LINE
PER REQUEST ENG. PIPELINE
|  | 300 | 278. B | [15 empty] | CONTRACTOR PIT HOLE IN THREE PLACES IN EMPTY LOT, S/O BEUNA VISTA FOR FUTURE CONSTRUCTION
REQUEST PER END. PIPE LINE
300; 281.25; 30604260
|  | 300B | 283.048 | [14 empty] | BAKERSFIELD | A FORM FILE; 300N SO#7045441-05; L-300B; M.P. 283.1368 (NORTH AVE)
|  | 300B | 283.81B | 34 | Transmission | [12 empty] | BAKERSFIELD | DIST G300N SO#7045447-05, L-300B, MP. 283.8552 (STOCKDALE AVE)
|  | 300B | 285.33B | [15 empty] | 300B, 285.33; PM 30604260;; ; INSTALL E.T.S STATION L-300B, M.P. 28533-B;
|  |  | 294.3002 | [14 empty] | SHAFTER | RT = 300B, M.P. 294.3002, 30604260; EXPOSED LINE TO INSTALL E.T.S. @ M.P. 294308; MAP IS ATTACHED
|  | 300B | 299.01 | [15 empty] | L-300B, M.P. 299.01
|  | 300B | 300.01 | [15 empty] | INSTALL TEST LEADS L-300B M.P. 300.01
|  |  | 302.4602 | [14 empty] | LOST HILLS | RT = 300B, M.P. 3024602, 30604260; EXPOSED LINE TO INSTALL NEW E.T.S. @ M.P. 302.468; MAP IS ATTACHED
|  |  | 306.6123 | [14 empty] | WASCO | RT = 300B, M.P. 306.6123; EXPOSED LINE TO INSTALL CATHODE WIRE FOR NEW ANODE SED. AT M.P. 306.61b; MAP ATTACHED
|  | 300B | 311.4 | [15 empty] | INSTALL E.T.S. STATION
|  | 300B | 350.2102 | [15 empty] | SO# 7056786, L-300B, M.P. 350.2102., ARROYO PEQUENO CREEK
|  | 300B | 352.55 | [15 empty] | INSTALL E.T.S. STATION M.P. 352.55 L-300B
L-300A... L-300B M.P. 354.09; CONTRACTORS WILL INSTALL A 34" PIPE TO CONNECT NEW PLANT TO 300.
|  | 300B | 359.65 | [15 empty] | 300B, M.P. 359.75; INSTALL TEST LEADS AT M.P. 359.65 L-300B; PICTURE ON NEXT PAGE
|  | 300B | 362.8276 | [15 empty] | L-300B, SO# 7056786-05, M.P. 362.8276, PASAJERO CREEK; GOUGE WAS REPAIRED BY KETTLEMAN DIST.
|  | 300B | 364.09 | [15 empty] | L-300B. M.P. 364.0900, DIST L-300N; CUST HAND DUG UNDER GAS LINE TO INSTALL WATER PIPE
|  | 300B | 394.23 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  | MEDOTA | SEE ATTACHED MAP FOR SKETCH
|  | 300B | 395.84 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  | MEDOTA | SEE ATTACHED MAP FOR SKETCH
|  | 300B | 396.7 | [15 empty] | SO# 7049869-04 BD549, M.P. 0.0212, L300N, SRC RTE: 300B, M.P. 396.70
|  | 300B | 400.29 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  | MEDOTA | RT 300B, M.P. 400.29; SEE ATTACHED MAP FOR SKETCH
|  | 300B | 401.51 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  | MEDOTA | RT 300B, M.P. 401.51; SEE ATTACHED MAP FOR SKETCH
|  | 300B | 401.51 | [15 empty] | SO# 7049869-04 L300B, M.P. 401.51, DIST L-300N
|  | 300B | 405.94 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  | MEDOTA | RT 300B, M.P. 405.94; SEE ATTACHED MAP FOR SKETCH
|  | 300B | 407.37 | [15 empty] | RT: 300N, M.P. 407.37
|  | 300B | 409.39 | [15 empty] | RT: 300B, M.P. 409.39
DIST: L300N, SO#7049826-02, M.P. 410.8647, L-300B, (MLV 410.87B); L-300B @M.P. 410.87B
|  | 300B | 410.87 | [15 empty] | RT: 300B, M.P. 410.87
|  | 300B | 412.75 | [15 empty] | RT: 300B, M.P. 412.75
|  | 300B | 415.84 | [15 empty] | RT: 300B, M.P. 415.84
|  | 300B | 419.11 | [15 empty] | DISTRICT: HOLLISTER, SO# 7049826-05, L-300B, M.P. 419.1047
|  |  | 419.1168 | [15 empty] | DISTRICT: HOLLISTER SO# 7049826-05, L-3OO, M.P. 419.1168
|  | 300B | 420 | 34 | [8 empty] | 2006-08-14 |  |  | Steel/Wrought Iron |  |  | SO# 7056267, ROUTE 300B, M.P. 420; RECOATED 4' AREA ON 34" LINE; ERCON PROJECT, SEVERAL PEICES OF COATING MISSING, WE EXCAVATED THE SITE TO EXPOSE 4" AND RECOAT SHORT SECTION BEFORE BUILDING ERCON REVETMENT WALL.
|  | 300B | 420.55 | [15 empty] | RT: 300B, M.P. 420.55
|  | 300B | 422.22 | [15 empty] | RT: 300B M.P. 422.22
|  | 300B | 422.97 | [15 empty] | RT: 300B, M.P. 422.97
|  | 300B | 425.19 | [15 empty] | RT: 300B, M.P. 425.19
|  | 300B | 425.54 | [15 empty] | RT: 300B M.P. 425.54
|  |  | 429.64 | [15 empty] | DIST: HOLLISTER L-300B @ 429.64, SO# 7049826-05, L-300B, M.P. 429.6346 (MLV 429.64); REPLACED MLV 429.64 & BRIDLE ASSEMBLY FOR SMART PIG RETROFIT.
|  |  | 429.64 | [15 empty] | DIST: HOLLISTER, L-300B @M.P. 429.64, SO# 7049826-05, L-300B SCRMP 429.64, RTE X6532, MP 0.0032; REPLACED MLV 429.64 & BRIDLE ASSEMBLY FOR SMART PIG RETROFIT
|  | 300B | 429.64 | [15 empty] | DIST: HOLLISTER, L-300B @ 429.64, SO# 7049826-05, (MLV 429.64) L-300B, M.P. 429.6464; REPLACE MLV 429.64 & BRIDLE ASSEMBLY FOR SMART PIG RETROFIT
|  | 300B | 435.6 | [14 empty] | PAICENES | L-300B, MP. 435.60, SO# 7032825-00, 435.70
|  |  | 436.84 | [15 empty] | RT= 300, M.P. 436.84, SO# 7055426-07, 6A/6B PLS REPLACE RELIEF V-F; SEE JOB PRINT
|  |  | 436.8485 | [15 empty] | DIST: HOLLISTER, SO# 7049826-05, (MLV 436.85B), L-300B, M.P. 436.8485; TIE IN SMART PIG BYPASS @ PL56B UPSTREAM OF MLV 436.85
|  |  | 436.8644 | [15 empty] | DIST: HOLLISTER, SO# 7049826-05, (MLV 436.85B), L-300B, M.P. 436.8644; TIE IN SMART PIG BYPASS @ PL56B D/S OF MLV 436.85
|  | 300B | 439.01 | [15 empty] | RT: 300B, M.P. 439.01
|  |  | 445.3229 | [15 empty] | L-300B U/S OF MLV 445.32B, SO# 7049826-05, L-300B, M.P. 445.3229; INSTALLATION OF 34" MLV & 12" BRIDLE VALVE ASSY
|  | 300B | 445.32 | [15 empty] | DIST: HOLLISTER, 300B D/S OF MLV 445.32B, SO# 7049826-05, L-300B M.P. 445.3265; INSTALLATION OF 34" MLV & 12" BRIDLE VALVE ASSY
|  | 300B | 450.22 | [15 empty] | RT: 300B, M.P. 450.22
|  | 300B | 450.39 | [15 empty] | SOUTH TIE IN RT: 300B M.P, 460.3883, PM# 40764692; L-300B @ M.P. 450.4 CLASS CHANGE SOUTH TIE-IN
|  | 300B | 450.43 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-300B HYDRO TEST, NORTH TIE-IN, RT-300B, M.P. 450.43; L-300B @ M.P. 450.4 CLASS CHANGE HYDRO TEST, NORTH TIE-IN
|  | 300B | 450.66 | [15 empty] | RT: 300B M.P. 450.66
|  | 300B | 450.79 | [15 empty] | HOLLISTER L-300B, 45' U/S OF MLV 450.79, L-300B, M.P. 450.7831; NOTE: 30% ASBESTOS IN PIPE WRAP
|  | 300B | 461.08 | [15 empty] | SO# 7053765; L-300B @ M.P. 461.08; REMOVE PRESSURE RELIEF VALVE. REMOVE MLV (PL56B) @ M.P. 461.08 & BRIDLE ASSEMBLY. INSTALL 34" OD X 0.505 WR API 5L, X-60
|  | 300B | 466.7 | [15 empty] | TRINCHER CONST. EXCAVATED W/BACKHOE SO I COULD SEE HOW DEEP OUR LINE WAS ]L-300B, APPROX M.P. 466.7] AT 8770 OLD LEAVESLET RD. GILROY AREA. 1 LOCATION HAD ALREADY BEEN LOWERED APPRX, 3' FROM TRINCHERO USING A SCRAPER [CAT 623B] WITHOUT ARE KNOWLEDGE OR CONSENT & WE NOW ONLY HAVE 12" OF COVER AT HIS LOCATION OF LOWER PART OF RD. GOING TO THE PAD FOR THE HOUSE ON THE SOUTH END OF PROPERTY & 33' ON THE UPPER PART OD THIS ROAD. ON THE ROAD GOING TO THE HOUSE PAD ON THE NORTH END OF PROPERTY WE HAVE 46" OF COVER. I STAKED OUT L-300B AT & BETWEEN THESE LOCATIONS & TOLD THEM NOT TO CROSS OUR PIPELINE WITH THERE SCRAPER, SHEEPFOOT [CAT 815B] WATER TRUCK, OR ANY OTHER HEAVY EQUIPMENT UNTIL THEY SUBMIT THERE PLANS TO OUT ENGINEER [TOSS ARNETT]. I SLOA GAVE THEM [MIKE] A USA BROCHURE & A COPY OF C.G.T. GUIDELINES & INFORMATION MIKE WE MAY HAVE TO DIG UP PIPELINE & INSPECT IT FOR ANY DAMAGES THAT MIGHT HAVE OCCURREED WHEN THEY WERE USING THERE SCRAPER OVER LINE TO REMOCER COVER WITHOUT OUR KNOWLEDGE OR CONSCENT & IF SO THEY MAY BE CHARDED FOR THIS. MIKE NORDGREEN 5-6-99
|  | 300B | 466.8 | 34 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ADDRESS-8770 LEAVESLEY RD., GILROY.
|  | 300B | 477.25 | 34 | Transmission | [12 empty] | MORGAN HILL
DIST: MILPITAS, 30635919-04, L-300B, M.P. 484.
|  | 300B | 490.89 | 34 | [13 empty] | SNA JOSE | GPS FILE R101316A, LOV #2
|  | 300B | 490.89 | 34 | Transmission | [12 empty] | SNA JOSE | GPS FILE R101316A, LOC# 1
|  | 300B | 489.17 | [15 empty] | L-300B HYDROTEST DUE TO CLASS CHANGE
|  | 300B | 490.1 | [15 empty] | L0300B HYDRO TEST DUE TO CLASS CHANGE
|  | 300B | 490.15
|  | 300B | 490.7 | 34 | Transmission |  | Girth Weld |  |  |  |  | 2000-01-13 | [5 empty] | SAN JOSE | GPS FILE # LOCATION #5
|  | 300B | 490.72 | 34 | Transmission | [12 empty] | SAN JOSE
|  | 300B | 490.73 | 34 | Transmission |  | Girth Weld | [10 empty] | SNA JOSE
|  | 300B | 490.74 | 34 | Transmission |  | Girth Weld |  |  |  |  | 2000-01-13 | [5 empty] | SAN JOSE
|  | 300B | 490.76 | 34 | Transmission |  | Girth Weld |  |  |  |  | 2000-01-13 | [5 empty] | SAN JOSE
|  | 300B | 490.8 | 34 | Transmission |  | Girth Weld |  |  |  |  | 2000-01-13 | [5 empty] | SAN JOSE | GPS FILE # LOCATION #2
|  | 300B | 490.9 | 34 | Transmission |  | Girth Weld |  |  |  |  | 2000-01-13 | [5 empty] | SAN JOSE | GPS FILE # ____ LOCATION #1
|  | 300B | 493.37 | 34 | [13 empty] | SAN JOSE
|  | 300B | 493.62 | 34 | Transmission | [13 empty] | PLS5 300B-20W
|  | 300B |  | 34 | Transmission | [7 empty] | 2002-01-07 | Other | REMOVED CASING | Steel/Wrought Iron |  | SAN JOSE | LINE 300-B; REMOVED CORRIGATED CASING 150' ON LINE 300B. CAPITOL EXPRESSWAY CROSSING. WORK COMPLETED ON 1-07-02 WORK DONE BY CONTRACTOR, COATING LOOKED OK. EXCEPT FOR 4 OR 5 LOCATIONS WHERE CASING WAS RESTING ON PIPE. WATER...VERY HIGH IN THIS AREA, VERY WET CONDITIONS. CLEARED AND WRAPED 150' WITH TRENTON WAX TAPE
|  | 300B | 493.65 | 34 | Transmission | [12 empty] | SAN JOSE | PLS5 300B-20N
|  | 300B | 497.3 | [15 empty] | L-300B, M.P. 497.3; IN...RIGHT OF WAY AT END OF DAHLI CT. THROUGH DOUBLE DOORS ALONG FWY 680, LIST # 0333270
|  | 300B | 498.15 | 34 | Transmission | [10 empty] | Steel/Wrought Iron | DSAW | MILPITAS | LOC #1 GPS FILE R081515A
|  | 300B | 498.65 | 34 | Transmission |  | Girth Weld | [10 empty] | SAN JOSE
|  | 300B | 498.15
|  | 300B | 499 | [14 empty] | MILPITAS | RT= 300B. M.P. 499.94 MILIPITAS DISTRICT
|  | 300B | 500.2645 | [14 empty] | MILPITAS | DISTR MILPITAS, L-300B, M.P. 500.2645 (POT HOLED); POT HOLED FUTURE USA PROPOSED SITE LINE 300B, USA TICKET # 0306022, INT THE PARKING LOT OF ADDRESS 760 E. CAPITOL/ APPIAN ENGINEERING
|  | 300B | 500.29 | 34 | Transmission |  | Girth Weld | [10 empty] | MILPITAS
|  | 300B | 498 | [14 empty] | MILPITAS
|  | 300B | 500.31 | 34 | Transmission |  | Girth Weld | [10 empty] | MILPITAS
|  | 300B | 500.46 | 34 | [13 empty] | MILPITAS
|  | 300B | 500.75 | 34 | Transmission |  | Girth Weld | [10 empty] | MILPITAS | GPS FILE R013119A LOC #1. WE DID NOT EXPOSE THE PIPE. WE ONLY EXPOS TEE CASE AT THIS LOCATION
|  | 300B | 500.57 | 34 | Transmission | [10 empty] | Steel/Wrought Iron | DSAW | MILPITAS | LOCATION #1 GPS FILE R081317B
|  | 300B | 501.02 | 34 |  |  | Girth Weld | [10 empty] | MILPITAS | GPS FILE R013120A SSF LOC #1. FOUND THE CASING NOT PIPE AT 96" COVER
|  | 300B | 501.66 | 34 | Transmission |  | Girth Weld | [10 empty] | MILPITAS | COMMENTS GPS FILE R218A LOC #1
|  | 300B | 501.94 | 34 | Transmission | [12 empty] | MILPITAS | GPS FILE R 120216B
|  | 300B | 501.97 | 34 | Transmission |  | Girth Weld | [10 empty] | MILPITAS | LOCATION #7
|  | 300B | 501.95 | 34 | Transmission |  | Girth Weld | [10 empty] | MILPITAS | LOCATION #6
|  | 300B | 501.99
|  | 300B | 501.65 | 34 | [14 empty] | GPS FILE
|  | 300B | 502.04 | [15 empty] | L-300B, M.P. 502.04; GPS FILE # PRESCHOOL
|  | 300B | 502.12 | 34 | Transmission |  | Girth Weld | [10 empty] | MILPITAS | L-300B, M.P. 502.12
|  | 300B | 502.13 | 34 | Transmission | [12 empty] | MILPITAS | GPS FILE R120618A
|  | 300B |  | 34 | Transmission | [7 empty] | 2002-10-26 | Other | RECOATED; | Steel/Wrought Iron |  |  | L-300, AT HWY 237 CROSSING CASING REMOVAL AND COATING REPAIR; REMOVED CASIN, REPAIRED COATINGS, POWER CRETE AND WAK TAPE; REMOVED CASING, RECOATED WTIH POWER CRETE & WAS TAPE OVER EXISTING TAR COATING.
|  | 300B | 502.14 | 34 | Transmission | [7 empty] | 2002-10-25 |  |  | Steel/Wrought Iron |  |  | LAMINATED PIT, L-300B CALAVERAS WEST CROSSING M.P. 502.14; L-300 # M.P. 502.14. LAMINATION PIT TES CAME CUT TO INSPET PIT & ESTABLISH IF PIPE IS OK.; AREA WAS SAND BLASTED AND RECOATED IN THE POWERCRETE. L-300B RECOAT, WE WERE SAN BLASTING WHEN # PIECE OF METAL BLEW OUT FROM THE SIDE OF THE MAIN. IT APPEARED TO BE A FORM OF LAMINAENT THE BIGGEST PART WAS 13/4" LONG BY 3/8" WIDE BY .04 DEEP. DAN KERE FROM PG&E TES CAM OUT ON 10-25-02 TO MAG-PARTICLE TEST THE AREA, SUFFICANT THE LAMINATED AREAS TILL CLEAR. NET TO EXCEED 40 MILES. AREA ...CREW BY DAIKERE, DAVE AGULAR, TODD ARNETT WE RESUMED THE RECOATING PROCESS. S. JAMESON
|  | 300B | 354.2 | 34 |  |  | Other |  | DRILL HOLE | Other | DRILLED WRONG LINE | 2007-08-13 | 2007-08-16 | Other | WELD 1" SAVE-A-VALVE | Steel/Wrought Iron |  | AVENAL | DRILLED WRONG LINE WITH A 15/64 DRILL; DRILL 15/64 HOLE ON 300B WHEN IT SHOULD OF BEED DRILLED ON 300A FOR A SNIFF HOLE TO REPLACE V-56 AT KETT. COMP. STA.
|  |  |  | 30 | Transmission | [7 empty] | 2002-10-16 | Other | RECOAT | Steel/Wrought Iron |  |  | REMOVED CASING REPAIRED COATING OVER COATED SOME OF THE EXISTING COATING; JOB WAS TO REMOVE CASING & CHECK COATING PIPE ON NORTH SIDE OF CALAVERAS WAS ...SEEPED AND REPAIRED. TAR COATING WAS FAIR WE COATE/OVER COATED TAR WITH WAX TAPE. WE ATTACHED TEST LEADS ON BOTH ENDS
|  | 300B |  | 36 | Transmission |  | Girth Weld | [10 empty] | MILPITAS
|  | 300B | [15 empty] | MILPITAS
|  | 300B | [15 empty] | MILPITAS
|  | 300B | [15 empty] | MILPITAS
|  | 300B | [15 empty] | MILPITAS
| 07-75047-1 | 186 |  | 4 | Transmission |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2007-11-21 | 2007-12-05 | Deactivate #TP Main |  | Steel/Wrought Iron |  | DOS PALOS | 275' OF NEW 4" STL BROAD IN UNDER WATER
| 06-60020-1 | 0 | 0 | 0.75 | Transmission |  | Fitting |  |  | Other |  | 2006-06-12 | 2007-12-10 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | HAYWARD | RT = 2403-02, M.P. 1.0779
| 07-00209-1 | 121 |  | 6 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 2007-12-23 | 2007-12-23 | Patch Welded |  | Steel/Wrought Iron |  |  | RTE 121, M.P. 0.7406; REWELDED 2" TEE ON 6" MAIN
| 07-30035-1 | [10 empty] | 2007-12-14 | [5 empty] | FORTUNA | MP=0
| 07-10198-1 | 6 |  | 6 | Transmission |  | Valves |  |  | Internal Corrosion | SAN JOSE | 2007-10-29 | 2007-11-27 | Replace Valve >= 2 inch |  | Steel/Wrought Iron |  |  | RTE =0813-09, M.P. 0.0146, DFM; REPLACED VALVE
| 07-30033-1 |  |  | 0.75 | Service |  | Valves |  |  | External Corrosion |  | 2007-11-23 | 2007-11-27 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | LOLETA | VALVE ON 3/4" DREG 4724; REBUILD HPR
| 07-60002-1 | [10 empty] | 2007-11-06 | [5 empty] | SEBASTOPOL
| 07-20136-1 | 500 |  | 8 | Transmission |  | Valves |  |  | Other |  | 2007-04-19 | 2007-10-18 | Other |  | Steel/Wrought Iron |  | SACRAMENTO | 0651.01 + DFM, M.P. 1.8700; VALVE WILL HAVE TO BE DUG UP
| 07-20307-1 | [10 empty] | 2007-10-31 | [5 empty] | SACRAMENTO | GRADE 0 119 B-1, MP 0.0272
| 07-10198-1 | [10 empty] | 2007-10-29 | [5 empty] | SAN JOSE | DFM 0813-09, M.P. 0.0146
| 07-55064-1 | 158 | [9 empty] | 2007-11-13 | [5 empty] | WOODLAND | DFM 0646-01, M.P. 6.8802
| 07-02086-1 | [10 empty] | 2007-10-24 | [5 empty] | LODI | TP DFM 1619-04, M.P. 0.6844
| 07-75047-1 | 186 |  | 4 | Transmission |  | Body of Pipe |  |  | Atmospheric Corrosion | DOS PALOS | 2007-11-21 |  |  |  | Steel/Wrought Iron |  |  | RT 186, M.P. 5.8105
| 07-60001-1 | [10 empty] | 2007-11-06 | [5 empty] | SEBASTOPOL | DFM 1302-02
| 07-30001-1 | 300B | 35420 | 34 | Transmission |  | Other |  |  | Other |  | 2007-08-13 | 2007-08-16 | Other |  | Steel/Wrought Iron |  | AVENAL | BB HCA REPAIRED L-300B, M.P. 354.1494; DRILLED WRONG LINE WITH 15/16" DRILL
| 07-02098-1 | 21F | 2.7 | [8 empty] | 2007-10-24 | [5 empty] | PETALUMA | T LT 021F-1 CASING; L-021F, MP 2.7000
| 07-02097-1 | 21F | 2.6044 | [8 empty] | 2007-10-24 | [5 empty] | PETALUMA | T LT 021-F; L-021F, MP 2.6044
| 99-30135-1 | 7221-10 | 14.584 | 8 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 1999-06-16 | 2007-07-30 | Other |  | Steel/Wrought Iron |  | MODESTO | T DFM 7221-10; MP 14.5845; WLD 2" SAV-A-VALVE O/PIT WRAP WAS DENIED
| 07-00129-1 | 121 | 2.03 | 6 | Transmission |  | Unknown |  |  | Unknown |  | 2007-08-01 | 2007-08-01 | Deactivate #TP Main |  | Steel/Wrought Iron |  | SUTTER | T LT 121 L-121, MP 2.03; DEACTIVATED APPROX. 105' STL. @T2.03 TO
| 07-10061-1 | 145 | 0.1188 | [8 empty] | 2007-08-21 | [5 empty] | SANTA CRUZ | DREG 5145, MP 0.1188
| 07-10062-1 | 145 | 0.1062 | [8 empty] | 2007-08-21 | [5 empty] | SANTA CRUZ | DREG 5145, MP 0.1062
| 07-55064-1 | 186 | 21.07 | 6 | Transmission |  | Body of Pipe |  |  |  |  | 2007-08-29 | 2007-08-31 | Replaced TP Main |  | Steel/Wrought Iron |  | CHOWCHILLA | T LT 186 L-186, MP 21.0067
| 99-50506-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  | 1999-02-25 | 2007-08-15 | Other |  | Steel/Wrought Iron |  | EMERYVILLE | 0112-01 D DFM, MP 0.5906; GREASED VALVE
| 07-75026-1 | 118A | 60.16 | [8 empty] | 2007-07-17 | [5 empty] | MERCED | T LT 118A; L-118A, MP 60.1460; EMAILED JCV8 TO CONFIRM IS ON L118A AND IS NEAR 16TH & 59, NOT 26TH & 59
| 95-35007-1 | 118B | 13.6976 | 12 | Transmission |  | Fitting |  |  | Construction Defect |  | 1995-04-24 | 2007-06-05 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MADERA | L-118B, MP 13.6976; SAVE VALVE CAP REMOVED, CLEANED, REINSTA
| 07-20002-1 | 200B4-1 | 0.14 | 10 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2007-05-07 | 2007-05-08 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | RIO VISTA | L-200B4-1, MP0.1416; INSTALL 28" OF 10" CAN
| 07-00458-1 |  | 0.0002 | [8 empty] | 2007-05-09 | [5 empty] | LINDA | DCUST 1705, MP0.0002; SRC RTE 1513-02, SRC MP 0.3808
| 07-80039-1 | 402 | 36.23 | 3 | Transmission |  | Valves |  |  | Other |  | 2007-05-01 | 2007-05-01 | Other |  | Steel/Wrought Iron |  | MOUNTAIN GA | L402; DREG 5490; DREG 5490 MP 0.0015, SRC RTE L-402, SRC MP 36.9463; INLET VALVE TO REG STATION DREG 5490; REPLACE GREASE FITTING
| 07-30054-1 | 8807-01 | 5.06 | 0.25 | Transmission |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2007-05-10 | 2007-05-11 | Other |  | Steel/Wrought Iron |  | SUNNYVALE | DFM 8807-01; DFM 8807-01, MP 4.0311; REPLACED 2" NIPPLE WELDED DIRECTLY TO 16
| 07-00457-1 | 50 | 0.533 | 2 | Transmission |  | Valves |  |  | Other |  | 2007-05-18 | 2007-05-18 | Other |  | Steel/Wrought Iron |  | LIVE OAK | 1513-02 VALVE #1; DFM 1513-02, MP 0.5330; REPLACED BOLTS IN VALVE CONNECT
| 07-53037-1 | 400 | 0.061 | 2 | Transmission |  | Valves |  |  | Material Failure |  | 2007-04-17 | 2007-04-18 | Other |  | Steel/Wrought Iron |  | VACAVILLE | DF3494 - OFF OF L400 VALVE #4; DF 3494, MP 0.0061, SRC RTE L-400, SRC MP 269.4735; REPLACED 2" FAILED VALVE. #4 PER GEORGE KARAKAZIS 6/11/07
| 07-15096-1 |  |  | 0.75 | Service |  | Riser |  |  | Unknown |  | 2007-05-15 | 2007-05-15 | Deactivated Entire Service |  | Steel/Wrought Iron |  | OAKLAND | DFM 0111... ; DCUST8798, MP 0.0002, SRC RTE TIDFM094-02, SRCMP 1.5459, SHUT OFF HI TI HI SET AND REMOVED METER
| 05-26102-1 |  | 4.73 | 4 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2005-11-09 | 2007-05-03 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ALAMO | DFM 3017-01; MP 4.73; TIGHTENED CAP ON SAVE A NIPPLE
| 05-21251-1 | 105 |  | 3 | Transmission |  | Valves |  |  | Other |  | 2005-10-06 | 2007-04-04 | Other | GREASED VALVE | Steel/Wrought Iron |  | OAKLAND | DISTRIBUTION DREG 4244; GREASED VALVE
| 06-80240-1 | 16"DFM | 0.178 | 16 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2006-10-19 | 2007-03-30 | Other |  | Steel/Wrought Iron |  | BERKELEY | DFM 0140-01; MP 0.1780; INST TP CLAMP TO REPAIR LEAK
| 05-21253-1 | 0.75 |  | 0.75 | Distribution Main |  | Fitting |  |  | Other |  | 2005-10-07 | 2007-04-05 | Other | M&C CREW TIGHTENED FITTINGS | Steel/Wrought Iron |  | ALAMEDA | LONG 122.7; LAT 37.788, DCUST782 / SERV; M&C CREW TIGHTENED FITTINGS
| 05-10017-1 | 126B | 4.97 | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2005-10-08 | 2007-02-15 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | EUREKA | L-126B; MP 4.9698; INSTALLED CLAMP AND ETS
| 05-00000-1 | 105 | 17.28 | 1 | Transmission |  | Tap Connection |  |  | Unknown |  | 2005-10-17 | 2007-03-19 | Other |  | Steel/Wrought Iron |  | SAN LEANDRO | L-X6460, MP 17.28; REDOPED THREADS ON PLUG AND TIGHTENED
| 07-20135-1 |  | 0.0657 | [8 empty] | 2007-04-18 | [5 empty] | SACRAMENTO | DREG4482, MP 0.0657
| 07-25076-1 |  | 0.0127 | [8 empty] | 2007-03-06 | [5 empty] | OAKLAND | DFM 0107-01; MP 0.0127
| 07-80027-1 | 402 | 0.0014 | 2 | Transmission |  | Valves |  |  | Other |  | 2007-03-15 | 2007-03-15 | Other | GREASED VALVE | Steel/Wrought Iron |  | MOUNTAIN GA | DREG 5488; MP 0.0014; GREASED VALVE
| 07-40060-1 | 130301 | 1.021 | 6 | Transmission |  | Body of Pipe |  |  |  |  | 2007-02-01 | 2007-03-03 | Replace Dist Main < 100 ft |  | Steel/Wrought Iron |  | SANTA ROSA | DFM 1303-01; MP 1.0210; REPLACED 20' OF T.P. PIPE
| 07-55015- |  | 0.0101 | 0.75 |  |  | Body of Pipe |  |  |  |  | 2007-03-19 | 2007-03-20 | Service Partially Replaced |  | Steel/Wrought Iron |  | LIVINGSTON | DCUST 1243; MP 0.0101
| 06-17401-1 | STUB8760 | 0 | 3.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2006-05-08 | 2006-05-23 | Other | CUT AND CAPPED 3" STUB | Steel/Wrought Iron |  | ARBUCKLE | CUT AND CAPPED 3" STUB
| 06-30202-1 | 302-023 | 0.16 | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2006-05-30 | 2006-09-27 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | MERIDIAN
| 06-30201-1 | 302-095 | 4.67 | 6 | Gathering |  | Fitting |  |  | Unknown |  | 2006-01-09 | 2006-01-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MERIDIAN | 2 LEAKS REPAIRED CAP ON GUAGE LINE-PLUG
| 07-31801-1 | 318 | 4.12 | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2007-01-30 | 2007-02-07 | Replace TP Main |  | Steel/Wrought Iron |  | ORLAND | LT TRANS DEF T; L 318; REPLACED 251' OF PIPE
| 06-19504-1 | 195B5-5 | 0.32 | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2006-04-26 | 2006-05-01 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | RIO VISTA | REPAIRED LEAK USING A 6" PLIDCO CLAMP
| 06-19503-1 | 195-043 | 0 | 10 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2006-04-17 | 2006-04-24 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | RIO VISTA | WELDED SLEEVE
| 06-19502-1 | 195-014 | 0 | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2006-04-08 | 2006-04-25 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | RIO VISTA | REPAIRED LEAK USING A 8" PLIDCO LEAK CLA
| 06-19501-1 | 195B5-3 | 0.31 | 6 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2006-02-16 | 2006-03-08 | Other | INSTALLED 6" PLIDCO LEAK CLAMP | Steel/Wrought Iron |  | RIO VISTA | INSTALLED 6" PLIDCO LEAK CLAMP
| 06-20001-1 | 200B3-3 | 0.14 | 12 | Gathering |  | Drip |  |  | Unknown |  | 2006-02-06 | 2006-02-10 | Other |  | Steel/Wrought Iron |  | RIO VISTA | REPAIRS WERE MADE BY REMOVING DRIP SVC A
| 06-16801-1 | 168-1-1 | 0.38 | 6 | Gathering |  | Body of Pipe |  |  | Unknown |  | 2006-01-09 | 2006-02-23 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | RIO VISTA | 2006-02-23
| 06-10016-1 | 0.75 |  | 0.75 | Service |  | Fitting |  |  | Other |  | 2006-01-27 | 2006-01-27 | Replace Partial Service |  | Steel/Wrought Iron |  | SANTA CRUZ | SRC. MP.: 1.8979; REBUILD HIGH TO HIGH REG ALSO MOVE 1' OV
| 06-10016-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 2006-01-27 | 2006-01-27 | Replace Partial Service |  | Steel/Wrought Iron |  | SANTA CRUZ | REBUILD HIGH TO HIGH REG ALSO MOVE 1' OV
| 06-50004-1 | MTY#1 | 7.95 | 0.75 | Transmission |  | Other |  |  | Construction Defect |  | 2006-02-01 | 2006-02-01 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | SRC RTE, DFM 1815-02; SRC MP, 7.9806; DREG 8583, M.P. 0.0225; CUT-OUT 3/4" 90 DEGREES SOCKET AND REPLA
| 05-20065-1 | 181B | 10.1265 | 16 | Transmission |  | Valves |  |  | Other |  | 2005-11-22 | 2006-02-17 | Other | GREASED LEAKING GAS VALVE | Steel/Wrought Iron |  |  | (VALVE A-10 V-10.12), L-181B, MP 10.1265; GREASED LEAKING GAS VALVE
| 05-50031-1 | 301B | 10.32 | 6 | Transmission |  | Valves |  |  | Other |  | 2005-04-21 | 2006-05-26 | Other | GREASED VALVE | Steel/Wrought Iron |  | SALINAS | SRC RTE, L-301B, SRC MP 11.0008, DREG 5413, MP 0.0000; GREASED VALVE
| 06-50044- | 301C | 1.1 | 0.75 | Single Service |  | Body of Pipe |  |  |  |  | 2006-04-27 | 2006-04-27 | Deactivated Entire Service |  |  |  | SALINAS | SRCRTE, 301C; SRCMP, 14.5050; DCUST2536; MP 0.0174; SHUT DOWN SERVICE AT PINOFF TEE AND RETHREAD
| 06-60077- | 312 | 2.14 | 8 | Transmission |  | Body of Pipe |  |  |  |  | 2006-07-18 | 2006-07-18 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | BAKERSFIELD | T LT L-312, MP 2.0734
| 04-30705-1 |  |  | 0.75 | Distribution Main |  | Other |  | CAP | Other | DRY DOPE | 2004-12-16 | 2006-06-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | M.V. | REDOPED PIPE
| 04-30705-1 |  | 1.693 | 0.75 | Distribution Main |  | Other |  |  | Other |  | 2004-12-16 | 2006-06-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MT VIEW | 8805-03, MP 1.693
| 06-30026-1 |  |  | 1 | Service |  | Riser |  |  | Atmospheric Corrosion |  | 2006-06-20 | 2006-06-20 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | EUREKA | INSTALLED CLAMP W/ ANODE (INSERTED SVC6)
| 05-10012-1 | 137A | 2.75 | 6 | Transmission |  | Other Welds |  |  | Construction Defect |  | 2005-09-12 | 2006-02-15 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | EUREKA | 137A, LT M.P. 2.746; WELDED 6" CAN/REWRAP MAIN 4' FROM ELL.
| 06-20014-1 | 101 |  | 0.75 | Service |  | Valves |  |  | Construction Defect |  | 2006-03-02 | 2006-03-02 | Other | GREASED 3/4" PLUG VALVE | Steel/Wrought Iron |  | SAN FRANCIS | IVILT M.P. 43.26; GREASED 3/4" PLUG VALVE
| 06-00013-1 | DFM |  | 0.75 | Service |  | Valves |  |  |  |  | 2006-02-03 | 2006-03-30 | Other |  | Steel/Wrought Iron |  | ST HELENA | 405-1, M.P. 22.7457
| 06-30029-1 | 12L177 | 124 | 12 | Transmission |  | Body of Pipe |  |  | Construction Defect |  | 2006-08-19 | 2006-08-19 | Other |  | Steel/Wrought Iron |  | MAD RIVER | 177A; M.P. 125.678; SHUT DOWN LINE (REPLACED 16' 12" ON 08/2
| 06-40121-1 | 1305-45 | 0.0165 | 0.75 | Transmission |  | Valves |  |  | Damage by 3rd Party |  | 2006-08-13 | 2006-08-13 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | SANTA ROSA | 1305-45; M.P. 0.0165; REPLACED 3/4" BALL VALVE
| 06-30029-1 | 12L177 | 124 | 12 | Transmission |  | Body of Pipe |  |  | Damage by Natural Forces |  | 2006-06-19 | 2006-08-19 | Other |  | Steel/Wrought Iron |  | MAD RIVER | ROUTE 177A; MP. 124.90; SHUT DOWN LINE (REPLACED 16' 12" ON 08/2
| 06-80096-1 | DRM |  | 2 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2006-03-24 | 2006-05-09 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | RICHMOND | INSTALLED WELD-CAN OVER PITS IN AND
| 06-25091-1 |  |  |  | Gathering |  | Valves |  |  | Unknown |  | 2006-02-15 | 2006-02-15 | Other |  | Other |  | RICHMOND | GREASED FIRE VALVE
| 06-12119-1 |  |  | 0.75 | Service |  | Riser |  |  | External Corrosion |  | 2006-04-21 | 2006-04-21 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | OAKLAND | INSTALLED CLAMP ON SVC
| 06-22053-1 | 105 | 0 | 0.75 | Transmission |  | Valves |  |  | Other |  | 2006-04-21 | 2006-05-24 | Other |  | Steel/Wrought Iron |  | OAKLAND | GREASED VALVE
| 04-26135-1 | DAN/DFM | 4.7019 | 8 | Transmission |  | Fitting |  |  | Construction Defect |  | 2004-09-28 | 2006-03-23 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ALAMO | INSTALLED NEW GASKET ON PCV AND TIGHTENE
| 05-21254-1 |  |  | 8 | Service |  | Valves |  |  | Other |  | 2005-10-10 | 2006-03-24 | Other |  | Steel/Wrought Iron |  | OAKLAND | 0170-01 M.P. 0.0; GREASED AND TURNED VALVE
| 06-35000-1 | 118 | 73.26 | 4 | Transmission |  | Valves |  |  | Unknown |  | 2006-03-03 | 2006-06-07 | Other |  | Steel/Wrought Iron |  | LIVINGSTON | LF3337- M.P. 0.0 (MLV 118A - MP 73.24)
06-11000-1 | DFM |  | 0.5956 | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2006-05-09 | 2006-05-30 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | FREMONT | 2405-01 MP 0.5956; WELDED SLEEVE ON 4" MAIN
| 00-35004-1 |  | 0.4387 | 4 | Distribution Main |  | Valves |  |  | Other |  | 2000-03-08 | 2006-10-20 | Other |  | Steel/Wrought Iron |  | WINTERS | DFM0626-01; MP0.4387; GREASED VALVE-FIRE VALVE 7
| 05-40088-1 | 1302-02 | 10.4816 | 6 | Transmission |  | Valves |  |  | Construction Defect |  | 2005-11-03 | 2006-12-02 | Replace Valve >= 2 inch |  | Steel/Wrought Iron |  | SEBASTOPOL | DFM 1302-02 MP 10.4816
| 06-04046-1 | 196 | 16.4457 | 0.75 | Single Service |  | Body of Pipe |  |  |  |  | 2006-11-22 | 2006-11-22 | Deactivated Partial Service |  | Steel/Wrought Iron |  | MOUNTAIN HOUSE | SRC RT: L-196; SRC MP 16.4457; DCUST 8444; MP 0.0004; WELDED 3/4" SPLIT M/2 + CUT, PLUGGED AND WELDED CAP
| 06-10127-1 | 10181601 | 0 | 0.75 | Transmission |  | Other |  |  | Other |  | 2006-11-18 | 2006-11-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | CAPITOLA | DFM 1816-01; MP 14.4662; BOX NEED TO BE ENLRGD TO SMALL TO OPRTE
| 06-10127-1 | 10181601 |  | 0.75 | Service | TRANSMISSION | Other |  | BLOW OFF | Other | DIRT IN SEAT | 2006-11-18 | 2006-11-20 | Tighten Cap or Bolt | BLEW OUT BLOW OFF | Steel/Wrought Iron |  | CAPITOLA | BOX NEEDS TO BE ENLARGED. TOO SMALL TO OPERATE PIN OFF TEE. FIXED BLOW OFF.
SOAP TEST
| 06-20058-1 |  |  | 0.25 | Distribution Main |  | Fitting |  |  | Other |  | 2006-07-27 | 2006-08-02 | Tighten Cap or Bolt |  | Other |  | WASCO | DREG 5498, MP 0.0237; SRC RTE, DFM 660601, SRC MP, 1.6022; MINOR LEAK @ 1/4" FITTING
| 06-30038-1 | 4"L126B | 413 | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2006-12-22 | 2006-12-22 | Other |  | Steel/Wrought Iron |  | EUREKA | L-126B, MP 4.1117; INSTALLED PLETCO CLAMP
| 06-42478-1 | 2408-05 | 8.63 | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2006-11-20 | 2006-11-21 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | DUBLIN | D DFM2408-05; MP8.5310
| 06-75042-1 | 118 | 14.3829 | 0.75 | Service |  | Valves |  |  | Vehicle |  | 2006-11-04 | 2006-11-06 | Patch Welded |  | Steel/Wrought Iron |  | MADERA | DCUST 1213, MP. 0.0003; T. LT SRC RTE L-118A, MP 14.3829; REWELD TEE BACK ON PIPE
| 06-00087- | DFM |  | 6 | Transmission |  | Fitting |  |  |  |  | 10/00/0000 | 2006-10-11 | Replaced TP Main |  | Steel/Wrought Iron |  |  | D DFM 0405-01; REPLACED 6' OF 6" STEEL GAS PIPE
| 05-21008-1 |  | 0.0015 | 0.75 | Service |  | Valves |  |  | Other |  | 2005-04-19 | 2006-10-04 | Other |  | Steel/Wrought Iron |  | OAKLAND | GREASED VALVES TO STOP LEAK
| 05-21006-1 |  |  | 0.75 | Service |  | Valves |  |  | Other |  | 2005-04-13 | 2006-10-04 | Other |  | Steel/Wrought Iron |  | OAKLAND | CLOSED VALVE ON HI TO HI SET-NOT IN USE
| 94-23724-1 |  |  | 0.75 |  |  | Valves |  |  |  |  | 1994-04-13 |  | Other |  | Steel/Wrought Iron |  | OAKLAND | GREASED 3/4" TP VALVE
| 05-21004-1 |  |  | 0.75 | Service |  | Fitting |  |  | Construction Defect |  | 2005-04-13 | 2006-10-04 | Other |  | Steel/Wrought Iron |  | OAKLAND | TIGHTENED 3/4" UNION
| 05-21044-1 |  |  | 1.25 | Service |  | Valves |  |  | Construction Defect |  | 2005-04-09 | 2006-10-02 | Other |  | Steel/Wrought Iron |  | OAKLAND | DCUST 780; REPAIRED 1 1/4" BY PASS
| 06-22320-1 |  | 0.0008 | [8 empty] | 2006-10-11 | [5 empty] | OAKLAND | D DFM 0114-01; MP 0.0008
| 06-22322-1 | [10 empty] | 2006-10-12 | [5 empty] | OAKLAND | DCUST 8652
| 06-50099- | 0.001 |  | 0.75 | Transmission |  | Body of Pipe |  |  |  |  | 2006-07-24 | 2006-07-24 | Other |  | Steel/Wrought Iron |  | FRESNO | CUT OFF HPR SET
| 06-80096-1 | DRM |  | 2 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2006-03-24 | 2006-05-09 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | RICHMOND | DCUST 8365; INSTALLED WELD-CAN OVER PITS IN AND
| 06-10016-1 |  |  | 0.75 | Service |  | Fitting |  |  | Other |  | 2006-01-27 | 2006-01-27 | Replace Partial Service |  | Steel/Wrought Iron |  | SANTA CRUZ | DCUST 1995; REBUILD HIGH TO HIGH REG ALSO MOVE 1' OV
| 05-21009-1 | 105 |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2005-04-19 | 2006-10-18 | Other |  | Steel/Wrought Iron |  | OAKLAND | DCUST 780; GREASED 3/4" TP VALVE
| 06-30080-1 |  |  | 0.75 | Service |  | Body of Pipe |  |  | External Corrosion |  | 2006-04-03 | 2006-04-04 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | SOUTH S F | CLAMP LEAK
| 06-30653- |  | 0.1516 | 0.75 | Transmission |  | Body of Pipe |  |  |  |  | 2006-10-20 | 2006-10-20 | Other |  | Steel/Wrought Iron |  | MT VIEW | GCUST 5783; MP 0.1516; WELD 3/4" CAP ON 3/4" PIPE
| 05-21124-1 | 153 |  | 24 | Transmission |  | Longitudinal Weld |  |  | Construction Defect |  | 2005-04-18 | 2006-10-07 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | OAKLAND | T LT L-153; MP-23.7902; INSTALLED 24" STEEL SLEEVE
| 05-21045-1 | 105N | 0.4234 | 4 | Transmission |  | Other Welds |  |  | Construction Defect |  | 2005-04-09 | 2006-10-09 | Patch Weld - Weld |  | Steel/Wrought Iron |  | OAKLAND | DFM 0115-...; MP 0.4234; DFM 011J-01; REWELD PATCH WELD
| 06-33104-1 |  |  | 4 | Distribution Main |  | Valves |  |  | Other |  | 2006-10-03 | 2006-10-17 | Other |  | Steel/Wrought Iron |  | VACAVILLE | DFM 0604-19; MP 0.1500; GREASED VALVE #17
| 00-00553-1 | LINCOLN | 0.2897 | 16 | Transmission |  | Body of Pipe |  |  | Digin |  | 2000-08-17 | 2000-08-17 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SAN RAFAEL | DFM 0402-01; MP 0.2897; INSTALLED 18" LONG SLEEVE
| 05-30201-1 | 302 | 1.9209 | 8 | Gathering |  | Body of Pipe |  |  | Damage by 3rd Party |  | 2005-04-17 | 2005-04-26 | Other | SAVE-A-VALVE |  |  | SUTTER | L-302-217; M.P., 1.92009; WELDED SAVE-A-VALVE OVER BULLET HOLE
| 05-30201-1 | 302 | 1.9209 | 8 | Gathering |  | Body of Pipe |  |  | Damage by 3rd Party |  | 2005-04-17 | 2005-04-26 | Other | SAVE-A-VALVE |  |  | SUTTER | RTE., L-302-217; M.P., 1.9209; WELDED SAVE-A-VALVE OVER BULLET HOLE
| 05-20001-1 | 200 | 0.9647 | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2005-01-18 | 2005-03-11 | Mechanical Repair Fitting - Fitting |  |  |  | RIO VISTA | L-200C7-3; M.P. 0.9647; INSTALLED PLIDCO LEAK CLAMP
| 05-20001-1 | 200 | 0.9647 | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2005-01-18 | 2005-03-11 | Mechanical Repair Fitting - Fitting |  |  |  | RIO VISTA | L-200C7-3; M.P. 0.9467; INSTALLED PLIDCO LEAK CLAMP
| 05-19501-1 | 195 | 0.4376 | 10.75 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2005-05-31 | 2005-06-27 | Welded Sleeve/Can - Weld |  |  |  | RIO VISTA | ROUTE: L195B7-9; MP 0.4376; SO#8072142; INSTALLED REPAIR SLEEVE
| 05-19501-1 | 195 | 0.4376 | 10.75 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2005-05-31 | 2005-06-27 | Welded Sleeve/Can - Weld |  |  |  | RIO VISTA | ROUTE: L195B7-9; MP 0.4376; S0#8072142; INSTALLED REPAIR SLEEVE; INSTALLED 10" REPAIR SLEEVE
| 05-30202-1 | 302-224 | 0.2454 | 6 | Gathering | SERVICE |  |  |  | Internal Corrosion | SUSPECT | 2005-11-28 | 2005-12-08 | Other | NEW PIPE |  |  | MERIDIAN | RTE. 302-224; MP. 0.2454; SEE DRAWING
| 05-30046- | 125 |  | 12 | Transmission |  | Drip |  |  | External Corrosion |  | 2005-11-08 | 2005-11-09 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | FORTUNA | GG L-125; OVER DRIP OFF OF 4" L-125
| 05-30046- | 125 |  | 12 | Transmission |  | Drip |  |  | External Corrosion |  | 2005-11-08 | 2005-11-09 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | FORTUNA | INSTALLED 12" REPAIR SLEEVE OVER CORROSION LEAK
| 05-30012- | 125 |  | 6 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2005-03-26 | 2005-04-02 | Other | BLEW DOWN PIPE | Steel/Wrought Iron |  | FORTUNA | GG L-125; INSTALLED 6" PLIDCO CLAMP; FOUND LEAK ON BOTTOM OF 6" T.P.
| 05-30012- |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2005-03-26 | 2005-04-02 | Other | BLOW DOWN PIPE | Steel/Wrought Iron |  | FORTUNA | INSTALLED 6" PLIDCO CLAMP; FOUND LEAK ON BOTTOM OF 6" T.P.
| 00-80023- | 300A |  | 0.75 | Transmission |  | Valves |  |  | Other | VALVE NEEDED GREASE | 2000-10-12 | 2005-04-26 | Other | GREASED VALVE | Steel/Wrought Iron |  | PANOCHE | DCUST 8417; MP 0.0074; SRC RTE. L-300A; SRC MP. 436.76A; GREASED GAS VALVE
| 03-11401-1 | 114 | 20.68 |  | Transmission |  | Physical/Mechanical Joint |  |  | Atmospheric Corrosion |  | 2003-09-19 | 2005-05-07 | Welded Sleeve/Can - Weld | REMOVED VALVE |  |  | N. OF LIVERMORE | REPAIRED BY REPLACING VALVE W/ SECTION
| 03-21083-1 |  |  | 24 | Transmission |  | Valves |  |  | Unknown |  | 2003-07-18 | 2005-07-12 | Other | GREASED VALVE #6 | Steel/Wrought Iron |  | SACRAMENTO | DREG 4325, MP.0.0005; GREASED VALVE #6 ON LINE 108 11:30; SOAP TEST - PETE VELASQUEZ - 07-12-05
| 03-21083-1 | [10 empty] | 2003-07-18 | [5 empty] | SACRAMENTO
| 04-00008-1 | 21E |  | 4 | Transmission |  | Valves |  |  | Unknown |  | 2004-03-22 | 2005-07-29 | Other | GREASED VALVE | Steel/Wrought Iron |  | UKIAH | DREG 3824, MP 0.0640; SRC RTE 21E; SRC MP 111.94; GREASED VALVE
| 04-00313-1 |  |  | 6 | Transmission |  | Valves |  |  | Other | VALVE | 2004-11-08 | 2005-05-19 | Other | RESET | Steel/Wrought Iron |  | NEWCASTLE | RESET RELIEF VALVE
| 05-00002-1 |  |  | 4 | Transmission |  | Valves |  |  |  |  | 2005-10-20 | 2005-12-06 | Other | GREASED & WORKED VALVE | Steel/Wrought Iron |  | HAYWARD | RT = DFD53676; EXCAVATED VALVE, WORKED & GREASED, LEAK WAS CORRECTED.
| 05-00002-1 | 153 | [9 empty] | 2005-10-20 | [5 empty] | HAYWARD
| 05-00002-1 | 153 | [9 empty] | 2005-10-20 | [5 empty] | HAYWARD
| 05-00189- | 55 |  | 1.25 | Transmission |  | Valves |  |  | Other |  | 2005-07-29 | 2005-07-30 | Other | GREASE | Steel/Wrought Iron |  | Y.C. | GREASED VALVE
| 05-00188- | 55 |  | 8 | Transmission |  | Other |  | NUT | Construction Defect |  | 2005-07-29 | 2005-07-30 | Other |  | Steel/Wrought Iron |  | YC | TIGHTEN NUT
| 05-00069-1 | 21 | 23.769 | 0.75 | Service |  | Other |  | BROKEN THREADS | Other | CAR DROVE OVER BOX | 2009-09-22 | 2005-09-22 | Other | TEMP. REPAIRS REBUILD SET WITH THREADED PIPE | Steel/Wrought Iron |  | NAPA | DCUST 8418; MP.0018; SRCRTE: L-210A; SRC MP 23.7690; ARC THREADED FITTINGS
| 05-00207-1 |  | 6.2852 | 6 | Transmission |  | Body of Pipe |  |  | Digin |  | 2005-08-10 | 2005-08-10 | Other | REPLACE <10 TRANS. MAIN | Steel/Wrought Iron |  | YUBA | DFM 1509-05; MP 6.2852; REPLACE 42" OF 6" STEEL PIPE
| 05-00257-1 | 173 | 5.5 | 12 | Transmission |  | Mechanical Joint |  |  | Construction Defect |  | 2005-09-22 | 2005-10-11 | Other | WELD ELBOW | Steel/Wrought Iron |  | ROCKLIN | DFM 1519-04; MP 0.0015; WELD FITTING
| 05-05701-1 | 57A | 6.37 | 18 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2005-01-04 | 2005-01-05 | Welded Sleeve/Can - Weld |  |  |  | DISCOVER BAY | ROUTE L-57A; MP 6.6030; WELDED 18" X 24" X .375, X 50 SMYS
| 05-05701-1 | 57A | 6.37 | 18 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2005-01-04 | 2005-01-05 | Welded Sleeve/Can - Weld |  |  |  | DISCOVER BAY | ROUTE L-57A; MP 6.37; WELDED 18" X 24" X .375, X 50 SMYS
| 05-10071- |  |  | 1.25 | Service |  | Valves |  |  | Other | NEED GREASE | 2005-04-29 | 2005-05-02 | Other | GREASE VALVE | Steel/Wrought Iron |  | M.H. | GREASED VALVE; SOAP TEST
| 05-11001-1 | 105 | 6.91 | 30 | Transmission |  | Valves |  |  | Unknown |  | 2005-05-24 | 2005-07-26 | Other | GREASED FITTING | Steel/Wrought Iron |  | FREMONT | GREASED VALVE, STOPPED LEAK; GREASED VALVE
| 05-16901-1 | 169 | 5.1 | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2005-04-11 | 2005-04-23 | Other | WELDED NEW PIPE SECTION |  |  | E/O WILLIAMS | L-169A, M.P. 5.1308; CUT OUT & REPLACED 179'-6" OF 16" L-169
| 05-16901-1 | 169 | 5.1 | 16 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2005-04-11 | 2005-04-23 | Other | WELDED NEW PIPE SECTION |  |  | E/O WILLIAMS | L-169A, M.P. 5.1308; CUT OUT & REPLACED 179'-6" L-169
| 05-20001-1 |  | 0.0001 | 2 | Transmission |  | Valves |  |  | Unknown |  | 2005-01-06 | 2005-01-06 | Other | GREASE | Steel/Wrought Iron |  | BAKERSFIELD | DFM 6601-01, MP 0.0001
| 05-20002-1 | 200 | 0.0066 | 6 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2005-02-16 | 2005-02-17 | ABANDON |  |  |  | RIO VISTA | ROUTE 200A3-7; MP 0.0066
| 05-20002-1 | 200A | 0.0066 | 6 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2005-02-16 | 2005-02-17 | ABANDON |  |  |  | RIO VISTA | ROUTE 200A3-7; MP. 0.0066
| 05-20065-1 | 181B | 10.126 | 16 | Transmission |  | Valves |  |  | Other | VALVE CORE LEAK | 2005-11-22 | 2006-02-17 | Other | GREASED VALVE | Steel/Wrought Iron |  | PAJARO | L-181B; MP 10.1268; GREASED VALVE
| 05-20229- |  | 3.2156 | 16 | Transmission |  | Valves |  |  | Unknown |  | 2005-08-31 | 2005-08-31 | Other | GREASED VALVE | Steel/Wrought Iron |  | ORANGEVALE | DFM 0617-08, M.P. 3.2156; GREASED VALVE & REPLACED 1/4" PLUG; GREASED VALVE - D3.5 - NO EXPOSED PIPE.
| 05-20577-1 | 132 | 48.2962 | 24 | Transmission |  | Valves |  |  | Other | DRY GREASE | 2005-09-07 | 2005-09-07 | Other | GREASED VALVE | Steel/Wrought Iron |  | S.S. | SRC RTE, L-132, SRC MP MP 48.2962; GREASED VALVE
| 05-20577-1 |  |  | 24 | Transmission |  | Valves |  |  | Other | DRY GREASE | 2005-09-07 | 2005-09-07 | Other | GREASED VALVE | Steel/Wrought Iron |  | S.S. | GREASED VALVE
| 05-21079-1 |  | 0.9829 |  | Distribution Main |  | Fitting |  |  | Other |  | 2005-11-30 | 2005-12-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SACRAMENTO | DFM 0607-01 MP. 0.9829; TIGHTENED PLUG ON GAGE TAP
| 05-40110-1 | 142S | 9 | 10 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2005-09-08 | 2005-09-09 | Welded Sleeve/Can - Weld | WEDDING BAND | Steel/Wrought Iron |  | BAKERS | L-142S; MP 8.8834; WELDED BAND AROUND LEAK 21" LEAD; 18" BAND WELDED OVER LEAK
| 05-42483-1 |  | 7.3322 | 6 | Transmission |  | Body of Pipe |  |  |  |  | 2005-11-10 | 2005-11-11 | Replace TP Main |  | Steel/Wrought Iron |  | SAN RAMON | DFM 2408-11; MP 7.3322; REPLACE FIVE FEET OF STEEL DFM
| 05-43042-1 | 191 | 2.8867 | 6 | Transmission |  | Fitting |  |  | Other | GREASE | 2005-02-10 | 2005-03-14 | Other | GREASED VALVE STEM | Steel/Wrought Iron |  | LAFAYETTE | L-191A, MP 2.8869; GREASED FITTING
| 05-50089-1 | 103 | 19.1733 | 103 | Transmission |  | Body of Pipe |  |  |  |  | 2005-11-19 | 2005-11-20 | Replaced TP Main |  | Steel/Wrought Iron |  | SALINAS | L-103 MP; 19.1733; REPLACED 9' OF TP MAIN 12" SMLS
| 05-50089-1 | 103 | 19.1733 | 12 | Transmission |  | Body of Pipe |  |  |  |  | 2005-11-20 | 2005-11-20 | Replaced TP Main |  | Steel/Wrought Iron |  | SALINAS | L-103; MP 19.1733; REPLACED 9' OF TP MAIN 12" SMLS
| 05-60415- | 101 | 19.43 | 0.75 | Transmission |  | Fitting |  |  | Construction Defect |  | 2005-12-10 | 2005-12-13 | Other | INSTALLED PLUG | Steel/Wrought Iron |  | REDWOOD CITY | REMOVE FLANGE & INSTALLED PLUG
| 08-35077-1 | [10 empty] | 2008-05-26 | [5 empty] | YOLO
| 07-62717-1 |  | 10.0603 | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2007-04-26 | 2007-04-26 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | PLEASANTON
| 08-00005-1 | 160701 |  | 8 | Transmission |  | Body of Pipe |  |  | Other |  | 2008-05-29 |  |  |  | Steel/Wrought Iron |  | STOCKTON | 1607-01; MP = 0.2154
| 08-00030-1 | 021E | 13721 | [8 empty] | 2006-04-28 | 2008-05-29 | Replace TP Main |  |  |  | WILLITS | DREG 3861; MP = 0
| 08-00031-1 | 021E | 13655 | [8 empty] | 2006-04-28 | [5 empty] | WILLITS | RT = DREG 3860, MP = 0
| 08-00032-1 | 021E | 13604 | [8 empty] | 2008-04-28 | [5 empty] | WILLITS | RT = DREG 3858; MP = 0
| 08-00033-1 | 021E | 13591 | [8 empty] | 2008-04-28 | [5 empty] | WILLITS | RT = DREG 3857; MP = 0
| 08-00034-1 | 021E | 13579 | [8 empty] | 2008-04-28 | [5 empty] | WILLITS | PT = DREG 3856; MP=0
| 08-00035-1 | 021E | 13504 | [14 empty] | WILLITS | DCUST 849; MP = 0
| 08-00036-1 | 021E | 13472 | [8 empty] | 2008-04-28 | [5 empty] | WILLITS | RT = DREG 3855; MP = 0
| 08-00041-1 | 021E | 12419 | [8 empty] | 2008-04-29 | [5 empty] | REDWOOD VALLEY | RT = DREG3849; MP = 0
| 08-00042-1 | 021E | 12419 | [8 empty] | 2008-04-29 | [5 empty] | REDWOOD VALLEY | RT = DREG3849 ; MP = 0
| 08-00043-1 | 021E | 12395 | [8 empty] | 2008-04-29 | [5 empty] | REDWOOD VALLEY | RT = DREG 3848; MP = 0
| 08-00044-1 | 021E | 12395 | [14 empty] | REDWOOD VALLEY | RT = DREG3848; MP = 0
08-00045-1 | [11 empty] | 2008-04-29 | [5 empty] | REDWOOD CITY | RT = DREG 3847; MP = 0
| 08-00039-1 | 021E | 13331 | [8 empty] | 2008-04-28 | [5 empty] | WILLITS | RT = DREG 9084; MP = 0.014
| 08-00038-1 | 021E | 13353 | [8 empty] | 2008-04-28 | [5 empty] | WILLITS | RT = DREG 9086; MP = 0.0057
| 08-00040-1 | 021E | 13304 | [8 empty] | 2008-04-28 | [5 empty] | WILLITS | RT = DREG 9087; MP = 0.0167
| 08-00037-1 | 021E | 13368 | [8 empty] | 2008-04-28 | [5 empty] | WILLITS | RT = DREG 9088; MP = 0.017
| 08-00046-1 | 021E | 12327 | [8 empty] | 04/29/0000 | [5 empty] | REDWOOD VALLEY | RT = DREG 3845; MP = 0
| 08-00047-1 | 021E | 12286 | [8 empty] | 2008-04-29 | [5 empty] | REDWOOD VALLEY | RT = DREG 3844; MP =0
| 08-00048-1 | 021E | 12286 | [8 empty] | 2008-04-29 | [5 empty] | REDWOOD VALLEY | RT = DREG 3844; MP= 0
| 08-00049-1 | 021E | 12260 | [8 empty] | 2008-04-29 | [5 empty] | REDWOOD VALLEY | RT = DREG 3843; MP = 0
| 08-00050-1 | 021E | 12234 | [8 empty] | 2008-04-29 | [5 empty] | REDWOOD VALLEY | RT = DREG 3841; MP = 0
| 08-00051-1 | 021E | 12214 | [8 empty] | 2008-04-29 | [5 empty] | REDWOOD VALLEY | RT = DREG 3840; MP 0.0078
| 08-00052-1 | 021E | 12214 | [8 empty] | 2008-04-29 | [5 empty] | REDWOOD VALLEY | RT = 3840; MP = 0.0078
| 08-00053-1 | 021E | 12180 | [8 empty] | 2008-04-29 | [5 empty] | REDWOOD VALLEY | RT = DREG 3834; MP = 0
| 08-00054-1 | 021E | 12149 | [8 empty] | 2008-04-29 | [5 empty] | REDWOOD VALLEY | RT = DREG 3838; MP = 0
| 08-00055-1 | 021E | [9 empty] | 2008-04-29 | [5 empty] | REDWOOD VALLEY | RT = DREG 3835; MP = 0
| 08-00058-1 | 021E | 12046 | [8 empty] | 2008-04-29 | [5 empty] | REDWOOD VALLEY | RT = DREG 3835; MP = 0
| 08-00057-1 | 021E | [9 empty] | 2008-04-30 | [5 empty] | UKIAH | RT = DREG 3833; MP = 0
| 08-00058-1 | 021E | [9 empty] | 2008-04-30 | [5 empty] | UKIAH | RT = DREG 3831; MP = 0.0089
| 08-00059-1 | 021E | [9 empty] | 2008-04-30 | [5 empty] | UKIAH | RT = DREG 3830; MP = 0
| 08-00060-1 | 012E | [9 empty] | 2008-04-30 | [5 empty] | UKIAH | DCUST 9089; MP = 0.0161
| 08-00061-1 | 021E | 11574 | [8 empty] | 2008-04-30 | [5 empty] | UKIAH | DREG 3828; MP = 0.0210
| 08-00062-1 | 021E | [9 empty] | 2008-04-30 | [5 empty] | UKIAH | RT = DCUST 850; MP = 0
| 08-00063-1 | 021E | 11462 | [8 empty] | 2008-04-30 | [5 empty] | UKIAH | RT = DCUST 847; MP = 0
| 08-00064-1 | 021E | 11260 | [8 empty] | 2008-05-01 | [5 empty] | UKIAH | RT = DREG 3825; MP = 0.0237
| 08-00065-1 | 021E | 12260 | [8 empty] | 2008-05-01 | [5 empty] | UKIAH | RT = DREG 3825; MP 0.0232
| 08-00066-1 | 021E | 11260 | [8 empty] | 2008-05-01 | [5 empty] | UKIAH | RT = DREG 3825; MP = 0.0018
| 08-00067-1 | 021E | 9937 | [8 empty] | 2008-05-01 | [5 empty] | HOPLAND | RT = DREG 9090; MP = 0.0082
| 08-00068-1 | 021E | 9931 | [8 empty] | 2008-05-01 | [5 empty] | HOPLAND | RT = DREG 3815; MP = 0
| 08-00662-1 | 173 | [9 empty] | 2008-03-12 | [5 empty] | PENRYN | RT = DREG 5007; MP = 0
| 08-10151-1 | 123 |  | 0.25 | Single Service |  | Fitting |  |  | Other |  | 2008-04-28 | 2008-05-21 | Other |  | Steel-Other |  | LINCOLN | RT = 1523-01; MP = 0.000; 1/4" VALVE STEM
| 08-10020-1 | 118 | 11.34 | [8 empty] | 2008-05-15 | [5 empty] | MADERA | RT = 118B; MP = 11.3273
| 08-20144-1 | [10 empty] | 2008-05-20 | [5 empty] | OAKLAND | RT = 153; MP = 27.7587
| 08-20145-1 | [10 empty] | 2008-05-20 | [5 empty] | OAKLAND | RT = 153; MP = 27.8301
| 08-20146-1 | [10 empty] | 2008-05-20 | [5 empty] | OAKLAND | RT = X9092; MP = 0.0019
| 08-20279-1 | [10 empty] | 2008-05-03 | [5 empty] | SAN MATEO | RT = 0209-01; MP = 0.5259
| 08-20282-1 | [10 empty] | 2008-05-04 | [5 empty] | BELMONT | 101; MP = 22.7851
| 08-20283-1 | [10 empty] | 2008-05-04 | [5 empty] | SAN MATEO | RT = 014-01; MP = 0.7126
| 08-20286-1 | [10 empty] | 2008-05-10 | [5 empty] | BURLINGAME | RT = 0211-01; MP = 0.6800
| 08-20287-1 | [10 empty] | 2008-05-10 | [5 empty] | BURLINGAME | RT = 101; MP = 30.4156
| 08-20294-1 | [10 empty] | 2008-05-08 | [5 empty] | MENLO PARK | RT = DREG 3743; MP = 0.0495
| 08-20295-1 | [10 empty] | 2008-05-09 | [5 empty] | ATHERTON | RT = DREG 8214; MP = 0.0610
| 08-20297-1 | [10 empty] | 2008-05-08 | [5 empty] | WOODSIDE | RT = 132; MP = 21.4026
| 08-20306-1 | 13-3347 | [9 empty] | 2008-05-21 | [5 empty] | ATHERTON | RT = 0205-1; MP = 0.6945
| 08-30566-1 | [10 empty] | 2008-04-30 | [5 empty] | SUNNYVALE | RT = 8807-01; MP = 0.4295
| 08-30571-1 | [10 empty] | 2008-04-30 | [5 empty] | SUNNYVALE | RT = 8807-01; MP = 0.1722
| 08-33002-1 | 210 |  | 4 | Transmission |  | Valves |  |  | Unknown |  | 2008-05-17 | 2008-05-17 | Other |  | Steel/Wrought Iron |  | FAIRFIELD | RT = DREG 5266; MP = 0.0284
| 08-33004-1 | [10 empty] | 2008-05-17 | [5 empty] | VACAVILLE | RT = DREG 4040; MP = 0.0400
| 08-33005-1 | [10 empty] | 2008-05-18 | [5 empty] | DIXON | RT = DCUST 937; MP = 0
| 08-62709-1 | [10 empty] | 2008-04-10 | [5 empty] | PLEASANTON | RT = DREG 5314; MP = 0.0005
| 08-10008-1 | [10 empty] | 2008-02-11 | [5 empty] | SANTA CRUZ | LINE 1816-15; MP = 1.6157
| 08-20015-1 |  |  | 6 | Distribution Main |  | Other |  |  | Other |  | 2008-01-30 | 2008-02-20 | Other |  | Other |  | BAKERSFIELD | DREG 5379; MP = 0.1183; ZONE VALVE
| 08-00021-1 | 021E | 11194 | 4 | Transmission |  | Valves |  |  | Other |  | 2008-03-19 | 2008-03-25 | Other |  | Steel/Wrought Iron |  | UKIAH | RT = DREG 3824; MP = 0.0011; GREASED VALVE
| 07-19501-1 | 195B7-9 | 0.09 | 10 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2007-10-18 | 2007-10-19 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | ISLETON | RT = 195B7-9 MP = 0.0907; INSTALL WELDED SLEEVE
| 08-20013-1 |  |  |  | Distribution Main |  | Regulator |  |  | Other |  | 2008-01-30 | 2008-02-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | BAKERSFIELD | RT = UTREG7783; MP = 0; TIGHENING FITTING AND REPLACED DIAPHRAGM
| 08-02068-1 | [10 empty] | 2008-03-22 | [5 empty] | MANTECA | RT = 1602-01; MP = 0.7300
| 07-19502-1 | 195-0140 | 0 | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2007-10-25 | 2007-10-25 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | BRANNAN ISLAND | RT = 195-0140; MP = 0; INSTALLED SS CLAMP
| 07-19503-1 | 195B7-9 | 0.09 | 10 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2007-11-05 | 2007-11-29 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | ISLETON | RT195B7-9; MP = 0.0924; INSTALLED 20' CAN, LEFT DEACTIVATED FOR
| 07-19504-1 | 195B7-9 | 0.45 | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2007-11-05 | 2007-11-05 | Deactivate #TP Main |  | Steel/Wrought Iron |  | ISLETON | RT = 195B7-9; MP = 0.4518; DEACTIVATED PIPELIN FOR 3RD PARTY SALE
| 07-19505-1 | STUB7787 | 0 | 1 | Gathering |  | Fitting |  |  | Material Failure |  | 2007-11-29 | 2007-11-29 | Other |  | Steel/Wrought Iron |  | ISLETON | RT = STUB 7787; MP = 0; REMOVED BROKEN GREASE FITTING
| 07-19601-1 | 196 | 0 | 6 | Gathering |  | Body of Pipe |  |  | Unknown |  | 2007-08-23 | 2007-08-23 | Deactivate #TP Main |  | Steel/Wrought Iron |  | THORNTON | RT = 196; MP = 0; N/A RETIRED IN PLACE
| 07-20001-1 | 200A15-2 | 0.23 | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2007-01-24 | 2007-03-28 | Deactivate #TP Main |  | Steel/Wrought Iron |  | RIO VISTA | RT = 200A15.2; MP = 0.2300; RETIRED PIPELINE INPLACE SO#6102223
| 08-10701-1 | 107 | 15.27 | 22 | Transmission |  | Other |  |  | Material Failure |  | 2008-03-10 | [5 empty] | LIVERMORE | RT = 107; MP = 0.3720
| 08-30201-1 | 302-213 | 22.57 | 6 | Transmission |  | Body of Pipe |  |  |  |  | 2008-02-29 | 2008-03-01 | Replace TP Main |  | Steel/Wrought Iron |  | SUTTER | RT = 302-213; MP = 22.5702
| 08-00017-1 | 21 |  | 3 | Transmission |  | Valves |  |  | Unknown |  | 2008-03-04 | 2008-03-05 | Other |  | Other |  | VALLEJO | RT = 021H; MP = 5.6976
| 07-30035-1 | 2L125 |  | 2 | Gathering |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2007-12-14 | 2008-01-15 | Replace Dist Main < 100 ft |  | Steel/Wrought Iron |  | FORTUNA | RT = 125; MP = 0; REPLACED 1'-2" STL PIPE
| 08-02011-1 | 021E |  | 0.75 | Transmission |  | Girth Weld |  |  | Unknown |  | 2008-03-06 | 2008-03-06 | Patch Welded |  | Steel/Wrought Iron |  | WINDSOR | RT = DREG 3706; MP = 0; WELD LEAK ON PREVIOUS WELD
| 08-00574-1 | DREG8724 | [9 empty] | 2008-03-14 | [5 empty] | EL DORADO HILLS | RT = DREG 8724; MP = 5.9363
| 08-00058-1 | 292 | [9 empty] | 2008-03-18 | [5 empty] | GRASS VALLEY | RT = DREG 5258; MP = 0
| 08-00566-1 | 173 | [9 empty] | 2008-03-10 | [5 empty] | PENRYN | RT = DREG 5011; MP = 0
| 08-00575-1 | 123 |  | 4 | Transmission |  | Valves |  |  | Other |  | 2008-03-17 | 2008-03-17 | Other |  | Steel/Wrought Iron |  | ROSEVILLE | RT = STUB 7516; MP = 0.0011; REGREASED & ACCTUATED
| 08-00577-1 | 1523-01 | [9 empty] | 2008-03-18 | [5 empty] | LINCOLN | RT = 1523-01; MP = 1.8161
| 08-00578-1 | 123 | [9 empty] | 2008-03-18 | [5 empty] | LINCOLN | RT = 123; MP = 9.5250
| 08-00565-1 | 173 | [9 empty] | 2008-03-10 | [5 empty] | PENRYN | RT = 173; MP = 14.4889
| 08-00016-1 | 21 |  |  | Transmission |  | Fitting |  |  | Construction Defect |  | 2008-03-04 | 2008-03-05 | Tighten Cap or Bolt |  | Other |  | BENICIA | RT = DREG 6902; MP = 0
| 08-02012-1 | 1307-01 |  | 6 | Transmission |  | Fitting |  |  | Unknown |  | 2008-03-13 | 2008-03-13 | Other |  | Steel/Wrought Iron |  | WINDSOR | RT = 1307-01; MP = 6.4717; REPLACED CENTER PLUG ON MULLER-REDOPE-TA
| 08-12448-1 | 1302-02 |  | 0.75 | Transmission |  | Valves |  |  | Unknown |  | 2008-03-05 | 2008-03-05 | Other |  | Steel/Wrought Iron |  | SEBASTOPOL | RT = DREG 4612; MP = 0; GREASE VALVE
| 08-13311-1 | DFM |  | 0.75 | Transmission |  | Regulator |  |  | Other |  | 2008-03-10 | 2008-03-10 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SONOMA | 1305-01; RT = DREG 4643 MP = 0; REDOPED CAP & PLUG
| 08-00059-1 | 202 | [9 empty] | 2008-03-19 | [5 empty] | PENN VALLEY | RT = DREG 5253; MP = 0
| 08-00576-1 | 1523-01 | [9 empty] | 2008-03-18 | [5 empty] | LINCOLN | RT = 1523-01; MP = 2.5852
| 08-20004-1 | [10 empty] | 2008-01-15 | [5 empty] | BAKERSFIELD | RT = 1425; MP = 1.2984; DREG 4805
| 07-20004-1 | [10 empty] | 2007-01-19 | [5 empty] | BAKERSFIELD
| 08-20004-1 | [10 empty] | 2008-01-15 | [5 empty] | BAKERSFIELD | RT = 1425; MP = 1.2984; DREG 4805
| 08-30002-1 | 132A |  | 0.75 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2008-01-16 | 2008-02-14 | Replace TP Main |  | Steel/Wrought Iron |  | MT VIEW | RT = 132A MP = 1.4444; 5' 3/4" TAP PIPI9NG REPLACED
| 08-20041-1 | [10 empty] | 2008-01-28 | [5 empty] | ALAMEDA | RT = 0117-03; MP = 0.0010
| 08-20058-1 | [10 empty] | 2008-02-13 | [5 empty] | EMERYVILLE | RT = DCUST777; MP = 0.0057
| 08-20070-1 | 105 | 43 | [8 empty] | 2008-02-13 | [5 empty] | EMERYVILLE | 0112-01 MP = 0.5907; 0112-01
| 08-20013-1 | [10 empty] | 2008-01-30 | [5 empty] | BAKERSFIELD | RT = UTPEG7783 MP = 0
| 08-20014-1 |  | 0 | [8 empty] | 2008-01-30 | [5 empty] | BAKERSFIELD
| 08-20015-1 | [10 empty] | 2008-01-30 | [5 empty] | BAKERSFIELD
| 08-20056-1 |  | 0.0099 | [8 empty] | 2008-02-13 | 2008-02-13 |  |  |  |  | EMERYVILLE
| 08-20059-1 |  | 0.016 | [8 empty] | 2008-02-13 | 2008-02-13 |  |  |  |  | EMERYVILLE
| 08-20016-1 |  | 0 | [8 empty] | 2008-01-31 | [5 empty] | BAKERSFIELD
| 08-20017-1 |  | 0 | [8 empty] | 2008-01-31 | [5 empty] | BAKERSFIELD
| 08-20018-1 |  | 0 | [8 empty] | 2008-01-31 | [5 empty] | ARVIN
| 08-00019-1 | 0406-01 | 0 | 0.75 | Transmission |  | Valves |  |  | Construction Defect |  | 2008-02-25 | 2008-02-25 | Other |  | Steel/Wrought Iron |  | NAPA | REPLACED BROKEN GREASE TAP INTO VALVE
| 08-02004-1 | 021E | 68.3285 | [8 empty] | 2008-02-06 | 2008-02-06 |  |  |  |  | HEALDSBURG
| 08-02007-1 |  | 70.1681 | [8 empty] | 2008-02-07 | [5 empty] | HEALDSBURG
| 08-11835-1 |  | 25.3101, 24.57 | [8 empty] | 2008-02-15 | [5 empty] | SANTA ROSA
| 07-55064-1 | 158 | 6.8802 | 6 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2007-11-13 | 2008-02-07 | Other |  | Steel/Wrought Iron |  | WOODLAND
| 08-00022-1 | 124 | 23.1153 | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2008-01-27 | 2008-01-28 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | MARYSVILLE | GC TO REPAIR LINE/INSTALL SLEEVE/X-RAY WELDS
| 08-00557-1 | 0617-06 | 20.0348 | [8 empty] | 2008-02-19 | [5 empty] | EL DORADO HILLS
| 08-00023-1 | 123 | 11.5348 | [8 empty] | 2008-01-02 | [5 empty] | LINCOLN
| 08-02025-1 |  | 1.945 | [8 empty] | 2008-02-28 | [5 empty] | STOCKTON
| 08-02026-1 | [10 empty] | 2008-02-28 | [5 empty] | STOCKTON
| 08-30016-1 |  | 0.0193 | [8 empty] | 2008-02-26 | [5 empty] | MODESTO
| 08-30007-1 | 311 | 7.55 | 6 | Transmission |  | Valves |  |  | Other |  | 2008-01-28 | 2008-04-01 | Other |  | Steel/Wrought Iron |  | CAMPBELL | GREASED VALVE
| 08-10001-1 | [10 empty] | 2008-04-26 | 2008-04-26 |  |  |  |  | RICHMOND
| 08-21020-1 |  | 0.0027 | 0.75 | Single Service |  | Valves |  |  | Unknown |  | 2008-02-10 | 2008-04-23 | Other |  | Steel/Wrought Iron |  | BERKELEY | GREASED 3/4" ROCKWELL VALVE.
| 07-42458-1 | 0 | 0.0211 | 6 | Transmission |  | Valves |  |  | Unknown |  | 2007-08-22 | 2008-04-16 | Other |  | Steel/Wrought Iron |  | LIVERMORE | GREASED VALVE & TIGHTENED BOLT.
| 08-30009-1 | 189 | 0.001 | [8 empty] | 2008-04-01 | 2008-04-01 |  |  |  |  | EUREKA
| 08-00025-1 | 021E | 11941 | 2 | Transmission |  | Valves |  |  | Other |  | 2008-04-04 | 2008-04-24 | Other |  | Steel/Wrought Iron |  | CALPELLA | GREASED VALVE & REPLACED GREASE FITTINGS; SOAPED, SERVICED VALVE & REPLACED GREASE STEM
| 07-20308-1 | 119 | N/A (6.6900) | 0.75 | Transmission |  | Fitting |  |  | Material Failure |  | 2007-10-31 | 2008-03-05 | Deactivated Entire Service |  | Steel/Wrought Iron |  | SACRAMENTO | CUT 3/4" LINE OFF 16" MAIN - RCV'D IN MAPPI; SOAP TESTED C/O
| 08-35049-1 |  | 1.0403 | [8 empty] | 2008-04-15 | [5 empty] | WINTERS
| 03-21198-1 | 101 | 43.26 | 0.75 | Single Service |  | Valves |  |  | Construction Defect |  | 2003-09-19 | 2008-04-21 | Other |  | Steel/Wrought Iron |  | SAN FRANCISCO | GREASED 3/4 PLUG VALVE
| 08-00567-1 | 173 | 0 | [8 empty] | 2008-03-13 | [5 empty] | ROCKLIN
| 08-00568-1 | 173 | N/A | 4 | Transmission |  | Fitting |  |  | Other |  | 2008-03-11 | 2008-04-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | LOOMIS
| 08-00569-1 | 1519-04 | 0.0014 | 12 | Transmission |  | Valves |  |  | Other |  | 2008-03-12 | 2008-04-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ROCKLIN
| 08-00573-1 | DREG4861 | [9 empty] | 2008-03-13 | [5 empty] | ROCKLIN
| 08-10080-1 |  | 34.88 | [8 empty] | 2008-04-22 | [5 empty] | CHOWCHILLA
| 08-10351-1 | 118 | 27.72 |  | Transmission | [6 empty] | 2008-04-11 | [5 empty] | MADERA
| 08-10352-1 | 118 | 27.67 | [8 empty] | 2008-04-11 | [5 empty] | MADERA
| 08-10354-1 | 118 | 28.58 | [8 empty] | 2008-04-14 | [5 empty] | MADERA
| 08-10356-1 |  | 16.64 | [8 empty] | 2008-04-14 | [5 empty] | MADERA
| 08-10355-1 | 118 | 28.47 | [8 empty] | 2008-04-14 | [5 empty] | MADERA
| 08-00028-1 | 021E | 11194 | 4 | Transmission |  | Valves |  |  | Other |  | 2008-04-24 |  |  |  | Steel/Wrought Iron |  | UKIAH
| 08-10002-1 | [10 empty] | 2008-04-26 | 2008-04-26 |  |  |  |  | RICHMOND
| 08-00570-1 | 173 | [9 empty] | 2008-03-12 | [5 empty] | ROCKLIN
| 08-00572-1 | 173 | 0.0029 | [8 empty] | 2008-03-13 | [5 empty] | ROCKLIN
| 08-10026-1 | 118 | 11.34 | [8 empty] | 2008-04-14 | 2008-04-18 |  |  |  |  | MADERA
| 09-30011-1 |  |  | 2 | Single Service |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2009-03-21 | 2009-03-21 | Other |  | Steel/Wrought Iron |  | LOLETA | SHUT OFF FIRE VALVE IN ST & INST DISK IN; SOAP TESTED
| 09-70087-1 | 1815-2 |  | 2 | Transmission |  | Valves |  |  | Other |  | 2009-03-26 | 2009-04-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MONTEREY | REPAIRED THREE LEAKS, TWO ON THE INLET MUELLER VALVES, CAPTS WERE LOOSE, DOPED BOTH - REPLACED 289 RELIEF
| 09-70078-1 | 1813 |  | 4 | Transmission |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2009-03-24 | 2009-03-24 | Welded Sav-A-Valve - Weld |  | Steel/Wrought Iron |  | SEASIDE | REPLACED A 20" SECTION OF 4" PIPE BETWEEN THE 10" MAIN AND THE #2 BRIDLE VALVE AT V. 12.95
| 09-00020-1 |  | 1.8729 | [8 empty] | 2009-03-20 | 2009-03-20 |  |  |  |  | VALLEJO
| 09-00021-1 |  | 1.8707 | [8 empty] | 2009-03-20 | 2009-03-20 |  |  |  |  | VALLEJO
| 09-00022-1 |  | 0 | [8 empty] | 2009-03-20 | 2009-03-20 |  |  |  |  | VALLEJO
| 09-00023-1 | [10 empty] | 2009-03-23 | 2009-03-23 |  |  |  |  | VALLEJO
| 09-00024-1 | [10 empty] | 2009-03-23 | 2009-03-23 |  |  |  |  | VALLEJO
| 09-00025-1 |  | 8 | [8 empty] | 2009-03-24 | 2009-03-24 |  |  |  |  | AMERICAN CANYON
| 09-00026-1 |  | 8 | [8 empty] | 2009-03-24 | 2009-03-24 |  |  |  |  | AMERICAN CANYON
| 09-00027-1 | [10 empty] | 2009-03-24 | 2009-03-24 |  |  |  |  | AMERICAN CANYON
| 09-00028-1 | [10 empty] | 2009-03-25 | 2009-03-25 |  |  |  |  | AMERICAN CANYON
| 09-00029-1 | [10 empty] | 2009-03-25 | 2009-03-25 |  |  |  |  | AMERICAN CANYON
| 09-00231-1 | 021E | 66 | [8 empty] | 2009-03-21 | [5 empty] | HEALDSBURG
| 09-00233-1 | 021E | 65.58 | [8 empty] | 2009-03-21 | [5 empty] | HEALDSBURG
| 09-02037-1 |  |  | 0.75 | Single Service |  | Regulator |  |  | Other |  | 2009-03-17 | 2009-04-09 | Other |  | Steel/Wrought Iron |  | LODI
| 09-02038-1 |  | 0.95 | [8 empty] | 2009-03-17 | [5 empty] | LODI
| 09-06073-1 | [10 empty] | 2009-02-28 | [5 empty] | ACAMPO
| 09-10036-1 | [10 empty] | 2009-03-05 | [5 empty] | SANTA CRUZ
| 09-15038-1 |  | 1.1623 | [8 empty] | 2009-03-17 | 2009-03-17 |  |  |  |  | ALAMEDA
| 09-20073-1 | [10 empty] | 2009-03-26 | [5 empty] | HALF MOON BAY
| 09-30008-1 | 126A | 9.1021 | [8 empty] | 2009-02-19 | [5 empty] | EUREKA
| 09-30062-1 | [10 empty] | 2009-03-09 | [5 empty] | HILMAR
| 09-40015-1 | 187 | [9 empty] | 2009-02-27 | [5 empty] | KING CITY
| 09-40017-1 | 187 | 26.1 | [8 empty] | 2009-03-11 | [5 empty] | KING CITY
| 09-40018-1 | 187 | 38.08 | [8 empty] | 2009-03-11 | [5 empty] | KING CITY
| 09-40049-1 | DFM | 2.2085 | 8 | Transmission |  | Girth Weld |  |  | Weld Failure |  | 2009-03-13 | 2009-03-15 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | RIDGECREST | WELDS WERE INSPECTED BY KEVIN RAWLINS OF VALLEY INDUSTRIAL BY X-RAY
| 09-56003-1 | DFM |  | 2 | Transmission |  | Body of Pipe |  |  |  |  | 2009-03-19 |  | Replace TP Main |  | Steel/Wrought Iron |  |  | INS... PIPE & NEW 3" VA (WRITING COVERED BY STICKY NOTE); DIG-IN ON V-1 TO DETERMINE POSITION OF VALVE STEM AFTER EMERGENCY CALL OF VALVE FAILURE AND PRE
| 09-80008-1 | 300B | 42392 | [8 empty] | 2009-03-05 | [5 empty] | HOLLISTER
| 09-90079-1 | [10 empty] | 2009-03-10 | [5 empty] | THERMALITO
| 09-30008-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2009-01-16 | 2009-02-26 | Deactivated Partial Service |  | Steel/Wrought Iron |  | SUNNYVALE | ABANDON 227' OF 2" MAIN
| 09-50006-1 | 301F | 2.3 | 0.75 | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2009-01-13 | 2009-03-18 | Other |  | Steel/Wrought Iron |  | SALINAS | H-202, RELIEF VALVE; RELIEF VALVE WAS WEEPING GAS, READJUSTED PRESSURE TO STOP GAS FROM LEAKING BYE.
| 08-20300-1 | 0210-01 |  | 2 | Transmission |  | Fitting |  |  | Other |  | 2008-05-14 | 2009-02-20 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | HALF MOON BAY | REPAIRED LEAKS ON H TO H SET; SOAP
| 09-70041-1 | 1813-02 | 15.7 | 1 | Distribution Main |  | Regulator |  |  | Construction Defect |  | 2009-02-13 | 2009-03-06 | Other |  | Steel/Wrought Iron |  | MONTEREY | CHANGE O-RING IN FISHER REG; REPLACED O-RING ON HP FISHER REGULATOR - SOAP TEST FOR LEAKS
| 09-50005-1 | 301F | 0.03 | 6 | Transmission |  | Valves |  |  | Unknown |  | 2009-01-13 | 2009-03-18 | Other |  | Steel/Wrought Iron |  | SALINAS | WHEEL VALVE; WHEEL VALVE WAS LEAKING, GREASED BY HAND PUMP STOPPED LEAKING. SKINNER CLAMP ON GREASE FITTING EXTENSION WAS LOOSE & LEAKING, TIGHTENE
| 09-20074-1 | 0210-01 |  | 2 | Transmission |  | Fitting |  |  | Other |  | 2009-03-26 |  |  |  | Steel/Wrought Iron |  | HALF MOON BAY
| 08-80777-1 |  |  | 12 | Single Service |  | Fitting |  |  | Other |  | 2008-11-21 | 2009-03-07 | Replace Entire Service |  | Steel/Wrought Iron |  | FRESNO | REPLACED SERVICE
| 09-10024-1 |  | 2.33 | [8 empty] | 2009-02-04 | [5 empty] | SANTA CRUZ
| 09-13101-1 | 131 | 9.08 | 12 | Transmission |  | Unknown |  |  | Unknown |  | 2009-01-27 | 2009-02-19 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | OAKLEY
| 09-10022-1 | 1816.15 | [9 empty] | 2009-02-04 | [5 empty] | SANTA CRUZ
| 09-10020-1 | [10 empty] | 2009-02-04 | [5 empty] | SANTA CRUZ
| 09-20022-1 | [10 empty] | 2009-02-04 | [5 empty] | HALF MOON BAY
| 09-50014-1 | 301E | 89 | [8 empty] | 2009-02-10 | [5 empty] | SALINAS
| 09-53026-1 | DFM | [9 empty] | 2009-02-04 | [5 empty] | DIXON
| 09-53027-1 | DFM | [9 empty] | 2009-02-07 | [5 empty] | VACAVILLE
| 09-70033-1 | [10 empty] | 2009-02-10 | [5 empty] | MARINA
| 09-70032-1 | [10 empty] | 2009-02-10 | [5 empty] | MONTEREY
| 09-70034-1 | 301 | [9 empty] | 2009-02-10 | [5 empty] | MARINA
| 09-70035-1 | [10 empty] | 2009-02-10 | [5 empty] | SEASIDE
| 09-70036-1 | [10 empty] | 2009-02-10 | [5 empty] | SEASIDE
| 09-70037-1 | [10 empty] | 2009-02-10 | [5 empty] | SEASIDE
| 09-70038-1 | [10 empty] | 2009-02-10 | [5 empty] | CARMEL
| 09-70041-1 | [10 empty] | 2009-02-13 | [5 empty] | MONTEREY
| 09-70042-1 | [10 empty] | 2009-02-13 | [5 empty] | MONTEREY
| 09-70043-1 | [10 empty] | 2009-02-13 | [5 empty] | MONTEREY
| 09-70044-1 | [10 empty] | 2009-02-13 | [5 empty] | MONTEREY
| 09-70045-1 | [10 empty] | 2009-02-13 | [5 empty] | MONTEREY
| 09-70046-1 | [10 empty] | 2009-02-13 | [5 empty] | MONTEREY
| 09-70047-1 | [10 empty] | 2009-02-13 | [5 empty] | MONTEREY
| 09-70048-1 | [10 empty] | 2009-02-13 | [5 empty] | MONTEREY
| 09-70049-1 | [10 empty] | 2009-02-13 | [5 empty] | MONTEREY
| 09-70049-1 |  |  | 3 | Distribution Main |  | Valves |  |  | Other |  | 2009-01-27 | 2009-01-27 | Other |  | Steel/Wrought Iron |  | BIGGS | ORB-58
| 09-02004-1 |  | 37.9105 | [8 empty] | 2009-01-09 | [5 empty] | SAN ANDREAS
| 08-30038-1 | 137B | 722 | 8 | Transmission |  | Girth Weld |  |  | Weld Failure |  | 2008-09-17 | 2009-02-15 | Patch Weld - Weld |  | Steel/Wrought Iron |  | ARCATA | GROUND OUT AND REPAIRED WELD
| 08-50095-1 | 103 | 1.7 | [8 empty] | 2008-11-21 | [5 empty] | SALINAS
| 08-00226-1 | DFM | 2.9573 | 4 | Transmission |  | Other |  |  | Material Failure |  | 2008-12-30 | 2009-01-07 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | MARYSVILLE | INSTALLED NEW 4" COMPLETION ON BOTTOM TA
| 08-02657-1 | 1305-01 |  | 2 | Transmission |  | Valves |  |  | Other |  | 2008-09-26 | 2009-01-26 | Other |  | Steel/Wrought Iron |  | SONOMA
| 08-50093-1 | 103 | 17.9992 | [8 empty] | 2008-11-20 | [5 empty] | SALINAS
| 08-50094-1 | 301C | 2.3 | 0.75 | Transmission |  | Other |  |  | Equipment Malfunction |  | 2008-11-21 | 2009-02-20 | Other |  | Steel/Wrought Iron |  | SALINAS
| 09-00000-1 |  | 0.9401 | [8 empty] | 2009-02-23 | [5 empty] | TRACY
| 09-02015-1 |  | 9.5217 | [8 empty] | 2009-02-03 | [5 empty] | ACAMPO
| 09-10019-1 | [10 empty] | 2009-02-03 | [5 empty] | SCOTTS VALLEY
| 08-50096-1 | 103 | 22.21 | [8 empty] | 2008-11-20 | [5 empty] | SALINAS
| 08-50091-1 | 301C | 13.85 | [8 empty] | 2008-11-21 | [5 empty] | SALINAS
| 08-50092-1 | 301C | [9 empty] | 2008-11-21 | [5 empty] | SALINAS
| 05-20069-1 | DREG5155 | 0.01 | 0.75 | Service |  | Valves |  |  | Other |  | 2005-11-22 | 2007-05-07 | Other |  | Steel/Wrought Iron |  | AROMAS | GREASED LEAKING FITTING ON GAS VALVE
| 08-10008-1 | 1816-15 | 1.6457 | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2008-02-11 | 2008-04-16 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | SANTA CRUZ
| 07-10061-1 | DREG5145 | 0.11 | 6 | Distribution Main |  | Valves |  |  | Other |  | 2007-08-21 | 2008-08-18 | Other |  | Steel/Wrought Iron |  | SANTA CRUZ | GREASED VALVE
| 08-30009-1 | 189 | 0.01 | 0.75 | Transmission |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2008-04-01 | 2008-05-29 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | EUREKA | WELDED COUPLING & REPLACED VALVE
| 07-60001-1 | DCUST7750 | 0.0025 | 2 | Transmission |  | Valves |  |  | Other |  | 2007-11-06 | 2008-03-22 | Other |  | Steel/Wrought Iron |  | SEBASTOPOL | GREASED VALVE
| 07-50021-1 | 118A | 81.62 | 4 | Transmission |  | Unknown |  |  | Unknown |  | 2007-01-25 | 2007-01-31 | Deactivate #TP Main | ; | Steel/Wrought Iron |  | HILMAR | MAIN C/O BY GC ON JOB #30298242
| 01-30040-1 | 7226-01 | 5.5866 | 0.25 | Distribution Main |  | Regulator |  |  | Construction Defect |  | 2001-06-19 | 2007-10-18 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | RIVERBANK | DOPED & TIGHTENED PLUG ON VALVE IN UPSTR
| 98-30232-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1998-10-30 | 2008-10-20 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | WESTLEY | CLAMPED PIT
| 07-55015-1 |  |  | 0.75 |  |  | Body of Pipe |  |  |  |  | 2007-03-19 | 2007-03-20 | Replace Partial Service |  | Steel/Wrought Iron |  | LIVINGSTON | INSTLD 20' OF NEW PIPE AND TWO HP COUPLINGS
| 07-25076-1 | 153 |  | 6 | Transmission |  | Valves |  |  | Other |  | 2007-03-06 | 2007-04-25 | Other |  | Steel/Wrought Iron |  | OAKLAND | GREASED VALVE
| 06-22320-1 | 0114-01 | 0.0008 | 2 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2006-10-11 | 2008-04-03 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | OAKLAND | REMOVED AND DOPED AND TIGHTENED CAP
| 08-20144-1 | 153 | 27.7587 | 20 | Transmission |  | Valves |  |  | Unknown |  | 2008-05-20 | 2008-07-29 | Other |  | Steel/Wrought Iron |  | OAKLAND | GREASED VALVE X-36
| 07-15096-1 | DCUST8798 | 0.0068 | 0.75 | Service |  | Riser |  |  | Unknown |  | 2007-05-15 | 2007-05-15 | Deactivated Entire Service |  | Steel/Wrought Iron |  | OAKLAND | SHUT OFF HI TO HI SET AND REMOVED METER
| 07-00458-1 | DCUST1705 | 0.0002 | 0.75 | Service |  | Fitting |  |  | Other |  | 2007-05-09 | 2007-06-21 | Other |  | Steel/Wrought Iron |  | LINDA | SHUT IN SET, TOOK APART & RE-DOPED FITTI
| 03-00053-1 | 0617-06 | 20.6689 | 6 | Distribution Main |  | Fitting |  |  | Unknown |  | 2003-02-15 | 2007-03-30 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | EL DORADO HILLS | REDOPED FITTINGS
| 08-00058-1 | DREG5258 |  | 8 | Transmission |  | Fitting |  |  | Other |  | 2008-03-18 | 2008-04-01 | Other |  | Steel/Wrought Iron |  | GRASS VALLEY
| 08-00577-1 | 1523-01 | 1.8161 | 8 | Transmission |  | Valves |  |  | Construction Defect |  | 2008-03-18 | 2008-08-05 | Other |  | Steel/Wrought Iron |  | LINCOLN | LOOSE PLUG - REDOPED & TIGHTENED
| 08-00570-1 | GCUST5857 |  | 3 | Transmission |  | Valves |  |  | Other |  | 2008-03-12 | 2008-05-23 | Other |  | Steel/Wrought Iron |  | ROCKLIN | TIGHTENED STEM BOLT
| 08-00572-1 | 173-15 | 0.0029 | 8 | Transmission |  | Valves |  |  | Other |  | 2008-03-13 | 2008-05-22 | Other |  | Steel/Wrought Iron |  | ROCKLIN | GREASED & REWELDED
| 08-00576-1 | 1523-01 | 2.5852 | 8.625 | Transmission |  | Valves |  |  | Other |  | 2008-03-18 | 2008-04-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | LINCOLN
| 08-00578-1 | 123 | 9.525 | 16 | Transmission |  | Valves |  |  | Other |  | 2008-03-18 | 2008-04-04 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | LINCOLN
| 05-26102-1 | 3017.01 | 4.7094 | 4 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2005-11-09 | 2007-05-03 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ALAMO | TIGHTENED CAP ON SAVE A NIPPLE
| 08-35001-1 | DCUST978 | 0.0024 | 0.75 | Single Service |  | Valves |  |  | Unknown |  | 2008-08-01 | 2008-09-19 | Other |  | Steel/Wrought Iron |  | MAXWELL | GREASED VALVE
| 08-33005-1 | DCUST93 |  | 0.75 | Single Service |  | Valves |  |  | Other |  | 2008-05-19 | 2008-05-29 | Other |  | Steel/Wrought Iron |  | DIXON
| 07-20001-1 | 200A15-2 | 0.23 | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2007-01-24 | 2007-03-28 | Deactivate #TP Main |  | Steel/Wrought Iron |  | RIO VISTA | RETIRED PIPELINE INPLACE SO#6102223
| 08-20004-1 | 200C1-2 | 0.38 | 8 | Gathering |  | Unknown |  |  | Internal Corrosion |  | 2008-04-30 | 2008-05-02 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | RIO VISTA | NO WELDING NEED AT LEAK LOCATION
| 08-20015-1 | DREG5379 | 0.119 | 6 | Distribution Main |  | Other |  |  | Other |  | 2008-01-30 | 2008-02-20 | Other |  | Other |  | BAKERSFIELD | ZONE VALVE
| 08-02025-1 | DREG4892 | 1.945 | 0.5 | Single Service |  | Body of Pipe |  |  | Plastic Crack Failure |  | 2008-02-28 | 2008-05-12 | Replace Partial Service |  | Aldyl A (Tan or Gray) |  | STOCKTON | AT SERV T TO 3069 CARPENTER RD INSTLD 18
| 08-20579-1 | DREG3752 | 0.0057 | 4 | Transmission |  | Tap Connection |  |  | Other |  | 2008-10-01 | 2008-10-02 | Other |  | Steel/Wrought Iron |  | BELMONT | TIGHTENED METER CAP
| 07-20135-1 | DREG4482 | 0.0647 | 4 | Single Service |  | Valves |  |  | Unknown |  | 2007-04-18 | 2007-04-18 | Other |  | Steel/Wrought Iron |  | SACRAMENTO | REPAIRED LEAK ON VALVE---REC MAPPING 5/
| 08-20146-1 | X9092 | 0.0019 | 4 | Distribution Main |  | Valves |  |  | Unknown |  | 2008-05-20 | 2008-07-29 | Other |  | Steel/Wrought Iron |  | OAKLAND | GREASED VALVE
| 08-20145-1 | 153 | 27.8301 | 20 | Transmission |  | Fitting |  |  | Unknown |  | 2008-05-20 | 2008-07-29 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | OAKLAND | TIGHTENED FITTING ON VALVE X-82
| 07-30004-1 | 137C | 4.36 | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2007-01-18 | 2007-01-18 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | EUREKA | INSTALLED 4" PLIDCO CLAMP
| 08-00226-1 | 1502-11 | 2.9573 | [8 empty] | 2008-12-30 | [5 empty] | MARYSVILLE
| 08-02857-1 |  | 6.0169 | [8 empty] | 2008-12-16 | [5 empty] | ROHNERT PARK
| 08-20442-1 |  | 1.78 | [8 empty] | 2008-12-26 | [5 empty] | SACRAMENTO
| 08-24117-1 |  | 18.0125 | [8 empty] | 2008-10-21 | [5 empty] | SAN LEANDRO
| 03-26125-1 | 3017-1 | 5.64 | 8 | Transmission |  | Body of Pipe |  |  | Other |  | 2003-08-06 | 2008-12-13 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | DANVILLE
| 08-06283-1 |  | 0.02 | 0.75 | Single Service |  | Other |  |  | Material Failure |  | 2008-12-20 | 2008-12-20 | Other |  | Steel/Wrought Iron |  | RIPON | REPLACED HPR SET.
| 08-30255-1 | 8807-02 | 0.336 | [8 empty] | 2008-09-22 | [5 empty] | SUNNYVALE
|  | 08-35160-1 | 0.0271 | [8 empty] | 2008-10-30 | [5 empty] | LIVINGSTON
| 08-50076-1 |  | 0.0013 | [8 empty] | 2008-11-21 | [5 empty] | SALINAS
| 08-00121-1 | 123 |  | 6 | Transmission |  | Valves |  |  | Equipment Malfunction |  | 2008-06-13 | 2008-12-12 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | LINCOLN | BODY BLOW DOWN VALVE; NOT ON 123
| 08-00686-1 | DFM | 1.58 | 2 | Transmission |  | Regulator |  |  | Construction Defect |  | 2008-12-18 | 2008-12-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ROSEVILLE | TIGHTENED PLUG ON FILTE PILOT RIGHT SD MON
| 08-00687-1 | 123 |  | 0.75 | Transmission |  | Valves |  |  | Construction Defect |  | 2008-12-18 | 2008-12-18 | Other |  | Steel/Wrought Iron |  | ROSEVILLE | OPEN VALVE TEE ALL THE WAY (NO READS)
| 08-00694-1 | NONE |  | 6 | Transmission |  | Fitting |  |  | Construction Defect |  | 2008-09-20 | 2008-12-17 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EL DORADO HILLS | SHUT IN SIDES OF STATION, BLEW DWN, RESLD
| 08-30566-1 | 8807-02 | 0.4295 | 10 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2008-04-30 | 2008-08-23 | Other |  | Steel/Wrought Iron |  | SUNNYVALE | INST'D STEEL CAP FROM A #2000 PSIG PINHO
| 08-13813-1 | DFM-SONO | 2.3916 | 6 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2008-03-18 | 2008-11-19 | Other |  | Steel/Wrought Iron |  | SONOMA
| 08-20012-1 | 126B | 10.57 | [8 empty] | 2008-11-10 | [5 empty] | EUREKA
| 08-20013-1 |  | 10.57 | [8 empty] | 2008-11-10 | [5 empty] | EUREKA
| 08-20015-1 | [10 empty] | 2008-11-14 | [5 empty] | EUREKA
| 08-25016-1 | 109 | 0.0217 | [8 empty] | 2008-09-19 | [5 empty] | ATHERTON
| 08-25017-1 | [10 empty] | 2008-09-19 | [5 empty] | MENLO PARK
| 08-25018-1 | [10 empty] | 2008-09-17 | [5 empty] | HILLSBOROUGH
| 08-25019-1 | [10 empty] | 2008-09-17 | [5 empty] | SAN MATEO
| 08-35003-1 |  | 0.0078 | [6 empty] | Unknown |  | 2008-11-05 | [5 empty] | DUNNIGAN
| 08-80777-1 |  | 9.3303 | [8 empty] | 2008-11-21 | [5 empty] | FRESNO
| 08-00557-1 | 0617-06 | 20.0348 | [8 empty] | 2008-02-19 | [5 empty] | EL DORADO HILLS
| 08-20279-1 | 0209-01 | 0.5259 | [8 empty] | 2008-05-03 | [5 empty] | SAN MATEO | DUPLICATE? ALREADY IN RECORD
| 08-20282-1 | 101 | 22.7851 | [8 empty] | 2008-05-04 | [5 empty] | BELMONT
| 08-20283-1 | 0214-01 | 0.7126 | [8 empty] | 2008-05-04 | [5 empty] | SAN MATEO | DUPLICATE? ALREADY IN RECORD
| 08-30033-1 | STUB6192 | [9 empty] | 2008-08-28 | [5 empty] | FERNBRIDGE | DUPLICATE? ALREADY IN RECORD
| 08-50060-1 | 103 | 22.2044 | [8 empty] | 2008-09-29 | [5 empty] | SALINAS
| 08-10020-1 | 118 | 11.34 | [8 empty] | 2008-05-15 | [5 empty] | MADERA
| 08-10026-1 | 118 | 11.34 | [8 empty] | 2008-04-14 | [5 empty] | MADERA | DUPLICATE? ALREADY IN RECORD
| 08-30571-1 | [10 empty] | 2008-04-30 | [5 empty] | SUNNYVALE | THIS WAS ORIGINALLY ENTERED IN GIS WITH A TYPO AS 08-30471-1 PLEASE CORRECT
| 09-30008-1 | [10 empty] | 2009-01-16 | [5 empty] | SUNNYVALE
| 08-20009-1 | 142 |  | 2 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2008-01-25 | 2009-01-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | BAKERSFIELD | DUP LEAK - REPAIRED ON LEAK #09-20007-1.
| 08-30014-1 | 306 |  | 20 | Transmission |  | Fitting |  |  | Unknown |  | 2008-08-26 | 2008-12-17 | Other |  | Other |  | AVENAL
| 08-30012-1 | 300B |  | 1 | Transmission |  | Fitting |  |  | Unknown |  | 2008-10-17 | 2008-12-17 | Soap and/or Tape - Other |  | Steel/Wrought Iron |  | AVENAL | CLEANED THREADS, TAPED, RE-TIGHTEN FITTI
| 08-30011-1 | 190 |  | 12 | Transmission |  | Fitting |  |  | Unknown |  | 2008-10-17 | 2008-12-08 | Tighten Cap or Bolt |  | Other |  | AVENAL | THERMO WELD ON METER RUN TO L-190 @ K.C.S.
| 08-20012-1 | 312 | 6.33 | 0.75 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2008-01-29 | 2009-01-16 | Other |  | Steel/Wrought Iron |  | BAKERSFIELD | VALVE 9
| 09-00101-1 |  |  | 0.75 | Single Service |  | Regulator |  |  |  |  | 2009-01-08 | 2009-01-08 | Other |  | Steel/Wrought Iron |  | YUBA CITY | REBUILT REGULATOR
| 09-20010-1 | 0614-13 |  | 6 | Transmission |  | Valves |  |  | Material Failure |  | 2009-01-05 | 2009-01-06 | Replace TP Main |  | Steel/Wrought Iron |  | SACRAMENTO | REPLACED LEAKING VALVE & 6" OF 6STL PIPE
| 09-50001-1 | MTY #1 | [9 empty] | 2009-01-02 | [5 empty] | SALINAS | ;
| 09-50005-1 | 301F | 0.03 | [8 empty] | 2009-01-13 | [5 empty] | SALINAS
| 09-50006-1 | 301F | 2.3 | [8 empty] | 2009-01-13 | [5 empty] | SALINAS
| 09-50009-1 | 301F | [9 empty] | 2009-01-13 | [5 empty] | SALINAS
| 09-50010-1 | 301F | 3.36 | [8 empty] | 2009-01-13 | [5 empty] | SALINAS
| 09-50008-1 | 301F | 1.63 | [8 empty] | 2009-01-13 | [5 empty] | SALINAS
| 09-50007-1 | 301F | 2.01 | [8 empty] | 2009-01-13 | [5 empty] | SALINAS
| 08-20012-1 | 312 | 6.33 | 0.75 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2008-01-29 | 2009-01-29 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | BAKERSFIELD | DUP LEAK-INFO FROM LEAK #09-20025-1
| 08-20442-1 |  |  |  | Distribution Main |  | Plastic Tee Cap |  |  | Incorrect Operation |  | 2008-12-26 | 2009-01-16 | Replace Dist Main < 100 ft |  | PE2406 (Yellow or Orange) |  | SACRAMENTO | AT TEE ON MAIN
| 08-35160-1 | VINEWOOD | 0.01 | 4 | Transmission |  | Valves |  |  | Other |  | 2008-10-30 | 2009-01-16 | Other |  | Steel/Wrought Iron |  | LIVINGSTON | VALVE 9
| 98-30232-1 |  | 0.6117 | 4 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 1998-10-30 |  |  |  | Steel/Wrought Iron |  | WESTLEY
| 08-80103-1 |  | 2.4647 | [8 empty] | 2008-10-22 | [5 empty] | KERMAN
| 08-80097-1 |  | 3.2643 | [8 empty] | 2008-10-22 | [5 empty] | KERMAN
| 08-80093-1 |  | 3.3265 | [8 empty] | 2008-10-22 | [5 empty] | KERMAN
| 08-80092-1 |  | 3.3578 | [8 empty] | 2008-10-22 | [5 empty] | KERMAN
| 08-80091-1 | [10 empty] | 2008-10-22 | [5 empty] | KERMAN
| 08-80081-1 | [10 empty] | 2008-10-20 | [5 empty] | HURON
| 08-70059-1 | [10 empty] | 2008-10-28 | [5 empty] | RED BLUFF
| 08-50067-1 | 301G | 22.6 | [8 empty] | 2008-10-10 | [5 empty] | MOSS LANDING
| 08-30040-1 |  | 2.5726 | [8 empty] | 2008-09-29 | [5 empty] | EUREKA
| 08-20638-1 | [10 empty] | 2008-09-29 | [5 empty] | ATHERTON
| 08-20633-1 |  | 0 | [8 empty] | 2008-09-28 | [5 empty] | REDWOOD CITY
| 08-20579-1 | 109 | 0.0057 | 4 | Transmission |  | Tap Connection |  |  | Other |  | 2008-10-01 |  |  |  | Steel/Wrought Iron |  | BELMONT
| 08-02569-1 |  | 0.0007 | [8 empty] | 2008-09-30 | [5 empty] | SONOMA
| 08-00695-1 |  | 0.3779
| 08-00694-1 |  | 5.94 | [8 empty] | 2008-09-20 | [5 empty] | EL DORADO HILLS
| 08-00687-1 |  | 0.0021 | [8 empty] | 2008-09-21 | [5 empty] | ROSEVILLE
| 08-00686-1 |  | 1.58 | [8 empty] | 2008-09-21 | [5 empty] | ROSEVILLE
| 08-00693-1 |  | 2.05 | [8 empty] | 2008-09-21 | [5 empty] | LINCOLN
| 07-20038-1 | DFM1 | 0.01 | [8 empty] | 2007-10-08 | [5 empty] | WATSONVILLE
| 07-20038-1 | [10 empty] | 2007-10-08 | [5 empty] | WATSONVILLE | ;
| 07-20038-1 | [10 empty] | 2007-10-08 | [5 empty] | WATSONVILLE
| 07-20038-1 | DFM1 | [9 empty] | 2007-10-08 | [5 empty] | WATSONVILLE
| 07-20038-1 | DFM1 | [9 empty] | 2007-10-08 | [5 empty] | WATSONVILLE
| 08-20068-1 |  | 0.7037 | [8 empty] | 2008-01-26 | [5 empty] | SACRAMENTO | MIKE RAAB CONFIRMED IT WAS NOT HCA AREA IN VICINITY (AND WAS REPAIRED) 2-10-08
| 08-30002-1 | 132A | 1.4592 | [8 empty] | 2008-01-16 | [5 empty] | MT VIEW
| 08-20008-1 | 142 | 12.31 | [8 empty] | 2008-01-25 | [5 empty] | BAKERSFIELD
| 08-20009-1 | 142 | 12.3121 | [8 empty] | 2008-01-25 | [5 empty] | BAKERSFIELD
| 08-20007-1 |  | 300.5117 | [8 empty] | 2008-01-23 | [5 empty] | SHAFTER
| 08-20006-1 |  | 0.1518 | [8 empty] | 2008-01-16 | [5 empty] | EMERYVILLE
| 08-20006-1 | [10 empty] | 2008-01-23 | [5 empty] | WASCO
| 08-20012-1 |  | 6.3375 | [8 empty] | 2008-01-29 | [5 empty] | BAKERSFIELD
| 08-20010-1 |  | 7.3696 | [8 empty] | 2008-01-29 | [5 empty] | BAKERSFIELD
| 08-20005-1 |  | 0.1044 | [8 empty] | 2008-01-16 | [5 empty] | EMERYVILLE
| 08-02000-1 | 021E | 65.58 | [8 empty] | 2008-01-22 | [5 empty] | HEALDSBURG
| 08-02001-1 | 021E | 66 | [8 empty] | 2008-01-22 | [5 empty] | HEALDSBURG
| 08-02002-1 | 021E | 65.58 | [8 empty] | 2008-01-22 | [5 empty] | HEALDSBURG
| 08-02003-1 | 021E | 64.36 | [8 empty] | 2008-01-23 | [5 empty] | HEALDSBURG
| 08-20001-1 | 6606-01 | 0.07? | 0.75 | Transmission |  | Fitting |  |  | Unknown |  | 2008-01-04 | 2008-01-04 | Other |  | Steel/Wrought Iron |  | WASCO | REBUILT PRIMARY REGULATOR AND TIGHTENED
| 07-20003-1 | 6606-01 | 0.021 | 0.75 | Transmission |  | Fitting |  |  | Unknown |  | 2007-01-12 | 2008-01-04 | Other |  | Steel/Wrought Iron |  | WASCO | REBUILT PRIMARY REGULATOR AND TIGHTENED
| 08-02546-1 |  | 0 | [8 empty] | 2008-08-27 | [5 empty] | SEBASTOPOL
| 08-02547-1 |  | 0 | [8 empty] | 2008-08-27 | [5 empty] | SEBASTOPOL
| 08-02585-1 | [10 empty] | 2008-09-18 | [5 empty] | PETALUMA
| 08-21148-1 | DFM | 0.7419 | 8 | Transmission |  | Other |  |  | Unknown |  | 2008-06-05 | 2008-09-02 | Other |  | Steel/Wrought Iron |  | FOLSOM | TIGHTENED THREADED PIPE
| 08-21169-1 | 119 | 0.0192 | 0.5 | Transmission |  | Other |  |  | Weld Failure |  | 2008-06-18 | 2008-09-15 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | SACRAMENTO | SOAP TEST- REPLACED 1/2" VALVE WITH NEW VALVE
| 08-21171-1 | 119 | 0.84 | 0.5 | Transmission |  | Valves |  |  | Unknown |  | 2008-06-18 | 2008-09-15 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | SACRAMENTO | REPLACED VALVE; REPLACED VALVE AND SOAP TESTED
| 08-21186-1 | 108 | 68.0077 | 24 | Transmission |  | Valves |  |  | Unknown |  | 2008-06-18 | 2008-09-16 | Other |  | Steel/Wrought Iron |  | SACRAMENTO | GREASED VALVE
| 08-30033-1 |  | 0 | [8 empty] | 2008-08-28 | [5 empty] | FERNBRIDGE
| 08-30038-1 | 137B | 7.1995 | [8 empty] | 2008-09-17 | [5 empty] | ARCATA
| 08-30039-1 | 137D | 0.1428 | [8 empty] | 2008-09-17 | [5 empty] | ARCATA
| 08-50060-1 |  | 22.2044 | [8 empty] | 2008-09-29 | [5 empty] | SALINAS
| 08-60041-1 |  | 0.0014 | [8 empty] | 2008-09-11 | [5 empty] | OROVILLE
| 08-60042-1 |  | 0.0029 | [8 empty] | 2008-09-11 | [5 empty] | OROVILLE
| 08-55030-1 | 118 | 24.4 | 8 | Transmission |  | Fitting |  |  |  |  | 2008-08-04 | 2008-08-04 | Welded Sav-A-Valve - Weld |  | Steel/Wrought Iron |  | MADERA | INSTLD 2" SAVE-A-VALVE OVER DAMAGED 3/4" SVC TEE
| 08-35001-1 | [10 empty] | 2008-08-01 | [5 empty] | MAXWELL
| 08-06166-1 |  | 0.0003 | 0.75 | Single Service |  | Regulator |  |  | Equipment Malfunction |  | 2008-08-11 |  |  |  | Steel/Wrought Iron |  | RIPON
| 08-55030-1 | 118 | 24.4 | 8 | Transmission |  | Fitting |  |  |  |  | 2008-08-04 | 2008-08-04 | Welded Sav-A-Valve - Weld |  | Steel/Wrought Iron |  | MADERA | INSTLD 2" SAVE-A-VALVE OVER DAMAGED 3/4" SVC TEE
| 08-35001-1 |  | 0.0024 | [8 empty] | 2008-08-01 | [5 empty] | MAXWELL
| 08-10103-1 |  | 1.6571 | [8 empty] | 2008-08-13 | 2008-08-13 | Other |  |  |  | SANTA CRUZ | 370" E/O ALICE ST, REPLACED HPR O-RINGS
| 08-02545-1 |  | 10.22 | [8 empty] | 2008-08-27 | [5 empty] | SEBASTOPOL
|  | 136 | 12.49 | [15 empty] | CRACKED WRAP WAS PULLED OFF WHEN DIRT WAS REMOVED FROM PIPE. WRAP WAS SCRAPED AWAY, PIPE WAS WIRE BRUSHED, PRIMERED, AND RE-WRAPPED
| 08-02198-1 |  | 0.9433 | [8 empty] | 2008-07-01 | [5 empty] | TRACY
| 08-10090-1 | 1816-01 | 14.6466 | [8 empty] | 2008-06-30 | [5 empty] | CAPITOLA
| 08-20008-1 | 126A | 0 | [8 empty] | 2008-07-15 | [5 empty] | EUREKA
| 08-20010-1 |  | 0 | [8 empty] | 2008-07-17 | [5 empty] | EUREKA
| 08-20278-1 | 109 | 0.4329 | 6 | Transmission |  | Body of Pipe |  |  | Construction Defect |  | 2008-05-03 | 2008-07-03 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | SAN MATEO | APPLIED CLAMP 405' S/O SCANNELL DR.; APPLIED 6" CLAMP ON STREET TRANSMISSION PIPE
| 08-21116-1 | 0 | 0 | 12 | Transmission |  | Other |  |  | Unknown |  | 2008-06-04 | 2008-06-25 | Other |  | Steel/Wrought Iron |  | FOLSOM
| 08-35096-1 |  | 0 | [8 empty] | 2008-04-08 | [5 empty] | WINTERS
| 08-40012-1 | 137C | 3.12 | 4 | Transmission |  | Body of Pipe |  |  |  |  | 2008-07-21 | 2008-07-22 | Replace TP Main |  | Steel/Wrought Iron |  | EUREKA | REPLACED 4' OF 4" TP MAIN
| 08-80088-1 |  | 0.0532 | [8 empty] | 2008-07-10 | [5 empty] | JOHNSON PARK
| 08-80076-1 |  | 0.0021 | [8 empty] | 2008-06-23 | [5 empty] | GLENBURN
| 08-70029-1 | [10 empty] | 2008-06-26 | [5 empty] | RED BLUFF
| 08-40001-1 | 400 | 82.33 | [8 empty] | 2008-05-29 | [5 empty] | BURNEY
| 08-30087-1 | 101 | 33.8877 | 101 | [7 empty] | 2008-06-18 | [5 empty] | SAN BRUNO
| 08-20304-1 |  | 0 | [8 empty] | 2008-05-19 | [5 empty] | HALF MOON BAY
| 08-20303-1 |  | 0 | [8 empty] | 2008-05-14 | [5 empty] | HALF MOON BAY
| 08-20301-1 | [10 empty] | 2008-05-14 | [5 empty] | HALF MOON BAY
| 08-20300-1 |  | 0.05 | [8 empty] | 2008-05-14 | [5 empty] | HALF MOON BAY
| 08-20299-1 |  | 0.01 | [8 empty] | 2008-05-14 | [5 empty] | HALF MOON BAY
| 08-20298-1 |  | 0 | [8 empty] | 2008-05-14 | [5 empty] | HALF MOON BAY
| 08-20302-1 |  | 0.0095 | [8 empty] | 2008-05-14 | [5 empty] | HALF MOON BAY
| 08-10045-1 | 124 | 0.605 | [8 empty] | 2008-06-05 | [5 empty] | WHEATLAND
| 08-00121-1 | 123 | 11.5335 | [8 empty] | 2008-06-13 | [5 empty] | LINCOLN | ;
| 08-20506-1 | 311 | 0.377 | [8 empty] | 2008-03-04 | [5 empty] | KRAMER
| 08-20506-1 | 300A/B | [9 empty] | 2008-03-04 | [5 empty] | KRAMER
| 07-60001-1 | 1125 | 0.0002 | 2 | Transmission |  | Valves |  |  | Other |  | 2007-11-06 | 2008-03-22 | Other |  | Steel/Wrought Iron |  | SEBASTOPOL | GREASED VALVE
| 08-20227-1 |  | 2.3538 | 3 | Distribution Main |  | Tap Connection |  |  | Construction Defect |  | 2008-06-03 | 2008-06-03 | Welded Sav-A-Valve - Weld |  | Steel/Wrought Iron |  | SACRAMENTO | INSTALLED TWO 3" M2 FITTINGS WELD 1"SAV
|  | 301G | 0 | [12 empty] | Steel/Wrought Iron |  |  | RT = 301G
|  | 301G | 10.85 | [12 empty] | Steel/Wrought Iron |  |  | RT: 301G; AT ROAD CROSSING OF OLD SAN JUAN HIGHWAY
|  | 301G | 10.85 | 30 | [11 empty] | Steel/Wrought Iron
|  | 301G | 11.05 TO 11.25 | 30 | [13 empty] | SAN JUAN BAUTISTA | L-301G, SO# 7029905-01; Line 301G between MP 11.05 and MP 11.25.
|  | 301G | 15.65 | [12 empty] | Steel/Wrought Iron
|  | 301G | 20.4 | [12 empty] | Steel/Wrought Iron |  |  | RT=301-G
|  | 301-G | 24.67 | 24 | Transmission | [12 empty] | MOSS LANDING | RT: 301-G, MP: 24.67
|  | 301-G | 24 | [12 empty] | Steel/Wrought Iron |  |  | EACH LOCATION EXC. 5' TOTAL 20' GPD CONDITION. MDN 5. COMPLETED 2-9-01.
|  | 301G | 4.32 | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT=301G; WRIGHT RD NEAR BUENA VISTA
|  | 301-G | 24.67 | 24 | Transmission | [12 empty] | MOSS LANDING
| 01-50090-1 | 301 | 22 | 12 | Transmission |  | Valves |  |  | Other |  | 2001-07-10 | 2001-07-24 | Other |  | Steel/Wrought Iron |  | MOSS LANDING | IN MOSS LANDING POWER, PRIMARY REG STATIO, OD 083811; VALVE STATION 22 AT MOSS LANDING POWER PLANT; LEAK WAS STOPPED BY ADDING PACKING MATER
|  | 301-G | 24.67 | 24 | Transmission | [12 empty] | MOSS LANDING | GIS
|  | 301-6 | 24.67 | 24 | Transmission | [12 empty] | MOSS LANDING | GIS
| 01-50090-1 | 301 | 22 | 12 | Transmission |  | Valves |  |  | Other |  | 2001-07-10 | 2001-07-24 | Other |  | Steel/Wrought Iron |  | MOSS LANDING | GIS IN MOSS LANDING POWER PLANT PRIMARY REG STATIO, OD 083811; VALVE STATION 22 AT MOSS LANDING POWER PLANT; LEAK WAS STOPPED BY ADDING PACKING MATER
|  | 301F | 7.30 TO 7.34
| 09-70034-1 | 301 | 5.8154 | [8 empty] | 2009-02-10 | [5 empty] | MARINA | 301F T LT, GIS & IGIS
| 10-81005-1 | 301F | 5.84 | 0.75 | Transmission |  | Mechanical Joint |  |  | Other |  | 2010-10-03 | 2010-10-14 | Other |  | Steel/Wrought Iron |  | MONTEREY | GIS; SS FITTNG ON RIGHT RUN REG PILOT.
| 10-81008-1 | 301F | 6.21 | [8 empty] | 2010-10-03 | [5 empty] | MONTEREY | GIS
| 10-81006-1 | 301F | 7.32 | [8 empty] | 2010-10-03 | [5 empty] | MONTEREY
|  |  | 0.37 | 4 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 30679509; RT: STUB 10598; BLIND FLANGED V-290 OFF L-302 AND RETIRED APROX. 1953' OF 4" STL FROM V-290 TO BILLIE JEAN 18-1 GAS WELL RISER.
|  | 302-040 | 0.15 | 12 | Transmission | [13 empty] | JOB# 30679509, RT 302-040; SEE STPR
|  | 302-209 | 0 | 2 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 3064697, L-302-204, GG LT; RETIRED 2" ST. MAIN FROM V-478 TO SNR #1 RISER
| 09-30203-1 |  | 0.004 | 20 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2009-04-20 | 2009-05-29 | Replace TP Main |  | Steel/Wrought Iron |  | GRIMES | DISTRICT: MERIDIAN, 30709311-09, DRIP 10511, 2GLT, SRC RT: 302-040, SRC MP: 0.5661; SAME; BLOWING GAS; REPLACCED 20" DRIP PIPE; REPLACED ENTIRE POUNDSTONE DRIP STATION ON PM# 30709311. SEE AS-BUILT FOR DETAILS.
|  | 302-245 |  | 3 | Transmission | GATHERING | [9 empty] | Steel/Wrought Iron |  |  | PM# 3061462, RT 302-295
|  | 302-106 | 0.1493 |  | Transmission | [10 empty] | Steel/Wrought Iron |  | GRIMES | DISTRICT: MERIDIAN, SO# 7065166-07; L-302-106
|  | 3.02 | 4.45 | [15 empty] | SO# 7042667-02; RT 302E-2
|  | 302-145 | 0.03 | [15 empty] | L-302-145, BRYANT 1-18, JOB# 7043045
|  | 302E | 11.6 | 20 | [11 empty] | Steel-Other |  |  | L-302E; INSTALLED 2' TAP
|  | 302E | 12.22 | 6 | [11 empty] | Other | GRB SMLS |  | L-302E, SO# 7036845-00, INST. BACK PRESSURE REG.
|  | 30.2 | 1.19 | 6 | [11 empty] | Steel-Other |  |  | 7030786/GREENLEAF DFM/BORE, MERIDIAN DISTRICT, 302E-1, SEG 113
| 00-30204-1 |  |  | 6 | [13 empty] | GRIMES | BUBBLES NEXT TO CORN FIELD, 6" L-302
| 00-17401-1 | 174 |  | 10 | Gathering | [6 empty] | 2000-06-30 | [5 empty] | ARBUCKLE | SUSPECT INTERNAL CORROSION IN ORCHARD AREA.
| 99-302-5 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-06-07 | 1999-07-20 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | GRIMES | UPSTREAM OF ANDREOTTI #11 MASTER METER BETWEEN V-245 & V-418, 419; REPLACED LEAK WITH 40" __PAC RESTED; SUCTION LINE ONLY COULD GET 80# FROM WELL
| 99-302-5 |  |  | 4 |  |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-06-07 |  |  |  | Steel/Wrought Iron |  | GRIMES | UPSTREAM OF ANDREOTTI #11 MASTER METER BETWEEN V-245 & V-418, 419; BUBBLES IN FLOODED RICE FIELD
| 99-302-5 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-06-07 | 1999-07-20 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | GRIMES | UPSTREAM OF ANDREOTTI #11 MASTER METER BETWEEN V-245 & V-418, 419; BUBBLES IN FLOODED RICCE FIELD. ISOLATED AND BLOWN DOWN.; REPLACED LEAK WITH 40" _ PAC RESTED
|  | 302 |  | 4 | [8 empty] | 2000-05-10 | [5 empty] | SO# 7029948-00; TIE... 4"... NEW VALVE V496 TO CONVERT 6" GATHERING SYSTEM...
|  | 302 |  | 6 | [8 empty] | 2000-05-10 |  |  | Steel-Other |  |  | SO# 7029948-00; TIE IN NEW 6" L302 GATHERING SYSTEM TO EXISTING 6" L302 #7029748
|  | 302 |  | 4 | [11 empty] | Steel-Other |  |  | M.O -GMER (MERIDIAN), RT302-015, MP 0.00, TAP OFF 302E, MP 10.19, JOB 6037306
|  | 302 | 0.24 | [15 empty] | ROUTE 302.092, SO# 6066203-01; DRY SLAUGHRO S/O S____ RD. TR__ STONEWALL #2
|  |  |  | 4.5 | [8 empty] | 2000-08-29 |  |  | Steel/Wrought Iron |  |  | L-302-130, SO# 6037323-00, INSTALL 4X3 TEE WITH TAP VALVE TO CONNECT NW GRIMES #1 GASWELL
|  | 302E | 12.22 | [12 empty] | Steel/Wrought Iron |  |  | 6" TIEIN; SO# 7040050-01, ABAND 24" DRIP, CALPINE METER STATION
|  | 302E | 12..22 | [12 empty] | Steel/Wrought Iron |  |  | 16" PIPE TIEIN; SO# 7040050-01, ABAN'D 24" DRIP, CALPINE METER STATION
|  | 302E | 12.22 | 16 | [11 empty] | Steel-Other |  |  | SO# 7029946; SACRAMENTO DRIP.
|  | 302-067 | [13 empty] | Steel/Wrought Iron |  |  | SO# 6070743-02, ROUTE: 302-067, MERIDIAN DISTRICT; RETIRE SOUTH SYCAMORE 14-IC
|  | 302-066 | [13 empty] | Steel/Wrought Iron |  |  | SO# 6070743-2, ROUTE 302-066, MERIDIAN DISTRICT; RETIRE SOUTH SYCAMORE 3
|  | 302-064 | [13 empty] | Steel/Wrought Iron |  |  | SO# 6070743-2, ROUTE 302-064, MERIDIAN DISTRICT
|  | 302-063 | [13 empty] | Steel/Wrought Iron |  |  | SO# 6070743-02, ROUTE 302-063, MERIDIAN DISTRICT; RETIRE SOUTH SYCAMORE 11T.
|  | 302-046 | [13 empty] | Steel/Wrought Iron |  |  | SO# 6070743, ROUTE 302-046; RETIRE SOUTH SYCAMORE 16.
|  | 302-062 | [13 empty] | Steel/Wrought Iron |  |  | SO# 6070743-02, ROUTE 302-062; RETIRE POWDSTONE 18-2
|  | 302-068 | [13 empty] | Steel/Wrought Iron |  |  | SO# 6070743-02, ROUTE 302-068; RETIRE SOUTH SYCAMORE 9-2, THIS PIPE IS NOT RETIRED SHOULD IT BE POSTED?
|  | 302-132 | [13 empty] | Steel-Other |  |  | ROUTE 302-132, SO# 60 69523-01; CUT OFF LOCATION FOR SANBORN 4-10 WELL
|  | 302-273 |  | 4 | [11 empty] | Steel-Other |  |  | L-302-273, SO# 6069524-01; V-272 PROGRESS RD..
|  | 302-012-1 | [16 empty] | L-302-012-1, SO# 7040945-02; RETIRE ARBUCKLE RD 39 WELL
|  | 302-008 | [16 empty] | L-302-008, SO# 7040945-02; RETIRE ARBUCKLE RD 25 WELL
|  | 302-029 | [16 empty] | L-302-029, SO# 7040945-02
|  | 302-041 | 0 | [12 empty] | Steel-Other |  |  | JOB 6068564, L-302-041, M.P. 0.00 OR 302-40 MP 0.46; C/O DL MOORE METER
|  | 302 | 11.53 | [12 empty] | Steel-Other |  |  | L-302E, JOB 6073363; TAD AT FS607+60 L-302
|  | 302-040 | 0.01 | [12 empty] | Steel/Wrought Iron |  |  | L-302-040, JOB 6073363
| 02-30201-1 | 302E | 3.31 | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-01-10 | [5 empty] | S/O SUTTER | 302E-2, SO# 8051016-02; BUBBLES IN FLOODED RICE FIELD; NO PITTING OR COROSION ON 8" HOLE WAS IN 6" STUB SEGMENT; 3° SEGMENT 109" TOTAL REPLACED
|  | 302-009 | 0 | [15 empty] | RT=302-009, SO# 6088523-02; RETIRE ARBUCKLE ROAD 20 WELL
| 98-30201-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  |  | 1998-06-10 | Replace Pipe |  | Steel-Other |  |  | PIPE UNREPAIRABLE - WILL RETIRE. CUT OUT LEAK. REPLACED WITH 30" PRETESTED PIPE. DUE TO HEAVY TROUGHING LINE WAS ABANDON
| 98-30202-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-01-05 | 1998-06-10 | Other |  | Steel-Other |  | GRIMES | PIPE UNREPAIRABLE - WILL RETIRE. SEVERE TROUGHING. NOTHING DONE AT THIS LOCATION. DUE TO LINE ABANDON
| 98-30203-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-01-05 | 1998-06-10 | Other |  | Steel-Other |  | GRIMES | PIPE UNREPAIRABLE - WILL RETIRE. SEVERE TROUGHING. LEAK WAS DETECTED 50' S/O LINE G-302 GOING TO CARLSON 7 GAS WELL. DID NOT REPAIR DUE TO ABANDON
| 98-30204-1 |  |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-02-03 | 1998-03-04 | Replace Pipe |  | Steel-Other |  | GRIMES | REPAIR LEAK E/O V173 WITH 22" .188 4" PRETESTED PIPE SO# 70107086
| 98-30205-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-02-23 | 1998-04-16 | Replace Pipe |  | Steel-Other |  | S/E MERIDIAN | REPAIR LEAK W/30" PRETESTED .188 X 42 6" PIPE. ISOLATED AND BLOWN DOWN.
| 98-30207-1 |  |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-03-19 | 1998-03-19 | Replace Pipe |  | Steel-Other |  | MERIDIAN | REPLACED WITH 32" PIECE OF .219 TESTED PIPE.
| 98-30206-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-02-24 | 1998-06-03 | Replace Pipe |  |  |  | GRIMES | REPLACED TWO 30" PIECES ON THE NORTH END OF PIPE ISOLATED. FOUND 150 FEET OF UNREPAIRABLE PIEP ON SOUTH END. THIS SECTION OF PIPE WILL BE RETIRED. ISOLATED AND BLOWN DOWN.
| 98-30210-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-03-19 | 1998-04-16 | Replace Pipe |  | Steel-Other | API SLX | S/E OF MERIDIAN | REPAIR LEAK WITH 42" .188 UT PRETESTED PIPE
| 98-30208-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-03-19 | 1998-03-20 | Replace Pipe |  | Steel-Other |  | MERIDIAN | REPLACED WITH 24" PIECE OF .219 TESTED PIPE
| 98-30208-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-03-19 | 1998-04-16 | Replace Pipe |  | Steel/Wrought Iron |  | S/E OF MERIDIAN | REPAIR LEAK WITH 42" .188 UT PRETESTED PIPE
| 98-30209-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-03-19 | 1998-04-16 | Replace Pipe |  | Steel-Other |  | S/E OF MERIDIAN | REPAIR LEAK WITH 42" .188 UT PRETESTED PIPE
| 98-30209-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-03-19 | 1998-03-20 | Replace Pipe |  | Steel-Other |  | MERIDIAN | REPLACED WITH 50" PIECE OF .219
| 98-30211-1 | 302 |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-05-05 |  | Replace Pipe |  | Steel/Wrought Iron |  | GRIMES | NOT REPAIRED YET! BLOWDOWN - AWAITING TO SEE IF PRODUCERS WILL PAY FOR REPAIR.
| 98-30212-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-06-25 | 1998-09-23 | Replace Pipe |  | Steel-Other |  | MERIDIAN | REPLACED 5'3" OF PIPE WITH PRETESTED PIPE GM 10277620
| 98-30213-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-06-25 | 1998-09-23 | Replace Pipe |  | Steel-Other |  | MERIDIAN | REPLACED 28" OF PIPE WITH PRETESTED PIPE GM 10277620; 6/10 MILE
| 98-30214-1 | 302 |  | 4 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-09-15 | 1998-12-14 | Replace Pipe |  | Steel-Other | API3L | GRIMES | REPAIR LEAK ON 4" MAIN - REPLACE 2" SECTION WITH TESTED .237 4"
| 98-30214-1 | 302 |  | 8 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-06-25 | 1998-11-17 | Replace Pipe |  | Steel-Other |  | MERIDIAN | REPAIR 8" LEAK WITH 30" PIECE OF TESTED PIPE. WILL MONITOR AND SCHEDULE REPAIRS.
| 98-30215-1 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-11-03 | 1998-11-10 | Replace Pipe |  | Steel/Wrought Iron |  | SUTTER | REPAIR LEAK WITH 3' 6" PIPE
| 98-30216-1 | 302 |  | 3 | Gathering |  | Body of Pipe |  |  | Internal Corrosion | [5 empty] | Steel/Wrought Iron |  | GRIMES | NOT REPAIRED YET!
| 98-30217-0 |  |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-10-05 | 1999-03-23 | ABANDON | WELDED SLEEVE/CAN | Steel/Wrought Iron |  | GRIMES | APPROX. 50 FT W/O DRY SLOUGH ROAD; PIPE TO BE REPLACED DUE TO INTERNAL; REPLACED 540 FT. OF 12" L-302 WITH 4" PIPE S.O. #6020523. NEW PIPE SHEET RETURNED TO SERVICE ON 4/15/99. C. BUSH (CALIF. PRODUCERS PAID FOR REPLACEMENT); REPLACED LEAKY PIPE FOR PIGGING ONLY!
| 99-30201-0 | 302 |  | 12 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-12-08 | 2000-04-20 | Other | CUT & CAP | Steel/Wrought Iron |  | GRIMES | SITE IN FIELD; CUT & CAPPED 20"X12" TEE WITH 12 CAP & SAV-A-VALVE; RETIRED SECTION OF PIPE S.O.# 8030916; X52; ENERTED 12" WITH NITROGREN TO BE RETIRES
| 99-30200-3 | 302 |  | 8 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2009-05-11 | 1999-08-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | S/O MERIDIAN | SAME AS ABOVE; REPAIRED WITH 25" .188WT X 42, PRETESTED PIPE ON GM# 496497-9
| 99-30200-4 | 302 |  | 8 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-05-11 | 1999-08-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | S/O MERIDIAN | SAME AS ABOVE; REPAIRED WITH 32" PRETESTED PIPE .188X42 GM# 496497-9
| 99-30200-5 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-06-07 | 1999-07-20 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | GRIMES | UPSTREAM OF ANDREOTTI #11 MASTER METER BETWEEN V-245 & V-418, 419; BUBBLES IN FLOODED RICE FIELD. ISOLATED AND BLOWN DOWN.; REPLACED LEAK WITH 40" & PRETESTED; SUCTION LINE ONLY COULD GET 80#, RM WELL
| 99-305-5 | 302 |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-06-07 | 1999-07-20 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | GRIMES | UPSTREAM OF ANDREOTTI #11 MASTER METER BETWEEN V-245 & V-418, 419; BUBBLES IN FLOODED RICE FIELD. ISOLATED AND BLOWN DOWN; REPLACED LEAK WITH 40"& PRETESTED; SUCTION LINE ONLY COULD GET 80# FROM WELL.
| 99-30200-6 |  |  | 4 | Gathering |  | Fitting |  |  | Other | SAV-A-VALVE | 1999-07-26 | 1999-10-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | GRIMES | 3 FEET EASTS OF V-337; 3 FT. EAST OF V-337 ON GRIMES- ARBUCKLE RD.; 2" SAV-A-VALVE LEAKING. REDOPED AND TIGHTEN; TIGHTENED SAV-A-VALVE STEM & CAP.
| 99-30200-7 | 302 |  | 8 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-08-19 | 1999-08-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | S/E OF MERIDIAN | SAME AS ABOVE; REPAIRED WITH 23 2/8 .188 WT X42 PRETESTED PIPE ON GM#4964929
| 99-30200-7 | 302 |  | 8 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-08-19 | 1999-08-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | S/E OF MERIDIAN | SAME AS ABOVE; FOUND WHILE MAKING ONE FINAL CHECK BEFORE SHUTDOWN ON 8/22/99; REPAIRED WITH 23 7/8. 188WTX42 PRETESTED PIPE ON GM#476497-9
| 99-30200-7 | 302 |  | 8 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-08-19 | 1999-08-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | S/E OF MERIDIAN | SAME AS ABOVE, FOUND WHILE MAKING ONE FINAL CHECK BEFORE SHUT DOWN ON 8/22/99.; REPAIRED WITH 23 7/8 .188WT X42 PRETESTED PIPE ON GM# 476497-9
| 99-30200-8 |  |  | 6 | Gathering | [6 empty] | 1999-11-05 | [5 empty] | SE/O MERIDIAN | INSIDE EAST LEVEE, INSIDE EAST SLOUGH NEXT TO EAST BANK.; SUTTER BYPASS -EAST SLOUGH 20 LINEAR FEET OF BUBBLES UNDER WATER; AWAITING REPLACEMENT
| 99-30200-9 | L302 |  | 20 | Transmission | GATHERING | Body of Pipe |  |  | Internal Corrosion |  | 1999-11-13 |  | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | COLLEGE CITY | SO# 8029776; SITE IN FIELD; REPAIRED WITH 94 7/8"... ; HYF STEINGER/ NOT PASS - LOW... CAP
| 99-30202-0 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-04-26 | 1999-04-30 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | GRIMES | SAME AS ABOVE; BUBBLES IN FLOODED RICE FIELD; REPAIRED WITH 6' OF 20" .375 WT; S.O.# 8023616
| 99-30202-0 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-04-26 | 1999-04-30 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | GRIMES | SAME AS ABOVE; BUBBLES IN FLOODED RICE FIELD; REPAIRED WITH 6' OF 20" .375 WT, STPR# A-1324
| 99-30203-3 |  |  | 8 | [7 empty] | 1999-05-11 | [5 empty] | S/O MERIDIAN | SAME AS ABOVE
| 99-30203-3 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-05-11 | 1999-08-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | S/O MERIDIAN | SAME AS ABOVE; REPAIRED WITH 25" .188WT X42 PRETESTED PIPE ON GM# 496497-9
| 99-30200-3 | 302 |  | 8 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-05-11 | 1999-08-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | S/O MERIDIAN | SAME AS ABOVE; REPAIRED WITH 25" .188 WT X42 PRETESTED PIPE ON GM#496497-9
| 99-30204-4 |  |  | 8 | [7 empty] | 1999-05-11 | [5 empty] | S/O MERIDIAN | SAME AS ABOVE
| 99-30204-4 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-05-11 | 1999-08-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | S/O MERIDIAN | SAME AS ABOVE; REPAIRED WITH 32" PRETESTED PIPE .188X42 GM#496497-9
| 99-30200-4 | 302 |  | 8 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-05-11 | 1999-08-22 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | S/O MERIDIAN | SAME AS ABOVE; REPAIRED WITH 32" PRETESTED PIPE .188 X42 GM# 496497-9
| 98-30217-0 | 302 | 12 |  | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1998-10-05 | 1999-03-23 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | GRIMES | APPROX. 50FT. W/O DRY SLOUGH ROAD; OUT IN DIRT FIELD (BETWEEN #1793 & 1449 ADDRESS); PIPE TO BE REPLACED DUE TO INTERNAL CORROSION (12' WILL BE REPLACED W/NEW 4"); REPLACED 540 FT. OF 12" L-302 WITH 4" PIPE. S.O. #6020523. NEW PIPE SECTION RETURNED TO SERVICE ON 4/15/99, C BISH (CALIF. PRODUCERS PAID FOR REPLACEMENT)
| 02-30205-1 | 302 | 0.49 | 4.5 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2002-05-08 | 2002-05-30 | Other | CAPPED & RETIRED LEAK STATION | Steel/Wrought Iron |  | S/E MERIDIAN | L-302E, RT= 302-162, SO# 7043786-02; VALVE TO MOBILWOOD #4-1; BUBBLES IN FLOODED FIELD. ISOLATED AND BLEW DOWN; RETIRED LEAK PIPING TO MOBIL-WOOD #4-1; CAPPED & RETIRED LEAK SECTION; RAPAI 5-30-02
|  | 302-139 | 0 | [12 empty] | Steel/Wrought Iron |  |  | SO# 7042045-02, RT= 302-139
|  | 302-053 | 0.18 | [15 empty] | SO# 7040929, ROUTE 302-053; C/O 3" ... 45 1000...
|  | 302-144 | 6.9 | [12 empty] | Steel/Wrought Iron |  |  | JOB# 7046545; RT 302-144; CAP 6" V-206
|  | 302-159 | 0.79 | [15 empty] | ROUTE= 302-159, SO# 7041407-03
|  | 302 | 0.0004 | [12 empty] | Steel/Wrought Iron |  |  | L-302, JOB# 7042374, STUD 7042; INSTALLED 4" CAP V-145 AND INJECTOR
|  | 302 | 0.0009 | [12 empty] | Steel/Wrought Iron |  |  | L-302, JOB# 7042374, STUB 7043; INSTALL 2" CAP V-168
|  | 302 | 0.0007 | [12 empty] | Steel/Wrought Iron |  |  | L-302, JOB# 7042374, STUB 7040, ROUTE 302-128; INSTALLED 4" CAP C/O FOR UNIT 3-1, 3-2, 3-3 LINE 302
|  | 302 | 1.6896 | [12 empty] | Steel/Wrought Iron |  |  | L-302, JOB# 7042374, STUB 7041, TAP OFF ROUTE 302-104; CAP 4" STUB COLUSA MM2
| 03-30207-1 | 302-006 | 0.235 | 6 | Gathering |  | Body of Pipe |  | SUSPECT | Internal Corrosion |  | 2003-05-17 | 2003-11-04 | ABANDON | RETIRED |  |  |  | APPROX. 200 YARDS E/O ARBUCKLE #17 METER; GAS BUBBLES IN FLOODED RICE FIELD; ISOALTED AND BLOWN DOWN PIPE WILL BE RETIRED AT A LATER DATE. V-400 CLOSED PERMANENTLY
|  | 302 | 0.0025 | [12 empty] | Steel/Wrought Iron |  |  | SO# 7047607, ROUTE 302-006; C/O 6" MAIN TO RETIRE ARBUCKLE 17 & 38 L302
|  | 302 | 0.0003 | [15 empty] | SO# 7047066, ROUTE STUB 7028; C/O 6" TO RETIRE 27-28-4 & 33-34-5 AT VALVE 52 OFF OF L302E
|  | 302 | 1.76 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT= 2_2-040, 7052246-04; WEST SIDE OF HWY 145 APROX 1 MILE N/O GRIMES
|  | 302 | 0.0006 | 4 | [8 empty] | 2004-11-17 |  |  | Steel-Other |  |  | SANBORN 30-3, 7047687-04, RTE 302-320; CUT REMOVE PEICE AND INSTALL 3" BLUNA FLANGE; SEE AS BUILTS
|  | 302 | 0.2954 | 4 | [7 empty] | 2004-11-17 | 2004-11-17 |  |  | Steel-Other |  |  | SAN BORN 25-1; 7047687-04, RTE. 302-111; CUT & CAP WITH SAV-A-VALVE; SEE AS BUILT
|  | 302 | 0.0003 | [15 empty] | 7052545-04; RTE 302-287, GMER; TIED TO EXISTING VALVE 493, NO WRAP REMOVED ON 3" L-302
|  | 302 |  | 3 | Gathering | [13 empty] | SO# 7046868-05; RT= STUB 7943 302-285; B SMLS; CUT & CAP 3" @ V.491 TO RETIRE DHAULAGIRI #1
|  | 302-040 | 0.56 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 302-040, JOB 7057326
|  | 302-106 | 0.2399 | [15 empty] | SO#7046758-05; RTE: STUB8285; SRCRTE: 302-106; DIST: MERDIAN; INSPECTED V-18S 2" FLANGED; GROVE BALL VALVE IN GOOD WORKING ORDER
|  | 302-001 | 0.2522 | [12 empty] | Steel/Wrought Iron |  |  | SO# 7059111, ROUTE 302-001, SACRAMENTO DIV
|  | 302 | 0.7935 | 6 | [11 empty] | Other | X42 |  | DIST: MERIDIAN, #7060547-06, RTE: 302-040; X42; WELD 2" SERVICE TEE TO CONECT TRINITY WELL SOAP @ 100 PSI BEFORE TAPPING OUT., SEE AS BUILT
|  | 302 | 0.0004 | 4 | [11 empty] | Steel/Wrought Iron |  |  | DIST: MERIDIAN, SO#7059167-06, 1059167, RTE 302-155
|  | 302 | 0.0133 | [12 empty] | Steel/Wrought Iron |  |  | DIST: MERIDIAN, SO# 7063265-06, L-302-214, 7063265, CONNECT MERIDIAN 2-5 & 2-7 GAS WELL
|  | 302-061 | 0.1694 | 4 | Transmission | GATHERING | [9 empty] | Steel/Wrought Iron |  |  | DISTRICT: MERIDIAN, PM 30604370-08, (HARLAN 124-RP GAS WELL); L-302-061-GG; CONNECT GAS WELL HARLAN 1-24
|  | 302-213 |  | 8.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM 30604323-08, DIST MERIDIAN (STUB9026), L-302-213; CUT OFF 3" (BUTTES CARROLL), BLIND FLANGED VALVE 330 OFF L-302., VALVE 330 IS IN GOOD CONDITION, INSTALLED ETS
|  | 302-119 | 2.9198 | 8.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIST: MERRIDAN, PM30604323-08, (STUB 9030) GG, L-302-119; INSTALLED 3" CAP ON V-146. VALVE IS IN GOOD CONDITION
|  | 302-208 | 0.6595 | 4.5 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIST: MERIDIAN, PM 30604323-08, WELL ABANDONMENT (STUB9029) GG, L-302-208; ABANDONMENT FOR GAS WELL ZZ-27-D3, CUT OFF AND ABANDONED APROX 191' OF 4" STL. PIPE, JOB #30604323
|  | 302 |  | 3 | Gathering | [7 empty] | 2008-05-30 | Deactivate #TP Main | CUT AND CAP 3" | Steel/Wrought Iron |  | GRIMES | JOB# 30633279; WIKINS F-2 GAS WELL LINE, L-302; CUT AND CAP 3"; CAP WITH SAVA VALVE AT 20" AND CUT OFF RISER 24" BELOW GROUND. CUT OFF AND ABANDONED APROX. 2420' OF 3" T.P. STL MAIN
|  | 302-126 | 1.0915 | 4 | Gathering | [13 empty] | RT= 302-126, PM# 30607964
| 08-56006- | 302E | 9.16 | 0.75 | Single Service |  | Regulator |  |  | Material Failure |  | 2008-12-18 | 2008-12-20 | Other | REG. | Steel/Wrought Iron |  | GRIMES | PM# 41025130, RT= 302E; LINE 302; REG; FOUND DAMAGED SEAT ON 3RD STAGE REG - REPLACED SEAT & INSTALLED NEW H-202 RV - SET PRESS @ 40# REG 45# R.V.
| 08-56006- |  |  | 0.75 | Single Service |  | Regulator |  |  | Material Failure |  | 2008-12-20 |  |  |  | Steel/Wrought Iron |  | GRIMES
|  |  |  | 10 | [11 empty] | Steel/Wrought Iron |  |  | REMOVE 4' OF 10" & 3" BYPASS VALVE CUT AND CAP 10" AND 3"
|  |  | 0.932 | 3 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | SYCAMORE 19, ROUTE 302-061, PM: 30650670; SOAP TESTED 3" CAP WELD.
|  | 302-048 | 0.0056 | 2 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | G.O.V. 7-4, ROUTE: 302-048, PM: 30650670; TIE IN WELD.
| 08-30203-1 | 302-040 | 0.54 | 12 | Transmission |  | Body of Pipe |  |  | Internal Corrosion |  | 2008-07-02 | 2008-07-16 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | MERIDIAN | PM# 40915234, ROUTE 302-040; X-RAY, INSTALL 70" CAN WITH SAV-A-VALVE * PRE-TESTED EMERGENCY PIPE
|  | 302 | 0.0008 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM# 30603584; ROUTE: STUB10100 (302)
|  | 302-122 | 0.2695 | 4 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | PM# 30606859; L 302-122; INSTALLED 3" BLIND FLANGE
|  | 302E | 12.1775 | 10.75 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | DISTRICT MERIDIAN 30689409-09, L-302E; INSPECTION OF EXISTING PIPE.
|  | 30.2 | 2.4251 | 4 | Gathering | [10 empty] | Steel/Wrought Iron |  | MERIDIAN | L-302E-1, SO# 30669266, GIRDNER RD .9MI W/O FARMIRE RD; SOAP TESTED WELD AT LINE PRESSURE.
|  | 30.2 | 4.2408 | 6 | [11 empty] | Steel/Wrought Iron |  |  | L-302E-1, SO# 30669266; OSWALD RD APP .95 MI E/O GARMIRE - VALVE # 284; SOAP TEST AT LINE PRESSURE. CUT OFF AND PIGGED
|  | 302E | 17.64 | 2 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 30669267, L-302E; SOAP TEST AT LINE PRESSURE. PIG AND ABANDON 2" STL. CUT OFF RISER.
|  | 302 |  | 6 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 30629361-40; SOAP TESTED AT LINE PRESSURE
|  | 303 | 0.03 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLEY | RT=303, INSIDE STATION
|  | 303 | 11.97 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD AREA | CROSS TIE BETWEEN L-303 & L-114; TRACY SO# 7054807-05, RTE. X6539; G.C. WELD ON 2" SAVE-A-VALVE FOR DRAFTING
|  | 303 | 3.53 | [12 empty] | Steel/Wrought Iron |  | ANTIOCH | SO#7022327-01; SOUTH LONE TREE WAY
|  | 303 | 18.8403 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | NORTH TIE-IN LINE 303 PAGE 2 OLD JOB# 7042512, OLD JOB# 30603496; DISTRICT: TRACY; RTE L-303; 40' PIPE EXPOSED FOR TIE-IN
|  | 303 | 19.0213 | 36 | Transmission | [13 empty] | OLD JOB# 7042512; NEW JOB# 30603496; DISTRICT: TRACY, PM 30603496-07; SOUTH TIE IN 303; RTE L-302; 40" PIPE LINE EXPOSED FOR TIE-IN ONLY
|  | 303 | 19.2 | [15 empty] | L-303/8040017 NORTH END OF JOB
|  | 303 | 20.43 | [15 empty] | L-303/8048017, SOUTH END OF JOB
|  | 303 | 25.55
|  | 303 | 27.2 | [15 empty] | L303
|  | 303 | 27.5
|  | 303 | 32.5 | 36 | Transmission | [7 empty] | 2000-12-28 | Welded Sleeve/Can - Weld |  |  |  |  | WELDED SLEEVE PPC# 10889030, 36.485 I.D.
|  | 303 | 34.64 | 36 | Transmission | [13 empty] | REFER TO 7047685 L303 MP 34.66
|  | 303 | 34.7027 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIST. TRACY, SO# 7047685-06; REFER TO 7047685 L303MP 34.66
|  | 303 | 41.11 | 36 | [14 empty] | L-303; MP 41.14
|  | 303 | 41.31 | [15 empty] | DEPTH DETERMINED BY PROBING AFTER EXCAVATING 5'
|  | 303 | 41.1 | 36 | [11 empty] | Steel/Wrought Iron |  | FREMONT | GPS FILE R101321A LOC#1
|  | 303 | 22.25 | [15 empty] | SOUND WALL TO BE BUILT OVER LINE 303 BY CALTRANS
|  | 303 | 28.8
|  | 303 | 7.5264 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | SO# 7049305, ROUTE 303; NORTH OF NEW INTERSECTION OF HWY 4 BY PASS & FAIRVIEW AVE.;
|  | 303 | 7.5644 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | SO# 7049305, ROUTE 303; NORTH OF NEW INTERSECTION OF HWY 4 BYPASS & FAIRVIEW AVE.
|  | 303 | 7.7396 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | SO# 7049305, ROUTE 303; SOUTH OF NEW INTERSECTION OF HWY 4 BYPASS & FAIRVIEW AVE.
|  | 303 | 7.7787 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | SOUTH OF NEW INTERSECTION OF HWY 4 BYPASS &
|  | 303 | 41.11 | [12 empty] | Steel/Wrought Iron |  |  | MILPITAS DIST, RTE 303
|  | 304 | 9.97 | 12.75 | Gathering | [7 empty] | 2010-01-08 | Grinding - Other |  | Steel/Wrought Iron |  |  | PM# 41161667, L304
|  | 304-1 | 6.5 | [15 empty] | DISTRICT: TRACY SO#7054275-05, L304-1 (GG), SRC RTF L-304 (LT), SRCMP 6.5986; 2" TAP (PIMENTAL WELL) V-26
|  | 304 | 11.2829 | 12.75 | Gathering | TRANSMISSION | [9 empty] | Steel/Wrought Iron |  |  | DISTRICT; TRACY SO#7062609-07, STUB 8979, SRC RTE L-304; CUT & CAP LINE 208
LATHROP
|  | 304 | 3.09 | 3 | Gathering | [10 empty] | Steel/Wrought Iron |  | TRACY | SO#7041689, ROUTE: STUB TAF OF L304-, GAS GATHERING; WEST TRACY 13-25 WELL RETIRE
|  |  | 10.82 | 8 | [11 empty] | Steel-Other |  |  | WELD SERVICE TEE ON 8" 50 PSI MAIN NEW SERVICE 4299 CARLIN RD.
|  | 304 | 10.82 | 8 | [11 empty] | Steel-Other |  |  | 6088104_; CAPED LINE 304, TAPED HPR SET IN AND CAPED TIED LOWER PILE BACK IN OLD LINE 304 (NOW 50 PSI 8" LINE)
|  | 304 |  | 8 | [11 empty] | Steel-Other |  |  | L-304-66; WELD RELOCATE SERVICE TEE TO 8" 50 PSI LINE (OLD 304 LINE)
|  | 304 |  | 8 | [10 empty] | ; | Steel-Other |  |  | CUT OF 8" & CAPED BORED 2" ACROSS CROKER RD. TIED 8" TO 2" SERVICE LINE
|  | 304 | 3.26 | 12.75 | [14 empty] | L-304, 3.2598; PRIMARY ELECTRIC CROSSING UNDER L-304. 4" PLASTIC CONDUIT.
|  | 304 | 6.59 | 12.75 | [14 empty] | SO# 7048593; ROUTE 304; SPER HC ORDER# 7048593
|  | 306 | 68.84 | 20 | Transmission | [7 empty] | 2006-08-07 |  |  | Steel/Wrought Iron |  | MORRO BAY | G300N; L-306, SO# 7056725-06; ERCON PROJECT, REPLACE OLD COATINGS WITH PCJ, INST SUPPORT; ERCON PROJECT, RECOAT A PORTION OF THE SPAN, AND TO INSTALL 4-PILES NEXT TO THE SPAN WITH 2 CLAMPS AS PIPE SUPPORTS.
|  | 306 | 53.8851 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | STAND BY FOR WATER PROJECT & REND WIDENING L-306
|  | 306 |  | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT=306, MP= 53.8722, MP=53.8788, MP=53.8753; POT HOLE IN 3 LOCATION TO RELOCATE ROAD
|  | 306 | 7.7 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | INSTALL TEST LEAD L-306
|  | 306 | 0.01 | [15 empty] | THIS FORM MADE OUT FOR SITE 2 ON THE 10" PIPING
|  | 306 | 54.64
|  | 310 | 37.52 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | KING CITY | L310, SO#7038172-02
91 | 82-30273- | [10 empty] | 1982-10-18
| 82-30273- | 215 | 0.0002 | [14 empty] | PATTERSON
| 02-10029- | 215 | 0.0112 | [14 empty] | PATTERSON | DELTETED; RT=215, MP=0.0112; NEW MP 20; DELETE - MOVE TO MULTI-PURPOSE TAG
91 | 97-70076-1 |  |  | 1 | Service |  | Fitting |  |  | Other |  | 1997-09-22 | 2001-03-19 | Other |  | Steel/Wrought Iron |  | CROWS LANDING | REPLACED LEAKING 3/4" BYPASS VALVE
91 | 79-10013-1 | 215 | 0.0825 | [8 empty] | 1979-08-09 | [5 empty] | PATTERSON | PATTERSON; LINE 215; RT=215, MP=0.0825
|  | 215 | 0.085 | 12 | [13 empty] | PATTERSON | RT=215; CALIFORNIA AQUEDUCT
|  | 215 | 0.0093 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | PATTERSON | OAK FLAT STATION; 215, JOB# 7050108
91 | 77-30160-1 | 215 | 0.267 | [8 empty] | 1977-05-18 | [5 empty] | PATTERSON | OAK LAT RD. METERING STA
|  | 215 | 0.4808 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | PATTERSON | TIECHANT CONST, RT=215; 18" SEVEN PIPE 12" OVER 12 T215
|  |  | 0.4838 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | PATTERSON | STAND BY, RT=215; AS" GAS IS 4' 5" TO TOP, 24" NEW GAS 9' TO TDP
|  | 215 | 0.4969 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | PATTERSON | RT=215; POT HOLED MAIN ABOUT 20' FROM ANGLE POINT
|  | 215 | 2.391 | [14 empty] | PATTERSON | RT-215
|  | 215 | 2.4144 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | PATTERSON AREA | RT=215
|  | 215 | 3.313 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | PATTERSON | RT=215
|  | 215 | 3.3835 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | PATTERSON | RT=215
| 99-70005- | 215 | 3.3947 | 2 | Distribution Main |  | Valves |  |  | Other |  | 1999-05-05 | 2000-05-12 | Other |  | Steel/Wrought Iron |  | PATTERSON | RT=215; GREASED & OPERATED VALVE - SOAP; TESTED & GAS PORT OK
|  | 215 | 4.3758 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | PATTERSON | RT=215
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | PATTERSON
|  | 215 | 4.4967 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | PATTERSON | RT=215
| 98-70002-1 | 215 | 4.5125 | 0.75 | Transmission |  | Regulator |  |  | Other |  | 1998-03-19 | 2000-04-07 | Other |  | Steel/Wrought Iron |  | PATTERSON | RT=215; REPL MONITOR REG BUBBLES AT VENT SLOWLY
91 | 97-70080-1 |  | 4.5127 | 12 | Transmission |  | Valves |  |  | Other |  | 1997-09-22 | 1997-09-24 | Other |  | Steel/Wrought Iron |  | PATTERSON | RT=215; GREASED & SOAP TESTED OK
91 | 98-30071-1 |  | 4.5177 | 0.75 | Distribution Main |  | Valves |  |  | Other |  | 1998-03-19 | 1998-08-05 | Other |  | Steel/Wrought Iron |  | PATTERSON | RT=215
|  |  | 4.7951 | [14 empty] | PATTERSON | 613-4893, RT=215, STANDBY, THURDAY NOV 13, 2003; NO CONFLRT O.K
|  |  | 4.9106 | [12 empty] | Steel/Wrought Iron |  | PATTERSON | RT=215;
|  |  | 6.8123 | 112 | [11 empty] | Steel/Wrought Iron |  | PATTERSON | RT=215
91 | 73-100871- |  | 8.0553 | 12 | Transmission |  | Fitting |  |  | Construction Defect |  | 1973-09-24 | 10/00/0000 | Other |  | Steel/Wrought Iron |  | CROWS LANDING | RT=215, CROWS LANDING, 336601
| 02-10034- |  | 10.5367 | [8 empty] | 2002-08-20 | [5 empty] | TURLOCK | RT=215;
| 92-30057-1 |  | 11.0547 | [14 empty] | TURLOCK | RT=215; DELETED
91 | 90-3064-1 | [16 empty] | TURLOCK
|  |  | 11.4532 | 12 | [11 empty] | Steel-Other |  | TURLOCK | RT=215
|  |  | 12.5951 | 0.75 | Service |  | Regulator |  |  | Material Failure |  |  | 2003-01-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | TURLOCK | RT=215; ON SVC @ H.P.R; BOLTS HAD TO BE REPLACED ON ONE OF THE REGULATORS; EXPOSED SV TEE @ MAIN TO SHUT SVC OFF
| 99-70079- |  | 14.087 | 0.75 | Transmission |  | Valves |  |  | Unknown |  |  | 2002-03-21 | Other | GREASED VALVE | Steel/Wrought Iron |  | TURLOCK | RT=215, ANNUAL; VALVE F&C IN INTERSECTION; DOWNGRADE TO 3 3/24/00___UPGRADE TO 23/20/01___; GREASED VALVE;
|  |  | 14.5639 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | IRISH CONST., STANDBY; RT=215; BONE WAI 36" DEEP FOR PHONE CABLE GAS WAS NOT EXPOSED
|  |  |  | 12 | Transmission | [12 empty] | TURLOCK | P.G.E 215 145696
|  |  | 14.5705 | 12 | Transmission | [12 empty] | TURLOCK | DIVISION: YOSEMITE, SO# 705011-05, L-215
|  |  | 14.5755 | 12 | Transmission | [12 empty] | TURLOCK | RT=215
|  |  | 14.5912 | [14 empty] | TURLOCK | RT=215; INSTALLED & 1/2" SERVICE &_____
|  |  | 14.7975 | 12 | [11 empty] | Steel-Other |  | TURLOCK | RT=215
|  |  | 14.9144 | 12 | [11 empty] | Steel-Other |  |  | RT=215; MAIN EXPOSED TO INSTALL 1/2" & 3/4" STEEL GAS SERVICE
|  |  | 14.9174 | 12 | [13 empty] | TURLOCK | RT=215; REPLACED 7' 3/4" SEAMLESS PIPE
91 |  |  | 15.0337 | [15 empty] | RT=215
91 |  |  | 15.0603 | [15 empty] | RT=215
91 |  |  | 15.1236 | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | TURLOCK | AT SERVICE TEE 240 E/O WASHINGTON
|  |  | 15.8281 | 12 | [11 empty] | Steel-Other |  | TURLOCK | 3368-B2; RT=215
91 |  |  | 16.6606 | 12 | [11 empty] | Steel-Other |  | TURLOCK | RT=215
|  |  | 17.0667 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | HILMAN/TURLOCK
91 | 90-30152-1 |  | 17.1053 | 12 | Transmission |  | Fitting |  |  | Other |  | 1990-01-29 | 1990-02-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | TURLOCK | RT=215; POSTED TO 35; MADE REPAIRS
|  |  | 18.2795 | 12 | [13 empty] | TURL
91 | 91- | 215 | 18.2899 | 12 | [11 empty] | Steel-Other |  | TURLOCK | KT = 215, M.P. 18.2899; INSTALL H.P.R. SET 1" SERV. PLASTIC PIPE
|  | 215 | 18.3359 | 12 | [13 empty] | TURLOCK | RT= 215, M.P. 18.3359
|  | 215 | 18.4197 | 12 | [13 empty] | TURLOCK | RT = 215, M.P. 18.4197
|  | 215 | 18.4743 | 12 | [14 empty] | RT = 215, M.P. 18.4743
91 |  | 215 | 18.534 | 12 | Distribution Feeder Main | [10 empty] | Steel/Wrought Iron |  | TURLOCK | RT= 215, M.P. 18.5340; 3300-...
|  | 215 | 18.534 | 12 | [14 empty] | RT = 215, M.P. 18.5340
|  | 215 | 18.556 | 12 | [14 empty] | RT = 215, M.P. 18.5560
|  | 215 | 19.0868 | 12 | [11 empty] | Steel-Other |  |  | RT = 215, M.P. 19.0868
|  | 215 | 19.2694 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT = 215, M.P. 19.2694; ; LINE 215 STA 28+10; ROUGHT 215; W. LINWOOD AVE & VENTURA AVE TURLOCK; LAT 37 28 41.59086, LONG -120 51 50.299904
91 | 76-10029-1 | 215 | 19.9788 | 12 | Transmission |  | Fitting |  |  | Other |  |  |  | Other |  | Steel/Wrought Iron |  | TURLOCK | RT = 215 M.P. 19.9788; S/E C/P SOUTH AVE & WEST AVE TURLOCK; 12" FEEDER MAIN (LINE 215)
|  |  |  | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  | PATTERSON
|  | 215 |  | 12 | Transmission | [12 empty] | PATTERSON | RT 215, M.P. ....;
|  |  |  | 12 | [13 empty] | TURLOCK
|  |  |  | 12 | Transmission | [12 empty] | MODESTO | STAND BY; POLE LOCATIONMOVED ADDISTIONAL 2 1/2 FEET AWAY FROM GAS CLEAR OK. NO ....
|  | 222 |  | 6.625 | [11 empty] | Other | SMLS PIPE |  | SO#7033590-01, TRACY DISTRICK, TIE IN FOR L-222 INSIDE TRACY STATION
[16 empty] | Steel/Wrought Iron |  |  | #7052206
|  | 220 |  | 10.62 | [8 empty] | 2001-05-11 |  |  | Steel/Wrought Iron |  |  | 10" LINE 200 AT SLEEVE REAPIR LOCATION JOB# 8046776 RIO VISTA DISTRICT; AIR TESTED SLEEVE; GPS LOCATION N-38 18 53" W 121 47 56"; INSTALLED 8FT. LONG 10" SLEEVE AND A 1" SAV-A-VALVE ROLLED 45 DEGREES TO THE EAST; SLEEVE INFORMATION MADE FROM .375 WALL A 516-70 PLATE 38,000SMYS MIN
| 03-22001-1 | 220 | 6.07 | 10 | Transmission |  | Body of Pipe |  |  | Damage by 3rd Party | DIG IN | 2003-10-15 | 2003-10-16 | Welded Sleeve/Can - Weld |  |  |  | SOLANO COUNTY | RIO VISTA LEAK #03-22001-1, SO# 8060341, ROUTE 220, M.P. 6.07; GAS BLOWING IN FIELD; INSTALLED 59" CAN
|  | 220 |  | 10 | Transmission | [13 empty] | A FORM CORRECTION BY A HASTINGS 11/29/2003 SO#7042491 L-220, M.P....
|  | 220 | 18.76 | 6 | Distribution Main | SERVICE | [9 empty] | Steel/Wrought Iron |  |  | SO# 7047491, ROUTE 220, M.P. 18.76
|  | 220 | 34.54 | 6 | Transmission | [12 empty] | YOLO TWON | YOLO WOODLAND E.T.S INSTALLATION; L220 M.P. 34.54 JOB 7043123 (LOCATION #1); DONE WITH SOFT DIG TECHNOLOGY, EXPOSING APPROX 1' PIPE FOR E.T.S. INSTALL
|  | 220 | 34.54 | 6 | Transmission | [12 empty] | YOLO TOWN | YOLO/WOODLAND E.T.S.; L220 M.P. 34.54 JOB 7043123; DONE WITH SOFT DIG TECHNOLOGY EXPOSING VERY SMALL WINDOW FOR E.T.S. INSTALLATION
|  | 312 | 7.8498 | 8 | Transmission | [12 empty] | BAKERSFIELD | L312 M.P. 7.8498
| 06-60077-1 | 312 | 2.14 | 8 | Transmission |  | Body of Pipe |  |  |  |  | 2006-07-18 | 2006-07-18 | Welded Sleeve/Can - Weld | SAV-A-VALVE | Steel/Wrought Iron |  | BAKERSFIELD | DIVISION KERN, 40631857-09, L312 M.P. 2.0944 A FORM FILE; WELDED 2" SAV-A-VALVE OVER DAMAGED AREA; CARLOS MENDOZA WAS EXCAVATION TO BURY A DEAD COW AT 12139 BEAR MT. BLV. (PALLA ROTA...) WHEN HE HIT L-312, A 8" TRANSMISSION MAIN OPERATING AT 540PSI, CAUSING GAS TO EXSCAPE. DID NOT CALL USA, BUT KNOW LINE WAS THERE. WE REPAIRED BY LOWING LINE PSI AND WELDING A 2" SAV0A0VALVE OVER DAMAGED AREA.; L312 MP 2.14 N35.20300 W-119.15727
|  | 314A | 0.1663 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE 314A MILE POINT 0.170 GPS NAD83 -117DEG 20.1583'; 34DEG 36.23060'; EXPOSED PIIPE BY THIRD PARTY (TXI CEMENT CO) TO CROSS UNDER THE LINE WITHA 3" PVC CONDUIT FOR FIBER OPTIC, 8" HDPE GAS MAIN, AND 6" HDPE SEWER. USA# A72480557. FOUND MANY ROCKS PUSHING INTO THE WRAP. REPAIRED THREE PLACES WHERE STEEL WAS SHOWING. NO RUST BUT FOUND WATER BETWEEN WRAP & PIPE.
|  | 314 | 11.5539 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DISTRICT G300S, L314, M.P. 11.5539; LINE 314 MILE POINT 11.553 GPS NAD83 -117.26375; 34.76162; EXPOSED PIPE BY THIRD PARTY TO CROSS UNDER THE LINE WITH AN 4" PVC CONDUIT FOR VERIZON COPPER WIRE CABLE. USA #A70781322
|  | 314 | 26.7856 | 10.75 | [14 empty] | DISTRICT G300S, L314, M.P. 26.7856; GPS NAD83 -1173 3013 DEG. 34.57272 DEG.; 2-3" PVC SC#80 CONDUITS FOR CTV ( COM CAST CABLE) ; LOCATION IS JUST SOUTH OF TURNER RD. VICTORVILLE, CA.
|  | 314 | 28.31 | [15 empty] | L-314, M.P. 28.31; REPAIR WRAP
| 02-31402-1 | 314 | 28.12 | 10 | Transmission |  |  |  |  | Construction Defect | EXTERNAL CORROSION | 2002-12-04 | 2003-01-08 | Welded Sleeve/Can - Weld |  |  |  | VICTORVILLE | SO# 8055656-02 RT= 314, M.P. 27.95 PER GSAVE; HOLIDAY IN WRAP CAUSED BY MOVEMENT WHILE ON SKIDS DURING INSTALLATION; LAT 37 33 38.170N, LON 117 19 25.438W, ALT 2810; LEAK REPAIRED
|  | 314 | 0.87 | [15 empty] | LAT 34 53 22.693N LONG 117 10 00.906W ALT 2190 D16#8; 12" PIPE AND WRAP CHECKED BY MEAR/CPG, INC. TEST COUPON AND E.T.S. INSTALLED 10' RECOATED W/POWER CRETE "J" PIPE TO SOIL .850 @PIPE .760 @ GROUND PH:
|  | 314 | 27.46 | [15 empty] | LOCATED 440' D/S OF TAP VALVE ON 8" LINE TO REG SET (VICTORVILLE "B") RUST FOUND ON DAMAGED WRAP FROM LIFTING WITH A CHAIN WHEN PIPE WAS INSTALLED. WATER FOUND BETWEEN WRAP AND PIPE. WRAP SAMPLE TAKEN TO TEST FOR ASBESTOS. FILTER/SEPORATOR FOR RAY STATION.
|  | 314 | 28.3 | [15 empty] | SO# 8048937-02. LAT 34 33 40.845N, LON 117 19 10.344W, ALT 27.98 D15 #1; 10' CHECKED AND TESTED BY MEARS CONTRACTORS. TEST COUPON INSTALLED NEXT TO HHE W/ E.T.S.. RECOATED WITH POWER CRETE "J" PIPE TO SOIL -.826MV
|  | 314 | 29.02 | [15 empty] | SO# 8048937-02. LAT 34 33 23.538N, LON 117 18 26.338W ALT 2683 DIG#7; 10" PIPE AND WRAP CHECKED BY MEARS, CPS, INC. TEST COUPON AND E.T.S. INSTALLED RECOATED WITH POWER CRETE "J" PIPE TO SOIL 1.052 @PIPE .960@GROUND. PH 5.5. THREE CACALOUS DEPOSITS FOUND ON 4" SWG PIPE PLASTIC SHEET INSTALLED BETWEEN PIPES
|  | 314 | 29.01 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#7048550-04, RT 314, M.P. 39.01; 144' OF 16" CASING INSTALLED
|  | 314 | 29.05 | [15 empty] | L314 29.05
|  | 314 | 29.05 | [15 empty] | 20' OF CASING INSTALLED FOR NEW RR TRACT AT CEMENT PLANT
|  | 314 | 29.07 | [14 empty] | VICTORVILLE | RT 314 MP 29.07, SO# 7043531.02, RR X-ING
|  | 314 | 29.07 TO 29.09 | [15 empty] | PIPE TO SOIL 1.050; PIPE TO CASING .710; CASING TO SOIL .336; ADDING 130' OF SPLIT 16" CASING FOR ADDITIONAL RR TRACKS OVER THE LINE STARTING @ D/S END OF EXISTING CASING FOR RR TRACKS 65" TOP IF CASING TO TOP OF EXISTING RAIL
|  | 314 | 29.2 | [15 empty] | L314 29.20
|  | 314 | 29.2 | [15 empty] | SO# 8048937-02. 23' OF CASING INSTALLED FOR NEW RR TRACKS @ CEMENT PLANT
|  | 314 | 31.88 | [15 empty] | LAT 34 35 29.160N, LON 117 16 48.849W, ALT 3011 DIS#6; 10" PIPE CHECKED BY MEARS/CPG, INC. TEST COUPON AND E.T.S. INSTALLED RECOATED W. POWER CRETE J. PIPE TO SOIL 1.290MV, PH, LINE OF LIGHT PITTING FOLLOWING THE SEAM OF THE FACTORY HHA WRAP TEST COUPON NOT ACTIVE AND DUE TO PIP LINE IS IN ROAD WAY
|  | 314 | 34.38 | [15 empty] | L314 34.38
|  | 314 | 34.45 | [15 empty] | L314; 34.45
|  | 314 | 34.47 | [15 empty] | L314; 34.47
|  | 314 | 34.48 | [15 empty] | L314; 34.48
|  | 314 | 34.5 | [15 empty] | L314; M.P. 34.50
|  | 314 | 34.46 | [15 empty] | SO# 70386...02, L314, M.P. 3455, I-15...FWY; COATING WELL BONDED P.C.F. TO REINSTALL FOR NEW SECTION OF 10" PIPE UNDER I-15 FREEWAY
|  | 314 | 34.63 | [15 empty] | SO# 7038625-02, L314 M.P. 34.71, I-15 MOJAVE FWY; COATING WELL BONDED P.C.F. TO BE INSTALLED FOR NEW SECTION 10" PIPE UNDER I-15 FREEWAY
|  | 314 | 34.77
|  | 314 | 35.55 | [15 empty] | GPS WG583 -117.230006, 34.61594; WORK DONE BY MEARS. FORM "H" COMPLETED BY MEARS.; 50" U/S & D/S OF...DUG UP WRAP REMOVED INSPECTED SAND BLASTED ...WITH POWERCRETE "J". NEW...ISNTALLED...(TWO WHITE) AND 10" L314 (2 BLACK) AT CROSSING
|  | 314 | 35.55 | [15 empty] | GPS A6583 -117.230006, 34.61594; WORK BY MEARS FORM H COMPLETED BY MEARS.; 1) WHITE WIRES ATTACHED TO SO CAL LINE; 2) BLACK WIRES ATTACHED TO L314; 3) COUPON ATTACHED
|  | 314 | 36.27 | [15 empty] | RT 314, M.P.36.27; 117 12 48.9, 34 36 57.5; LINE CROSSING BY VICTORVALLEY WASTE WATER RECLAMATION AUTHORITY
|  | 314 | 37 | [15 empty] | AZ PIPELINE CROSSED UNDER L-314 AT MP 37.0 (DALE EUENS PRKWY)
|  | 314 | 36.7 | [15 empty] | LAT 34 36 57.493N, LON 117 12 23.045W, ALT 3038; 8" PIPE AND WRAP CHECKED BY MEARS/CPG. INC. TEST COUPON AND E.T.S. INSTALLED RECOATED WITH POWER CRETE "J" PIPE TO SOIL .887 GROUNG .950 @ PIPE PH 6.5
|  | 314 | 37.72 | [15 empty] | LAT 34 36 57.385N, LAT 117 11 09.593W, ALT 3128; 8" PIPE CHECKED BY MEARS CONTRACTOR. TEST COUPON TEST INSTALLED RECOATED W/ POWERCRETE "J" PIPE TO SOIL 1.16MV
|  | 314 | 39.28 | [15 empty] | LAT 34 36 50.578N, LON 117 09 36.544W, ALT 3230 DIG#3; 8" PIPE CHECKED BY MEARS CONTRACTOR TEST COUPON AND E.T.S. INSTALLED AT THIS SITE RECOATED W/ POWERCRETE J. PIPE TO SOIL 1.185MV
|  | 314 | 43.19 | [15 empty] | SO# 8048937-02. LEAK INVESTIGATION NONE FOUND ON PIPE
|  | 314 | 0.08 | [15 empty] | ...FOR KRGT PIPELINE
|  | 300A | 1.9 | [15 empty] | POT HOLE FOR KRGT PIPELINE
|  | 300B | 191.18 | [15 empty] | LAT 35 00 03.651N, LONG 117 42 12.828W, ALT 2385; BORED 42" MOJAVE/KERN P.L. 15' DEEP. VAC. TRUCK POT HOLE 11' DEEP NEXT TO L-300B, 57" COVER ON L-300B
|  | 316 | 0.2697 | 12 | Gathering | [7 empty] | 2008-10-13 | Other | WRAP PIPE WITH STACK WRAP | Steel/Wrought Iron |  | BRENTWOOD | PM# 40956253, L316-2, M.P. 0.267; ... 3 1/2" CIRCLE DENT
|  | 316 |  | 8.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | BRENTWOOD REGULATOR STATION BRENTWOOD, CONTRA COSTA COUNTY
|  | 316 | 6.19
|  | 316 | 6.19 | [15 empty] | 993
|  | 316 | 6.19
|  | 316 | 6.19 | [15 empty] | ROUTE 316-20, M.P. 0.5459
|  | 316-21 | 0.9701 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 316-21, M.P. 0.9701;; LINE 114 STA 4+80 ROUTH 316-21; MP 0.9705; LAT 37 57 20.21903; LONG -121 41 46.54806; ; ON BRENTWOOD BLVD; 497 NORTH OF GRANT RD BRENTWOOOD; ; MISC. COMMENTS/INFORMATION: ORIGINAL CENTER OF DIG WAS MOVED 2' NORTH PER MIKE WEST TO AVOID TEMPERING WITH PERPENDICULAR GASLINE CROSSING. THE OLD TAPE COATING WAS IN EXCELLENT CONDITION, WELL ADHEARED. ONLY MINOR KNICKS FROM PROBING WERE PRESENT. CLEAN PIPE; NO CORROSION FOUND. EDGE MT FOUND TWO INDICATIONS THAT WERE ABLE TO BE GROUNG OUT. THE PIPE WAS RECOATED WITH PROTAL 7200 AND THE EDGES WERE WAX TAPED TO IMPEDE THE TRANSITION OF THE OLD TAPE COATING TOTHE NEWLY APPLIED PROTAL 7200
|  | 316-21 | 0.9701 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 316-21 MP 0.9701;; LINE 114 STA 4+80 ROUTH 316-21; MP 0.9705; ; LAT 37 57 20.21903; LONG -121 41 46.54806; ; ON BRENTWOOD BLVD.; 497 NORTH OF GRANT RD. BRENTWOOD; ; MISC. COMMENTS/INFORMATION: ORIGINAL CENTER OF DIG WAS MOVED 2' NORTH PER MIKE WEST TO AVOID TEMPERING WITH PERPENDICULAR GASLINE CROSSING. THE OLD TAPE COATING WAS IN EXCELLENT CONDITION, WELL ADHERED. ONLY MINOR KNICKS FROM PROBING WERE PRESTENT. CLEAN PIPE; NO CORROSION FOUND. EDGE MT FOUND TWO INDICATIONS THAT WERE ABLE TO BE GROUND OUT. THE PIPE WAS RECOATED WITH PROTAL 7200 AND THE EDGES WERE WAX TAPED TO IMPEDE THE TRANSITION OF THE OLD TAPE COATING TO THE NEWLLY APPLIED PROTAL 7200.
|  | 316N | 0.31 | 3.5 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | L 316N, M.P. 0.31, SO#70...8126 STATION; BRENTWOOD REGULATOR STATION BRENTWOOD, CONTRA COSTA COUNTY
|  | 316N | 0.31 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | BRENTWOOD | L 316N, M.P. 0.31 SO# 7048126 STATION; BRENTWOOD REGULATOR STATION BRENTWOOD; CONTRA COSTA COUNTY
|  | 316A |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  | BETHEL ISLAND | SO# 7042005 ROUTE 316A; M52 & M53 GAS WELL YARD BETHEL ISLAND SOUTH OF CANAL RD. CONTRA COSTA COUNTY
|  | 316A | 0.0152 | 6.62 | Gathering | [10 empty] | Steel/Wrought Iron |  | JERSEY ISLAND | SO# 7050406, SO# 7049245, ROUTE 316A MP 0.0152; JERSEY ISLAND CONTRA COSTA COUNTY +/- 20' WEST OF JERSEY ISLAND RD. & +/- 1/2 NORTH JERSEY ISLAND BRIDGE
|  | 316A | 2.308 | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  | BETHEL ISLAND | DIST TRACY, RTE: L-316A, M.P. 2.3080, SO# 7051508-06; CONNECT MSDP #1 LINE 316 BETHEL ISLAND, CONTRA COSTA COUNTY
|  | 316-3 | 0.35 | 6.625 | [14 empty] | ROUTE ..316-3, MP 0.35
|  | 318 | 1.61 | [12 empty] | Steel/Wrought Iron |  |  | MERIDIAN; SO# 7052353-05 SRC RTE L-318, M.P. 1.6100, RTE STUB8164, M.P. 0.0
|  | 318 | [16 empty] | SO# 6073383, L318 MERIDIAN DISTRICT RETIRE...; PIPE HAD LIGHT...FILM
|  | 318-1-2 | [13 empty] | Steel/Wrought Iron
[5 empty] | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DISTRICT MERIDIAN, SRC RTE L318-7GG, SRC MP 0.0029, RTE STUB8150, M.P. 0.000, SO# 7048988-05; LIGHT OIL INTERNALY
|  | 318 | 0 | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  |  | 2008-06-19 | Deactivated Partial Service |  | Steel/Wrought Iron |  |  | ...30635915; INFO ON 34" CANINSTALLATION 6-19-08 A0372-01; CUT OUT EXSISTING 6" TEE INSTALLED 34" PRETESTED 6" .156WT X 42 SOAP @ 100 PSI
|  | 318 | 0.33 | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  | ORLAND | L-318, M.P. 0.33; 30635915
|  | 318 | 0.33 | 3.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | L-318 M.P. 0.33 30635915; INFO ON 10" CAN INSTALLED 6-19-08 A-0110-01
|  | 400 | 170.86 | 2 | Transmission | [10 empty] | Steel/Wrought Iron |  | ORLAND | RT 318-4, PM# 30603489, M.P. 0; NO WELDING CUT OFF 3" BOLTED 2 " BLING FLANGE ON 2" VALVE (HOT TAP) LINE 400
|  |  | 0.0031 | 4 | Distribution Main | [10 empty] | Steel/Wrought Iron |  |  | # 30629977-09, DSBN 5737, M.P 0.0031; SOAP TESTED WELD AT LINE PRESSURE
|  |  | 0.0012 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | #...629977-09, STUBB 10246; MP 0.002; SOAP TESTED WELD AT LINE PRESSURE
|  | 313 | 0.0103 | 3 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DISTRICT MERIDIAN; #30629977-09, L313 (LT), M.P. 0.0103; SOAP TESTED TIE-IN WELD AT 100IBS AND LINE PRESSURE
|  |  |  | 3 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SOAP TESTED AT THE PRESSURE
|  | 331A | 4.8291 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 331A, M.P. 4.8291, PM# 30708565
|  | 331B-1 | 0.0062 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 331B-1 M.P. 0.0062, PM#30708565
|  | 331A | 2.9854 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ? COULD NOT LOCATE; PM# 30708565 RT 331A, M.P. 2.9854
|  | 331 |  | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ? COULD NOT LOCATE
|  | 331 | [16 empty] | PM# 30701925, RT 331A, MP 0.0236, RT 331B-2 M.P 0.0013
|  | 331 |  | 06.00 & 12.00 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM# 30701925, RT 331A, M.P. 0.4788 RT 331B-2 M.P. 0.4495
|  | 331A | 0.78 | 6 | [14 empty] | PM# 30701925, RT 331A, M.P. 0.78
|  | 331A | 5.5874 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LT 331A, M.P 5.5874;; ; LINE 331 STA. 3+10 LOS BANOS; ROUGHT GCUST 5916; MP 0.0072; LATIT 37 06 44.69353, LONG -120 56 36.0746 MISC.; ; COMMENTS/INFOMRATION: THIS DIG SITE IS LOCATED AT 12045 S. INGOMAR GRADE IN LOS BANOS, CA. THE DIG SITE IS SOUTHEST ONTO THE PROPERTY OF THE LIBERTY PACKING PLANT AND WEST OF THE RAILROAD TRACKS. UPON ARRIVA; TO SITE, A PORTION OF THE PIPE WAS ALREADY DUG OUT WITH A PORTION OF THE PIPE EXPOSED FROM A PRIOR PG & E DIG. THE DITCH WAS EXTENDED TO INSPECT A 10' BELL HOLE. WATER WAS FOUND IN DITCH ARE, SAMPLES WERE TAKEN AND GIVEN TO ATS ON 3/23/2010. EATER HAD TO BE PUMPED OUT OF DITCH AREA. EXISTING COATING WAS BLACK TAPE. EXISTING COATING IN EXCELLENT CONDITION. NO CORROSION FOUND ON PIPE. SAVER NIPPLE 6.2.5" FROM U/S EDGE. MT PERFORMED BY ATS WITH NO LINER INDICATIONS. PIPE WAS WAX TAPED DIE TO WATER IN DITCH. A LAYER OF TUFF-N-NUFF WAS APPLIED E.T.S. WAS INSTALLED AT U/S EDGE. PIPE WAS BACKFILLED WITH NATIVE SOIL 1. ;
|  |  |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | LINE 331 STA. 3+10 LOS BANOS; ROUGHT GCUST 5916; MP 0.0072; LATIT 37 06 44.69353, LONG -120 56 36.0746 MISC.; ; COMMENTS/INFORMATION: THIS DIG SITE IS LOCATED AT 12045 S. INGOMAR GRADE IN LOS BANOS, CA. THE DIG SITE IS SOUTHWEST ONTO THE PROPERTY OF THE LIBERTY PACKING PLANT AND WEST OF THE RAILROAD TRACKS. UPON ARRIVAL TO SITE, A PORTION OF THE PIPE WAS ALREADY DUG OUT WITH A PORTION OF THE PIPE EXPOSED FROM A PRIOR PG & E DIG. THE DITCH WAS EXTENDED TO INSPECT A 10' BELL HOLE. WATER WAS FOUND IN DITCH AREA, SAMPLES WERE TAKEN AND GIVEN TO ATS ON 3/23/2010. WATER HAD TO BE PUMPED OUT OF DITCH AREA. EXISTING COATING WAS BLACK TAPE. EXISTING COATING IN EXCELLENT CONDITION. NO CORROSION FOUND ON PIPE. SAVER NIPPLE 6.2.5" FROM U/S EDGE. MT PERFORMED BY ATS WITH NO LINER INDICATIONS. PIPE WAS WAX TAPED DUE TO WATER IN DITCH. A LAYER OF TUFF-N-NUFF WAS APPLIED BACK FILLED WITH NATIVE SOIL 1
|  | 339-1-5 | 0.0003 |  | Transmission | [13 empty] | DISTRICT MERIDIAN, ORIGINAL 7048485-05, NEW RET STUB8163 OLD RTE GG339-1-5, M.P. .0003, SACRTE L-177A, M.P. 14.1279; DIDN'T EXPOSE MAIN
|  | 375 | 4.2913 | 16 | [11 empty] | Steel-Other |  |  | l 375, M.P 4.2913 (STA 228+23);; ; LINE 375 STA. 228+23 M.P. 4.2913; LATITUDE .35 26 09.13844 LOGITUDE -119 04 33.477721; EAST SIDE OF HWY 99, IN BETWEEN HWY 99 & PORTERVILLE HWY 65; ; MISC. COMMENTS/INFORMATION: THIS SITE IS LOCATED 1800' SOUTH AND 320' WEST OF THE INTERSECTION OF 7TH STANDARD ROAD AND HIGHWAY 65. THE SIRE IS IN THE BACK PARKING LOT OF NORTH BAKERSFIELD TOYOTA SCION DEALERSHIP. THE EDGE OF THE EXCAVATION IS ALONG SIDE OF A CURB. THE CURB HAS TO BE REMOVED TO PERFORM THE EXCAVATION. THERE WERE 2 BUSHES THAT WERE REMOVED DURING EXCAVATION, AND REPLANTED AT FINISH. THE DEPTH OF COVER OVER THE PIPE WAS 7'. THE PIPE HAD A PLASTIC WRAP COATING IN 2 LAYERS: 1ST WHITE, AND 2ND BLACK. THERE WAS NO COATING DAMAGE. THE PIPE HAD 2 WIRES THAT WERE CAD WELDED TO IT, AND ONE OF THE WIRES WAS LOOSE AND UNATTACHED WITH SLIGHT PRESSURE. THE WIRES WERE DISCONNECTED BEFORE MEDIA BLASTING. THE PIPE WAS MEDIA BLASTED TO A NEAR WHITE FINISH WITH KLEENBLAST 30/60. UPON INSPECTION, THE EXISTING WIRES TO THE PIPE AT THE D/S EDGE OF INSPECTION AT 12:00. WE CAD WELDED 2 WIRES AT 12:00 ON THE U/S EDGE OF INSPECTION. THE PIPE WAS COATED WITH PROTAL 7200. WE INSTALLED A COUPON AND E.T.S. AT THE U/S EDGE AT 9:00 SPRING LINE TO THE PIPE. A REGERENCE ELECTRODE WAS PLACED SPRING LINE TO THE PIPE AT THE 3:00 POSITION. WE APPLIED WAX PRIMER AND WAX TAPE AT THE TIE-IN'S ON EACH END, AS WELL AS OVER THE CAD WELDS FOR THE E.T.S AND THE EXISTING WIRES. THE BELL HOLE WAS BACK FILLED WITH SAND AND BASE ROCK AND WAS COMPACTED. A CONCRETE REPAIR COMPANY WILL BE REPLACING THE CURB DURING THE WEEK OF 5-2211. THE PLANTS THAT WERE REMOVED HAVE BEEN REPLANTED. JIM AIRD
|  |  |  | 16 | [11 empty] | Steel-Other |  |  | LINE 375 STA; 247+91 M.P. 4.6634; LATITUDE 35 26 28.08778 LONGITUDE -119 04 30.41980; ; MISC. COMMENTS/ INFORMATION: THE SIRE IS LOCATED IN THE SW CORNER OF THE INTERSECTION OF HWY 65 AND MERIE HAGGARD. THE SITE IS IN THE GRASS JUST EAST OF DENNY'S. THERE WAS A SPRINKLER LINE THAT WAS AT THE TOP OF THE EXCAVATION THAT WE HAD TO CUT. DUE TO NEARBY UTILITIES, WE USED A BADGER VACCUM TRUCK TO PEERFORM THE EXCAVATION. THERE WERE 3 PEICES OF CONDUIT RUNNIGN ABOVE THE PIPE. THE DEPTH OF COVER WAS 8.5' AT THE U/S EDGE AND 9.5 AT THE D/S EDGE. THE PIPE HAD TAPE COATING IN 2 LAYERS. AFTER COATING REMOVAL, THE PIPE APPEARED TO BE IN GOOD CONDITION. THE PIPE WAS MEDIA BLASTED WITH KLEEN BLAST 30/60 TO A NEAR WHITE FINISH. THE PIPE WAS INSPECTED AND WAS FOUND TO BE IN GOOD CONDITION. EDGE PERFORMED THE MT INSPACTION AND FOUND NO INDICATIONS. WE INSTALLED CADWELDS ON 2 TEST WIRES AT 12:00, 2' FROM THE U/S EDGE. THE PIPE WAS COATED WITH PROTAL 7200. WE APPLIED WAX TAPE AND WAX PRIMER AT THE U/S AND D/S TRANSITIONS. A REFERENCE CELL AND COUPON ETS WERE INSTALLED AT 9:00 2' FROM THE U/S EDGE OF INSPECTION. THE EXCAVATION WAS BACK FILLED WITH IMPORTED SAND AND SLURRY. A LANDSCAPING COMPANY IS REPAIRING THE GRASS AT THE SITE.; ; MISC. COMMENTS/INFOMRATION ABOUT AREA SURROUNDING DITCH: THE SIRE IS LOCATED IN THE SW CORNER OF THE INTERSECTION OF HWY 65 AND LERIE HAGGARD. THE SITE IS IN THE GRASS EAST OF DENNY'S. JIM AIRD
[5 empty] | Transmission >= 20% SMYS | [10 empty] | Steel-Other |  |  | LINE 375 ROUTE 375 STA 249+38 MP 4.6885; LATITUDE 35 26 29.53382, LONGITUDE -119 04 30.45307; 7TH STANDARD & HWY 65 BAKERSFIELD; ; MISC. COMMENTS/INFORMATION: THIS SITE IS LOCATED IN THE NW CORNER OF THE INTERSECTION OF HWY 65 AND MERIE HAGGARD. THE SIRE IS IN THE GRASS AT THE SHELL STATION.; ; THE SIDE WALK HAD TO BE SAW CUT TO COMPLETE THE EXCAVATION. THERE WAS AN ANODE JUNCTION BOX THAT WAS INSIDE OF A BOX LEVEL WITH THE SIDE WALK. THE BOX WAS REMOVED AND THE JUNCTION BOX WAS HELD SECURE DURING EXCAVATION. THE DEPTH OF COVER WAS 13' TO THE TOP OF THE IPE. THERE WERE MULTIPLE UTILITIES IN THE AREA OF EXCAVATION. DUE TO THE MULTIPLE UTILITIES, THE SIRE WAS EXCAVATED WITH A VACCUM TRUCK BY BADGER. COMING FROM THE ANODE JUNCTION BOX, THERE WERE MULTIPLE PIECES OF CONDUIT WITH ANODE WIRES IN THEM. 2 OF THE ANODES WERE EXPOSED DURING EXCAVATION SPRING LINE TO THE PIPE. 1 OF THE ANODES WAS COMPLETELY DEPLETED. AND THE OTHER HAD VERY LITTLE MATERIAL LEFT. WE WERE INSTRUCTED BY BRIAN WINGET IF THERE WAS NO CORROSION, THEN LEAVE AS IS. THE SIDE DIDN'T PRESENT ANY CORROSION. THE CASING END SEAL ENTERS THE AREA OF EXCAVATION, AND THE AMOUNT THAT WE WERE ABLE TO INSPECT WAS 7.5' THE END SEAL APPREARED TO HAVE BROKEN WHEN THE CASING WAS WAX FILLED, AND LARGE AMOUNTS OF WAX WERE IN THE SOIL AROUND THE END SEAL. BRIAN WINGET WAS MADE AWARE OF THE SITUATION. WHEN OBTAINING THE PIPE-TO-SOIL POTENTIALS, IT WASS MADE EVIDENT THAT THEY WERE GREATER THAN +450MV DIFFERENCE THEN THE PREVIOUS POTENTIALS. THE STANDBY PERSON WAS MADE AWARE OF THE SITUATION AND FOUND THAT A RECTIFIER ACROSS THE STREET HAD A BLOWN FUSE. THE COATING WAS WELL ADHERED TO THE PIPE. AFTER COATING REMOVAL, THE PIPE WAS IN GOOD CONDITION. THE PIPE WAS MEDIAL BLASTED WITH KLEEN BLAST 30/60 TO A NEAR WHITE FINISH. EDGE PERFORMED THE MAGNETIC PARTICL INSPECTION AND FOUND NO INDICATIONS. CAD WELDS WERE INSTALLED AT 12.00 2' FROM THE U/S EDGE OF INSPECTION. THE PIPE WAS RECOATED WITH PROTAL 7200. WE APPLIED WAX PRIMER AND WAX TAPE AT THE TRANSITIONS. A COUPON E.T.S. AND A REFERENCE CELL WERE INSTALLED SPRINGLINE TO THE PIPE AT 9:00. THE EXCAVATION WAS BACK FILLED WITH SLURRY. ; ; MEARS JOB# 9101123034; EXCAVATION SIZE 13' X 10'; ; JIM AIRD
|  | 375 | 4.6929 | 16 | Transmission >= 20% SMYS | [10 empty] | Steel-Other |  |  | LINE 375 STA. 249+58 M.P. 4.6931; LATITUDE 35 26 29.73592, LONGITUDE -119 04 30.40884; ; MISC. COMMENTS/INFORMATION: THIS SITE IS LOCATED IN THE NW CORNER OF THE INTERSECTION OF HIGHWAY 65 AND MERIE HAGGARD. THE SITE IS IN THE ASPHALT AT THE SHELL STATION. THE DEPTH OF COVER WAS 14.5' TO THE TOP OF THE PIPE. THE SITE WAS EXCAVATED WITH A VACUUM TRUCK BY BADGER. THERE WERE MULTIPLE CONDUIT PIES RUNNING JUST ABOUVE THE PIPE THAT HAD TEST LEAKDS TO ANODES. NO ANODES WERE EXPOSED. THE PIPE HAD A PI IN THE MIDDLE OF THE AREA OF INSPECTION. THE COATING WAS A TAPE COATING AND WAS NOT WELL ADHERED AROUND THE PI. WHILE PERFORMING THE COATING HOLIDAY DETECTOR TEST, THE ENTIRE PI WAS AN INDICATION AND THE COATING WAS LOOSE AROUND THE PI AT 3:00 ALONG THE ENTIRE SECTION, THERE WAS A LOOSE POCKET IN THE ROCKSHIELD AS VISIBLE IN THE PHOTOS. AFTER THE COATING WAS REMOVED, SEVERAL CORROSION CELLS WERE FOUND. AFTER MEDIAL BLASTING, 9 EXTERNAL CORROSION CELLS WERE FOUND TO HAVE A MAXIMUM PIT DEPTH OF OVER 10%. THESE WERE ALL MEASURE, PHOTOGRAPHED, AND NOTATED. NO PITS WERE FOUND WITH WALL LOSS GREATER THEN 20%. A MAJORITY OF THE CORROSION WAS FOUND ON THE U/S AND D/S GIRTH WELDS OF THE PI AROUND 1:00 & 4:00. WE INSTALLED CAD WELDS ON THE D/S SIDE OF THE PI AT 12:00. THE PIPE WAS RECOATED WITH PROTAL 7200. WE APPLIED WAX PRIMER AND WAX TAPE AT THE TRANSITION. A REFERENCE CELL AND COUPON WAS INSTALLED SPRINGLINE TO THE PIPE AT 9:00. THE SITE WS BACKFILLED WITH SLURRY. THE PAVEMENT WILL BE REPAIRED IN THE FOLLOWING WEEK, PHOTO'S WILL FOLLOW; ; JIM AIRD
|  | 400 | 42.2195 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | COUPON INTALL M-42 L-400 42.2195; L 400 M.P. 42.2195, JOB 7053752
|  | 400 | 51.05 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | COUPON INSTALL M-51.05 L-400; L400 M.P. 51.05 JOB 7053752
|  | 400 | 66.89 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | FALL RIVER L-400 HYDROTEST. LOCATION #3 STA. "P" 2975+43. L-400 M.P 66.89
|  | 400 | 69.38 | [15 empty] | ALL OK
|  | 400 | 70.27 | 36 | Transmission | [10 empty] | Wrought Iron |  |  | JOB# 8032376. BURNEY/FALL RIVER L-400 HYDRO TEST, LOCATION #2 STA. P 3156+03
|  | 400 |  | 36 | [11 empty] | Steel-Other |  |  | THIS IS A NEW TAP MP 81.63 JUST NORTH OF BURNEY
|  | 400 | 121.1231 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | COUPON INSTALL M-121 L-400; L-400 M.P. 121.1231 JOB 7053752
|  | 400 | 143.69 | 36 | [8 empty] | 2003-06-09 | Other |  |  |  | RED BLUFF | BLENDED DAMAGED AREA W/60 GRIT PAD
|  | 400 | 115.28 | [15 empty] | JOHNSON TAP 1"; 1" LINE U/S TAP VALVE. REWRAPPED 1" X 2" SECTION AFTER REMOVING CORRAGATED PIPE TO MAKE REPAIRS TO VALVE. FOUND ABOVE PLASTIC PIPE SITTING ON 1" X 2" SECTION
|  | 400 | 159.08 | [15 empty] | RT 400, M.P. 159.08
|  | 400 | 159.09 | 36 | Transmission | [10 empty] | Steel-Other |  | CORNING | SO# 7049246, RT 400, M.P. 15909;
|  | 400 | 162.2 | [12 empty] | Steel/Wrought Iron |  |  | L-400 M.P. 162.20, SO# 6059585-01
|  | 400 | 193.8252 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  | GLEN COUNTY | L-400 M.P. 193.8252; LINE 400 M.P. 193.8252 JOB 30647341; WELDED PIPING & TEE TO LINE 400. PREVIOUSLY TESTED BY M. SHAEFFER. PUMPED 3" LINE UPTO 100IBS AND SOAP TESTED TEE WELD.; LINE 400 M.P. 193.8252 JOB 30647341
|  | 400 | 197.6686 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM# 316...RT 400, M.P. 197.6686
|  | 400 | 197.958 | [12 empty] | Steel/Wrought Iron |  |  | RT 400 M.P. 197.9580 JOB 7041188-03; 2-10" TAP VALVES. WRAP CONTAINS 2% ASBESTOS. SEAM AT 3:00
|  | 400 | 197.83 | [12 empty] | Steel/Wrought Iron |  |  | DELEVAN COMPRESSOR STA. L-400 MP 197.83 SO# 7054106-05
|  | 400 | 241.32 | [12 empty] | Steel/Wrought Iron |  |  | SO# 7049214 ROUTE 400 M.P. 41.32; INSTALLED 2" SERVICE TEE ON L-400. TESTED TEE AT 105 PSI BEFORE TAPPING
|  | 400 | 241.3463 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7049214-04 ROUTE 400 M.P. 241.3463; WORK AREA IS ON M-400 SOUTH OF DUNNIGAN AT M.P. 241.35. FUTURE 2" TAP FOR DE HI FEED FROM GAS WELL IN THE AREA. IF MORE INFO IS NEEDED CONTACT CGT WILLOWS DIST.
|  | 400 | 242.85 | 36 | [14 empty] | JOB# 7043036 36" LINE 400; WILLOWS DIST. RTE L-400, M.P. 242.85, SO#704303 AFORM...
| 07-53037-1 | 400 | 269.47 | 2 | Transmission |  | Valves |  |  | Material Failure |  | 2007-04-17 | 2007-04-18 | Other | REPLACED VALVES | Steel/Wrought Iron |  | VACAVILLE | 2" BROKEN VALVE OFF OF L-400 VACA/REG BB400 M.P. 269.41...; REPLACED FAILED 2'"VALVE; VACA REG 2" VALVE; VACA/DIXON SUB L-400-2" TO REG PIT
|  | 400 | 269.48 | 16 | Transmission | [13 empty] | RT = DCUST, M.P. 269.48; SO# 7037479-02 L-400 MLV-269.48; BLOW OFF USED TO TIE NEW POWER PLANT
|  | 400 | 280.24 | [15 empty] | RT 400, M.P. 280.24, SO# 7042666-04; COPY A FORM FOR FILE L-400, M.P. 280.24; CASING REPLACED AND APPROX 60 FEET STRIPPED AND RECOATED. LIGHT GOUGES REPAIRED BY GRINDING, SEE ATTACHED SHT.
|  | 400 | 280.25 | [15 empty] | CASING REPLACED AND APPROX. 60 FEET STRIPPED AND RECOATED. LIGHT GOUGES REPAIRED BY GRINDING SEE ATTACHED SHT.
|  | 400 | 286.6754 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM# 30607405; ROUTE 400, M.P. 286.6754
256.67
|  | 400 | 208.29 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  | MAXWELL | SO# 7050034, RT 400, M.P. 208.29; 24" THICH CONCRETE CAP; CHIPPED TOP OF CAP 10" TO MAINTAIN FLOW LINE AFTER MAT IS PUMPED PER ENGINEER GEORGE KARKAZIS
|  | 400 | 286.68 | [12 empty] | Steel/Wrought Iron |  |  | 7056627; DIST: RIO VISTA #7056627-07; L-400, M.P. 286.6732; L-400 M.P. 286.68; N 38 10.210'; W 121 48.486'
|  | 400 | 297.9 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L- 400, M.P. 297.9 CONCRETE WIEGHTED
|  | 400 | 298.16 | [15 empty] | 42" CASING EXPOSED EXTERNAL INSPECTION ONLY TO CASING
|  | 400 | 297.86 | [12 empty] | Steel/Wrought Iron |  | ANTIOCH | L400 M.P. 297.88, SO# 7038466, SO# 7029705; LINE 400 AT CCPP +/- 1/4 MILE NORTH WILBER AVE. ANTIOCH, CONTRA COSTA COUNTY; WRAP NOT TESTED THIS PROJECT WRAP WAS TESTED LAST YEAR ON SO 7030008, WHICH WAS LOCATED +/- 1/4 MILE SOUTH. SAMPLE SHOWED ASBESTO'S
|  | 400 | 297.8 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-400 M.P.-297.8, CONCRETE WEIGHTED
|  | 400 | 298.29 | [12 empty] | Steel/Wrought Iron |  | ANTIOCH | SO# 7030008-00, RT 400, M.P. 297.29; ANTIOCH CONTRA COSTA COUNTY
|  | 400 | 298.18 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ROUTE 400, M.P. 298.18L DIABLLO DIV.; CASING EXPOSED (STEEL) 42" LINE 400 NOT EXPOSED M.P. 298.18, WILBUR AVE.
|  | 401 | 42 | 42 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | COUPON INSTAL M-42 L-401; VERSIONS A-FORM ...400/401 COUPON.;...
|  | 400 | 51.05 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | COUPON INSTALL M-51.05 L-400
|  | 400 | 42 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | COUPON INSTALL M-42 L-400
|  | 400 | 121 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | COUPON INSTALL M-121 L-400
|  | 400 | 0.0094 | 2.37 | Transmission | [10 empty] | Steel/Wrought Iron |  | ANTIOCH | DISTRICT LOS MEDANOS, 30756166-10; DRIP 7995, M.P. 0.0094, 11 OF 16; REPAIR TAPS L400A 36" DRIP GATEWAY POWER PLAND CONTRA COSTA COUNTY NEAR ANTIOCH
|  |  | 0.0114 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7056191, ROUTE BD9140, M.P. 0.0114; JOB 7056191. SEE AS BUILT PRINT 4800578
|  | 400-2 | 142.62 | 26 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | SO# 7056191, ROUTE 400-2, M.P. 142.62;; JOB 7056191. SEE ASBUILT PRINT 4800578
|  | 400 | 142.5735 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#7056191, ROUTE 400 M.P. 142.5735; JOB 7056191. SEE AS BUILT PRINT 4800578
|  |  | 0.2877 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#7056191, ROUTE BD9150, M.P. 0.2877; INSTALL X-COMPRESSION FOR L-400 PIGGING PROJECT
|  |  | 0.5258 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#7056191, ROUTE BD9144 M.P. 0.5258
|  |  | 0.0264 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#7056191, ROUTE DB678, M.P. 0.0264; JOB#7056191 SEE AS BUILT PRINT 385637 REVS & 384938 REV S
|  |  | 0.0185 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#7056191 ROUTE DB9128, M.P.; SIE CRNR BURNEY COMP ST. - BURNEY. INSTALLED (1) 16X16X12 TEE & 12" STL PIPE. JOB #7056191.
|  | 400 | 82.3715 | 36 | [11 empty] | Steel/Wrought Iron |  |  | SO#7056191, ROUTE L-400, M.P. 82.3715; JOB#7056191 AS BUILT PRINT 4800577 REV2
|  | 400 | 82.38 | 36 | [11 empty] | Steel/Wrought Iron |  |  | SO#7056191 ROUTE L-400, M.P. 82.38; JOB# 7056191 AS BUILT PRINT 4800577 REV2
|  |  | 0.0095 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO# 7056191, ROUTE BD9134; M.P 0.0095; JOB# 7056191 SEE AS BUILT PRINTS 385637 REV2 & 384938 REV 2
|  | 400 | 298.87 | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLEY | RT = 400, M.P. 298.87...;
|  | 401 | 419.1444 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DISTRICT G300N; 30604380-10; L-401, M.P.-419.1444; GILL RANCH INTERCONNECT METER STATION.
|  | 401 | 82.368 | 42 | Transmission | [10 empty] | Steel/Wrought Iron |  | BURNEY | SO# 30603924, ROUTE 401; MP 82.3680; INSTALLED 42" PIG LAUNCHER @ THE BURNEY COMP. STA. WELDED 42" .625"W.T. TO EXSITING 42" .547" WT AT NORTH TIE-IN
|  | 401 | 82.33 | 42 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | GIS L-401, M.P. 82.33; AREA EXPOSED IS TO INSTALL TAP AND VAULT ON L-401 D/S OF SULFER ANALYZER BLDG. NEXT TO L-401 B/D
|  | 401 | 0.0355 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | BURNEY | SO# 30603924 ROUTE BD9872, M.P. 0.0355; INSTALLED 24" X 24" 12" TEE INTO THE 24" X500 W.T. 42" L-401 BLOW OFF TO BE USED IN CONJUNCTION WITH THE 42" PIG LAUNCHER INSTALLED IN L-401 @ THE BURNEY COMP. STA. INSTALLED 66' 8 3/4" OF 1275" O.D. X .375 W.T. STEEL PIPE. REF: PM#30603924 PRINT: 4800657 REV 1
|  | 401 |  | 36 | Transmission
|  | 401 | 149.1476 | 42 | Transmission | [10 empty] | Steel/Wrought Iron |  | GERBER | SO# 30603924, ROUTE 401, M.P.14914.76; INSTALLED 42" PIG RECIEVER ON L-401 GERBER COMP. STA.
|  | 401 | 149.154 | 42 | Transmission | [10 empty] | Steel/Wrought Iron |  | GERBER | SO#306039... ROUTE 401, M.P. 149.1540; INSTALLED 42" PIG RECIEVER ON L-401 GERBER COMP STA.
|  | 401 | 317.9784 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | BETHANY COMP. STA. INSULATING JOINT. PM...ROUTE 401, M.P. ....;PLEASE SHOW LOCATION
|  | 401 |  | 12.75 | Transmission | [13 empty] | BETHANY COMP. STA. 12" KICKER; PM# 30662486 ROUTE STA8376; PLEASE SHOW LOCATION
|  |  |  | 36 | Transmission | [13 empty] | SUCTION TEE; PM#30662486 BETHANY COMP. STA. ; PLEASE SHOW LOCATION
|  |  |  | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DISCHARGE TEE; PM# 30604141 BETHANY COMP. STA. ; PLEASE SHOW LOCATION
|  |  |  | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | BRIDLE; PM#30604141 BRTHANY COMP. STA. ; PLEASE SHOW LOCATION
|  | 401 | 83.3789 | 42 | Transmission | [10 empty] | Steel/Wrought Iron |  | BURNEY | SO#30603924, ROUTE 401, M.P. 83.3789; TIE-IN S/END OF 42" PIG LAUNCHER ON L-401. WELDED 42" .472" W.T. TO EXISTING 42" .407 W.T.; REF:PM 30603924; PRINT 4800657 REV 1
|  | 401 | 69.41 | [12 empty] | Steel/Wrought Iron |  |  | L-401, T-6941 SO#7031665. MCARTHUR PRIMARY REG STATION ; HYDRO TEST
|  | 401 | 69.38 | [15 empty] | ALL OK
|  | 401 | 68.13 | [12 empty] | Steel/Wrought Iron |  |  | L-401, T-68.13, SO#7031665; HYDRO TEST
|  | 401 | 68.38 | [12 empty] | Steel/Wrought Iron |  | GLENBURN | L-401, T-68.38, SO#7031665; HYDRO TEST
|  | 401 | 42.1652 | 42 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | COUPIN INSTALL M-42, L-401, 42.1652; L401 M.P. 42.1652, JOB70553752
| 00-40101-1 | 401 | 129.37 | 42 | Transmission |  | Unknown |  |  |  |  | 2000-03-13 | [5 empty] | REDBLUFF | COPY; DONE...3/25/00
|  | 401 | 242.85 | 42 | [14 empty] | JOB#7043036 42" LINE 401; RTE 401, M.P. 242.85 JOB#7043036 42" LINE 401, SO#7043036-05. ALL ELLS & TEE ARE ALL SOCKET WELD FITTINGS. BRIDAL SET ALL TESTED AS ONE UNIT.
|  | 401 | 317.9641 | 36.16 | Transmission | [10 empty] | Steel/Wrought Iron |  | BETHANY | SO#7052985, RT 401, M.P.317.9641
|  | 401 | 319.2328 | 36 | Transmission | [6 empty] | 2007-07-28 |  |  |  | Steel/Wrought Iron |  | BETHANY | SO#7066905, ROUTE 401, M.P. 319.2328; CUT OUT ANOMALIES NORTH LOCATION
|  | 401 | 325.48 | [14 empty] | TRACY | SEE BACK
|  | 401 |  | 42 | [11 empty] | Steel-Other |  |  | THIS IS A NEW TAP MP. 81.63 JUST NORTH OF BERNEY
|  | 401 | 80.94 | [12 empty] | Steel/Wrought Iron |  |  | L-401, T-80.94, SO#7031665
|  | 401 | 321.75 | 36 | [14 empty] | ROUTE-401, M.P.321.7351 & 321.7660; DRAWING ON BACK
|  | 401 | 325.67 | [15 empty] | L-401 AT GRAVEL RD IS 9' 8" T.O.P.
|  | 2 | 139.76 | [15 empty] | LINE 2 AT GRAVEL RD. IS 5' 8" T.O.P.
|  | 401 | 325.72 | [15 empty] | GPS FILE #R080308E; USA TICKET #279519
|  | 401 | 354.65 | 36 | [14 empty] | ROUTE 401, M.P....; SEE ATTACHMENT FOR SKETCH
|  | 401 | 332.0332 | 36 | Transmission | [6 empty] | 2007-07-26 | 2007-08-25 |  |  | Steel/Wrought Iron |  | TRACY | SO# 7066905, ROUTE 401; M.P. 332.0332; REMOVE ANOMALIES IN LINE 401 SOUTH END
|  | 401 | 122.06 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  | WESTLEY | SO#...; ROUTE L-401, M.P. 344.4979; EXPOSED TO LOCATE LINE FOR CLEARANCE OF NEW LINE 2 PIG RECEIVER
|  | 401 | 336.61 | 36 | [14 empty] | RT = 401, M.P. 336.6101; SEE BACK OF PAGE
|  | 401 | 354.68 | 36 | [14 empty] | ROUTE 401, M.P....;SEE ATTACHMENT FOR SKETCH
|  | 401 | 354.7 | 36 | [14 empty] | SEE ATTACHMENT FOR SKETCH
|  | 401 | 378 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  | SANTA NELLA | RT=401, M.P...., SO# 7042586-03
|  | 401 | 354.69 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  | PATTERSON | 401, M.P. 354.69 OAK FLAT STA. JOB 7050108
|  | 401 | 379.2 | 36 | [14 empty] | L-401; 401, M.P. 379.20; SEE BACK. WE HAVE 3 CROSSINGS, ONE STORM DRAIN, ONE WATER, AND ONE NON-POTABLE WATER. THE STORM DRAIN IS 30" CONCRETE PIPE. THE WATER LINES ARE 12" PLASTIC. THE BOTTOM OF DITCH FOR THE 30" CONCRETE PIPE WAS 13'6". THE BOTTOM OF DITCH FOR THE 12" WATER LINE WAS 10'6". THE BOTTOM OF DITCH FOR THE 12" NONPOTABLE LINE WAS 11". ALL THESE DEPTHS WILL CHANGE A PAVED ROAD WILL GO OVER THESE LINES.
|  | 401 | 417.76 | [12 empty] | Steel/Wrought Iron |  |  | L-401 M.P. 417.76. EXPOSED 12' WRAP IN EXCELLENT CONDITION 82" COVER 36" O.D. PIPE.
|  | 401 | 417.76 | [12 empty] | Steel/Wrought Iron |  |  | L-401 M.P. 417.76 EXPOSED 12" WRAP IN EXCELLENT CONDITION 82" COVER 36" O.D. PIPE
|  | 401 | 418.45 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-401, M.P. 418.45, SO#7039826-01
|  | 401 | 419 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-401,M.P. 419.00
|  | 401 |  | 16 | Transmission | [10 empty] | Steel/Wrought Iron | ; |  | L-401, RT=X, LODI GAS STORAGE METER STA. SO#7028045-02
|  | 401 | 42 | 42 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | COUPON INSTALL M-42 L-401
|  | 400 | 51.05 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | COUPON INSTALL M-51.05 L-400
|  | 400 | 42 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | COUPON INSTALL M-42 L-400
|  | 400 | 121 | 36 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | COUPON INSTAL M-121 L-400
|  | 0402-1 | 0.2197 | 12 | [11 empty] | Steel-Other
|  | 0402-01 | 0.2823 | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL | RT 0402-01, M.P. 0.2823
| 00-00553-1 | LINCOLN | 0.2879 | 16 | Transmission |  | Body of Pipe |  |  | Digin |  | 2000-08-17 | 2000-08-17 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SAN RAFAEL | DIG-IN REPAIR SLEEVE; RT 0402-01, M.P. 0.2879; PEDRO RD. 23' OFF P/L INSTALLED 18" LONG SLEEVE
|  | 0402-01 | 0.2909 | [12 empty] | Steel/Wrought Iron |  | SAN RAFAEL | DIG IN-NO DAMAGE? RT= 0402-01, M.P.0.2909; 2927-IS
| 00-00553-1 | LINCOLN | 0.2925 | 16 | Transmission |  | Body of Pipe |  |  | Digin |  | 2000-08-17 | 2000-08-17 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SAN RAFAEL | RT = 0402-01, M.P. 0.2925; ON 16" TRANS MAIN.; PEDRO RD. 23' OFF P/L -INSTALLED 18" LONG SLEEVE
40 | 78-00316-1 |  |  | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1978-06-27 | 1978-06-22 | Patch Welded |  | Steel/Wrought Iron |  | SAN RAFEL | RT= 0402-01, M.P. 0.491A; VENTED PATCH WELDED ON BY G.C. WELDER 44" N/E OF HPR TIGHTENED LEAKING SERVICE TEE CAP OF AN ABANDONED SERVICE. LARGE ROCKS ARE WEDGED AROUND THE MAIN. THESE ROCKS ARE LIKELY TO CAUSE FURTHER PROBLEMS
40 | 90-00076-1 | 0402-01 | 0.4969 | 12 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1990-01-22 | 1990-01-29 | Weld Over Sleeve or Can |  | Steel-Other |  | SAN RAFEL | INST'D 2" SAV-A-VALVE OVER CORROSION LEAK ON 12" DFM MAIN INST'D E.T.S.
|  | 0402-01 | 0.8381 | 16 | [7 empty] | 1989-05-03 |  |  |  | Steel-Other |  |  | TIE-IN LOCATION RT-0402-01, M.P. 0.8381; SO. TIE-IN ON GM 4529442
|  |  |  | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL | RT=02-01, M.P. 0.9385 MAG ANODES (2ES); INSTALLED 6-5 BOX FOR E.T.S. AND (2) 32# MAG ANODES.
|  | 0402-01 | 0.9745 | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL
|  | 0402-01 | 1.2082 | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL
|  | 0402-01 | 1.4506 | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL | JOB IN PRGORESS GM4432688
|  | 0402-01 | 1.9184 | 16 | Distribution Feeder Main | [6 empty] | 1987-03-26 |  |  |  | Steel/Wrought Iron |  | ; SAN RAFAEL | JOB IN PROGRESS GM 4432688
|  | 0402-01 | 2.0497 | 20 | Distribution Feeder Main | [6 empty] | 1987-03-26 |  |  |  | Steel/Wrought Iron |  | SAN RAFAEL | RT= 0402-01, M.P. 204.97
4 |  | 0402-01 | 2.1114 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN RAFAEL | ISNTALLED E.T.S. ON 16" LINCOLN AVE LINE AT 3RD AND LINCOLN AVE. CITY PAVED & 2' X 2' 3' SLAB FOR DIGNAL LIGHTS...TO 16" MAIN & E.T.S. LOCATION
|  | 0402-01 | 2.3144 | 16 | [11 empty] | Steel-Other |  |  | RT 0402-01, M.P. 2.3144; PUT CORAGATED PIPE AND MAIN
|  | 0402-01 | 2.3421 | [15 empty] | RT 0402-01, M.P 2.3421, L-21; PUT CORAGATED PIPE AROUND GAS MAIN
|  | 0402-01 | 2.4323 | 16 | [13 empty] | SAN RAFAEL | RT= 0402-01,M.P. 2.4323
|  | 0402-01 | 2.4403 | [14 empty] | SAN RAFAEL | DEPTH CHECK; RT 0402-01; M.P. 2.4403
|  | 0402-01 | 2.4789 | 16 | [11 empty] | Steel-Other |  | SAN RAFAEL | RT 0402-01, M.P. 2.4789; CAD WELDED 2 #10 WIRES ON 16" MAIN FOR RECTIFIER
| 98-00162-1 |  |  | 16 | Distribution Feeder Main |  | Longitudinal Weld |  |  | Construction Defect |  | 1998-04-22 | 1998-06-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SAN RAFAEL | WELDED CAN OVER PIPE
|  | 0402-01 | 2.6342 | 10.75 | [14 empty] | RT= 0402-01, M.P. 2.6342; REMOVED VALVE
|  | 0402-01 | 5.3932 | 16 | [11 empty] | Steel-Other |  | LARKSPUR | RT 0402-01, M.P.5.3932
|  | 402 | 20.75 | [12 empty] | Steel/Wrought Iron |  |  | SO#7045148, ROUTE L-402, M.P. 20.75; INSTALLED NEW 2" T-2074 ON L-402
|  | 402 | 22.53 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | REDDING | L-402, M.P. 22.53
|  | 402 | 24.86 | 10.75 | [8 empty] | 2002-02-08 | Other | FILED CLEAN |  |  | REDDING | RT=402, M.P. 24.86; FILED EDGESS CENTER OF GOUGE REMOVED APPROX .001" OF METAL STAC WRAPPED 5' OF PIPE
|  | 402 | 32.8 | 10.75 | Transmission | [7 empty] | 2001-04-16 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | SHASTA LAKE CITY | L-402; M.P. 32.80; SO# 7004453-01; WHILE DIGGING TIE-IN HOLE CREW FOUND NICK IN 10" T.P. MAIN; WHILE EXCAVATING TIE-IN HOLE. CREW FOUND DAMAGE TO 10" L-402
|  | 0402-01 |  | 12 | [11 empty] | Steel-Other |  | SAN RAFAEL
| 84-00201-1 | 0402-05 | 0.026 | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1984-06-07 | 1984-06-14 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | SAN RAFAEL | INTGR LINCOLN PALOMF S/E CORNER NEXT CURB; RT 0402-05; M.P. 0.0260; WELD PATCH ON 8" T.P. MAIN 6-13-84
|  |  | 180.33 | 6.62 | Service | [10 empty] | Steel/Wrought Iron |  | CONCORD | SO#9713860; CONTRA COSTA COUNTY SEWER DISTRICT CONCORD: CONTRA COSTA COUNTY
|  | SP3 | 171.9828 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ROUTE....MP.171.9828; #1 AFORM PER GPS PRINTS STANPAC 3. APPROX M.P. 172.0; USE GPS FILE R072621A
|  | SP3 | 171.9958 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ROUTE=SP3; M.P. 171.9958; #2 A FORM PER GPS POINTS STA-PAC 3
|  | SP3 | 172.0203 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ROUTE SP3, M.P. 172.0203; #3 A FORM PER GPS POINTS STAPAC 3
|  | SP3 | 172.039 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ROUTE SP3; MP. 172.0390; #4 A FORM PER GPS POINTS STA PAC 3
|  | SP3 | 172.1015 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ROUTE SP3, M.P.172.1015; #5 A FORM PER GPS POINTS STANPAC3
|  | SP3 | 172.1306 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ROUTE SP3; M.P. 172.1306; #6 A FORM PER GPS POINTS STANPAC3
|  | SP3 | 173.9 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SP3, M.P. 173.9; REWRAPPED ABOUT 6' OF SP3 WITH STAC WRAP OVER EXISTING WRAP. INSTALLED TEST LEADS, REFERENCE CELL AND BONDING CABLE ON SP3. M.P. 173.9 APPROX. THIS CROSSING IS ON THE CONTRA COSTA CANAL RD. ON THE NORTH SIDE OF CANAL, WE HAVE A SPAN ON SP3 AT THE CANAL AT THAT LOCATION
|  | SP3 | 174.47 | [15 empty] | SP3. M.P. 174.0656; POT HOLE (GPS M.P. 174.0650)
|  | SP3 | 174.47 | [15 empty] | SP3 M.P. 174.0509; POT HOLE
|  | SP3 | 174.46 | [15 empty] | SP3, M.P. 174.0329; POT HOLE (GPS 174.0329)
|  | SP3 | 174.45 | [15 empty] | SP3, M.P. 174.0098; POT HOLE (GPS M.P. 174.0098)
|  | SP3 | 174.44 | [15 empty] | SP3., M.P. 197.9844; POT HOLE (GPS M.P. 173.9844)
|  | SP3 | 174.4 | [15 empty] | SP3, M.P. 173.9678; POT HOLE (GPS 173.9678)
|  | SP3 | 174.42 | [15 empty] | SP3 M.P. 173.75.05 ( GPS m.P. 173.7505)
|  | SP3 | 174.91 | [15 empty] | SP3, M.P.173.9269; POT HOLE (GPS M.P. 173.9269)
|  | SP3 | 176.1485 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ROUTE SP3, M.P. 176.1485; 26" SP3
|  | 214 | 0.00 TO 0.0218 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | CONCORD | LOS MEDANOS (BANSHEE #1RP); PM 30604371-09; L-214, M.P. 0.00-0.0218; SRC RTE SR3 M.P. 176.75; SP3 M.P. 176.76 LOCATION +/- 2/10 MILE WEST OF WILLOW PASS RD & +/- 1/2 MILE NORTH OF EVORA RD. CONCORD AREA; CONTRA COSTA COUNTY
|  | SP3 | 182.75 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | MARTINEZ | SO#9704960, ROUTE SP3; M.P. 182.75; SP3 PACHECO BLVD. ; MARTINEZ CONTRA COSTA COUNTY. COULD NOT VERIFY SEAM BECAUSE TOP OF PIPE WAS ONLY EXPOSED.
|  | SP3 | 183.95 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | MARTINEZ | SO#9704960 ROUTE SP3, M.P. 183.95; SP3 ON SHELL AVE; MARTINES CONTRA COSTA COUNTY
|  | SP3 | 193.72 | [12 empty] | Steel/Wrought Iron |  |  | SP3; M.P. 193.72; 1861 CANYON DR. PINOLE
|  | SP3 | 195.37 | [12 empty] | Steel/Wrought Iron |  |  | SP3 MP 195...; 3220 BLIME DR. RICHMOND
|  | SP3 | 197.4 | [12 empty] | Steel/Wrought Iron |  |  | SP3, M.P. 197.40; MISSION BELL DR. & COLLEGE LN. SAN PABLO
|  | SP3 | 198.66 & 198.55 | 16 | Transmission | [12 empty] | SAN PABLO | RT SP3; M.P.198.66 & M.P. 198.55; SO#7043671
|  | SP-3 | 198.05 | 6.625 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN PABLO | SO# 9706800, ROUTE BD8916, M.P. 0.0008; TIE-IN FOR SP-3 ILI PROJECT # 9706800
|  | SP3 | 5.78 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#9706800, ROUTE SP3; M.P. 167.4455; WELD ON AND TAP OUT M/2 2" SAVE- A- VALVE
|  | SP3 | 176.1479 & 176.1388 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  | CONCORD | SO# 9706800, ROUTE SP3; M.P. 176.1479 & 176.1388; LINE SP3 AT LOS MEDANOS PRESSURE LIMITING STATIOON EAST SIDE OF YARD CONCORD; CONTRA COSTA COUNTY
|  | SP3 | 176.1861 & 176.1834 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | CONCORD | SO#9706800, ROUTE SP3, MP 176.1861 & 176.1834; LINE SP3 AT LOS MEDANOS PRESSURE LIMITING STATION WEST SIDE OF YARD CONCORD; CONTRA COSTA COUNTY
|  | SP3 | 180.83 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | MARTINEZ | SO# 9706800, ROUTE SP3, M.P. 180.8204; EXPOSED DRIP 7974 FOR SP3 ILI PROJECT
|  | SP3 | 191.15 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | HERCULES | SP#9706800 ROUTE SP3, M.P. 191.3186; WELD ON AND TAP OUT 2" SAVE A VALVE (SNIFF HOLE LOCATION) FOR SP3 ILI #9706800
|  | SP3 | 191.15 |  | Transmission | [10 empty] | Steel/Wrought Iron |  | HERCULES | SO# 9706800 ROUTE SP3, M.P. 191.6231; REPLACE VALVE M-20 WITH A NEW WELD-IN 4" BALL VALVE ANSI 300 AND A NEW WELD IN INSULATED FITTING ANSI 300; SP3 ILI#9706800 4" PIPE API 5L GR X 42 ERW 0.156"
|  | SP3 | 191.15 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | HERCULES | SO#9706800 ROUTE SP3 M.P. 141.7600; WELD ON AND TAP OUT 2" SAVE-A-V-ALVE
|  | SP3 | 192.82 | 24 | Transmission >= 20% SMYS | [10 empty] | Steel/Wrought Iron |  | HERCULES | SO#9706800, ROUTE SP3, M.P. 192.8567 TIED-IN 24" PIPE AND WELD ON AND TAP OUT 2" SAVE-A-VALVE SP-3 ILI #9706800
|  | SP-3 | 193.06 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PINOLE | SO#9706800 ROUTE SP3 M.P. 193.0833; TIED IN 24" PIPE AND WELD ON AND TAP OUT 2" SAVE-A-VALVE
|  | SP-3 | 194.2 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PINOLE | SO#9706800 ROUTE SP3, M.P. 193.9231 & 193.9420; INSTALL 2" SAVE-A-VALVE (SNIFF HOLE) HYDRO TEST SP3 #9706800
|  | SP-3 | 194.2 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | PINOLE | SO#9706800, ROUTE SP3, M.P. 194.1460 & 194.1643; INSTALL 2" SAVE-A-VALVE (SNIFF HOLE) W/S OF TIGHT OF WAY HYDRO TEST E/S OF RIGHT WAY SP3 ILI #9706800
|  | SP-3 | T196.30 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | RICHMOND | SO#9706800, ROUTE SP3, M.P. 196.4594 & 196.4703; HYDRO TEST #3 SP3 ILI PROJECT
|  | SP-3 | T196.30 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | RICHMOND | SO#9706800 ROUTE SP3, M.P. 196.6198 & 196.6205; CUT OUT 36" CAN, FOR THE PURPOSE OF LOCATION THE 24" POLY PIG WITH A ROBTIC CAMERA
|  | SP-3 | T196.30 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | RICHMOND | SO#9706800, ROUTE SP3 M.P.196.9141; CUT 41" CAN TO RETRIEVE 24" POLY PIG FROM 24" 90 DEG. ELBOW
|  | SP-3 | T196.30 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | RICHMOND | SO#9706800 ROUTE SP3, M.P. 197.0713; HYDRO TEST #3 SP3 ILI PROJECT #9706800
|  | SP-3 | 198.05 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN PABLO | SO#9706800 ROUTE SSP3, M.P. 198.4873; TIE-IN FOR SP3 ILI PROJECT #9706800
|  | SP-3 | T196.30 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | RICHMOND | SO#9706800 ROUTE SP3 MP196.8255; CUT OUT 60" CAN, DUE TO LOCATING A DENT ON THE BOTTOM OF THE 24" PIPE.
|  | SP-3 | 198.05 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  | SAN PABLO | SO#9706800 ROUTE SP3, MP 198.4882; TIE-IN FOR SP3 ILI PROJECT # 9706800
|  | SP3 | 179.3 | 8.65 | Service | [10 empty] | Steel/Wrought Iron |  | CONCORD | PM#6107143, GCLLST 5740 SP3 M.P 178.3; TESORO REFINERY GAS METER SET # SP3 MP 179.3 CONCORD; CONTRA COSTA COUNTY
|  | SP3 | 180.98 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SP3, M.P. 180.98; FROM MIKE WEST 10/27/10 MAPPED 10/28/10;; LINE SP3 DIG#4 MP 80.98; LATIT 38 00 45.27415, LONG -122 06 59.10764; ; MISC. COMMENTS/INFORMATION: THIS SITE IS LOCATED IN A SWAMP ABOUT HALF A MILE WEST OF THE INTERSECTION ON IMHOFF ROAD AND WATERBIRD WAY, THE DIG WAS INA SWAMP THAT HAD TO BE DAMNED OFF AND THEN HAD THE WATER PUMPED OUT OF THE DAMED AREA AND INTO A NEARBY FIELD. AFTER DRAINING THE WATER FROM THE SWAMP WE USED MATS TO GET THE EXCACATOR OUT INTO POSITION TOBEGIN DIGGIN, AFTER REVIELING THE PIPE THE ANOMALY WAS FOUND AT THE U/S EDGE BUT CONTINUED PAST THE COATING REMOVAL AREA SO THEN THE DIG WAS EXPANDED PER PG&E AFTER INSPECTION A GRID WAS SENT TO HAVE RSTRENG RAN ON IT AND IT PASSED, THE CONSTRUCTION CREW THEN CONTINUED BY INSTALLING FINK AND COUPON AND THE PIPE WAS COATED WITH WAXTAPE AND TUFF-N-NUFF. ON FINAL VOLT READING FROM COUPON THE CP WAS ONLY .645MV BUT IN THE HOLE I WAS GETTING READINGS OF 1.1 V, THE SITE WAS THEN BACKFILLED AND THE DAM TAKEN DOWN
|  | SP3 | 0.0137 | 8.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | CONCORD | DISTRICT LOS MEDANOS 9705420-10...M.P.0.0137; RYER ISLAND TAP TO SP3; LOS MEDANOS PRESSURE LIMITING STATION, LOS MEDANOS STORAGE FACILITES CONCORD; CONTRA COSTA COUNTY
|  | SP3 | 0.0185 | 8.62 | Transmission | [10 empty] | Steel/Wrought Iron |  | CONCORD | DISTRICT LOS MEDANOS 9705420-10; RTE RYERS (SP3) M.P. 0.0185; RYER ISLAND TAP TO SP3. LOS MEDANOS PRESSURE LIMITING STATION, LOS MEDANOS STORAGE FACILITIES, CONCORD; CONTRA COSTA COUNTY
|  | SP4Y | 3.82 | 12.75 | [14 empty] | JOB# 9703660-01 L-SP4Y, M.P. 3.82
|  | SP4Y | 3.81 | 12.75 | [14 empty] | JOB# 9703660-01, L-SPAY M.P. 3.81
| 01-00401-1 | SP4Y | 3.92 | 12.75 | Transmission |  | Body of Pipe |  |  | Atmospheric Corrosion | EXTERNAL CORROSION | 2001-08-01 | 2001-08-06 | Other | INSTALL PIPE |  |  | RIO VISTA | INSTALLED 58' 9 5/8" OF 12" PIPE; ISNTALLED 58' 9 5/8" OF 12" PIPE
|  | SP4Z | 8.71 | [14 empty] | ANTIOCH | INSTALLED E.T.S. PLACED A PVC AND FIBER TYPE MATERIAL TO ACT AS AN ELECTROLYSIS BARRIER.
|  | SP4Y | 3.82 | [9 empty] | 2004-06-28 | [5 empty] | RT SP4Y, M.P. 3.8100; NO LEAK FOUND (PITTING); AREA WAS SAND BLASTED AND COATED WITH POWER CRETE J; GPS 38 04 29.8, 121. 42 55.7; NO LEAK FOUND PITTING ON SPAN#5 PITTING WAS MAPPED OUT AND SETN TO DAVE AGUIAR FOR R-STRING CALCULATIONS
|  | SP4Z | 8.1795 | 12.75 | Transmission | [10 empty] | Steel/Wrought Iron |  | OAKLEY | DIST: LOS MEDANOS LINE SP4Y, M.P. 8.1795 SO#9707580-06; LINE SP4 LAURITEN HARBOR VALVE PIT +/- M.P. 8.18
|  | SP4Z | 8.78 | 8 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT SP4 2, M.P. 8.78
|  | SP5 | 1.13 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIST: LOS MEDANOS LSP5, M.P. 0.9776, M.P. 1.0063
|  |  | 0.0236 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ROUTE RYER, M.P. 0.0236; RYER SSL. 6"
|  | SP5 | 2.6721 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | ANTIOCH | DIST: LOS MEDANOS; SP5, M.P. 2.6721, SO# 9707380-06
|  | SP5 | 2.6817 | 24 | Transmission | [10 empty] | Steel/Wrought Iron |  | ANTIOCH | DIST: LOS MEDANOS, SP5, M.P. 2.6817, SO#9707380-06
|  | SP5 | 4.9153 | 30 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-SP5; M.P. 4.9153; ; ; LINE SP5 STA 151+39, M.P. 4.9153; LATIT 38 00 01.34580, LONG -121 49 42.35762; ; ANTIOCH MISC, COMMENTS/ INFORMATION: FOUND PIPE DEPTH OF COVER TO BE 7' THAN PROPOSED 18" DEPTH OF COVER. P/S READS FELL BELOW STANDARD -850 MV, FOUND READINGS TO AVERAGE OUT 5,2 PH U/S & 5.2 PH D/S. MINOR CORROSION FOUND, LESS THAN 10% WALL LOSS (DEEPEST PIT WAS 16 MILS). MINOR SURFACE RUST & CALCEROUS DEPOSITS FOUND. MANUFACTURE ROLL MARKS AT 3:00. WAX TAPED PER MIKE WEST, DOUBLE SPIRALLY WRAPPED;
|  | SP5 | 5.3 |  | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SP5, M.P. 5.30;; LINE SP5 STA 172+01; MP. 5.3032; LATIT 37 59 52.30510, LONG, -120 50 00.55293; ; CONCRETE CAP IS 6" THICK 12" WIDE X 80' LONG. PIPE DEPTH 33". DID NOT REMOVE COATING AND TAKE A P/S UNDER THE CONCRETE CAP. WE ONLY POTHOLED. I DID HOWEVER, READ THE TEST STATION WIRES RIGHT NEXT TO THE CONCRETE CAP AND THE READ WAS -0.750 VOLTS AS STATED BELOW
|  | SP5 | 5.775 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ROUT SP5, M.P. 5.7750; HOLE #3 SP3 DELTA FAIR SEE ATTACHED MAP
|  | SP3 | 167.3124 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ROUTE SP3 M.P. 167.3124; HOLE #2 SP3 DELTA FAIR SEE ATTACHED MAP
|  | SP3 | 167.3227 | 26 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | ROUT SP3, M.P. 167.3227; HOLE #1 SP3 DELTA FAIR SEE ATTACHED MAP
| 02-30101-1 | 301A | 0.01 | 20 | [7 empty] | 2002-04-03 | [5 empty] | HOLLISTER | GIS MILPITAS A FORMS L-301A, M.P. 0.01
|  | 301A | 0 | [12 empty] | Steel/Wrought Iron |  |  | GIS RT: 301A, MP 0.00, .002
| 02-30101-1 | 301A | 0.01 | 20 | [13 empty] | HOLLISTER | MIPLITAS A FORMS L-301A, M.P. 0.01
|  | 301A | 0 | [12 empty] | Steel/Wrought Iron |  |  | RT 301A, M.P. 000, .0028
|  | 301A | 0.7498 | 20 | Transmission | [13 empty] | DIST: HOLLISTER L301A, M.P. 0.7498
|  | 301A | 1.44 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | INSPECTION ONLY, NO LEAK; L 301A, M.P. 1.4365 JOB 7053486; SEE AS BUILT FOR SO#7053486
|  | 301A | 1.44 | [12 empty] | Steel/Wrought Iron |  | HOLLISTER | DIST: HOLLISTER, SO#7053486-06, L301A, M.P 1.4468
|  | 301A | 1.72 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  | HOLLISTER | DIST: HOLLISTER L301A, M.P. 1.7202
|  | 301A | 2.2441 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | GIS 301A, M.P.2.2441;; HOLLISTER LINE 301A, STA8+84, M.P. 2.2441; LATIT 36 51 47.82916, LONG 121 24 16.50612
|  | 301A | 2.2441 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 301A, M.P. 2.2441;; HOLLISTER LINE 301A STA 8+84, M.P. 2.2441; LATIT 36 51 47.82916, LONG 121 24 16.50612
|  | 301A | 4.41 | 20 | Transmission | [13 empty] | ....M.P.4.40
|  | 301A | 21.5 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  | ELKHORN | 301A, M.P.21.38, PM#30604215
|  | 301A | 21.5 | 20 | Transmission | [10 empty] | Steel/Wrought Iron |  | ELKHORN | 301A, M.P. 21.71, PM#30604215
|  | 301A | 24.03 | 20 | Transmission | [13 empty] | RT 301A, M.P. 24.03
|  | 301A | 23.95 | 24 | Transmission | [13 empty] | RT301A, M.P. 23.95
|  | 301A | 24.75 | 20 | Transmission | [12 empty] | MOSS LANDING | RT 301A, M.P. 24.75; ONLY 20" OF COVER LINE WAS EXPOSED IN DRAIN DITCH 5'11" FROM TOP OF PAVEMENT *SEE MAP*
|  | 301A | 20.4 | [12 empty] | Steel/Wrought Iron |  |  | RT 301A, M.P. 20.40; DONE WYL IIIIA;...
|  | 301A | 11.02 | [12 empty] | Steel/Wrought Iron |  |  | RT 301A, M.P. 11.02; AT ROAD...OF OLD SAN JUAN HIGHWAY
|  | 301A | 11.02 | 20 | [11 empty] | Steel/Wrought Iron
|  | 301A | 11.24 TO 11.45 | 20 | [14 empty] | 31A, L-301A M.P.11.24 TO 11.45, SO#70299....; LINE 301A BETWEEN M.P. 11.24 AND M.P. 11.45, 25 FEET OF MAIN EXPOSED AT TWO TIE IN LOCATIONS LIGHT RUST- WRAP BRITTLE- WRAP COLD FLOW CONDITION TO BOTTOM OF MAIN.
|  | 301A | 15.85 | [12 empty] | Steel/Wrought Iron
RT 301A, M.P. 21.4 |  | 301A | 21.4 | 20 | Transmission
|  | 301A | 24.75 | 20 | Transmission | [12 empty] | MOSS LANDING | RT 301A. M.P. 24.75; * SEE MAP *
| 97-00042-1 | 301B | 5.14 | 2.75 | Transmission |  | Body of Pipe |  |  | Digin |  | 1997-06-19 | 1997-06-20 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | CASTROVILLE | REPLACED 60' SECTION OF TRANSMISSION MAIN
| 02-50086-1 | 301B | 6.94 | 12 | Transmission |  | Body of Pipe |  |  | Digin |  | 2002-06-03 | 2002-06-04 | Replace TP Main |  | Steel/Wrought Iron |  | SALINAS | SO# 8053259.02, RT 301B, M.P. 6.94; AGRICULTURE RIPPED DIGS INSTO PIPE; REPLACED 15FT. OF PIPE W/ PRETESTED .375" GRB SMLS.
| 09-50425-1 | 301B | 6.91 | 12 | Transmission |  | Body of Pipe |  |  |  |  | 2009-10-23 | 2009-10-23 | Replace TP Main |  | Steel-Other |  | SALINAS | DIVISION: CENTRAL COST; 41208... L-301B, M.P. 0.91 4 OF 3; SHUT DOWN APPROX 8 MILE SECTION OF PIPE W/ VALVES. FARMER WAS RIPPING FIELD AND STRUCK A 12" STEEL TRANSMISSION LINE, CAUSING A HOLE 2" X 2 1/2". MARKERS HAD BEEN MOVED.
|  | 301B | 13.96 | [15 empty] | L-301B, M.P.0.00 TO 13.96; A FORM FOR BELLHOLE, INSPECTION (48) SO#8038157-02, SEE JOB FOLDER
|  | 301B | 9.41 | 12 | Transmission |  | Body of Pipe |  |  | Construction Defect |  |  | 2001-12-11 | Other | GRIND OUT PER S4134 | Steel/Wrought Iron |  |  | DUG UP PIPE BASED ON PIPE COMP. SURVEY.; REPAIR MADE BY GRINDING OUT THE PIT PER S4134. TABLE I-D AND PARAGRAPH IV-F. GRIND LENGTH WAS 1.5 INCHES AND CIRCULAR TOTAL GRIND PATTERN. MAX ALLOWABLE GRIND OF 2.57 INCHES PER EQUATION. PIT WAS MAGNETIC PARTICL MEASURED EXAMINED BEFORE AND AFTER REPAIRS, BOTH NEGATIVE. FINAL GRIND DEPTH OF .060 MEASSURED BY PIT SAGE BECAUSE U.T. GAVE FALSE READING DUE TO CONTOUR GRIND. REPAIR APPROVED BY T.R.H. VERBAL
| 08-50091-1 | 301C | 13.85 | [8 empty] | 2008-11-21 | [5 empty] | SALINAS | 301C, T, CT, GIS, M.P.13.63
|  | 189 | 1.72 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DIVISION:NORTH COAST 30609001-09; L 189, M.P. 1.72; HUMBOLT BAY....; INSIDE HB PP NEW GEN.; INSPECTION LOCATION AT 10" TOW SPHERICAL SIDE OUT
|  | 190 | 6 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-190, M.P. 6.00
|  | 190 | 7.73 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-190, M.P. 7.73; L190, M.P. 7.73
|  | 190 | 8.2917 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT= 190, M.P 8.2917; L-190 BYPASS FEED TO...
|  | 190 | 9.0302 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-190, SO# 7056786-05, M.P. 9.0302, (G300N) PASAJERO CREEK; COUGE WAS REPAIRED BY KETTLEMAN DIST.
| 99-19301-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-01-05 | 1999-09-30 |  |  | Steel/Wrought Iron |  | KIRKWOORD | ISOLATED AND BLOWN DOWN. AWAITING SEASONAL STREM TO BECOME DRY AND AWAITING PRODUCER PAYMENT FOR REPAIRS, TO BE RETIRED; WELDED 5' OF TESTED PIPE TO REPAIR LEAK. PIPE LINE NOT TO BE ACTIVE. NO X-RAY NO 100 SOAP TEST LINE TO BE RETIRED AT LATER DATE; PIPELINE WILL BE RETIRED. ENGINEERING PREPARING A FORMAL JOB FOR RETIREMENT
| 99-16900-1 | [16 empty] | KIRKWOOD | 6" L-169 PARALLEL TO 10" L-177 GATHERING LINE IN RICE CREEK FIELD
| 99-19301-1 |  |  | 6 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 1999-01-05 |  |  |  | Steel/Wrought Iron |  | KIRKWOOD | 6" L-193 PARALLEL TO 10" L-177; GATHERING LINE IN RICE CREEK FIELD BETWEEN VALVES #13, & #15; ISLOATED AND BLOWN DOWN, AWAYITING SEASONAL STREAM TO BECOME DRY AND AWAITING PRODUCER PAYMENT FOR REPAIRS
|  | 193 |  | 6.25 | [8 empty] | 2001-05-18 |  |  | Steel-Other |  |  | ROUTE...SO#6080623-01; CUT & CAP TO ABANDON 181 HARSIN GAS WELL
|  | 193 |  | 2 | [11 empty] | Steel-Other |  |  | L-193 ROUTE 193-025; 6084744-01
|  | 193 |  | 3 | [14 empty] | L-193 ROUTE 193-002, SO#6074224-01, MERIDIAN DISTRICT
|  | 193 | [10 empty] | 2001-08-22 |  |  |  |  | ORLAND | 193-0...SO#6088106-01, HEATH 10-1 WELL
|  | 195 |  | 6.625 | [11 empty] | Steel/Wrought Iron |  | RIO VISTA | JOB# 6082243, DETAIL 4, L-195 GG. RIO VISTA
|  | 195 |  | 4.5 | [11 empty] | Steel/Wrought Iron |  | RIO VISTA | JOB# 6082243, CUT OFF AT TEE TO WELL # FEE #8, L-195 RIO VISTA;
|  | 195 |  | 6.625 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 6082243 CROSS TIE LOCATION DETAIL #1. PIPE FROM PETER COOK #6
|  | 195 |  | 6.625 | [11 empty] | Steel/Wrought Iron |  | RIO VISTA | JOB#6082243, DETAIL #2, AT VALVE 62; L-195 RIO VISTA; REMOVED 56" OF 6".156 WALL
|  | 195 |  | 8.625 | [11 empty] | Steel/Wrought Iron |  | RIO VISTA | JOB# 6082243 DETAIL #3 AT 8" TEE TO 5" LINE; L-195 RIO VISTA
|  | 195 |  | 6.625 | [11 empty] | Steel/Wrought Iron |  | RIO VISTA | JOB#6082243 CROSS TIE LOCATION DETAIL #1 PIPE FROM PETER COOK #7; L-195 RIO VISTA
|  | 193 | 0 | [12 empty] | Steel/Wrought Iron |  |  | JOB# 7044031 RT= 193-048, M.P.0.00
|  | 193 | 0 | [12 empty] | Steel/Wrought Iron |  |  | JO# 7041398-02, RT= 193-050, M.P. 0.00
|  | 193 | 0.4 | [15 empty] | SO#7042447-02, RT=193-058, M.P. 0.40; C/O...LINE
|  | 193 | 0.01 | [15 empty] | SO#7042507; RT-193.019, M.P. 0.01; CUT & CAP...LINE...
|  | 193 | 0.32 | 6 | [11 empty] | Steel-Other |  | MERIDIAN | SO#6080405, RT 193-015, M.P. 0.32 MERIDIAN
|  | 193 | 0.59 | [12 empty] | Steel/Wrought Iron |  |  | SO#7043685-03, RT= 193-035, M.P. 0.59
|  | 193 | 0 | [12 empty] | Steel/Wrought Iron |  |  | SO# 7043685-03, RT 193-035, M.P. 0.00
|  | 193 | 0 | [12 empty] | Steel/Wrought Iron |  |  | SO# 7043685, RT 193-037. 3" CUT & CAP SAUR.
|  | 193 | 0.0002 | [15 empty] | SO#7046853-03, RT =193-063, M.P. 0.0002
|  | 193 | [16 empty] | C.O AT ROAD TO RETIRE 12-1 & LEAK. UPRATED 6" TP. PRESURE TO FEED HIGH TO HIGH SET
|  | 193 | [13 empty] | Steel/Wrought Iron |  |  | SO#704495.. ROUTE 193-016, M.P. 0.5...
|  |  | 0.2637 | [12 empty] | Steel/Wrought Iron |  |  | SO#7044989...M.P. 0.2637
|  | 193 | 0.375 | [12 empty] | Steel/Wrought Iron |  |  | SO#7044989 ROUTE 193-017, M.P.....
|  | 193 | 0.297 | [12 empty] | Steel/Wrought Iron |  |  | SO#7044987, ROUTE 193-024, M.P. 0.2970
|  | 193 | [16 empty] | SO#7050695 ROUTE 193-013, M.P....; C/O AT ROAD TO RETIRE 12-1...
|  | 193 | 22.1565 | 10.75 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | DISTRICT MERIDIAN; L-193-068; SOURCE RTE L-177A; SOURCE M.P. 22.1565; DF8154, L-193-068; CONNECT VICTOR RANCH #18-8 SO#7052685-05
|  | 193 | 0.0392 | 3 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | DISTRICT: MERIDIAN SO#7066230-07; (L-193)(DFM 1004-11) GG., SUB8913, M.P. 0.0392
|  | 193 | 0 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  | MERIDIAN | MERIDIAN; SRC ROUTE 193-003, SRC MP.0.0000; ROUTE SUB 10043, ROUTE M.P. 0.000; JOB# 30669260-09; FOR MAPPING ARCHIVE "RAYS FILE"
|  | 193 |  | 4 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | 30693867, RT 193-07, M.P....; SOAP TESTED WELD @ 100 PSI OK @ V-36
|  | 193 |  | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | 30693867, RT 193-016, M.P...; SOAP TESTED TIE-IN WELDS @ 100 PSI, OK
|  | 194 | 0.0027 | 4 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | SO#7063588-06 DIV STOCKTON; L-194, M.P. 0.0027
|  | 194 |  | 6.04 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | LAKE CLASSY GRASS MCMULKIN RANCH WELL33-24; SO#7045690, ROUTE 194, M.P....
|  |  |  | 4 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | HAYS ROAD, WELL 87X; SO#7045690, ROUTE....
|  |  |  | 6 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | BOYCE PROPERTY- NILE ROAD
|  | 192 | 0.0149 | 6 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | CORNER OF AIRPORT WAY & MCMULKIN ROAD; SO#7045690-...ROUTE L... (GATHERING), M.P. 0.0149
|  |  | 0.0004 | 2.02 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | MCMULKIN ROAD, MCMULLIN WELL 2Y; SO#7045690, ROUTE ..., M.P. 0.0004
|  |  | 0.0004 | 3 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | MCMULLING ROAD, WELL MCMULLIN #3; SO#7046590...ROUTE, .... M/P/ 0.0004
|  |  | 0.0004 | 2 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | MCMULLING ROAD, MCMULLING WELL 22-25; SO#7045690, ROUTE..., M.P. 0.0004
|  |  | 0.0004 | 6 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | MCMULLING ROAD, WELL 33-25, MCMULLING, SO#70456...
|  | 194 | 1.52 | [15 empty] | 194...
|  | 195 |  | 4 | Gathering | [10 empty] | Steel/Wrought Iron |  | RIO VISTA | PM 7054811; REEDWOOD BOX REPLACED AND EMS MARKER AVOVE 36" DROP BOX
|  | 195-092 |  | 16 | Gathering | [6 empty] | 2005-05-12 | [5 empty] | RIO VISTA; | RIO VISTA; DAMAGE ONLY, L115-092, M.P....; NO LEAK GOUGE ONLY; BUFFED COUGES SMOOTH PARIMOR DEPTH .0215 & .0205
| 99-00001-1 | 195 |  | 6 | Gathering |  | Body of Pipe |  |  | Damage by 3rd Party |  | 1999-04-16 |  | ABANDON |  | Steel/Wrought Iron |  | ISLETON | LINE WAS ISOLATED AND WILL BE RETIRED/ ABANDONED
|  | 195 |  | 6.62 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 6088923, 6 WEST SIDE HIGHWAY 160 AT 10" CROSSING; DEACTIVATED PIPE NOT POSTED; RT 195A4-2
|  | 195 | [13 empty] | Steel/Wrought Iron |  |  | ERT 195A4-2; JOB# 6088923, 10" MAIN WEST SIDE HIGHWAY 160. DEACTIVATED PIPE.
|  | 195A4-6 |  | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | RT L-195A4-6; JOB# 6088423 REC BOARD 7 CUT OFF; DEACTIVATED PIPE NOT POSTED
|  | 195A4-2 |  | 10.62 | [11 empty] | Steel/Wrought Iron |  |  | RT 195A4-2; JOB#6088923, 10" MAIN EAST SIDE HIGHWAY 160; DEACTIVATED PIPE NOT POSTED
|  | 195A4-2 |  | 6.62 | [11 empty] | Steel/Wrought Iron |  |  | RT L-195A4-2; JOB#6088923; 6" EAST SIDE OF HIGHWAY 160 AT 10" CROSSING
| 01-19501-1 | 195 |  | 8 | Gathering |  | Other |  | GASKET LEAK | Material Failure |  | 2001-02-07 | 2001-02-28 | Other | NEW GASKET |  |  | RIO VISTA | REPLACE NEW GASKET AND BOLTS IN 8" FLANGE; REPLACED GASKET AND BOLTS
|  | 195 |  | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | JOB#6021544 UPMAIN #3 GAS WELL RISER; L-195, ROUTE 195B8-1
|  | 195 |  | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 6021544 UPMAIN #3 GAS WELL FS 25+6B AT CUT OFF LOCATION; L-195, ROUTE 195B8-1
|  | 195 | 1.06 | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | CUT OFF POINT FOR REC BOARD 10; JOB# 6088923 DETAIL #2; L195A4-2, M.P. 1.06
|  | 195 | 1.73 | 3.5 | [11 empty] | Steel/Wrought Iron |  |  | DETAIL 4, JOB# 6088923; L-195A4-2, M.P. 1.73
|  | 195 | 0 | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | DETAIL 5, JOB#6088923; L-195A4-5, M.P. 0.0
|  | 195B8-4 | 0.25 | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | DETAIL JOB# 6088923; L-195B8-4, M.P. 0.25
|  | 195B8-4 |  | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | JOB#6088923 DETAIL 3; L195B8-4, M.P. 0.25
|  |  | 0 | 4.5 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 6088923 CUT OFF POINT OF REC BOARD 3, DETAIL 7; L-STUB, M.P. 0.00 ( NEAR L131, M.P. 0.44, L-195-008, M.P. 0.00
|  | 195 | 3.49 | 12.75 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 8043222 DCVG PRIOR -1...VTM83 620086, 4223316; RT 195, M.P. 3.49; VERY SHALLOW PIPE AND EXPOSED IN DITCH; SERVICE TEE MALEABLE CAP 3/4" STUB SMASHED FLAT AT END ALET WELDED 12" LONG CURVED UP; SEE ATTACHED PHOTO; NOTE: HOME MADE SERVICE TEE CONCRETE BLOCK POURED AROUND IT PER BRIAN MCCOY
|  | 195 | 4 | 12.75 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 8043222; DCVG. PRIOR-O...UTM83 620786, 4223725; RT 195, M.P. 4.00; SOMSTIC PIPE WRAP APPEARED TO BE IN EXCELLENT SHAPE IN THIS AREA, NO HOLIDAYS CRACKS OR NILES
|  | 195 | 6.66 | 12.75 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 8043222 DCVG PRIOIR; RT 195, M.P. 2.66; RT 195A3-2.0, M.P. 0.11; TAR WRAP APPEAR IN FAIR CONDITION FOR ARE FOUND NO LEAK PROBLEMS
|  | 195 | 0.51 | 16 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 8043222 DCVG PRIOR-0...UTM83, 66007, 4222542; RT 195-1, M.P. 0.51; VERY SHALLOW PIPE THIS LOCATION DCVG PRIOR-O...UTM83 616007, 4222542
|  | 195A7-2 | 0.77 | [12 empty] | Steel/Wrought Iron |  |  | JOB 7042378 AT TIE-IN POINT VALVE 229; RT 195A7-2, M.P. 0.72; WAITING FOR PLSS....
|  | 195A7-2 | 0.27 | 6.62 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 704029 DONE #1; ROUTE 195A7-2, M.P. 0.27
|  | 195A4-2 | 1.33 | 3.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB#7041024...; ROUTE 195A4-2, M.P. 1.73
|  | 195A4-2 | 1.08 | 6.62 | [11 empty] | Steel/Wrought Iron |  |  | JOB#7041029 DETAIL #2; STUB...OFF L-195A4-2, N.P. 1.08
|  | 195A7-2 | 0.05 | 6.62 | [11 empty] | Steel/Wrought Iron |  |  | JOB#704...DETAIL #3; ROUTE 195A7-2, M.P.0.05
|  | 195B8-5 | 0 | 8.62 | [11 empty] | Steel/Wrought Iron |  |  | JOB#7041029 DETAIL 3, SECTION OF 8 RETIRED & REMOVED; ROUTE 195B 8.5, M.P. 0.00
|  | 195B8-4 | 0.5 | 8.62 | [11 empty] | Steel/Wrought Iron |  |  | JOB#7041029 DETAIL 4; ROUTE195B8.4 MP 0.50
|  | 195-081 | [13 empty] | Steel/Wrought Iron |  |  | SO#7043532 ROUTE 195-081 (DEACTIVATED GATHERING PIPE)
|  | 195 | 0 | [12 empty] | Steel/Wrought Iron |  |  | SO#7043532, RT 195-081, M.P. 0.00
[16 empty] | Steel/Wrought Iron |  |  | SO#70435...ROUTE ... ABANDON PIPE.
|  | 195-089 | [13 empty] | Steel/Wrought Iron |  |  | SO#7043532, ROUTE 195-089(DEACTIVATED GATHERING PIPE)
| 04-19502-1 | 195A-3-1 |  | 6.625 | Transmission | TO DIST REG | Body of Pipe |  |  | Internal Corrosion |  | 2004-08-13 | 2003-08-12 |  |  | Steel/Wrought Iron |  | ISLETON | INSTALLED 4' OF .188 WALL API5LX42ERW PIPE AND 7 DEG. ANGLE. 1" SAV-A-VALVE ROLLED 45 DEGREES TO NORTH.
|  | 195 | 0.0445 | [9 empty] | 2004-03-11 | Other | A SLEEVE |  |  |  | ROUTE 195-058 GG. M.P. 0.0445; INSTALLED 2 "A" SLEEVES TO COVER DENTS IN LINE; GPS FILE #R138207B SSF; INSTALLED 2 6" "A" SLEEVES TO COVER DENTS IN LINE
|  | 195 |  | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | 2009295 INSTALL A TYPE SLEEVES 6" LINE 195; INSTALLED 2ES 6" "A" TYPE SLEEVES. SEE ATTACHED SLEEVE HF4 PAPERS W/ SPECS. BONDED A SLEEVES TO MAIN WITH #10 WIRE CAD WELDED. GPS FILE #R1302078.SSF; A SLEEVE #0101 COVERING 2 DENTS. A SLEEVE #0103 COVERING 1 DENT
|  | 195-088 |  | 6.25 | Gathering | [13 empty] | JOB#7048367 LOC#1 ALSO LOC #3 JOB #8056739; 7048367-04 L-195-088
|  | 195-088 |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB#8056734 LOC #3 JOBE # 7048367 LOC #1; 7048367-04 STUB 8125 (L195-088); LOC #1
|  | 195 | 0.0004 | 3.5 | Gathering | [13 empty] | JOB#8056739 LOC#8 ALSO JOB #7043867 LOC#2, SO#7048367-04, L-195, STUB8117, M.P. 0.0004
|  |  | 0.0003 | 6.625 | Gathering | [13 empty] | JOB #8056739 LOC#3 AT VALVE 91. ALSO JOB 7048367 LOC #3. GRVI, SP-STUB8115, M.P. 0.0003 4Z. SO#7048367-04
|  |  | 0.0005 | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB 8056739 LOC#13 AT VALVE 94 ALSO JOB 7048367 LOC#. SO#7048367-04. GRVI. SP-STUB8116, M.P. 0.0005
|  | 195A | 0.6116 | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 7048367 LOC4 ST RISER WILCOX 7 GAS WELL L-195A4-7, M.P. 0.6116, SO# 7048367-04; GRVI; UNABLE TO REMOVE TOTAL RISER DUE TO CALPINE EQUIPMENT ON WELL PAD. HAND DUG DOWN 24" AND CUT OFF AND REDWOOD PLUGGED
|  | 195-1 | 0.1804 | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | GRVI; JOB# 8056739, 7048367, LOC4 AT VALVE 52 L-195-1, STUB 8118 M.P. 0.1804, SO# 7048367-04
|  | 195 |  | 8.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 7048367 LOC#6 AT VALVE 134 SOUTH END OF PIT; RTE 195B3-1; EXCESSIVE GAS WELL SAND INPIPE
|  | 195B4-8 |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 7048367, LOC# 6 AT VALVE 135, RTE 195B4-8
|  | 195A |  | 8.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 7048367, LOC#5 8" TO 4" TEE AT CANAL, RTE 195A3-20
|  | 195 |  | 8.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB#7048367 LOC#5 AT VALVE 17, RTE 195A3-2.0
|  | 195 |  | 8.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB#7048367 LOC#6 AT VALVE CLUSTER RTE195B3-1
|  | 195-088 |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 7048367 AT VALVE 81 7048367-04, GRVI LOC #7, L-195-088
|  | 195 |  | 6.25 | Gathering | [13 empty] | GRVI, JOB# 7048367 LOC#7 AT VALVE 81 SO# 7048367-04, L-195-085
|  | 131Y | 0.54 | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | JOB# 7048367 AT VALVE 85 LOC #7; 7048367-04 SCR RTE L131Y, SCR M.P. 0.5400, STUB 8120
|  | 195 | 0.2741 | 16 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | SO#8056739 ROUTE 195B5-...M.P. 0.2741; OPERATIONS MAP 383081 SHEET 1; SKETCH LOC 2(8056739)
|  | 195 | 0.25 |  | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATIONS MAP 383081 SHEET 1 SO#8056739 ROUTE STUB 8125, M.P. 0.25; SKETCH LOC 3(8056739)
|  | 195 | 0.0011 |  | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATIONS MAP 383081 SHEET 1; SO#8056739 ROUTE 195A4-7 (ABANDON) M.P. 0.0011; SKETCH LOC4 (8056739)
|  |  |  | 8.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATIONS MAP 383081 SHEET 1, SO#8056739, ROUTE STUB8232; SKETCH LOC5 (8056739)
|  |  |  | 8.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATING MAP 383081 SHEET 1...; SKETCH LOC6 (8056739)
|  | 195 |  | 8.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATING MAP 383081 SHEET 1 SO#8056739, ROUTE 195B1-1; SKETCH LOC6 (8056739)
|  | 195B5-1 | 2.1204 / 2.1198 |  | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATING MAP 383081 SHEET 1; SO#8056739 ROUTE 195B5-1, M.P. 2.1204, M.P. 2.1198; SKETCH LOC6 (8056739); INSPECTION 36" C 12.15" O. D. .375" WT; INSPECITON 4.50: O.D. .188" 60" C; OPERATING MAP 383081 SHEET1; THERE AINT STAR FOR WT. 0.188" 1 BELIEVE IT SHOULD BE 0.237"
|  | 195 | 0.4996 | 8.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATING MAP 383081 SHEET 1; SO#8056739 ROUTE 195A3-2.0, M.P. 0.4996; SKETCH LOC6 (8056739); INSPECTION; OPERATING MAP 383081 SHT 1
|  | 195 | 0.5283 | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATING MAP 383081 SHEET 1 SO#8056739; ROUTE 195A3-2.0, M.P. 0.5283; SKETCH LOC6 (8056739); INSPECTION; OPERAINF MAP 3833081 SHEET1
|  | 195 | 2.1272 |  | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATING MAP 383081 SHEET 1 SO#8056739, STA8229 (GATHERING) 195B5-1 M.P. 2.272; SKETCH LOC 6; INSPECTION 12.75" O.D. .354" WT 34"C; INSPECTION 8.625" O.D. 0.219" W.T. 41"C; OPERATING MAP 383081 SHEET 1
|  | 195B3-1 |  |  | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATING MAP 383081 SHEET 1; SO#8056739 ROUTE 195B3-1; SKTECH LOC6; INSPECTION; OPERATING MAP 383081 SHT 1
|  | 195 | 0.2036 |  | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATING MAP 383081 SHEET 1, SO #8056739 ROUTE 195B1-3 ROUTE L-195, M.P. 0.2036 (ABANDON); SKETCH LOC7 (8056739) ; REMOVED METERING EQUIPMENT AND RISER FROM WELL PAD PLUGGED LINES OF PRODUCTION FLUIDS AND INSERT WITH AIR . INSTALLED REBWOOD PLUGS; JOB #8056739, LOC 7RETIREMENT OF ISLETON COMMUNITY #1 GAS WELL; OPERATIONS MAP 38308/ SHEET 1; 84" INSPECTION; RETIRED TO VALVE 34. RETIREMENT INDCLUDED VALVE 36 SEE SHEET 2 OF 3 OF AS BUILTS; INSTALLED LOCATING WIRE AND LINE MARKER AT 4" CAP. INSTALLED 4" CAP
|  |  |  | 2.375 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATIONS MAP 383081 SHEET 1; SO#8056739, ROUTE ....; SKETCH LOC7; JOB#8056739 LOC 7 REMOVAL OF CHECK VALVE 51 AS BUILT; INSTALLED 2" FLANGE AND 3/4 PIPING ON VALVE 50 FOR FUTURE PIGGING AND TO ...FOR ANY PRESSURE UNTIL RETIREMENT. OPERATING DIAFRAM 085546 REV 22; INSTALLED WIRES TO KEEP CP ON LINE WHITE TO LANGHARD ....BLACK; 6" LINE FREASH .V 50 TO LANGHART SPECKLES GAS WELL IS FLAT BUT NOT PIGGED ...PRODUCTION....OR METERED JOB IN FUTURE FOR RETIREMENT PER BRIAN MCCOY. INSTALLED 6" GOO BLING FLANGE; REMOVED 6" CHECK VALVE 51 6" FLANGE AND 36" OF 6" PIPE; INSPECTION 36" C (OPERATIONS MAP 383081 SHEET 1)
|  | 195 | 0.0025 |  | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATIONS MAP 383081 SHEET SO#8056739 ROUTE 195B4-2 (ABANDON) M.P. 0.0025; SKETCH LOC 7 (8056739); REMOVED V36; 1 EA 4" VALVE 2EA 4" FLANGE 2 EA 90 DEG. ELLS 2 EA REDUCERS. ; OPERATIONS MAP 383081 SHEET 1
|  |  | 0.0006 |  | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATIONS MAP 383081 SHEET 1; SO#8056739 ROUTE STUB 8117, M.P. 0.0006; SKETCH LOC8 (8056729); OPERATIONS MAP 383081 SHEET 1; JOB#8056739 LOC#8 ALSO JOB# 7043867 LOC #2 AS BUILT; NOTE: LOCATION OF VALVE 232 GPS: N 38 07.878, W121 40.342; INSPECTION; GROVE VLAVE HOT TAP 600 SERIES INSTALLED 3" BLIND FLANGE; REMOVED 3" FLANGE 24" OF PIPE 90 DEG. ELL ROLLED DOWN
|  | 195 |  |  | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATING MAP 383081 SHEET SO#8056739 ROUTE STUB8236; SKETCH LOC 9(8056739); INSPECTION; OPERATING MAP 383081 SHT 1
|  | 195 | 0.00 / 0.4904 |  | Gathering | [10 empty] | Steel/Wrought Iron |  |  | SO# 8056739 ROUTE STUB8238, 195B8-6,M.P.0.00, M.P. 04904; OPERATIONS MAP 383081 SHEET 1; SKETCH LOC 11 (8056739); INSPECTION; INSPECTION; G.C. GAS NOR CAL X-RAY; OPERATIONS MAP 383081 SHEET 1
|  | 195 |  |  | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATIONS MAP 383081 SHEET 1 SO#8056739; ROUTE L131Y, M.P. 0.0213, L131Z, M.P. 0.0005, L-195-052, M.P. 0.00019 X6326; SKETCH LOC 12 (8056739) 23"C INSPECTION; INSPECTION 24"C; INSPECTION 60"C; INSPECTION 60"C; CAP INSTALLED ON JOB 4M175670-72 DID NOT EXPOSE; REMOVED VALVE 88 &89 INSTALLED 16X 16 X 12 TEE 16X 10 REDUCER 18" ANGLE AND PIPING; NOTE: RETIRED 10" PIPE LINE 131 TO DEAD END AT SOUTH SIDE BREANNAN ISLAND RD.
|  | 195 | 0.8683 | 20 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATING MAP 383081 SHEET 1; SO#8056739 ROUTE L-195B8-8 M.P. 0.8683, L-195-091; SKETCH LOC 12 (8056739); OPERATIONS MAP 383081 SHEET 1; INSPECTION S/O V-195; INSPECTION 33' S.O V-188; INSTALLED 20" CAP AND 30 " CAN .375W X 52 DSAW AND 2" SAV-A-VALVE; INSTALLED GM1428244-83 LOC 32;
|  | 195 | 0.0291 |  | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATING MAP 383081 SHEET 1 SO#8056739 ROUTE X6326 M.P. 0.0291; SKETCH LOC12 (8056739); INSPECTION @V-225; REMOVED 3" VALVE PLAT 4...; REVAMPED 3/4" ODORIZER, LINES TO PRESSURE TAPS USED EXISTING PIPEING.
|  |  | 0.0008 |  | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATING MAP 383132 SO#8056739 ROUTE STUB 8115, M.P. 0.0008, ROUTE STUB 8241, M.P. 0.0008; SKETCH LOC 13 (8056739); OPERATIONS MAP 383132; INSPECTION 66" 6.625 O.D.; INSPECTION 48"C 6.625"O.D.; INSTALLED 6" CAP 9" CAN... GRD3...INSTALLED 6" CAP 9" CAN .280 WALL GRD B SMLS, 1" SAV-A-VALVE TDC INTALL 6" CAP. UNABLE TO SHORTEN UP DUE TO 2" WIDE STRAPS TOP AND BOTTOM OF METER OFF SET UP....REMOVED 18" OF PIPE AND 6" WAS SLEEVE.
|  |  | 0.0029 |  | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATING MAP 383132 SO#8056739, ROUTE...; SKETCH LOC 14 (8056739); NOTE! VALVE194 12A 4" ...FEXWE VALVE NEXT TO 12" MAIN IS A FEXWE GROUVE BALL 600 SEE NOTE BOTTOM PAGE; 4" KERO TEST FITTING & 6X4 REDUCER & 4 X4 X 4TEE ALL WELDED WITH NO CANS IN BETWEEN EXSISTING INSTALLED WIRES BOTH SIDES AND CONNECTED IN LITTLE FINK; NOTE:FOR SOME REASON VALVE 194 15 DOUBLED UP EVIDENTLY THE GROVE BALL VALVE ON THE 12" MAIN HAD SOME TYPE OF PROBLEM WHEN TAPPED. SO THEY BOLTED ONTHE ROC....VALVE IS ON SEALING ...NO INFO AT THIS GATE ...PROBABLY LEAKING THRU BALL; INSPECTION 35"C; OPERATING MAP 383132
|  | 195A4-2 | 0.9295 | 6.25 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATIONS MAP 383081 SHEET 1, SO#8056739 ROUTE L-195A4-2; M.P. 0.9295; SKETCH LOC 15 (8056739); NOTE LOC 15 N TIED TO REC BOARD...TO 30PSI SYSTEM LOC 15B TIED REC BOARD TO 450 PSI SYSTEM; INSPECTION; OPERATIONS MAP 383081 SHEET 1 LOCATION 15 B
|  | 195A | 0.9291 | 3.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATIONS MAP 383081 SHEET SO#8056739 ROUTE L-195A4-2, M.P. 0.9291; SKETCH LOC 15 (8056739) OPERATIONS MAP 383081 SHEET 1 LOCATION 15 B; INSPECTION
|  | 195A7-2 | 0.2314 | 6.25 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | SO#8056739 ROUTE 195A7-2,M.P. 0.2314; OPERATIONS MAP 383081 SHEET 1; SKETCH LOC 15 (8056739) OPERTIONS MAP 383081 SHT 1; LOCATION 15 A; INSPECTION; NOT LOC 15A TIED REC BOARD 2 & 4 TO 30 PSI SYSTEM LOC 15 B TIED REC BOARD 6 TO 450 PSI SYSTEM
|  | 195A7-2 | 0.2316 | 3.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | OPERATIONS MAP 383081 SHEET 1; SO#8056739 ROUTE 195A7-2, M.P. 0.2316; SKETCH LOC 15 (8056739); OPERATIONS MAP 383081 SHEET 1, LOCATIONS 15A; NOTE LOC 15 A TIED REC BOARD 2 & 4 TO 30 PSI SYSTEM LOC 15 B TIED REC BOARD 6 TO 450 PSI SYSTEM
|  | 195 |  | 4.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | INSPECTION; CUT OFF WELCH FEE 1
|  | 195 | 0.18 | 12 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | SO#7043062-02, L-195B5-7, M.P. 0.1800; INSPECTIONL CUT OFF WELCH FEE 5
|  | 195-0151 | 0.54 | 4 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | PM30606060 L-195-0151, M.P. 0.54, KUHN #5 30606060; DUG UP 8" L-195 WHERE IT REDUCED TO 4" FOR WELL (KUHN #5). CUT AND CAPPED 4" PIGGED 4" LINE TO WELL RISER (KUHN #5). REWRAPPED 4" CAP AND RED WOOD PLUGGED ABANDONN 4" ENDS. DUG UP AND REMVOED 3" RISER AT (KUHN #5) {7' COVER ON ABANDON PIPE WELL PAD AREA}
|  | 195A6-4 | 0.0316 | 6 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | INSPECTION 195A6-4, PM#30610678
| 08-19501-1 | 195-0151 | 0.0872 | 8.625 | Distribution Main | [7 empty] | 2008-08-18 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  |  | PM40934931 8"; FOREIGN 195-015' M.P. 0.0872; INSTALLED SS GAS CLAMP PER BRIAN MCCOY AND MIEL J. ...
| 08-19503-1 | 191-0151 | 0.0872 | 8 |  |  | Body of Pipe |  |  | Internal Corrosion |  |  |  | SS Clamp w/Anode - Clamp | STAINLESS STEEL | Steel/Wrought Iron |  | RIO VISTA | 40934931 FOREIGN 191-0151 M.P.0.872; TAPE WRAP AND WAXED WRAP SS FITTING. FITTING WAS STAINLESS STEEL FITTING TO 120 PSI; PIPELINE SOLD TO ROSETTA RESOURCES AS PART OF RIO VISTA 30 PSIG GAS GATHERING ACTIVE PIPELINE SALE ON ORDER #30604361 EFFECTIVE 1/1/09
|  | 195 |  | 8 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | RT 195, ... MAIN... 30613755, ROUTE STUB10415; K&A MAIN JOB#30613755; THE 8" CAP WELD END X-RAYED. THE ENT 8" MAIN WAS CUT AND CAPPED TO REMOVE PIPE FOING INTO BRANNAN ISL. STA.
|  | 196 | 0.0003 | 3.5 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | ...L-196-6, M.P. 0003,...0189; OPERATING MAP 382899 SHEET 1
|  | 196A | 0.0005 | [12 empty] | Steel/Wrought Iron |  |  | #7059886; ROUTE 196A, M.P. 0.0005
|  | 196 |  | 6.625 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 6088723 AT MUELLER AND TIE-IN LOCATION L-196 TO PIACINTINE 1-27 WELL
|  | 196 | 0.0112 | 6.625 | [14 empty] | GG RIO VISTA, JOB#7050966 AT 6 X 3 REDUCER TIE POINT L-196-3, M.P.0.112, SO 7050966-05
|  | 196-2 | 0.0129 | [12 empty] | Steel/Wrought Iron |  |  | DIST: RIO VISTA PM3060436-5, PM30604365-07; RTE 196-2 GG-6T, M.P. 0.0129
|  | 196 | 0.02 | 3.5 | [14 empty] | GG RIO VISTA JOB 7050966 AT OLD L-196-4, M.P.0.02 AND ACROSS RISER CUT OFF SO7050966-05
|  | 196 |  | 1.05 | [7 empty] | 2005-01-03 | [6 empty] | JOB 8068826-05 L-196 DRIP8014 TEMP REPAIR M.P. 0.0399, M.P. 0....
|  | 196 |  | 1.05 | [7 empty] | 2005-01-03 | 2005-03-09 | Other | INSTALLED NEW SECTION OF PIPE |  |  |  | ...RIO VISTA; JOB# 8068526-05 PERMANENT REPAIR L-196 DRIP 8044, M.P.0.0399, M.P. 0.0336, M.P. 0.0334; REPLACED 54" OF 3/4" DRIP LINE; GPS FILE R030913A & B
|  | 196 |  | 1.05 | Gathering | [6 empty] | 2005-01-03 | 2005-01-05 | Other | AQUA WRAP |  |  | ISLETON | GPS COODS = 38 09.689 LAT 121 36.175 LONG *DAMAGED AREA; NO LEAK DETECTED; MEARS/ HEMKER REAPIRED DAMAGE WITH AQUA WRAP
|  | 196 | 0.38 | 6.625 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | RT 196, M.P. 0.3800, JOB# 7042390 DETAIL 1- CUT OFF LOCAITON
|  | 196 | 0.38 | 6.625 | [14 empty] | GGR A FORM FILE; 7050966 AT VALVE 7; L-196, M.P. 0.38, SO#7050966-05; INSPECTION; VALVE LOCATION GPS CORDINATES N 38 05.061; W 121 25.452 INSTALLED LINE MARKER AND E.T.S. AT 6' FEET WEST OF VALVES, BURIED IN YELLOW FIBER GLASS BOX
|  | 196 | 0.38 | 3.5 | [14 empty] | GG RIO VISTA 6B 7050966 AT OLD L-196, M.P. 0.38 AND ACROSS #1 TIE POINT AT VALVE 7, SO#7050966-05; VALVE LOCATION GPS CORDINATES N38 05.061 W 121 25.452 INSTALLED LINE MARKER AND E.T.S. AT 6' FEET WEST OF VALVE, BURIED IN YELLOW FIBER GLASS BOX
|  | 196 |  | 6.625 | [11 empty] | Steel/Wrought Iron |  |  | 7042370 L-196, M.P....; TIE-IN HOLE @ JACKSON WELL LINE 196 REMOVED APPROX 6' OF .156 GIM
|  | 196 | 0.38 | 6.625 | [11 empty] | Steel/Wrought Iron |  |  | 7042370 L-196 M.P. 0.38; TIE-IN HOLE @ JACKSON WELL LINE 196 REMOVED APPROX 6' OF .156 GIM
|  | 196 | 0.8753 | 6 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | PM 30604399, RT 196, M.P. 0.8753; CAPPED OFF.
| 09-19601-1 | 196 | 0.9527 | 01.56 / 06.00 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2009-03-17 | 2009-05-14 | Other | RETIRE LINE 196 | Steel/Wrought Iron |  | LODI | RT L196B-Z RETIRED, M.P. 0.9527, CIRV11-09; REFER TO STOCKTON DIV. LEAK NO 09-02038-1 3/17/09
| 09-19601-1 | 196 |  | 01.56 / 04.00 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2009-03-17 | 2009-05-14 | Other | RETIRED LINE 196 | Steel/Wrought Iron |  | LODI | REFER TO STOCKTON DIV. LEAK NO 09-02038-1, 3/17/2009; C/O AND REMOVED.
| 09-19601-1 | 196 |  | 01.56 / 06.00 | Gathering |  | Body of Pipe |  |  | Internal Corrosion |  | 2009-03-17 | 2009-05-14 | Other | RETIRE LINE 196 | Steel/Wrought Iron |  | LODI | RT 196B-Z RETIRED, M.P. CI. RV11-09; REFER TO STOCKTON DIV. LEAK NO 09-02038-1, 3/17/2009
|  | 196 | 1.252 | 6 | Gathering | [10 empty] | Steel/Wrought Iron |  |  | L196, M.P. ... PM#30604... (GAMBLE WELL) WOOD BRIDGE RD; 6" PIPE LINE WAS DEACTIVATED -PRIOR-. PINNED OFF SERVICE TEE, CUT AND CAPPED W 3/4" SOCKET (H.P. SOCKET CAP STEAL). LEFT 1' STUB OFF MAIN. REMOVED 3 STAGE HIGH TO HIGH SETS. 5' COVER ON 6" GAS MAIN BACKFILLED LOCATIONS & CLEANED UP JOB SITE.
|  | 196 | 1.73 | 6 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | PM 30604399; 6" MAIN HAS BEEN GASED UP TO 50PSI
|  | 196B | 2.53 | 16 | [11 empty] | Steel/Wrought Iron |  |  | JOB# 6088747 LODI GAS STORAGE CONNECTION WOOD BRIDGE RD. F.S.25+79 L-196B, M.P. 2.53
|  | 196 | 6.1333 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | RT= 196,M.P. 6.1333, #30609729, L-196 LIVE OAK 136; #30609729 L-196 LIVE OAK 136; #30609729 L-196 LIVE OAK 136; CUT OFF AND RETIRED LIVE OAK GAS WELL FEED TO L-196. CUT AND CAPPED 2", AND LEFT VALVE #1 IN CLOSED POSITION. NOTE: (VALVE #1 IS A BURIED VALVE) REMOVED VALVE FRAMME AND COVER WRAPPED VALVE AND BACKFILLED JOB LOCATION. LEFT PG & E FIBERGLASS TUB OVER VALVE FOR PROTECTION
|  | 196 | 6.89 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-196 LINE INSPECTION ORDER #7048609, M.P. 6.89; L.... 196A, M.P. 6.89; X-RAY HIGH MOUNTAIN
|  | 196 | 7.42 | 12 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | L-196 LINE INSPECTION ORDER #7048609; L... 196A, M.P. 7.42; X-RAY HIGH MOUNTAIN
|  | 196A | 9.8763 | 16 | Transmission | [10 empty] | Steel/Wrought Iron |  |  | JOB# 30604363; RIO VISTA....M.P.9.8763; JOB# 30604363; EXPOSED APPROX 7' OF L-196, 12" TRANSMISSION LINE FOR GAS WELL TIE IN OFF (V-3B) WHICH IS TIED INTO L-196. V30 WAS BLING FLANGE OFF PRIOR TO THIS JOB, AND WAS RE-UTILIZED FOR ENTRY INTO PIPELINE. (NO REPAIRS DOEN TO PIPELINE); *NOTE: AS BULT FOR NEW 3" PIPE INSTALLED FOR WALNUT GROVE RP WILL BE IN JOB FOLDER; * COVER ON L*196 12" AT V30 LOCATION WAS 36" . NO REPAIRS WERE MADE TO THIS PIPELINE FOR THIS JOB
|  | 196 | 9.9259 | [12 empty] | Steel/Wrought Iron |  |  | RT-196A, M.P. 9.9259; NEW VALVE
|  | 196 | 9.92 | 12 | Transmission | [7 empty] | 2002-09-23 | Other | WRAP |  |  |  | RE-WRAPPED 20' OF L-196 WITH WAX TAPE; GPS FILE #R092416A. SSF. REWRAPPED PIPE WITH WAX TAPE.
|  | 196A | 13.45 | 12.75 | [11 empty] | Steel/Wrought Iron |  |  | SO#6088504, L-196A...; L-196A...; L196A 13345 JOB 6088504
96 | 10-88555-1 | 302-780 |  | 0.75 | Single Service |  | Regulator/Pilot |  |  | Other | LOOSE BOLTS ON REG FLANGE | 2010-10-21 | 2011-02-28 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SUTTER | TIGHTEN REG FLANGE BOLTS
96 | 10-88556-1 | 302-780 | 59 | 0.75 | Single Service |  | Fitting | Regulator/Pilot |  | Other | LOOSE UNION | 2010-10-21 | 2011-02-28 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SUTTER | TIGHTEN UNION; SOAP TEST OK
96 | 10-88558-1 | DREG7086 | 0.01 | 0.75 | Distribution Main <= 60 PSIG |  | Other |  |  | Equipment Malfunction |  | 2010-10-22 | 2011-01-27 | Other |  | Steel-Other |  | MERIDIAN | REG NOT LOCKING UP; REG NOT LOCKING UP. CAUSING RELIEF VALVE TO LEAK. rE-BUILT REG. EVERYTHING NORMAL.
96 | 10-88560-1 | 302-225 | 0.26 | 1 | Branch Service |  | Other |  | FACILITY REMOVED | Other | FACILITY REMOVED | 2010-10-22 | 2011-02-22 | Other | FACILITY REMOVED | Steel/Wrought Iron |  | SUTTER | FACILITY REMOVED; FACILITY REMOVED ON CAPITOL JOB #3060499-'10
96 | 10-88568-1 | 120-1 | 97 | 0.75 | Single Service |  | Line Valve |  |  | Other | LOOSE PACKING NUT ON VALVE | 2010-10-26 | 2011-03-04 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SUTTER | TIGHTEN PACKING NUT ON INLET VALVE
96 | 10-88568-1 | 120-1 | 97 | [8 empty] | 2010-10-26 | [5 empty] | SUTTER
20 | 10-81001-1 | 1520-01 | 1.17 | [8 empty] | 2010-10-06 | [5 empty] | ROSEVILLE
20 | 10-81013-1 | 173 | 12.06 | [8 empty] | 2010-10-07 | [5 empty] | NEWCASTLE
20 | 10-81014-1 | 173 | 10.73 | [8 empty] | 2010-10-07 | [5 empty] | PENRYN
20 | 10-81016-1 | 173 | 9.3 | 0.75 | Distribution Main <= 60 PSIG |  | Line Valve |  |  | Other | REQUIRED GREASE | 2010-10-07 | 2011-02-23 | Greased - Other |  | Steel-Other |  | PENRYN | NO SOAP TEST AFTER VALVE BEING GREASED WAS GOOD - NO BUBBLES.
20 | 10-81020-1 | 173 |  | 0.75 | Distribution Main |  | Line Valve |  |  | Other | NEEDED GREASE | 2010-10-07 | 2011-02-23 | Greased - Other |  | Steel-Other |  | PENRYN | GREASED PLUG VALVE; SOAP TEST AFTER BEING GREASED - NO BUBBLES
20 | 10-88025-1 | 173 | 13.42 | [8 empty] | 2010-10-21 | [5 empty] | AUBURN
11 | 10-81005-1 | 1502-11 |  | 0.75 | Single Service |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-10-04 | 2011-03-11 | Other | REPLACE REG. & RELIEF | Steel/Wrought Iron |  | MARYSVILLE | REPLACED REG. SET; SOAP TEST OK
11 | 10-81010-1 | 1502-11 | 143 | 0.25 | Distribution Main <= 60 PSIG |  | Fitting | Compression Coupling Stainless Steel |  | Other | LOOSE S/S FITTING | 2010-10-05 | 2011-02-09 | Other | TIGHTEN S/S F | Steel/Wrought Iron |  | MARYSVILLE | TIGHTENED 2 STAINLESS STEEL COMP FITTINGS; SOAP TEST OK!
11 | 10-81028-1 | 124A | 22.96 | [8 empty] | 2010-10-08 | [5 empty] | MARYSVILLE
11 | 10-81031-1 | 1501-01 | 0 | [8 empty] | 2010-10-08 | [5 empty] | YUBA CITY
11 | 10-81032-1 | 1501-01 | 0 | [8 empty] | 2010-10-08 | [5 empty] | YUBA CITY
11 | 10-81033-1 | 1501-1 | 0 | [8 empty] | 2010-10-08 | [5 empty] | YUBA CITY
11 | 10-81034-1 | 124A | 23.01 | [8 empty] | 2010-10-08 | [5 empty] | YUBA CITY
11 | 10-81041-1 | 1501-01 | 6.87 | 0.75 | Single Service |  | Regulator/Pilot |  |  | Equipment Malfunction |  | 2010-10-08 | 2011-02-09 | Other | REPLACED REG | Steel-Other |  | YUBA CITY | REPLACED FISHER 627 REG & H202 RV; SOAP TEST OK!
11 | 10-81049-A | 1514-01 | 1.63 | 0.75 | Branch Service |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-10-09 | 2011-03-03 | Other |  | Steel/Wrought Iron |  | YUBA CITY | REPLACED REG, RELIEF, AND ALL PIPING BETWEEN UNIONS.; PRESSURE TEST SERVICE FROM HPR TO RISER.
11 | 10-81501-1 | 1502-01 | 1.27 | 0.75 | Distribution Main <= 60 PSIG |  | Fitting |  |  | Other |  | 2010-10-11 | 2011-03-10 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | MARYSVILLE | TIGHTEN UNION; SOAP TEST OK!
11 | 10-81502-1 | 050A | 4.82 | 2 | Single Service |  | Regulator/Pilot |  |  | Equipment Malfunction |  | 2010-10-13 | 2011-03-05 | Other | REPLACE RELIEF | Steel-Other |  | YUBA CITY | REPLACE RELIEF REG + PILOT; SOAP TEST OK
11 | 10-88001-1 | 202 | 6.03 | 0.75 | Single Service |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-10-15 | 2011-03-04 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | WHEATLAND | TIGHTEN THREADS UNDER RELIEF; SOAP TEST OK
21 | 10-81000-1 | 0617-06 | 19.22 | 4 | Transmission >= 20% SMYS |  | Line Valve |  |  | No/Deteriorated Pipe Dope |  | 2010-10-07 | 2011-03-11 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | EL DORADO HILLS | REMOVE AND REDOPED CAP & TIGHTEN -- TIGHTEN BOLTS ON FLANGE; TIGHTENED CAP & BOLTS. iNSTALLED NEW FRAME AND LEADER. SOAP TESTED ALL AREAS - SOAP TEST GOOD!
|  |  |  | 2 | Transmission |  | Other |  | NO LEAK |  |  | 2010-06-30 | 2010-07-06 | Replace Partial Service |  | Steel-Other |  | YUBA | INSTALL 23' OF 2" STL SRVC
|  | 123 |  | 12 | Transmission |  | Other |  | NO LEAK |  |  |  | 2010-02-23 | Other | USED GRINDER TO FEATHER OUT GOUGES AND MAGNAFLUXED | Steel/Wrought Iron
| 10-00007-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | ORING FAILURE | 2010-02-19 | 2010-04-30 | Other | R&R CAP | Steel/Wrought Iron |  | YUBA CITY | R&R ORINGS IN CAP, REINSTALL, SOAP TEST
| 10-00008-1 | [10 empty] | 2010-02-19 | [5 empty] | YUBA CITY
| 10-00009-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | O-RING FAILURE | 2010-04-30 | 2010-04-30 | Other | R&R ORINGS ON CAP | Steel/Wrought Iron |  | YUBA CITY | R & REPLACE ORINGS, REINSTALL, SOAP TEST (GOOD)
| 10-00010-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | O-RING FAILURE | 2010-02-19 | 2010-04-30 | Other | R&R CAP | Steel/Wrought Iron |  | YUBA CITY | REMOVE & REPLACE O-RINGS IN ONE, REINSTALL
| 10-00012-1 |  |  | 1.25 | Transmission |  | Valves |  |  | Other | LOOSE | 2010-02-19 | 2010-03-26 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | YUBA CITY
| 10-00011-1 | [10 empty] | 2010-02-19 | [5 empty] | YUBA CITY
| 10-00012-1 |  |  | 1.25 | Transmission |  | Valves |  |  | Other | LOOSE; | 2010-02-19 | 2010-03-26 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | YUBA CITY
| 10-00016-1 | 50 |  | 8 | Transmission |  | Fitting |  |  | Construction Defect |  | 2010-03-16 | 2010-04-15 | Replace TP Main |  | Steel/Wrought Iron |  | LIVE OAK | REPLACED 35" SPOOL, REPLACED FITTING; REMOVED LEAKING FITTING & REPLACED W 35" SPOOL
| 10-00021-1 |  |  | 1.25 | Distribution Main |  | Body of Pipe |  |  | Damage by 3rd Party |  | 2010-04-15 | 2010-04-15 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | GRANITE BAY | MADE REPAIR WITH (1) 1 1/4" MET FIT REPAIR COUPLING; UNKNOWN PERSON POUNDED TREE STAKE INTO 1 1/4" PL GAS MAIN
| 10-00072- | 50 | 11.55 | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-14 | 2010-10-26 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | LIVE OAK | FOUND CORROSION LEAK ON PIPE. PUT ON PLIDCO LEAK CLAMP, SOAP TEST AT LINE PRESSURE AND BACKFILLED
| 10-01060-1 | 202 |  | 0.75 | Transmission |  | Other |  | RELIEF | Other | SEAT WORN | 2010-10-07 | 2010-10-07 | Other | REPLACE H-202 RELIEF | Steel/Wrought Iron |  | PENN VALLEY | PLACED HIGH TO HIGH REG SET ON BYPASS + REPLACED H-202
| 10-00016-1 | 50 |  | 8 | Transmission |  | Fitting |  |  | Construction Defect |  | 2010-03-16 | 2010-04-15 | Replace TP Main |  | Steel/Wrought Iron |  | LIVE OAK | REPLACED 35" SPOOL, REPLACED FITTING; REMOVED LEAKING FITTING & REPLACED W/ 35" SPOOL
| 00-50012-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Damage by 3rd Party | Plastic Crack Failure | 2000-04-03 | 2000-04-03 | Mechanical Repair Fitting - Fitting |  | TR 418 |  | SALINAS | SOUTH SIDE OF CHRUCHHILL WAY 2' FROM FRONT TR, 5' FROM WEST TR; INST. 18" OF 2" PLASTIC PIPE AND 2-2" X 2" AWP-FIT COUPLING; 2" PLASTIC MAIN
| 00-50055- |  |  | 2 |  |  | Body of Pipe |  |  | Digin |  | 2000-11-08 | 2000-11-08 | Mechanical Repair Fitting - Fitting |  | TR 418 |  | CASTROVILLE | MAIN DIG IN; REPLACED 18" OF 2" PL. PIPE
5 | 76-00305-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-03-22 | 1976-03-22 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | TRANSMISSION LINE 103, M.P. 17.5; ORIGINAL IN LINE FOLDER
5 | 76-00306-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Damage by outside Forces |  | 1976-10-15 | 1976-10-15 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  |  | MASUP RD; 301-F; ORIGINAL IN LINE FOLDER
| 10-50198-1 | 301-B | 7.9 | 0.75 | Transmission |  | Valves |  |  | Unknown |  | 2010-10-08 | 2011-01-03 | Other | GREASED VALVE | Steel/Wrought Iron |  | SALINAS | IGIS...HPR 290; INLET VALVE HAS LEAK; H.P.R. SET NEEDS GREASE; GREASED AND OPERATED VALVE, SOAP TEST OK; LUBE AND OPERATE
| 10-50199-1 | [10 empty] | 2010-10-08 | [5 empty] | SALINAS | IGIS H.P.R. 292; RELIEF VALVE, MULTIPLE LEAKS; H.P.R. SET, YELLOW PAINT; SOAP TEST OK.
5 | 81-00110-1 |  |  | 8 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 1981-03-24 | 1981-03-27 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  |  | ORIGINAL LINE FOLDERS
5 | 10-81010-1 | DCST1912 |  | 0.75 | Transmission >= 20% SMYS |  |  |  |  | Unknown |  | 2010-10-01 | 2010-12-15 | Other |  | Steel-Other |  | SALINAS | HIGH 2 HIGH SET DCUST1912; SAME -10/09/10 10:00 A257 WAS UNABLE TO; LUBED & OPERATED FIRE VLV; LUBED AND OPERATED V-1
| 09-33312-1 | 210B |  | 12 | Transmission |  | Mechanical Joint |  |  | Other |  | 2009-10-05 |  |  |  | Steel/Wrought Iron |  | SUISUN | BP445; N/E CORNER HWY 12 AND EMPEROR DR. SUISUN CITY; KIRSTEN- THIS HAS ALREADY BEEN MAPPED; REPAIRED BUT PLEASE RELOCATE TO BLOW DOWN SG. IT DOES NOT APPEAR TO BE ON HCA PIPE 210B, THANKS
| 09-50557-1 | MTY-1 | [9 empty] | 2009-12-16 | [5 empty] | SALINAS | 1815-02 T DFM, GIS DETAIL... 2/16/10; 4.08 VALVE PIT; NON-LEAK PER JIMMIE LOPEZ
| 10-81531-1 | 00817-01 |  | 0.75 | Single Service |  | Fitting |  |  | Unknown |  | 2010-10-10 | 2010-10-10 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | SAN JOSE | MUELLER CAP ON PIN OFF TEE LOOSE; MUELLER CAP. LOOSE ON PIN OFF TEE, REDOPED & TIGHTENED. (SOAP TEST OK)
| 10-81531-1 | 00817-01 |  | 0.75 | Single Service |  | Fitting |  |  | Unknown |  | 2010-10-10 | 2010-10-10 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | SAN JOSE | MUELLER CAP ON PIN OFF TEE LOOSE; MUELLER CAP. LOOSE OFF TEE, REDOPED & TIGHTENED. (SOAP TEST OK)
76 | 10-20333-B |  |  | 0.75 | Distribution Main > 60 PSIG |  | Line Valve |  |  | Other |  | 2010-12-11 | 2010-12-11 | Greased - Other |  | Steel-Other |  | WATSONVILLE | @ TAP VALVE UPSTREAM FROM H.P.R.; LEAK ON VALVE IN FRAME/COVER; GREASED VALVE TO CORRECT LEAK; VALVE LEAKING AT STEM, GREASED TO CORRECT
| 10-40002-1 | 187 | 35.78 | 0.75 | Transmission |  | Valves | Other |  | Unknown |  | 2010-01-20 | 2010-01-20 | Other | DISASSEMBLE & RESEALED | Steel/Wrought Iron |  | GREENFIELD | IGIS LL 0020; ON HIGH TO HIGH SET FEEDING HOUSE # 38730; MP 35.78; REMOVED LEAKING FITTINGS, CLEANED RESEALED & REINSTALLED, SOAP TEST OK
| 09-50107-1 | 301A | [9 empty] | 2009-04-25 | [5 empty] | MOSS LANDING | (DELETED); MOSS LANDING TAPS, V1 AND V2 LEAKING .5; SAME, NO GAS FOUND
| 10-40007-1 | 187 | [9 empty] | 2009-05-01 | [5 empty] | SOLEDAD | 10-40007-1; OFF HIGHWAY 101 - H&H SET FISHER BLOW OFF
| 10-40008-1 | [10 empty] | 2010-03-04 | [5 empty] | KING CITY | COMPLETED DELETED 4-19-10; GAUGE LEAK AND BY VALVE; NO LEAK FOUND (DELETED)
4 | 10-40015-1 | [10 empty] | 2010-05-28 | [5 empty] | KING CITY | SAN BERNABE VINEYARD H & H SET IN 24 X 36 BOX; FOUND ON RECHECK OF 09-40140-1; NO LEAK FOUND; NO LEAK FOUND
| 10-40017-1 | 187 | 39.91. | 0.75 | Single Service |  | Other |  | RELIEF BLOWING | Other | REGULATOR POOR U/U | 2010-07-15 | 2010-07-15 | Other | REPLACED REGULATOR | Steel/Wrought Iron |  | SOLEDAD | IN IGS 187, T&R; FISHER B/OFF BLOWING GAS; FISHER B/OFF; FOUND RELIEF BLOWING AT A SINGLE SERVICE HPR POOR LOCK UP ON REGULATOR SO REPLACED IT, RELIEF OK JUST DOING ITS JOB
| 74-00070-1 | [16 empty] | LOS GATOS | LEAKING 2" H.P. GAS MAIN....BY ARC...12" X 3" PATCH LEAK. INST. #9 ANODE.; 37-31; CAUSE OF LEAK WRAP DAMAGE...WHEN...AT THIS LOCATION; LEAKAGE FOUND 90% J.W. 3-27-74
80 | 74-30351-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1974-03-27 | 1974-04-03 |  |  | Steel/Wrought Iron
| 75-01029- |  |  | 2 | [11 empty] | Steel-Other |  | SUNNYVALE | LOCATED AND ...J.W. AREA OK; GAS FOUND NEAR TO DRIVEWAY 1% 12-1-75 RICKSON; WELDED 5" X 3" PATCH ON LEAK DUE TO CORROSION. ROCKED AND BACKFILLED. AREA CLEAR D. ANDER...
8 | 75-0102 - |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  |  | 12/00/0000 | Patch Welded |  | Steel/Wrought Iron
| 10-81018-1 | 11 |  | 0.75 | Single Service |  | Valves |  |  | Other | ADD GREASE | 2010-10-05 | 2010-10-14 | Other | INSTALL FITTING & ADD GREASE | Steel/Wrought Iron |  | YUBA CITY | 30' N/O M/BOX 4817 IN PGE BOX; SAME; GREASED VALVE; SOAP TEST; PACKING ON INLET VALVE LEAKING APPLIED GREASE. LEAK STOPPED.
| 10-81019-1 | 11 |  | 0.75 | Single Service |  | Fitting |  |  | Other | THREAD LEAK | 2010-10-05 | 2010-10-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | LIVE OAK | FARM TAP; SAME; SHUT IN REG. SET. REPAIRED THREAD LEAKS.; SOAP TEST OK; UNION THREAD LEAK; RELIEF THREAD LEAK.
11 | 10-81052-1 | 202 | 0.03 | 0.5 | Transmission >= 20% SMYS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2010-10-11 | 2010-12-22 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | MARYSVILLE | 70' FROM S. BEALE RD. ON SOUTHSIDE/O OSTRUM RD.; SAME; TIGHTENED PLUG ON 1/2" BALL VALVE; SOAP TEST OK; CAMP FAR WEST. OSTROM & SOUTH BEALE RD. WHEAT LAND. GREASED & TIGHTENED PLUG ON BALL VALVE.
| 10-81019-1 | 173 |  | 0.75 | Single Service |  | Other |  | UNION | Other | LOOSE FITTING | 2010-10-07 | 2010-10-22 | Other | TIGHTEN UNION | Steel/Wrought Iron |  | OPHIR | REG. 158 FITTING AFTER REG.; SAME; TIGHTEN UNION; SOAP TESTED; TIGHTENED UNION
| 10-88000-1 | 124B | 7.83 |  | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-14 | 2010-10-28 | Replace TP Main | 8' | Steel/Wrought Iron |  | SHERIDAN | 1200' N OF HWY 65 PAINTED FENCE POST/FLAGGED AREA; 1200' N OF HWY 65 FENCE POST/FL; EXTENSIVE CORROSION/ REPLACED 8' OF PIPE; CUT OUT AND REPLACED 8' OF 8" PIPE BECAUSE OF CORROSION LEAK
| 10-81149-1 | 1111111 |  | 0.75 | Transmission |  | Valves |  |  | Other | NO GREASE | 2010-09-29 | 2010-10-17 | Other | GREASED | Steel/Wrought Iron |  | FREMONT | VALVE STAND NXT TO FENCE FOR FRWY; SAME; GREASED VALVE OPERATED; GREASED VALVE & SOAP TESTED .
| 10-81781-1 | 153 | 0.62 | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-09 | 2010-10-16 | Patch Weld - Weld |  | Steel/Wrought Iron |  | FREMONT | XST CURTIS; 138' FRM BRTANO PARK EAST; WELDED PATCH ON 2" STL MAIN DISTRIBUTION; WELDED PATCH ON 2" STL MAIN; WELDED PATCH ON 2" STL MAIN (SOAP TESTED).
| 10-81801-1 | DREG4868 | 15 | 6 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  |  | 2010-10-18 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | NEWARK | IN ASPHALT 50' FROM ADRSS; FOUND LEAK ON 6" DISTRIBUTION MAIN; INSTALLED 6" FULL CIRCLE CLAMP ON MAIN; INSTALLED 6" CLAMP ON 6" STL MAIN (SOAP TESTED).
| 10-81082-1 | 0112-09 | 0.27 | 0.75 | Transmission |  | Valves |  |  | Other | PLUG | 2010-10-06 | 2010-10-25 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EMERYVILLE | AX FRM ADRS; BARHOLE 40' S/O MARKETPLACE ENTR.; SERVICE VALVE HIGH TO HIGH BOX.
| 10-81084-1 | 0112-09 | 0.07 | 0.75 | Transmission |  | Other |  | GREASE | Unknown |  | 2010-10-05 | 2010-10-23 | Other | GREASE | Steel/Wrought Iron |  | EMERYVILLE | POLE61-5858; 30'S/O N/E CRNR XST SHELMOUND; SERVICE VALVE DUPLICATE WITH 10-80185 LEAK NOT ON VALVE; GREASE VALVE
| 10-81085-1 | 0112-08 | 0.47 | 0.75 | Transmission |  | Other |  | GREASE | Unknown |  | 2010-10-05 | 2010-10-23 | Other | GREASE | Steel/Wrought Iron |  | EMERYVILLE | N/W CRN XST CHRISTIE' 80' N; POLE 32-5839; LEAK NOT ON VALVE; SERVICE VALVE IN STREET (GREASE) DUPLICATE WITH 10-81084;
| 10-81172-1 | 0107-01 | 1 | 0.75 | Transmission |  | Valves |  |  | Unknown |  | 2010-10-04 | 2010-10-13 | Other | GREASED | Steel/Wrought Iron |  | OAKLAND | VALVE B17 ON FRUITVALVE N/O ALAMEDA; SERVICE VALVE (GREASE VALVE); GREASE VALVE; DUG UP THEN GREASED VALVE
| 10-81189-1 | 0115-01 | 0.31 | 0.75 | Transmission |  | Other |  | UNION | Construction Defect |  | 2010-10-05 | 2010-10-23 | Other | UNION | Steel/Wrought Iron |  | OAKLAND | VALVE IN STR INFO ADRSS; REFER TO T&R; RELACED UNION
| 10-81193-1 | 105N | 35.06 | 3 | Distribution Main |  | Valves |  |  | Unknown |  | 2010-10-05 | 2010-10-18 | Other | GREASED VALVE | Steel/Wrought Iron |  | OAKLAND | D72 VALVE IFO ADRSS; VALVE C72 & D38 NO VALVE D72 NEED GREASE;GREASED VALVE TO REPAIR LEAK; GREASED 3" MAIN VALVE TO STOP LEAK
| 10-81196-1 | 153 | 26.68 | 0.75 | Transmission |  | Valves |  |  | Other | TIGHTEN FITTING | 2010-10-05 | 2010-10-22 | Other | GREASE VALVE | Steel/Wrought Iron |  | OAKLAND | LEAK VISUAL W/SOAP ON BYPASS VALVES & THREADS; REFER TO T&R OR SERVICE; SOAP TEST FOUND NO OTHER LEAKS
| 10-81206-1 | 153 | 25.15 | 20 | Transmission |  | Valves |  |  | Atmospheric Corrosion |  | 2010-10-06 | 2010-10-22 | Other |  | Steel/Wrought Iron |  | OAKLAND | 15' FROM SW CORNER OF ADDRESS/@ CURB FT OF 25A; FV SIDEWALK GREASE;
| 10-81207-1 | 153 | 25.08 | 0.75 | Transmission |  | Valves |  |  | Other | NO GREASE | 2010-10-06 | 2010-10-23 | Other | GREASE | Steel/Wrought Iron |  | OAKLAND | H AT ENT. TO PIER ON SW SIDE; SAME; SAME; REFER TO T&R
| 10-81245-1 | 0111-02 |  | 1 | Transmission |  | Other |  | NIPPLES | Other | FITTINGS | 2010-10-08 | 2010-10-23 | Tighten Cap or Bolt | DOPE FITTINGS | Steel/Wrought Iron |  | OAKLAND | SERICE TO BUILD OFF WOOD ST. MTR#42385530; SAME; SAME; HOT CISET AT SEWER TRACTMENT PLANT HIGH TO HIGH; DOPE FITTINGS
| 10-81246-1 | 0111-02 | 0.39 | 0.75 | Single Service |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-08 | 2010-10-27 | Other | C/O SVC | Steel/Wrought Iron |  | OAKLAND | READINGS W/I 5' OF WALL OFF WOOD ST.; LK ON MAIN IN VENT; MAIN IN ST. VENT; C/O 3/4" STL SVC/ GAS LINE NOT IN SVC; C/O SVC TOMAIN IN SIDEWALK.
| 10-81128-1 | 1 |  | 20 | Transmission |  | Fitting |  |  | Other | FITTING LOOSE | 2010-10-07 | 2010-10-16 | Other | GREASE | Steel/Wrought Iron |  | RICHMOND | XST ADAMS; REG STA, V-10/FV-66; N111, N112 0%; V109/FV67 2%; VF110/FV66 1%; VAULT .1%; LOOSE FITTINGS @ LEAKING VIL; SOAP TEST; VLV N-109 FOUND GREASE FITTING LOOSE. VLV N-110 FOUND GREASE FITTING LOOSE; TIGHTENED FITTINGS. ALSO GREASED FITTING LEAKING @ VLV GREASED BUTTON HEADS.
| 10-81163-1 | 0141-01 | 0.39 | 0.25 | Distribution Main |  | Fitting |  |  | Other | LOOSE FITTING | 2010-10-04 | 2010-10-20 | Other | TIGHTENED FITTING | Steel/Wrought Iron |  | CROCKETT | VALVE T MTR B4 CUST. PIPELINE; SAME; TIGHTENED FITTING; T @ ECAT SENSING LINE LEAKING, THIS IS A DISTRIBUTION 50# SERVICE TO C&H SUGAR
| 10-81173-1 | 00141-01 |  | 2 | Transmission |  | Girth Weld |  |  | Weld Failure |  | 2010-10-04 | 2010-10-05 | Patch Weld - Weld |  | Steel/Wrought Iron |  | CROCKETT | READINS OVER SERVICE TO BOILER ROOM @ TRUCK AREA; LEAK ON WELD BYPASS TAPE UP; REWELDED BY PASS; ALL ABOVE GROUND SEE ATTACHMENT
| 10-81082-1 | 3017-01 |  | 4 | Transmission |  | Unknown |  |  | Unknown |  | 2010-10-03 | 2010-10-16 | Other | REMOVED PIPE & CAP | Steel/Wrought Iron |  | DANVILLE | REMOVED PIPE; SOAP TEST; G.C. REMOVED REG. STA.; SEE ATTACHED
30 | 10-81086-B |  |  | 0.5 | Single Service |  | Body of Pipe | Other |  | Construction Defect |  | 2010-10-03 | 2010-12-07 | Replace Partial Service |  | Aldyl A (Tan or Gray) |  | ALAMO | LOCATED CENTER LINE OF MIRANDA IN FRONT OF 3154; OUR DIST. MAIN; SAME; OVER SVC T; REPALCED 1' OF 1/2" PL & INSTALLED STIFFNER; ISNTALLED 1' OF 1/2" PL & NEW STIFFNER AT SVC T
| 10-81087-1 | 3017-01 |  | 1.25 | Single Service |  | Other |  | PLUG | Other |  | 2010-10-03 | 2010-10-19 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ALAMO | STONE VLY & MIRANDA INSIDE MN VLV REGULATIOR; PLUG ON OUTLET TEE; NOT TRANMISSION LEAK, LEAK ON DOWNSTREAM SIDE OF OUTR.; SEE ATTACHED
30 | 10-81203-A | 11 |  | 2 | Transmission >= 20% SMYS |  | Fitting |  |  | Other | GASKET | 2010-10-04 | 2010-10-15 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | MARTINEZ | E/S BRIONES; 60' S/EDGE OF ALAMGED VALLEY: M/H; YELLOW; SAME; REPLACED GASKET & TIGHTENED BOLTS; REPLACED GASKET & TIGHTENED BOLTS
| 10-81524-1 | [10 empty] | 2010-10-03 | [5 empty] | LAFAYETTE | 15% GAS AT ELEC POLE IN PARKING AREA; OVR DISTRIBUTION; MIGRATING
| 10-81563-1 | X6499 |  | 12 | Transmission |  | Valves |  |  | Other |  | 2010-10-02 | 2010-10-19 | Other | GREASED | Steel/Wrought Iron |  | MORAGA | (T.P. LEAK); 40' S/O STMARYS RD, NXT TO VALVE B28; SAME; GREASED VALVE;
| 10-81644-1 | 1111 |  | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2010-11-04 | 2010-10-02 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | MARTINEZ | OLIVE & SHELL; PATCH ON SHELL, OLD PAINT DOT; SAME; SOAP
| 10-81102-1 | 177A | 158.23 | 12 | Transmission |  | Girth Weld |  |  | Construction Defect |  | 2010-10-11 | 2010-10-15 | Welded Sleeve/Can - Weld |  | Steel/Wrought Iron |  | Elevation 2438 | 6FT. FROM INR'CTION LOCATOR POLE; BY YELLOW FLAG REG DAMAGE; WELDED SLEEVE
| 10-81102-1 | 137C |  | 4 | Transmission |  | Other Welds |  |  | Construction Defect |  | 2010-10-02 | 2010-11-11 | Patch Weld - Weld |  | Steel/Wrought Iron |  | BAYSIDE | DOMAIN #1106. GROUP #L137C. DIST#37.; WELD REPAIR
| 10-81042-1 | 21G |  | 8 | Transmission |  | Valves |  |  | Other | GREASE FITTING | 2010-10-02 | 2010-10-14 | Other | TIGHTENED GREASE CAP. SMALL FUZZ LEAK. | Steel/Wrought Iron |  | SAN RAFAEL | SPRUCE & SEQUOLA REG. ST. 9110; YELLOW DOT; SAME; SAME; TIGHTENED GREASE CAP.
| 10-81082 | 0402-05 | 0.92 | 3 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-01 | 2010-12-20 | Skinner Clamp - Clamp |  | Steel-Other |  | SAN RAFAEL | IN FRONT OF DRIVEWAY @ YELLOW DOT; IN FRONT OF DRIVEWAY @ YELLOW DOT DISTRIBUTION MAIN; INSTALLED SKINNER CLAMP; PUT 5" SKINNER CLAMP 11' W/O 10" T.P. MAIN.
| 10-81062-1 | 1 |  | 0.75 | Service |  | Fitting |  |  | Unknown |  | 2010-10-05 | 2010-10-19 | Other | TIGHTEN UNION | Steel/Wrought Iron |  | BENICIA | VAULT NXT TO ELEC BOX; SAME; TIGHTENED UNION; NO CHANGE IN ORIGINAL SKETCH; SEE BACK.
| 10-81024-1 | 0405-01 | 22.07 | 0.75 | Transmission |  | Regulator | Tap Connection |  | Other | LOOSE FITTINGS | 2010-10-09 | 2010-10-19 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | ST. HELENA | YELLOW DOT HPR SVC FOR BOTTLING PLANT; SAME;
| 10-81043-1 | 0407-01 | 12.15 | 0.75 | Single Service |  | Fitting |  |  | Other | LOOSE | 2010-10-07 | 2010-10-27 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | YOUNTVILLE | IFO STORE; YELLOW PAINT; SAME; TIGHTENED CAP ON PIN-OFF TEE; SOAP TEST
| 10-81044-1 | 0407-01 | 11.92 | 0.75 | Transmission |  | Regulator |  |  | Other | LOOSE THREADS | 2010-10-07 | 2010-10-19 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | YOUNTVILLE | GTLS SPECIAL SURVEY 1003 N-CANFIELD DFM; YNTVIL INN HOTEL BY MTR YELLOW DOT; SAME; TIGHTENED LOOSE THREADS
| 10-81046-1 | 0407-01 | 10.08 | 0.75 | Transmission |  | Regulator |  |  | Equipment Malfunction |  | 2010-10-07 | 2010-10-19 | Other | REPLACED REGULATOR | Steel/Wrought Iron |  | YOUNTVILLE | REG STA. INFO 5452 W/ YELLOW DOT; SAME; REPLACED REGULATOR; SOAP TEST
| 10-81047-1 | 0407-01 | 9.75 | 0.75 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2010-10-07 | 2010-10-20 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | YOUNTVILLE | GTLS SPECIAL SURVEY 1003 N-CAN FIELD DFM; IFO 5340 W/YELLOW DOT; SAME; TIGHTENED FITTING; SOAP TEST
| 10-81050-1 | 0407-01 |  | 2 | Transmission |  | Valves |  |  | Unknown |  | 2010-10-07 | 2010-10-20 | Other | GREASED VALVE | Steel/Wrought Iron |  | NAPA | S/W CRNR W/XST SALVADOR; YELLOW DOT; SAME; GREASED VALVE 11-22-10; NO CHANGE TO SKETCH
| 81051-1 | 0407-01 |  | 0.75 | Single Service |  | Fitting |  |  | Other | LOOSE | 2010-10-07 | 2010-10-27 | Other | REPLACED UNION | Steel/Wrought Iron |  | NAPA | XST SLAVADOR NXT TO BUS STOP; YELLOW DOT; REG OR VALVE?; REPLACED UNON; SOAP TEST
| 10-81054-1 | 0407-01 | 4.7 | 8 | Transmission |  | Mechanical Joint |  |  | Other | LOOSE FITTINGS | 2010-10-08 | 2010-10-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | NAPA | TIGHTEN GREASE CAPS, REPLACED BODY BLEED VALVE
| 10-81057-1 | 0407-01 | 6.45 | 1 | Transmission |  | Other |  | CAP ON SAVA VALVE | Construction Defect |  | 2010-10-08 | 2010-10-18 | Other | NEW 1440 CAP REDOPED TIGHTEND | Steel/Wrought Iron |  | NAPA | NEW 1440 CAP REDOPED & TIGHTENED UNION
| 10-81059-1 | 1 |  | 4 | Transmission |  | Valves |  |  | Other | NEED GREASE | 2010-10-10 | 2010-11-19 | Other | GREASE | Steel/Wrought Iron |  | NAPA | GREASED VALVE; SOAP TEST
| 10-81142-1 | DF9905 | 1 | 3 | Transmission |  | Valves |  |  | Unknown |  | 2010-10-06 | 2010-10-11 | Other | GREASE VALVE & SERVICE | Steel/Wrought Iron |  | NAPA | INJECT GREASE IN VALVE TO REPAIR
| 10-81143-1 | 0408-01 | 2.81 | 0.75 | Transmission |  | Other |  | TUBE FITTING | Other | LOOSE FITTING | 2010-10-06 | 2010-10-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | NAPA | TIGHTEN UP & SEAL LOOSE FITTING; FOUND SCADA TAP FITTING LEAKING TIGHTEN UP TO REPAIR
| 10-81145-1 | 0408-01 | 1.12 | 2 | Transmission |  | Fitting |  |  | Construction Defect |  | 2010-10-08 | 2010-12-27 | Other | SEE ABOVE | Steel/Wrought Iron |  | NAPA | REMOVED, REDOPED AND RETIGHTENED CAP; REMOVED, REDOPED, & RETIGHTENED CAP ON SAVE-A-VALVE
| 10-81166-1 | 0406-08 | 0.45 | 2 | Transmission |  | Valves |  |  | Other | LUBE | 2010-10-08 | 2010-10-16 | Other | LUBED VALVE | Steel/Wrought Iron |  | NAPA | LUBE & CYCLED VALVE
| 10-81205-1 | 1 |  | 0.75 | Transmission |  | Other |  | PIN OFF T CAP | Unknown |  | 2010-10-10 | 2010-10-20 | Other | TAPED SEALANT | Steel/Wrought Iron |  | NAPA | TAPED & DOPED CAP; NO CHANGE TO EXISTING SKETCH; SEE ATTACH
| 10-81094-1 | 1303-01 |  | 0.75 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2010-10-06 | 2010-10-11 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SANTA ROSA | REDOPED & TIGHTEN
| 10-81024-1 | 108 | 71.43 | 0.75 | Single Service |  | Body of Pipe |  |  | External Corrosion |  | 2010-10-05 | 2010-10-18 | Replace Entire Service |  | Steel/Wrought Iron |  | SACRAMENTO | RENEW G.S. PM. 30810519; RENEW GAS ON PM 30810519
| 10-81042-1 | 119B | 1.97 | 0.75 | Single Service |  | Other |  | STL CAP | Construction Defect |  | 2010-10-10 | 2010-11-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SACRAMENTO | RELACED BRASS PLUG & CAP TIGHTENED; SOAP TESTED @ LINE PRESSURE OK
| 10-81044-1 | 0608-01 | 1.78 | 1 | Single Service |  | Valves |  |  |  |  | 2010-10-04 | 2010-11-09 | Other | REPLACED GREASE FITTING & GREASE VALVE | Steel/Wrought Iron |  | SACRAMENTO | DUG OUT VALVE FRAME, REPLACED GREASE GITTINIGS, GREASED VALVE. SOAPED OK.; DUG OUT VALVE CASING, REPLACED GREASE FITTING. GREASED VALVE. SOAPED OK. REPAIR LOCATION INSIDE VALVE CASING FOR CURB VALE.
| 10-81042-1 | 118A |  | 0.75 | Transmission |  | Regulator |  |  | Incorrect Operation |  | 2010-10-01 | 2010-10-17 | Other | REBUILT REGULATOR | Steel/Wrought Iron |  | FRESNO | REBUILT REGULATOR; SOAP TESTED REPAIRS OK
| 10-81044-1 | 118A |  | 0.25 | Transmission |  | Other |  | 1/4" PLUG | Other | LOOSE | 2010-10-01 | 2010-10-19 | Other | REDOPED & TIGHTEN 1/4" PLUG | Steel/Wrought Iron |  | FRESNO | REPLACED PLUG AND TIGHTENED (NO LEAK) (COMPLETED); SOAP TEST OK; SEE ATTACHED DWG
| 10-81045-1 | 1202-08 |  | 2 | Distribution Main |  | Valves |  |  | Other | OPERATED VALVE | 2010-10-01 | 2010-10-16 | Other | ADJUSTED | PE2406/2708 (Yellow) |  | FRESNO | VALVE RESEATED ITSELF IN BODY OF VALVE; SEE ATTACHED DRAWING
| 10-81047-1 | 118A |  |  | Transmission |  | Regulator |  |  | Other | LOSE FITTING | 2010-10-02 | 2010-11-01 | Other | UNION | Steel/Wrought Iron |  | FRESNO | TIGHTENED UNIONS ON REGULATOR; TIGHTENED UNONS- SOAP TEST
| 10-81048-1 | 118A |  | 0.75 | Single Service |  | Regulator |  |  | Other | RUST IN REGULATOR | 2010-10-02 | 2010-10-22 | Other | REPLACED REGULATOR H202 RELIEF, AND DOWNSTREAM VALVE | Steel/Wrought Iron |  | FRESNO | REGULATOR DIRTY RUSTY INSIDE (COMPLETED); REPLACED REGULATOR, H202 RELIEF, AND DOWNSTREAM BROKEN VALVE (TANG). CHECKED REGULATOR FOR LOCK UP, TESTED H202 RELIEG WITH EATON. SOAP TESTED OK (COMPLETED)
| 10-81049-1 | 1217-01 |  | 0.25 | Transmission |  | Other |  | FILTER | Other | LOOSE FITTING | 2010-10-02 | 2010-10-16 | Other | TIGHTENED FITTING | Steel/Wrought Iron |  | FRESNO | TIGHTENED STAINLESS STEEL FITTING/SOAP TEST
| 10-81050-1 | 118A |  | 0.25 | Distribution Main |  | Fitting |  |  | External Corrosion |  | 2010-10-02 | 2010-10-17 | Fill Weld - Weld |  | Steel/Wrought Iron |  | FRESNO | WELDED GAUGE TAP SHUT; SOAP TESTED WELDED
| 10-81083-1 | 1111111 |  | 0.75 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2010-10-03 | 2010-10-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN JOAQUIN | TIGHTENED CAP/NO LEAK; TIGHTENED 3/4" PLUG AND GREASED VALVE ON DRIP/COMPLETED NO LEAK
| 10-81084-1 | 1111111 |  |  | Transmission |  | Valves |  |  | Other | NEEDED GREASE | 2010-10-03 | 2010-10-14 | Other | GREASED VALVE | Steel/Wrought Iron |  | FRESNO | GREASED VALVE (COMPLETED); SOAP TESETD; SEE ATTACHED DRAWING
| 10-81103-1 | 1202-22 |  | 6 | Transmission |  | Regulator |  |  | Other | O-RING | 2010-10-02 | 2010-10-21 | Other | 'O' RINGS | Steel/Wrought Iron |  | FRESNO | REPLACED OUTER 'O' RINGS; REPLACED O-RINGS (OUTER) IN REGULATOR R-4 (GROVE) SOAP TESTED OK
| 10-81107-1 | 11 |  | 12 | Transmission |  | Valves |  |  | Other | GREASE | 2010-10-04 | 2010-11-02 | Other | GREASE | Steel/Wrought Iron |  | FRESNO | VALVE NEEDED GREASE
| 10-81124-1 | 122001 |  | 0.5 | Transmission |  | Fitting |  |  | Other | LOSE FITTING | 2010-10-04 | 2010-11-02 | Other | TIGHTENED FITTING | Steel/Wrought Iron |  | SANGER | GREASE FITTING ON VALVE; TIGHTENED FITTING
| 10-81125-1 | 11 |  |  | Transmission |  | Regulator |  |  | Other | NIPPLE GOING INTO REGULATOR LEAKING | 2010-10-04 | 2010-11-02 | Other | REDOPED & RETIGHTENED | Steel/Wrought Iron |  | FRESNO | REDOPED & RETIGHTENED PIPE NIPPLE; SEE BELOW (SOAP TEST)
| 10-81142-1 | 11 |  | 0.625 | Transmission |  | Regulator |  |  | Construction Defect |  | 2010-10-03 | 2010-10-11 | Tighten Cap/Bolt - Fitting |  | Other | S. S. TUBE FTG | ATWATER | TIGHTENED FITTING; LEAK NOTED S.S. FITTING V-2 RUN FIRST. CUT VAULT MOONEY REG. PILOT. T&R TIGHENED FITTING, LEAK STOPPED. SOAP TESTED OK
| 10-81143-1 | 11 |  | 8 | Transmission |  | Fitting |  |  | Other | DRY PIPE DOPE | 2010-10-03 | 2010-10-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MERCED | RESEALED 3/4" PLUG; REMOVED 3/4" PLUG TOP OF MUNNER APPLIED SEALANT REINSTALLED
| 10-81144-1 | 11 |  | 2 | Distribution Main |  | Valves |  |  | Other | GREASE | 2010-10-03 | 2010-10-08 | Other | GREASED | Steel/Wrought Iron |  | MERCED; | ADDED GREASE; SOAP TEST OK
| 10-81145-1 | 11 |  | 6 | Transmission |  | Valves |  |  | Other | NEEDED GREASE | 2010-10-03 | 2010-10-08 | Other | GREASED VALVE | Steel/Wrought Iron |  | MERCED | GREASE, SOAP PER SXGE; SOAP TEST OK
| 10-81146-1 | 11 |  | 2 | Transmission |  | Valves |  |  | Other | NEEDED GREASE | 2010-10-03 | 2010-10-08 | Other | GREASED VALVE | Steel/Wrought Iron |  | MERCED | GREASE, SOAP; BLOW-OFF VALVE V-B SOAP TEST OK
| 10-81149-1 | 11 |  | 2 | Transmission |  | Other |  | FILTER | Other | BOLTS | 2010-10-04 | 2010-10-08 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | CHOWCHILLA | TIGHTEN BOLTS; SOAP TEST OK
| 10-81150-1 | 11 |  | 0.75 | Single Service |  | Fitting |  |  | Other | UNION THREADS | 2010-10-04 | 2010-10-07 | Other | TIGHTEN UNION | Steel/Wrought Iron |  | CHOWCHILLA | TIGHTEN UNION; SOAP TEST OK
| 10-81151-1 | 11 |  | 0.75 | Single Service |  | Valves |  |  | Other | GREASED | 2010-10-04 | 2010-10-08 | Other | GREASED | Steel/Wrought Iron |  | FAIRMEAD | GREASED VALVE; SOAP TEST OK
| 10-81157-1 | 118A | 23.37 | 2 | Distribution Main |  | Valves |  |  | Other | GREASE | 2010-10-04 | 2010-11-10 | Other | GREASED VALVE | Steel/Wrought Iron |  | MADERA | GREASED & OPERATED; SOAP TESTED PER DJGE
| 10-81166-1 | 1 |  | 0.75 | Transmission |  | Other |  | FILTERS | Other | SEALS | 2010-10-07 | 2010-10-19 | Other | DESSICANT POT | Steel/Wrought Iron |  | MADERA | REMOVE AND REPLUMBED; SOAP TEST OK
| 10-81167-1 | 1 |  | 0.25 | Transmission |  | Fitting |  |  | Other | RE-DOPE | 2010-10-07 | 2010-10-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MADERA | DOPED & RETIGHTENED; SOAP TEST OK
| 10-81168-1 | 1 |  | 3.5 | Transmission |  | Valves |  |  | Other | GREASE | 2010-10-07 |  | Other | GREASED | Steel/Wrought Iron |  | FIREBAUGH | GREASED VALVE; BURIED VALVE
| 10-81170-1 | 1 |  | 0.25 | Transmission |  | Other |  | PLUG THREADS | Other | DRY DOPE | 2010-10-07 | 2010-10-11 | Other | RE-DOPE & THIGHTEN PLUG. | Steel/Wrought Iron |  | FIREBAUGH | RE-DOPED & TIGHTENED 1/4" STL. PLUG; RE-DOPED & TIGHTENED 1/4" PLUG ON 1/4" GAUGE TAR IN PRIMARY REG. VAULT SOAP TEST OK.
| 10-81172-1 | 134 | 1.75 | 0.75 | Single Service |  | Valves |  |  | Other | GREASE | 2010-10-07 | 2010-10-22 | Other | GREASED | Steel/Wrought Iron |  | MENDOTA | GRESED VALVE; HPR RD-09
| 10-81174-1 | 134A | 21.34 | 8.625 | Transmission |  | Valves |  |  | Other | GREASE | 2010-10-08 | 2010-10-20 | Other | GREASE | Steel/Wrought Iron |  | MENDOTA | GREASED VALVE; BURIED BLOW-OFF SEPARATED MAIN LINE VALVE SOAP TEST
| 10-81203-1 | 1 |  | 0.75 | Single Service |  | Other |  | RELIEF | Other | DIRT | 2010-10-08 | 2010-10-22 | Other | RELIEF VALVE | Steel/Wrought Iron |  | DOS PALOS | REPLACE RELIEF PRESS LOCK UP OK ; SOAP TEST OK
| 10-81222-1 | 7207-01 | 51 | 0.75 | Single Service |  | Fitting |  |  | Other | TIGHTEN | 2010-10-06 | 2010-10-14 | Other | UNION | Steel/Wrought Iron |  | MENDOTA | CLEAN THREADS TIGHTEN UNON; SOAP TEST OK PAINTED SET
| 10-81224-1 | DREG5444 | 0.01 | 0.75 | Service |  | Valves |  |  | Other | GREASE | 2010-10-08 | 2010-10-16 | Other | GREASED VALVES | Steel/Wrought Iron |  | FIREBAUGH | GREASED VALVES IN REG STATION SOAP TEST OK; SOAP TEST OK
| 10-81225-1 | 7207-01 | 0.59 | 0.75 | Single Service |  | Other |  | RELIEF | Other | SEAT | 2010-10-09 | 2010-10-18 | Other | FISHER RELIEF | Steel/Wrought Iron |  | MENDOTA | RELIEF ON HPR WAS REPLACED; SOAP TEST
| 10-81241-1 | 331A | 8.39 | 4 | Single Service |  | Valves |  |  | Other | GREASE | 2010-10-06 | 2010-10-14 |  |  | Steel/Wrought Iron |  | SANTA NELLA | GREASE; SOAP TEST OK
| 10-81281-1 | 7210-01 | 7.99 | 4 | Distribution Main |  | Valves |  |  | Other | GREASE DRY | 2010-10-06 | 2010-10-20 | Other | GREASED | Steel/Wrought Iron |  | LOS BANOS | GREASED; GREASED; SOAP TEST OK
| 10-81282-1 | 7210-01 | 7.96 | 4 | Distribution Main |  | Fitting | Other | 4" M/2 CAP. | Other | DRIED DOPE | 2010-10-06 | 2010-10-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | LOS BANOS | REDOPE TIGHTEN CAP ON 4" HZ; REDOPED & TIGHTENED CAP ON 4" H/Z CAP. SOAP TEST
| 10-81283-1 | 7210-01 | 6.36 | 0.75 | Transmission |  | Other |  | CRACKED FITTING | Other | CRACKED 3/4 STL H.P ELBOW | 2010-10-06 | 2010-10-28 | Fill Weld - Weld |  | Steel/Wrought Iron |  | LOS BANOS | WELDED OVER CRACK IN FITTING; FOUND CRACKED 3/4 STL ELBOW INLET SIDE OF H.P.R. @ NAGE OF H.P.R.
| 10-81284 | 7210-01 | 5.43 | 0.75 | Branch Service |  | Fitting |  |  | Construction Defect |  | 2010-10-06 | 2010-11-21 |  |  | Steel-Other |  | LOS BANOS | WELD REPAIR; WELD REPAIR ON FITTING. SOAP TEST
| 10-81285-1 | 7210-01 | 0.96 | 2 | Transmission |  | Valves |  |  | Other | GREASE | 2010-10-09 | 2010-10-16 | Other | GREASED VALVE | Steel/Wrought Iron |  | LOS BANOS | GREASED VALVE; SOAP TEST OK
| 10-81401-1 | 11 |  | 2 | Distribution Main |  | Valves |  |  | Other | GREASE | 2010-10-06 | 2010-10-11 | Other | GREASED | Steel/Wrought Iron |  | WINTON | GREASED & OPERATED; SOAP TEST OK
| 10-81421-1 | DREG5507 | 0 | 4 | Distribution Main |  | Valves |  |  | Other | GREASE | 2010-10-06 | 2010-10-13 | Other | GREASED | Steel/Wrought Iron |  | MERCED | GREASED & OPERATE; SOAP TEST OK
| 10-81422-1 | 1 |  | 4 | Distribution Main |  | Valves |  |  | Other | GREASE | 2010-10-07 | 2010-10-12 | Other | ADDED GREASE | Steel/Wrought Iron |  | MERCED | ADD GREASE; ADD GREASE; TIGHTEN S.S. FITTING MONITOR REG. AT SOAP TEST
| 10-81423-1 | 118A | 56.85 | 1.25 | Transmission |  | Fitting |  |  | Other | THREADS | 2010-10-10 | 2010-10-17 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MERCED | REDOPED AND TIGHTENED 11/4" PLUG, SOAPED; SOAP TESTED OK
| 10-81441-1 | DCUST868 | 0 | 0.75 | Single Service |  | Fitting |  |  | Other | PIPE DOPE | 2010-10-06 | 2010-10-11 | Deactivated Entire Service |  | Steel/Wrought Iron |  | MADERA | REPAIRED SHUT OFF SET NOT NEEDED; SOAP TEST OK
| 10-81461-1 | 1 |  | 0.25 | Transmission |  | Fitting |  |  | Other | LOOSE PLUG | 2010-10-07 | 2010-10-12 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MERCED | TAPPED & TIGHTENED
| 10-81462-1 | 1 |  | 0.75 | Single Service |  | Valves |  |  | Other | DIRT | 2010-10-07 | 2010-10-12 | Other | REPLACE RELIEF | Steel/Wrought Iron |  | MERCED | REMOVE DIRT & REPLACE RELIEF
| 10-81464-1 | 1 |  | 0.75 | Single Service |  | Valves |  |  | Other | PACKING | 2010-10-07 | 2010-10-11 | Other | PACKING NUT | Steel/Wrought Iron |  | CHOWCHILLA | TIGHTEN PACKIG NUT
| 10-81469-1 | 118A | 17.94 | 8 | Transmission |  | Valves |  |  | Other | GREASE | 2010-10-08 | 2010-10-18 | Other | GREASED | Steel/Wrought Iron |  | MADERA | GREASED & OPERATED; SOAP TEST OK
| 10-81473-1 | 118A | 60.48 | 0.25 | Transmission |  | Fitting | Other | PLUG | Other | DOPE DRY | 2010-10-10 | 2010-10-15 | Tighten Cap or Bolt | TIGHTEN | Steel/Wrought Iron |  | MERCED | TIGHTEN FITTINGS; SOAP TEST OK
| 10-81475-1 | DREG4416 |  | 4 | Transmission |  | Valves |  |  | Other | GREASE | 2010-10-10 | 2010-10-18 | Other | GREASE | Steel/Wrought Iron |  | MADERA | GREASE VALVE TO FIX LEAK; GREASED VALVE AND SOAP TESTED
| 10-81700-1 | 118B | 8.09 | 0.25 | Single Service |  | Valves |  |  | Other | GREASE | 2010-10-08 | 2010-10-13 | Other | GREASE | Steel/Wrought Iron |  | MADERA | GREASED; OPERATED; SOAP TEST OK
| 10-81705-1 | 118B | 10.3 | 0.75 | Transmission |  | Other |  | SAV-A-VALVE CAP LOOSE | Other | LOOSE CAP. | 2010-10-14 | 2010-11-08 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | MADERA | REMOVED CAP REDOPED TIGHTENED; FOUND LOOSE 3/4" CAP ON SAV-A-VALVE; *NOTE( THERE ARE FOR SOME REASON (2) INTERSECTING POINTS OF ¦ ST. *READINS FOR THE S/W NEEDED
| 10-81108-1 |  |  | 0.75 | Single Service | DISTRIBUTION SIDE | Fitting |  |  | Unknown |  | 2010-09-26 | 2010-10-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN JOSE | FOUND MUELLER CAP LEAKING GAS (DISTRIBUTION SIDE); FOUND MUELLER CAP LEAKING, REMOVED, REDOPED & TIGHTENED BACK UP (SOAP TEST OK); SEE ATTACH
| 10-81532-1 | 0817-01 | 0.71 | 0.75 | Single Service |  | Other |  | THREADS @ SERVICE VALVE | Other | LOOSE VALVE | 2010-10-10 | 2010-10-29 | Other | TIGHTEN SVC VALVE @ METER SET | Steel/Wrought Iron |  | SAN JOSE | REPAIRED LEAK; TIGHTENED FITTINGS- SOAP TEST OK (VALVE)
| 10-81683 | 300A | 473.97 | 4 | Transmission >= 20% SMYS |  | Fitting |  |  | Other | TIGHTEN | 2010-10-11 | 2010-12-14 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | MORGAN HILL | TIGHTEN; TIGHTEN, SOAPED OK
| 10-81685 | 300A | 473.97 |  | Transmission >= 20% SMYS |  | Other |  | SCADA TAP VALVE | Other | RESEAT | 2010-10-11 | 2010-12-14 | Other | RESEATED | Steel-Other |  | MORGAN HILL | RESEATED; RE-SEATED VALVE-(PINN-OFF) SOAP TEST; SEE ATTACHED SKETCH
| 10-81205 |  |  | 2 | Transmission |  | Other |  | PILOT REGULATOR | Other | BAD O RING | 2010-09-25 | 2010-10-04 | Other | INSTALL NEW ORFICE BLOCK | Steel/Wrought Iron |  | MOUNTAIN VIEW | SHUT DOWN REG STA. FOR REPAIR
| 10-81206-1 |  |  | 0.375 | Transmission |  | Fitting |  |  | Other | NEEDED DOPE | 2010-09-25 | 2010-10-12 | Tighten Cap or Bolt | PIPE DOPE | Steel/Wrought Iron |  | MT. VIEW | PIPE DOPE SENCE LINE FITTING; SOAP TESTED, NO LEAKS
| 10-81642-1 | 5814/132 | 9 | 4 | Transmission |  | Valves |  |  | Other | NEED DOPE - GREASE | 2010-10-10 | 2010-10-15 | Other | GREASED VALVE | Steel/Wrought Iron |  | PALO ALTO | GREASED VALVE; SOAP TESTED, NO LEAKS
| 10-81643-1 | 5814/1 | 9 | 4 | Transmission |  | Valves |  |  | Other | NEEDED GREASE | 2010-10-10 | 2010-10-15 | Other | GREASED VALVE | Steel/Wrought Iron |  | PALO ALTO | GREASED VALVE; SOAP TESTED, NO LEAKS
| 10-81039-1 | 402 |  | 6 | Transmission |  | Fitting |  |  | Other | LOOSE CAP | 2010-09-30 | 2010-10-18 | Tighten Cap or Bolt | TIGHTENED FITTING | Steel/Wrought Iron |  | ANDERSON | TIGHTENED GAUGE CAP PIN-OFF "T"; SOAP TESTED, DOPED THREADS TIGHTENED CAP
| 10-81042-1 | 402 |  | 1 | Single Service |  | Fitting |  |  | Other | DRY DOPE | 2010-09-30 | 2010-10-08 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | REDDING | RE-GREASE AND TIGHTEN CAP; SOAP TEST VISUAL 580 PSIG OK
| 10-81043-1 | 402 |  | 2 | Transmission |  | Fitting |  |  | Other | GREASED FITTING | 2010-09-30 | 2010-10-06 | Other | GREASE, OPERATE | Steel/Wrought Iron |  | REDDING | GREASED AND OPERATED VALVE; GREASED AND OPERATED VALVE. SOAP TEST. PIPE CONDITION UNKNOWN SAW TOP OF VALVE ONLY. MAIN WAS NOT EXPOSED
| 10-81044-1 | 402 |  | 10 | Transmission |  | Fitting |  |  | Other | GREASE FITTING | 2010-09-30 | 2010-10-06 | Other | GREASE OPERATE | Steel/Wrought Iron |  | REDDING | TIGHTENED FITTING, ADDED GREASE; TIGHTENED GREASE FITTING. GREASED VA;VE P[ERATED SOAP TEST. PPE CONDITION UNKNOWN ONLY SAW TOP OF VALVE. MAIN WAS NOT EXPOSED
| 10-81045-1 | 402 |  | 10 | Transmission |  | Fitting |  |  | Other | LOOSE CAP | 2010-09-30 | 2010-10-15 | Tighten Cap or Bolt | OTHER | Steel/Wrought Iron |  | REDDING | TIGHTENED CAP ON PIN OFF "T"; SOAP TESTED TIGHTENED CAP, RE-WRAPPED
| 10-81046-1 | 5486/402 |  | 2 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2010-10-01 | 2010-10-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SHASTA LAKE CITY | TIGHTEN FITTINGS; VISUAL SOAP TEST 580PSIG OK
| 10-81047-1 | 5789/402 |  | 10 | Distribution Main |  | Regulator |  |  | Unknown |  | 2010-10-01 | 2010-10-07 | Other | CLEANING | Steel/Wrought Iron |  | SHASTA LAKE CITY | REMOVED, CLEANED; SOAP TESTED
| 10-81048-1 | 402 |  | 10 | Transmission |  | Regulator |  |  | Other | LOOSE BOLT | 2010-10-01 | 2010-10-07 | Tighten Cap or Bolt | OTHER | Steel/Wrought Iron |  | SHASTA LAKE CITY | TIGHTEN BOLT; SOAP TESTED, TIGHTENED BOLT IN BODY OF REG
| 10-81049-1 | 5485/402 |  | 10 | Transmission |  | Fitting |  |  | Unknown |  | 2010-10-01 | 2010-10-07 | Other | WIRE BRUSH PIPE DOPE | Steel/Wrought Iron |  | SHASTA LAKE CITY | WIRE BRUSH AND PIPE DOPE FORE REPAIR; SOAP TESTED, WIRE BRUSH, PIPE DOPE TIGHTEN
| 10-81050-1 | 5485/402 |  | 2 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2010-10-01 | 2010-10-09 | Other | TIGHTEN FITTING | Steel/Wrought Iron |  | SHASTA LAKE CITY | TIGHTEN FITTING; SOAP TEST VISUAL 580PSIG
| 10-81051-1 | 402 |  | 3 | Transmission |  | Valves |  |  | Other | DRY GREASE | 2010-10-01 | 2010-10-08 | Other | GREASE VALVE | Steel/Wrought Iron |  | REDDING | GREASE & OPERATE VALVE; GREASE, OPERATE VALVE, SOAP TEST VISUAL 580 PSI
| 10-81077-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | Other | SPLIT SEAM | 2010-09-29 | 2010-10-19 | Replace Dist Main < 100 ft |  | Steel/Wrought Iron |  | REDDING | INSTALLED (2) 3" M-2 FITTINGS. CUT OUT 2' OF 3" STEEL, REPLACED; INSTALLED (2) GAUGE-TEES, (2) 3" M-2. REPLACED 2' OF 3" STEEL
| 10-81042-1 | 118A |  | 0.75 | Single Service |  | Fitting | Other | RELIEF | Other | REGULATOR NO LUCK UP | 2010-10-05 | 2010-10-18 | Other | SEE ABOVE | Steel/Wrought Iron |  | HILMAR | PIPE & TIGHTEN FITTING. REPLACED REGULATOR; FIXED FITTING, REPLACED REGULATOR & RELIEF, SOAP TEST;
| 10-81043-1 | 118A | 84.31 | 0.75 | Single Service |  | Fitting |  |  | Other | DRIED PIPE DOPE | 2010-10-06 | 2010-10-18 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | TURLOCK | REMOVE CAP AND REDOPE; REMOVED CAP, DOPED AND REINSTALLED CAP. SOAP TESTED
| 10-81044-1 | 118A | 79.78 | 0.75 | Single Service |  | Fitting |  |  | Other | DRIED OUT PIPE DOPE | 2010-10-06 | 2010-10-19 | Other | REDOPED FITTINGS TIGHTEN FITTINGS | Steel/Wrought Iron |  | HILMAR | REDOPED PIPE FITTINGS & TIGHTENED FITTINGS; SOAP TESTED. REDOPED PIPE FITTINGS AND TIGHTEN UNONS. SOAP TESTED
| 10-81046-1 | 215 | 17.1 | 6 | Transmission |  | Fitting |  |  | Other | LOOSE | 2010-10-06 | 2010-10-16 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | TURLOCK | TIGHTEN FLANGE; TIGHTEN BOLTS ON FLANGE BLOW OFF. SOAP TEST.
| 10-81047-1 | 118E | 84.02 | 0.75 | Single Service |  | Fitting |  |  | Other | NEED PIPE DOPE | 2010-10-06 | 2010-10-18 | Tighten Cap or Bolt | PIPE DOPE & TIGHTEN CAP | Steel/Wrought Iron |  | TURLOCK | TIGHTEN CAP; PIPE DOPE CAP & TIGHTEN. SOAP TESTED
| 10-81064-1 | 148 |  | 8 | Transmission |  | Girth Weld |  |  | Weld Failure |  | 2010-10-02 | 2010-10-21 | Other | 8" PCF MUELLER | Steel/Wrought Iron |  | MODESTO | INSTALLED 8" PCF; SOAP TESTED. X-RAYED-FITTING IS NOT TAPPED OUT
| 10-81066-1 | 7219-01 |  | 0.75 | Service |  | Fitting |  |  | Other | DRIED PIPE DOPE | 2010-10-05 | 2010-10-22 | Other | REPLACED NIPPLE | Steel/Wrought Iron |  | MODESTO | REPLACED NIPPLE. TIGHTEN ALL FITTINGS; REPLACED NIPPLE ON REG. SOAP TESTED, REBUILT SET
| 10-81067-1 | DCST2656 |  | 0.75 | Single Service |  | Fitting |  |  | Other | NO DOPE | 2010-10-05 | 2010-10-15 | Other | REDOPE | Steel/Wrought Iron |  | MODESTO | REDOPED AND TIGHTENED; SOAP TEST
| 10-81068-1 | 7219-01 | 1.24 | 4 | Transmission >= 20% SMYS |  | Valves |  |  | Other | NEED GREASE | 2010-10-06 | 2010-10-19 | Other | GREASED VALVE | Steel/Wrought Iron |  | MODESTO | GREASED VALVE; GREASED VALVE AND SOAP TEST
| 10-81142-1 | 11 |  | 0.75 | Single Service |  | Fitting |  |  | Other | NO DOPE | 2010-10-03 | 2010-10-11 | Other | REDOPE | Steel/Wrought Iron |  | NEWMAN | REDOPED 2 FITTINGS; SOAP TEST
| 10-81144-1 | 11 |  | 0.75 | Single Service |  | Fitting |  |  | Other | DRY DOPE | 2010-10-03 | 2010-10-11 | Other | REBUILT | Steel/Wrought Iron |  | NEWMAN | REBUILT HPR SET. NEW REG & RELIEF; SOAP TEST; REBULT HPR SET FOUND LOTS OF LEAKS ON OLD SET
| 10-81146-1 | 7220-01 | [9 empty] | 2010-10-03 | [5 empty] | NEWMAN | PERFORM LEAK INVESTIGATION. HAVE PIN POINTED LEAK ON DISTRIBUTION MAIN
| 10-81147-1 | 7220-01 |  | 0.75 | Single Service |  | Valves |  |  | Other | DRIED DOPE | 2010-10-03 | 2010-10-06 | Other | GREASED VALVE | Steel/Wrought Iron |  | NEWMAN | GREASED VALVE; SOAP TESTED; VALVE IN HPR LEAKING GREASED VLAVE
| 10-81149-1 | 7220-01 | [9 empty] | 2010-10-03 | [5 empty] | GUSTINE
| 10-81151-1 | 7220-01 |  |  | Single Service |  | Fitting |  |  | Other | LOOSE UNION | 2010-10-07 | 2010-10-19 | Other | TIGHT UNION | Steel/Wrought Iron | ; | NEWMAN | TIGHTEN UNION & SOAP TEST; TIGHTEN UNON IN HPR BOX. SOAP TEST
| 10-81165-1 | 7228-16 |  | 6 | Transmission |  | Valves |  |  | Other | GREASE | 2010-10-04 | 2010-10-14 | Other | GREASED | Steel/Wrought Iron |  | RIVERBANK | GREASED & SOAPED; GREASED AND SOAP TEST
| 10-81167-1 | 7226-01 | 5.61 | 6 | Transmission |  | Valves |  |  | Other | NO GREASE | 2010-10-04 | 2010-11-04 | Other | GREASED VALVE | Steel/Wrought Iron |  | RIVERBANK | GREASED VALVE LEAK STOPPED
| 10-81082-1 |  |  | 2 | Distribution Main |  | Other |  | CAP | Other | DRY DOPE | 2010-09-26 | 2010-10-16 | Other | DOPE & RETIGHTEN CAP | Steel/Wrought Iron |  | STOCKTON | REDOPED & TIGHTEN CAP 2" SPLIT MUELLER; REDOPE & TIGHTEN 2" CAP ON SPLIT MUELLER. SOAP TEST
| 10-81084-1 | 1609-01 |  | 0.75 | Single Service |  | Fitting |  |  | Construction Defect |  | 2010-09-27 | 2010-10-07 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | STOCKTON | TIGHTEN TEE CAP; SOAP TESTED
| 10-81102-1 | 1613-01 |  | 0.75 | Transmission |  | Valves |  |  | Other | NEEDED GREASE | 2010-09-27 | 2010-10-06 | Other | GREASED VALVE | Steel/Wrought Iron |  | STOCKTON | GREASED VALVE; SOAP TESTED
| 10-81184-1 | 1617-01 | 0.8 | 0.75 | Transmission |  | Other |  | INLET VALVE TRANSMISSION | Atmospheric Corrosion |  | 2010-10-09 | 2010-10-17 | Other | TRANSMISSION INSTALLED NEW HPR | Steel/Wrought Iron |  | TRACY | REPLACED HPR SET; DUG UP AND REPLACED HPR SET, AND SOAP TESTED
| 10-81242 | 108 | 32.81 | 2 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | Unknown |  | 2010-09-28 | 2010-12-15 | Replace Entire Service | REPLACE DIST MAIN >= 100FT | Steel-Other |  | STOCKTON | INSTALLED 1 1/4" PL BY INSTERTING OLD MAIN. INSERTED 3 SERVICES; MAIN REPLACED BY INSERTING FOOTAGE AND MAP INCLUDED ON BACK, SERVICES INSERTED 1 SERVICE OUT TESET & TRANSFERED; SEE ATTACHED
| 10-81243-1 | 108 |  | 16 | Transmission |  | Valves |  |  | Other | CORE LEAK @ VALVE | 2010-09-28 | 2010-10-14 | Other | GREASED VALVE | Steel/Wrought Iron |  | THORNTON | GREASED VALVE TO STOP LEAK; SOAP TEST; SEE ATTACH MAP
| 10-81245-1 | 162A |  | 0.25 | Single Service |  | Valves |  |  | Other | LOOSE | 2010-09-28 | 2010-10-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | TRACY | TIGHTEN PACKING NUT; TIGHTEN PACKING NUT 1/4" METRIC- SOAP TEST
| 10-81323-1 |  |  | 0.75 | Transmission |  | Fitting |  |  | Atmospheric Corrosion |  | 2010-09-29 | 2010-10-15 | Other | REPLACED HPR | Steel/Wrought Iron |  | TRACY | REPLACED HPR & FITTINGS; SOAP TESTED - HPR BOX
| 10-81325-1 | 162 |  | 0.75 | Single Service |  | Regulator |  |  | Atmospheric Corrosion |  | 2010-09-29 | 2010-10-16 | Other | REBUILT REG STATION | Steel/Wrought Iron |  | TRACY | REBUILT REG; SOAP TEST
| 10-81421-1 | 197-AB |  | 0.5 | Transmission |  | Fitting |  |  | Material Failure |  | 2010-09-28 | 2010-10-13 | Other | VALVE BODY BLEED REPAIR | Steel/Wrought Iron |  | WOODBRIDGE | INSTALLED 3/4 SPLIT WITH SLEEVE REMVD PRESS RELIEF INSTD BELL VALVE; SOAP TESTED
| 10-81542-1 | 1615-04 |  | 0.25 | Single Service |  | Other |  | THRD'D PLUGS ON METRICS | Other | REDOPED TIGHTENED | 2010-09-29 | 2010-10-16 | Other | RE-DOPED/TIGHTENED | Steel/Wrought Iron |  | RIPON | REDOPED TIGHTENED 2 1/4" PLUGS; SOAPT TEST; SEE ATT'D
| 10-81545-1 | 1111111 |  | 0.375 | Transmission |  | Other |  | TIGHTENED TUBING FITTING | Other | TIGHTENED TUBING FITTING | 2010-09-29 | 2010-10-15 | Other | TIGHTENED 3/8" TUBING FITTING | Steel/Wrought Iron |  | RIPON | TIGHTENED 3/8" TUBING FITTING; SOAP TEST; SEE ATT'D
| 10-81546-1 | 1615-04 |  | 0.375 | Single Service |  | Other |  | STAINLESS FITTING IN VAULT | Other | LOOSE FITTING | 2010-09-29 | 2010-10-15 | Other | TIGHTENED | Steel/Wrought Iron |  | RIPON | TIGHTENED SENSE LINE FITTING IN PRIMARY; SOAP TEST; SEE ATTACHED
| 10-81547-1 | 1615-01 |  | 0.376 | Transmission |  | Other | Valves | 3/8" STAINLESS CONNECTOR FITTING IN VAULT | Other | RE-TAPED TIGHTENED FITTING | 2010-09-29 | 2010-10-15 | Other | RE-DOPED, TIGHTENED | Steel/Wrought Iron |  | RIPON | RETAPED FITTING, TIGHTENED; SOAP TEST; SEE ATTACHED
| 10-81550-1 | 1615-07 |  | 0.75 | Transmission |  | Other |  | RELIEF VALVE | Other | OLD VALVE | 2010-09-30 | 2010-10-15 | Replace Valve < 2 inch | RELIEF | Steel/Wrought Iron |  | RIPON | REPLACED RELIEF VALVE; REPLACED RELIEF VALVE - SOAP TEST
| 10-81551-1 | 1615-01 |  | 12 | Transmission |  | Valves |  |  | Other | PACKING LEAK ON 3/4" BALL VALVE | 2010-09-30 | 2010-10-15 | Other | TIGHTEN NUT OF 3/4" BALL VALVE | Steel/Wrought Iron |  | RIPON | TIGHTENED HEX NUT ON BALL VALVE; REPAIRED LEAK BY TIGHTENING UP PACKING NUTS ON HANDLE LOCATED IN VALVE FRAME & COVER SOAP TEST
| 10-81552-1 | 1615-04 |  | 0.75 | Transmission |  | Valves |  |  | Other | DRY DOPE | 2010-09-30 | 2010-10-15 | Other | REDOPE PLUG 1/4" | Steel/Wrought Iron |  | RIPON | REDOPE 1/4" PLUG; REDOPE 1/4" PLUG - SOAP TEST
| 10-81553-1 | 1615-04 |  | 0.75 | Transmission |  | Fitting |  |  | Other | DRY DOPE | 2010-09-30 | 2010-10-14 | Other | TIGHTEN 3/4" UNION DOPE 1/4" PLUG | Steel/Wrought Iron |  | RIPON | TIGHTEN 3/4" UNION & REDOPE 1/4" PLUG; TIGHTEN UNION - REDOPE PLUG SOAP TEST
| 10-81554-1 | 1 | [9 empty] | 2010-10-09 | [5 empty] | RIPON
| 10-81581-1 | 1611-03 |  | 6 | Distribution Main |  | Valves |  |  | Other | NO GREASE | 2010-09-30 | 2010-10-16 | Other | GREASED VALVE | Steel/Wrought Iron |  | STOCKTON | GREASED VALVE; SOAP TEST
| 10-81661-1 | 160701 |  | 6 | Distribution Main |  | Valves |  |  | Other | GREASE PACKING | 2010-09-30 | 2010-10-16 | Other | GREASE VALVE | Steel/Wrought Iron |  | MANTECA | GREASE VALVE TO STOP LEAK. REPAIRED GREASE FITTING; LEAK WAS ON VALVE, REPLACED GREASE FITTING, REPACKED VALVE WITH GREASE STOPPED LEAK SOAP TEST
| 10-88538- | 302-141 | 0.65 | 6 | Gathering |  | Other |  |  | Internal Corrosion | (SUSPECT) | 2010-10-19 | 2010-11-01 | Deactivate #TP Main |  | Steel/Wrought Iron |  | SUTTER | SHUT IN GAS PROD.; PIPELINE TO BE RETIRED ON JOB# 30818707; L-302 PIPE IS STRANED AND USED BY GAS PRODUCER. IT WILL BE RETIRED IN PLACE ON JOB # 30818707. PIPELINE WAS NOT EXCAVATED. PRODUCER WAS NOTIFIED TO SHUT IN THIS SECTION OF PIPE. PENDING RETIREMENT AND SALE.
| 10-88615-1 | 172A | 70.07 | 0.25 |  | SUPPLY | Other |  | UNION FITTING | Other | TIGHTEN FITTING | 2010-11-04 | 2010-11-18 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | DUNNIGAN | REPAIRED LEAK @ UNION AND PLUG ON SUPPL PACH
| 10-88730-1 | 220 |  | 10 | Transmission |  | Other |  | BELL/BELL-CHILL RING/JOINT | Unknown |  | 2010-10-20 | 2010-10-23 | Replace TP Main |  | Steel/Wrought Iron |  | DIXON | L-220 REPAIR COMPLETE
|  |  |  | 3 | Distribution Main |  | Other |  |  | Other |  | 1974-02-04 |  |  |  | Steel |  | FRESNO
13 | 10-88023-1 | 151 | 8.36 | 6 | Transmission >= 20% SMYS |  | Longitudinal Weld |  |  | Construction Defect |  | 2010-10-22 | 2011-04-07 | Replace #TP Main < 50 ft |  | Steel-Other |  | RICHVALE | CAN IN 2' NEW PIPE; SOAP TESTED AT 100 16 AND LINE PRESSER. 4" PIPE INSTALLED IS FROM MARYSVILLE WAREHOUSE EMERGENCY STOCK, SERIAL # A-0107-01. SEE ATTACHED STPR AND CHART.
30 | 10-81204-1 | 191-1 |  | 2 | Distribution Main <= 60 PSIG |  | Line Valve |  |  | Other |  | 2010-10-04 | 2011-01-22 | Greased - Other |  | Steel-Other |  | MARTINEZ; | GREASED DOWNSTREAM VALVE; GREASED VALVE
| 10-81483-1 | 1111 |  | 4 | Transmission |  | Regulator |  |  | Other | LOOSE PLUG | 2010-10-04 | 2010-10-14 | Other | TIGHTENED PLUG | Steel/Wrought Iron |  | PITTSBURG; | SOAP TEST FIXED 1 LEAK 1/4 PLUG TIGHTEN HW,WK.
30 | 10-81564-1 | 3001-01 |  | 4 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other |  | 2010-10-02 | 2011-01-29 | Greased - Other |  | Steel-Other |  | MORAGA | GREASED VALVE; GREASED VALVE
30 | 10-81566-1 | 300-01 |  | 2 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other |  | 2010-10-03 | 2011-01-28 | Greased - Other |  | Steel-Other |  | CONCORD | GREASED & OPERATED VALVE, REPAIRED LKS IN REG VAULT; GREASED VALVE, TIGHTENED SEVERAL FITTINGS INSIDE OF REG STATION, REPLACED ONE LEAKY PILOT AS WELL.
| 10-81567-1 | 191-1 |  | 0.75 | Transmission |  | Valves |  |  | Other | LOOSE PLUGS | 2010-10-03 | 2010-10-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | CONCORD | TIGHTEN/DOPE FTGS; SOAP TESTED- OK
| 10-81682-1 | 5640/SP3 |  | 2 | Distribution Main |  | Fitting |  |  | Other | LOOSE FITTING | 2010-10-03 | 2010-10-15 | Other | TIGHTENED | Steel/Wrought Iron |  | PITTSBURG | TIGHTENED 2" NIPPLE - REDOPED & TIGHTENED PLUG; SOAP TESTED
30 | 10-81684-1 | SP5 | 4.29 | 6 | Distribution Main <= 60 PSIG |  | Line Valve |  |  | Other |  | 2010-10-04 | 2011-03-15 | Greased - Other |  | Steel-Other |  | ANTIOCH | GREASED & EXERCISE VALVE; GREASED AND EXERCISED VALVE
| 10-81741-1 | 3006-01 |  | 0.5 | Distribution Main <= 60 PSIG |  | Fitting |  |  | Other |  | 2010-10-03 | 2011-01-22 | Tighten Cap/Bolt - Fitting | SOAP AND/OR TAPE - OTHER |  |  | CONCORD | TIGHTENED PLUG ON GAUGE TAP VALVE
30 | 10-81900-1 | 3001-01 | 2.22 | 4 |  |  | Line Valve |  |  | Other |  | 2010-10-04 | 2011-02-09 | Greased - Other |  | Steel-Other |  | LAFAYETTE | GREASED VALVE
| 10-81041-1 | X6896 |  | 1.5 | Transmission |  | Valves |  |  | Other | PACKING GLAND. | 2010-10-01 | 2010-10-08 | Other | LUBE VALVE | Steel/Wrought Iron |  | LARKSPUR
| 10-81080-1 | 11 |  | 24 | Transmission |  | Other |  | PACKING | Other | LOOSE | 2010-10-05 | 2010-10-22 | Other | TIGHTENED PACKING | Steel/Wrought Iron |  | VALLEJO | TIGHTENED PACKING; SOAP TEST
| 10-81080 | 11 |  | 10 | Transmission |  | Other |  | PACKING | Other | LOOSE | 2010-10-05 | 2010-10-22 | Other | TIGHTENED PACKING | Steel/Wrought Iron |  | VALLEJO | TIGHTENED PACKING; SOAP TEST
| 10-81080 | 11 |  | 10 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2010-10-05 | 2010-10-22 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | VALLEJO | TIGHTENED FITTING; SOAP TEST
| 10-81100-1 | 1 | 4.18 | 4 | Transmission |  | Fitting |  |  | Other | LOOSE | 2010-10-05 | 2010-10-19 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | VALLEJO | TIGHTENED FITTING; SOAP TEST; SEE ATTACHED MAP
42 | 10-81220-1 | 0403-01 | 0.74 | 4 | Distribution Main >60 PSIG and <20% SYMS |  | Line Valve |  |  | Other |  | 2010-10-05 | 2011-03-31 | Greased - Other |  | Steel-Other |  | VALLEJO | GREASED STOPPED LEAK; NO CHANGE TO LATEST DRAWING
| 10-81223-1 | 403-01 |  | 6 | Transmission |  | Other |  | FILTER | Other | LOOSE FITTING | 2010-10-14 | 2010-10-19 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | VALLEJO | TIGHTENED FILTER CLOSURE; SOAP TEST
42 | 10-88025-1 | 210C | 27.65 | 10 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other | NEED GREASE | 2010-10-27 | 2011-02-23 | Greased - Other |  | Steel-Other |  | BENICIA | GREASED VALVE; TURNED IN TAG TO HAVE ALL EQUIPMENT @ THIS LOCATION PAINTED
42 | 10-88050-1 | 210C | 28.17 | 2 | Transmission >= 20% SMYS |  | Curb Valve |  |  | Other | NEED GREASED | 2010-10-27 | 2011-02-10 | Greased - Other |  | Steel-Other |  | BENICIA | GREASED VALVE
| 10-81027-1 | 0405-01 | 22.95 | 0.75 | Transmission |  | Regulator |  |  | Other | NO LOCK UP | 2010-10-09 | 2010-10-18 | Other | CLEARED VALVE SEAT ON REG. | Steel/Wrought Iron |  | ST. HELENA | REMOVE DEBRIS FROM SEAT
| 10-81028-1 | 1 |  | 0.75 | Transmission |  | Valves |  |  | Other | LUBE | 2010-10-10 | 2010-10-19 | Other | LUBE/OPERATE | Steel/Wrought Iron |  | ST. HELENA
| 10-81055-1 | 0407-01 | 5.51 | 8 | Transmission |  | Unknown |  |  | Unknown |  | 2010-10-08 |  | Other | SOAPY WATER VISUAL | Steel/Wrought Iron |  | NAPA | NO LEAK FOUND ON TRANSMISSION LINE
| 10-81164-1 | 0406-03 | 1.14 | 4 | Transmission |  | Valves |  |  | Other | LUBE | 2010-10-08 | 2010-10-16 | Other | LUBE/OPERATE | Steel/Wrought Iron |  | NAPA | LUBED 2 OPERATED REPEATEDLY.
| 10-88025-1 | 1 | [9 empty] | 2010-10-28 | [5 empty] | ST. HELENA
| 10-88101 | DREG3774 | 0.01 | 2 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other |  | 2010-10-28 | 2010-12-23 | Greased - Other |  | Steel-Other |  | NAPA | GREASED VALVE, HARD TO SEE PIPE CONDITION; NO CHANGE TO SKETCH
| 10-88102 | 021B | 3.73 | 1 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-10-28 | 2010-12-23 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | NAPA | REDOPED; NO CHANGE TO SKETCH
43 | 10-88104-1 | 021BX | 0.03 | 1 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-11-01 | 2011-02-18 | Replace Valve < 2 inch |  | Steel-Other |  | NAPA | CHANGED VALVE TO BAALL VALVE
43 | 10-88125-1 | 210B | 23.92 | 0.75 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-11-01 | 2010-11-30 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | NAPA | FOUND HPR LEAKING @ UNION. REDOPED & REPAIRED; REPAIRED LEAK @ UNION
| 10-88126 | 210B | 24.23 | 2 | Transmission >= 20% SMYS |  | Fitting |  |  | Other | LOOSE | 2010-11-01 | 2011-01-11 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | NAPA | TIGHTENED UNION
43 | 10-88127-1 | 210B | 24.32 | 1 | Transmission >= 20% SMYS |  | Other |  |  | Other |  | 2010-11-01 | 2011-02-23 | Greased - Other |  | Steel-Other |  | NAPA | GREASED VALVE; NO CHANGE TO LATEST SKETCH
| 10-88150-1 | 1 |  | 1 | Transmission |  | Valves |  |  | Unknown |  | 2010-11-02 | 2010-11-09 | Other | GREASED VALVE | Steel/Wrought Iron |  | NAPA | GREASED PLUG VALVE IN PROPER PIPE PLUG
| 10-88151 | BD15 | 19.03 | 0.5 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-11-02 | 2010-12-23 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | NAPA | RETAPE & SEAL; NO CHANGE TO SKETCH
| 10-88152-1 | 1 |  | 6 | Transmission |  | Other |  | BLOW DOWN CAP | Unknown |  | 2010-11-02 | 2010-11-19 | Other | CLEAN & GREASED GASKET | Steel/Wrought Iron |  | NAPA | CLEANED GASKET RE-TIGHTENED; NO CHANGE TO LATEST SKETCH
43 | 10-88153-1 | 1 |  | 6 | Transmission >= 20% SMYS |  | Other |  | FLANGE | Other | LOOSE BELT | 2010-11-02 | 2011-03-03 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | NAPA | TIGHTENED BOLTS ON FLANGE; CORRECTIVE TAG TO HAVE LOCATION DUG UP AND COATING REPAIRED
| 10-81027-1 | DREG4673 | 0.12 | 6 | Distribution Main |  | Body of Pipe |  |  | Unknown |  | 2010-10-05 | 2010-10-09 | Other | VALVE | Steel/Wrought Iron |  | SANTA ROSA | GREASED; GREASED VALVE & SOAPED
44 | 10-81086-1 | 1303-01 | 0.5 | 4 | Distribution Main <= 60 PSIG |  | Girth Weld |  |  | Construction Defect |  | 2010-10-05 | 2011-01-05 | Patch Weld - Weld |  | Steel-Other |  | SANTA ROSA | REPARIED LEAKING WELD; REPARIED WELD BY NORTH END OF 4" BY PATCH WELDING
| 10-81089-1 | 1 |  | 8 | Transmission |  | Other |  | DRIP | Other | 2" VALVE | 2010-10-05 | 2010-10-21 | Replace TP Main |  | Steel/Wrought Iron |  | PETALUMA | CUT OUT DRIP; CUT OUT DRIP/REPLACE W/ 47" 8" STEEL .188 WALL
| 10-81092-1 | 1303-05 |  | 0.5 | Transmission |  | Regulator |  |  | Other | TUBING FITTING | 2010-10-05 | 2010-10-09 | Other |  | Steel/Wrought Iron |  | SANTA ROSA | SAME AS ABOVE; REMOVED FITTING/ REDOPED & RE-INSTALLED & SOAP TEST OK
| 10-81093-1 | 11 |  | 2 | Service |  | Valves |  |  | Other | THREADS | 2010-10-06 | 2010-10-09 | Other | RE-DOPED THREADS | Steel/Wrought Iron |  | SANTA ROSA | REINSTALLED BYPASS VALVE; REMOVED BYPASS VALVE -REDOPED- REINSTALLED VALVE SOAP TEST OK
| 10-81126-1 | 021F |  | 0.75 | Transmission |  | Regulator |  |  | Material Failure | UNKNOWN | 2010-10-05 | 2010-10-11 | Replace Valve >= 2 inch | OTHER - REPLACED | Steel/Wrought Iron |  | PETALUMA | REPLACED REGULATOR; REPLACED REGULATOR & GREASED VALVE & SOAPED
| 10-88046-1 | DREG3806 | 69.68 |  | Transmission |  | Line Valve |  |  | Other | GREASE | 2010-11-01 | 2011-01-28 | Greased - Other |  | Steel-Other |  | CLOVERDALE | FOUND NO LEAKS AT VALVE AND 2 HPR BOXES
44 | 10-88048-1 | 021E | 69.44 | 0.75 | Transmission >= 20% SMYS |  | Regulator/Pilot |  |  | Other |  | 2010-11-02 | 2011-02-09 | Other |  | Steel-Other |  | HEADLSBURG | REPLACED PRIMARY REGULATOR; REPLACED PRIMARY REG WITH REBUILT REG
44 | 10-88126-1 | 0413-03 | 0 | 0.75 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other | VALVE NEEDED GREASE | 2010-10-28 | 2011-02-01 | Greased - Other |  | Steel-Other |  | PETALUMA | GREASED VALVE; REPAIRED 3/4" TAP VALVE WITH GREASE CLEARED & PAINTED
44 | 10-88208-1 | 021E | 69.7 | 0.75 | Distribution Main >60 PSIG and <20% SYMS |  | Line Valve |  |  | Other |  | 2010-11-03 | 2011-01-28 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SANTA ROSA | LEAK ON H.P.R. & VALVE
| 10-81027 | DREG5262 | 0 | 4 | Transmission >= 20% SMYS |  | Other |  |  | Other Natural Forces |  | 2010-10-14 | 2010-12-03 | Greased - Other |  | Steel-Other |  | FAIRFIELD | REPAIRED LEAK @ TOP OF FILTER; REMOVED, CLEARED, LUBED "O" @ TOP OF FILTER
| 10-88022 | 220 | 10.22 | 1 | Transmission >= 20% SMYS |  | Fitting |  |  | Other |  | 2010-11-04 | 2011-01-10 | Other | GREASED VALVE | Steel-Other |  | DIXON | ; GREASED INLET FIRE VALVE; GREASEED VLAVE; *SEE ATTACHED PLAT
50 | 10-81014-1 | 0646-01 | 8.39 | 1 | Transmission >= 20% SMYS |  | Fitting |  |  | Other | LOOSE FITTINGS | 2010-10-09 | 2011-02-10 | Tighten Cap/Bolt - Fitting | SOAP AND/OR TAPE - OTHER; OTHER - DOPE | Steel-Other |  | YOLO | TAPED & DOPED THREADED FITTINGS ON BOTH REG & RELIEF; REPAIRED MULTIPLE LEAKS @ THREADED FITTINGS ON REG & RELIEF. TAPED & DOPED FITTINGS. CLEANED & PAINTED PIPING & EQUIPMENT. SOAPED, NO LEAKS
50 | 10-81027-1 | 220 |  | 0.75 | Distribution Main <= 60 PSIG |  | Fitting |  |  | Other |  | 2010-10-14 | 2011-03-01 | Other | REBUILT HI TO HI | Steel-Other |  | DAVIS | REBUILT HI TO HI (FINAL STAGE); REPAIRED LEAK @ THREADED FITTING ON FINAL STAGE REG. NO LOCK UP ON REG. REPLACED W/ NEW REG. TAPED & DOPED ALL FITTINGS. CLEANED & PAINTED. S OAP TESTED, NO LEAKS FOUND
| 10-81032-1 | DREG4102 | 0.01 | 2 | Transmission |  | Valves |  |  | Unknown |  | 2010-10-14 | 2010-10-28 | Other | GREASED VALVE | Steel/Wrought Iron |  | DAVIS | GREASED VALVE - NO LEAKS W/ SOAP TEST; GREASED BYPASS VALVE TO STOP LEAK NO BUBBLES SOAP TEST
| 10-81041-1 | 116 |  | 8 | Transmission |  | Valves |  |  | Unknown |  | 2010-10-02 | 2010-10-29 | Other | GREASED VALVE | Steel/Wrought Iron |  | DAVIS | GREASED VALVE TO STOP LEAK; GREASED VALVE TO STOP LEAK - NO BUBBLES W/ SOAP TEST. LEAK AT GREASE FITTING - NOT AT VALVE
| 10-88019 | 220 |  | 8 | Transmission |  | Body of Pipe |  |  | External Corrosion |  | 2010-11-04 | 2010-11-05 | Replace TP Main |  | Steel/Wrought Iron |  | DAVIS | REPLACE 4' OF 8" T.P. LINE (MAIN); PIPE DATA 188 2 ERW 8" (A-1343-01 TEST RECORD)
| 10-81017-1 | 0615-01 |  | 0.5 | Transmission |  | Other |  | GAUGE TAPS | Other | LOOSE FITTINGS | 2010-09-29 | 2010-10-08 | Other | TIGHTENED | Steel/Wrought Iron |  | SACRAMENTO | TIGHTENED 1/2" GAUGE TAPS BEFORE REGS ON BOTH SIDES; REPAIRED SMALL LEAKS ON 1/2" GAUGE TAPS BEFORE REGS ON BOTH SIDES SOAPED PIPEING & EQUIP NO OTHER LEAKS FOUND. SEE ATTACHED PLAT
52 | 10-81038-1 | 0606-01 | 1.18 | 4 | Transmission >= 20% SMYS |  | Fitting |  |  | Construction Defect |  | 2010-10-05 | 2011-01-21 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | ELK GROVE | TIGHTENED CAP ON 2" TEE ON 4" MAIN
| 10-81041-1 | 0605-01 | 7.17 | 0.5 | Transmission |  | Other |  | THREADED PLUGS TOP OF 1/2" VALVES FOR PRESSURE TAPS | Other | DRY PIPE DOPE ON PLUG THREADS | 2010-10-06 | 2010-11-02 | Other | REPLACED (2) 1/2" PLUGS SOAPED OK | Steel/Wrought Iron |  | GALT | REPLACED (2) 1/2" THREADED PLUGS, USED TAPE & DOPE ON THREADS, SOAPED OK; REPLACED (2) 1/2" THREADED PLUGS, USED TAPE & DOPE ON THREADS, SOAPED OK
| 10-81053-1 | 116 | 12.85 | 0.75 | Transmission |  | Valves |  |  | Other | LOOSE | 2010-10-12 | 2010-11-16 | Other | TIGHTEN R/O VALVE | Steel/Wrought Iron |  | SACRAMENTO | TIGHTENED VALVE; TIGHTENED VALVE; TIGHTEN VALVE & SOAP TESTED
| 10-81004-2 |  |  | 0.75 | Transmission |  | Fitting |  |  | Construction Defect |  | 2010-10-21 | 2010-10-21 | Other | GREASED FITTING | Steel/Wrought Iron |  | SOUTH CITY SSF | GREASED FITTING; LEAKING GREASE FITTING AT VALVE. GREASED TO STOP LEAK
| 10-81004-3 |  |  | 0.5 | Transmission |  | Valves |  |  | Construction Defect |  | 2010-10-20 | 2010-10-20 | Other | REDOPED & REINSTALLED 1/2" VALVE | Steel/Wrought Iron |  | SOUTH SAN FRANCISCO | RE-DOPED & RE-INSTALLED 1/2" VALVE; STOPPED PIN-OFF MUELLER TEE AT MAIN & REMOVED 1/2 VALVE. CLEANED THREADS & RE-INSTALLED 1/2" VALVE
| 10-81004-4 |  |  | 0.75 | Transmission |  | Other |  | CAP ON 3/4" MULLER TEE | Construction Defect |  | 2010-10-20 | 2010-10-20 | Tighten Cap/Bolt - Fitting |  | Steel/Wrought Iron |  | SSF | RE-DOPED & TIGHTEN CAP; FIXED LEAK ON CAP 3/4" TP TEE
| 10-81014-1 | 101 | 26.72 | 8 | Transmission |  | Fitting |  |  | Other | GASKET | 2010-10-09 | 2010-10-25 | Other | REPLACED GASKET | Steel/Wrought Iron |  | SAN MATEO | REPLACED GASKET; SOAP TEST OK; REPLACED GASKET ON 8" BLIND FLANGED BLOW OFF.
| 10-81520-1 | 142S | 11.47 | 0.75 | Transmission |  | Fitting |  |  | Construction Defect |  | 2010-10-16 | 2010-10-27 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | BAKERSFIELD | TIGHTENED FITTING; SOAP TESTED
| 10-81106-1 | 1202-04 | 0.6 | 0.75 | Transmission |  | Other |  | H202 RELIEF | Other | WATER & MUD | 2010-10-03 | 2010-10-16 | Other | REPLACED H202 RELIEF | Steel/Wrought Iron |  | FRESNO | REPLACED H202 RELIEF
| 10-81500-1 | 118A | 12.76 |  | Transmission |  | Valves |  |  | Atmospheric Corrosion |  | 2010-10-03 |  |  |  | Steel/Wrought Iron |  |  | JOB IN ENGINEERING TO GET ESTIMATED; CONECTIVE WORK FROM ORDER# 41271518/ NOTIFICATION #10452926
| 10-81501-1 | 1217-01 | 0.01 | 16 | Transmission |  | Valves |  |  | Other | VALVE GREASE FITTING | 2010-10-06 | 2010-10-27 | Other | RE-GREASED VALVES | Steel/Wrought Iron |  | FRESNO | RE-GREASED VALVE FITTING; REGREASED 2 VALVES, SOAP TESTED OK
| 10-81502-1 | 138C | 43.66 | 0.75 | Transmission |  | Other |  | H202 RELIEF | Other | DIRT/DUST | 2010-10-20 | 2010-10-28 | Other | REPLACE H-202 RELIEF | Steel/Wrought Iron |  | FRESNO | REPLACED H-202 RELIEF IN PIT - SOAP TESED OK (NO LEAK)
| 10-88081-1 | 1201-02 | 0.4 | 0.75 | Distribution Main |  | Other |  | H202 RELIEF | Damage by 3rd Party |  | 2010-10-21 | 2010-11-15 | Other | REPLACED H-202 RELIEF ON DIST SIDE OF SINGLE CUST HPR BOX | Steel/Wrought Iron |  | FRESNO | REPLACED H202 RELIEF, SOAP TESTED OK; REPLACED H202 RELIEF, DUE TO DAMAGE, SET #55# SOAP TESTED OK
| 10-88141-1 | 351 | 8.51 | 0.75 | Transmission |  | Other |  | VALVE PLUG | Other | LOOSE | 2010-10-27 | 2010-11-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | FRESNO | TIGHTENED PLUG ON 3/4" VALVE ON BODY BLEED; SOAP TESTED / NO LEAKS
| 10-81342-1 | 118A | 33.09 | 4 | Transmission |  | Valves |  |  | Other | GREASE DRY | 2010-10-07 | 2010-10-07 | Other | GREASED | Steel/Wrought Iron |  | CHOWCHILLA | GREASED VALVE; GREASED OPERATED SOAP TEST OK
| 10-81362-1 | 1 |  | 4 | Single Service |  | Unknown |  |  | Unknown |  | 2010-10-06 | 2010-10-12 |  |  | Steel/Wrought Iron |  | MADERA | SOAP TEST FOUND NO LEAK
| 10-81472-1 | DREG4446 | 0.01 | 0.25 | Transmission |  | Fitting |  |  | Other | LOOSE FITTING | 2010-10-10 | 2010-10-17 | Other | TIGHTEN 1/4" PLUG | Steel/Wrought Iron |  | MERCED | SOAP TEST TIGHTENED 1/4" PLUG; SOAP TEST OK
| 10-81202-1 |  |  | 8 | Transmission |  | Valves |  |  | Other | NEEDED GREASE | 2010-09-24 | 2010-10-05 | Other | GREASED VALVE | Steel/Wrought Iron |  | SAN JOSE | GREASED VALVE; SOAP TEST OK; SEE ATTACHED
| 10-81210-1 |  |  | 10 | Transmission |  | Fitting |  |  | Other | DOPED CAP | 2010-09-25 | 2010-10-08 | Tighten Cap or Bolt | OTHER - DOPED CAP | Steel/Wrought Iron |  | LOS GATOS | DOPED CAP ON 1 1/4" SAVER VALVE; SOAP TEST
| 10-81041-1 | 402 |  | 2 | Transmission |  | Other | Fitting |  | Other | LOOSE | 2010-09-30 | 2010-10-09 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | REDDING | TIGHTEN FITTING; SOAP TEST VISUAL 580PSIG
| 10-81065-1 | 7222-01 |  | 6.625 | Transmission |  | Valves |  |  | Other | DRIED PIPE DOPE | 2010-10-02 | 2010-10-07 | Other | PIPE DOPE & TIGHTEN PLUG | Steel/Wrought Iron |  | MODESTO | PUT PIPE DOPE & TIGHENED PLUG; TIGHTEN PLUG & SOAP TESTED
| 10-81204-1 | 7222-01 |  | 8 | Transmission |  | Valves |  |  | Other |  | 2010-10-04 | 2010-10-05 | Other | GREASED | Steel/Wrought Iron |  | MODESTO | GREASED VALVE, SOAP TEST; GREASED VALVE, THERE WAS A VERY SMALL LEAK, AFTER GREASING VALVE SEEN NO LEAK, SOAP TESTED
| 10-81210-1 | DREG5569 | 0.01 | 2 | Transmission |  | Valves |  |  | Other | NO GREASE | 2010-10-05 | 2010-10-23 | Other | GREASED VALVE | Steel/Wrought Iron |  | MODESTO | GREASED VALVE; GREASED VALVE SOAP TEST BURRIED VALVE
| 10-81164-1 | 1608-01 | 0.01 | 12 | Transmission |  | Valves |  |  | Material Failure |  | 2010-09-28 | 2010-10-18 | Other | REPLACE BOLTS ON VALVE BONNET | Steel/Wrought Iron |  | STOCKTON | REPLACED BONNET BOLTS IN 12" KEROTEST M1 GATE VALVES; SOAP TESTED BONNET BODY FLANGE OF KEROTEST M-1 VALVE (12"); SEE ATT'D
| 10-81183-1 | 1617-01 |  | 0.75 | Transmission |  | Fitting |  |  | Other | DRY PIPE DOPE | 2010-09-27 | 2010-10-05 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | TRACY | DRY DOPE/ DOPED & TIE CAP; SOAP TEST
| 10-81244-1 | 108 | 29.14 | 0.5 | Transmission |  | Valves |  |  | Other | 1/2" VALVE LOOSE | 2010-09-28 | 2010-10-16 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | STOCKTON | INSTALLED 1/4" PCF FTG., PLUGGED OFF CHANGED 1/2" VALVE; WELDED ON 3/4" SPLIT FITTING, PLUGGED DOWN AND CHANGED 1/2" VALVE SOAP TESTED.
| 10-81501-1 | 1603-01 |  | 0.75 | Transmission |  | Fitting |  |  | Other | DRY PIPE DOPE | 2010-09-29 | 2010-10-15 | Other | HP COUPLING | Steel/Wrought Iron |  | MANTECA | REDOPED FITTING ON HPR; REDOPED COUPLING ON HPR SET, SOAP TESTED
| 10-81521-1 | 162A |  | 8 | Transmission |  | Valves |  |  | Other | DRY NEEDS GREASE | 2010-09-29 | 2010-10-14 | Other | GREASED VALVE | Steel/Wrought Iron |  | TRACY | GREASED 8" VALVE; GREASED STEM LEAKING - GREASED VALVE, LEAK STOPPED/ SOAP TEST; SEE ATTACHED MAP FOR LOCATION
| 10-81541-1 | 1615-01 |  | 12 | Transmission |  | Valves |  |  | Other |  | 2010-09-29 | 2010-09-29 | Other | GAUGE TAP BALL VALVES LEAKING | Steel/Wrought Iron |  | RIPON | TEMPARY, NEED TO EXCAVATE; GAUGE TAPS ON LEAKING AT THREADS AND ON BALL VALVE. UNABLE TO ISOLATE TO REPLACE AND RE-DOPE. INJECTED GREASE (1033) INTO TUBES. PAST BALL VALVE GUAGE TAPS. WHICH GREATLY REDUCED LEAKING. NEED TO EXCAVATE TO MAKE PERMANENT REPAIR
| 10-81543-1 | 1615-04 |  | 0.75 | Transmission |  | Fitting |  | VALVE - FITTING | Other | TIGHTENED 1/4" METRIC PLUG | 2010-09-29 | 2010-10-15 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | RIPON | TIGHTENED PLUG; SEE ATT'D
| 10-81555-1 | 1615-04 | 6.61 | 0.75 | Transmission |  | Valves |  |  | Other | GREASE VALVE | 2010-10-09 | 2010-10-15 | Other | GREASE VALVE | Steel/Wrought Iron |  | RIPON | GREASE VALVE; GREASE VALVE TO STOP LEAK - SOAP TEST
| 10-81556-1 | 1615-07 | 0.02 | 0.75 | Transmission |  | Valves |  |  | Other | GREASE FITTING | 2010-10-09 | 2010-10-15 | Other | INJECTED GREASE INTO GREASE FITTING | Steel/Wrought Iron |  | RIPON | GREASED FITTING; SOAP TEST; SEE ATT'D
| 10-81558-1 | 1615-01 | 6.71 | 0.75 | Transmission |  | Fitting |  |  | Other | DRY DOPE | 2010-10-09 | 2010-10-14 | Other | TIGHTENED LOOSE FITTING | Steel/Wrought Iron |  | RIPON | TIGHTENED FITTING; VALVE INSIDE VAULT - TIGHTNED FITTING / SOAP TEST
| 10-81559-1 | 1615-04 | 6.73 | 0.75 | Transmission |  | Valves |  |  | Other | DRY DOPE | 2010-10-09 | 2010-10-14 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | RIPON | INSTALL NEW 1/4" VALVE; REPLACED 1/4" METRIC VALVE - TO DRY DOPE SOAP TEST
| 10-81560-1 | 1615-04 | 6.69 | 0.75 | Transmission |  | Regulator |  |  | Other | DRY DOPE | 2010-10-09 | 2010-10-14 | Other | REDOPED NIPPLE BETWEEN REGS HPR | Steel/Wrought Iron |  | RIPON | REDOPED NIPPLES IN BETWEEN REGS. HPR; REDOPE NIPPLES BETWEEN REG SOAP TEST
| 10-81681-1 | 1615-04 |  | 0.75 | Transmission |  | Valves |  |  | Other | DRY DOPE | 2010-09-30 | 2010-10-14 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | RIPON | REPLACED 1/4" METRIC VALVE & DOPE; REPLACED 1/4" METRIC VALVE - SOAP TEST
| 10-88302-1 | 148 | 1.39 | 0.75 | Transmission |  | Valves |  |  | Other | OLD HPR | 2010-10-20 | 2010-11-10 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | MANTECA | INSTALL NEW STL VALVE & HPR REG SET SOAP TEST; REPLACED STL VALVE & REG & RELIEF / REBUILD HPR SET AND SOAP TESTED
| 10-82001-1 |  |  | 8 | Transmission |  | Fitting |  |  | Other | DRY PIPE DOP | 2010-09-17 | 2010-09-20 | Other | REDOPED SAVE A VALVE RECAP AND RETIGHTENED; | Steel/Wrought Iron |  | TRACY | REDOPED CAP ON SAVE A VALVE; SOAP TESTED CAP AFTER REDOPING 3/4" SAVER VALVE. TIGHTENED CAP 9-20-10
| 10-82009-1 |  | 0 | 6 | Distribution Main |  | Mechanical Joint |  |  | Other | LEAK AT JOINT ON ORFICE METER | 2010-09-24 |  |  |  | Steel/Wrought Iron |  | LODI
98 | 10-82011-1 | 2011-02-06 | 0.7 | 3.5 | Transmission >= 20% SMYS |  | Other Mechanical Joint |  |  | Other |  | 2010-09-23 | 2011-06-02 | Other |  | Steel-Other |  | ISLETON | REMOVED METER TUBE & BOUND FLANGE; REMOVED SEALING OF PIPE INSTALLED BLIND FLANGE ON BOTH ENDS
96 | 10-82019-1 | 0617-14 | 3.49 | 8 | Transmission >= 20% SMYS |  | Line Valve |  |  | Other | FAILED VALVE - LEAKING | 2010-10-01 | 2011-02-23 | Replace Valve >= 2 inch |  | Wrought Iron |  | RANCHO CORDOVA | REPLACED VALVE
| 10-82034-1 | 400 | 82.3 |  | Transmission |  | Fitting |  |  | Construction Defect |  | 2010-10-08 | 2010-10-11 | Mechanical Repair Fitting - Fitting |  | Steel/Wrought Iron |  | BURNEY | INSTALLED NEW FITTING; REMOVED NIPPLE & CAP AND REPLACED WITH PLUG
| 10-82055-1 | 400 | 48.64 |  | Transmission |  | Valves |  |  | Other | VALVE NEEDED GREASED | 2010-10-08 | 2010-10-12 | Other | GREASED VALVE |  |  |  | GREASED VALVE; GREASED V-A AND STOPPED LEAK THIS IS A BURRIED VALVE
| 10-82077 | 136 |  | 0.75 | Single Service |  | Regulator |  |  | Construction Defect |  | 2010-10-07 | 2010-10-07 | Other | CHANGED OUT REGULATOR |  |  | CHICO | REPLACED REGULATOR; SOAP TESTED: OK
| 10-82078-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2010-09-27 | 2010-09-28 | Other | FITTINGS | Steel/Wrought Iron |  | SANTA ROSA | TIGHTENED FITTING; REPAIRED FITTING & SOAPED
96 | 10-82084-1 | 057A-T2 | 0 | 4 |  |  | Other Mechanical Joint |  |  | Other |  | 2010-09-18 | 2011-03-17 | Other |  | Steel-Other |  | HOLT | NO LEAK DETECTED W/ SOAP; MULTIPLE LEAKS REPAIRED BY PLM WORK REQUEST; WR 173784: NO LEAK DETECTED AT THIS FIELD PRESSURE; WR 173785: REPLACE FILTE HOUSING O-RING. SOAP TEST OK; WR 173786: INJECTED STEM PACKING. SOAP TEST OK;
96 | 10-82085-1 | 057A-MT | 0.35 | 0.75 |  |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-09-18 | 2011-03-14 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | HOLT | REDOPED & TIGHENED; REDOPED AND TIGHTENED THREADED PLUG ON DRIP LINE VALVE. SOAP TEST OK AFTER REPAIR
96 | 10-88606-1 | DREG8692 | 0 | 2 | Transmission >= 20% SMYS |  | Line Valve |  |  | Construction Defect |  | 2010-11-02 | 2011-01-20 | Greased - Other |  | Steel-Other |  | WILLOWS | GREASED VALVE; GREASED VLAVE
96 | 10-88687-1 | 114 | 3.76 | 0.25 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-11-05 | 2011-03-12 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | RIO VISTA | THREADS LEAKING AT FITTING GOING TO P-SAMPLE TUBING; REMOVED FITTING INSTALLED TEFLON TAPE INSTALLED FITTING
96 | 10-88714-1 | 195-1 | 0.03 | 0.25 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-11-08 | 2011-03-12 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | RIO VISTA | REMOVED PLUG INSTALLE DTHREAD SEALANT REINSTALLED; REMOVE 1/4 PLUG INSALLED THREAD SEALANT REINSTALLED
96 | 10-88715-1 | 195-1 | 0.02 | 1 | Transmission >= 20% SMYS |  | Threads |  |  | No/Deteriorated Pipe Dope |  | 2010-11-08 | 2011-03-12 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | RIO VISTA | REMOVED PLUG INSTALLED THREAD SEALANT REINSTALLED; REMOVED 1" PLUG INSTALLED THREAD SEALANT REINSTALLED
| 10-88940-1 | 400 | [9 empty] | 2011-10-21 | 2010-11-12 | Other | REMOVED OIL & OTHER HYDRO CARBONS FROM DRIP LEG ON VALVE. |  |  | WILLOWS | GC USED VAUUM TRACK TO EXPOSE AREA. FOUND NO LEAK OR EVIDENCE OF LEAK. SOIL WAS SAND & MAY HAVE BEEN SATURATED WITH GAS DUE TO VALVE LUBRICATOR THAT IS VENTED INTO DRIP PAN NEAR AREA THAT WAS MARKED BY LEAK CONTRACTORS
| 10-81397-1 | 300B | 66.25 | 34 | Transmission |  | Fitting | Valves |  |  |  | 2010-10-04 | [5 empty] | WEST OF CADIES
| 10-81407-1 | 300B | 55.9 | 12 |  |  | Other |  |  | Unknown |  | 2010-10-26 |  |  |  | Steel/Wrought Iron |  | NEEDLES
98 | 10-82007-1 | 300B | 450.79 | 34 | Transmission >= 20% SMYS |  | Other |  | BODY BLEED VALVE | Unknown | OTHER - PLUG LEAKING | 2010-09-19 | 2010-09-19 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | HOLLISTER | CLOSED BAD, BLEED VALVE & DOPED PLUG; SOAP TESTED BODY BLEED VALVE & PLUG
| 10-82016-1 |  |  | 0.75 |  |  | Valves |  |  | Other | NEEDED GREASE | 2010-10-03 | 2010-10-03 | Other | GREASED VALVE | Steel/Wrought Iron |  | FRESNO | GREASED 3/4" VALVE AFTER INSTALLING NEW GREASED FITTING SOAP TESTED OK
98 | 10-82017-1 | 138 | 20.39 | 18 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | External Corrosion |  | 2010-09-29 | 2011-03-04 | Replace #TP Main < 50 ft |  | Steel-Other |  | BURREL
| 10-82029-1 | 138 | 0.02 | 0.5 | Distribution Main |  | Regulator |  |  | Material Failure |  | 2010-09-28 |  |  |  | Steel/Wrought Iron |  | COALINGA
| 10-82045-1 | 138 | 22.04 | 6 | Transmission |  | Fitting |  |  | Other | O-RING | 2010-09-29 | 2011-03-29 | Tighten Cap or Bolt | BLOW OFF | Steel/Wrought Iron |  | BURRELL | GREASED VALVES, CLEANED, OILED, GREASED O-RINGS, MADE GAKSET AND RESET BLOW OFF. SOAP TESTED NO LEAKS
| 10-82053-1 | 300A | 319.98 | 12 | Transmission |  | Other |  | UNI-BOLT CAP | Material Failure |  | 2010-10-07 |  |  |  | Steel/Wrought Iron |  | LOST HILLS
| 10-82058-1 | 138 | 14.94 | 10 | Transmission |  | Valves |  |  | Other | O-RINGS | 2010-09-29 | 2010-10-16 | Other | O-RINGS | Steel/Wrought Iron |  | HELM | REPLACED O-RINGS WINDOWS ON
| 10-82063-1 | 300B | 103.51 | 34 | Transmission |  | Fitting | Valves |  | Unknown |  | 2010-09-29 | 2011-05-05 | Soap and/or Tape - Other |  | Steel/Wrought Iron |  | TOPOCK DISTRICT PIPELINE | REPAIRED MULTIPLE FITTINGS
| 10-82064-1 | 300B | 103.51 | 0.5 | Transmission |  | Fitting | Valves |  | Unknown |  | 2010-09-29 | [5 empty] | TOPOCK DISTRICT PIPELINE
| 10-82070-1 |  |  | 0.5 | Gathering |  | Fitting |  |  |  |  | 2010-10-04 | 2010-10-06 | Tighten Cap or Bolt | SOAP AND/OR TAPE | Steel/Wrought Iron |  | MENDOTA
| 10-82075-1 |  |  | 0.75 | Transmission |  | Valves |  |  | Other | LOOSE PLUG | 2010-09-30 | 2010-10-07 | Other | TIGHTEN PLUG | Steel/Wrought Iron |  | CHOWCHILLA | DOPED AND REINSERTED PLUG; REDOPEDAND TIGHTENED PLUG ON INLET VALVE
| 10-82092-1 |  |  | 3 | Transmission |  | Valves |  |  | Other | GASKET |  | 2010-09-30 | Other | GASKET | Steel/Wrought Iron |  | MADERA | REPLACED GASKET ON VALVE
| 10-88034-1 | 300B | 388.6 | 12 | Transmission |  | Other |  | UNI-BOLT CAP |  |  | 2010-10-21 |  |  |  | Steel/Wrought Iron |  | KETTLEMAN CITY
98 | 10-88092-1 | 300B | 241.4 | 0.25 | Transmission >= 20% SMYS |  | Threads |  |  | Other |  | 2010-10-19 | 2011-02-19 | Soap and/or Tape - Other |  | Steel-Other |  | BEAR VALLEY SPR | REMOVE - TAP - REINSTALL PLUG
| 10-88794-1 | 300B | 40.49 | 34 | Transmission |  | Other |  | STEM PACKING | Other | OLD STEM PACKING | 2010-10-22 |  |  |  | Steel/Wrought Iron |  | NEEDLES TOPOCK DISTRICT PIPELINES
| 10-88794-3 | 300B | 40.49 | 0.75 | Transmission |  | Fitting |  |  | Weld Failure |  | 2010-10-27 |  |  |  | Steel/Wrought Iron |  | NEEDLES - TOPOCK DISTRICT PIPELINE
| 10-43345 | [10 empty] | 2010-09-26 | [5 empty] | ORINDA
30 | 79-22899-1 |  |  | 2 | Distribution Main |  | Tap Connection |  |  | Construction Defect |  | 1979-06-08 | 1979-06-12 | Other |  | Steel/Wrought Iron |  | MARTINEZ | REDOPED AND TIGTENED CAP ON 2" TEE TO ELIMINATE LEAKAGE
| 10-26600-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Unknown |  | 2010-09-02 | 2010-11-15 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | LAFAYETTE | SEE BELOW; SOAP TEST @ SKINNER CLAMP
| 04-43032 | [16 empty] | CONCORD
| 04-43032-1 | [10 empty] | 2004-02-13 | 2005-08-09 |  |  |  |  | CONCORD
| 10-20323-1 | [10 empty] | 2010-09-30 | [5 empty] | OAKLEY
| 10-40077 | [10 empty] | 2010-06-09 | [5 empty] | OAKLEY
| 07-23018 |  |  | 2 | Distribution Main <= 60 PSIG |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2007-04-24 | 2010-12-29 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | WALNUT CREEK | TIGHTEN REDOPE CAP
30 | 04-20023-1 |  |  | 1.25 | Distribution Main <= 60 PSIG |  | Other |  |  | Equipment Malfunction |  | 2004-07-14 | 2010-12-27 | Replace Dist Main >= 100 ft | REPLACE DIST MAIN <100FT - REPLACE | Steel-Other |  | ANTIOCH | CUT IN NEW 1.25 MAIN ¦ TEE AND CUT IN NEW 1.25 MAIN; SCREWED TEE/ BAD 1.25 PIPE CUT OUT TEE PUT NEW PIPE IN.
30 | 04-20023-1 |  |  | 1.25 | Distribution Main <= 60 PSIG |  | Other |  |  | Equipment Malfunction |  | 2004-07-14 | 2010-12-27 | Replace Dist Main >= 100 ft | REPLACE DIST MAIN <100FT - REPLACE | Steel-Other |  | ANTIOCH | CUT IN NEW 1.25 MAIN ¦ TEE AND CUT IN NEW 1.25 MAIN; SCREWED TEE/BAD 1.25 PIPE CUT OUT TEE PUT NEW PIPE IN.
30 | 09-96135-B |  |  | 4 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | Construction Defect |  | 2009-06-17 | 2010-11-30 | Skinner Clamp - Clamp |  | Steel-Other |  | WALNUT CREEL | INSTALLED 4" SKINNER CLAMP ON 4" GM.; INSTALLED 4" SKINNER CLAMP 47' W/O SAND WEDGE PL
30 | 09-93760-1 |  |  | 2 | Distribution Main <= 60 PSIG |  | Girth Weld |  |  | Construction Defect |  | 2009-11-16 | 2011-05-11 | Direct Deposition Weld - Weld |  | Steel-Other |  | MARTINEZ | D.D. WELD; AL RAN A HOT PASS OVER WELD E/, 25' E/O WAVERLY
30 | 09-23707-1 |  |  | 2 | Distribution Main <= 60 PSIG |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2009-10-26 | 2011-04-04 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | CONCORD | REDOPE & TIGHTEN
30 | 09-23648-1 |  |  | 1.25 | Distribution Main <= 60 PSIG |  | Tap Connection |  |  | Equipment Malfunction |  | 2009-10-22 | 2011-03-21 | Replace Main Valve < 2-inch |  | Aldyl A (Tan or Gray) |  | CONCORD | INST. 2' 1/4 METFIT TO REPAIR BOLT ON TEE; INST. 2 11/4 MET FITTS FUZE NEW SER TEE REPLACE 8' PLA MAIN
30 | 09-23779-1 |  |  |  | Distribution Main <= 60 PSIG |  | Riser Valve Threads |  |  | No/Deteriorated Pipe Dope |  | 2009-11-04 | 2011-02-03 | Tighten Cap/Bolt - Fitting |  |  |  | CONCORD | TIGHTEN SERVICE VALVE; TIGHTEN SERVICE VALVE APPLYED PIPE DOPE.
30 | 09-24043-1 |  |  | 0.5 | Distribution Main <= 60 PSIG |  | Riser Valve Threads |  |  | No/Deteriorated Pipe Dope |  | 2009-12-01 | 2011-02-05 | Tighten Cap/Bolt - Fitting |  | Aldyl A (Tan or Gray) |  | CLAYTON | TIGHTEN SERVICE VALVE APPLY PIPE DOPE; TIGHTEN SERVICE VALVE APPLYED PIPE DOPE
30 | 09-24132-1 |  |  | 0.5 | Distribution Main <= 60 PSIG |  | Riser Valve Threads |  |  | No/Deteriorated Pipe Dope |  | 2009-12-15 | 2011-02-03 | Tighten Cap/Bolt - Fitting |  |  |  | CLAYTON | TIGHTEN SERVICE VALVE; TIGHTEN SERICE VALVE AT RISER THREADS.
30 | 10-13072-1 |  |  | 4 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2010-05-08 | 2010-02-04 | Skinner Clamp - Clamp |  | Steel-Other |  | MORAGA | 4" SKINNER; PIPE LAYING ON SHALE ROCK NO SAND BED
30 | 09-24196-1 |  |  | 0.5 | Distribution Main <= 60 PSIG |  | Riser Valve Threads |  |  | No/Deteriorated Pipe Dope |  | 2009-12-15 | 2011-01-28 | Tighten Cap/Bolt - Fitting |  |  |  | CLAYTON | REPAIRED LEAK BELOW SERVICE VALVE ON THREADS; TIGHTEN SERVICE VALVE TO STOP LEAK BELOW SERVICE VALVE
30 | 09-93998-1 |  |  | 3 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2009-11-22 | 2011-01-22 | Replace Dist Main < 100 ft |  | Steel-Other |  | PLEASANT HILL | REPLACED 15' OF 3" STL; REPLACE 15' OF 3" STL TO CORRECT CLEARANCE ON WATER MAIN; SEE ATTACHED MAP
30 | 09-94557-1 |  |  | 2 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2009-12-04 | 2011-01-22 | Skinner Clamp - Clamp |  | Steel-Other |  | PLEASANT HILL | 2" SKINNER CLAMP
30 | 09-96348-1 |  |  | 8 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2009-07-27 | 2011-01-09 | Fill Weld - Weld | PATCH WELD - WELD | Steel-Other |  | WALNUT CREEK | FILL WELD & PATCH
| 09-97297 |  |  | 2 | Distribution Main <= 60 PSIG |  | Pressure Control Fittings |  |  | No/Deteriorated Pipe Dope |  | 2009-08-25 | 2011-02-03 | Tighten Cap/Bolt - Fitting | (X2) | Steel-Other |  | WALNUT CREEK | TIGHTEN CAPS (X2); TIGHTEN CAPS ON FITTINGS 86' E/O LARKEY LN.
| 10-26601-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Other | DRY PIPE DOPE | 2010-09-01 | 2010-11-10 | Other | SEE COMMENTS | Steel/Wrought Iron |  | LAFAYETTE | SEE COMMENTS; REMOVED PLUG & CAP ON 2" BOTTOM TAP- REDOPED & RETIGHTENED 25' E/O EVELYN CT.
| 98-60036-1 |  |  | 4 | Transmission |  | Valves |  |  | Material Failure |  | 1998-08-21 | 1998-09-04 | Other | REPLACE VALVE | Steel/Wrought Iron |  | HAYWARD | REPLACED LEAKING 4" VALVE; REPLACED 4" VALVE LEAKAGE AND TO OPERATE
24 | 11-10059-B | 105 | 10.55 | 6 | Transmission >= 20% SMYS |  | Line Valve |  |  | External Corrosion |  | 2011-05-26 | 2011-05-27 | Replace Main Valve >= 2-inch |  | Steel-Other |  | NEWARK | REPLACE 6" VALVE; HYDRO TEST AT 850 PSIG. XRAY WELDS REPLACED VALVE E69 IN SAME LOCATION. 105' FROM VALVE TO THORNTON.; REPLACE VALVE ON LINE 105 GOING TO REG PIT; *ENTRY INTO METALLIC PIT DEPTH WAS ENTERED AS .001. BECAUSE OF IGIS REQ.
| 08-22035-1 |  |  | 0.5 | Single Service |  | Valves |  |  | Incorrect Operation |  | 2008-08-05 | 2008-10-25 | Replace Valve < 2 inch |  | PE2406/2708 (Yellow) |  | UNION CITY | CHANGED VALVE TO CORRECT LEAKAGE
| 00-42478-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Damage by 3rd Party |  | 2000-11-27 | 2000-11-27 | Mechanical Repair Fitting - Fitting |  | Aldyl A (Tan or Gray) |  | SAN RAMON | REPLACED 2' OF 1/2 PIPE- INSTALLED TWO 1/2" PERMANENT COUPLINGS
| 00-62708-1 |  |  | 0.5 | Service |  | Physical/Mechanical Joint |  |  | Other |  | 2000-12-11 | 2000-12-11 | Other | REPLACE FITTING | Aldyl A (Tan or Gray) |  | PLEASANTON | REPLACED TEE WITH PERFECTION TEE
| 02-42407-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 2002-01-23 | 2002-01-23 | Other | INSTALL DEAD END | TR 418 |  | LIVERMORE | LOWERED END OF SERVICE. INSTALLED 1/2" DEAD END; SOAP TESTED
24 | 05-20057-1 |  |  | 2 | Distribution Main >60 PSIG and <20% SYMS |  | Fitting |  |  | No/Deteriorated Pipe Dope |  | 2005-04-29 | 2011-02-23 | Remove/Replace Completion Plug Fitting |  | Steel-Other |  | HAYWARD | REDOPED TIGHTENED NEW CAP; M-2 THREADS LEAKING AND TOP OF CAP LEAKING
| 08-62715-1 |  |  | 1.25 | Single Service |  | Valves |  |  | Unknown |  | 2008-10-24 | 2008-10-24 | Other |  | Steel/Wrought Iron |  | PLEASANTON
| 08-61121-1 |  |  | 0.5 | Single Service |  | Other |  | BOLT TEE 1/2" PL. | Material Failure |  | 2008-08-13 | 2008-08-13 | Other | ELECTRO FUSION 1/2 PL. TEE | Aldyl A (Tan or Gray) |  | FREMONT | REPLACED 1/2" PL. BOLT ON TEE WITH ELECTRO FUSION 1/2" PL. TEE
24 | 09-62713-1 |  |  | 2 | Distribution Main <= 60 PSIG |  | Line Valve |  |  | Other | MULTI TURN VALVE | 2009-06-24 | 2010-12-13 | Replace Main Valve >= 2-inch |  | Steel-Other |  | PLEASANTON | VALVE REMOVED.; REPAIRED LEAK ON 2" STEEL VALVE. DICISION MADE BY TAIR, TO REMOVE VALVE C-13 ON DIVISION ST. + ST. FAIR ST. ALL WELDS WERE SOAP TESTED.
24 | 09-21199-1 |  |  | 0.75 | Single Service |  | Body of Pipe |  |  | External Corrosion |  | 2009-07-28 | 2011-01-18 | Replace Entire Service |  | Steel-Other |  | NEWARK | RE-RUNED GAS SERVICE; RE-RUNED 3/4" STL SERVICE WITH 1/2" PL INSERTED SERVICE AND INSTALLED 1/2" NEW EFV AT MAIN.
24 | 09-21283-1 |  |  | 4 | Distribution Main >60 PSIG and <20% SYMS |  | Body of Pipe |  |  | Construction Defect |  | 2009-09-30 | 2011-02-09 | Replace Dist Main < 100 ft |  | Aldyl A (Tan or Gray) |  | FREMONT | REPLACE 58" OF 4" MAIN; SOAP TEST ELECTRO-FUSION COUPLINGS
| 09-20134-1 |  |  | 0.75 | Distribution Main |  | Fitting |  | ON MAIN | External Corrosion |  | 2009-05-28 | 2010-11-15 | Other | FITTING ON MAIN LEAKING | Steel/Wrought Iron |  | HAYWARD | STOPPED LEAK; CLAMPED THROAT ON BLOW OFF TEE- SOAP TESTED NO LEAK
| 09-20280 |  |  | 2 | Distribution Main <= 60 PSIG |  | Girth Weld |  |  | Weld Failure |  | 2009-07-22 | 2011-01-10 | Fill Weld - Weld |  | Steel-Other |  | HAYWARD | WELDER CAME OUT AND WASHED BOTTOM TAP FIXED LEAK; WELDER CAME OUT AND WASHED OVER 2" STL BOTTOM TAP.
24 | 11-62702-1 |  |  | 4 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | Construction Defect |  | 2011-01-12 | 2011-04-05 | Skinner Clamp - Clamp |  | Steel-Other |  | PLEASANTON | REPAIRED LEAKING SKINNER CLAMP; REPAIRED LEAKING 4" 2 BOLT SKINNER CLAMP
| 99-22737-1 |  |  | 0.5 | Service |  | Plastic Tee Cap |  |  | Material Failure |  | 1999-05-04 | 2000-11-27 | Other | REPAIR KIT; | Aldyl A (Tan or Gray) |  | SAN RAMON | REPAIRED BLACK CAP TEE WITH REPAIR KIT
28 | 87-00269 |  |  | 20 | Distribution Main |  | Body of Pipe |  |  | Corrosion |  | 1987-03-09 | 1987-03-10 | Patch Welded | -3 | Steel/Wrought Iron |  | RICHMOND | REPAIR MAIN / ARC WELDED PATCHES; REPMOVED TREE PLANTED DIRECTLY OVER MAIN. IN TRAFFIC ISLAND - INFORMED AND GOT OK. FROM BOB BARROWS / PARKS AND REC. RICH
28 | 84-40175-1 |  |  | 2 | Transmission |  | Tap Connection |  |  | Construction Defect |  | 1984-05-07 | 1984-05-07 | Other |  | Steel/Wrought Iron |  |  | FOUND LEAK WHOLE TRYING TO C/O 1 1/4" MAIN. MAIN HAS BEEN C/O LEAK ON CAP.
25 | 86-30092-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1986-11-25 | 1986-12-03 | Patch Welded |  | Steel/Wrought Iron |  |  | BAR TESTED 87 BEST READ AT WATER MAIN VALVE AT 9 INST. (1) 12 X 12 PATCH ON 20" MAIN
| 76-40061 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-02-18 | 1976-02-18 | Patch Welded |  | Steel/Wrought Iron |  | RICHMOND | ON 20" T.P. MAIN ON BOTTOM AT 800 FOUND ONE PIT ABOUT 1/2" X 1/2" LONG. WELDED 6" X 6" STACK PATCH OVER PIT FOR REPAIRS. WELD 2" COLD PLATE PATCH OVER SMALL PIT ON TOP OF MAIN (VERY SHALLOW PIT).; SEE ATTACHED PAT SHEET
1 | 87-00264-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-03-09 | 1987-03-09 | Patch Welded |  | Steel/Wrought Iron |  | RICHMOND | PATCH 20" T.P. MAIN IN PLACED (BACKHOE SCRATCH FROM WATER MAIN)
28 | 82-20589 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1982-04-14 | 1982-04-27 | Patch Welded |  | Steel/Wrought Iron |  | RICHMOND | WELDED PATCH OVER PIT LEAK AT APROX 10:OO O'CLOCK LEAK APPEARS TO HAVE BEEN HERE FOR A LONG TIME. 10" X 10" R/C
28 | 81-20191-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1981-02-25 | 1982-03-25 | Patch Welded |  | Steel/Wrought Iron |  | RICHMOND | REPAIRED PIT APPROX 3" DIAMITER WITH PIN HOLE LEAK. PPE TESTED ON GM 4208492 WELDED PATCH ON 20" T.P. MAIN
28 | 87-00263-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-03-09 | 1987-03-19 | Patch Welded |  | Steel/Wrought Iron |  | RICHMOND | WELDED 2 PATCHES OVER LEAKING PITS ON 20" T.P.
28 | 74-40116-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1974-03-12 | 1974-03-13 | Patch Welded |  | Steel/Wrought Iron |  | RICHMOND | LEAK; 180" N/O LUCAS INST. WELD PATCH 2>ED INST. (2) 9LB ANODES.
| 99-21068-1 |  |  | 3 | Gathering |  | Valves |  |  | Unknown |  | 1999-07-14 | 2004-05-05 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | RICHMOND | REPAIRED TIGHTEN NUT; ALL IN VFC ON VALVE. NO SKETCH REQUIRED
| 76-40356-F |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1976-12-15 | 1976-12-23 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | RICH | THIS PLAIN IS PITTED BAD
| 86-30101-1 | [10 empty] | 1986-12-03 | 1986-12-03 |  |  |  |  | BERKELEY | FOUND 301 ON BLOW OFF STACK
28 | 87-60008-1 |  |  | 4 | Distribution Feeder Main |  | Body of Pipe |  |  | Corrosion |  | 1987-01-26 | 1987-01-26 | Patch Welded |  | Steel/Wrought Iron |  | BERKELEY | REF 20020; INST (1) PATON PATCH OVER LEAK ON 4" T.P. MAIN AND O/ " PCF.
28 | 83-20117-1 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1983-01-13 | 1983-07-14 | Patch Welded |  | Steel/Wrought Iron |  | BERK | INST. (1) PATTEN WELD PATCH ON T.P. MAIN R. VEGA 7-14-83 PERM REPAIRS
28 | 97-80005-1 |  |  | 24 | Transmission |  | Fitting |  |  | Other |  | 1997-01-06 | 1996-01-06 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | HERCULES | ISNT. NEW CAP ON 3/4" FITTING FOR 3/4" IN OFF TP P.C.F.
28 | 89-80404-1 |  |  | 2 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1989-11-09 | 1989-11-20 | Patch Welded |  | Steel/Wrought Iron |  | BERK | WELDED 2" PATTEN PATCH OVER CORROSION PIT.; ISNT. 2" PATTEN PATCH ON LEAKING CORROSION PIT.
26 | 72-05324-1 | [10 empty] | 1972-07-03 | [6 empty] | REFER TO GM 469165-72
| 02-20080-1 |  |  | 3 | Gathering |  | Valves |  |  | Other | NEEDED GREASE | 2002-04-12 | 2002-10-29 | Other | GREASED | Steel/Wrought Iron |  | OAKLAND | GREASED VALVE TO STOP GAS LEAK.
| 80-00011-1 | [5 empty] | Body of Pipe |  |  | Corrosion |  | 1980-01-08 | 1980-04-25 | Patch Welded |  |  |  | OAK | E. 9TH & 23RD AVE.; NEAR MAIN A DEAD END; .3% OVER MAIN IN V.F.C. 105- MAIN; WELD PATCH ON 20" T.P. MAIN - REPAIRED LEAK
| 85-10071 | 105 |  | 20 | [7 empty] | 1985-02-14 | 1985-02-14 |  |  | Steel-Other |  | OAKLAND | ARC WELDED TWO PATCHES OVER TWO HOLES ON 20" T.P. GAS MAIN AND OVER PATCH OVER LINE 105
| 84-30091-M | 105 |  | 20 | [7 empty] | 1984-02-02 | 1985-02-14 |  |  | Steel-Other |  | OAKLAND | ARC WELD PATCH OVER HOLE ON TOP OF 20" T.P. GAS MAIN.
26 | 75-20994-1 | 105 |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-09-24 | 1975-11-07 | Patch Welded |  | Steel/Wrought Iron |  | OAKLAND | GAS VALVE ON SIDEWALK; 10% AT CURB VALVE IN S/W.; MARKING FOR LINE 105 IS 4' OFF
| 84-20458-F |  |  | 12 | [7 empty] | 1984-08-29 |  |  |  | Steel-Other |  | ALAMEDA | PERM LEAK ON 12" T.P. MAIN WELD PATCH FOR PERM REP, ALSO WELDED PATCHES ON BAD PITTS MAIN IN BAD SHAPE IN 22' AREA EXPOSED.
| 74-55272 |  |  | 20 | Transmission |  | Other |  |  | Other |  |  | 1974-11-19 | Other |  | Steel-Other |  |  | DUG 2 HOLES OVER FLAME PACKS MARKS FOUND NO LEAKAGE ON TRANSMISSION LINE 105
|  |  |  | 2 | Transmission |  | Valves |  |  | Material Failure |  | 1980-11-06 |  | Other | GREASE | Steel/Wrought Iron
26 | 87-11009-5 |  |  | 2 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1987-01-09 | 1987-01-09 | Patch Welded |  | Steel/Wrought Iron |  | ALA. | WELDED (1) 4" CIRCLE PATCH ON 2" T.P. MAIN
| 84-11419-F |  |  | 24 | [7 empty] | 1984-09-05 | [5 empty] | OAKLAND | CREW FOUND 301 IN V.F.C. ON 3" METRIC VALVE; TIGHTEN UP 1/2" METRIC VALVE ON 105 LINE, DUE TO LEAKAGE
| 85-20238-F |  |  | 8 | [7 empty] | 1985-04-23 | [5 empty] | OAKLAND
1 | 98-20306-1 |  |  | 3 | Gathering |  | Other Welds |  |  | Construction Defect |  | 1998-06-10 | 1998-06-29 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | OAKLAND | REPAIRED LEAKAGE ON WELD AT SAVE-A-VALVE NIPPLE
| 86-10021-C |  |  | 0.75 | [7 empty] | 1986-01-17 |  |  |  | Steel-Other |  | OAKLAND | BROKEN METRIC RETHREAD & INSTALLED NEW METRIC
1 | 96-13883-1 |  |  | 6 | Transmission |  | Valves |  |  | Other |  |  |  | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | OAK | TIGHTENED VALVE ON SENSING LINES
| 85-30066-M |  |  | 6 | [7 empty] | 1985-01-22 |  |  |  | Steel-Other |  | OAK | INST 12" LONG PIECE OF 6" 1/2 SOLE TO REPAIR 301. MAIN IN GOOD CONDITION EXPECT WRAP WAS DAMAGED BY FILL
| 85-11089-F |  |  | 2 | [7 empty] | 1985-02-25 | [5 empty] | EMERYVILLE | C/O 2" T.P. AT 6" MAIN FOR PERM REPAIRS TO 4245 HOLLECK
2 | 90-40299-5 |  |  | 4 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1990-04-14 | 1990-04-14 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | EMERYVILLE | INSTALLED 4" 1/2 SOLE WELDED FOR PERM REPAIRS
28 | 11-80029-B |  |  | 0.75 | Distribution Main > 60 PSIG | TRANSMISSION (>=20% SMYS) | Line Valve |  |  | Other Natural Forces |  | 2011-01-18 | 2011-01-18 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | BERKELEY | STOPED OFF GAS SERVICE AND T&r TIGHTEN VALVE; STOPED OFF GAS SERVICE AT TEE AND T&R TIGHTEN VALVE IN CURB METER
| 04-52001 | 0112-01 |  | 1.25 | Transmission |  | Mechanical Joint |  |  | Construction Defect |  | 2009-04-01 | 2009-04-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | EMERYVILLE | REPLACED SEVERAL NIPPLES TO REPAIR LEAKS AND CLEANED MONTOR & REG. (H.P.R) OVER TO WATER LEAKS
| 09-45155 |  |  | 3 | Gathering |  | Other |  | SVC TEE | Construction Defect |  | 2009-10-24 | 2009-10-25 | Replace Dist Main < 100 ft |  | Aldyl A (Tan or Gray) |  | OAKLAND | REPLACE 4' OF 3" MAIN AND INSTALLED NEW SVC; REPLACE 4' OF 3" PL MAIN, DUE TO IK ON 3" X 1 1/4" SVC TEE.
| 09-45092 |  |  | 1.25 | Gathering |  | Valves |  |  | Construction Defect |  | 2009-06-24 | 2004-06-25 | Replace Valve >= 2 inch |  | Aldyl A (Tan or Gray) |  | OAKLAND | SQUEEZED PL. REPLACED 1 1/4" SVC VALVE; SQUEEZED 1" PL AND REPLACED 1 1/4" SVC VALVE
| 09-32089-1 | [10 empty] | 2009-01-16 | [5 empty] | OAKLAND
| 09-90720 |  |  | 0.75 | Transmission |  | Other |  | THREADS | Construction Defect |  | 2009-06-09 | 2009-06-09 | Tighten Cap or Bolt | OTHER-DOPED & TIGHTENED | Steel/Wrought Iron |  | OAKLAND
| 10-21229-1 |  |  | 3 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2010-08-27 | 2010-11-24 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | OAKLAND | INSTALL 3" (3-BOLT) FULL CIRCLE CLAMP ONTO MAIN; ISNTALL 3" FULL CIRCLE CLAMP (3-BOLT) ONTO MAIN IN ST.
| 10-21606 |  |  | 3 | Distribution Main <= 60 PSIG |  | Fitting | Other | TIGHTEN PLUG & CAP ON 3" M\2 FITT. | Construction Defect |  | 2010-10-05 | 2010-12-30 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | OAKLAND | REPLACED 3" FITTING PLUG & TIGHTEN CAP ON M/2; REPLACED 3" M/2 PLUG & RETIGHTENED CAP.
| 10-51013-1 |  |  | 1.25 | Gathering |  | Plastic Tee Cap |  |  | Construction Defect |  | 2010-05-07 | 2010-07-30 | Aldyl A Overcap - Plastic |  | Aldyl A (Tan or Gray) |  | OAKLAND | INSTALLED ELECTROFUSION OVER CAP KIT; INSTALLED ELECTROFUSION OVER CAP KIT
| 10-41101-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | Internal Corrosion |  | 2010-09-11 | 2010-12-06 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | OAKLAND | INSTALLED 1-2" CLAMP; BAD BACKFILL ROCK ON MAIN 1-2" CLAMP FOR REPAIR
| 10-41086 |  |  | 1.25 | Gathering |  | Valves |  |  | Construction Defect |  | 2010-07-26 | 2010-07-28 | Replace Valve < 2 inch |  | PE2406 (Yellow or Orange) |  | OAKLAND | REPLACE BY PASS VALVE / TIGHTEN 1 1/4"; REPLACE 3/4" BYPASS VALVE & TIGHTENED 1 1/4" SCV VALVE. BOTH WERE EXPOSED FACILITIES
| 10-21305 |  |  | 1.25 | Gathering |  | Plastic Tee Cap |  |  | Construction Defect |  | 2010-08-19 | 2010-08-19 | Aldyl A Overcap - Plastic |  | Aldyl A (Tan or Gray) |  | OAKLAMD | INSTALLED OVER CAP KIT; INSTALLED OVER CAP KIT.
| 10-11071 |  |  | 1 | Gathering |  | Fitting |  |  | Construction Defect |  | 2010-05-14 | 2010-05-14 | Replace Partial Service |  | Aldyl A (Tan or Gray) |  | OAKLAND | REPLACE 1' OF 1" PL.; LK ON FITTING, REPLACE 1' OF 1" PL.
| 10-21321-1 |  |  | 1.25 | Distribution Main |  | Plastic Tee Cap |  |  | Construction Defect |  | 2010-09-03 | 2010-11-30 | Other | OVER MET CAP | Aldyl A (Tan or Gray) |  | OAKLAND | INSTALLED ELECTROFUSION OVER CAP KIT; REPAIRED LK @ B/K CAP. INSTALLED OVER CAP KIT.
| 10-21208 |  |  | 0.75 | Gathering |  | Plastic Tee Cap |  |  | Construction Defect |  | 2010-07-29 | 2010-07-29 | Aldyl A Overcap - Plastic |  | Aldyl A (Tan or Gray) |  | OAKLAMD | INSTALLED ELECTROFUSION OVER CAP; INSTALLED ELECTROFUSION OVER CAP
| 10-21232-1 |  |  | 1.25 | Gathering |  | Plastic Tee Cap |  |  | Construction Defect |  | 2010-08-24 | 2010-11-17 | Aldyl A Overcap - Plastic |  | Aldyl A (Tan or Gray) |  | OAKLAND | INSTALLED OVER CAP KIT
| 10-21232-1 | [10 empty] | 2010-08-24 | [5 empty] | OAKLAND
1 | 11-10045-A | 0111-02 |  | 10 | Transmission >= 20% SMYS |  | Threads |  |  | Other |  | 2011-03-16 | 2011-03-16 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | OAKLAND | PIPE DOPE THREADS TIGHTEN CAP; FLAME PACK AFTER REPAIRS . A OK DONE BY JAVA
26 | 11-10018-1 |  |  | 3 | Distribution Main <= 60 PSIG |  | Fusion Joint |  |  | Root Damage |  | 2011-02-09 | 2011-05-06 | Replace Dist Main < 100 ft |  | Aldyl A (Tan or Gray) |  | OAKLAND | REPLACE 2 1/2" OF 3" PL AND INSTALLED NEW 3 X 1 1/4 SVC TEE; REPLACE 3 X 1 1/4" SVC TEE AND 2 1/2' OF 3PL MAIN. TREE ROOT PUSH SVC TEE OFF OF 3" LP. MAIN
52 | 09-21108-1 | 0639-02 |  | 0.75 | Transmission >= 20% SMYS |  | Threads |  |  | Other |  | 2009-04-15 | 2011-05-10 | Soap and/or Tape - Other |  | Steel-Other |  | SACRAMENTO | REMOVED PLUG CLEANED THREADS REDOPED & TIGHTEN; REMOVED PLUG. CLEANED THREADS USED PIPE DOPE ON THREADS & RETIGHTEN. SOAPED NO MORE LEAKS FOUND.
| 09-90823-1 |  |  | 0.75 | Gathering |  | Riser |  |  | Construction Defect |  | 2009-08-10 | 2009-11-23 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | SACRAMENTO | SOAP TESTED AFTER REPAIR.
| 09-90935-1 |  |  | 0.75 | Single Service |  | Riser |  |  | Construction Defect |  | 2009-08-18 | 2009-11-21 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | SACRAMENTO | SOAP TESTED AFTER REPAIR
| 09-90937-1 |  |  | 0.75 | Gathering |  | Valves |  |  | Construction Defect |  | 2009-08-18 | 2009-11-18 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | SACRAMENTO | SOAP TESTED AFTER REPAIR
| 09-91482-1 |  |  | 6 | Transmission |  | Fitting |  |  | Construction Defect |  | 2009-10-15 | 2010-01-11 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SACRAMENTO | LEAKING CAP; CAP LEAKING ON GAUGE TAP, REMOVED, REDOPED, AND RETIGHTENED
| 09-92379-1 |  |  | 1 | Single Service |  | Plastic Tee Cap |  |  | Plastic Crack Failure |  | 2009-11-18 | 2009-12-23 | Replace Plastic Tee Cap - Plastic |  | PE2406 (Yellow or Orange) |  | SACRAMENTO | REPLACED CRACKED CAP W/ REPAIR CAP.; TESTED REPAIR CAP AT LINE PRESSURE.
| 09-93087-1 | [10 empty] | 2009-12-04 | [5 empty] | SACRAMENTO
| 09-93684-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2009-12-23 | 2010-11-18 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | NORTH HIGHLANDS | INSTALLED 7 1/2" W CLAMP.; PUT 7 1/2" CLAMP ON MAIN 136' EAST OF WATT AVE.
| 10-20326-1 |  |  | 4 | Distribution Main |  | Other |  | GREASE FITTING | Unknown |  | 2010-09-22 | 2010-12-09 | Other | GREASED VALVE | Steel/Wrought Iron |  | SACRAMENTO | SMALL LEAK @ GREASE FITTING ON VALVE. GREASED VALVE SOAP TESTED, NO LEAKS FOUND.; SOAPED TOP OF VALVE (V-1). SMALL LEAK @ GREASE FITTING. GREASED VALVE. SOAPED VALVE, NO LEAKS FOUND.; SEE ATTACHED PLAT.
52 | 10-20403-1 |  |  | 2 | Distribution Main <= 60 PSIG |  | Pressure Control Fittings |  |  | No/Deteriorated Pipe Dope |  | 2010-11-05 | 2011-01-12 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | RANCHO CORDOVA | RE-DOPE & TIGHTEN CAP
| 10-22057 |  |  | 2 | Distribution Main <= 60 PSIG |  | Pressure Control Fittings |  |  | No/Deteriorated Pipe Dope |  | 2010-09-15 | 2010-12-03 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SACRAMENTO | REDOPED & TIGHTEN M2 CAP.; TIGHTENED AND REDOPED M2 CAP SOAP TESTED FITTING
| 10-22070-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2010-09-16 | 2010-11-15 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | SACRAMENTO | INSTALLED 2" X 6" SS. CLAMP WITH 5# ANODE; SOA[ TESTED CLAMP SVC TEES & PIPE (A) LINE PRESSURE. INSTALLED 2" X 6" SS. CLAMP W/ 5# ANODE
| 10-22093-1 | [10 empty] | 2010-09-23 | [5 empty] | SACRAMENTO
| 10-22093 | [10 empty] | 2010-09-23 | [5 empty] | SACRAMENTO
52 | 10-22110-1 |  |  | 0.5 | Distribution Main <= 60 PSIG |  | Plastic Tee Cap |  |  | Construction Defect |  | 2010-09-24 | 2011-01-03 | Replace Plastic Tee Cap - Plastic |  |  |  | RANCHO CORDOVA | O-RING DAMAGED REPLACED O-RING
| 10-22110-1 | [10 empty] | 2010-10-29 | [5 empty] | RANCHO CORDOVA
52 | 10-22533-1 |  |  | 2 | Distribution Main >60 PSIG and <20% SYMS |  | Fitting |  |  | Construction Defect |  | 2010-10-18 | 2011-04-22 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SACRAMENTO | TIGHTEN CAP
| 10-22533 | [10 empty] | 2010-10-18 | [5 empty] | SACRAMENTO
52 | 11-20152 |  |  | 3 | Distribution Main > 60 PSIG |  | Fitting |  |  | Weld Failure |  | 2011-04-28 | 2011-04-28 | Patch Weld - Weld |  | Steel-Other |  | SACRAMENTO | REPAIR ON TEE ON 3" MAIN; FOUND LEAK ON TEE (WELD) THAT WAS SCHEDULTED TO BE ABANDONED. PINNED ISOLATED REPAIR AND THEN ABANDONED. CUT-OFF CAPPED AND SOAP TESTED AT LINE PRESSURE.
52 | 11-21303-B | 0617-06 |  | 0.75 | Transmission >= 20% SMYS |  | Other |  |  | Other | GREASE FITTING | 2011-04-14 | 2011-05-14 | Greased - Other |  | Steel-Other |  | ORANGEVALE | GREASED VALVES; 1) SOURCE OF LEAK IDENTIFIED AS: FITTINGS 2) DATE OF SOURCE DTERMINATION: 5-14-11 3) PROMPT REPAIRS REQUIRED Y/N = Y
52 | 11-21306-B |  |  | 6 | Distribution Main <= 60 PSIG |  | Plastic Tee Cap |  |  | Material Failure |  | 2011-04-19 | 2011-04-19 | Replace Plastic Tee Cap - Plastic |  | PE2406/2708 (Yellow) |  | SACRAMENTO | REPLACED PLASTIC TEE CAP; REPLACED CRACKED CAP
48 | 09-33234-1 |  |  | 1.25 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | Unknown |  | 2009-06-25 | 2010-12-13 | Replace Dist Main < 100 ft |  | Aldyl A (Tan or Gray) |  | VACAVILLE | REPLACED 3' OF DIST. MAIN.; REPLACED 3' OF 1 1/4" PL MAIN. BUILDED 1" BYPASS WITH 2-1 1/4" BY 1" ELECTRO-FUSION SERV. TEES.
52 | 95-20187-1 |  |  | 8 | Transmission |  | Valves |  |  | Construction Defect |  | 1995-04-26 | 1995-04-26 | Other |  | Steel/Wrought Iron |  | RANCO CORDOVA | GREASED VALVE T&R CREW; GREASED VALVE! T&R CREW
| 02-60109 |  |  | 1 | Service |  | Body of Pipe |  |  | Digin |  | 2002-04-15 | 2002-04-15 | Service Partially Replaced |  | TR 418 |  | FAIR OAKS | INST. 2' OF 1" PL.
| 03-60107-1 |  |  | 1.25 | Service |  | Body of Pipe |  |  | Digin |  | 2003-04-18 | 2003-04-18 | Service Partially Replaced |  | TR 418 |  | SACTO | INSTALLED 3' OF 1 1/4" PIPE & 2- 11/4" MGD FITS COUPLINGS
52 | 94-20243-1 |  |  | 6 | Transmission |  | Fitting |  |  | Other |  | 1994-04-06 | 1999-04-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SACRAMENTO | REPAIRED SMALL LEAK ON PLUG
| 05-21040-1 | [10 empty] | 2005-04-23 | [5 empty] | SACRAMENTO
| 03-60139-1 |  |  | 0.5 | Service |  | Body of Pipe |  |  | Digin |  | 2003-05-23 | 2003-05-23 | Other | C/O SVC | Aldyl A (Tan or Gray) |  | SACTO | INSTALLED 1/2" DE
52 | 88-20194-1 |  |  | 6 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1988-04-27 | 1989-07-27 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SACTO | WELD REINFORCING BAND ON LINE 18" LONG
52 | 88-20196-1 |  |  | 16 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1988-04-27 | 1989-07-27 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SACTO | WELD REINFORCING BAND ON LINE 27" LONG
| 94-50031-1 |  |  | 0.75 | Transmission | SERVICE | Fitting |  |  | Other |  | 1994-10-12 | 1994-10-12 | Other |  | Steel/Wrought Iron |  | WATS | LEAK ON HI TO HI; ADJUST REG.
4 | 11-40001-B | 187 | 1.03 | 6 | Transmission >= 20% SMYS |  | Bell Joint |  |  | Digin/Excavation |  | 2011-01-25 | 2011-01-26 | Replace #TP Main < 50 ft |  | Steel-Other |  | SAN ARDO | C/O STRUCK PIPE (4) & REPLACED W/4' 6" 0.188" W.T. X-42 ERW
|  | 187 |  | 6 | Transmission | [13 empty] | A FARM EMPLOYEE WAS RIPPING A FIELD AND STRUCK LINE 187, A 6" TRANSMISSION PRESSURE GAS LINE.
5 | 11-50081-B | 301A | 51.22 | 0.75 | Transmission >= 20% SMYS |  | Threads |  |  | Other |  | 2011-05-21 | 2011-05-21 | Other | TIGHTEN GREASE STEM | Steel-Other |  | PRUDALE | TIGHTEN GREASE STEM; TIGHTEN GREASE STEM
76 | 10-20333-B |  |  | 0.75 | Distribution Main > 60 PSIG |  | Line Valve |  |  | Other |  | 2010-12-11 | 2010-12-11 | Greased - Other |  | Steel-Other |  | WATSONVILLE | GREASED VALVE TO CORRECT LEAK; VALVE LEAKING AT STEM, GREASED TO CORRECT
76 | 10-20333-B |  |  | 0.75 | Distribution Main > 60 PSIG |  | Line Valve |  |  | Other |  | 2010-12-11 | 2010-12-11 | Greased - Other |  |  |  | WATSONVILLE | GREASED VALVE TO CORRECT LEAK; VALVE LEAKING AT STEM, GREASED TO CORRECT
8 | 11-80006-A | 300B |  | 0.75 | Distribution Main <= 60 PSIG |  |  |  |  | Vehicle | TRACTOR | 2011-05-06 | 2011-05-06 | Mechanical Repair Fitting - Fitting |  | Steel-Other |  | HOLLISTER | SHUT VALVE, REBUILT HPR SET.
76 | 11-10014-B |  |  | 1 | Distribution Main <= 60 PSIG |  | Fitting |  |  | Stress Corrosion Cracking |  | 2011-03-26 | 2011-03-26 | Replace #TP Main >= 50 ft | REPLACE DIST MAIN < 100 FT.; | Other | AM FIT TEE | CAPITOLA | 1' MET FIT TEE AND BRANCHED SAN JOSE, 120; 1" MET. FIT TEE, 1/2" PERMANENT TEE FOR BRANCH
76 | 11-10014-B |  |  | 1 | Distribution Main <= 60 PSIG |  | Fitting |  |  | Stress Corrosion Cracking |  | 2011-03-26 | 2011-03-26 | Replace #TP Main >= 50 ft | REPLACE DIST MAIN < 100 FT. | Other | AM FIT TEE; | CAPITOLA | 1' MET FIT TEE AND BRANCHED SAN JOSE, 120; 1" MET FIT TEE, 1/2" PERMANENT TEE FOR BRANCH
76 | 11-10014-B |  |  | 1 | Distribution Main <= 60 PSIG |  | Fitting |  |  | Stress Corrosion Cracking |  | 2011-03-26 | 2011-03-26 | Replace #TP Main >= 50 ft | REPLACE DIST. MAIN < 100 FT | Other | AM FIT TEE | CAPITOLA | 1' MET FIT TEE AND BRANCHED SAN JOSE, 120; 1" MET FIT TEE, 1/2" PERMANENT TEE FOR BRANCH
76 | 11-10022-A |  |  | 0.75 | Transmission >= 20% SMYS |  | Body of Pipe |  |  | Atmospheric Corrosion |  | 2011-03-31 | 2011-03-31 | Other | REPLACE 3/4" NIPPLE | Steel-Other |  | SANTA CRUZ | REPLACED LEAKING NIPPLE- RE-SOALED THREADS; REPLACED NIPPLE ABOVE REG, RESOALED THREADS, SOAP TEST OK
| 04-10062-B |  |  | 4 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2010-12-10 | 2011-02-07 | SS Clamp w/Anode - Clamp |  | Steel-Other |  | SANTA CRUZ | INSTALLED SS CLAMP FULL CIRCLE AND DRIVEABLE ANODE; 158' FROM 15TH AVE TO SS CLAMP, 160 TO ABANDON 1/4" TEE. EXTREME PITTING AT ABANDON TEE SHOULD REPLACE 30" SECTION OF MAIN
| 04-10062-1 | [10 empty] | 2004-08-04 | [5 empty] | SANTA CRUZ
| 04-10060-1 |  |  | 0.75 |  |  | Other |  | NONE NO LEAK |  |  | 2004-08-04 | 2009-10-26 | Soap and/or Tape - Other |  |  |  | S. CRUZ | NO LEAK FOUND ON GAS MAIN NOR GAS SER. TEE. ; DID NOT FIND ANY GAS LEAK ON THE GAS MAIN OR GAS SERVICE. SOAP TEST THEN BACK FILL
| 04-10062-B |  |  | 4 | Distribution Main <= 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2010-12-10 | 2011-02-07 | SS Clamp w/Anode - Clamp |  | Steel-Other |  | SANTA CRUZ | INSTALLED SS CLAMP FULL CIRCLE AND DRIVEABLE ANODE; 158' FROM 15TH AVE TO SS CLAMP, 160 TO ABANDON 3/4" TEE. EXTREME PITTING AT ABANDON TEE SHOULD REPLACE 30" SECTION OF MAIN.
| 83-20195-F | 101 |  | 20 | [7 empty] | 1983-08-17 | 1983-12-14 |  |  | Steel-Other |  | S.SF.
| 83-20195 |  |  | 20 | [8 empty] | 1983-12-15 |  |  | Steel-Other |  | SO. SF | WELD 10" X 10" PATCH ON TOP OF MAIN PERM. REP. LEAK BY GC
| 11-30086-B |  |  | 6 | Distribution Main > 60 PSIG |  | Line Valve |  |  | Other | GREASE FITTING | 2011-05-06 | 2011-05-06 | Greased - Other |  | Steel-Other |  | SAN BRUNO | INSTALLED NEW GREASE FITTING & GREASED VALVE; INSTALLED NEW GREASE FITTING & GREASED VALVE #982
82 | 73-20048-1 |  |  | 8 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-03-22 | 1973-03-22 | Patch Welded |  | Steel/Wrought Iron |  | BURLINGAME | ARC WELDED PATCH ON 8" MAIN INST. 9# ANODE
82 | 84-30571 | 132 |  | 1.25 | Distribution Main |  | Fitting |  |  | Other |  | 1984-10-22 | 1985-02-01 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | M.P. | DOPE & RETIGHTEN CAP ON 1 1/4" CAP
| 06-60307 |  |  | 0.5 |  |  | Body of Pipe |  |  |  |  | 2006-09-12 | 2006-09-12 | Replace Partial Service |  |  |  | ATHERTON | SPLICE 1' OF 1/2 PLASTIC TO EXISTING SERVICE 4' S/OF TEE ON MAIN.; WEST VALLEY CONSTRUCTION CO. DUG INTO 1/2" PL GAS SVC. ON SHORT SIDE SVC. SVC NOT DUE TO LOCA FOR THAT WATER MAIN TO BE INSTALLED ON OTHER SIDE OF GAS MAIN LONG SIDE STREET BEING; INCORRECT MAPPED 1/2 PL" (3/4) & CONTRACTOR NO SPECIFIED WHEN WATER MAIN TO BE INSTALLED ON WHAT SIDE OF THE STREET. CONTRACTOR DID NOT DELEGATE PROPERLY.
| 06-60159 |  |  | 0.75 | Service |  | Unknown |  |  | Construction Defect |  | 2006-03-08 | 2006-03-09 | Replace Entire Service |  | Steel/Wrought Iron |  | EPA | INSERTED 3/4" STL. W/ 1/2" PL.
| 06-20041 |  |  | 0.75 | Gathering |  | Body of Pipe |  |  | Damage by 3rd Party |  | 2006-12-04 | 2007-02-15 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | BELMONT | ISNTALLED 3/4" X 2" & 3/4" X 4" CLAMPS OVER LEAK; YEARS AGO WHEN 6" AC WATERMAIN INSTALLED WRAP WAS KNOCKED OFF GAS SERVICE.
| 09-20077-1 | 109 |  |  | Transmission |  | Other |  | VALVE | Other | GREASED VALVE | 2009-03-30 | 2009-04-02 | Other | GREASED VALVE | Steel/Wrought Iron |  | MENLO PARK | GREASED VALVE; GREASED VALVE .490
| 10-20143-1 | 101 |  | 0.75 | Transmission |  | Valves |  |  | Other |  | 2010-09-11 | 2010-09-13 | Other | GREASE VALVE | Steel/Wrought Iron |  | BELMONT | GREASE VALVE; GREASE VALVE
| 10-20157 | 132 |  | 0.25 | Transmission |  | Mechanical Joint | Valves |  | Unknown |  | 2010-09-13 | 2010-09-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | STANFORD | TIGHTENED PACKING
| 10-60281-A | 132 |  | 2 | Distribution Main > 60 PSIG |  | Line Valve |  |  | Construction Defect |  | 2010-11-23 | 2010-11-24 | Greased - Other |  | Steel-Other |  | HILLSBOROUGH | GREASED VALVE
| 10-20132-1 | 132 |  | 2 | Transmission |  | Valves |  |  | Unknown |  | 2010-09-10 | 2010-09-12 | Other | GREASE VALVE | Steel/Wrought Iron |  | SAN MATEO | GREASED VALVE; GRASED VALVE
| 10-20155-1 |  |  |  | Distribution Main |  | Other |  |  | Other |  | 2010-09-12 | 2010-09-13 | Other | NO LEAK FOUND | Steel/Wrought Iron |  | SAN MATEO
| 10-20155 | 101 |  | 0.75 | Transmission |  | Fitting |  |  | Other | NO DOPE | 2010-09-12 | 2010-09-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN MATEO | REDOPE PLUG; REDOPE & TIGHTEN PLUG
| 10-20152 | 101 |  | 8 | Transmission |  | Other |  | REG STAT. FILTER | Other |  | 2010-09-12 | 2010-09-13 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN MATEO | TIGHTEN BOLTS ON TOP FLANGE; TIGHTEN BOLTS ON TOP FLANGE
| 10-20139-1 | 101 |  | 0.625 | Other | REG STATION | Fitting |  |  | Other | TIGHTEN | 2010-09-10 | 2010-09-12 | Tighten Cap or Bolt |  | Other | STAINLESS STEEL | SAN MATEO | TIGHTEN PILOT CONTROL LOOP; TIGHTEN FITTINGS ON CONTROL LOOP
| 10-20139-1 | 101 | [9 empty] | 2010-09-10 | [5 empty] | BURLINGAME
| 11-60147-A |  |  | 0.75 | Distribution Main > 60 PSIG |  | Regulator/Pilot |  |  | Material Failure |  | 2011-04-25 | 2011-04-25 | Other | REPLACED 3/4" REG | Steel-Other |  | HALF MOON BAY | REPLACED FISHER 627 REG IN VAULT; REPLACED FISHER 627 REG IN VAULT
| 11-60062-B | DFM |  | 6 | Transmission >= 20% SMYS |  | Threads |  |  | Other | TIGHTEN LOOSE THREADS | 2011-02-07 | 2011-02-08 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | BURLINGAME | TIGHTEN THREADS ON FITTING; SEE SKETCH FOR REG STATION A-31
| 11-60099-B |  |  | 2 | Distribution Main > 60 PSIG |  | Line Valve |  |  | Other | DRIED GREASE | 2011-03-16 | 2011-03-22 | Greased - Other |  | Steel-Other |  | SM | GREASED VALVE- FIXED LEAK
| 11-60080-B |  |  | 6 | Transmission >= 20% SMYS |  | Pressure Control Fittings |  |  | Construction Defect |  | 2011-02-24 | 2011-05-03 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SAN MATEO | CALLED T&R WHO TIGHTENED BOLT ON PCF CAP; T&R TIGHTENED PCF BOLTS, SOAPED AND WRAPPED 6" FITTING
| 11-60061-B |  |  | 0.75 | Transmission >= 20% SMYS |  | Pressure Control Fittings |  |  | No/Deteriorated Pipe Dope |  | 2011-02-09 | 2011-02-11 | Other | RE-DOPE FITTING | Steel-Other |  | SAN CARLOS | SHUT DOWN / REDOPED & INSTALL NEW FITTINGS; WORKED WITH T&R TO REPAIR LEAKS ON HP FITTINGS
| 11-60093-B |  |  | 1 | Distribution Main <= 60 PSIG |  | Tap Connection |  |  | Damage by Earth Movement |  | 2011-03-08 | 2011-04-07 | Replace Partial Service |  | PE2406 (Yellow or Orange) |  | PORTOLA VALLEY | REMOVED STRESS BUT CUT 1" PL FROM TRANSITION AT TEE ON MAIN 1/2" OF 1 " PL; REPLACED 1 1/2' OF 1" PLASTIC GAS SERVICE TESTED. REMOVED BROKEN STRESS BENT 1" PL FROM TRANSITION FITTING AT TEE TIED IN AND RESTORED SERVICE
8 | 86-09 |  |  | 22 | Transmission |  | Valves |  |  | Other |  | 1986-10-25 | 1987-11-24 | Other |  | Steel/Wrought Iron |  | HILLS | VALVES GREASED NO GAS WITH J.W. LANE TO CHARGE TO NO. 3 KEY
82 | 72-20384-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-02-03 | 1972-03-03 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | SAN MATEO | ARC WELDED FULL CIRCLE BAND OVER OLD BUTT WELD AND THE LEAK ALSO FULL CIRCLE BAND 35" LONG OVER DEEP SCRATCH ON TOP OF MAIN. ALSO ARC WELEDED SEVERAL LARGE PATCHES OVER DEEP LARGE PITS.
82 | 77-20604 |  |  | 20 | Transmission |  | Valves |  |  | Atmospheric Corrosion |  | 1977-10-31 | 1977-11-08 | Replace Pipe and/or Service |  | Steel/Wrought Iron |  | BELMONT | FOUND SMALL FUSS LEAK ON 4" BRIDLE VALVE GREASE VALVE. STOP LEAKS
82 | 74-40085-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1974-05-13 | 1974-05-13 | Patch Welded |  | Steel/Wrought Iron |  | S.M. | WELDED A COMPLETE CIRCULAR SLEEVE AROUND 20" PIPE 20' X 40" PUT A COMPLETE CIRCULAR SLEEVE OVER EXISTING WELD. PUT A 16" X 16" PATCH ON MAIN AND A 10" X 8" PATCH. HUNG TWO 17 LB ANODES WITH FRAME AND COVER
82 | 72-40050 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-02-05 | 1972-02-16 | Patch Welded |  | Steel/Wrought Iron |  | SAN MATEO | ARC WELDED 3 LARGE PATCHES TO REPAR LEAKS AND PITS. ALSO ARC WELDED FULL CIRCLE BAND OVER OLD BUTT WELD
82 | 74-20006-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1974-01-30 | 1974-02-01 | Patch Welded |  | Steel/Wrought Iron |  |  | ARC WELD 1- (12" X 12") PATCH AND 2-(3" X 3") PATCHES OVER LEAK AND PITS ON 20" MAIN.
82 | 72-50095-1 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1972-04-13 | 1972-04-14 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | REDWOOD CITY | ARC WELDED FULL CIRCLE WELD IN BAND OVER LEAK & WELD
82 | 80-30510 |  |  | 20 | Transmission |  | Other Welds |  |  | Damage by outside Forces |  | 1980-01-02 | 1980-01-03 | Clamp |  | Steel/Wrought Iron |  | RC | FOUND CRACK IN WELD INST. A 20" -1 BOLT LEAK CLAMP ON LEAK. CRACK IS APPROX 2 1/2" LONG. THIS WASH SQUARE PATCH APPROX 2 1/2" X 6"
82 | 77-30356 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1977-11-08 | 1978-05-11 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | R.C. | HRC WELDED 8" X 8" PATCH OVER LEAK ON 20" GAS MAIN (LINE 101)
82 | 78-00000 |  |  | 20 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-11-02 | 1978-12-11 | Patch Welded |  | Steel/Wrought Iron |  | REDWOOD | REPATIED LEAK ON 20" LINE. LEAK LOCATED 1" FROM WELD JOINT. INST. 110 WELDING BAND OVER LEAK AND WELD. INST. 20" WELDING BAND NEXT TO THE 110
82 | 78-50330 |  |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-09-04 | 1978-09-04 | Clamp |  | Steel/Wrought Iron |  |  | INSTALLED 2 -22" SKINNER LEAK CLAMPS
82 | 78-50321 | 109 |  | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1978-12-18 | 1978-12-18 | Clamp |  | Steel/Wrought Iron |  | ATHERTON | CLAMP INSTALLED
82 | 81-30058 |  |  | 24 | Transmission | [6 empty] | 08/07/1381 |  |  |  | Steel/Wrought Iron |  | ATHERTON
82 | 79-50215 | 132 |  | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-04-19 | 1979-05-01 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | M.P. | WELDED A 24" X FULL CIRCLE ON LINE 132. PIT THE SIZE OF A QUARTER. SIZE OF THE SHARPENED END OF A LEAD PENCIL
82 | 79-50214 | 132 |  | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-04-19 | 1979-05-01 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | M.P. | WELDED A 24" X FULL CIRCLE ON LINE 132 TO REPAIR LEAK
82 | 73-50194-1 |  |  | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1973-06-01 | 1973-06-08 | Patch Welded |  | Steel/Wrought Iron |  | MENLO | WELDED 7 PATCHES OVER 2 LEAKS & PITS
82 | 79-50054 | 109 | 16 | 22 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1979-02-18 | 1979-03-06 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | STANF | WELDED A 2' SLEEVE OVER PITS ON BOTTOM OF LINE 109 SOME OIL BLOWING OUT OF PIT
82 | 77-30450-1 | 132 |  | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1977-10-27 | 1978-10-24 | Clamp |  | Steel/Wrought Iron |  | MENLO PARK | INST. A 24" X 6" LEAK CLAMP & A 15 ON THE 24" TRANS LINE 132. PERMANENT REPAIRS WILL BE
82 | 75-30188 |  |  | 3 | Distribution Main | [6 empty] | 1975-12-11 | 1976-10-13 |  |  | Steel/Wrought Iron |  | STANFORD
82 | 75-30063 |  |  | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-02-11 | 1977-11-30 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | STANFORD | FOUND 1/2" PIT LEAKING ON LINE 132 475' SOUTH OF LOS CHECKED FOUNF
82 | 75-30189 |  |  | 24 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1975-12-11 | 1976-10-13 | Weld Over Sleeve or Can |  | Steel/Wrought Iron |  | STANFORD | DUCT INSIDE OF CATCH BASIN TOP GAS VENTING 100,000 CHECKED FOUND
82 | 77-30147-1 |  |  | 22 | Transmission |  | Longitudinal Weld |  |  | Construction Defect |  | 1977-10-25 | 1978-04-19 | Patch Welded |  | Steel/Wrought Iron |  | MENLO PARK | 2 - FULL ENCIRCLEMENT WELDED ON: ONE OVER BUTT WELD; OVER WELD INST.
| 83-20196-F |  |  | 20 | [7 empty] | 1983-08-25 | 1983-09-06 |  |  | Steel-Other |  | BRISBANE | CAR ON 2" FITTING REPAIRED 25' S/SMARKER ON QUARRY RD. CAD WELD WIRES ON S/S OF FLANGE AND BROUGHT ANODE WIRE UP IN BOX
| 09-20429-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2009-07-23 | 2011-01-19 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | SAN JOSE | INSTALLED CLAMP; CLAMPED MAIN
77 | 94-40213-1 |  |  | 12 | Transmission |  | Body of Pipe |  |  | Corrosion |  | 1994-06-15 | 1994-06-16 | Patch Welded |  | Steel/Wrought Iron |  | SANTA CALRA | WELD A 6 X 6 PATCH ON MAIN
78 | 91-20403-1 |  |  | 2 | Transmission |  | Valves |  |  | Other |  | 1991-08-23 | 1991-10-01 | Other |  | Steel/Wrought Iron |  | SAN JOSE | GREASED VALVE
78 | 91-20407-1 |  |  | 0.34 | Transmission |  | Valves |  |  | Other |  | 1991-08-23 | 1991-10-01 | Other |  | Steel/Wrought Iron |  | SAN JOSE | GREASED VALVE
| 00-20035 |  |  | 4 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2000-02-09 | 2011-01-25 | Soap and/or Tape - Other |  | Steel/Wrought Iron |  | SAN JOSE | INSTALLED SOAP & TAPE OVER MULTIPLE PITS ON MAIN; INSTALLED SOAP & AQUA SEAL OVER PITTED 4" L.P. STL. MAIN SOAP TESTED REPAIR O.K.
| 00-40051 |  |  | 0.75 | Service |  | Body of Pipe |  |  | External Corrosion |  | 2000-04-11 | 2000-04-20 | Other |  | Steel/Wrought Iron |  | SAN JOSE | INSERT SRV WITH 1/2" PL
78 | 09-96534-1 |  |  | 1.25 | Distribution Main > 60 PSIG |  | Curb Valve |  |  | External Corrosion |  | 2009-10-23 | 2011-04-12 | Other | VALVE STEM REPLACED | Steel-Other |  | SANTA CLARA | VALVE STEM EXTENSION CORRODED BUILT NEW EXT.; FOUND VALVE STEM AND EXTENSION WAS CORRODED. BUILT A NEW EXTENSION AND REPLACED THE OLD ONE. GREASED AND OPERATED VALVE. SOAP TESTED.
| 09-96107-1 | 100 | 146.3 | 24 | Transmission |  | Valves |  |  | Other | NEED LUBE | 2009-08-28 | 2009-11-12 | Other | GREASED | Cast/Ductile Iron |  | SAN JOSE | 3 VALVES; LUBED- SOAP TEST GOOD
| 09-95581-1 |  |  | 2 | Distribution Main |  | Other |  | STL. CAP | Unknown |  | 2009-07-13 | 2010-11-24 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SANTA CLARA | TIGHTEN 2" PLUG & CAP; TIGHTEN CAP ON 2" STL. MUELLER CAP
78 | 09-93424-1 |  |  | 2 | Distribution Main <= 60 PSIG |  | Pressure Control Fittings |  |  | Construction Defect |  | 2009-11-17 | 2011-05-11 | Tighten Cap/Bolt - Fitting |  | Steel-Other |  | SAN JOSE | TIGHTENED COMPLETION PLUG, RE-DOPED & TIGHTENED CAP; TIGHTENED PLUG & CAP ON 2" SPLIT CONTROL TO STOP LEAK "SOAP TESTED OK"
| 09-93424-1 | [10 empty] | 2009-11-17 | [5 empty] | SAN JOSE | INFO ONLY
| 09-92750-1 |  |  | 2 | Distribution Main |  | Other |  | STEEL CAP | Construction Defect |  | 2009-08-04 | 2011-01-14 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN JOSE | TIGHTEN CAP RE-DOPED; TIGHTENED LEAKING SERVICE CAP, SOAP TEST OK.
| 09-92223-1 |  |  | 1.25 | Gathering |  | Valves |  |  | Construction Defect |  | 2009-06-26 | 2009-09-10 | Other | TIGHTENED SERVICE VALVE | PE2406/2708 (Yellow) |  | SAN JOSE | REPAIRED A LEAK BELOW THE SERVICE VALVE
| 09-91232-1 |  |  | 0.75 | Gathering |  | Valves |  |  | Unknown |  | 2009-04-14 | 2009-04-14 | Replace Valve < 2 inch |  | Steel/Wrought Iron |  | GILROY | REPLACED SVC. VALVE 4-14-09
78 | 11-20559-1 | 132 |  | 0.25 | Transmission >= 20% SMYS |  | Curb Valve | Fitting |  |  |  | 2011-04-26 | 2011-05-26 | Greased - Other | SOAP AND/OR TAPE - OTHER | Steel-Other |  | SANTA CLARA | BALL VALVE GREASE FITTING. SEAL WELD 911 GREASED; 1/4" WOLFE FITTING GREASE PLUG LEAK FIXED BY 911 GREASED BOTH VALVES IN FRAME & COVER
78 | 11-10096-B |  |  | 1.25 | Distribution Main > 60 PSIG |  | Fitting |  |  | Damage by Earth Movement |  | 2011-03-25 | 2011-03-26 | Replace Dist Main < 100 ft |  | PE2406/2708 (Yellow) |  | SAN JOSE | CHANGED 2'- 1 1/4" PL & MET FIT ELBOW; INSTALLED 2' 11/4" PL & 1 98 ELBOW & 2- COUPLINGS MET FIT (DISCOVERED LEAK ON PRIMARY LEAD LEG)
78 | 11-10134-B |  |  | 0.75 | Distribution Main > 60 PSIG |  | Body of Pipe |  |  | External Corrosion |  | 2011-05-04 | 2011-05-06 | Replace Partial Service |  | Steel-Other |  | SAN JOSE | REPLACED 3' 11" OF 3/4" STEEL
| 10-20152-1 |  |  | 1 | Gathering |  | Fusion Joint |  |  | Other | TREE ROOT | 2010-02-11 | 2010-02-11 | Other | REPLACE FUSION JOINT, WITH MET FIT 1" COUPLING ELBOW | PE2406 (Yellow or Orange) |  | SAN JOSE | INSTALL 1 1" MET FIT ELBOW
| 10-20395-1 |  |  | 2 | Distribution Main |  | Fitting |  |  | Construction Defect |  | 2010-03-22 | 2011-01-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN JOSE | TIGHTENED LEAKING 2" SIDE TAPE CONTROL CAP; APPLIED PIPE DOPE & TIGHTENED 2" SIDE TAPE CONTROL CAP. SOAP TESTED OK.
| 10-20518 |  |  | 1.25 | Gathering |  | Valves |  |  | Equipment Malfunction |  | 2010-03-25 | 2010-03-25 | Replace Valve < 2 inch | OTHER - REPLACE 1 1/4" VALVE | Steel/Wrought Iron |  | SAN JOSE | REPLACE 1 1/4" VALVE AT RISER;
| 10-20572-1 |  |  | 1.25 | Gathering |  | Body of Pipe |  |  | External Corrosion |  | 2010-04-19 | 2010-12-23 | Replace Entire Service |  | Steel/Wrought Iron |  | SAN JOSE | REPLACE SERVICE; INSERT 44' OF 1/2" PL PIPE
| 10-20584-1 |  |  | 1.25 | Distribution Main |  | Unknown |  |  | Unknown |  | 2010-04-22 | 2011-01-20 | Deactivate Dist Main =>1 foot |  | Aldyl A (Tan or Gray) |  | SAN JOSE | C/O 14' OF 1 1/4" PL MAIN & REPLACED 18' OF 1/2" SVC; C/O 14' OF 1 1/4" ALDYL-A MAIN DUE TO LEAK UNDER LARGE TREE. RE-ROUTED 18' OF 1/2" PL. SVC, FEEDING BLDG "G", AROUND TREE AIR TESTED ENTIRE SVC & SOAP TESTED NEW TEE & DEAD END ON MAIN.
| 10-20626-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2010-05-05 | 2010-11-16 | Skinner Clamp - Clamp |  | Steel/Wrought Iron |  | SANTA CLARA | INSTALLED 2" SKINNER CLAMP OVER PIT ON MAIN; INSTALLED 2" SKINNER CLAMP OVER PIT ON MAIN. SOAP TESTED CLAMP O.K.
| 10-20968-1 |  |  | 0.75 | Distribution Main |  | Fitting |  |  | External Corrosion |  | 2010-08-19 | 2010-11-08 | Other | CAP | Steel/Wrought Iron |  | SAN JOSE | REPLACE CAP ON SAVER VALVE; SOAP TEST CAP. PIN HOLE IN CAP OF SAVER VALVE
| 09-20968-1 |  |  | 0.75 |  |  | Fitting |  |  | External Corrosion |  | 2009-11-16 |  |  |  | Steel/Wrought Iron |  | SAN JOSE
| 10-21168 |  |  | 6 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2010-06-23 | 2011-01-04 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | MIPLITAS | SAOP TEST, AND INSTALL 6" CLAMP
| 10-21389-1 |  |  | 2 | Distribution Main |  | Other |  | CAP | Unknown |  | 2010-07-28 | 2011-03-21 | Tighten Cap or Bolt |  | Steel/Wrought Iron |  | SAN JOSE | TOOK CAP OFF AND REITGHTED IT. ; SOAPED CAP
| 10-21575 |  |  | 1.25 | Gathering |  | Riser |  |  | Equipment Malfunction |  | 2010-08-13 | 2010-08-13 | Replace Partial Service | OTHER - REPLACE RISER | Steel/Wrought Iron |  | SAN JOSE | SOAP TEST
| 10-21635-1 |  |  | 2 | Distribution Main |  | Body of Pipe |  |  | External Corrosion |  | 2010-08-27 | 2010-11-22 | SS Clamp w/Anode - Clamp |  | Steel/Wrought Iron |  | SAN JOSE | INSTALLED 2.00 SS CLAMP W/ANODE; INSTALLED 2" SS CLAMP W/ANODE (SOAP TEST)
| 10-21668-1 |  |  | 1.25 | Gathering |  | Valves |  |  | Equipment Malfunction |  | 2010-08-31 | 2010-11-22 | Replace Valve < 2 inch |  | PE2406 (Yellow or Orange) |  | SAN JOSE | REPLACE VALVE; REPLACE 1 1/4" VALVE, SOAP TEST