## BestEstimate
Attachment 1
Southern California Edison
Historical System Reliability Data
Best Estimate 1999 - 2004
|  | All Interruptions Included |  |  | Major Events Excluded1
YEAR | SAIDI2 | SAIFI | MAIFI | SAIDI2 | SAIFI | MAIFI
1999 | 50.3739 | 0.77724 | 1.4927 | 50.3739 | 0.77724 | 1.4927
95% Confidence Lower Bound | 48.4389 | 0.76524 | 1.4807 | 48.4389 | 0.76524 | 1.4807
95% Confidence Upper Bound | 52.3089 | 0.78924 | 1.5047 | 52.3089 | 0.78924 | 1.5047
2000 | 47.484 | 0.83492 | 1.5148 | 47.484 | 0.83492 | 1.5148
95% Confidence Lower Bound | 45.447 | 0.82192 | 1.5018 | 45.447 | 0.82192 | 1.5018
95% Confidence Upper Bound | 49.521 | 0.84792 | 1.5278 | 49.521 | 0.84792 | 1.5278
2001 | 52.2159 | 0.77033 | 1.4377 | 52.2159 | 0.77033 | 1.4377
95% Confidence Lower Bound | 49.8589 | 0.75833 | 1.4257 | 49.8589 | 0.75833 | 1.4257
95% Confidence Upper Bound | 54.5729 | 0.78233 | 1.4497 | 54.5729 | 0.78233 | 1.4497
2002 | 54.0898 | 0.95316 | 1.4622 | 51.8116 | 0.80413 | 1.4514
95% Confidence Lower Bound | 51.9645 | 0.94183 | 1.4509 | 49.6944 | 0.79285 | 1.4401
95% Confidence Upper Bound | 56.2152 | 0.96449 | 1.4735 | 53.9287 | 0.81542 | 1.4627
2003 (w/o subst.) | 90.6753 | 1.0407 | 1.7777 | 65.4375 | 0.8687 | 1.5409
95% Confidence Lower Bound | 86.8099 | 1.0267 | 1.7636 | 62.74 | 0.85619 | 1.5283
95% Confidence Upper Bound | 94.5407 | 1.0548 | 1.7917 | 68.135 | 0.88122 | 1.5534
2003 (w/ subst.) | 82.3902 | 1.0024 | 1.7678 | 59.2361 | 0.83605 | 1.5391
95% Confidence Lower Bound | 78.6112 | 0.98767 | 1.753 | 56.5868 | 0.82279 | 1.5259
95% Confidence Upper Bound | 86.1692 | 1.0172 | 1.7825 | 61.8855 | 0.84932 | 1.5524
2004 (w/o subst.) | 76.6976 | 0.93795 | 1.5947 | 68.0837 | 0.87907 | 1.5019
95% Confidence Lower Bound | 73.5447 | 0.92305 | 1.5798 | 65.1812 | 0.86508 | 1.4879
95% Confidence Upper Bound | 79.8504 | 0.95285 | 1.6096 | 70.9861 | 0.89305 | 1.5159
2004 (w/ subst.) | 69.7979 | 0.90402 | 1.593 | 63.7377 | 0.85494 | 1.5108
95% Confidence Lower Bound | 66.7217 | 0.88948 | 1.5784 | 60.8781 | 0.8412 | 1.4971
95% Confidence Upper Bound | 72.8741 | 0.91856 | 1.6075 | 66.5974 | 0.86868 | 1.5246
1 Major Event Exclusions in Year 2004:
Winter storms in December resulted in a declaration of a State of Emergency and were reflected by excluding all outages occurring on Decmeber 28, 29, 30 and 31.
The Bark Beetle infestation in Southern California forests resulted in a declaration of a State of Emergency and was reflected by a) subtracting all outages occurring in 2004 in all
circuits in Bark Beetle areas, and b) substituting in their place the averaged ten-year (1993-2002) outage history for those same circuits, with and without historical major events
and no excluded 8 SAIDI Measured Events.
2 Adjusted to reflect the variance introduced by Southern California Edison's convention of declaring All Load Up (ALU) when power had been restored
up to the last residential transformer - an estimate was added to the annual CMI base to arrive at the normalized SAIDIs.

## Historical
Attachment 2A
Southern California Edison
Historical System Reliability Data
Traditional Calculation Method 1995 - 2004
|  | All Interruptions Included |  |  |  | Major Events Excluded1
YEAR | SAIDI2 | SAIFI | MAIFI |  | SAIDI2 | SAIFI | MAIFI
1995 | 66.87 | 0.87 | 1.1 |  | 66.87 | 0.87 | 1.1
1996 | 125.96 | 1.42 | 1.4 |  | 61.89 | 0.97 | 1.38
1997 | 77.02 | 1.1 | 1.34 |  | 77.02 | 1.1 | 1.34
1998 | 78.48 | 1.31 | 1.39 |  | 78.48 | 1.31 | 1.39
1999 | 49.05 | 1.04 | 1.23 |  | 49.05 | 1.04 | 1.23
2000 | 46.87 | 1.12 | 1.23 |  | 46.87 | 1.12 | 1.23
2001 | 51.59 | 1.05 | 1.16 |  | 51.59 | 1.05 | 1.16
2002 | 52.62 | 1.27 | 1.15 |  | 50.31 | 1.12 | 1.14
2003 (w/o sub) | 87 | 1.38 | 1.43 |  | 63.72 | 1.18 | 1.23
2003 (w/ sub) | 78.85 | 1.34 | 1.43 |  | 57.63 | 1.15 | 1.23
2004 (w/o sub) | 75.13 | 1.33 | 1.21 |  | 67.03 | 1.25 | 1.13
2004 (w/ sub) | 68.31 | 1.29 | 1.21 |  | 62.76 | 1.22 | 1.15
1 Major Event Exclusions in Year 2004:
Winter storms in December resulted in a declaration of a State of Emergency and were reflected by excluding all outages occurring on Decmeber 28, 29, 30 and 31.
The Bark Beetle infestation in Southern California forests resulted in a declaration of a State of Emergency and was reflected by a) subtracting all outages occurring in 2004 in all
circuits in Bark Beetle areas, and b) substituting in their place the averaged ten-year (1993-2002) outage history for those same circuits, with and without historical major events
and no excluded 8 SAIDI Measured Events.
2 Adjusted to reflect the variance introduced by Southern California Edison's convention of declaring All Load Up (ALU) when power had been restored
up to the last residential transformer - an estimate was added to the annual CMI base to arrive at the normalized SAIDIs.

## Conf Intervals
CONFIDENTIAL - ATTORNEY/CLIENT PRIVILEGE
This sheet received from Shinjini Menon on 09/23/2004
THIS TABLE USED FOR YEAR 2003 DATA
95% Confidence intervals | SAIDI (± mins) | SAIFI (±) | MAIFI (±)
YEAR2003: wBB_wMajor | 3.8654 | 0.014077 | 0.014077
YEAR2003: wBB_woMajor | 2.6975 | 0.012517 | 0.012517
YEAR2003: woBB_wMajor | 3.779 | 0.014772 | 0.014772
YEAR2003: woBB_woMajor | 2.6494 | 0.013267 | 0.013267
YEAR2002: wMajor | 2.1253 | 0.011328 | 0.011328
YEAR2002: woMajor | 2.1172 | 0.011286 | 0.011286
THIS TABLE USED FOR YEAR 2004 DATA
95% Confidence intervals | SAIDI (± mins) | SAIFI (±) | MAIFI (±)
YEAR2004: wBB_wMajor | 3.1529 | 0.014901 | 0.014901
YEAR2004: wBB_woMajor | 2.9024 | 0.013984 | 0.013984
YEAR2004: woBB_wMajor | 3.0762 | 0.014541 | 0.014541
YEAR2004: woBB_woMajor | 2.8597 | 0.013741 | 0.013741

## List >12 Sustained
Year | Circuit | Circuit Name | Number of customers experiencing > 12 sustained outages | Year | Circuit | Circuit Name | Number of customers experiencing > 12 sustained outages
1995 | 3485 | CHINA RANCH | 4 | 2003 | 2290 | BROOKINGS* | 1
| 7657 | GRIMSHAW | 69 |  | 2370 | BUDD | 252
| 8735 | HOT WATER | 32 |  | 2881 | CAPANERO | 292
| 14926 | REVERSE PEAK | 8 |  | 3240 | CEDAR GLEN* | 407
| 15282 | ROBINSON CREEK | 140 |  | 5850 | ELSTER | 43
| 16600 | SODA SPRINGS | 47 |  | 8410 | HIGH SCHOOL* | 341
| 17955 | TOLL | 75 |  | 8670 | HOOK CREEK* | 550
| 15415 | ROSEBUD | 536 |  | 9320 | JORDAN | 667
1996 | 14955 | RHINEDOLLAR | 14 |  | 9549 | KELLPEAK* | 10
1997 | 11448 | MCCLENNY | 57 |  | 11448 | MCCLENNY | 55
| 14349 | POSO PARK | 49 |  | 12190 | MORITZ* | 1345
| 17190 | SUGARLOAF | 114 |  | 12860 | NORTH SHORE* | 528
| 1640 | BIG PINES | 242 |  | 14349 | POSO PARK | 49
| 9320 | JORDAN | 698 |  | 14690 | RANGER* | 730
| 11270 | MARSH | 848 |  | 15922 | SAUNDERS* | 733
| 12190 | MORITZ | 502 |  | 16049 | SEALS | 93
| 17063 | STONEMAN | 80 |  | 16839 | SQUINT* | 778
1998 | 3890 | CONCEPCION | 126 |  | 17190 | SUGARLOAF | 131
| 16600 | SODA SPRINGS | 53 |  | 17997 | TORONTO* | 53
| 14652 | RAMAC | 7 | 2004 | 390 | ALPINE* | 589
| 17663 | TENNECO | 307 |  | 1630 | BIG ROCK | 534
| 19150 | WELLS | 123 |  | 3387 | CHAWA | 894
1999 | 3170 | CATTLE | 296 |  | 5085 | DINKEY CREEK | 85
| 15475 | ROWCO | 849 |  | 6432 | FINGAL | 16
2000 | 5085 | DINKEY CREEK | 37 |  | 8670 | HOOK CREEK* | 297
| 8702 | HOSSACK | 100 |  | 8930 | INTAKE | 13
| 10945 | MAHOGANY | 6 |  | 9060 | IVERSON | 125
| 12910 | NOVAC | 272 |  | 9194 | JEEP* | 2
| 13959 | PERIMETER | 7 |  | 9205 | JENKS LAKE* | 121
| 17672 | TERMINUS | 137 |  | 11760 | METTLER | 340
2001 | 1626 | BIGFOOT | 47 |  | 12136 | MONTREAL* | 630
| 2664 | CALCADIA | 5 |  | 12190 | MORITZ* | 1447
| 3890 | CONCEPCION | 68 |  | 12840 | NORTH BAY* | 223
| 5018 | DEVINE | 8 |  | 13959 | PERIMETER | 1090
| 5146 | DOGWOOD | 1890 |  | 14705 | RANIER | 7
| 12722 | NIPTON | 27 |  | 15275 | ROBIN | 51
| 15680 | SALT CREEK | 118 |  | 15415 | ROSEBUD | 734
| 19134 | WEINING | 64 |  | 15986 | SCHMIDT | 470
2002 | 1630 | BIG ROCK | 469 |  | 17915 | TITAN | 79
| 4635 | DANBY | 57 |  | 17985 | TOPOC | 92
| 9060 | IVERSON | 124 |  | 17997 | TORONTO* | 684
[5 empty] | 19694 | ANGELES | 1136
* bark beetle circuit

## No Service by Hourly Interval
Attachment 2C
| WSCC Pacific Intertie | WSCC Pacific Intertie | WSCC Pacific Intertie | Mira Loma RAS | Mira Loma RAS | Mira Loma RAS | Santa Ana Wind Storm | Santa Ana Wind Storm | ï Description of event
Time | 1996-08-10 | 1996-08-11 | 1996-08-12 | 2002-06-26 | 2002-06-27 | 2002-06-28 | 2003-01-06 | 2003-01-07 | ïDate of event
0 | 2640 | 4709 | 159 | 1973 | 459 | 365 | 152558 | 24149
1 | 2851 | 1762 | 98 | 1995 | 459 | 1054 | 178860 | 26720
2 | 211 | 1888 | 108 | 22 | 459 | 1116 | 191240 | 35678
3 | 211 | 2829 | 108 | 0 | 9716 | 1610 | 171284 | 23267
4 | 3065 | 3235 | 108 | 0 | 459 | 10112 | 129501 | 41711
5 | 704 | 527 | 108 | 0 | 4571 | 531 | 113799 | 48693
6 | 266 | 579 | 1656 | 469 | 2136 | 469 | 101011 | 35370
7 | 610 | 2750 | 76 | 0 | 589 | 3731 | 86230 | 31423
8 | 588 | 393 | 3556 | 131 | 589 | 4279 | 86946 | 15173
9 | 293 | 382 | 2403 | 0 | 501 | 598 | 58992 | 13628
10 | 12 | 317 | 2402 | 412 | 768 | 1779 | 63936 | 26507
11 | 2812 | 1517 | 856 | 114 | 1548 | 845 | 60261 | 35443
12 | 12 | 4630 | 9389 | 1053 | 451 | 432 | 69743 | 30041
13 | 72036 | 2004 | 14339 | 622 | 360 | 370 | 77406 | 24075
14 | 72033 | 176 | 15568 | 622 | 275 | 275 | 61304 | 10701
15 | 1725167 | 4951 | 11504 | 0 | 347 | 275 | 45025 | 9033
16 | 1819090 | 6114 | 17419 | 0 | 1422 | 275 | 25292 | 8628
17 | 1610131 | 11226 | 1723 | 0 | 2164 | 4341 | 25852 | 11222
18 | 1299530 | 4400 | 3476 | 664331 | 4489 | 2950 | 25773 | 7709
19 | 31614 | 876 | 1326 | 112065 | 365 | 473 | 29423 | 12265
20 | 20946 | 4437 | 2018 | 6960 | 365 | 1314 | 51181 | 14995
21 | 17018 | 263 | 1604 | 3244 | 365 | 473 | 27891 | 12993
22 | 5492 | 959 | 2624 | 459 | 365 | 473 | 20583 | 10023
23 | 9331 | 1095 | 1193 | 2827 | 365 | 473 | 34829 | 11230
Attachment 2C
| Santa Ana Wind Storm | Southern California Wild Fires | Southern California Wild Fires | Southern California Wild Fires | Winter Rain Storm | Winter Rain Storm | Winter Rain Storm | Winter Rain Storm | ï Description of event
Time | 2003-01-08 | 2003-10-24 | 2003-10-25 | 2003-10-26 | 2004-12-28 | 2004-12-29 | 2004-12-30 | 2004-12-31 | ïDate of event
0 | 5099 | 0 | 99 | 6168 | 12202 | 86942 | 3841 | 1127
1 | 9867 | 81 | 4491 | 60988 | 7187 | 73688 | 4368 | 1906
2 | 7212 | 1681 | 47 | 7531 | 24357 | 63479 | 3324 | 1444
3 | 5691 | 110 | 47 | 216964 | 40904 | 49689 | 3834 | 2590
4 | 4315 | 81 | 1847 | 91757 | 21739 | 32836 | 3737 | 3755
5 | 4155 | 602 | 14854 | 59708 | 15571 | 25442 | 3249 | 3888
6 | 4102 | 6403 | 41 | 31397 | 11448 | 20278 | 1972 | 9143
7 | 4137 | 521 | 3546 | 7319 | 30504 | 18659 | 1219 | 7295
8 | 6844 | 1134 | 19363 | 9418 | 81142 | 16293 | 4717 | 12424
9 | 7833 | 637 | 1317 | 5964 | 30040 | 13825 | 1640 | 19566
10 | 9774 | 129989 | 4454 | 8866 | 42290 | 15650 | 1745 | 7628
11 | 8491 | 653 | 3256 | 7916 | 30355 | 12288 | 5737 | 8981
12 | 11349 | 574 | 2912 | 6377 | 16991 | 14872 | 4276 | 16928
13 | 11607 | 15893 | 2295 | 28222 | 17970 | 15703 | 5481 | 10208
14 | 26750 | 600 | 2991 | 16783 | 13537 | 11964 | 4109 | 6843
15 | 6676 | 590 | 30036 | 14395 | 5871 | 8301 | 6491 | 11140
16 | 4368 | 575 | 7055 | 11363 | 11953 | 14115 | 807 | 8410
17 | 4000 | 575 | 9159 | 10280 | 92301 | 6384 | 629 | 2556
18 | 3030 | 1171 | 1279 | 8013 | 7091 | 5731 | 2592 | 2034
19 | 2930 | 616 | 2759 | 5761 | 14838 | 8300 | 2904 | 2536
20 | 2091 | 586 | 3800 | 5995 | 12547 | 5740 | 705 | 2522
21 | 2026 | 727 | 3087 | 5622 | 9958 | 4092 | 1738 | 4294
22 | 2313 | 3652 | 4829 | 5757 | 8750 | 3280 | 2262 | 4122
23 | 1540 | 1606 | 4722 | 4068 | 19519 | 6271 | 4535 | 4375

## No Service by Duration
Attachment 2D
| Northridge Earthquake | WSCC Pacific Intertie | Mira Loma RAS | Santa Ana Wind Storm | Southern California Wild Fires | Winter Rain Storm | ïDescription of event
Outage Duration | 01/17/1994 - 01/19/1994 | 08/10/1996 - 08/12/1996 | 06/26/2002 - 06/28/2002 | 01/06/2003 - 01/08/2003 | 10/24/2003 - 10/26/2003 | 12/28/2004 - 12/31/2004 | ïDate of event
0 to 1 hour | 427074 | 117623 | 667539 | 792126 | 512773 | 409522
1 to 5 hours | 117355 | 1826710 | 47086 | 172324 | 73838 | 151205
5 to 10 hours | 294165 | 23673 | 5835 | 61154 | 11577 | 62049
10 to 15 hours | 143152 | 10502 | 1203 | 57778 | 4883 | 38830
15 to 20 hours | 78136 | 234 | 2744 | 55373 | 1996 | 16205
20 to 24 hours | 41360 | 0 | 0 | 15325 | 4081 | 11582
1 to 2 days | 5160 | 0 | 0 | 56503 | 11169 | 17805
2 to 3 days | 0 | 0 | 275 | 24949 | 1734 | 1062
3 to 4 days | 0 | 0 | 0 | 5524 | 5040 | 0
4 to 5 days | 0 | 0 | 0 | 0 | 7169 | 2564
5 to 6 days | 0 | 0 | 0 | 900 | 3478 | 0
6 to 7 days | 0 | 0 | 0 | 0 | 25 | 0
> 7 days | 0 | 0 | 0 | 0 | 1003 | 7
Total | 1106402 | 1978742 | 724682 | 1241956 | 638766 | 710831

## Top 10 SAIDI each year
2004 | [6 empty] | Attachment 2E
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption (min) | Number of people used to restore service | CPUC major event?
1 | Winter Rain Storm | 12/28/2004 - 12/31/2004 | 8.0972 | 710831 | 38065 | 1005 | Y
2 | Wind Storm | 2004-11-21 | 2.5709 |  |  |  | N
3 | Wind Storm | 2004-10-27 | 2.3873 |  |  |  | N
4 | Rain Storm | 2004-10-17 | 1.9942 |  |  |  | N
5 | Moorpark A-Bank | 2004-09-11 | 1.6219 |  |  |  | N
6 | Rain Storm | 2004-10-20 | 1.6104 |  |  |  | N
7 | Lightning Storm | 2004-08-12 | 1.5739 |  |  |  | N
8 | Rain Storm | 2004-10-19 | 0.98851 |  |  |  | N
9 | Wind Storm | 2004-11-22 | 0.90408 |  |  |  | N
10 | Lightning Storm | 2004-08-13 | 0.88309 |  |  |  | N
2003 | [6 empty] | Attachment 2E
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption (min) | Number of people used to restore service | CPUC major event?
1 | Santa Ana Wind Storm | 01/06/2003 - 01/08/2003 | 17.21 | 1241956 | 7731 | 2551 | Y
2 | Southern California Wild Fires | 10/24/2003 - 10/26/2003 | 6.0652 | 638766 | 12808 | 1919 | Y
3 | Rain Storm & Mud Slides | 12/25/2003 | 3.4669 |  |  |  | N
4 | Lightning Storm | 11/12/2003 | 3.0194 |  |  |  | N
5 | Santa Ana Wind Storm | 01/05/2003 | 2.4373 |  |  |  | N
6 | Rain Storm | 02/25/2003 | 2.3019 |  |  |  | N
7 | Rain Storm | 10/31/2003 | 1.1247 |  |  |  | N
8 | Wind Storm | 03/17/2003 | 0.94569 |  |  |  | N
9 | Wind Storm | 02/12/2003 | 0.79558 |  |  |  | N
10 | Lightning Storm | 08/20/2003 | 0.769 |  |  |  | N
2002 | [6 empty] | Attachment 2E
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption (min) | Number of people used to restore service | CPUC major event?
1 | Rain/Wind Storm | 2002-12-16 | 2.7805 |  |  |  | N
2 | Rain/Wind Storm | 2002-11-08 | 2.4152 |  |  |  | N
3 | Mira Loma RAS / Louisiana Fire | 06/26/2002 - 06/28/2002 | 2.3071 | 724682 | 3996 | 50 | Y
4 | Rain/Wind Storm | 2002-11-09 | 1.0429 |  |  |  | N
5 | Rain Storm | 2002-11-25 | 1.0143 |  |  |  | N
6 | Wind Storm | 2002-02-09 | 0.85849 |  |  |  | N
7 | Car Hit Pole | 2002-10-04 | 0.84707 |  |  |  | N
8 | Rain/Wind Storm | 2002-11-07 | 0.70412 |  |  |  | N
9 | Heat Storm | 2002-09-01 | 0.66042 |  |  |  | N
10 | Rain Storm | 2002-02-17 | 0.64036 |  |  |  | N
2001 | [6 empty] | Attachment 2E
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption (min) | Number of people used to restore service | CPUC major event?
1 | Rain/Snow/Wind Storm | 2001-02-13 | 3.106 |  |  |  | N
2 | Wind Storm | 2001-01-11 | 1.7288 |  |  |  | N
3 | Rain/Wind Storm | 2001-11-24 | 1.6705 |  |  |  | N
4 | Rain/Wind Storm | 2001-11-12 | 1.1803 |  |  |  | N
5 | Wind Storm | 2001-01-10 | 0.91992 |  |  |  | N
6 | Wind Storm | 2001-09-30 | 0.59811 |  |  |  | N
7 | Rain Storm | 2001-10-30 | 0.59 |  |  |  | N
8 | Lightning Storm | 2001-07-06 | 0.56447 |  |  |  | N
9 | Structure Fire | 2001-06-21 | 0.56441 |  |  |  | N
10 | Rain/Snow/Wind Storm | 2001-02-12 | 0.55418 |  |  |  | N
2000 | [6 empty] | Attachment 2E
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption (min) | Number of people used to restore service | CPUC major event?
1 | Equipment Failure | 2000-10-26 | 1.5705 |  |  |  | N
2 | Rain/Wind Storm | 2000-04-18 | 1.2847 |  |  |  | N
3 | Rain/Wind Storm | 2000-02-20 | 0.94447 |  |  |  | N
4 | Rain/Wind Storm | 2000-02-21 | 0.8196 |  |  |  | N
5 | Car Hit Transmission Pole | 2000-04-03 | 0.80443 |  |  |  | N
6 | Wind Storm | 2000-03-21 | 0.77422 |  |  |  | N
7 | Rain/Wind Storm | 2000-03-05 | 0.63785 |  |  |  | N
8 | Rain Storm | 2000-09-22 | 0.6329 |  |  |  | N
9 | Rain/Wind Storm | 2000-04-17 | 0.57183 |  |  |  | N
10 | Equipment Failure | 2000-05-13 | 0.55115 |  |  |  | N
1999 | [6 empty] | Attachment 2E
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption (min) | Number of people used to restore service | CPUC major event?
1 | Hector Mines Earthquake | 1999-10-16 | 3.314 |  |  |  | N
2 | Rain/Wind Storm | 1999-01-25 | 2.0993 |  |  |  | N
3 | Rain Storm | 1999-11-08 | 1.6926 |  |  |  | N
4 | Rain/Wind Storm | 1999-04-03 | 1.0897 |  |  |  | N
5 | Rain Storm | 1999-04-06 | 0.99027 |  |  |  | N
6 | Laguna Bell A-Bank | 1999-07-07 | 0.73652 |  |  |  | N
7 | Rain/Wind Storm | 1999-02-09 | 0.67476 |  |  |  | N
8 | La Cienega A-Bank | 1999-01-07 | 0.66321 |  |  |  | N
9 | Wind Storm | 1999-02-11 | 0.65328 |  |  |  | N
10 | Heat/Lightning Storm | 1999-07-11 | 0.62073 |  |  |  | N
1998 | [6 empty] | Attachment 2E
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption (min) | Number of people used to restore service | CPUC major event?
1 | La Nina Heat Storm | 08/29/1998 - 09/04/1998 | 9.3727 |  |  |  | N
2 | El Nino Rain Storm | 02/03/1998 - 02/05/1998 | 8.9347 |  |  |  | N
3 | Wind Storm | 12/09/1998 | 5.5171 |  |  |  | N
4 | Wind Storm | 12/06/1998 | 2.6246 |  |  |  | N
5 | Rain Storm | 02/23/1998 | 1.6497 |  |  |  | N
6 | Rain Storm | 03/24/1998 | 1.1831 |  |  |  | N
7 | Rain Storm | 11/08/1998 | 1.119 |  |  |  | N
8 | El Nino Rain Storm | 02/06/1998 | 1.0561 |  |  |  | N
9 | El Nino Rain Storm | 02/02/1998 | 0.95933 |  |  |  | N
10 | Rain Storm | 02/24/1998 | 0.89477 |  |  |  | N
1997 | [6 empty] | Attachment 2E
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption (min) | Number of people used to restore service | CPUC major event?
1 | Rain Storm | 01/06/1997 - 01/09/1997 | 21.9161 |  |  |  | N
2 | Rain Storm | 1997-01-13 | 1.9715 |  |  |  | N
3 | Plane Crash | 1997-08-05 | 1.7605 |  |  |  | N
4 | Wind Storm | 1997-12-11 | 1.4818 |  |  |  | N
5 | Wind Storm | 1997-12-06 | 1.221 |  |  |  | N
6 | Rain Storm | 1997-09-25 | 1.2155 |  |  |  | N
7 | Wind Storm | 1997-11-10 | 1.2062 |  |  |  | N
8 | Rain Storm | 1997-11-26 | 1.1881 |  |  |  | N
9 | Lightning Storm | 1997-09-02 | 0.78466 |  |  |  | N
10 | Wind Storm | 12/10/1997 | 0.68581 |  |  |  | N
1996 | [6 empty] | Attachment 2E
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption (min) | Number of people used to restore service | CPUC major event?
1 | WSCC Intertie Disturbance | 08/10/1996 - 08/12/1996 | 64.0715 | 1978742 | 1038 | 300 | Y
2 | Wind Storm | 1996-12-22 | 3.0236 |  |  |  | N
3 | Wind Storm | 1996-12-15 | 2.9425 |  |  |  | N
4 | Wind Storm | 1996-01-01 | 2.8298 |  |  |  | N
5 | Wind Storm | 1996-12-14 | 2.1172 |  |  |  | N
6 | Wind Storm | 1996-10-30 | 1.96 |  |  |  | N
7 | Wind Storm | 1996-10-25 | 1.5081 |  |  |  | N
8 | Wind Storm | 1996-10-21 | 1.4034 |  |  |  | N
9 | Wind Storm | 1996-11-27 | 1.0157 |  |  |  | N
10 | Wind Storm | 1996-10-29 | 0.80286 |  |  |  | N
1995 | [6 empty] | Attachment 2E
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption (min) | Number of people used to restore service | CPUC major event?
1 | Wind Storm | 12/31/1995 - 01/03/1996 | 9.6784 |  |  |  | N
2 | Snow Storm | 1995-01-04 | 4.1573 |  |  |  | N
3 | Snow Storm | 1995-03-10 | 3.88 |  |  |  | N
4 | Wind Storm | 1995-01-10 | 1.5011 |  |  |  | N
5 | Snow Storm | 1995-01-05 | 1.4371 |  |  |  | N
6 | Wind Storm | 1995-03-11 | 1.0955 |  |  |  | N
7 | Wind Storm | 1995-09-02 | 1.0094 |  |  |  | N
8 | Wind Storm | 1995-03-23 | 0.83806 |  |  |  | N
9 | Wind Storm | 1995-12-12 | 0.78277 |  |  |  | N
10 | Vehicle Hit Pole | 1995-02-14 | 0.69805 |  |  |  | N