## AGHistorical
Attachment 1
Southern California Edison
Historical System Reliability Data
1994 - 2003
|  | All Interruptions Included |  |  | Major Events Excluded
YEAR | SAIDI | SAIFI | MAIFI | SAIDI | SAIFI | MAIFI
1994
1995
1996
1997
1998
1999
2000
2001
2002 | 49.58 | 0.936 | 1.47 | 47.56 | 0.79 | 1.47
20031 | 81.61 | 1.001 | 2.283 | 57.9 | 0.835 | 1.99
1 2003 results exclude outages for all circuits in areas designated to be bark beetle-infested areas, and replaced with a ten year average performance.

## Historical
Attachment 2
Southern California Edison
Historical System Reliability Data
1994 - 2003
|  | All Interruptions Included |  |  | Major Events Excluded
YEAR | SAIDI1 | SAIFI | MAIFI | SAIDI1 | SAIFI | MAIFI
1994 | 124.132 | 0.853 | 1.2416 | 43.9529 | 0.67953 | 1.1485
1995 | 66.8662 | 0.87004 | 1.096 | 66.8662 | 0.87004 | 1.096
1996 | 125.9625 | 1.4178 | 1.4033 | 61.891 | 0.9725 | 1.3798
1997 | 77.0214 | 1.0996 | 1.3382 | 77.0214 | 1.0996 | 1.3382
1998 | 78.4768 | 1.3073 | 1.3874 | 78.4768 | 1.3073 | 1.3874
1999 | 49.0461 | 1.044 | 1.226 | 49.0461 | 1.044 | 1.226
2000 | 46.8684 | 1.1163 | 1.2334 | 46.8684 | 1.1163 | 1.2334
2001 | 51.589 | 1.0478 | 1.1602 | 51.589 | 1.0478 | 1.1602
2002 | 52.6172 | 1.2665 | 1.1488 | 50.3101 | 1.1164 | 1.1391
20032 | 80.8485 | 1.3484 | 1.4346 | 57.5732 | 1.1477 | 1.2264
1 Normalized to reflect the variance introduced by Edison International's convention of declaring All Load Up (ALU) when power had been restored
up to the last residential transformer - an estimate was added to the annual CMI base to arrive at the normalized SAIDIs.
2 2003 results exclude outages for all circuits in areas designated to be bark beetle-infested areas, and replaced with a ten year average performance.

## List >12 Sustained
NEW SUSTAINED OUTAGE DEFINITION
Year | Circuit | Circuit Name | Number of customers experiencing > 12 sustained outages | Year | Circuit | Circuit Name | Number of customers experiencing > 12 sustained outages
1994 | 4635 | DANBY | 25 | 2003 | 2290 | BROOKINGS | 1
| 3130 | CASTLE | 713 |  | 2370 | BUDD | 252
1995 | 3485 | CHINA RANCH | 4 |  | 2881 | CAPANERO | 292
| 7657 | GRIMSHAW | 69 |  | 3240 | CEDAR GLEN | 407
| 8735 | HOT WATER | 32 |  | 5850 | ELSTER | 43
| 14926 | REVERSE PEAK | 8 |  | 8410 | HIGH SCHOOL | 341
| 15282 | ROBINSON CREEK | 140 |  | 8670 | HOOK CREEK | 550
| 16600 | SODA SPRINGS | 47 |  | 9320 | JORDAN | 667
| 17955 | TOLL | 75 |  | 9549 | KELLPEAK | 10
| 15415 | ROSEBUD | 536 |  | 11448 | MCCLENNY | 55
1996 | 14955 | RHINEDOLLAR | 14 |  | 12190 | MORITZ | 1345
1997 | 11448 | MCCLENNY | 57 |  | 12860 | NORTH SHORE | 528
| 14349 | POSO PARK | 49 |  | 14349 | POSO PARK | 49
| 17190 | SUGARLOAF | 114 |  | 14690 | RANGER | 730
| 1640 | BIG PINES | 242 |  | 15922 | SAUNDERS | 733
| 9320 | JORDAN | 698 |  | 16049 | SEALS | 93
| 11270 | MARSH | 848 |  | 16839 | SQUINT | 778
| 12190 | MORITZ | 502 |  | 17190 | SUGARLOAF | 131
| 17063 | STONEMAN | 80 |  | 17997 | TORONTO | 53
1998 | 3890 | CONCEPCION | 126
| 16600 | SODA SPRINGS | 53
| 14652 | RAMAC | 7
| 17663 | TENNECO | 307
| 19150 | WELLS | 123
1999 | 3170 | CATTLE | 296
| 15475 | ROWCO | 849
2000 | 5085 | DINKEY CREEK | 37
| 8702 | HOSSACK | 100
| 10945 | MAHOGANY | 6
| 12910 | NOVAC | 272
| 13959 | PERIMETER | 7
| 17672 | TERMINUS | 137
2001 | 1626 | BIGFOOT | 47
| 2664 | CALCADIA | 5
| 3890 | CONCEPCION | 68
| 5018 | DEVINE | 8
| 5146 | DOGWOOD | 1890
| 12722 | NIPTON | 27
| 15680 | SALT CREEK | 118
| 19134 | WEINING | 64
2002 | 1630 | BIG ROCK | 469
| 4635 | DANBY | 57
| 9060 | IVERSON | 124

## No Service by Hourly Interval
THIS TABLE CONTAINS ROLLING DAY DATA. | [8 empty] | NEW SUSTAINED OUTAGE DEFINITION
| Northridge Earthquake | Northridge Earthquake | Northridge Earthquake | WSCC Pacific Intertie | WSCC Pacific Intertie | WSCC Pacific Intertie | Mira Loma RAS | Mira Loma RAS | ï Description of event
Time | 1994-01-17 | 1994-01-18 | 1994-01-19 | 1996-08-10 | 1996-08-11 | 1996-08-12 | 2002-06-26 | 2002-06-27 | ïDate of event
0 | 2637 | 46721 | 57 | 2640 | 4709 | 159 | 1973 | 459
1 | 3171 | 4542 | 57 | 2851 | 1762 | 98 | 1995 | 459
2 | 195 | 3312 | 57 | 211 | 1888 | 108 | 22 | 459
3 | 195 | 3115 | 7 | 211 | 2829 | 108 | 0 | 9716
4 | 903390 | 1650 | 541 | 3065 | 3235 | 108 | 0 | 459
5 | 541461 | 4771 | 7 | 704 | 527 | 108 | 0 | 4571
6 | 532081 | 3044 | 7 | 266 | 579 | 1656 | 469 | 2136
7 | 576456 | 7339 | 174 | 610 | 2750 | 76 | 0 | 589
8 | 477808 | 4256 | 174 | 588 | 393 | 3556 | 131 | 589
9 | 448021 | 1338 | 174 | 293 | 382 | 2403 | 0 | 501
10 | 439365 | 5406 | 174 | 12 | 317 | 2402 | 412 | 768
11 | 427073 | 2219 | 7 | 2812 | 1517 | 856 | 114 | 1548
12 | 420299 | 2962 | 0 | 12 | 4630 | 9389 | 1053 | 451
13 | 415879 | 1752 | 0 | 72036 | 2004 | 14339 | 622 | 360
14 | 316889 | 803 | 0 | 72033 | 176 | 15568 | 622 | 275
15 | 224531 | 666 | 0 | 1725167 | 4951 | 11504 | 0 | 347
16 | 158073 | 566 | 0 | 1819090 | 6114 | 17419 | 0 | 1422
17 | 127152 | 675 | 0 | 1610131 | 11226 | 1723 | 0 | 2164
18 | 117840 | 142 | 964 | 1299530 | 4400 | 3476 | 664331 | 4489
19 | 107412 | 19 | 2803 | 31614 | 876 | 1326 | 112065 | 365
20 | 100287 | 7 | 71 | 20946 | 4437 | 2018 | 6960 | 365
21 | 97352 | 2307 | 71 | 17018 | 263 | 1604 | 3244 | 365
22 | 78803 | 7 | 71 | 5492 | 959 | 2624 | 459 | 365
23 | 69910 | 57 | 1360 | 9331 | 1095 | 1193 | 2827 | 365
THIS TABLE CONTAINS ROLLING DAY DATA. | [8 empty] | NEW SUSTAINED OUTAGE DEFINITION
| Mira Loma RAS | Santa Ana Wind Storm | Santa Ana Wind Storm | Santa Ana Wind Storm | Southern California Wild Fires | Southern California Wild Fires | Southern California Wild Fires |  | ï Description of event
Time | 2002-06-28 | 2003-01-06 | 2003-01-07 | 2003-01-08 | 2003-10-24 | 2003-10-25 | 2003-10-26 |  | ïDate of event
0 | 365 | 152558 | 24149 | 5099 | 0 | 99 | 6168
1 | 1054 | 178860 | 26720 | 9867 | 81 | 4491 | 60988
2 | 1116 | 191240 | 35678 | 7212 | 1681 | 47 | 7531
3 | 1610 | 171284 | 23267 | 5691 | 110 | 47 | 216964
4 | 10112 | 129501 | 41711 | 4315 | 81 | 1847 | 91757
5 | 531 | 113799 | 48693 | 4155 | 602 | 14854 | 59708
6 | 469 | 101011 | 35370 | 4102 | 6403 | 41 | 31397
7 | 3731 | 86230 | 31423 | 4137 | 521 | 3546 | 7319
8 | 4279 | 86946 | 15173 | 6844 | 1134 | 19363 | 9418
9 | 598 | 58992 | 13628 | 7833 | 637 | 1317 | 5964
10 | 1779 | 63936 | 26507 | 9774 | 129989 | 4454 | 8866
11 | 845 | 60261 | 35443 | 8491 | 653 | 3256 | 7916
12 | 432 | 69743 | 30041 | 11349 | 574 | 2912 | 6377
13 | 370 | 77406 | 24075 | 11607 | 15893 | 2295 | 28222
14 | 275 | 61304 | 10701 | 26750 | 600 | 2991 | 16783
15 | 275 | 45025 | 9033 | 6676 | 590 | 30036 | 14395
16 | 275 | 25292 | 8628 | 4368 | 575 | 7055 | 11363
17 | 4341 | 25852 | 11222 | 4000 | 575 | 9159 | 10280
18 | 2950 | 25773 | 7709 | 3030 | 1171 | 1279 | 8013
19 | 473 | 29423 | 12265 | 2930 | 616 | 2759 | 5761
20 | 1314 | 51181 | 14995 | 2091 | 586 | 3800 | 5995
21 | 473 | 27891 | 12993 | 2026 | 727 | 3087 | 5622
22 | 473 | 20583 | 10023 | 2313 | 3652 | 4829 | 5757
23 | 473 | 34829 | 11230 | 1540 | 1606 | 4722 | 4068

## No Service by Duration
NEW SUSTAINED OUTAGE DEFINITION
| Northridge Earthquake | WSCC Pacific Intertie | Mira Loma RAS | Santa Ana Wind Storm | Southern California Wild Fires | ïDescription of event
Outage Duration | 01/17/1994 - 01/19/1994 | 08/10/1996 - 08/12/1996 | 06/26/2002 - 06/28/2002 | 01/06/2003 - 01/08/2003 | 10/24/2003 - 10/26/2003 | ïDate of event
0 to 1 hour | 427074 | 117623 | 667539 | 792126 | 512773
1 to 5 hours | 117355 | 1826710 | 47086 | 172324 | 73838
5 to 10 hours | 294165 | 23673 | 5835 | 61154 | 11577
10 to 15 hours | 143152 | 10502 | 1203 | 57778 | 4883
15 to 20 hours | 78136 | 234 | 2744 | 55373 | 1996
20 to 24 hours | 41360 | 0 | 0 | 15325 | 4081
1 to 2 days | 5160 | 0 | 0 | 56503 | 11169
2 to 3 days | 0 | 0 | 275 | 24949 | 1734
3 to 4 days | 0 | 0 | 0 | 5524 | 5040
4 to 5 days | 0 | 0 | 0 | 0 | 7169
5 to 6 days | 0 | 0 | 0 | 900 | 3478
6 to 7 days | 0 | 0 | 0 | 0 | 25
> 7 days | 0 | 0 | 0 | 0 | 1003
Total | 1106402 | 1978742 | 724682 | 1241956 | 638766

## Top 10 SAIDI each year
1994 | NEW SUSTAINED OUTAGE DEFINITION
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption (min) | Number of people used to restore service | CPUC major event?
1 | Northridge Earthquake | 01/17/1994 - 01/19/1994 | 80.1791 | 1106402 | 2270 | N/A | Y
2 | Rain Storm | 1994-10-04 | 0.89114 |  |  |  | N
3 | Lightning Storm | 1994-08-13 | 0.70297 |  |  |  | N
4 | Lightning Storm | 1994-04-26 | 0.69375 |  |  |  | N
5 | Wind Storm | 1994-02-07 | 0.66839 |  |  |  | N
6 | Equipment Failure | 1994-03-24 | 0.61868 |  |  |  | N
7 | Heavy Fog | 1994-11-10 | 0.59503 |  |  |  | N
8 | Wind Storm | 1994-11-16 | 0.58207 |  |  |  | N
9 | Lightning Storm | 1994-08-12 | 0.53937 |  |  |  | N
10 | Wind Storm | 1994-11-26 | 0.52845 |  |  |  | N
1995 | NEW SUSTAINED OUTAGE DEFINITION
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption (min) | Number of people used to restore service | CPUC major event?
1 | Wind Storm | 12/31/1995 - 01/03/1996 | 9.6784 |  |  |  | N
2 | Snow Storm | 1995-01-04 | 4.1573 |  |  |  | N
3 | Snow Storm | 1995-03-10 | 3.88 |  |  |  | N
4 | Wind Storm | 1995-01-10 | 1.5011 |  |  |  | N
5 | Snow Storm | 1995-01-05 | 1.4371 |  |  |  | N
6 | Wind Storm | 1995-03-11 | 1.0955 |  |  |  | N
7 | Wind Storm | 1995-09-02 | 1.0094 |  |  |  | N
8 | Wind Storm | 1995-03-23 | 0.83806 |  |  |  | N
9 | Wind Storm | 1995-12-12 | 0.78277 |  |  |  | N
10 | Vehicle Hit Pole | 1995-02-14 | 0.69805 |  |  |  | N
1996 | NEW SUSTAINED OUTAGE DEFINITION
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption (min) | Number of people used to restore service | CPUC major event?
1 | WSCC Intertie Disturbance | 08/10/1996 - 08/12/1996 | 64.0715 | 1978742 | 1038 | 300 | Y
2 | Wind Storm | 1996-12-22 | 3.0236 |  |  |  | N
3 | Wind Storm | 1996-12-15 | 2.9425 |  |  |  | N
4 | Wind Storm | 1996-01-01 | 2.8298 |  |  |  | N
5 | Wind Storm | 1996-12-14 | 2.1172 |  |  |  | N
6 | Wind Storm | 1996-10-30 | 1.96 |  |  |  | N
7 | Wind Storm | 1996-10-25 | 1.5081 |  |  |  | N
8 | Wind Storm | 1996-10-21 | 1.4034 |  |  |  | N
9 | Wind Storm | 1996-11-27 | 1.0157 |  |  |  | N
10 | Wind Storm | 1996-10-29 | 0.80286 |  |  |  | N
1997 | NEW SUSTAINED OUTAGE DEFINITION
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption (min) | Number of people used to restore service | CPUC major event?
1 | Rain Storm | 01/06/1997 - 01/09/1997 | 21.9161 |  |  |  | N
2 | Rain Storm | 1997-01-13 | 1.9715 |  |  |  | N
3 | Plane Crash | 1997-08-05 | 1.7605 |  |  |  | N
4 | Wind Storm | 1997-12-11 | 1.4818 |  |  |  | N
5 | Wind Storm | 1997-12-06 | 1.221 |  |  |  | N
6 | Rain Storm | 1997-09-25 | 1.2155 |  |  |  | N
7 | Wind Storm | 1997-11-10 | 1.2062 |  |  |  | N
8 | Rain Storm | 1997-11-26 | 1.1881 |  |  |  | N
9 | Lightning Storm | 1997-09-02 | 0.78466 |  |  |  | N
10 | Wind Storm | 12/10/1997 | 0.68581 |  |  |  | N
1998 | NEW SUSTAINED OUTAGE DEFINITION
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption (min) | Number of people used to restore service | CPUC major event?
1 | La Nina Heat Storm | 08/29/1998 - 09/04/1998 | 9.3727 |  |  |  | N
2 | El Nino Rain Storm | 02/03/1998 - 02/05/1998 | 8.9347 |  |  |  | N
3 | Wind Storm | 12/09/1998 | 5.5171 |  |  |  | N
4 | Wind Storm | 12/06/1998 | 2.6246 |  |  |  | N
5 | Rain Storm | 02/23/1998 | 1.6497 |  |  |  | N
6 | Rain Storm | 03/24/1998 | 1.1831 |  |  |  | N
7 | Rain Storm | 11/08/1998 | 1.119 |  |  |  | N
8 | El Nino Rain Storm | 02/06/1998 | 1.0561 |  |  |  | N
9 | El Nino Rain Storm | 02/02/1998 | 0.95933 |  |  |  | N
10 | Rain Storm | 02/24/1998 | 0.89477 |  |  |  | N
1999 | NEW SUSTAINED OUTAGE DEFINITION
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption (min) | Number of people used to restore service | CPUC major event?
1 | Hector Mines Earthquake | 1999-10-16 | 3.314 |  |  |  | N
2 | Rain/Wind Storm | 1999-01-25 | 2.0993 |  |  |  | N
3 | Rain Storm | 1999-11-08 | 1.6926 |  |  |  | N
4 | Rain/Wind Storm | 1999-04-03 | 1.0897 |  |  |  | N
5 | Rain Storm | 1999-04-06 | 0.99027 |  |  |  | N
6 | Laguna Bell A-Bank | 1999-07-07 | 0.73652 |  |  |  | N
7 | Rain/Wind Storm | 1999-02-09 | 0.67476 |  |  |  | N
8 | La Cienega A-Bank | 1999-01-07 | 0.66321 |  |  |  | N
9 | Wind Storm | 1999-02-11 | 0.65328 |  |  |  | N
10 | Heat/Lightning Storm | 1999-07-11 | 0.62073 |  |  |  | N
2000 | NEW SUSTAINED OUTAGE DEFINITION
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption (min) | Number of people used to restore service | CPUC major event?
1 | Equipment Failure | 2000-10-26 | 1.5705 |  |  |  | N
2 | Rain/Wind Storm | 2000-04-18 | 1.2847 |  |  |  | N
3 | Rain/Wind Storm | 2000-02-20 | 0.94447 |  |  |  | N
4 | Rain/Wind Storm | 2000-02-21 | 0.8196 |  |  |  | N
5 | Car Hit Transmission Pole | 2000-04-03 | 0.80443 |  |  |  | N
6 | Wind Storm | 2000-03-21 | 0.77422 |  |  |  | N
7 | Rain/Wind Storm | 2000-03-05 | 0.63785 |  |  |  | N
8 | Rain Storm | 2000-09-22 | 0.6329 |  |  |  | N
9 | Rain/Wind Storm | 2000-04-17 | 0.57183 |  |  |  | N
10 | Equipment Failure | 2000-05-13 | 0.55115 |  |  |  | N
2001 | NEW SUSTAINED OUTAGE DEFINITION
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption (min) | Number of people used to restore service | CPUC major event?
1 | Rain/Snow/Wind Storm | 2001-02-13 | 3.106 |  |  |  | N
2 | Wind Storm | 2001-01-11 | 1.7288 |  |  |  | N
3 | Rain/Wind Storm | 2001-11-24 | 1.6705 |  |  |  | N
4 | Rain/Wind Storm | 2001-11-12 | 1.1803 |  |  |  | N
5 | Wind Storm | 2001-01-10 | 0.91992 |  |  |  | N
6 | Wind Storm | 2001-09-30 | 0.59811 |  |  |  | N
7 | Rain Storm | 2001-10-30 | 0.59 |  |  |  | N
8 | Lightning Storm | 2001-07-06 | 0.56447 |  |  |  | N
9 | Structure Fire | 2001-06-21 | 0.56441 |  |  |  | N
10 | Rain/Snow/Wind Storm | 2001-02-12 | 0.55418 |  |  |  | N
2002 | NEW SUSTAINED OUTAGE DEFINITION
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption (min) | Number of people used to restore service | CPUC major event?
1 | Rain/Wind Storm | 2002-12-16 | 2.7805 |  |  |  | N
2 | Rain/Wind Storm | 2002-11-08 | 2.4152 |  |  |  | N
3 | Mira Loma RAS / Louisiana Fire | 06/26/2002 - 06/28/2002 | 2.3071 | 724682 | 3996 | 50 | Y
4 | Rain/Wind Storm | 2002-11-09 | 1.0429 |  |  |  | N
5 | Rain Storm | 2002-11-25 | 1.0143 |  |  |  | N
6 | Wind Storm | 2002-02-09 | 0.85849 |  |  |  | N
7 | Car Hit Pole | 2002-10-04 | 0.84707 |  |  |  | N
8 | Rain/Wind Storm | 2002-11-07 | 0.70412 |  |  |  | N
9 | Heat Storm | 2002-09-01 | 0.66042 |  |  |  | N
10 | Rain Storm | 2002-02-17 | 0.64036 |  |  |  | N
2003 | NEW SUSTAINED OUTAGE DEFINITION
Rank | Description | Date | SAIDI | Number of customers affected | Longest customer interruption (min) | Number of people used to restore service | CPUC major event?
1 | Santa Ana Wind Storm | 01/06/2003 - 01/08/2003 | 17.21 | 1241956 | 7731 | 2551 | Y
2 | Southern California Wild Fires | 10/24/2003 - 10/26/2003 | 6.0652 | 638766 | 12808 | 1919 | Y
3 | Rain Storm & Mud Slides | 12/25/2003 | 3.4669 |  |  |  | N
4 | Lightning Storm | 11/12/2003 | 3.0194 |  |  |  | N
5 | Santa Ana Wind Storm | 01/05/2003 | 2.4373 |  |  |  | N
6 | Rain Storm | 02/25/2003 | 2.3019 |  |  |  | N
7 | Rain Storm | 10/31/2003 | 1.1247 |  |  |  | N
8 | Wind Storm | 03/17/2003 | 0.94569 |  |  |  | N
9 | Wind Storm | 02/12/2003 | 0.79558 |  |  |  | N
10 | Lightning Storm | 08/20/2003 | 0.769 |  |  |  | N