## sys indx
Report on California System Reliability
Sierra Pacific Power Company
Report Year 2003
System Indices: Sierra Pacific Power Co.
| Major Events Included |  |  | Major Events Excluded
YEAR | SAIDI | SAIFI | MAIFI* | SAIDI | SAIFI | MAIFI*
| CMI |  |  | CMI
1989* | 78.6 | 1.13 |  | 78.6 | 1.13
1990 | 256.3 | 2.29 |  | 183.6 | 1.64
1991 | 319.2 | 1.92 |  | 71.9 | 0.84
1992 | 161.4 | 2.02 |  | 100.6 | 1.61
1993 | 160.1 | 1.21 |  | 64.1 | 0.84
1994* | 214.3 | 2.44 |  | 214.3 | 2.44
1995 | 463.31 | 4.89 |  | 244.8 | 4.04
1996 | 638.03 | 3.11 |  | 168.6 | 2.68
1997 | 323.01 | 2.62 |  | 124.8 | 1.82
1998* | 164.33 | 3.15 | 3.78 | 164.33 | 3.15 | 3.78
1999* | 137.94 | 1.81 | 1.8 | 137.56 | 1.81 | 1.8
2000 | 219.3 | 2.37 | 2.78 | 118.857 | 1.65 | 2.78
2001 | 153.24 | 1.2224 | 0.901 | 166.044 | 1.2301 | 0.901
2002 | 951.522 | 14.97 | 1.4909 | 82.065 | 1.281 | 1.4909
2003* | 84.162 | 1.4027 | 0.5954 | 84.2 | 1.4027 | 0.5954
* No major storms, resulting in no major events being excluded.
NORMALIZATION EXCEPTIONS:
A. The SPPCo definition of an outage is loss of power to one or more customers
for greater than five minutes, like the Nevada Standard.
B. SPPCo excludable outages are not based on 10% of a very limited customer
base, alone, but on a combination of (1) storm severity, (2) system design limits,
(3) customers out and (4) total customer hours.
At the end of 2002, only 13.3% (42,689) of SPPCo electric customers lived
in its California Service area.
C. SPPCo existing data base and reporting would have to
be changed.

## soe1
Significant Outage Events: SPPCo. 2003
RANK | Description | Date | Number of Customers Affected | Longest Customer Interruption-(hours) | C-hrs | Number of People used to restore Service | CPUC Major Event?
1 | Overhead Trees | 2003-04-13 | 5743 | 11.85 | 11941.6 | n/a | n
2 | Overhead Trees | 2003-04-13 | 3548 | 2 | 6630.2 | n/a | n
3 | 3D Car Pole | 2003-02-07 | 3475 | 7 | 6476 | n/a | n
4 | OH Birds/Animals | 2003-07-13 | 4018 | 5.33 | 4636.4 | n/a | n
5 | OH Other | 2003-04-14 | 2742 | 4.27 | 3846.8 | n/a | n
6 | UG Elbow | 2003-09-16 | 2558 | 1.67 | 3297.5 | n/a | n
7 | Lightning | 2003-07-31 | 1444 | 4.5 | 2266.4 | n/a | n
8 | UG Cable | 2003-01-06 | 250 | 12.5 | 2425 | n/a | n
9 | Overhead Trees | 2003-04-13 | 165 | 13.87 | 1176.2 | n/a | n
10 | UG Cable | 2003-01-06 | 1444 | 7.1 | 1063.4 | n/a | n
Significant Outage Events: SPPCo. 2002
RANK | Description | Date | Number of Customers Affected | Longest Customer Interruption-(hours) | C-hrs | Number of People used to restore Service | CPUC Major Event?
1 | Green Trees/Storm | 12/14-12/20/02 | 81820 | 113.42 | 533479 | n/a | y
2 | Green Trees/Storm | 11/07-11/10/02 | 47895 | 30.65 | 43424 | n/a | y
3 | UG Cable | 2002-01-10 | 5120 | 13.95 | 5489.7 | n/a | n
4 | Trees | 2002-12-28 | 4120 | 1.17 | 1099.1 | n/a | n
5 | 3D tree Trimming | 2002-07-18 | 4120 | 8.97 | 1798.7 | n/a | n
6 | Trees | 1973101 | 4120 | 7.08 | 2571.5 | n/a | n
7 | 3D Car/Pole | 2002-06-21 | 3315 | 0.5 | 1657.5 | n/a | n
8 | Trees | 2002-05-19 | 3587 | 5.25 | 4134.6 | n/a | n
9 | Lightning | 2002-07-18 | 3587 | 1.52 | 4161.4 | n/a | n
10 | Birds/Animals | 2002-09-25 | 3587 | 1.33 | 2241.7 | n/a | n
Note: The 12/14 and 11/07 storms affected multiple same circuit outages from high winds and snow loading on
green trees.
Significant Outage Events: SPPCo. 2001
RANK | Description | Date | Number of Customers Affected | Longest Customer Interruption-(hours) | C-hrs | Number of People used to restore Service | CPUC Major Event?
1 | Birds & Animals | 2001-09-08 | 8005 | 3.4 | 21181 | n/a | n
2 | Trees | 2001-12-02 | 4120 | 9.05 | 17371 | n/a | n
3 | Trees | 2001-12-03 | 2596 | 16.3 | 11540 | n/a | n
4 | Trees | 2001-11-21 | 2656 | 10.83 | 8426 | n/a | n
5 | Wire Down | 2001-12-03 | 960 | 7.42 | 7120 | n/a | n
6 | Capacitor | 2001-12-24 | 3141 | 1.58 | 4972 | n/a | n
7 | Birds/Animals | 2001-10-01 | 7295 | 0.65 | 4742 | n/a | n
8 | OH Insulator | 2001-03-05 | 3266 | 1.43 | 4680 | n/a | n
9 | Snow Unloading | 2001-12-02 | 922 | 4.83 | 4456 | n/a | n
10 | Trees | 2001-08-01 | 1444 | 16.43 | 4121 | n/a | n
Significant Outage Events: SPPCo. 2000
RANK | Description | Date | Number of Customers Affected | Longest Customer Interruption-(hours) | C-hrs | Number of People used to restore Service | CPUC Major Event?
1 | Trees (Storm) | 2000-02-14 | 30343 | 34.92 | 70836 | n/a | y
2 | 3D Other (3rd party tree) | 2000-02-22 | 4000 | 5.63 | 15091 | n/a | n
3 | OH Hardware/Matls. | 2000-08-10 | 4038 | 5.23 | 13465.6 | n/a | n
4 | OH Debris | 2000-05-29 | 4038 | 2.75 | 7807 | n/a | n
5 | Trees | 2000-12-17 | 4038 | 5 | 6757 | n/a | n
6 | 3D Dig in | 2000-11-09 | 4038 | 1.83 | 6216.7 | n/a | n
7 | OH Wire Down | 2000-01-16 | 2537 | 2.73 | 3762.9 | n/a | n
8 | SB Hardware/Matls. | 2000-07-19 | 3235 | 0.97 | 3101.1 | n/a | n
9 | SB Hardware/Matls. | 2000-07-19 | 2969 | 0.98 | 2828.6 | n/a | n
10 | OH Insulator | 2000-02-14 | 5298 | 0.5 | 2649 | n/a | n
Significant Outage Events: SPPCo. 1999
RANK | Description | Date | Number of Customers Affected | Longest Customer Interruption-(hours) | C-hrs | Number of People used to restore Service | CPUC Major Event?
1 | Wire Down | 1999-02-10 | 2766 | 4.35 | 7917 | n/a | n
2 | Trees | 1999-02-07 | 2656 | 3.25 | 6878 | n/a | n
3 | Trees | 1999-02-08 | 5298 | 2.4 | 6305 | n/a | n
4 | Hardware Failure | 1999-03-04 | 2656 | 2.3 | 4515 | n/a | n
5 | Wire Down | 1999-02-10 | 1968 | 1.77 | 3477 | n/a | n
6 | Trees | 1999-02-23 | 2766 | 1.08 | 2995 | n/a | n
7 | Birds/Animals | 1999-05-09 | 1439 | 2 | 2878 | n/a | n
8 | UG Cable | 1999-06-23 | 2518 | 12.45 | 2580 | n/a | n
9 | Birds/Animals | 1999-09-06 | 2700 | 0.83 | 2249 | n/a | n
10 | Birds/Animals | 1999-08-06 | 2049 | 1.07 | 2186 | n/a | n
Significant Outage Events: SPPCo. 1998
RANK | Description | Date | Number of Customers Affected | Longest Customer Interruption-(hours) | C-hrs | Number of People used to restore Service | CPUC Major Event?
1 | Trees | 1998-01-18 | 2550 | 15.33 | 24564 | n/a | n
2 | Trees | 1998-11-22 | 4000 | 3.25 | 6875 | n/a | n
3 | Birds/animals | 1998-02-13 | 2550 | 2.63 | 6222 | n/a | n
4 | Tree Trimming | 1998-10-01 | 2536 | 2.18 | 5536 | n/a | n
5 | Snow unloading | 1998-03-25 | 2550 | 2.52 | 4185 | n/a | n
6 | Trees | 1998-11-07 | 200 | 17.75 | 3550 | n/a | n
7 | Trees | 1998-11-23 | 2536 | 2.8 | 3141 | n/a | n
8 | Car pole/down guy | 1998-04-13 | 4000 | 2.75 | 3015 | n/a | n
9 | Trees | 1998-11-21 | 2550 | 1 | 2656 | n/a | n
10 | Hardware Failure | 1998-11-18 | 1760 | 1.5 | 2607 | n/a | n
Significant Outage Events: SPPCo. 1997
RANK | Description | Date | Number of Customers Affected | Longest Customer Interruption-(hours) | C-hrs | Number of People used to restore Service | CPUC Major Event?
1 | wind/snow | 1997-01-02 | 21042 | 21.2 | 81683 | 20 | y
2 | wind/snow | 1997-01-22 | 17059 | 15.5 | 64517 | 21 | y
3 | wind/trees | 1997-04-02 | 19924 | 8.6 | 30427 |  | n
4 | s. equip. | 1997-04-18 | 7154 | 1.2 | 8227 |  | n
5 | poles down | 1997-01-24 | 2519 | 6.2 | 5322 |  | n
6 | elbow | 1997-03-14 | 2656 | 1.4 | 3631 |  | n
7 | 3d trees | 1997-01-03 | 2656 | 3.4 | 2647 |  | n
8 | trees | 1997-11-26 | 1121 | 1.7 | 1869 |  | n
9 | trees | 1997-11-19 | 961 | 1.6 | 1553 |  | n
10 | lightning | 1997-07-30 | 14355 | 0.1 | 758 |  | n
Significant Outage Events: SPPCo. 1996
RANK | Description | Date | Number of Customers Affected | Longest Customer Interruption-(hours) | C-hrs | Number of People used to restore Service | CPUC Major Event?
1 | forest fire | 1996-06-23 | 15626 | 24.12 | 291433 | 45 | y
2 | wind/snow | 1996-01-27 | 11718 | 15.3 | 30845 | 22 | y
3 | trees | 1996-01-23 | 4038 | 3.97 | 10363 |  | n
4 | trees | 1996-12-29 | 4038 | 4.75 | 7681 |  | n
5 | trees | 1996-04-24 | 4038 | 4.42 | 7065 |  | n
6 | trees | 1996-02-22 | 5298 | 2.05 | 5713 |  | n
7 | s. eqp | 1996-12-23 | 850 | 10.17 | 4992 |  | n
8 | trees | 1996-01-25 | 4038 | 7.03 | 4713 |  | n
9 | trees | 1996-04-24 | 5289 | 2.08 | 3855 |  | n
10 | car pole | 1996-03-12 | 1439 | 3.9 | 3506 |  | n
Significant Outage Events: SPPCo. 1995
RANK | Description | Date | Number of Customers Affected | Longest Customer Interruption-(hours) | C-hrs | Number of People used to restore Service | CPUC Major Event?
1 | wind/snow | 1995-12-12 | 31374 | 24.38 | 120596 | 21 | y
2 | trees | 1995-01-27 | 4038 | 12.62 | 29019 |  | n
3 | s. arrestor | 1995-03-10 | 14325 | 1.53 | 21960 |  | n
4 | trees | 1995-12-10 | 4038 | 6.3 | 7978 |  | n
5 | s. animal | 1995-08-18 | 7850 | 0.9 | 7065 |  | n
6 | trees | 1995-01-12 | 5298 | 2.7 | 6770 |  | n
7 | s. switch | 1995-04-23 | 5298 | 1.27 | 6712 |  | n
8 | trees | 1995-11-25 | 2548 | 7.17 | 6408 |  | n
9 | car pole | 1995-05-28 | 4038 | 13.01 | 5356 |  | n
10 | trees | 1995-01-10 | 5298 | 0.85 | 4157 |  | n
Significant Outage Events: SPPCo. 1994
RANK | Description | Date | Number of Customers Affected | Longest Customer Interruption-(hrs) | C-hrs | Number of People used to restore Service | CPUC Major Event?
1 | car pole | 1994-11-04 | 7700 | 8.18 | 36190 | n/a | n
2 | s. relay | 1994-05-07 | 5000 | 10.52 | 12477 |  | n
3 | s. reg. | 1994-06-30 | 14325 | 0.57 | 7794 |  | n
4 | trees | 1994-11-01 | 2000 | 3.3 | 5478 |  | n
5 | cable | 1994-08-08 | 1000 | 20.68 | 4692 |  | n
6 | arrestor | 1994-06-27 | 2500 | 3.88 | 4612 |  | n
7 | trees | 1994-07-20 | 5293 | 0.65 | 3440 |  | n
8 | trees | 1994-05-23 | 2000 | 1.67 | 3334 |  | n
9 | trees | 1994-11-09 | 2000 | 2.67 | 3333 |  | n
10 | range fire | 1994-08-04 | 2476 | 1.75 | 3192 |  | n
Significant Outage Events: SPPCo. 1993
RANK | Description | Date | Number of Customers Affected | Longest Customer Interruption-(hrs) | C-hrs | Number of People used to restore Service | CPUC Major Event?
1 | wind/snow | 1993-01-21 | 14587 | 40.67 | 64010 | 35 | y
2 | trees | 1993-11-22 | 1998 | 3.63 | 7259 |  | n
3 | trees | 1993-11-22 | 3200 | 29.77 | 7034 |  | n
4 | trees | 1993-05-03 | 2500 | 1.43 | 3583 |  | n
5 | trees | 1993-12-13 | 3200 | 6.67 | 3499 |  | n
6 | trees | 1993-01-22 | 400 | 6.6 | 2640 |  | n
7 | pole down | 1993-03-17 | 1450 | 11.25 | 2565 |  | n
8 | trees | 1993-11-08 | 2652 | 30.5 | 1476 |  | n
9 | trees | 1993-01-25 | 1500 | 0.8 | 1033 |  | n
10 | trees | 1993-11-23 | 114 | 8.87 | 1010 |  | n
Significant Outage Events: SPPCo. 1992
RANK | Description | Date | Number of Customers Affected | Longest Customer Interruption-(hrs) | C-hrs | Number of People used to restore Service | CPUC Major Event?
1 | wind/snow | 1992-12-28 | 16561 | 23.2 | 40533 | 41 | y
2 | car pole | 1992-08-10 | 17000 | 1.17 | 18289 |  | n
3 | wire down | 1992-01-01 | 3795 | 3.73 | 7361 |  | n
4 | hardware | 1992-06-30 | 3795 | 1.58 | 5101 |  | n
5 | splice | 1992-12-21 | 2060 | 6.58 | 3907 |  | n
6 | trees | 1992-11-22 | 2500 | 3.25 | 3733 |  | n
7 | trees | 1992-12-30 | 750 | 4.75 | 2687 |  | n
8 | ext. syst | 1992-05-27 | 2656 | 0.9 | 2436 |  | n
9 | trees | 1992-03-06 | 1300 | 2.5 | 2167 |  | n
10 | lightning | 1992-09-18 | 1710 | 2.25 | 1616 |  | n
Significant Outage Events: SPPCo. 1991
RANK | Description | Date | Number of Customers Affected | Longest Customer Interruption-(hrs) | C-hrs | Number of People used to restore Service | CPUC Major Event?
1 | wind/snow | 1991-03-04 | 30360 | 19.88 | 162731 | 46 | y
2 | t. trimmers | 1991-07-12 | 2113 | 4.33 | 9156 |  | n
3 | car pole | 1991-07-18 | 1400 | 6.55 | 5050 |  | n
4 | car pole | 1991-08-04 | 2656 | 1.83 | 4868 |  | n
5 | trees | 1991-11-20 | 1940 | 1.07 | 1792 |  | n
6 | insulator | 1991-10-25 | 1940 | 0.8 | 1552 |  | n
7 | elbow | 1991-03-15 | 2049 | 0.57 | 1161 |  | n
8 | trees | 1991-10-25 | 1710 | 0.67 | 1141 |  | n
9 | trees | 1991-10-23 | 400 | 2.83 | 1133 |  | n
10 | pole fire | 1991-05-30 | 1100 | 1.85 | 1103 |  | n
Significant Outage Events: SPPCo. 1990
RANK | Description | Date | Number of Customers Affected | Longest Customer Interruption-(hrs) | C-hrs | Number of People used to restore Service | CPUC Major Event?
1 | mud slide | 1990-02-16 | 26133 | 3.33 | 48489 |  | y
2 | s. insul | 1990-07-15 | 15304 | 11.75 | 58475 |  | n
3 | operations | 1990-08-03 | 5298 | 4.08 | 5426 |  | n
4 | wire down | 1990-01-14 | 3360 | 2.53 | 5367 |  | n
5 | lightning | 1990-08-08 | 2656 | 1.93 | 4839 |  | n
6 | s insul | 1990-06-09 | 2656 | 1.78 | 4736 |  | n
7 | cable | 1990-06-07 | 2200 | 2.65 | 4649 |  | n
8 | t. trimmers | 1990-06-22 | 2100 | 12.17 | 3200 |  | n
9 | cable | 1990-01-07 | 496 | 9.58 | 2306 |  | n
10 | cable | 1990-03-01 | 410 | 16.97 | 1939 |  | n
Significant Outage Events: SPPCo. 1989
RANK | Description | Date | Number of Customers Affected | Longest Customer Interruption-(hrs) | C-hrs | Number of People used to restore Service | CPUC Major Event?
1 | trees | 1989-11-26 | 2211 | 3.28 | 7259 | n/a | n
2 | lightning | 1989-08-07 | 2370 | 8.42 | 4540 |  | n
3 | trees | 1989-11-26 | 2255 | 7.55 | 3435 |  | n
4 | insulator | 1989-02-03 | 2254 | 2.43 | 2897 |  | n
5 | insulator | 1989-03-02 | 1100 | 1.85 | 2035 |  | n
6 | lightning | 1989-08-08 | 2370 | 2.53 | 1991 |  | n
7 | trees | 1989-02-01 | 200 | 14.77 | 1773 |  | n
8 | car pole | 1989-05-02 | 5300 | 0.37 | 1765 |  | n
9 | car pole | 1989-05-12 | 2000 | 1.9 | 1464 |  | n
10 | arrestor | 1989-03-25 | 2000 | 0.67 | 1334 |  | n

## soe2
Significant Outage Events: SPPCo 2003
Outage Duration | Date of Outage | Description of Outage | Number of Customers Effected
0 to 1 hour
1 to 5 hours
5 to 10 hours
10 to 15 hours
15 to 20 hours
20 to 24 hours
1 to 2 days
2 to 3 days
3 to 4 days
4 to 5 days
5 to 6 days
6 to 7 days
> 7 days
* = Customers effected exceeds population due to momentaries
** = Customers effected exceeds population due to repetitive
same line outages
Outage Duration | Date of Outage | Description of Outage | Number of Customers Effected
0 to 1 hour | 12/14-12/20/2002 | Green/Trees/Storm | 102446*
1 to 5 hours | 12/14-12/20/2002 | Green/Trees/Storm | 54289**
5 to 10 hours | 12/14-12/20/2002 | Green/Trees/Storm | 37120
10 to 15 hours | 12/14-12/20/2002 | Green/Trees/Storm | 29563
15 to 20 hours | 12/14-12/20/2002 | Green/Trees/Storm | 16376
20 to 24 hours | 12/14-12/20/2002 | Green/Trees/Storm | 20054
1 to 2 days | 12/14-12/20/2002 | Green/Trees/Storm | 17154
2 to 3 days | 12/14-12/20/2002 | Green/Trees/Storm | 11056
3 to 4 days | 12/14-12/20/2002 | Green/Trees/Storm | 9979
4 to 5 days | 12/14-12/20/2002 | Green/Trees/Storm | 337
5 to 6 days
6 to 7 days
> 7 days
* = Customers effected exceeds population due to momentaries
** = Customers effected exceeds population due to repetitive
same line outages
Significant Outage Events: SPPCo 2002 (2 of 2)
Outage Duration | Date of Outage | Description of Outage | Number of Customers Effected
0 to 1 hour | 11/7-11/10/2003 | Green/Trees/Storm | 48011*
1 to 5 hours | 11/7-11/10/2003 | Green/Trees/Storm | 14144
5 to 10 hours | 11/7-11/10/2003 | Green/Trees/Storm | 3864
10 to 15 hours | 11/7-11/10/2003 | Green/Trees/Storm | 1482
15 to 20 hours | 11/7-11/10/2003 | Green/Trees/Storm | 717
20 to 24 hours | 11/7-11/10/2003 | Green/Trees/Storm | 624
1 to 2 days | 11/7-11/10/2003 | Green/Trees/Storm | 60
2 to 3 days
3 to 4 days
4 to 5 days
5 to 6 days
6 to 7 days
> 7 days
* = Customers effected exceeds population due to momentaries
Significant Outage Events: SPPCo 2001 (NONE)
Outage Duration | Date of Outage | Description of Outage | Number of Customers Effected
0 to 1 hour
1 to 5 hours
5 to 10 hours
10 to 15 hours
15 to 20 hours
20 to 24 hours
1 to 2 days
2 to 3 days
3 to 4 days
4 to 5 days
5 to 6 days
6 to 7 days
> 7 days
Significant Outage Events: SPPCo 2000 (NONE)
Outage Duration | Date of Outage | Description of Outage | Number of Customers Effected
0 to 1 hour | 2000-02-14 | Trees/Storm | 30343
1 to 5 hours | 2000-02-14 | Trees/Storm | 30343
5 to 10 hours | 2000-02-14 | Trees/Storm | 11930
10 to 15 hours | 2000-02-14 | Trees/Storm | 8818
15 to 20 hours | 2000-02-14 | Trees/Storm | 2111
20 to 24 hours | 2000-02-14 | Trees/Storm | 2111
1 to 2 days | 2000-02-14 | Trees/Storm | 2111
2 to 3 days | 2000-02-14 | Trees/Storm | 0
3 to 4 days
4 to 5 days
5 to 6 days
6 to 7 days
> 7 days
Significant Outage Events: SPPCo 1999 (NONE)
Outage Duration | Date of Outage | Description of Outage | Number of Customers Effected
0 to 1 hour |  | n / a
1 to 5 hours
5 to 10 hours
10 to 15 hours
15 to 20 hours
20 to 24 hours
1 to 2 days
2 to 3 days
3 to 4 days
4 to 5 days
5 to 6 days
6 to 7 days
> 7 days
Significant Outage Events: SPPCo 1998 (NONE)
Outage Duration | Date of Outage | Description of Outage | Number of Customers Effected
0 to 1 hour |  | n / a
1 to 5 hours
5 to 10 hours
10 to 15 hours
15 to 20 hours
20 to 24 hours
1 to 2 days
2 to 3 days
3 to 4 days
4 to 5 days
5 to 6 days
6 to 7 days
> 7 days
Significant Outage Events: SPPCo 1997
Outage Duration | Date of Outage | Description of Outage | Number of Customers Effected
0 to 1 hour | 1997-01-02 | wind/snow | 21042
1 to 5 hours |  |  | 21042
5 to 10 hours |  |  | 4038
10 to 15 hours |  |  | 3300
15 to 20 hours |  |  | 2000
20 to 24 hours |  |  | 1600
1 to 2 days |  |  | 0
2 to 3 days
3 to 4 days
4 to 5 days
5 to 6 days
6 to 7 days
> 7 days
Significant Outage Events: SPPCo 1997
Outage Duration | Date of Outage | Description of Outage | Number of Customers Effected
0 to 1 hour | 1997-01-22 | wind/snow | 17059
1 to 5 hours |  |  | 17059
5 to 10 hours |  |  | 3910
10 to 15 hours |  |  | 2500
15 to 20 hours |  |  | 758
20 to 24 hours |  |  | 0
1 to 2 days
2 to 3 days
3 to 4 days
4 to 5 days
5 to 6 days
6 to 7 days
> 7 days
Significant Outage Events: SPPCo 1996
Outage Duration | Date of Outage | Description of Outage | Number of Customers Effected
0 to 1 hour | 1996-06-23 | forest fire | 15626
1 to 5 hours |  |  | 15626
5 to 10 hours |  |  | 15626
10 to 15 hours |  |  | 14260
15 to 20 hours |  |  | 14000
20 to 24 hours |  |  | 8500
1 to 2 days |  |  | 0
2 to 3 days
3 to 4 days
4 to 5 days
5 to 6 days
6 to 7 days
> 7 days
Significant Outage Events: SPPCo 1996
Outage Duration | Date of Outage | Description of Outage | Number of Customers Effected
0 to 1 hour | 1996-01-27 | wind/snow | 11718
1 to 5 hours |  |  | 11718
5 to 10 hours |  |  | 8250
10 to 15 hours |  |  | 3300
15 to 20 hours |  |  | 850
20 to 24 hours |  |  | 0
1 to 2 days
2 to 3 days
3 to 4 days
4 to 5 days
5 to 6 days
6 to 7 days
> 7 days
Significant Outage Events: SPPCo 1995
Outage Duration | Date of Outage | Description of Outage | Number of Customers Effected
0 to 1 hour | 1995-12-12 | wind/snow | 31374
1 to 5 hours |  |  | 31374
5 to 10 hours |  |  | 23612
10 to 15 hours |  |  | 17300
15 to 20 hours |  |  | 7000
20 to 24 hours |  |  | 2500
1 to 2 days |  |  | 200
2 to 3 days |  |  | 0
3 to 4 days
4 to 5 days
5 to 6 days
6 to 7 days
> 7 days
Significant Outage Events: SPPCo 1994
Outage Duration | Date of Outage | Description of Outage | Number of Customers Effected
0 to 1 hour |  | n / a
1 to 5 hours
5 to 10 hours
10 to 15 hours
15 to 20 hours
20 to 24 hours
1 to 2 days
2 to 3 days
3 to 4 days
4 to 5 days
5 to 6 days
6 to 7 days
> 7 days
Significant Outage Events: SPPCo 1993
Outage Duration | Date of Outage | Description of Outage | Number of Customers Effected
0 to 1 hour | 1993-01-21 | wind/snow | 14587
1 to 5 hours |  |  | 14587
5 to 10 hours |  |  | 12000
10 to 15 hours |  |  | 7500
15 to 20 hours |  |  | 3100
20 to 24 hours |  |  | 850
1 to 2 days |  |  | 400
2 to 3 days |  |  | 0
3 to 4 days
4 to 5 days
5 to 6 days
6 to 7 days
> 7 days
Significant Outage Events: SPPCo 1992
Outage Duration | Date of Outage | Description of Outage | Number of Customers Effected
0 to 1 hour | 1992-12-28 | wind/snow | 16561
1 to 5 hours |  |  | 16561
5 to 10 hours |  |  | 12400
10 to 15 hours |  |  | 7500
15 to 20 hours |  |  | 4500
20 to 24 hours |  |  | 400
1 to 2 days |  |  | 0
2 to 3 days
3 to 4 days
4 to 5 days
5 to 6 days
6 to 7 days
> 7 days
Significant Outage Events: SPPCo 1991
Outage Duration | Date of Outage | Description of Outage | Number of Customers Effected
0 to 1 hour | 1991-03-04 | wind/snow | 30360
1 to 5 hours |  |  | 30360
5 to 10 hours |  |  | 20000
10 to 15 hours |  |  | 15000
15 to 20 hours |  |  | 7800
20 to 24 hours |  |  | 0
1 to 2 days
2 to 3 days
3 to 4 days
4 to 5 days
5 to 6 days
6 to 7 days
> 7 days
Significant Outage Events: SPPCo 1990
Outage Duration | Date of Outage | Description of Outage | Number of Customers Effected
0 to 1 hour | 1990-02-16 | mud slide- | 26133
1 to 5 hours |  | transmission | 0
5 to 10 hours |  | lines down
10 to 15 hours
15 to 20 hours
20 to 24 hours
1 to 2 days
2 to 3 days
3 to 4 days
4 to 5 days
5 to 6 days
6 to 7 days
> 7 days
Significant Outage Events: SPPCo 1989
Outage Duration | Date of Outage | Description of Outage | Number of Customers Effected
0 to 1 hour |  | n / a
1 to 5 hours
5 to 10 hours
10 to 15 hours
15 to 20 hours
20 to 24 hours
1 to 2 days
2 to 3 days
3 to 4 days
4 to 5 days
5 to 6 days
6 to 7 days
> 7 days

## ce
Customers Experiencing > 12 Sustained Outages in 2002
Division | Feeder Name | Number of Customers Experiencing > 12 Sustained Outages
SPPCO | n / a | ZERO
The format of our data base is not designed to readily obtain
this information.
The format of our data base is not designed to readily obtain
this information.
Customers Experiencing > 12 Sustained Outages in 2001
Division | Feeder Name | Number of Customers Experiencing > 12 Sustained Outages
SPPCO | n / a | ZERO
The format of our data base is not designed to readily obtain
this information.
Customers Experiencing > 12 Sustained Outages in 2000
Division | Feeder Name | Number of Customers Experiencing > 12 Sustained Outages
SPPCO | n / a | ZERO
The format of our data base is not designed to readily obtain
this information.
Customers Experiencing > 12 Sustained Outages in 1999
Division | Feeder Name | Number of Customers Experiencing > 12 Sustained Outages
SPPCO | n / a | ZERO
The format of our data base is not designed to readily obtain
this information.