Rule 21	Sheet 1 of 7

NON-EDISON OWNED GENERATING FACILITIES

INTERCONNECTION STANDARDS

A.	General

This rule sets forth requirements and conditions for interconnected non-Edison-owned generation where such generation may be connected for (1) parallel operation with Edison’s electric system, but only in those instances where such interconnection is not subject to regulation by the Federal Energy Regulatory Commission (FERC); or (2) isolated operation with standby or breakdown service provided by Edison.  For purposes of this rule, the interconnecting entity shall be designated the Producer.

B.	Conditions.

1.	Producers receiving Qualifying Facility ("QF") benefits must meet the criteria for a Qualifying Facility as defined under the Code of Federal Regulations, Title 18, Chapter 1, Section 292, subpart B of the FERC’s regulations.

2.	An agreement executed by Edison and the Producer shall be required for interconnected service.  Terms for the purchase of Producer’s electric power by Edison, if applicable, shall be included therein.

3.	Interconnection with Edison’s electric system under this rule may not be made for the transmission or distribution of the Producer’s electric power by Edison.

4.	Interconnection with Edison's electric system may not be made until and unless Edison has determined that the interconnection complies with the design and operating requirements set forth herein.

5.	Where interconnection protective equipment is owned, operated and maintained by the Producer, the Producer shall be responsible for damages to Edison or to others arising out of the misoperation or malfunction of the Producer-owned equipment.

6.	The Producer is solely responsible for providing adequate protection for the Producer's facilities interconnected with Edison's electric system.

(Continued)

Rule 21	Sheet 2 of 7

NON-UTILITY OWNED GENERATING FACILITIES

INTERCONNECTION STANDARDS

(Continued)

C.	Design and Operating Requirements.

1.	Each non-Edison-owned generation facility which is or can be connected to Edison's electric system shall be designed and operated so as to prevent or protect against the following adverse conditions on Edison's system.  These conditions can cause electric service degradation, equipment damage, or harm to persons:

a.	Inadvertent and unwanted re-energization of a Edison dead line or bus.

b.	Interconnection while out of synchronization.

c.	Overcurrent.

d.	Voltage imbalance.

e.	Ground faults.

f.	Generated alternating current frequency outside permitted safe limits.

g.	Voltage outside permitted limits.

h.	Poor power factor or reactive power (VARs) outside permitted limits.

i.	Abnormal waveforms.

2.	Criteria, operating rules, and explanatory information regarding the above requirements for small (below 100 kW), medium (100-1000 kW), and large (above 1000 kW) facilities are contained in Edison's Requirements for Operating, Metering, and Protective Relaying for Non-Edison Owned Generating Facilities ("Requirements").  Copies of the Requirements are available from Edison.

3.	All Producers shall test their protection equipment at the intervals specified within their Power Purchase Agreements ("PPAs") or Interconnection Agreements (“IAs”).  For those Producers not having a testing interval specified in their PPA or IA, the testing interval will then be determined by Section 2.2.7 of the Requirements.

(Continued)

Rule 21	Sheet 3 of 7

NON-EDISON OWNED GENERATING FACILITIES

INTERCONNECTION STANDARDS

(Continued)

C.	Design and Operating Requirements.  (Continued)

4.	For Edison electric system voltages 34.5 kV and below, the necessary protection equipment at the point of interconnection, including breaker(s), may be owned, operated, and maintained by the Producer or Edison pursuant to Section H of Edison's Rule 2.  For system voltages above 34.5kV, Edison shall own, operate, and maintain the protection equipment unless waived by Edison, at its sole discretion.  All protection equipment to be owned, operated, and maintained by Edison shall be constructed to Edison's specifications.  Protection equipment owned by the Producer shall be subject to Edison's review and approval.

5.	It shall be the responsibility of the Producer to provide sufficient Volt/VAR control.  Producers connected at Edison’s electric system voltages of 55 kV to 500 kV may be required to maintain a volt/VAR schedule.

6.	Producers connected at primary distribution voltages (2.4 kV to 34.5 kV) and subtransmission voltages (55 kV to 115 kV) shall operate their equipment in accordance with the Phase and Voltage Specifications in Edison's Rule 2, Description of Service.

7.	Producers are required to maintain the reactive power supply requirements of their particular generation technology (synchronous or induction generators, or inverter systems) as specified in Section 2.3 of the Requirements.

D.	Interconnection Facilities.

1.	Interconnection facilities include all required means, and apparatus installed, to interconnect the Producer's generation with Edison's electric system.  Where the Producer desires to sell power to Edison, interconnection facilities also include all required means, and apparatus installed, to enable Edison to receive power deliveries from the Producer.  Interconnection facilities may include, but are not limited to:

(Continued)

Rule 21	Sheet 4 of 7

NON-EDISON OWNED GENERATING FACILITIES

INTERCONNECTION STANDARDS

(Continued)

D.	Interconnection Facilities.

1.	Interconnection facilities … (Continued)

a.	Connection, transformation, switching, communications, control, protective and safety equipment; and

b.	Any necessary reinforcements and additions to Edison's electric system by Edison.

2.	Where interconnection facilities are to be installed for the Producer's use as added facilities, the Producer shall advance to Edison the installed cost of the added facilities.  At the Producer's option, and where such Producer's generation is a QF and the Producer has established creditworthiness to Edison's satisfaction, Edison shall finance those added facilities it deems to be removable and reusable equipment.  Such equipment shall include, but not be limited to, transformation, disconnection, and metering equipment.  Added facilities provided under either of the foregoing arrangements are subject to the monthly charge as set forth in Section H of Edison's Rule 2, Description of Service, on file with and authorized by the Commission.

3.	When a Producer wishes to reserve facilities paid for by the Producer, but idled by an energy sale conversion or otherwise, Edison shall impose a special facilities charge reimbursing Edison for costs related to its operation and maintenance of the facility.  When a Producer no longer needs facilities for which it has paid, the Producer shall, at a minimum, receive from Edison credit for the net salvage value of the facilities dedicated to Edison use.  If Edison is able to make use of these facilities to serve other customers, the Producer shall receive the fair market value of the facilities determined as of the date the Producer either decides no longer to use the facilities or fails to pay the required maintenance fee.

4.	The Producer shall be responsible for the costs of exploring the feasibility of a project or its interconnection with Edison electric system, including reasonable advance charges imposed by Edison for specific feasibility studies.

(Continued)

Rule 21	Sheet 5 of 7

NON-EDISON OWNED GENERATING FACILITIES

INTERCONNECTION STANDARDS

(Continued)

D.	Interconnection Facilities.  (Continued)

5.	A study conducted by Edison to determine the requirements and costs for interconnecting any Producer’s generating facility shall take no more than one year to complete, provided data to be supplied by Producer is readily available.

6.	The Producer shall be responsible for costs of telemetering, and safety checks except to the extent that, under Edison's effective tariffs, a comparable customer would not be similarly charged.

7.	Edison shall, upon request, give the Producer a binding estimate for line extension and interconnection costs; however, such estimates shall be in effect for a period not to exceed one year from the date provided.  A reasonable breakdown of cost estimates shall also be provided in a form sufficiently detailed and understandable by the Producer.

8.	Edison shall have the right to review and approve the design of the Producer's interconnection facilities (including protection equipment).

9.	Edison shall have the right to inspect the Producer's interconnection facilities prior to the commencement of parallel operations and require modifications as necessary.

10.	The site of interconnection facilities shall be accessible to Edison personnel.

E.	Allocation of Edison's Existing Line Capacity.

1.	For Producers who execute an agreement with Edison that provides for Edison to purchase the Producer’s power, existing capacity on Edison's electric system and a priority to such line capacity will be allocated in accordance with the terms of such agreement.

(Continued)

Rule 21	Sheet 6 of 7

NON-EDISON OWNED GENERATING FACILITIES

INTERCONNECTION STANDARDS

(Continued)

E.	Allocation of Edison's Existing Line Capacity.  (Continued)

2.	Where existing line capacity is allocated to a Producer, the Producer shall incur no obligation for costs associated with future line upgrades needed to accommodate other Producers or customers.  If two or more Producers establish priority rights simultaneously, the Producers shall share the costs of any additional line upgrade necessary to facilitate their cumulative capacity requirements.  Costs shall be shared based on the relative proportion of capacity each Producer will add to the line.

F.	Interconnection Reinforcement and/or Additions.

Edison's effective tariffs governing interconnection costs and added or special facilities agreements shall be applied to line and system reinforcement and/or additions.  In addition, the following shall apply:

1.	A Producer shall pay for new or additional line capacity if necessary for Edison to receive the Producer's power.

2.	The costs of any line reinforcement and/or addition undertaken at the option of Edison to serve additional future customers or Producers shall be borne by Edison.

3.	The applicable Edison tariff provisions shall be applied to a Producer who pays for interconnection reinforcement and/or additions that later accommodate a second Producer as those provisions which would be applied to a comparable Edison customer.

4.	The Producer shall be responsible for the costs of only those future system alterations which are necessary to maintain the California Public Utilities Commission's adopted interconnection standards for the Producer's particular interconnection facilities.  The relevant interconnection standards shall be those in effect at the time the contract is signed.  Should such alterations not be directly required by, or beneficial to the Producer, the Producer shall be treated like any other customer on Edison's system.

(Continued)

Rule 21	Sheet 7 of 7

NON-EDISON OWNED GENERATING FACILITIES

INTERCONNECTION STANDARDS

(Continued)

G.	Metering

1.	If the Producer desires to sell electric power to Edison, all necessary meters and associated equipment to be utilized for the measurement of energy and capacity for determining Edison's payment to the Producer shall be provided per Edison’s specification at the Producer’s expense.

2.	For purposes of monitoring generator operation and determination of standby charges, Edison shall have the right to install generation metering at the Producer's expense.  Where the Producer's generation is 10 MW or greater, telemetering equipment may also be required at the Producer's expense.

3.	The Producer shall provide, at no expense to Edison, a suitable location for all meters and associated equipment in accordance with Rule 16, Service Connections and Facilities on Customer's Premises.

4.	Where necessary, Edison and the Producer shall agree on an appropriate compensation method for transformer losses as specified in a PPA between the Producer and Edison.

5.	Edison shall install a ratchet device so as to prevent reverse operation on the meter(s) recording power provided by Edison, and where appropriate in each of the following cases, on (i) the meter(s) recording reactive demand imposed on Edison's electric system, and (ii) the meter(s) recording power purchased by Edison.

6.	Provision for meter tests and adjustments of bills or payments to the Producer for meter error shall be consistent with Rule 17, Adjustment of Bills and Meter Tests.