Rule No. 2	Sheet 1 of 16

DESCRIPTION OF SERVICE

A.	General

1.	The character of service available at any particular location should be ascertained by inquiry at Edison's office.

2.	The rate schedules included herein are applicable to both electric service and Company services provided beyond Edison's Point of Delivery.

3.	The rate schedules included herein are applicable for service where the customer purchases his entire electrical requirements from Edison, except where such schedules specifically provide otherwise, and are not applicable where a part of the customer's electrical requirements are supplied from some other source.

4.	The rate schedules included herein are only applicable for service provided from overhead distribution facilities (or where underground distribution facilities are provided for Edison's operating convenience or in accordance with the provisions of Rules Nos. 15, 16, and 20) except where schedules specifically provide otherwise.

5.	Alternating current service of approximately 60-cycle frequency will be supplied.

6.	Voltages referred to in the tariff schedules are nominal voltages.

B.	Phase and Voltage Specifications

1.	Standard nominal voltages of Edison are as follows:

a.	Distribution voltages:  120, 120/240, 240, 240/480, 277/480, 2,400, 4,160 volts; or, depending on location, 4,800, 12,000, 14,400/24,900, 16,500 or 33,000 volts.

b.	Voltages in excess of 33,000 volts are transmission voltages.  For its operating convenience, Edison may elect to supply a customer from lines of transmission voltage.  In such case, the customer may select as a standard delivery voltage one of the following:  2,400, 4,160, 6,900, 12,000, 13,800, 16,500 volts, or such other voltage as Edison may approve, provided that in no case shall a customer be required to advance to Edison a greater amount of money to obtain service than he would be required to advance under Edison's rules applicable to the particular load, if he were regularly served from Edison's nearest appropriate facilities ordinarily employed.

c.	Where Edison maintains four-wire wye-connected polyphase secondary mains:   (1) 120, 120/208, and 208 volts.

d.	Where Edison maintains four-wire delta-connected polyphase secondary mains:   120, 120/240, and 240 volts.

e.	In Santa Catalina Island:  120, 120/240, 277/480, and 2,400 volts.

(Continued)

Rule No. 2	Sheet 2 of 16

DESCRIPTION OF SERVICE

(Continued)

B.	Phase and Voltage Specifications (Continued)

2.	Customer Service Voltages

a.	Under all normal load conditions, distribution circuits will be operated so as to maintain secondary service voltage levels to customers within the voltage ranges specified below:

Maximum Service	Maximum

Nominal		Voltage On	Service Voltage

Two-Wire	Minimum	Residential	On Agricultural

and Multi-Wire	Voltage to	and Commercial	and Industrial

Service Voltage	All Services	Distribution Circuits	Distribution Circuits

120	114	120	126

208	197	208	218

240	228	240	252

277	263	277	291

480	456	480	504

b.	Exceptions to Voltage Limits.  Voltage may be outside the limits specified when the variations:

(1)	Arise from the temporary action of the elements.

(2)	Are infrequent momentary fluctuations of a short duration.

(3)	Arise from service interruptions.

(4)	Arise from temporary separation of parts of the system from the main system.

(5)	Are from causes beyond the control of Edison.

3.	Customer Utilization Voltages

a.	All customer-owned utilization equipment must be designed and rated in accordance with the following utilization voltages specified by the American National Standard C84.1 if customer equipment is to give fully satisfactory performance:

Nominal	Minimum	Maximum

Utilization	Utilization	Utilization

Voltage	Voltage	Voltage

120	110	125

208	191	216

240	220	250

277	254	289

480	440	500

(Continued)

Rule No. 2	Sheet 3 of 16

DESCRIPTION OF SERVICE

(Continued)

B.	Phase and Voltage Specifications (Continued)

3.	Customer Utilization Voltages  (Continued)

b.	The differences between service and utilization voltages are allowances for voltage drop in customer wiring.  The maximum allowance is 4 volts (120 volt base) for secondary service.

c.	Minimum utilization voltages from American National Standard C84.1 are shown for customer information only as Edison has no control over voltage drop in customer's wiring.

d.	The minimum utilization voltages shown in a. above, apply for circuits supplying lighting loads.  The minimum secondary utilization voltages specified by American National Standard C84.1 for circuits not supplying lighting loads are 90 percent of nominal voltages (108 volts on 120 volt base) for normal service.

e.	Motors used on 208 volt systems should be rated 200 volts or (for small single phase motors) 115 volts.  Motors rated 230 volts will not perform satisfactorily on these systems and should not be used.  Motors rated 220 volts are no longer standard, but many of them were installed on existing 208 volt systems on the assumption that the utilization voltage would not be less than 187 volts (90 percent of 208 volts).

4.	Single-phase Service

a.	General

Minimum Load	Maximum Load

Voltage      	      Required       	         Allowed

120 volts	None	1-15 amp and 1-20 amp

branch circuit

120/240 or 240 volts	None	400 amp main switch

240/480 volts	15 kVA	200 amp main switch

2,400 volts or over	Varies with location	40 amp main switch

b.	The maximum size 120 volt single-phase motor allowed is 1 hp and the maximum size 240 volt, or higher voltage, single-phase motor allowed is 10 hp.

(Continued)

Rule No. 2	Sheet 4 of 16

DESCRIPTION OF SERVICE

(Continued)

B.	Phase and Voltage Specifications (Continued)

4.	Single-phase Service  (Continued)

c.	Single-phase service may be supplied to installations having a proposed main service switch in excess of the switch capacities specified above provided the approval of Edison has been first obtained as to the number and size of switches, circuits, and related facilities.  120/240 volt installations will be supplied by one of the following methods as determined by Edison.

(1)	From two or three separate 120/240 volt service connections at one location.  Energy so supplied will be totalized for billing purposes.  The connected load on any service connection shall not be greater than twice that on any other service connection.

(2)	From one 120/240 volt connection where the proposed main service switch does not exceed 600 amperes capacity.

d.	Where Edison maintains four-wire wye-connected 120/208 volt secondary mains, single-phase service is supplied at 120/208 volts, three-wire, for which the maximum allowed is a 100-ampere main switch.  Loads in excess of a 100-ampere main switch will be supplied at 120/208 volts, four-wire.

5.	Three-phase Service.

a.	General.

Minimum	  Maximum	     Maximum

Connected	  Demand	   Main Switch

Voltage          	  Load Required   	  Allowed  	Capacity Allowed

240 volts	3 kVA	1,000 kVA	4,000 Amp

77/480 volts	25 kVA	3,000 kVA	4,000 Amp

2,400 volts or 4,160 volts	Varies w/location	12,000 kVA	3,000 Amp

12,000 volts or 16,500 volts	Varies w/location	30,000 kVA	Not Specified

b.	Single-Family Domestic Service.  In areas where Edison does not maintain three-phase secondary mains, only single-phase service will be supplied unless the applicant's load includes at least one motor rated in excess of 10 hp.

c.	Where three-phase service is supplied from a four-wire wye-connected 120/208 volt service, the maximum demand allowed is 1,000 kVA.

(Continued)

Rule No. 2	Sheet 5 of 16

DESCRIPTION OF SERVICE

(Continued)

B.	Phase and Voltage Specifications. (Continued)

5.	Three-phase Service.  (Continued)

d.	Service to all loads of 1,000 kVA maximum demand, or over, must be approved by Edison as to adequacy of facilities for service.

e.	Loads on three-phase service must be balanced between phases in accordance with good engineering practice.

f.	Three-phase service may be supplied to installations having a proposed main service switch in excess of the switch capacities specified above provided approval of Edison has first been obtained as to the number and size of switches, circuits and related facilities.  Such service will be supplied from two or three separate service connections at one location.  Energy so supplied will be totalized for billing purposes.  The loads will be balanced as closely as practicable between the services.

6.	Combined Single-phase Service and Three-phase Service.

a.	Service may be supplied at 120/208 volts four-wire wye-connected where Edison does not maintain four-wire secondary polyphase mains provided:  (1) written application is made for such service by the customer; (2) the customer's load is of such a size as to require an individual transformer installation of not less than 15 kVA of transformer capacity; and (3) the customer provides space acceptable to Edison on his premises to accommodate the installation of Edison's facilities when, in the opinion of Edison, such space is considered necessary.

b.	In underground areas where Edison maintains 120/208 volt or 240 volt three-phase mains, service may be supplied at 277/480 volts, four-wire provided:  (1)  written application is made for such service by the customer, and (2) the customer provides space acceptable to Edison on his premises to accommodate the installation of Edison's facilities when, in the opinion of Edison, such space is considered necessary.

(Continued)

Rule No. 2	Sheet 6 of 16

DESCRIPTION OF SERVICE

(Continued)

B.	Phase and Voltage Specifications. (Continued)

6.	Combined Single-phase Service and Three-phase Service.  (Continued)

c.	Service may be supplied at 120/240 volts four-wire delta-connected where Edison does not maintain four-wire secondary polyphase mains provided:  (1) written application is made for such service by the customer; (2) the customer's load is of such a size as to require an individual transformer installation of not less than 15 kVA of transformer capacity; (3) the unbalance between phases is less than 100 kW; and (4) the customer provides space acceptable to Edison on his premises to accommodate the installation of Edison's facilities when, in the opinion of Edison, such space is considered necessary.

d.	The maximum demand allowances for combined single-phase and three-phase are as set forth in B.5. above.

7.	At the option of Edison, the above voltage and phase specifications may be modified because of service conditions at the location involved.

C.	Motor Protection and Equipment.  Customer's motor equipment must conform with the following requirements:

1.	Motors that cannot be safely subjected to full rated voltage on starting or that drive machinery of such a nature that the machinery, itself, or the product it handles will not permit the motor to resume normal speed upon the restoration of normal supply voltage shall be equipped with devices that will disconnect them from the line upon failure of supply voltage and that will prevent the automatic reconnection of the motors upon restoration of normal supply voltage.

2.	All motors of 1 hp or larger shall be equipped with thermal relays, fuses, or other automatic overcurrent interrupting devices to disconnect completely such motors from the line as a protection against damage due to overheating.

3.	Three-phase motors driving elevators, hoists, tramways, cranes, conveyers, or other equipment, which would create hazard to life in the event of uncontrolled reversal of motor rotation, shall be provided with reverse-phase and open-phase protection to disconnect completely the motors from the line in the event of phase reversal or loss of one phase.

(Continued)

Rule No. 2	Sheet 7 of 16

DESCRIPTION OF SERVICE

(Continued)

C.	Motor Protection and Equipment.  (Continued)

4.	Wind machines thermostatically controlled with automatic reclosing switches must be equipped with suitable time-delay devices, as hereinafter specified, at the customer's expense, to permit the required adjustment of the time of reclosure after interruption of service.

A suitable time-delay device, within the meaning of this rule, is a relay or other type of equipment that can be preset to delay with various time intervals the reclosing of the automatic switches (and the consequent starting up of the electric motors on the wind machines) and to stagger the reconnection of the load on Edison's system, and such device must be constructed so as effectively to permit a variable overall time interval of not less than five minutes with adjustable time increments of not greater than ten seconds.  The particular setting to be utilized for each separate installation is to be determined by Edison from time to time in accordance with its operating requirements, and the customer is to obtain from Edison the setting for each installation as thus determined.

D.	Allowable Motor Starting Currents.

1.	The starting current drawn from Edison's lines shall be considered the nameplate locked rotor current or that guaranteed by the manufacturer.  At its option Edison may determine the starting current by test, using a stop ammeter with not more than 15% overswing or an oscillograph, disregarding the value shown for the first 10 cycles subsequent to energizing the motor.

If the starting current for a single motor exceeds the value stated in the following tables, reduced voltage starting or other suitable means must be employed, at the customer's expense, to limit the current to the value specified, except where specific exemptions are provided in Sections D.2., 3., and 4.

(Continued)

Rule No. 2	Sheet 8 of 16

DESCRIPTION OF SERVICE

(Continued)

D.	Allowable Motor Starting Currents. (Continued)

TABLE 1

Alternating Current - Single-phase Motors

Allowable Locked

Rotor Currents

Rated Size   	 120 Volts	    240 Volts

1  hp and less	50 amperes	 36 amperes

1 1/2 hp		 48 amperes

2  hp 		 60 amperes

3  hp 		 80 amperes

5  hp 		120 amperes

7 1/2 hp		170 amperes

10  hp 		220 amperes

TABLE 2

Alternating Current - Three-phase Motors

Allowable Locked

Rotor Currents

Rated Size	240 Volts	    480 Volts   	2,400 Volts

3  hp	 64 amperes	32 amperes

5  hp	 92 amperes	46 amperes

7 1/2 hp	127 amperes	63 amperes

10  hp	162 amperes	 81 amperes

15  hp	232 amperes	116 amperes

20  hp	290 amperes	145 amperes

25  hp	365 amperes	183 amperes

30  hp	435 amperes	218 amperes

40  hp	580 amperes	290 amperes

50  hp	725 amperes	363 amperes	70 amperes

60  hp		435 amperes	87 amperes

75  hp		535 amperes	107 amperes

100  hp		725 amperes	142 amperes

Over 100 hp - Edison should be consulted for allowable locked rotor currents.

2.	Where service conditions permit, subject to utility approval, reduced-voltage starters may be omitted in the original installation until such time as Edison may order the installation of a reduced-voltage starter to be made, and, similarly, Edison may at any time require starting current values lower than set forth herein where conditions at any point on its system require such reduction to avoid interference with service.

(Continued)

Rule No. 2	Sheet 9 of 16

DESCRIPTION OF SERVICE

(Continued)

D.	Allowable Motor Starting Currents. (Continued)

3.	Reduced-voltage starters may be omitted on any motor of a group installation provided that its starting current does not exceed the allowable starting current of the largest motor of the group.

4.	A reduced-voltage starter may be omitted on any motor in a group installation provided that its starting current does not exceed three times the maximum demand in amperes of the entire installation.

E.	Interference With Service.

1.	Customers who operate equipment which causes detrimental voltage fluctuations (such as, but not limited to, hoists, welders, radio transmitters, X-ray apparatus, elevator motors, compressors, and furnaces) must reasonably limit such fluctuations upon request by Edison.  The customer will be required to pay for whatever corrective measures are necessary.

2.	Prior to the installation of any new arc furnace or design modification of an existing furnace, the customer shall provide basic design information for the installation to aid Edison in determining a method of service and the allowable level of load fluctuations.

3.	Any customer who superimposes a current of any frequency upon any part of his electrical system, other than the current supplied by Edison, shall, at his expense, prevent the transmission of such current beyond his electrical system.

F.	Power Factor.  Edison may require the customer to provide, at his own expense, equipment to increase the operating power factor of each complete unit of neon, fluorescent, or other gaseous tube lighting equipment to not less than 90%, lagging or leading.

G.	Wave Form.  Edison may require that the wave form of current drawn by equipment of any kind be in conformity with good engineering practice.

H.	Added Facilities.

1.	Where an applicant requests and Edison agrees to install facilities which are in addition to, or in substitution for the standard facilities Edison would normally install, the costs thereof shall be borne by the applicant.  Such costs shall include continuing ownership costs as may be applicable.  Unless otherwise provided by Edison's filed tariff schedules, these added facilities (special facilities) will be installed, owned and maintained or allocated by Edison solely as an accommodation to the applicant.  Added Facilities are defined as:

(Continued)

Rule No. 2	Sheet 10 of 16

DESCRIPTION OF SERVICE

(Continued)

H.	Added Facilities.  (Continued)

1. (Continued)

a.	Facilities requested by an applicant which are in addition to or in substitution for standard facilities which Edison would normally provide for delivery of service at one point, through one meter, at one voltage class under its tariff schedules, or

b.	A pro rata portion of the facilities requested by an applicant, allocated for the sole use of such applicant, which would not normally be allocated for such sole use.

Added Facilities may include, but are not limited to, all types of equipment normally installed by Edison in the development of its electrical transmission and distribution systems and facilities or equipment related to Edison's provision of service to a customer or a customer's receipt or utilization of Company's electrical energy.  Added Facilities also include the differential costs for equipment for electrical transmission and distribution systems designed by Edison which, in Edison's sole opinion, is in excess of equipment required for Edison's standard serving system.  Added Facilities may include poles, lines, structures, fixtures, transformers, service connections, load control devices and meters.  However, the installation of meters capable of recording and providing hourly data that are in addition to or in substitution for standard meters shall be provided under the provisions of Rule 2.1, Section C, Hourly Metering Facilities.

2.	Added facilities will be installed under the terms and conditions of a contract in the form on file with the California Public Utilities Commission.  Such contract will include, but is not limited to, the following terms and conditions:

a.	Where new facilities are to be installed for applicant's use as added facilities, the applicant shall advance to Edison the additional installed cost of the added facilities over the cost of standard facilities.  At Edison's option, Edison may finance the new facilities.

b.	The following monthly ownership charges are applicable to Added Facilities Contracts with an effective date prior to 1/20/96:

(1)	Applicants being served by Company-financed added facilities shall pay a monthly charge of 1.31% of the cost associated with the added facilities.

(2)	Applicants being served by the Customer-financed added facilities shall pay a monthly charge of 0.43% of the cost associated with the added facilities.

(Continued)

Rule No. 2	Sheet 11 of 16

DESCRIPTION OF SERVICE

(Continued)

H.	Added Facilities.  (Continued)

(3)	Where existing facilities are allocated for applicant's use as added facilities, the applicant shall pay a monthly charge for the added facilities of 1.31% of Edison's Reconstruction Cost New Less Depreciation value of that portion of the existing facilities which are allocated to the customer as Added Facilities.

c.	The following monthly ownership charges include a replacement component into perpetuity and are applicable to Added Facilities Contracts with an effective date on or after 1/20/96:

(1)	Applicants being served by Company-financed added facilities shall pay a monthly charge of 1.38% of the cost associated with the added facilities.

(2)	Applicants being served by the Customer-financed added facilities shall pay a monthly charge of 0.43% of the cost associated with the added facilities.

(3)	Where existing facilities are allocated for applicant's use as added facilities, the applicant shall pay a monthly charge for the added facilities of 1.38% of Edison's Reconstruction Cost New Less Depreciation value of that portion of the existing facilities which are allocated to the customer as Added Facilities.

Where Edison agrees to provide replacement options, Applicant shall pay the following monthly ownership charges:

Company Financed	Customer Financed

Without	With	Without	With

Replacement	Replacement	Replacement	Replacement

Perpetuity		20 Yr. Term	Perpetuity 		20 Yr. Term

Monthly Rate	1.31%	1.32%	0.36%		0.37%

Under these options, where existing facilities are allocated for applicant's use as added facilities, the applicant shall pay a monthly ownership charge equal to the applicable Company-financed monthly rate.  Edison-financed monthly rate will be applied to Company's Reconstruction Cost New Less Depreciation value of that portion of the existing facilities which are allocated to the customer as Added Facilities.

(Continued)

Rule No. 2	Sheet 12 of 16

DESCRIPTION OF SERVICE

(Continued)

H.	Added Facilities.  (Continued)

d.	Where Edison determines the collection of continuing monthly ownership charges is not practicable, the applicant will be required to make an equivalent one-time payment in lieu of the monthly ownership charges.  The applicable payment options, if any, will be selected solely by Edison.

e.	All monthly ownership charges shall be reviewed and refiled with the Commission when changes occur in Edison's costs for providing such service.  However, Edison will not refile if Edison's cost change is less than 10 basis points.

3.	Edison shall not be liable for any loss, damage, or injury arising from Edison's installation, operation, maintenance, or control of the Added Facilities, unless such loss, damage, or injury results from Edison's sole negligence, and, in no event, shall Edison be liable for loss of profits, revenues, or other consequential damages.  No adjustment shall be made to reduce the billings if damage to, or malfunction of the Added Facilities results from any cause other than the negligence or willful act of Edison.

I.	Welder Service.

1.	Rating of Welders.  Electric welders will be rated for billing purposes as follows:

a.	Motor Generator Arc Welders.  The horsepower rating of the motor driving a motor generator type arc welder will be taken as the horsepower rating of the welder.

b.	Transformer Arc Welders.  Nameplate maximum kVA input (at rated output amperes) will be taken as the rating of transformer type arc welders.

c.	Resistance Welders.  Resistance welder ratings will be determined by multiplying the welder transformer nameplate rating (at 50% duty cycle) by the appropriate factor listed below:

(Continued)

Rule No. 2	Sheet 13 of 16

DESCRIPTION OF SERVICE

(Continued)

I.	Welder Service  (Continued)

1.Rating of Welders  (Continued)

Factor

Transformer Nameplate	Company-Owned	Customer-Owned

Type of Welder	Rating @ 50% Duty Cycle	Distrib. Transf.	Distrib. Transf.

Rocker Arm, Press

or Projection Spot	20 kVA or less	.60	.50

Rocker Arm or

Press Spot       	Over 20 kVA

Projection Spot 	21 to 75 kVA, incl.	.80 	.60

Flash or Butt    	100 kVA or over

Seam or Portable Gun	All sizes

Flash or Butt	67 to 100 kVA, incl.	*	*

Projection Spot	Over 75 kVA

Flash or Butt	66 kVA or less	1.20	.90

*	Each flash or butt welder in this group will be rated at 80 kVA where distribution transformer is owned by Edison or 60 kVA where distribution transformer is owned by the customer.

d.	Ratings prescribed by a., b., and c., above, normally will be determined from nameplate data or from data supplied by the manufacturer.  If such data are not available or are believed by either Edison or customer to be unreliable, the rating will be determined by test.

e.	If established by seals approved by Edison, the welder rating may be limited by the sealing of taps which provide capacity greater than the selected tap and/or by the interlocking lockout of one or more welders with other welders.

f.	When conversion of units is required for tariff application, 1 welder kVA will be taken as 1 horsepower for tariffs stated on a horsepower basis and 1 welder kVA will be taken as 1 kilowatt for tariffs stated on a kilowatt basis.

(Continued)

Rule No. 2	Sheet 14 of 16

DESCRIPTION OF SERVICE

(Continued)

I.	Welder Service.  (Continued)

2.	Billing of Welders.  Welders will be billed at the regular rates and conditions of the tariffs on which they are served subject to the following provisions:

a.	Connected Load Type of Schedule.  Welder load will be included as part of the connected load with ratings as determined under Section 1., above, based on maximum load that can be connected at any one time, and no allowance will be made for diversity between welders.

b.	Demand Metered Type of Schedule.  Where resistance welders are served on these schedules the computation of diversified resistance welder load shall be made as follows:

Multiply the individual resistance welder ratings, as prescribed in Sections 1.c. to 1.f. inclusive, above, by the following factors and add the results thus obtained:

1.0 times the rating of the largest welder

0.8 times the rating of the next largest welder

0.6 times the rating of the next largest welder

0.4 times the rating of the next largest welder

0.2 times the ratings of all additional welders

If this computed diversified resistance welder load is greater than the metered demand, the diversified resistance welder load will be used in lieu of the metered demand for rate computation purposes.

J.	Hourly Metering Facilities

1.	This rule is applicable to the installation of hourly metering and associated devices when the hourly metering is not added as part of other transmission and distribution facilities.  When added as part of other transmission and distribution facilities installed as Added Facilities, the costs of hourly metering are covered under Rule 2, Section H.

2.	Hourly Metering may include, but is not limited to, the components as defined in Rule 1 under Metering Facilities.

3.	Where a customer elects, and Edison agrees, Edison will install, own, and/or maintain  hourly metering which is in addition to, or in substitution for, standard metering for the customer’s use.  The costs of such metering shall be borne by the customer.

(Continued)

Rule No. 2	Sheet 15 of 16

DESCRIPTION OF SERVICE

(Continued)

J.	Hourly Metering Facilities (Continued)

4.	The costs of hourly metering will be as set forth in the Direct Access and Bundled Services (DABS) Catalogue.

5.	Hourly Metering Charges

a.	Hourly metering will be installed, owned, and maintained under the terms and conditions of a contract on file with the Commission.  Where a customer requests, Edison may agree to own and finance the Metering Facilities.  Maintenance will be a required element of the contract.

b.	Customer Ownership:  The costs of purchasing and installing the Metering Facilities will be as set forth in the DABS Catalogue.  Edison may require the customer to replace the substitute Metering Facilities with other Metering Facilities if necessary to conform to subsequent metering standards or system requirements.

c.	Edison Ownership:  Where Edison financing is offered, the customer shall pay for the costs associated with installing and purchasing hourly metering through a monthly capital-related charge based on a monthly percentage times the cost of the hourly metering as set forth in the DABS Catalogue.  The rate shall be 1.93% per month.  The following provisions will apply:

(1)	The customer will be obligated to pay the monthly capital-related charge for the useful life of the Metering Facilities, but not less than ten years.  Should the customer request removal of the substitute Metering Facilities prior to completing ten years of payments, the customer will remain responsible for the remainder of payments over the ten years less any salvage value of the substitute meter, but not less than zero.

(Continued)

Rule 2	Sheet 16 of 16

DESCRIPTION OF SERVICE

(Continued)

J.	Hourly Metering Facilities (Continued)

5.	Hourly Metering Charges (Continued)

c.	Edison Ownership:  (Continued)

(2)	Edison may remove substitute Metering Facilities and replace them with standard Metering Facilities or may require the customer to replace the substitute Metering Facilities, at Edison's convenience.  In the event Edison requires removal of Edison-owned substitute Metering Facilities, the customer shall not be obligated to pay any further monthly capital-related charges associated with the removed facilities, even if removal occurs during the first ten years.

d.	Maintenance Charge:  For Edison-owned Metering Facilities, the customer shall pay for maintenance costs as set forth in the DABS Catalogue.  This charge shall include repair and replacement of the substitute Metering Facilities, as necessary to provide for continued operation.  The customer shall remain liable for repair or replacement due to damage from misuse, or hazards such as fire, theft, or vandalism.  The customer shall pay the maintenance charge for the hourly metering during the useful life of the Metering Facilities, as long as the customer contract is in effect.

e.	Edison will update the installation, purchasing and maintenance costs, and the monthly capital-related charges when changes occur in Edison's costs for providing such services and will file these updates with the Commission.