Appendix B

DIRECT ACCESS METER SITE INSTALLATION

INSPECTION AND TESTING REQUIREMENTS

- DA Site Inspection and Audit:  This work includes only Task #1 (Visual Inspection) in Exhibit B

- DA Site Testing: This work includes all Tasks in Exhibit B.  Tasks #2 through #8 shall be done as appropriate.

Matrix of Site Inspection & Testing Requirements

|  |  | TASK |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| C O D E | Type of Meters/Registers | 1 Visual Inspec-tion | 2 Voltage Test | 3 Light& Full Load Test | 4 Demand Test | 5 Register Verifi-cation | 6 Phase Angle Test | 7 Separate Element Test | 8 Burden Test |  | Possible Other Types Í | COMMENTS | C O D E |
| (a) | Self-Contained kWH Meters | X | X | X |  |  |  | X |  |  | (g), (j) | Mechanical Meter | (a) |
| (b) | Transformer-Rated kWH Meters | X | X | X |  |  |  | X | X |  | (g), (j) | Mechanical Meter | (b) |
| (c) | Hybrid/Electro-Mechanical Meters | X | X | X | X | X |  | X |  |  | (i), (j) |  | (c) |
| (d) | Solid State Meters | X | X | X | X | X |  |  |  |  | (g), (i), (j) |  | (d) |
| (e) | Transformer-Rated kVARH Meters | X | X | X |  |  | X | X | X |  | (j) | Mechanical Meter | (e) |
| (f) | Multi-Quadrant Meters | X | X | X |  | X |  | X | X |  | (g), (j) |  | (f) |
| (g) | Solid State Recorders | X | X |  | X |  |  |  |  |  |  |  | (g) |
| (h) | Mechanical Registers | X |  |  |  |  |  |  |  |  | (g), (j) |  | (h) |
| (i) | Electronic Registers | X |  |  |  |  |  |  |  |  | (g), (j) |  | (i) |
| (j) | Pulse Devices | X |  |  | X |  |  |  |  |  |  |  | (j) |
| (k) | Self-Contained Network Meters | X | X |  |  |  |  |  |  |  | (g), (j) |  | (k) |

  Performed if demand is present.

  Energy Consumption Investigation (ECI) is necessary.

  Performed when deemed necessary

Í The alphabetical codes in the “Possible Other Types” column refer to the “Code” column on this matrix and indicate that additional tests must be performed as required if the other types exist at the sites.

Task #1: Visual Inspection and Communication Verification

All Meter Sites Visually inspect all meter sites for the following conditions:

- Electrical Hazards:

- Exposed wiring.

- Damaged sockets: Loose or burnt wiring or jaws.

- Auto-bypass devices: Load jaws still hot when meter is removed.

- Loose or missing screws in meterman's working area (i.e., bypass area).

- Missing panels.

- High voltage arrestor: Remove or cut in clear if present.

2.	Physical Hazards:

- Tripping hazards.

- Slippery or uneven surfaces.

- Debris or materials stored in the working space.

- Overhead hazards: Stored materials or workers above meter locations.

- Environmental hazards: Chemical, caustic, hearing, biological, etc.

3.	Energy Diversion:

- Suspicious wiring.

- Broken or missing seals.

- Excessive wear on meter blades and socket jaws.

- Unmetered taps on line side of metering: Fire alarms or security systems.

- Jumpers across bypass links.

- Unsealed pull section: Check for unmetered connections.

4.	Clock Load:

- Calculate customer's load at time of arrival and record on test tag.

5.	DA Metering Verification:

- Check for proof of DA meter certification or meter types that have been certified and approved.

- Verify for correct billing information (records versus meters) including billing constant, meter number, accuracy test results, customer information, etc.

- Verify for correct meter and service (voltage, form, etc.).

6.	DA Communication Verification:

- Verify for correct phone or other communication devices and connections if remote read

- Verify for successful communication handshakes and data retrieval if remote read (This can be done by another person at a remote location, and data accuracy is not verified at this time).

- Verify for successful meter reading if manual read.

Task #1: Visual Inspection (Cont.)

Transformer Rated Meter Sites

In addition to the inspections described in the All Meter Sites Section above, visually inspect all Transformer Rated Meter sites for the following conditions:

1.	Billing Constant:

- Verify for correct billing constant (records versus sites: CT’s and PT’s ratios).

2.	Proper Wiring:

- Current by-pass links not shorted.

- Current secondary wired in reverse.

- Voltage and current circuits not matched.

- Secondary wires pinched or rubbing near panel hinges.

3.	Energy Diversion:

- Test switch cover secure and sealed.

- Unmetered taps on bus at line side of metering transformers (i.e., taps for fire alarms or ground fault interrupter circuits).

- Jumpers across current leads at bottom of test switch unsealed.

- Unmetered connections in pull sections.

Pole Mounted Meter Sites

In addition to the inspections described in the All Meter Sites Section above, visually inspect pole-mounted meter sites for the following conditions:

- Cutouts

- Open Cutouts

- Blown Triple Link Fuses: This condition should be corrected before performing any work at the site.

2.	Ground

- Proper ground: Ensure that the ground conductor and connections are not broken at any point between the meter enclosure and the ground rod.

3.	Customer premises

- Customer Owned Stairs, Railings, Platforms etc.: Observe them to ensure a safe workplace and refer unsafe conditions to the appropriate department in your division for replacement or repair.

4.	Insects

- Doors and Panels: Carefully inspect for insects when opening doors or removing panels because stinging surprises may cause you to throw a cover or body part into an energized bus.

Task #2: Voltage Test

On all services, measure the voltage, with an approved volt meter,  between the line phases and line to ground even if it is an ungrounded service and record all voltage readings on the test tag.  All nominal voltages have an allowable tolerance of ±5%.

Secondary Distribution Voltages: 	Normal rating of 115 Vac.

Table 1: Nominal Voltages and allowable limits on Secondary

| Nominal Voltage (Volt) | Maximum (Volt) | Minimum (Volt) |
| --- | --- | --- |
| 120 | 126 | 114 |
| 208 | 218 | 198 |
| 240 | 252 | 228 |
| 277 | 291 | 263 |
| 480 | 504 | 456 |

Table 2: Service Voltages and allowable limits on Secondary

| Service Voltage (Volt) | Measured Voltage (Volt) | Maximum (Volt) | Minimum (Volt) |
| --- | --- | --- | --- |
| 120/240V 3w 1ø | 120V Phase to Ground 240V Phase to Phase | 126 252 | 114 228 |
| 120/208V 3w 1ø | 120V Phase to Ground 208V Phase to Phase | 126 218 | 114 198 |
| 120/208V 4w 3ø | 120V Phase to Ground 208V Phase to Phase | 126 218 | 114 198 |
| 120/240V 4w 3ø | 120V Phase to Ground 208V Phase to Ground 240V Phase to Phase | 126 218 252 | 114 198 228 |
| 277/480V 4w 3ø | 277V Phase to Ground 480V Phase to Phase | 291 504 | 263 456 |
| 240V 3w 3ø | 240V Phase to Phase | 252 | 228 |
| 480V 3w 3ø | 480V Phase to Phase | 504 | 456 |

Primary Distribution and Transmission Voltages: These voltages have secondary voltage rating of 115 Vac or 120 Vac.   The voltage transformer primary may be connected either wye or delta.

Table 3: Primary and Transmission Voltages with their secondary voltages and ratios

| Possible System L-L Voltage (Volt) | VT Primary Voltage (Volt) | Secondary Rating (Volt) | Ratio |
| --- | --- | --- | --- |
| 2,400 or 4,200 | 2,400 | 120 | 20:1 |
| 4,200 or 7,200 | 4,200 | 120 | 35:1 |
| 7,200 or 12,000 | 7,200 | 120 | 60:1 |
| 12,000 or 20,125 | 12,000 | 120 | 100:1 |
| 17,200 | 18,000 | 120 | 150:1 |
| 20,125 or 34,500 | 20,125 | 115/67.08 | 175/300:1 |
| 60,000 | 34,500 | 115/69 | 300/500:1 |
| 69,000 | 40,250 | 115/67.08 | 350/600:1 |
| 115,000 | 69,000 | 115/69 | 600/1,000:1 |
| 230,000 | 138,000 | 115/69 | 1,200/2,000:1 |
| 500,000 | 287,500 | 115/69 | 2,500/4,200:1 |

Task #3: Light Load  &  Full Load Test

Perform the light load and full load test to check for the accuracy of the meter under test by comparing its test results with a Standard Meter of known traceable accuracy.  The following tests and corrective actions need to be performed for this test:

- No Load or Creep Test (for mechanical and hybrid meters only):

Test meters will be energized with no connected load, and the disk observed for rotation.  A minimum amount of creep is acceptable if the rotation stops when an anti-creep hole reaches the meter stator.

- Accuracy test:

Single phase and polyphase meters are to be tested with potential coils connected in parallel and the current coils connected in series.  Tests will be done at light load (normally 10% of name plate or test Amp rating) and at full load (normally 100% of name plate or test Amp rating).  Both are performed at 100% power factor, and their results are compared with the Standard and reported on the electric measurement test form.  The minimum duration of the test will be 1 disk revolution for light load and 10 disk revolutions for full load.

Note:	For solid state meters, calculated pseudo revolutions will be used.  Changing the Kh constants on these solid state meters will vary the speed of the pseudo disk or the disk simulator.  Because the KWH is calculated directly from the measured voltage and current in the meter, there is no real Kh in these solid state meters as well as no real disk.  Because the mechanical meters have been used in the industry for many years and people are very much familiar with disk revolutions and Kh values, these terms are still applied for solid state meters to avoid confusions and they are simply the byproducts of the calculated KWH in the meters.  This also means that changing the Kh values inside the solid state meters will not affect the calculated KWH or meter accuracy.

- Adjustments:

Meters found within the limits of ±1% need not be adjusted.

- Correction Factor Calculation:

Correction factors for light load and full load will be determined by dividing the observed value displayed on the test standard by the expected test constant.  The correction factor of the test meter is different from the correction factor of the site.  The correction factor of the site is to be recorded in proper keypunch boxes on the test form.

Task #4: Demand Test

Mechanical Demand Meters

Test for the accuracy of the demand registers by checking the marked register ratio and time interval as follows:

- Advancing Mechanism:

Visually inspect the pusher arm and gears for worn out parts.  The pusher arm and gears should be clean.

- Clutch:

Check that the pusher arm returns to zero at the end of interval when the clutch releases it.  Verify that this is a smooth operation and the pusher arm it returns to the stop position.

- Timing Motor:

Check that the timing motor is operating.  If the motor is not operating the demand reading will most likely be off scale.

- Time Interval:

Test the time interval to insure that it is as marked on the register name plate.  This may be done by timing the motor gear and clocking an interval, or performing a demand test.

- Demand Mechanism:

Check that the demand reset returns the pointer to zero on a reset action and that the pointer will advance to full scale.

- Reporting:

Record the demand test results on the electric measurement test form.

Task #4: Demand Test (Cont.)

Solid State Meters and Electronic Registers

Test for the accuracy of the demand registers by measuring and comparing the demand of the test meter with the standard.  Because solid state meters and electronic registers are designed differently, they required slightly different procedures when performing a demand test.  Below is a typical procedure for a demand test on a solid state meter or an electronic register.

| Step | Action |
| --- | --- |
| 1 | Place the meter register in the TEST MODE . |
| 2 | Press reset button to clear all test registers and start new demand interval. |
| 3 | Apply full load current for 25 disk revolutions as a minimum. |
| 4 or... | Scroll the register display to show present KW demand or display KW (i.e., 000.72) |
| 4 | Scroll the register display to show pulses (i.e., 00300) and calculate the display KW as follows: · · |
| - 5 | Use of Revolutions IB-10 or SC-10 Test Standards to calculate the standard KW · · |
| or ... 5 | Use of Watt-hours-Radian Test Standard to calculate the standard KW · · |
| 6 | Return the meter to the NORMAL MODE. Calculate the correction factor by dividing the standard KW by the display KW and record the results on the electric measurement test form. |

Task #5: Register Verification

Mechanical Register

Visually inspect and verify that the register is correct for the watt-hour meter, and  that the register constant, gear ratio, and register ratio are correct for the register.

- Gear mechanism:

Check that the gears are clean, and check the proper engagement between gears and between the first gear and the disk shaft.  Some meters have intermediate gears which are part of the over all gear ratio.

- Mechanical register test:

Check that the register ratio is the same as marked.  The register ratio (Rr) is determined by counting the number of revolutions required of the first gear to cause the first dial pointer to make one complete revolution.  Check the watt-hour constant Kh by running a 1 kW load test on the meter.

Electronic register

Because electronic registers are different for each type and manufacturer, manufacturer’s manual should be referred to for specific procedures for these registers.  Some registers can be self-tested once a day for demand rate schedules, at midnight for TOU rate schedules, upon power-up, or upon optical communication.  Below are a typical procedure for verifying electronic registers after they are programmed with a proper parameters:

- Check all numerical segments and display identifiers are displayed on the LCD.

- Check the meter is scrolling properly through all registers.  This indicates that the meter and its internal components are functional.

- Check the function of the registers by disconnecting and then restoring power on the meter.  If the meter resumes normal display operations and reading after this power outage, this verifies normal operation of the registers.

- Verify the programming parameters are correct.

- Check the register memory and load profile data memory to verify that data is being stored.

Task #6: Phase Angle Test

Check for correct wiring on a reactive metering site and proper phase shift on each phase circuit.  If the rotation is not correct, the site will have a leading Power Factor.  When the rotation is correct, the site will have a lagging Power Factor.

- Reactiformer voltage:

Measure the voltage on the top of the reactiformer to insure the proper voltage is applied to the potential coil in the RKVAH meter.  If the voltage is not correct, the following are possibilities of errors:

1) Factory incorrect wiring on the reactiformer

2) Incorrect voltage for the applied service

3) Incorrect wiring at the site during installation

- Power Factor Calculation:

Calculate the load on the KWH and the RKVAH meters and the power factor for the site.  This power factor is used as a cross check for the measured phase angle.

- Current Measurement:

Measure each phase current and record it accordingly.

- Phase Angle Measurement:

Use phase angle meter to measure each phase angle and record it accordingly.

- Phase Angle Plot:

After measuring all voltages, currents and phase angles, plot a phase angle test and cross check with the calculated power factor.

Task #7: Separate Element Test

Check individual elements of transformer rated and self contained meters for proper disk rotation or registration by performing the following:

- Testing

Energize with the appropriate phase potentials and place current on individual elements, and check for forward rotation or positive registration

- Correct phasing

Check that the proper potential coil and current coil are wired correctly in the meter.  If the meter is installed correctly on the socket, the meter disk will rotate forward.

- No forward rotation

If an element has no rotation check the following:

- Open potential coil - Check for an open potential coil with a magnet or an ohmmeter.

- No load current - Clamp an Amp meter on all phase conductors to ensure no customer load.

- Note

u	Phase angle relationships may cause slight reverse rotation in cases where there is a poor power factor.  If any substantial reverse rotation is observed, the service should be checked for unmetered loads.  This will only occur on three wire three phase metered service sites.

u	Some solid state meters may appear to have a cross phase condition.  This is the nature of the electronic circuit design and power measurement in these meters.

Task #8: Burden Test

Check the operating conditions of current transformers in the field by performing the following conditions:

- Method

Put built-in burdens of a multi-range Amp meter in series with the secondary of the test current transformers (CT) to obtain the Amp readings. These amp readings should have the same deflection for any given balanced load because most three phase sites have the same brand, size, and type of current transformers.  Imposing additional secondary burden on a good CT does not cause any change in the secondary current amp reading.

- Possible Problems

If one CT has a reading significantly different from the others, it probably has shorted turns or other problem stated below:

u	Short circuited primary turns.

u	Short circuited secondary turns.

u	High resistance connections in the secondary circuit.

u	Short circuited secondary wiring.

u	Grounding of normally ungrounded wire.