PROPOSAL

FOR

METERING AND DATA COMMUNICATIONS STANDARDS

In the

DIRECT ACCESS IMPLEMENTATION WORKSHOP

Electric Services Industry Restructuring

California Public Utilities Commission

Submitted by

THE OFFICE OF RATEPAYER ADVOCATES

(ORA)

June 27, 1997

Metering And Data Communications Standards

I.	EXECUTIVE SUMMARY

## Purpose of the Metering and Data Communications Standards (M&DCS) workshop and relationship to the Retail Settlements and Information Flow (RSIF) workshop

Metering and Data Communications Standards (M&DCS) are needed to reconcile the need for continuity of retail settlement and information flow, formerly guaranteed by a vertically integrated utility monopoly, with the interconnectivity required for a competitive marketplace for retail energy services.

Whereas the RSIF workshop attempts to define the information needs (which influences data acquisition in M&DCS) of the stakeholders in a restructured electric services industry, this M&DCS workshop attempts to define the standards appropriate to open-architecture metering and data communications systems to collect and distribute retail information to stakeholders.  This includes specifying the data formats, the communication protocols, and the data editing, validating, and posting rules that will meaningfully advance the ultimate goal of component (meters, meter-reading systems, and meter data management) interconnectivity.

## Key findings resulting from the M&DCS workshop process

### Legacy Systems Are Inadequate

Existing legacy systems are inadequate, in a restructured electric services industry, to meet the minimum data requirements for retail settlement and information flows necessary for Direct Access and Customer Choice.

### Customer Choice Requires Interoperability

Meaningful Customer Choice requires interoperable systems for the metering, meter-reading, meter data management, and other revenue cycle services; and that interoperability can only be accomplished by means of an Open Architecture developed and maintained under a regime of national standards.

### National Standards Required for a National Market

Direct Access and Customer Choice will take place in a national market for energy services and products that can only be effectively accomplished under a regime of national standards.

### Interoperability Not Available by January 1, 1998

Open Architecture based interoperable metering and data communication systems cannot be fully accomplished by January 1, 1998, largely due to the short-term unavailability of interoperable equipment and systems, due in turn to the lack of comprehensive national standards to guide such interoperability.

### Interoperability Is Feasible

Open Architecture based interoperable metering and data communication systems are feasible, in the foreseeable future, due to the recent and imminent development of appropriate and applicable national standards.

### National Standards Should be Enforced After Reasonable Notice

National standards should be enforced upon 90 days after publication and at least one year after having been voted out of the cognizant coordinating committee.

### Practical Methodologies Are Needed For Transition

Practical methodologies are needed for supporting the continuity of retail settlement and information flow, beginning January 1, 1998, or as soon as possible thereafter, and continuing only as a transitional accommodation until supplanted by various national standards.

## Significant areas of agreement and disagreement among the UDC’s and among/between the other participants.

ORA has participated in discussions with other parties to the M&DCS and RS&IF workshops, notably the American Meter Reading Association (AMRA), Consumer Choice in Electric Services (CCES), the Electric Power Research Institute (EPRI), and the Meter And Data Management Working Group (MADAWG).  Much common ground has resulted from those discussions, avoiding the need for ORA to duplicate filings by these groups.  ORA may or may not agree with all points ultimately made in presentations by these parties, but any refinements in position can be made at the workshop, after their proposals are in final form.

ORA prepared sections III.E and III.F, and portions of section III.I, of the CCES proposal, and is prepared to present this proposal at the workshop concerning adjustments for line losses, load profiles, and the use of WENet.

ORA discussed its positions relative to Open Architecture interoperability with AMRA and EPRI extensively, and believes that its proposal is fully and completely consistent with the proposals of those organizations.

## Organization of the remainder of the report

# BACKGROUND

## Metering and Data Communications Standards (M&DCS) are needed to reconcile the need for continuity of retail settlement and information flow, formerly guaranteed by a vertically integrated utility monopoly, with the interconnectivity required for a competitive marketplace for retail energy services.

## Relevant legislative and regulatory decisions to date: CPUC, FERC, AB 1890, etc.

## Summary of the new market structure

### Changes in market participants

### Roles and responsibilities (regardless of whether participants contract out actual work to others)

Customer Choice implies customer responsibility.  ESPs, UDCs, and other qualified parties may operate as agents for customers, to accomplish the provision, installation, or operation and maintenance of meters, meter reading, and meter data management.  But, the end-use customer must retain ultimate responsibility for the accomplishment of these functions and ultimate choice of the agents or vendors by which to accomplish them.

ESPs and UDCs may provide customers any functional service for which they are certified and otherwise qualified to perform and for which the customer is willing to engage them.

UDCs may be required, at least throughout the transition period, to perform any one or more of the metering and data communication functions upon election of any of their distribution customers, at the regulated cost of service.

### UDC as default provider and distribution system responsibility

## The workshop process, including pre-workshop activities

## Summary of the critical information needs of the market participants (from the RSIF workshop)

### ISO requirements

Different ISO requirements apply to customers connected to the ISO Controlled Grid than to other end-use customers.  Pursuant to sections 10.1 to 10.5 of the ISO Tariff (which are more detailed than this summary), data from meters for entities connected to the ISO Controlled Grid are made available to the ISO revenue metering data acquisition and processing system.  Meters for these customers must comply with standards and accuracy requirements set forth in Appendix J of the ISO Tariff, which states that “all metering shall be of a revenue class metering accuracy in accordance with the ANSI C12 standards on metering and any other requirements of the relevant UDC or local regulatory authority that may apply.”  (Appendix J also illustrates this requirement for 1/1/98 by listing the ANSI C12 standards that existed at the time of the ISO Tariff’s drafting.)  The ISO's revenue metering data acquisition and processing system will collect and process meter data for operational purposes, and settlement quality meter data for metered entities who are also end-users will be provided in accordance Section 10.6 of the ISO Tariff.  Access by third parties to meter data held by the ISO will be coordinated through the Scheduling Coordinators representing the customer, not directly from the ISO.  A meter service agreement for each metered entity will set out security, validation, and audit procedures, which will include data correction and substitution algorithms to estimate, substitute and flag inaccurate or missing data before the data is sent to the ISO’s settlement system.

Section 10.6 of the ISO Tariff applies to Scheduling Coordinators representing end-users located within the boundaries of the ISO controlled grid or an interconnected UDC distribution system.  Scheduling Coordinators will provide the ISO with end-use meter data for all of the end-users served by the Scheduling Coordinator no later than the day required by the ISO’s settlements process (within 38 days of the energy usage).  End-use meter data will be either (1) an accurate measure of the end-user’s actual consumption in each settlement period, or (2) for end-users connected to a UDC Distribution System, a profile of that consumption derived from an accurate cumulative measure of actual consumption and an allocation of that consumption using the applicable, authorized load profile.  For end-users connected to a UDC's distribution system, Scheduling Coordinators will adjust the meter data by an estimated distribution system loss factor.  Such estimated distribution loss factors are to be approved by the relevant Local Regulatory Authority (e.g., the CPUC) prior to their use.  Scheduling Coordinators will aggregate equivalent ISO grid-level end-user meter data by congestion zone and scheduling point.  Each scheduling coordinator, in conjunction with the relevant Local Regulatory Authority, will ensure that each customer’s meter complies with the metering standards set forth in Appendix J of the ISO Tariff (i.e., compliance with ANSI C12 standards and any other regulatory standards).  Hourly meter data will carry a flag indicating whether the data represents an hourly time-stamped value or profiled value and, in the case of profiled values, a reference to the approved load profile used to allocate the cumulative energy consumption to hours.

Each Scheduling Coordinator will be responsible for the collection of end-user meter data and for ensuring that the data supplied to the ISO meets the requirements of the ISO Tariff.  Scheduling Coordinators must approve and certify meters of those end-users whom they represent, and shall upon request of the ISO supply promptly copies of all certificates issued.  (End-user meters in place as of the ISO Operations Date are deemed to be certified.)  Once certified, meters need not be re-certified provided they are maintained as required under Appendix J;  re-certification is not required by the ISO when an end-user changes its Scheduling Coordinator.  The ISO will enter into meter service agreements with Scheduling Coordinators responsible for providing end-user meter data to the ISO, specifying that Scheduling Coordinators will require the same meter requirements to those set forth in the ISO Tariff.  These meter service agreements will set out the security and data validation procedures that the Scheduling Coordinator will apply to the hourly and cumulating meter data, in order to comply with the ISO Tariff.

The ISO may adopt a set of standards for meter data security and validation, editing and estimating, at its discretion.  Scheduling Coordinators are to obtain the approval of the relevant Local Regulatory Authority (e.g., the CPUC) to any proposed revisions to the ISO's set of standards before submitting them to the ISO for approval.  The ISO reserves the right to inspect, test and otherwise audit each end-use metering installation, including meters, instrument transformers, meter data, metering systems and records pertaining thereto, including:  (a) software audits to test whether the Scheduling Coordinator's collection, validation, and communication for meter data provided by the Scheduling Coordinator, to the ISO, conform with the ISO's requirements; and (b) unannounced audits during normal business hours to confirm whether physical meter data is consistent with that delivered to the ISO by the Scheduling Coordinator.  End-use meter data remains the property of the end-user and shall be made available to third parties only upon the express permission of the end-user or as otherwise required by law or provided for in the ISO Tariff.  The ISO shall be granted access to end-use meter data obtained by Scheduling Coordinators.

### Scheduling coordinator/PX requirements

The PX’s requirements are substantially the same as the ISO’s, including end-user meter standards in the PX Tariff’s Appendix C that parallel those in the ISO Tariff’s Appendix J and require conformance with the ANSI C12 standards and any other local regulatory authority requirements.  Communication of end-use meter data to the PX will use the PX’s communication protocols and formats, which may be distinguishable from the ISO’s.  The PX reserves the right to inspect, test and otherwise audit each end-use metering installation, including meters, instrument transformers, meter data, metering systems and records pertaining thereto, in addition to the ISO’s reservation of these rights.

The settlement processes of the ISO and PX require hourly meter reads, submitted no later than 38 days after energy is consumed, unless a customer is providing ancillary services, which require more frequent reads.  In contrast, some data needs of UDC tariffs, such as calculation of demand charges, may require meter reads to occur on 15-minute intervals.

### non-UDC ESP/aggregator requirements

### UDC requirements

## Organization of this M&DCS Workshop Report

# OBJECTIVES FOR METERING AND DATA COMMUNICATIONS STANDARDS

Appropriate standards for open-architecture metering and data communications systems must resolve a number of technical, economic, and public policy issues.  This can only be accomplished through the application of a uniform conceptual framework which, in turn, is derived from accepted principles, an understanding of data requirements, and the limitations of previous regulatory decisions.

## Principles

The following principles are defined for the M&DCS workshop:

### Open System

An Open System is one in which the interfaces, services, protocols, and data formats are developed in an open, consensual, vendor-neutral process accredited to a recognized national standards or international standards body and published.

#### Non-proprietary System

An Non-proprietary System is one in which vendor-specific interfaces, services, protocols, and data formats are released into the public domain, but this is not an “open” system.

#### Licensed System

A Licensed System is one in which vendor-specific interfaces, services, protocols, and data formats are not released into the public domain, but merely licensed to other parties; but this is not an “open” system.

### National Standards

In the United States, national standards are those adopted in processes accredited to the American National Standards Institute, a member body of the International Standards Organization.  The Institute of Electrical and Electronic Engineers, among others, is accredited to ANSI to develop national standards

### Open Architecture

Open Architecture extends the definition of an Open System to include an ensemble of Open Systems interconnected to form a integrated operational environment.  This is accomplished with national standards for interfaces, services, protocols and data formats to enable configuration, operation and substitution of the entire system, its application or its components, with other implementations available from different vendors.

It is important to recognize that systems not meeting all of the above defined conditions, e.g., previously proprietary specifications or formats which are made available for use by the industry, are not “Open” in the context of the above definition.

### Plug-and-Play

Plug-and-Play means that any provider’s component for any part of the system will be fully matched to the remainder of the system and cannot normally be incorrectly calibrated, installed, or operated; this is the best case of Open System Interoperability.

### Interoperability

Interoperability is not a specification, but design criteria for an efficient system, implemented through an Open Architecture and the use of competitively produced components.   By using competitive components, designed to performance specifications driven by market preferences (and minimum requirement for good public policy, such as auditing), vendors compete “within the box”.  By using the standardized interfaces, services, communication protocols, and data structures of the Open Architecture among those components, i.e. “between the boxes”, the illusion of competition, where it would otherwise yield minimum returns, is avoided.  As the technical, economic, and policy circumstances determining such a design persistently change, this represents a relative goal, to be advanced or retarded, more than an absolute requirement to be met or not.

## Metering Requirements of End Use Customers

### Direct access customers

### Virtual direct access customers (hourly Power Exchange (PX) pricing option) - IDR meter required for all customers electing this option

### Default energy purchase via UDC - Existing meters adequate

### IDR meter general parameters

#### Hourly energy consumption recording,

#### Metering capability as required under UDC tariff

#### Data to be recorded (as required by tariffs or contracts)

#### Time interval for recording (i.e. 15 minute, hourly)

#### Meter read frequency, i.e. Monthly, Daily, Other

The metering requirements of end-use customers have been detailed in the MADAWG recommendations.

## Metering Provision

### Metering requirements

### Meter standards development

The key standard for Utility Industry End Device Data Tables that define how meters are read (via communications links) and programmed and read, IEEE/ANSI is complete and available from ANSI.  All new meters to be read via communications links and installed for direct access customers having a demand of 20 kW or greater after 6/1/98 shall be ANSI C12.19 compliant.

Likewise, the key standard for Optical Port Meter Reading ANSI C12.18 has been approved by ANSI.  All meters to be installed after 1/1/98, which will be read via optical ports, should be ANSI C12.18 compliant.

### Certification process for meters and suppliers

As discussed in section III.H, the ISO and PX Tariffs have established a workable set of metering requirements, by stipulating the use of the ANSI C12 standards, and have also established a workable certification process, which assigns the responsibility for certification to the Scheduling Coordinator.  That is, UDCs do not also need to assert additional metering requirements (other than to ensure that they receive all the data needed for billing under their CPUC-approved tariffs) or certification processes.

ANSI C12 standards are endorsed, as supplemented by standards adopted by other national and international standards organizations where they do not conflict with the ANSI standards.  When a standard has reached this level of acceptance, the CPUC is assured that industry experts have considered all pertinent technical judgments.  When this level of acceptance has not been reached, there may be outstanding technical issues that still need resolution among industry experts, and a more prudent course for the CPUC to follow in achieving resolution of these issues would be to rely on the recognized standards organizations to resolve them, rather than undertaking its own judicial process to address highly technical matters that are being addressed elsewhere.

## Meter Installation, Operation, and Maintenance

### Installation and maintenance requirements

### Installation and maintenance standards development

### Certification process

Recommendation are discussed in section III.C.

## Meter Reading Requirements

### Meter reading methods standards development

ANSI has developed a suite of standards for metering and meter reading, ANSI C12.18, C12.19, C12.20 and C12.21 All of these standards are complete and should be utilized for direct access metering needs in California.  (IEEE 1377 is under final review by IEEE and is identical to ANSI C12.19.

### Timeliness requirements

### Communications methods

There are many methods via which meters can be read using data communications technology.  It is important that the methods used comply with modern data communications standards as specified by National Standards organizations including IEEE and ANSI, in order to ensure interoperability and reliability of data transfer between communicating Direct Access entities.

### Communications protocols

EPRI has developed the UCA communications architecture to serve the needs of the electric, gas and water utility industries. The architecture consists of a suite of data communications protocols including protocols which are suited for the meter reading needs of direct access in California.  All of the included protocols are full International Standards.  One application layer protocol, the Common Application Services Model is being forwarded to the IEEE Standards Coordinating Committee (SCC) 36 and is expected to be balloted and approved within one year.

### Parties requiring data

### Certification process

### Meter read frequency

Meter-reading requirements for 1998 have been detailed in the MADAWG recommendations.  Goals for future requirements should be guided by Open Architecture based interoperability, as contemplated in the ongoing work of IEEE Standards Coordinating Committee 36 for the Utility Communications Architecture.

## Meter Data Transformation

### Validation, estimating, editing  of consumption data

### Transforming usage/other data into common forms/formats

IEEE/ANSI defines meter data elements in a consistent manner and enables different meter vendors to provide meter data to users in a consistent way.  The UCA meter data format presents meter data in an object oriented manner enabling irrespective of the underlying data communications link or vendor.  The UCA meter data format is extensible, i.e., additional data elements can be added to the format at a later point in time without major changes in client software.  This consistent format mechanism is very important to direct access as it assures interoperability among entities and competition by enabling a consistent meter data format

### Timeliness requirements

### Certification process

Meter data transformation requirements have been detailed in the MADAWG recommendations.

## Meter Data Transfer and Storage systems

### Parties requiring data

### Timeliness requirements

### Communications methods

### Communications protocols

### Meter records

### Certification process

### Types of data

Meter data transfer and storage requirements for 1998 have been detailed in the MADAWG recommendations.  Goals for future requirements should be guided by Open Architecture based interoperability, as contemplated in the ongoing work of IEEE Standards Coordinating Committee 36 for the Utility Communications Architecture

## ISO/PX metering requirements for end use customers

### ANSI/IEEE Standards

ANSI has developed a suite of standards for metering and meter reading, ANSI C12.18, C12.19, C12.20 and C12.21. IEEE has developed a standard for telephone reading of meters, IEEE 1390. The UCA specifies a variety of local and wide area networks, as well as links between them, which are suitable for this Direct Access application.  All of these standards are complete and should be utilized for direct access metering needs in California.

### Hourly read capability

### Meter read frequency

# DATA MODEL

The Data Models implicit in both ANSI C.12-19 and IEEE SCC36 UCA-2, while complex, are fully compatible and, in fact, have already been mapped into one another in the process of developing the CASM element of UCA-2.

A simple Data Model is appropriate for the limited task of developing an interim methodology for use immediately after January 1, 1998, until the national standards currently under development are completed.  A typical Data Model, structure for illustrative purposes, may be prepared for use at the workshop.

# ESTABLISHMENT AND USE OF STANDARDS

One of the most productive innovations in the history of modern industry has been the concept of component standardization.  From the McCormack reaper to “plug & play” computer accessories, standardized components have been associated with astonishing gains in economic efficiency and historic shifts in industrial organization.  Whether improving the throughput of an assembly line or creating a mass market for information technology, the standardization of components in a competitive market yields more competitive products, whether they be stand-alone assemblies of fitted parts or the complex information systems upon which we are to build a new electric services industry.

## Types Of Standards

### Proprietary, i.e. manufacturer’s

Proprietary standards are inherently reflect a single vendor’s competitive strategies and should never be the basis for the implementation of Direct Access in California.

### Utility specifications and standards

Utility specifications were typically developed in an environment where vertical integration allowed utilities to optimize performance across multiple functions.  In a competitive environment, it is inappropriate for such legacy standards to be the basis upon which new market entrants compete with established utilities and their targeted-market affiliates.  It is in the best interests of all parties concerned  --the customers, the UDCs, and all other new market participants to broader-based policies, such as statewide procedures for business practices and national level standards for technological interoperability, particularly in data communications and the transfer of meter data among the various entities. Utility-specific standards should only be used where statewide and national standards do not exist and are not anticipated.

### De facto standards

De facto standards should be used only in the absence of open national standards in the implementation of direct access in California.  A transition strategy should be used to migrate these systems to national standard-based Open Systems at the earliest possible time, to ensure interoperability.

### State and local, i.e. electrical codes

### National standards, i.e. ANSI, IEEE

ANSI has developed a suite of standards for metering and meter reading, ANSI C12.18, C12.19, C12.20 and C12.21.  IEEE has developed a standard for telephone reading of meters, IEEE 1390.  All of these standards are complete and should be utilized for direct access metering needs in California.  EPRI has developed the UCA communications architecture to serve the needs of the electric, gas and water utility industries. The architecture consists of a suite of data communications protocols, which are suited for meter reading, and data transfer needs of direct access in California.  The protocols will enable efficient and reliable transfer of data over any standard communications method used, including: telephone, radio, satellite, Internet, etc. All of the included protocols are either full national or International Standards.  One application layer protocol, the Common Application Services Model (CASM) is being forwarded to the IEEE Standards Coordinating Committee (SCC) 36 and is expected to be balloted and approved within one year.

## Existing Metering Standards

### Meters

ANSI has developed a suite of standards for metering and meter reading, ANSI C12.18, C12.19, C12.20 and C12.21 All of these standards are complete and should be utilized for direct access metering needs in California.

### Communications

EPRI has developed the UCA communications architecture, which consists of a suite of national or international standard data communications protocols, which are suited for meter reading and data transfer needs of direct access in California.

### Installation and maintenance

### Reading

### Records

### Programming

### Security

### Testing

### Vendor certification

### Service Entrance equipment

### Instrument transformers

### Service connect/disconnect

### Data transfer capabilities

### National Standards, i.e. ANSI C12

#### IEEE 1377 / ANSI C12

ANSI has developed a suite of standards for metering and meter reading, ANSI C12.18, C12.19, C12.20 and C12.21. IEEE has developed a standard for telephone reading of meters, IEEE 1390.  All of these standards are complete and should be utilized for direct access metering needs in California.

#### UCA

EPRI has developed the UCA communications architecture to serve the needs of the electric, gas and water utility industries. The architecture consists of a suite of data communications protocols, which are suited for meter reading, and data transfer needs of direct access in California. All of the included protocols are either full national or International Standards.  One application-Layer protocol, the Common Application Services Model (CASM) is being forwarded to the IEEE Standards Coordinating Committee (SCC) 36 and is expected to be balloted and approved within one year.

### Other standards

“Substantive Rules” (similar to the CPUC’s General Orders) from the Texas Public Utilities Commission exist concerning metering.  In an Appendix to this proposal, is to be found a draft adaptation of the Texas rules to the California market.  Because those rules are oriented toward a monopoly utility environment, the adapted rules necessary for the future interactions among multiple market participants will extend beyond the wording changes contained in the Appendix, and are discussed in the body of this proposal.  However, this adaptation of the Texas PUC’s rules can form a starting point for rules that will be adopted by the CPUC.

## Evaluation Of Existing Metering Standards Suitability For Direct Access

### Data types

The ANSI/IEEE data tables specify a complete range of data types, making this a suitable standard for direct access.

### Data recording interval

The ANSI/IEEE data tables allow any authorized user to specify any required data-recording interval, making this a suitable standard for direct access.

### Meter read frequency

The ANSI/IEEE data tables allow any authorized user to specify any required meter reading frequency - including any required unscheduled readings - making this a suitable standard for direct access.

### Communications capability

The communications capabilities options in the UCA specification, the suite consisting of ANSI C12.18, C12.19, C12.20 and C12.21, and the IEEE1390 telephone standard provide a wide range of communications capabilities for both existing and future needs and including both local and wide area networks, making the existing set of standards suitable for direct access.

### ISO/PX requirements

The UCA specification, the suite consisting of ANSI C12.18, C12.19, C12.20 and C12.21, combined with the IEEE1390 telephone standard provide a wide range of communications capabilities for both existing and future needs and including both local and wide area networks, making the existing set of standards suitable for direct access.

### Data transfer capability

The data transfer capabilities in the UCA specification, the suite consisting of ANSI C12.18, C12.19, C12.20 and C12.21, IEEE1390 telephone standard provide a wide range of data transfer capabilities for both existing and future needs and including both local and wide area networks, making the existing set of standards suitable for direct access.

### ANSI C12 compliance

The UCA specification, the suite consisting of ANSI C12.18, C12.19, C12.20 and C12.21, combined with the IEEE1390 telephone are all compatible and compliant with (and include) ANSI C12, making the existing set of standards suitable for direct access.

### Other considerations

## Migration to Standards

It is imperative that any interim metering, meter reading, and meter data management and communication programs proposed or adopted for implementation on January 1, 1998, contain explicit plans for migration to national standards in a timely manner.  The overwhelming majority of utility equipment for metering, meter reading, and meter data management and communication does not conform to the newly emerging and proposed national standards, nor do most current utility metering, meter reading, and meter data management and communication programs currently contemplate migration to national standards and, so, such direction is needed.

An appropriate migration plan would take steps such as the following:

- Accepting the existing legacy metering and meter reading environment as a starting point;

- Require new interval meters and meter reading systems to be compliant with national standards over time;

- Migrate from the PG&E proposed meter data format required to support the data exchange / billing between MDMAs and other entities on 1/1/97 to a national standard meter data format to ensure extensibility of meter functions and meter data to be supported;

- Work with meter manufacturers to imbed national open standard meter data format and data communications interfaces in their product.

# STANDARDS FOR THE PROVISION, INSTALLATION, OPERATION, AND MAINTENANCE OF METERING SYSTEMS

## Who Will Be Allowed To Provide, Install, Operate, And Maintain Metering?

Metering provision, installation, or operation and maintenance may be performed by any eligible, certified Meter Vendor, Meter Installer, or Meter Maintenance Provider chosen by the customer or the customer’s agent.

Meters shall be owned by the end-use customer of record or any other party acting as the agent of the end-use customer of record.

### UDC

Utility Distribution Companies (UDCs) must, for the duration of the transition period, establish and maintain certification for metering provision, installation, and operation and maintenance and must provide any one or more of those services to any of their distribution customers so electing; other distribution service providers may qualify for and establish and maintain certification for metering provision, installation, and/or operation and maintenance and may, as may UDCs, offer any one or more of those services to anyone.

### Qualified Energy Service Providers (ESP)

Energy Service Providers (ESPs) may qualify for and establish and maintain certification for metering provision, installation, and/or operation and maintenance and offer any one or more of those services to anyone.

### Other qualified parties

Other Parties may qualify for and establish and maintain certification for metering provision, installation, and/or operation and maintenance and offer any one or more of those services to anyone.

### Functions performed

Electric Load Metering is the detection of electric load flows and the production of a reliable representation of those load flows, and is a distinct function within the electric services industry metering and data communication system; a meter is any customer premises device or system that accomplishes electric load metering. The representation (the “raw meter data”) must be capable of being sensed or otherwise acquired from without the meter proper, whether visually, optically, mechanically, electronically, or otherwise; although existing electric metering is primarily either electromechanical, producing a visual representation, or electronic, producing a digital electronic representation.  Electric metering does not include any instrument transformers needed for particular meter forms.

Metering Provision is the sale or leasing of revenue-quality electric load meters to end-use customers of record, or to their agents.

Metering Installation is the physical connection of a meter into the appropriate electrical circuit at the meter panel or other point of connection to either the end-use customer’s premises wiring or the distribution line serving that customer.

Metering Operation and Maintenance is the periodic or occasional calibration, programming, inspection, testing, maintenance, minor repair or similar services necessary for the continued reliable and efficient performance of a meter.

## Proposed Standards for Metering Equipment and Systems

### Revenue Meters

The ANSI/IEEE data tables contain all specifications required to address issues of register types and programs for both existing and future needs, making the existing set of standards suitable for direct access.

### Meter communications requirements

#### Local read capability

#### Remote read capability

#### Multiple party read capability

#### Formats and protocols

IEEE/ANSI defines meter data elements in a consistent manner and enables different meter vendors to provide meter data to users in a consistent way.  UCA provides a Meter Data Model, which makes the meter data available to a user in an object-oriented format.  This format will enable the user of the data to access the data in a consistent logical manner.  The model is extensible, so additional data can be added without change-out of user software.  Additional information is provided in the Attachment to this proposal.

#### Security

UCA incorporates a multi-level security mechanism that will allow restrictions to views of data elements.

#### Other requirements

### Inspection and checkout of meters prior to placing in service

## Proposed Standards For Metering Installation, Operation, Maintenance, and Testing

### Installation and maintenance of metering

### Programming of meters

### Inspection and checkout of metering prior to placing in service

### Meter testing

## Certification Process For Meter Vendors

### Vendor certification

### Equipment evaluation

### Equipment testing

### Performance standards

### Enforcement provisions

## Certification Process For Meter Installation, Operation, Maintenance, And Testing Vendors

### Vendor certification

### Licensing - Electrical Contractor

### Liability and financial

### Experience and training

### Performance standards

### Enforcement provisions

# STANDARDS FOR THE INSTALLATION, OPERATION, AND MAINTENANCE OF METER READING SYSTEMS

## Who Will Be Allowed To Read Meters?

Meter-Reading may be performed by any eligible, certified Meter-Reading System Operator chosen by the electric service customer or the customer’s agent.

### UDC

Utility Distribution Companies (UDCs) must establish and maintain certification for meter reading and must provide this service to any of their distribution customers so electing; any other distribution service providers may qualify for and establish and maintain certification for meter reading and may offer that service to anyone that takes both energy service and distribution service from providers with which the meter-reading distribution service provider maintains reciprocal data agreements.

### Qualified Energy Service Providers (ESP)

Energy Service Providers (ESPs) may qualify for and establish and maintain certification for meter reading and offer that service to any distribution customer of any UDC with which the ESP maintains reciprocal agreements.

### Other qualified parties

Other Parties may qualify for and establish and maintain certification for meter reading and offer that service to anyone that takes both energy service and distribution service from providers with which the meter-reading provider maintains reciprocal data agreements..

### Functions performed

Meter-Reading is the sensing or other acquisition of the metering analog (“raw meter data”) and its communication to a Meter Data Management Agent and is a distinct function within the electric services industry metering and data communication system; a meter-reading system is any process, manual or automated, that accomplishes meter-reading.

## Proposed Standards for Meter Reading Systems

### Meter Reading

### Communications

### Inspection and checkout of meter reading systems prior to placing in service

## Certification Process For Meter Reading Vendors

### Vendor certification

### Liability and financial

### Experience and training

### Performance standards

### Enforcement provisions

# STANDARDS FOR THE INSTALLATION, OPERATION, AND MAINTENANCE OF METER DATA MANAGEMENT SYSTEMS

## Who Will Be Allowed To Provide, Install, Operate, And Maintain Meter Data Management Systems?

Meter Data Management may be performed by any eligible, certified Meter Data Management Agent chosen by the electric service customer or the customer’s agent.

### UDC

UDCs must maintain certification for meter data management and perform that service for any of their distribution customer so electing; and may also offer that service to any energy service customer of any ESP with which the UDC maintains reciprocal data agreements.

### Qualified Energy Service Providers (ESP)

Energy Service Providers (ESPs) may qualify for and establish and maintain certification for meter data management and offer that service to any distribution customer of any UDC with which the ESP maintains reciprocal data agreements.

### Other qualified parties

Other Parties may qualify for and establish and maintain certification for meter data management and offer that service to anyone taking both energy service and distribution service from providers with which the Other Qualified Party maintains reciprocal data agreements.

### Functions performed

Meter Data Management is defined as the process of editing and validating raw meter data and making that edited and validated data, and possibly other related data, from other sources, available to customers, distribution service providers, and energy service providers alike and is a distinct function in the electric services industry metering and data communication system.

## Proposed Standards for Meter Data Management Systems

### Data Transformation

### Data Storage

### Data Transfers

#### Timeliness requirements

MDMAs should eventually be expected make meter data available to all users (customers, UDCs, and ESPs) as necessary to support their other regulatory requirements, such as to scheduling coordinators and the ISO.

#### Communications methods

There are many methods via which meter data can be transferred using data communications technology.  It is important that the methods used comply with modern data communications standards as specified by National Standards organizations in order to ensure interoperability and reliability of data transfer between communicating Direct Access entities.

#### Communications protocols

#### Security

#### Accuracy

#### Reliability

### Meter Records

#### Common meter data model

See Section IV. Data Model.

#### Meter number assignment

#### Meter specification documentation

#### Customer and premise records will be addressed by the Implementation Plans

### Collection of data from sources other then meters or meter communications systems.

There is no reason that MDMAs cannot serve to distribute information, pertinent to the restructured electric services industry other than just meter data.

### Inspection and checkout of meter data management systems prior to placing in service

## Certification Process For Meter Data Management Vendors

### Vendor certification

### Liability and financial

### Experience and training

### Performance standards

### Enforcement provisions

# APPENDICES

Adaptation of Texas PUC Meter Standards

Illustrative Data Model

## Adaptation of Texas PUC Meter Standards

ORA’s research on meter standards has revealed the existence of ‘Substantive Rules’ (similar to the CPUC’s General Orders) concerning metering, and the Appendix to this proposal is a draft adaptation of these rules to California’s market.  Because the Texas rules are oriented toward a monopoly utility environment, the rules necessary for the future interactions among multiple market participants will extend beyond the wording changes contained in this Appendix, and are discussed in the body of this proposal.  However, this adaptation of the Texas rules can form a starting point for rules that will be adopted by the CPUC.

The original text of the Texas PUC’s rules can be found on the Internet at

- http://www.puc.texas.gov/sr-tc.htm,

- http://www.puc.texas.gov/23-47.htm,

- http://www.puc.texas.gov/23-51.htm, and

- http://www.puc.texas.gov/23-62.htm.

### Purpose and scope.

- The provisions of this section are intended to establish a comprehensive regulatory system to assure that the practices involving metering and billing are just and reasonable, and to establish the rights and responsibilities of utilities, energy service providers, and customers.

- Customers may use Energy Service Providers or other agents to accomplish meter provision, installation, or operation and maintenance, meter reading, or meter data management, as described herein, but such agents would also be subject to these provisions.

- For purposes of enforcement, customers and energy service providers, as well as utilities are subject to the enforcement pursuant to the Public Utilities Code, which may involve civil penalties of up to ___ for each offense and criminal penalties for willful and knowing violations.

### Meter requirements.

#### Use of meter.

All electrical energy sold by a utility or energy service provider shall be charged for by meter measurements, except where otherwise authorized by the commission.

#### Standard type.

No utility or energy service provider shall furnish, set up, or put in use any meter which is not reliable and of a standard type which meets industry standards, as set by the American National Standards Institute, Incorporated (ANSI), Standard C12;  provided, however, special meters not necessarily conforming to such standard types may be used for investigation or experimental purposes.

#### Accuracy requirements for meters.

No meter that exceeds the test calibration limits, shall be placed in service or left in service.  Whenever on installation, periodic, or other tests, a meter is found to exceed these limits, it shall be adjusted.  Meters shall be adjusted as closely as practicable to the condition of zero error.  The tolerances are specified only to allow for necessary variations.

All electrical current transformers, potential transformers, or other such devices used in conjunction with an electric meter shall meet test calibration and phase angle limits set by ANSI C12 and C57.13 for revenue billing.

### Installation of meters.

Meters and service switches in conjunction with the meter shall be installed in accordance with the latest revision of American National Standards Institute (ANSI), Incorporated, Standard C12 (American National Code for Electricity Metering), or other standards as may be prescribed by the commission, and will be readily accessible for reading, operation and maintenance (including testing and inspection), and where such activities will cause minimum interference and inconvenience to the customer.

Customer shall provide, without cost to the utility or energy service provider, at a suitable and easily accessible location:

- a properly installed meter,

- sufficient and properly located space for other apparatus of the utility or energy service provider, and

- other equipment and facilities as required.

All meters installed after the effective date of these rules shall be located as set forth in this section, provided that, where installations are made to replace meters removed from service, this section shall not operate to require any change in meter locations which were established prior to the effective date of these rules, unless the old location is no longer suitable or proper, or the customer desires that the location be changed.  When the customer changes the location of a previously established meter location on his own premises at the request of the any other party, the customer shall be compensated for his expense by the requesting party.

### Meter testing.

#### Meter tests prior to installation.

No permanently installed meter shall be placed in service unless its accuracy has been established. If any such meter shall have been removed from actual service and replaced by another meter for any purpose whatsoever, it shall be properly tested and adjusted before being placed in service again unless such meter is monitored by a test program approved by the commission.

#### Testing of meters in service.

Meter test periods for all types of meters shall conform to the latest edition of American National Standards Institute, Incorporated, Standard C12 unless specified otherwise by the commission.  If the statistical sampling method is used, the method of sampling, the results of the tests, and any planned corrective action shall be reported annually to the commission.  All other types of meters shall be tested at least annually unless specified otherwise by the commission.

#### Qualified experts.

Each meter installation provider or meter operations and maintenance provider shall engage qualified experts to provide such instruments and other equipment and facilities as may be necessary to perform the meter installations or the meter inspections, tests, programming, or maintenance required or repair allowed by this section.  Such equipment and facilities shall generally conform to ANSI, Standard C12, unless otherwise prescribed by the commission, and shall be acceptable to the commission and shall be available at all reasonable times for the inspection by its authorized representatives.

#### Testing equipment.

Each meter operations and maintenance provider shall, unless specifically excused by the commission, (1) either with its own facilities or a standardizing laboratory of recognized standing, provide such meter laboratory, standard meters, instruments and other equipment and facilities as may be necessary to make the meter tests required by these rules, and (2) provide portable test instruments for testing billing meters.  Such equipment and facilities shall generally conform to American National Standards Institute, Incorporated Standard C12, unless otherwise prescribed by the commission, and shall be acceptable to the commission and shall be available at all reasonable times for the inspection by its authorized representatives.

#### Reference standards.

Each meter operations and maintenance provider shall provide or have access to suitable indicating electrical instruments as reference standards for insuring the accuracy of shop and portable instruments used for testing billing meters.  Reference standards of all kinds shall be submitted once each year or on a scheduled basis approved by the commission to a standardizing laboratory of recognized standing, for the purpose of test and adjustment.

#### Calibration of test equipment.

All shop and portable instruments used for testing billing meters shall be calibrated by comparing them with a reference standard at least every 120 days during the time such test instruments are being regularly used.  Test equipment shall at all times be accompanied by a certified calibration card signed by the proper authority, giving the date when it was last certified and adjusted.  Records of certifications and calibrations shall be kept on file in the office of the meter operations and maintenance provider.

### Meter readings.

#### Meter unit indication.

In general each meter shall indicate clearly the kilowatt-hours or other units of service for which charge is made to the customer.

#### Reading of meters.

As a matter of general practice, service meters shall be read at no longer than monthly intervals, and as nearly as possible on the corresponding day of each meter reading period, but may be read more frequently, as determined between the customer and his respective service providers.

#### Customer-read.

If customers, ESPs, and UDCs mutually establish a customer-read program in which customers read their own meters and report their usage monthly, such readings shall be considered an actual meter reading by the ESP and the UDC for billing purposes, subject to routine editing and validation by the MDMA.  However, the customer-read program shall ensure that the meters of customers on a customer-read program are independently verified at least every 12 months to verify the accuracy of the meter records.

### Meter records.

Each meter installation provider, meter operations and maintenance provider, and MDMA, as appropriate, shall maintain and make available for inspection at its office during reasonable business hours, by the customer, UDC, or ESP, the following records:

#### Meter equipment record.

A record of all of its meters, showing the customer's address and date of the last test.

#### Readings and Billings.

All meter readings and billings for the current month and the 12 preceding months;

#### Records of meter tests.

All meter tests shall be properly referenced to the meter record.  The record of each test made on customer's premises or on request of a customer shall show the identifying number and constants of the meter, the standard meter and other measuring devices used, the date and kind of test made, by whom made, the error (or percentage of accuracy) at each load tested, and sufficient data to permit verification of all calculations.

#### All records shall be made available to the commission upon request.

### Meter tests on request of customer.

Each meter operations and maintenance provider shall, upon the request of a customer or the customer’s ESP or UDC, make a test of the accuracy of the customer's meter, without expense to the party making the request.  The test shall be made during normal working hours at a time convenient to the requester if he desires to observe the test.  The test shall be made preferably on the customer's premises, but may, at the meter operations and maintenance provider’s discretion, be made at the test laboratory.  If the meter has been tested, and within a period of four years any party requests a new test, the test shall be repeated, but if the meter is found to be within the accuracy standards established by the American National Standards Institute, Incorporated, (ANSI), Standard C12 (American National Code for Electricity Metering), the meter operations and maintenance provider may charge the requester a fee which reflects the cost to test the meter, but this charge shall in no event be more than $15 for a residential customer.  However, if the meter's accuracy is not within the appropriate accuracy standards, no charge shall be made to the requester for making the test.  Following the completion of any requested test, the customer, the UDC, and the ESP shall be promptly advised of the date of removal of the meter, the date of the test, the result of the test, and who made the test.

### Bill adjustment due to meter error.

If any meter is found to be outside of the accuracy standards established by the American National Standards Institute, Incorporated, proper correction shall be made of previous readings for the period of six months immediately preceding the removal of such meter from service for the test, or from the time the meter was in service since last tested, but not exceeding six months, as the meter shall have been shown to be in error by such test, and adjusted bills shall be rendered.  No refund is required except to the customer last served by the meter prior to the testing.  If a meter is found not to register for any period, unless bypassed or tampered with, a charge for units used, but not metered, for a period not to exceed three months, shall be based on amounts used under similar conditions during the period preceding or subsequent thereto, or during corresponding periods in previous years.

### Meter tampering.

For purposes of these sections, meter tampering, bypass, or diversion shall be defined as tampering with any metering or meter reading equipment, bypassing the same, or other instances of diversion, such as physically disorienting the meter, objects attached to the meter to divert service or to bypass, insertion of objects into the meter, and other electrical and mechanical means of tampering with, bypassing, or diverting electrical service.  The burden of proof of meter tampering, bypass, of diversion is on the UDC or ESP.  Photographic evidence or any other reliable and credible evidence may be used;  however, any evidence must be accompanied by a sworn affidavit when any action regarding meter tampering as provided for in these sections is initiated.  A court finding of meter tampering may be used instead of photographic or other evidence, if applicable.

### Severability clause.

- The adoption of this section will in no way preclude the Commission from altering or amending them in whole or in part, or from requiring any other or additional service, equipment, facility, or standard, either upon complaint or application or upon its own motion.  Furthermore, these provisions will not relieve in any way a customer from any of its duties under the Public Utilities Code, or other laws of this state or the United States.  If any provision of this section is held invalid, such invalidity shall not affect other provisions or application of this section which can be given effect without the invalid provision or application, and to this end, the provisions of this section are declared to be severable.  The provisions of this section shall not be construed so as to enlarge, diminish, modify, or alter the jurisdiction, powers, or authority of the commission or the substantive rights of any persons.