Pacific Gas and Electric Company (PG&E)

San Diego Gas and Electric Company (SDG&E)

Southern California Edison Company (SCE)

Meter and Data Communications Standards (MDCS)

Workshop Report

Table of Contents

I. EXECUTIVE SUMMARY

I.A. Purpose of the workshop and relationship to the Retail Settlement and Information Flow (RSIF) workshop that preceded it.

I.B. Key findings resulting from this workshop (proposed)

I.C. Significant areas of agreement and disagreement among the UDCs and among/between the other participants (to be added after the workshop)

I.D. Organization of the remainder of the report

II. BACKGROUND

II.A. Purpose of MDCS workshop process

II.B. Relevant legislative and regulatory decisions to date: CPUC, FERC, AB 1890, etc.

II.C. Summary of the new market structure

II.D. The workshop process, including pre-workshop activities

III. OBJECTIVES FOR METERING AND DATA COMMUNICATIONS STANDARDS

III.A. Principles

III.B. Metering Requirements of End Use Customers

III.C. THE FOLLOWING TOPICS WILL BE DISCUSSED IN THE REMAINDER OF THIS REPORT

IV. ESTABLISHMENT AND USE OF STANDARDS

IV.A. Types Of Standards

IV.B. Existing Metering Standards

IV.C. Meters & Metering Equipment.

IV.D. Evaluation of Existing Metering Standards Suitability For Direct Access

IV.E. Migration To Standards

V. STANDARDS FOR THE PROVISION, INSTALLATION, OPERATION, AND MAINTENANCE OF METERING SYSTEMS

V.A. Who Will Be Allowed To Provide, Install, Operate, and Maintain Metering?

V.B. Proposed Standards for Metering Equipment and Systems

V.C. Meter Installation, Maintenance, and Testing Qualification Process For Meter Agents

VI. STANDARDS FOR THE INSTALLATION, OPERATION, AND  MAINTENANCE OF METER READING SYSTEMS

VI.A. Meter Reading

VI.B. Proposed Standards for Meter Reading Systems

VI.C. Certification Process For Meter Reading Vendors

VII. STANDARDS FOR THE INSTALLATION, OPERATION, AND MAINTENANCE OF METER DATA MANAGEMENT SYSTEMS

VII.A. Who Will Be Allowed To Provide, Install, Operate, And Maintain Meter Data Management Systems?

VII.B. Proposed Standards for Meter Data Management Systems

VII.C. Certification Process For Meter Data Management Vendors

Appendixes

Appendix A: Metering Product Certification Tests

Appendix B: DA Meter Site Installation Inspection and Testing Requirements

Appendix C: MDMA Acceptance Criteria

Appendix D: MADAWG Technical Sub-Group

Appendix E: MDMA Data Formats

EXECUTIVE SUMMARY

Purpose of the workshop and relationship to the Retail Settlement and Information Flow (RSIF) workshop that preceded it.

In Decision 97-05-039, dated May 6, 1997, the CPUC ordered that certain revenue cycle services, including metering, be unbundled from standard utility service to Direct Access customers. The decision also ordered that these services be opened to competition on January 1, 1998.

PG&E, SDG&E, and SCE (the UDCs) were ordered by Decision 97-05-039, dated May 6, 1997, to confer with interested parties and attempt to develop the necessary standards for equipment and functions to ensure that reliable service to customers would continue, regardless of the metering service entity.  This report is submitted to the Commission in compliance with that directive.

The RSIF workshop is scheduled to identify the information requirements of the existing and new market entities under the new industry structure. A common model/understanding of necessary and desired information flows under the new market structure is also scheduled to be identified.

This workshop examines the technical requirements for gathering, generating and communicating the necessary information to meet the needs of the new market place, focusing on metering, meter reading, and meter data procedures and standards.

Key findings resulting from this workshop

Open Architecture will be defined at the meter and the MDMA Server and this will allow the market to begin on 1/1/98 and allows for adoption of new metering technologies.

Certification, auditing and enforcement processes will be required for meters, meter installers and MDMA providers.

Certification, auditing and enforcement processes for meter installation, maintenance and testing may take a lengthy period of time and an interim process may need to be developed.

There are numerous applicable national, state and local standards for meters but there are limited standards available for meter installation, maintenance, tests and reading.

An ongoing standards revision process must be developed to support this market.

The requirements for performing various functions should, to the extent possible, be the same for all entities performing that function.

The entities performing metering functions will be fully responsible for their safe, accurate, and reliable service.

The entities performing reading and meter data management functions will be fully responsible for the accurate and timely communication of their data.

New enforcement mechanisms need to be established to ensure market performance compliance with the DA requirements.

It maybe necessary for additional NEC and CAL-OSHA rules to be established to cover new electrical work that was previously exempt as a result of utility performing the work.

Recommended CPUC Actions

The commission should adopt the “Open Architecture” recommendations detailed in Section III.

The Commission should approve workshop recommended standards for meters, meter installation, maintenance and testing, meter reading and MDMA functions.

The Commission must decide on the physical demarcation point that separates the UDCs bundled service responsibility and the facilities open to competitive services.

The Commission should adopt the workshop recommendations on timeliness of data delivery to market participants.

The Commission should ensure that the certification, auditing and enforcement processes necessary for the DA marketplace are established.

The Commission should adopt the license and/or certification requirements recommended in this report for metering equipment; meter installation, calibration, maintenance, testing; and meter reading and data management.

The Commission (or another appropriate regulatory authority) should establish the structures to certify and monitor the performance of the entities who will be offering metering services effective January 1, 1998. This structure should include a mechanism for accepting and resolving any performance-related complaints.  It is the strong sentiment of the market participants generally that the UDCs should not assume an enforcement role, and the UDC plans for Direct Access implementation are based on that assumption.

The Commission should adopt the end-use meter data transformation and communication methodologies proposed in Section VII of this report. These methodologies meet the requirements defined in the RSIF workshop for data validation, quality (e.g., how much can be estimated versus measured), and timeliness.

data editing and estimating techniques;

standard data format;

data storage rules; and

data transfer protocols.

Market participants will need an acceptance period to ensure their processes and systems can interface prior to the start-up of any metering or meter reading entities.  This acceptance period will ensure that the business processes which are being separated will maintain acceptable levels of operation.  Details will be specified in Appendix C.

Significant areas of agreement and disagreement

There was general agreement on the majority of significant issues contained in this workshop.  Areas where no consensus opinion was developed are noted in the Key Findings and Requested CPUC Actions subsections of this report.

Organization of the remainder of the report

Section II contains background information on relevant events prior to this workshop, including the MADAWG (Meter and Data Working Group) process.

Section III describes the overall objectives for the Commission’s consideration when evaluating proposals for the Meter and Communications Standards, including “Open Architecture” principles.

Section IV provides a review of existing Meter and Data Communication Standards and their suitability for service under the new market structure.

Section V proposes standards and certification processes for meters and ancillary equipment, installation, operation, maintenance, and testing.

Section VI proposes standards, certification and performance monitoring processes for meter reading systems, including installation, reading, and communications.

Section VII proposes standards, certification, and performance monitoring processes for meter data management systems (i.e., data transformation editing and estimating to validate data, along with standards for communicating data, storage and transfers).

BACKGROUND

Purpose of MDCS workshop process

Develop a set of statewide Metering and Data Communications Standards that can be used by all market participants in the Direct Access Market.

The statewide Meter and Data Communication Standards will be based on the following guiding principles:

Promote Open Market

Use Existing Standards Where Available

Equal Requirements for All DA Metering Marketing Participants

Not Sacrifice Workers Or Public Safety

Encourage and Manage Interoperability

Protect California Electric Energy Industry Revenue

Relevant legislative and regulatory decisions to date: CPUC, FERC, AB 1890, etc.

Summary of the new market structure

Changes in market participants

CPUC decision 97-05-039 allows for any qualified Meter Agent to install and maintain Direct Access metering.  Thus an ESP can use the UDC or a qualified Meter Agent to do their metering requirements.

Develop roles and responsibilities to cover all parties who may perform work for Direct Access.

UDC as default provider and distribution system responsibility

In the event that an ESP or Customer wants the UDC to perform meter services, the UDC will take on that role.

The workshop process, including pre-workshop activities

Several pre-workshops and groups have been formed and have contributed to this workshop including: Meter & Data Access Working Group (MADAWG), Retail Settlements and Information Flow (RSIF) workshop, and the Direct Access Working Group (DAWG).

OBJECTIVES FOR METERING AND DATA COMMUNICATIONS STANDARDS

This section addresses the metering requirements of end use customers participating in Direct Access and identifies the Metering and Data Communications areas where standards may be required.

Principles

Open Architecture

Definition

MDCS “Open Architecture” (OA) is defined as meter system elements that are easily changed and communicate through open interfaces.  The key metering and data communications system elements are the meter, the meter data communications system and the Meter Data Management Agent Server (MDMA).  Figure 1 shows a conceptual view.  Open Architecture begins with ANSI approved sockets (mounting standards) that facilitates competition and interoperability of multiple manufacturers’ meters.  The open interface defines physical data connections and is protocol and data format independent.  Between the meter and the communications system there are two parts.  First, meter manufacturers should license the interface to their meters to all comers at no more that a nominal charge.  Second, communications system suppliers should license the interface into their communications system to all comers at no more than a nominal charge.  These two conditions allow for competition between meter manufacturers and for competition between communications system suppliers.

The open interface between the communications system and the meter data management system is the interface through which data will be published to the MDMA Server.  Market participants, including UDCs, ESPs, and the ISO, will retrieve data from the meter data server mailboxes to carry out their market responsibilities.  This interface will be defined as part of the MDCS and RSIF workshops.  The same interface format will be used to publish data into the mailboxes and to retrieve data out of the mailboxes.

Power Measurement and Enron took exception with the meter socket portion of this recommendation.  They stated that other mounting provisions in addition to sockets should be allowed.  It was suggested that the only requirements on meter packaging should relate to safety and tamper protection.

The Plug & Play concept was discussed at length at the MDCS workshop.  The majority of attendees believe this concept will not be a technical possibility in the near future (1-3 years).

Figure 1: Open Architecture

Implementation plan

Taking this approach allows us to meet our objectives of OA beginning 1/1/98 and also allows us to adopt new architecture technologies as they arise in our industry.

Metering Requirements of End Use Customers

Direct Access customers

Interval data recording (IDR) meters are required for all DA customer with maximum demands at or above 20 kW.

For customers below 20 kW their existing meter is adequate for Direct Access using load profiles.  Metering requirements remain uncertain for customers with loads between 20 kW and 50 kW.  This issue will be addressed in another workshop.

IDR meters are optional for Direct Access customers below 20 kW demand.

Implementation plans and associated rules, tariffs, and ESP conditions will determine specific requirements for end use customer metering.

Virtual Direct Access customers (hourly Power Exchange (PX) pricing option)

IDR meters are required for all customers electing this option.

For bundled service customers

UDCs will own all meters and existing meters are adequate.

IDR meter general parameters

Time interval for recording

All meters shall be capable of recording minimum data demanded by the market.  This is defined as:  1) hourly data required for DA settlement process and  2) data required to bill applicable UDC tariffs.  It is recognized that there are a multitude of differing usage data requirements in the industry.  As a result, meters that provide 15 minute interval data will meet a majority of these needs and are recommended.  We acknowledge that other interval data frequencies may be required on a customer by customer basis.

The CEC and Power Measurement expressed a concern that this report should address meters and metering systems which provide power quality information (outages, voltage sags, etc.) to applicable parties.

Meter read frequency

Meters will be read no less than monthly and in accordance with UDC/ESP contract. For further details, see Section VI.

THE FOLLOWING TOPICS WILL BE DISCUSSED IN THE REMAINDER OF THIS REPORT

Metering Ownership

Meter Installation, Operation, and Maintenance

Meter Reading Requirements

Meter Data Transformation

Meter Data Transfer and Storage systems

ESTABLISHMENT AND USE OF STANDARDS

This section provides a review of existing standards and their suitability for Direct Access.

Types Of Standards

The following are different types of metering and metering-related standards that are currently available in the industry National standards: ANSI/IEEE C12 Metering Standards, EEI Handbook of Electricity Metering

State and Local: Independent System Operator (ISO) Metering Specifications, NFPA 70 National Electrical Code (NEC), GO 95 & 128 and CAL OSHA

Local UDC specifications, standards and Rules For The Sale of Electric Energy filed and approved by the CPUC

Proprietary (i.e., manufacturers standards, etc.)

Service Equipment Standards:  Electric Utility Service Equipment Requirements Committee (EUSERC)

Military Inspection Standards (for inspection of meters and metering equipment):  MIL-STD-105D and MIL-STD-414

Sampling Procedures and Tables For Inspection:  ANSI/ASQC Z1.4 and ANSI/ASQC Z1.9

Existing Metering Standards

Meters & Metering Equipment:  Below is the list of the known existing standards and specifications for meter equipment and systems.  Not all of these will be applicable to all meter equipment and systems.

Meters

Meters currently installed in the UDC which meet requirements for DA and are accurate and reliable may be retained by the UDC.

Meters presently meet the following applicable sections of ANSI C12 standards; ANSI C12.1 Code for Electricity Metering; ANSI C12.4 Mechanical Demand Registers; ANSI C12.5 Thermal Demand Meters; ANSI C12.6 Marketing & Arrangement of Terminals for Phase Shifting Devices Used in Metering; ANSI C12.7 Watt-hour Meter Socket; ANSI C12.10 Electromechanical Watt-hour Meters; ANSI C12.13 Electronic Time-of-Use Registers for Electricity Meters; ANSI C12.20 (0.2% and 0.5% Accuracy Classes, approved but not yet released);  and Specification MTR1-96 Engineering Specification for Polyphase Solid State Electricity Meters for use on the ISO (Independent System Operator) Grid.

Power Measurement stated that in addition to these standards, ISO 9000 (International Organization for Standardization) should be adopted for Direct Access metering.

Meters meet local UDC standards

Meters meet ISO Specification MTR1-96: Engineering Specification for Polyphase Solid State Electricity Meters for Use on the ISO Grid.

Communications

Meters may have optical port type 2 ANSI C12.18, protocol specification for optical port.

Schlumberger takes exception to the use of ANSI C12.18.

Meters meet FCC Regulations, Part 15, Class B.

ANSI C12.21 is the Protocol Specifications for Telephone Modem (not yet approved); and ANSI C12.22 is an Electric Meter Interface to a Network Protocol Gateway (not yet approved).  Both of these standards need to be further evaluated.

Programming of Meters and Data Tables

Meters may be programmable through type 2 Optical ports, as defined in ANSI C12.18 and ANSI C12.19.

Itron, Schlumberger, and CellNet expressed concerns over adopting  ANSI C12.19 for Direct Access metering.  It was felt that further review of these standards is warranted.

AMRA and NERTEC felt that ANSI C12.19 is an acceptable standard for DA Metering.

GE stated that they have incorporated ANSI C12.18, and ANSI C12.19 into their meters.

Meters are programmed with laptops, hand-helds or remotely using UDC programs and vendor software. This is done through optical ports, other computer connectors, or remotely transmitted via telephone, radio, etc.

No approved standard exists for table driven protocols today but specific standards need to be developed.

Manufacturers’ Certification

Meter manufacturers’ products are certified through standards, specifications, manufacturers’ certifications, test documentation, and independent laboratory testing.

Metering Transformers

Metering transformers and auxiliary devices are tested in accordance with ANSI standards, ANSI C12.1, ANSI C12.11, ANSI C57.13, EEI Electricity Metering Handbook and local UDC requirements.

All metering transformers meet 0.3% accuracy class.

Service Entrance Equipment

Service and metering equipment must meet local jurisdiction requirements and UDC published electrical service and metering requirements.

Installation and maintenance

There are no national standards for metering installation and maintenance.  However, UDCs currently have their own internal practice for metering installation and maintenance.

Installation

Meters are currently installed according to UDC Electrical Service Requirements.  These requirements will be used until national or statewide standards are developed and approved.

Records

The UDC currently maintains records for all metering devices including:  Billing data history, test reports, in-service history, special conditions and meter characteristics.

Testing

UDCs currently have routine maintenance schedules and meter test requirements.

Service Connect/Disconnect

Procedures are based on UDC Rules for the Sale of Electric Energy filed with the CPUC and state and local ordinances.

Security

Meters and meter panel installations are secured with UDC approved locking devices (i.e. seals, locking rings and meter password protection).

Safety

Meter installers adhere to safe work practices and all CAL OSHA safety rules governing work near energized electrical facilities.

Meter Reading

Reading and Data Transfer

All UDC meters are currently read by various data acquisition methods and data is transferred daily to UDC billing systems.

Evaluation of Existing Metering Standards Suitability For Direct Access

Existing accepted industry standards should be used, where available.  Approved standards should not exclude any existing technologies that also meet relevant standards such as ANSI and the other minimum requirements of this workshop standard.

Migration To Standards

The hourly meters and communications systems used by customers who choose Direct Access must be designed, manufactured and certified to meet the approved specifications and standards recommended by this workshop and approved by the CPUC.  Certification to these standards, if different from the standards that are used to design and produce these products today, will not be required immediately.  However, certification for all products to the standards established by this workshop must be accomplished for all products to be installed for DA applications after 1/1/99.  All UDC meters and systems in service when these workshop standards are approved that have adequate data functionality are deemed DA compliant, and therefore will be grandfathered.

Standards will continue to change and evolve and it is not practical to immediately enforce new standards.  Therefore, the transition period for implementing standards should be 24 months from the date of new standard publication.

An ongoing standards and software revision review process needs to be developed so that any standards adopted now will continue to be refined to reflect changes in technology and the market place on an ongoing basis.

STANDARDS FOR THE PROVISION, INSTALLATION, OPERATION, AND MAINTENANCE OF METERING SYSTEMS

A Direct Access Implementation Plan Report was filed on July 1, 1997.  This report specifies DA service options available to customers and ESPs, and specifies the roles, responsibilities, and commercial relationships that will govern transactions between the UDCs and other market participants.  Additional details may be contained in the UDC-ESP Metering Agreement that must be submitted for CPUC approval.  This section identifies proposed standards and certification processes for metering system equipment, installation, operation, maintenance and testing.

Overview:

The proposed standards were developed to facilitate competition, keep costs as low as possible, minimize unnecessary customer technology investment risks while ensuring the safety, consistency and accuracy of metering systems installation, operation and maintenance.  Although national standards such as ANSI, IEEE, etc. exist for metering equipment, industry standards for many areas of the business; such as procedures for metering installation, operation and maintenance do not exist except those used by UDCs.  The challenge remains to ensure that these standards, once developed, must remain useable and effective in defining the basic requirements applicable to California’s rapidly changing energy market place.  Further, an ongoing standards review process needs to be developed so that any standards adopted now will continue to be refined to reflect changes in technology and the market place on an ongoing basis.

Who Will Be Allowed To Provide, Install, Operate, and Maintain Metering?

UDC

UDCs will provide, install, maintain, and test metering for bundled customers.

The UDC will provide DA metering services for a fee if requested by the ESP or customer.

Qualified parties

Qualified Meter Agents will be allowed to provide, install and maintain metering for DA customers.

Functions performed

There is general agreement with the functions performed, as described below.  However, there are different views on the ownership of metering transformers.  Specifically, there is disagreement on the demarcation point where UDC responsibilities end and competitive services begin.

UDCs will install and maintain all secondary wiring including metering transformers, meter loop wiring, test switches and phasing transformers (additional comments on metering will include the UDCs analysis of this issue).

PG&EÕs position is that metering transformers are an integral part of the meter and should be owned, installed, and maintained by the metering agent who is responsible for metering.

There is a split view on whether metering transformers should be part of metering systems.  Below are comments from different entities:

Southern Energy:  Metering transformers ownership should not provide the owners any competitive advantage in Direct Access.

LADWP:  Believes that UDCs should not be required to provide or maintain assets (metering transformers) used solely for third party metering agent.

ORA and ENRON:  Metering transformers should not be part of metering systems even though they are used solely for revenue metering.

CCES:  Is neutral on issue of meter transformer ownership.

The party who provides the metering transformers shall be responsible for giving metering transformer information (e.g. ratios) to any applicable party.

Qualified parties wishing to install metering must comply with CPUC approved meter installation standards developed in this workshop.

ESPs replacing a UDC meter will coordinate with the UDC prior to replacing the meter in accordance with the UDC/ESP contract.  The contract should include at a minimum the following:

Joint meeting requirements (if any)

Deposition of removed meters

Schedule of work

Meter records

Meter Removal Reads

Notification to all appropriate parties of unsafe or abnormal conditions that do not meet UDC specifications.

Any new customer meter access information including unrestrained animals.

Meters identified as not complying with CPUC approved standards (e.g., safety, accuracy) must be replaced within three calendar days of notification.

ESPs will be responsible to provide UDCs with accurate meter installation and removal information in a time frame consistent with standards described in later sections.

Entry into customer panels behind security seal must comply with UDC policy until state or local standards are adopted.

Proposed Standards for Metering Equipment and Systems

California should utilize applicable existing national standards for Direct Access Metering, a position strongly supported by all workshop participants.  The challenge is to determine which standards should be utilized and within what time frame.  The recommendations are in the following tables.

Table 1:  Existing Standards and Their DA Applicability

| Standards | Applicable for DA? | Proposed Effective Date | Comments |
| --- | --- | --- | --- |
| ANSI C12.1-1995, Code for Electricity Metering | Yes | 1/1/99 |
|  | ANSI C12.4 Mechanical Demand Registers | No |
| ANSI C12.5, Thermal Demand Meters | No |
| ANSI C12.6 Marketing & Arrangement of Terminals for Phase Shifting Devices used in Metering | Yes | 1/1/99 |
|  | ANSI C12.7 Watt-hour Meter Socket | Yes | 1/1/99 |
|  | ANSI C12.10 Electromechanical Watt-hour Meters | Yes | 1/1/99 |
|  | ANSI C12.11, Instrument Transformers for Revenue Metering, 10 kV-350 kV BIL (0.6-69 kV NSV) | Yes | 1/1/99 |
|  | ANSI C12.13, Electronic TOU Registers for Electricity Meters | Yes | 1/1/99 |
|  | ANSI C12.18, Type 2 Optical Port | Yes | 1/1/99 |
|  | ANSI C12.19, Utility Industry End Device Data Table | Yes | 1/1/99 |
|  | ANSI C12.20, 0.2% & 0.5% Accuracy Class Meters (approved but not yet released) | Yes | 1/1/2000 | 24 months from the publication date |
| ANSI C12.21, Protocol Specification for Telephone Modem (not approved) | TBD | TBD | 24 months from the publication date |
| ANSI C12.22, Meter Interface to Network Protocol Gateway (not approved) | TBD | TBD | 24 months from the publication date |
| ANSI C37.90.1, Surge Withstand Test | Yes | 1/1/99 |
|  | ANSI 57.13, Instrument Transformers (70 kV - 230 kV NSV) | Yes | 1/1/99 |
|  | ANSI Z1.4 and ANSI Z1.9, Sampling Procedures and Tables for Inspection | Yes | 1/1/99 |
|  | EEI Electricity Metering Handbook | Yes | 1/1/99 |
|  | MTR1-96 Specification for ISO Applications | No |
| Electric Utilities Service Equipment Requirements Committee (EUSERC) Book | Yes | 1/1/98 |
|  | Cal OSHA | Yes | 1/1/98 |
|  | CPUC GO 95 & 128 | Yes | 1/1/98 |
|  | NEC & Local Requirements | Yes | 1/1/98 |
|  | UDCs Service Requirements | Yes | 1/1/98 |
|  | UDC Standards for metering installations, maintenance and testing | Yes | 1/1/98 |
|  | NIST Standards | Yes | 1/1/98 |

Table 2:  Recommended Standards by Category

| Metering Equipment and Systems | Specifications/ Standards Applied | Proposed Effective Date for DA |
| --- | --- | --- |
| Meter & Metering Equipment |
| Accuracy |

*  UDC Standards

* ANSI C12.20 (approved & not yet released)

1/1/99

| 1/1/2000 |
| --- |
| Reliability | Appendix A and ANSI C12.1-1995, ANSI C37.90 | 1/1/99 |
| Physical Parameters | ANSI C12.1 and UDC Standards | 1/1/99 |
| Communication | ANSI C12.18, FCC Regulation Part 15 Class B | 1/1/99 |
| Data Storage | UDC Standards | 1/1/99 |
| Programming |

*  ANSI C12.13

* ANSI C12.20 (approved & not yet released)

1/1/99

| 1/1/2000 |
| --- |
| Program Accuracy | ANSI C12.19 & UDC Standards | 1/1/99 |
| Certification Testing | Appendix A and ANSI C12.1-1995, ANSI C37.90, NIST | 1/1/99 |
| Instrument Transformers | ANSI C12.1-1995, ANSI C12.11, ANSI C57.13, EEI Handbook, UDC Standards | 1/1/99 |
| Safety | ANSI C12.1-1995, OSHA, UDC Standards, CPUC GO 95 & 128 | 1/1/98 |
| Service Entrance Equipment | EUSERC, UDC Service Requirements | 1/1/98 |
| Metering Installation & Maintenance |
| Quality | Appendix B, UDC Standards | 1/1/98 |
| Meter Mounting | ANSI C12.6, ANSI C12.7, EUSERC | 1/1/99 |
| Inspection and Compliance | UDC Standards | 1/1/98 |
| Metering Records | ANSI C12 Standards and UDC Standards | 1/1/99 |
| Metering Testing | ANSI C12.1, Appendix B, UDC Standards | 1/1/99 |
| Service Connect/ Disconnect | UDC Standards | 1/1/98 |
| Security | UDC Standards | 1/1/98 |
| Safety | OSHA, Appendix B and UDC Standards | 1/1/98 |
| Meter Reading |
| Removal Reads | UDC Standards | 1/1/98 |
| Data Transfer | UDC Standards | 1/1/98 |
| Safety | OSHA, UDC Standards, AB 400 | 1/1/98 |

Metering and Metering Equipment

Meters

Accuracy

DA meter accuracy shall meet the design accuracy requirements of ANSI C12.20 (0.2% and 0.5% Accuracy Classes) due to be released in late 1997. Until that time, the meter shall meet existing UDC meter accuracy requirements of 0.3% for solid state meters and 0.5% for electromechanical.

Meter installations will have their wiring and billing constants verified by UDC qualified meter personnel at the UDC option.

In-service meters must comply with proposal requirements in Appendix A.

Reliability

All new meters shall meet the certification testing requirements approved by the CPUC (see Appendix A).

Meters and Interval Data Recorders purchased for DA customers must have a minimum three year manufacturer warranty.

In-service meters shall have a maximum failure rate of 2.0% per calendar year and a design life of at least 15 years.  If the annual failure rate of an in-service meter type exceeds 2.0% in any particular year, that meter type shall be deemed unacceptable and will be disqualified for further purchase for Direct Access.  All such meters already in service may continue to be used.  In order for a disqualified meter type to be re-qualified for Direct Access, it shall be considered as a new product and must go through the DA certification process.  The failure rate is defined as the ratio of the number of annual failed meters to the total in-service meters by manufacturer and model.

Voltage and Current Rating, Form or Physical Parameters

Must meet ANSI C12.1 requirements and the UDC requirements for supplied voltage, current, form, service entrance, and the applicable CPUC approved Rules for the Sale of Electric Energy, Rule 2, requirements.

Communications

Meter agents shall utilize communication systems and interfaces that are in compliance with FCC Regulation, Part 15, Class B.  If the customer or ESP desires the UDCs meter reading services, the meters shall have the communications interface consistent with the UDCs existing meters and retrieval systems.  All meters must have an optical port (ANSI C12.18, type 2) or other suitable means of on-site or remote interrogation.  The existing meters currently in service with individual UDCs are deemed in compliance with FCC Regulation, Part 15, Class B and will be grandfathered.

Data Storage

Meters or meter systems shall be capable of providing and storing required interval data for a minimum of 35 days.

Programming

The meter agent shall check and verify the program parameters and overall meter operations to assure the meter is in proper working condition or reprogram the meter if necessary.

Meters shall have the register types and programs that meet requirements of ANSI C12.13, ANSI C12.20, UDCs existing tariffs and ESP data requirements.  Data and program shall be retained during power outages and loss of DC back-up system.

Programmable meters are presently available which are capable of being programmed via the following ways:  An optical port, phone line or other communication means such as radio.  If the customer or ESP desires the UDCs meter installation, maintenance and testing services, the meters shall have the programming methodology consistent with the UDCs existing meters and systems.

Program Accuracy

Programs must be written to allow the meter to accurately capture and store all data required for Direct Access and UDC Tariffs.  Programs must produce fully compliant ANSI C12.19 Standard, Direct Access data meeting UDC tariff requirements.

Program verification

Meter Agents must provide evidence of compliant meter programming upon request.

Reliability

Meter programs and all meter data must be stored in non-volatile memory.  Time keeping to be backed up by an appropriate power supply.  Battery life must be 10 years or longer.  The program parameters shall be stored in the memory after programming and retained in the memory during power outage and loss of DC backup source.

Timeliness

Meter program must be confirmed or installed at the time of installation (including setting the clock).

When determination has been made that a meter program has been corrupted, the ESP or UDC shall be notified, and resolution will take place within 2 working days.  If corrections are not completed on ESP meters, the UDC may replace the meter at its discretion and at the ESPs expense.

Each entity who is authorized to program the meter shall have its own ID and password that shall be encoded into the meter once the meter is programmed.

Manufacturers’ (Vendor) and Meter Agent Responsibilities

Meter Agents must provide evidence of meter or metering device compliance with CPUC approved standards (See Appendix A for test requirements).

Evidence of certification shall be prominently displayed on the meter.  This evidence shall include the date and standard used for certification.

Meter manufacturers and/or vendors shall meet credit, quality, and business qualifications as defined by meter agreements as filed in the Direct Access Implementation Plan.

Certification Testing

It is agreed that certification is needed and should be specified and enforced by the CPUC or State agency.  The certification should be performed by approved or certified facilities with equipment traceable to NIST Standards.  Certification processes must be developed, and meters need to be identified as certified via consistent approved labeling.

Meters must conform to ANSI C12.1 certification test requirements and to the one supplementary test described in Appendix A.  All of these tests will be performed in accordance with the clarifications also described in Appendix A.  When published and applicable, any additional certification tests described in ANSI C12.20 will also be required.   Efforts will be taken to make any tests that are included in this addendum, which are not currently defined by ANSI, part of these national standards.

Meters certified and approved in accordance with these test requirements will be placed on a centralized list of meters that can be used for Direct Access service.

Metering equipment including meters, metering transformers and ancillary devices currently used and installed by UDCs are deemed DA compliant and therefore will be grandfathered.  Otherwise, metering equipment shall be certified to meet the following certification requirements as specified in the CPUC-approved metering standards:

Certification testing to prove equipment is safe, reliable and accurate

If applicable, shop testing to prove equipment is operational as specified by the vendor

If applicable, field testing and evaluation requirements to prove equipment is safe, reliable and accurate under actual field conditions.

The ESP/Meter Agent should have  the applicable business licenses to conduct business in the UDCs territory.

The meter agent or ESP shall maintain metering equipment information, all test results, and equipment removal records to include reasons for removal (including failures).  The ESP or Meter Agent will keep this information current and will submit it to the CPUC at the end of each calendar year.  This information will include total metering equipment in service, new, removed, failed, etc., as required by the CPUC.

Liability and Financial

Meter Agents are responsible for damage to customer property or injury to personnel when a non-UDC person performs metering work on UDC or customer equipment.

The UDC recognizes in its agreement with the ESP that all sub-contracted work (including metering) will be the responsibility of the ESP to ensure safety, accuracy, quality and reliability.   Any re-work performed by the UDC will be billed to the ESP.

Enforcement Provisions

ESPs/Meter Agents who fail to provide meters per CPUC standards may result in disqualification from supplying meters for Direct Access use.

Metering Transformers

Metering transformers and auxiliary devices are tested in accordance with ANSI standards (ANSI C12.1, ANSI C12.11, & ANSI C57.13), EEI Electricity Metering Handbook and local UDC requirements.

All instrument transformers shall be 0.3% accuracy class.

Safety

All meters and installations shall meet UDC safety requirements which include ANSI C12.1 and Appendix A safety tests.

Meter installers shall follow manufacturers’ guidelines regarding meter safety

Optical Port type 2 must be isolated from any energized meter parts.

Service Entrance Equipment

Service and metering equipment must meet local UDC published electrical service and metering requirements based on Electric Utility Service Equipment Requirements Committee (EUSERC).

Other Requirements

If a calendar is required, it must include all legal holidays, daylight saving time, season changes, leap years and the new millennium.  At time of program calendar must be at a minimum of 10 years.

Installation and Maintenance

Installation And Maintenance

Quality

Meter installation and maintenance work shall be in accordance with Appendix B included in this document.

It is understood that the approved meter installation and maintenance standards must reflect present day minimum requirements for the industry.  Therefore, the existing practices must be carefully reviewed to ensure that the legacy processes remain valued and are essential to perform California’s DA metering work safely and consistently, in lieu of any other available National Standard for installation and maintenance work.

Mounting

The standard for mounting DA meters shall meet ANSI C12.10 approved standards.  Existing installed meters that otherwise meet the requirements of DA that have different mounting configuration shall be deemed acceptable.

Some market participants do not agree with this limited approach and would favor presently non-standard installations.  Our recommendation is that present non-standard installation methods be adopted through consensus national standard processes, such as ANSI, prior to use.

Connections to be used for mounting DA electric meters must be safe and meet national, state and local codes, including EUSERC.

Code, Ordinance, and other Legal Requirements

Meter installations may be subject to permit and inspections by the local authority having jurisdiction for compliance with local codes and ordinances.  The local authority having jurisdiction shall release all inspection clearances to the UDC.  ESPs may not install metering on new installations without approval from the UDC.

All Meter Agents and their employees shall be knowledgeable of, follow and comply with applicable federal, state and local code and inspection requirements.

The placement of meter communication output devices, other than within the meter, must comply with UDC service requirements.

Meter installation inspection:

The UDC, at their discretion, will do an inspection test or verification on new installations of ESP/third party meters. On existing UDC installations, meter change outs must be coordinated with the UDC.  Meter installer is responsible for notifying customer and UDC of required repairs. When using multi-ranging voltage meters, the service voltage should be prominently displayed near the meter, (e.g. a permanent sticker).

Records

In order to promote effective transitions and interchangeability of meters between ESPs and UDCs, it is proposed that a state-wide standard for numbering meters be developed.  Another option might be possible for manufacturers to develop a simple method of replacing meter numbers on their in-service meters.

Must be compatible with specific UDC system limitations.

Meter numbers must be assigned prior to installation.

Manufacturers shall provide meter and metering device information as requested by UDCs/ESPs.  The ESP is expected to return all metering information for meters they are responsible for.  At the discretion of the UDCs, the UDC may also maintain this information in their meter information systems.

Meter data includes UDC/ESP requested meter test data and meter nameplate information as specified in ANSI C12 standards.

Metering transformer data includes utility number, manufacturer serial number, test date, ratio correction and phase angle factors at both full load and light load.

ESPs will provide UDC with requested meter data (i.e. form, volts, Kh, Kt, Ke, register functionality, memory size, etc.).

SDG&E wants this data prior to the meter set.

PG&E and SCE want this data within two days of the meter set.

Universal Identifier:  MDCS also recommended that a statewide standard be evaluated and implemented that would define each usage point.  RSIF has accepted responsibility for creating this identifier, (Southern California Gas).

Testing

The Meter Agent is responsible for maintaining and testing the meter.  Testing procedures and schedules will be in accordance with Appendix B.

Customers, ESPs or UDCs may inspect third party metering installations or observe third party meter agent performance.

Based on the findings of these observations, if more than random infrequent errors are observed, increased observations or inspections (up to 100%) may be performed by or on behalf of these parties at the Meter Agents’ expense.

A meter test plan will be established by all Meter Agents for all in-service DA meters.  Meters will be tested in accordance with standards and schedules adopted by the CPUC.

Existing CPUC compliant test plans in use by the UDCs are deemed acceptable.

Initially the frequency for testing will be (1) consistent with current UDC policy, or (2) in accordance with requirements defined in ANSI C12.1.

Solid state meters that are not recommended by the manufacturer to be re-calibrated in the field must be replaced if found to be inaccurate or defective.

After a meter accuracy/performance test is performed that results in the confirmation of an accurate and properly working meter, a test report shall be submitted to the UDC by third parties within 10 working days of the performance test. Meter accuracy/performance tests that reveal an inaccurate or defective meter will require immediate notification to the ESP, UDC, and customer; and the meter must be repaired or replaced within three calendar days.

The meter accuracy of all meters for use in Direct Access shall be tested prior to shipping or selling.  This test data shall accompany the meter prior to installation.

An on-site installation test, including a meter accuracy test will be conducted for all new transformer rated installations and whenever wiring or transformer rated changes occur. The meter agent shall test the accuracy of the meter if requested by the customers.  The customer shall have the opportunity to observe the next regularly scheduled meter test or pay to have an additional meter test completed on a more accelerated basis.  The meter accuracy test results shall be submitted to the UDCs along with the meter accuracy test results provided by the meter manufacturer.

Communications Test

A communications verification test shall be performed during the installation procedure per Appendix B.

The ESP must provide certification documentation of all installed DA meters to the UDC within ten working days from the time of installation.

Service Connect/Disconnect

UDCs will be solely responsible for service connections and disconnections.  ESPs/Meter Agents must coordinate with the UDCs to accomplish this function.

Security

A security code password shall be required to prevent access to programmable registers for the purpose of unauthorized changing of the program and stored data.

All Meter Agents must develop programs to safeguard these passwords.

A meter installations shall be secured with a UDC approved seal or ring-type security device as a minimum.  If additional security is warranted, the meter agent shall coordinate with the UDC.

All Meter Agents and UDCs will develop and implement energy diversion programs and train their employees on the identification, reporting and documentation of energy diversion occurrences.

Existing UDC energy diversion programs are deemed satisfactory for this requirement.

ESPs/Meter Agents and UDCs are responsible for reporting energy diversion as it is observed.

Responsibility for correcting diversion belongs to the party responsible for the facility/equipment directly involved in the diversion (e.g. meter diversion-Meter Agent, service entrance - UDC).

Safety

All meter installations must comply with Cal OSHA, and safety rules as described in Appendix B.

Other Requirements

The UDCs will require a “Hold Harmless” and “Indemnify” agreement for accidents or damage caused by an ESP or their Meter Agent.

Meter Reading

Removal reads

Prior to removing existing meter, a kWH (also kVARH if applicable) meter read will be recorded and provided to the meter owner.  If the UDC requires IDR, peak demand or TOU meter reads as well, the ESP/Meter agent must coordinate the meter removal with the UDC.

If the UDC or meter owner determines that a joint meet is not required when removing the meter, the ESP must return the meter to UDC or meter owner within 48 hours, in working condition,  or pay appropriate charges.

Data Transfer

Data transfer is described in Chapter VI.

Safety

Meter Reading safety issues are described in Chapter VI.

Meter Installation, Maintenance, and Testing Qualification Process For Meter Agents

Technical Certification

All workers who will install, maintain or test DA electric meters must have successfully completed the requirements of a State approved/certified training program and become State certified.

This training and certification progress will be administered by the State Department of Industrial Relations.

The CEC believes that this certification program would be more appropriately positioned in the California Department of Food and Agriculture, Division of Weights and Measures.

Workers who desire to perform this DA metering work and have not received prior California certification may apply to this state agency for consideration for advanced placement in a certified training program or eligibility for certification testing based on relevant work experience, knowledge or training received elsewhere.

UDC employees who have completed the appropriate established utility metering training programs will be considered qualified for this work.

Qualified personnel must carry and produce their certification card upon customer, auditor, ESP, or UDC request.

Certification of meter workers may be revoked by the State for failure to comply with CPUC policies.  Customers, ESPs, or UDCs may file complaints with the State to investigate non-compliant work for consideration to suspend licenses to perform metering work.

The UDC,  as well as other qualified parties, may at their discretion, offer training for these individuals, once a curriculum has been approved by the state.

No such certification program presently exists and must be established by the State before third party meter employees will be qualified and available to perform DA metering work.

It is further recommended that the CPUC coordinate this process to quickly achieve this goal.

Auditing and Enforcement

No auditing or enforcement program presently exists for DA metering activities and must be established by the State to ensure overall compliance and market place effectiveness.

It is further recommended that the CPUC coordinate the development of these processes quickly.

STANDARDS FOR THE INSTALLATION, OPERATION, AND MAINTENANCE OF METER READING SYSTEMS

This section identifies proposed standards and certification processes for meter reading systems.

Meter Reading

Who can read meters?

UDC

The UDC will provide meter reading service for bundled customers.

The UDC may also provide unbundled meter reading services.

Other Qualified Parties

Qualified ESPs may read DA meters or ESPs may contract with other qualified parties to read DA meters

ORA: If customers, ESPs and UDCs mutually establish a customer-read program in which customers read their own meters and report their usage monthly, such readings shall be considered an actual meter reading by the ESP and the UDC for billing purposes, subject to routine editing and validation by the MDMA.  However, the customer-read program shall ensure that the meters of customers on a customer-read program are independently verified at least every 12 months to verify the accuracy of the meter records.

Interface to Other Qualified Parties

ORA:  Each Scheduling Coordinator will be responsible for the collection of end-user meter data and for ensuring that the data supplied to the ISO meets the requirements of the ISO Tariff.

ORA:  The ISO will enter into meter service agreements with Scheduling Coordinators responsible for providing end-user meter data to the ISO, specifying that Scheduling Coordinators will require the same meter requirements to those set forth in the ISO Tariff.  These meter service agreements will set out the security and data validation procedures that the Scheduling Coordinator will apply to the hourly and cumulating meter data, in order to comply with the ISO Tariff.

Functions Performed

The ESP providing MDMA services is responsible for all of the following functions.  In order for the market to function effectively on 1/1/98, a single party shall be responsible for coordinating/managing all of the following functions.  This means separate entities can be used to perform any or all of the following functions (not entity dependent).

Manage meter reading schedule

Read and retrieve meter data

Validate, edit and estimate meter data

Calculate usage

Format data

Store data on MDMA server

Manage data on MDMA server

Manage data access to MDMA server

Meter/device management (i.e., when the meter/device was installed, what the device type is, what the service history has been, what the service parameters of the meter are, etc.)

The ORA believes that these functions can be the responsibilities of each party performing them.

Proposed Standards for Meter Reading Systems

Meter Reading

100% of data passed to the validation process will be based on actual meter registration.

Meters shall be read in-order to meet over all data delivery performance requirements (timeliness and quality).

Safety Requirements of Meter Reading Agents and Employees

Comply with AB 400 (False Representation Public Utility or District Employees Law).

Comply with Cal OSHA requirements.

Comply with approved safety requirements.

Report meter, safety, and hazardous conditions to UDC and ESP.

Maintain site specific information and provide to UDC and ESP.

Access to meter locations must be compatible with UDC guidelines.

Timeliness

Meters must be read at least monthly.

Meters must be read to ensure overall data delivery timeliness and quality (as described in Chapter VII).

CEC:  ISO and CPUC requirements only dictate monthly reads at this time.  Daily reads would provide benefits in 2 ways: (1) reducing the length of intervals where meter data is bad without being detected, and (2) providing access to the meter data to support rapid access applications such as load forecasting (load scheduling to the ISO and load bidding to the PX).

Data transfer systems between meter collection and MDMA Server.

Will not be specified in this report.

Consensus opinion is that communication technology should not be defined and can be installed at the discretion of the Meter Reading Agent.  Selected technologies should comply with Open Architecture definition set forth earlier in this document.

Data transfer must insure data delivery in compliance with performance standards.

ORA:  The data transfer capabilities in the UCA specification, the suite consisting of ANSI C12.18, C12.19, C12.20 and C12.21, IEEE 1390 telephone standard provide a wide range of data transfer capabilities for both existing and future needs and including both local and wide area networks, making the existing set of standards suitable for Direct Access.

Accuracy.

See comment, VI.B.1.d)(ii)

·    CellNet:  Meter reads must be accurate to within 1.0 kilowatt hours of actual usage, subject to CPUC Rule 17 (for PG&E and SCE) and CPUC Rule 18 (for SDG&E).  The CPUCs comfort with the use of these standards was indicated in D.97-06-060 (Conclusion of Law 20).

Reliability

See comment, VI.B.1.d)(ii)

·    CellNet:  For monthly data, no more than 1.0 percent of meter reads can be estimated.  For hourly data, no more than 5.0 percent of hourly date can be estimated (CellNet is comfortable with a higher standard, but defers to the majority opinion expressed in MADAWG effort.)

AMR Standards

· 	Southern California Gas:  AMRA (AMR Association) /IEEE SCC.31 Standards Committees have been developing a complete set of AMR standards which are applicable for services including electric, natural gas and water.  The AMRA standards shall be fully adopted for Direct Access Implementation.

Data Management

Thirty six months of raw meter read history must be retained by the meter reading agents and made available to appropriate parties upon request.

·	CellNet:  Retention period - 30 and 60 day storage on-line for the current and previous billing period.  Archival off-line for 5 years.

Security measures shall be put in place to ensure that only authorized users will have access to their data.

Inspection and checkout of meter reading prior to placing in service

All meters and communications systems shall be inspected at the time of installation or maintenance in accordance to Appendix B to ensure they are capable of providing reliable metering data to market participants.

Meter reading agents shall verify any new meter reading system with their respective UDCs to ensure the meter read data delivery and quality is met.

Starting November 1, 1997, ESPs wishing to provide MDMA services can begin submitting application to local UDCs.

These applications will be processed on a first come first serve basis

On or before 1/1/98, UDCs will begin administering MDMA acceptance tests.

Upon successful completion of the MDMA acceptance test, the meter reading agent will be recommended by the UDCs to be certified by the CPUC to provide MDMA services.

UDC costs for providing this service shall be paid for by the ESPs

Changes in MDMA hardware, software, or firmware methodology shall require additional acceptance tests.

For all customers 500 kW and larger the following acceptance test of the meter and/or meter reading system will be required:

Between one day and five days after installation of the meter, the MDMA must confirm that the system is working properly and that the data gathered is valid.

Certification Process For Meter Reading Vendors

Vendor certification

These specifications are under serious review and maybe partially or completely replaced by Appendix C.

Meter reading agents who currently perform meter reading in California will be grandfathered to perform meter reading work. Otherwise, meter reading agents shall meet the following certification requirements:

Meet UDC/ESP credit worthiness requirements.

Obtain state and other local licenses to perform meter reading work

Bonded

Registered to conduct business in California

Meets requirements outlined in sections VI.A. and VI.B. above.

Ability to provide data to the MDMA server.

Certificate of Insurance

Credit Rating

Bonding

Vendor Employee Requirements

All personnel reading meters must successfully complete a meter reading training course provided by the meter reading agent using appropriate meter reading training tools.

CellNet:  ESPs are responsible for any metering activities they elect to perform, and are given permission by the CPUC to perform.  The meter reading company, whether the ESP or its agent, must be certified.  Certification is done by having an independent firm review and test the meter reader's processes and performance.  The processes must ensure repeatable and reliable performance, including consideration for customer impacts (e.g. training of human meter readers in customer contact procedures).  The performance must meet the timeliness, accuracy, and reliability standards specified in this standard.  A certification report must be filed with the CPUC Energy Division and will be available for public review (excluding proprietary information).

Enforcement provisions

Failure of a meter reading agent to comply with these standards may result in de-certification to read meters.

Other

Schlumberger:  All market participants need to be held to the same meter reading performance standards

Service providers must have emergency and/or disaster plans and backup systems.

STANDARDS FOR THE INSTALLATION, OPERATION, AND MAINTENANCE OF METER DATA MANAGEMENT SYSTEMS

This section identifies proposed standards and certification processes for meter data management systems.  The MADAWG Technical Subgroups have focused on the MDMA server specifications and their most recent status report is attached as Appendix D. We are inclined to accept this subgroupÕs recommendations for the MDMA server.

Who Will Be Allowed To Provide, Install, Operate, And Maintain Meter Data Management Systems?

UDC

Qualified Energy Service Providers (ESP)

CEC:  The ESPs should not be allowed to install, operate, or maintain meter data management systems.  ESPs can retrieve data from the MDMAs and do not require direct meter communication system access.

Other Qualified Parties

Interface to Other Qualified Parties

ORA:  Scheduling Coordinators will provide the ISO with end-use meter data for all of the end-users served by the Scheduling Coordinator no later than the day required by the ISOs settlements process (within 38 days of the energy usage).  End-use meter data will be either (1) an accurate measure of the end-user's actual consumption in each settlement period, or (2) for end-users connected to a UDC Distribution System, a profile of that consumption derived from an accurate cumulative measure of actual consumption and an allocation of that consumption using the applicable, authorized load profile.

CEC:  Meter Agents should not be allowed to install, operate, or maintain meter data management systems.  However, they may need to access some information directly from the meter.  They should not be able to access any meter data not consistent with their business responsibilities.

Proposed Standards for Meter Data Management Systems

Interval Data Transformation

Standard and approved quality checks on raw meter read data will be performed. These checks include validating, estimating and/or editing consumption data to render it validated where required by market participants as defined in this section.

CCES:  The MDMA is responsible for editing, validation, formatting and posting "raw" meter data obtained from meter reading entities for delivery to the UDC, ESP and other end-use customers.  The following are basic rules: a) where raw data is available with incomplete entries or entries whose time stamps do not match users requirements, the MDMA may transform data using any statistically valid method that produces interval data accurate within 2% at a 95% confidence level.  Such data may be reported as estimated or corrected data.

Data will be complete for each given time period.  Missing or incorrect data will be estimated using approved and documented algorithms.

The MDMA will fill in gaps with estimated data.

Greater than two continuous hours of missing interval data.

Compute the average daily profile by using the days from the current usage period and as much historical data (up to 90 days) as required to select three complete days (which were not estimated) corresponding to the day of week or holiday with missing data.  If no historical holidays exist, use Sundays. The historical data used should be that data immediately preceding the usage period, regardless of seasonal crossover.

Estimate the missing data by applying the appropriate average daily profile to fill the missing intervals.

Two hours or less of contiguous missing interval data.

Use the point to point linear interpolation method to estimate the missing data where there is a gap in the data.  If the gap occurs at the beginning of the span, use the last interval from the historical data as the first point, if the historical data is available and the interval data is not estimated. Otherwise, use the second point (the nearest good interval data) as the first point (i.e., a flat load).  If the gap occurs at the end of the span, use the first point as the second point (i.e., a flat load).

Consumption data will be validated and corrected using the following approved and documented validations and algorithms:

Spike Check

Spike checks are to be performed on a calendar day basis (i.e. 24 hour period based on PST time).  The highest interval cannot exceed the third highest for that day by more than 180%.  In the case of partial days, the spike check should be performed for the adjacent 24 hours (i.e. the 24 hour period spans over two days).  If the data starts at 20:00, the first days spike test should be performed from 20:00 to 20:00 on the next day, and the second day should be performed from 0:00 to 24:00.

If a spike is found, the MDMA may try repolling to verify the spike did indeed occur.

Spikes in the data must be set to missing and the missing intervals estimated according to the missing data estimation rules.

High Low Average Daily Usage Check

This check is no longer at the interval level but at the billing cycle level for settlement quality.

Using the last year’s data for the same billing month, compute an average day usage (historical average daily total consumption).

If last year's data is not available, use the last billing cycle of historical data.

If there is not enough historical data, the High / Low Average Daily Usage check is not valid.

Using the current span of data, compute an average day usage (current average daily total consumption).

When checking for the reasonableness of the current average daily total consumption use plus or minus 50% of the historical average daily total consumption.

If the current average daily total consumption is outside these limits, the data should be verified by the MDMA (i.e., repolling, meter test, etc.).  If the data comes back the same after verification, the data should be flagged as verified.

Sum Check

The sum check compares the energy use recorded by the meter to the energy use recorded by the pulse recorder over the same time period to ensure that the difference is within an acceptable range.

The difference must be less than or equal to one meter multiplier, where the meter multiplier is defined as the constant used to convert the meter reads to kWH.

If the difference is greater than one meter multiplier, the data should be verified by the MDMA (i.e., repolling, meter test, etc.) looking for possible meter configuration problems (wrong pulse multiplier, meter multiplier, etc.).  If the data comes back the same after verification, the data should be flagged as verified.

For non-redundant solid-state meters the sum check needs to be performed before any missing or spike data is changed.  Running the sum check after estimating data, guarantees that the meter read and interval data will not balance (even though it may still be within 1 meter multiplier).

For mechanical dial meters, the sum check is valid whether or not any data is estimated.

Hardware Checks

MDMA must ensure that the collection (polling) device is synchronized to the national time standard daily before data collections.

The time tolerance check verifies that the time difference in the meter and the collection device (i.e., hand-held) is within 180 seconds for a 30 day period.

A meter with a time difference that is less than 180 seconds is acceptable.

The MDMA must flag a meter with a time difference that is greater than 180 seconds and synchronize the meter.

If the meter has failed the time tolerance three consecutive months, the MDMA must set the quality indicator to “Meter Needs Maintenance” and notify the meter owner so that the meter can be inspected.

The interval tolerance check determines that the number of expected intervals equals the number of intervals received, otherwise a time drift occurred.

A meter with a time drift of plus or minus 1 interval is still acceptable.  However, the MDMA must prorate and flag the data by redistributing the data throughout the correct number of intervals.

If a meter has a time drift of plus or minus 4 intervals, more than likely either the meter or the collection device is not correctly handling the current time zone (PST versus PDT).  The MDMA must contact the meter owner to resolve the problem and make the appropriate time changes in the data.

If a meter has any other time drift which is no more than plus or minus 5 intervals (i.e., data is salvageable), check for time zone problems, and prorate and flag the data by redistributing the data throughout the correct number of intervals.  The MDMA must set the quality indicator to “Meter Needs Maintenance” and notify the meter owner so that the meter can be inspected.  Meter maintenance will determine whether the meter needs to be replaced.

If the data is not salvageable (the time drift is greater than plus or minus 5 intervals), the data must be set to missing and the missing intervals estimated according to the missing data estimation rules.  The MDMA must set the quality indicator to “Meter Needs Maintenance” and notify the meter owner so that the meter can be inspected.  Meter maintenance will determine whether the meter needs to be replaced.

The pulse overflow check determines whether the meter was unable to record all the pulses in a single interval.  If this check fails, it is usually because of a bad pulse multiplier or incorrectly sized equipment.  The data must be set to missing and the missing intervals estimated according to the missing data estimation rules.  The MDMA must contact the meter owner to resolve the problem and make the appropriate changes.

KVARH (If Collected) (additional estimation rules)

If the kWH channel has zero consumption and for the corresponding time the kVARH channel has registered consumption, the kWH data must be set to missing.

If the current average power factor is consistent with the historical average power factor for the customer, and the kVARH data is consistent with historical kVARH data, estimate the kWH usage by using the historical average power factor and the corresponding kVARH data.  Otherwise, use the missing data estimation rules.

Calculate the current average power factor by ignoring the missing intervals and by using the total consumption of the good kWH data and the total consumption of the good kVARH data.  Validate that the current average power factor is within plus or minus 50% of the historical average power factor (using last three billing periods).

Validate that the total consumption of the current kVARH data is within plus or minus 50% of the historical average kVARH usage (using the last three billing periods)

Validation results will be stored with and at the same interval frequency as the source data.

Estimated usage data will be identified.  The estimation technique will accompany this identification.

Usage data will be translated to and maintained in the agreed upon MDMA data exchange format, (See Appendix E).

CEC:  Common data formats proposed in MADAWG must be utilized by all participants needing to exchange settlement quality validated consumption data commencing on 1/1/98.  Reliance upon interim data format necessary to permit implementation on 1/1/98 should not preclude implementation of improved standards recommended by a continuation of stakeholder discussions concerning data exchange.

Usage data will be represented in the appropriate Engineering Units at the same interval length that was captured in the meter.

Accuracy

Meter clocks will be maintained on Pacific Standard Time within +/- three minutes of the National Time Standard

Usage data will be accurate unless otherwise indicated.  Data known to be inaccurate or missing will be estimated and flagged as estimated.

No more than 10% of the accounts will contain estimated data.

Reliability

Timeliness

CellNet:  Meter reads suitable for use in billing must be available to the Meter Data Server within 12 hours of collection from the meter (this requires, for example, that a meter read collected at 7 a.m. be posted to the Server by 7 p.m., so a human meter reader has sufficient time to complete his or her route, then upload the data to the Server).  This requirement is needed to ensure that billing can be completed in a timely manner and UDC and ESP cash flows are not adversely affected by the implementation of competitive metering.

First Point believes that the precision should be measured against data and not accounts.

Interval Data Availability Standards

80% of all the usage data will be made available within 2 days of the scheduled read date of the meter.

SDG&E requires that 80% of all usage data be available on the scheduled read date of the meter.

90% of all the usage data will be made available within 3 days of the scheduled read date of the meter.

SDG&E requires that 90% of all usage data be available within 1 day of the scheduled read date of the meter.

100% of all the usage data will be made available within 5 days of the scheduled read date of the meter.

Non-Interval (Monthly) Data

This section is currently under development

Data Transformation Formats

See Appendix E

EPRI:  IEEE/ANSI defines meter data elements in a consistent manner and enables different meter vendors to provide meter data to users in a consistent way.  The UCA meter data format presents meter data in an object oriented manner enabling irrespective of the underlying data communications link or vendor.  The UCA meter data format is extensible, i.e., additional data elements can be added to the format at a later point in time without major changes in client software.  This consistent format mechanism is very important to Direct Access as it assures interoperability among entities and competition by enabling a consistent meter data format.

Data Storage

Retention Period

After data is posted to the MDMA server it will remain there for three days.

Data will be recoverable for at least three years.

Format: Data posted to the MDMA server will be stored in the MDMA data exchange format.  See Appendix E

EPRI:  IEEE/ANSI defines meter data elements in a consistent manner and enables different meter vendors to provide meter data to users in a consistent way.  UCA provides a Meter Data Model, which makes the meter data available to a user in an object-oriented format.  This format will enable the user of the data to access the data in a consistent logical manner.  The model is extensible, so additional data can be added without change-out of user software.

Types of data:  All supported data elements will be defined within the MDMA data exchange format.

Power Measurement:  Must not preclude complex data types.  Customers need direct real-time access to the meter.  Multiple communication channel to the meter will be required.

Data Transfers

Timeliness requirements: The MDMA will provide an infrastructure that supports retrieval of all data currently available to a MDMA client within a two hour window.

Communications methods: Communication of usage data will be over Internet addressable MDMA servers.

Communications protocols: Usage data will be exchanged using the HyperText Transfer Protocol (HTTP) over TCP/IP Communications protocols

ORA:  The communications capabilities options in the UCA specification, the suite consisting of ANSI C12.18, C12.19, C12.20 and C12.21, and the IEEE 1390 telephone standard provide a wide range of communications capabilities for both existing and future needs and including both local and wide area networks, making the existing set of standards suitable for Direct Access.

·	ORA:  EPRI has developed the UCA communications architecture to serve the needs of the electric, gas and water utility industries.  The architecture consists of a suite of data communications protocols including protocols which are suited for the meter reading needs of Direct Access in California.  All of the included protocols are full International Standards.  One application layer protocol, the Common Application Services Model is being forwarded to the IEEE Standards Coordinating Committee (SCC) 36 and is expected to be balloted and approved within one year.

·	CEC:  No single communication protocol appears to be best suited to serve all of the customers within the diverse service areas of the three IOUs.

·	Workshop comments suggest that WENET should be investigated as a potential transfer protocol.

Security

The Secure Sockets Layer (SSL) data encryption standard will provide data transmission security

MDMA clients will be authenticated using SSL.

Authenticated MDMA clients will have access only to usage data for which they are authorized.

EPRI:  UCA has incorporated a multi-level security mechanism that will allow restrictions to views of data elements.  The Common Application Services model security model embodies a role based mechanism that provides for the secured "views" that achieve access based on the validated "role" of the communicating entity.  The model ensures that data is made available to only individuals that have proper authorization to gain access to that data.  In addition, UCA supports authentication and the use of several encryption mechanisms.

Meter Records

Meter number assignment:  A meter numbering standard that provides for unique identification of all customers, meters, ESPs, meter locations, and MDMAs is required and will be developed.

Access to MDMA Server

Meter Data Management Agent must provide access and direction to all qualified parties.

Certification Process For Meter Data Management Vendors

(See Appendix C)

Enforcement provisions

ENRON, Meter Installation, and Meter Data Management Auditing Process required for ESPs and UDCs.  All UDCs agreed with this concept.

# Text boxes

Meter Data

Communications

Meter Socket

MDMA Server

Open Architecture

Meter

Market Participants

(UDC, ESP, ISO, etc.)