MDMA Users Group - Technical Conference Call, 11/4/97

Participants:

Tom Lofgren - Cellnet

Kathy Smith - ABB

Steve Sanford - SCE

Sherman Severin - First Point

Greg Lizak - Itron

James Harry - Schlumberger

Scott Thorton - Pacificorp

Nia - Pacificorp

Evelyne - Pacificorp

Suzie Lucking - Pacificorp

Contact for CMEP issues - David Harrison at PG&E - dlhf@pge.com

Changes recommended for the CMEP specification

- Add “ADJUSTED” to MD01.9 for sending adjusted readings, and the associated data should include at least one interval with an “A” on it

- In MD01.13, monthly reads will be indicated by an 01 in the MM porton of the interval field, and each data value (usually just one) will have the actual date and time of the reading

- In the units description on page 5, PULSE should be replaced by KWHPULSE, KVAHPULSE, KVARHPULSE and GASPULSE so that different pulse channels can be identified

- In MD02.12, values should be added for all seasons to be more generic.  Add “P” for Spring, “F” for fall

- If pulses are reported, the MD01.12 should be the combination of the KH and the PT/CT multipliers

- Use Dun and Bradstreet number for MD01.3

- MD01.4 can be blank if MDMA has not assigned their own account number

- MD01.5 should also be Dun & Bradstreet number

Questions to be answered on the CMEP specification

- For monthly meters, should the reported values be register readings or monthly usage?

- Should the MDMA report a closing reading for a meter that got pulled out during the billing period, or is the closing read reported with thte meter changeout transaction sufficient?

- How does the MDMA know how to report TOU readings and what labels to attach to each reading?

VEE Comments and Questions

- Raw data is defined as pre-VEE data, and it could be either raw data from the meter or converted.

- VII.B.2 - we need to come up with a standard list of holidays for VEE purposes - not UDC or ESP specific

- VII.B.5.c.ii - For the sum check test, the starting and ending intervals can be prorated in order to match the time of the register readings.

- VII.B.5 - It seems like it should say interval data, not consumption data

- VII.B.5.a - Is the spike check done on pre-estimated or post-estimated data?

- VII.B.5.a.i - Does the 24 hour period go from midnight to midnight local time, or can any 24 hour period be used?

- VII.B.5.a.i - If the sum check passes but a spike exists, can the spike be reported as is, or should it be marked as missing and then estimated?  Would this then be marked as estimated data even though it might not be?  If you repoll the meter, and the spike really exists, can you leave it in there as non-estimated data?

- VII.B.5.b.ii - We assume that the historical data used for this check is validated data, not raw data.

- VII.B.5.b - We assume that historical data can be either the sum of validated interval data or register readings.

- VII.B.5.b.v - When is repolling the meter enough, and when is a meter test required?

- VII.B.5.c.iii - If you are off by more than one multiplier and do not or can not repoll the meter, is the whole month marked as missing?  What do you do?  What are the requirements for verification?

- VII.B.5.c.v - What does this mean - do we skip the sum check for mechanical dial meters?

- VII.B.5.d.ii - third bullet - Is the quality indicator meant to be in the CMEP when reporting readings? Or is it just an internal flag to check the meter?

- VII.B.5.d.ii - How do you prorate if time drift has occurred?  We need details from whoever knows.

- VII.B.5.d.ii - If you are more than 5 intervals off, and you have to mark data as missing, which data is marked?  All the data?  Do you add some to beginning or ending of the data stream?

- VII.B.5.e.ii - Is it true that no estimation of KVARH interval data is required?

- VII.B.7 - There are no labels in CMEP to support method of estimation (linear interpolation or historical filling).

- We need a sequence of tests to be defined, and a decision on how much weight to give the sum check.  Does the data have to satsify the sum check in the end?

- We need to have a further effort after 1/1/98 to go through the monthly VEE rules (VII.B.13.d in the MDCS report).

Possible contacts for VEE questions

George Samaniego SDGE - contact person Jim Teeter (619) 654-8399 jteeter@sdge.com

Kris Hardie from PG&E?