# MDMA/MRSP Acceptance Process and Performance Standards

Purpose

Pursuant to Decision 97-______ [the MDCS decision], any ESP wishing to be a Meter Data Management Agent (MDMA) and/or Meter Reading Services Provider (MRSP) must meet certain qualifications in order to perform MDMA and/or MRSP functions. The purpose is to ensure that meters are being read in an accurate and safe manner. This document describes the process by which an MDMA or MRSP is accepted in order to meet this requirement and the ongoing standards and requirements in order for the MDMA/MRSP to be able to continue offering services.

Existing Regulated Utilities

The existing regulated utilities, as of November 1997, are deemed qualified to perform MDMA and MRSP services. All utility employees who have successfully completed the utility’s training programs regarding meter reading, and related safety programs, shall be permitted to carry out the meter reading activities required of an MRSP. All utility employees who have successfully completed the utility’s training programs regarding meter data management (validation, editing, etc.) and entry shall be permitted to carry out the meter data management activities required of an MDMA. The UDCs are not required to perform and acceptance test. However, they must also meet the CPUC-approved standards and requirements for MDMA/MRSPs as enumerated below.

Acceptance Procedure: MDMA/MRSP Services by ESPs and Other Entities

- Written Request. All non-utility entities and ESPs seeking to offer MDMA/MRSP services shall be required to submit a written request to each UDC in whose service territory the ESP or entity seeks to offer such services. The written request shall include the following information: name of the person or entity; business address and telephone number; a description of the requesting party’s experience in meter reading; and a description of what educational and training requirements in meter reading and related electrical safety the MDMA/MRSP will require of its employees before they are allowed to carry out the MDMA/MRSP functions (see document, MDMA/MRSP Qualifications). The UDCs will verify that the request has been received by notifying the MDMA/MRSP in writing within five business days.

- Training Manuals. The potential MDMA/MRSP shall attach all pertinent training manuals and materials which describe the training that all of its employees have received or will undergo before the employee is allowed to perform MDMA/MRSP-related activities. These documents will also describe the MDMA/MRSP’s educational requirements for its employees.

- Acceptance Test. The MDMA/MRSP must successfully carry out and document the MDMA/MRSP Acceptance Test (see document), and provide the test report to the UDC along with the training manuals.

- UDC Review. Upon receipt of the request, the UDC shall review the written documents and any attached materials, and to confirm in writing with the potential MDMA/MRSP whether the proposed educational and training requirements are comparable with the UDC’s requirements and whether the MDMA/MRSP has carried out the required acceptance testing. If the UDC states that the proposed MDMA/MRSP’s educational and training requirements are not comparable, the person or entity may file a formal complaint with the CPUC with regard to such qualifications. The UDC must accept the proposed MDMA/MRSP’s acceptance test report unless the test report shows the test was not passed successfully, the test was done improperly or was incomplete, or the UDC finds another material reason to reject the report. Unless the reason for rejection was failing the test, the MDMA/MRSP may immediately correct the deficiency and resubmit the test report. If the MDMA/MRSP failed the test, the MDMA/MRSP must wait three months before resubmitting a new test report.

If the UDC states that the proposed MDMA/MRSP’s educational and training requirements are sufficient and the MDMA/MRSP Acceptance Test has been performed, passed, and documented, then the MDMA/MRSP may begin offering MDMA/MRSP services so long as it has signed a valid MDMA/MRSP Service Agreement with the UDC. Once one UDC has accepted the MDMA/MRSP’s educational and training requirements and MDMA/MRSP Acceptance Test, the other UDC’s will consider the MDMA/MRSP’s educational and training program to be adequate without performing their own, independent review.

Ongoing Acceptance

- New Acceptance. Submission of a new written request for acceptance, including copies of documentation and a complete test report, is required in the following circumstances:

  - If the MDMA/MRSP discontinues service for any period of time exceeding one month, regardless of reason

  - If the MDMA/MRSP replaces its current technology with entirely new technology, such as converting from one communications technology to another, or makes other changes to its technology or systems that significantly affect the MDMA/MRSP's ability to meet the performance standards. Such resubmission of a request for acceptance is required within 30 days of implementing such new or changed technology.

- Disaster Recover Test. The MDMA must test its disaster recovery plan every two years and provide a copy of the test report to each UDC in whose service territory the MDMA provides MDMA services

- Performance Standards. The MDMA/MRSP must meet certain performance standards and provide a monthly report to each UDC in whose service territory the MDMA/MRSP provides MDMA/MRSP services documenting that the MDMA/MRSP is meeting the standards. Failure to meet the standards will result in the actions described in Section H.8 of Appendix A of the Direct Access Tariffs Decision (97-10-087). Standards are as follows:

  - Each meter must be read each month, every 27 to 33 days, as defined by the UDC’s meter reading schedule

  - Timeliness For Validated Meter Reading Data. The following standards shall be used to establish the time requirements for posting validated meter reading data on the MDMA server.

    - Interval Data:

- (i) 80% of all usage data must be available on the first day after the scheduled reading date of the meter.

- (ii) 90% of all usage data must be available within two days of the scheduled reading date of the meter.

- (iii) 99.99% of all usage data must be available within four days of the scheduled reading date of the meter.

    - Non-Interval (Monthly) Data:

- (i) 90% of all monthly meter readings must be available by 6:00 a.m. on the 1st working day after the scheduled meter reading date.

- (ii) 95% must be available by 6:00 a.m. on the 2nd working day after the scheduled meter reading date.

- (iii) 99.99% must be available by 6:00 a.m. on the 4th working day after the scheduled meter reading date.

  - The MDMA Server must contain 3 days of (rolling) read history.

  - The MDMA is required to keep the most recent 12 months of customer consumption data for each Direct Access customer. This information must be archived for three years and released on request to the customer, via the ESP, or, if authorized by the customer to any ESP or to the UDC.

  - Information must be posted to the server at least once per business day.

  - [Monthly reads may be posted according to the time and date of the meter read; interval reads must be posted in whole calendar days??]

  - No more than 10% of the meter readings for a single account may be estimated each year.

  - Within five days after installation of a meter, the MDMA/MRSP must confirm that the meter and meter reading system is working properly and that the billing data gathered is valid.

- Other Performance Requirements. The MDMA/MRSP must meet certain other performance requirements. Failure to meet these requirements will result in the actions described in Section H.8 of Appendix A of the Direct Access Tariffs Decision (97-10-087). The requirements are as follows:

  - MRSP/MDMAs must report meter, safety, and hazardous conditions to the UDC and ESP, and keep site-specific information

  - Whenever the MRSP/MDMA becomes aware of any non-conforming meters or errors in the provision of meter services affecting billing, it shall promptly notify the ESP and UDC.

  - The MDMA/MRSPs who are not public utilities must be sure that their employees do not represent themselves as public utility employees. They must clearly identify what company they are from and what the purpose of their visit is, as well as carry company-issued identification cards and a letter or some other writing which describes which ESP the services are being rendered for.

  - MDMA/MRSPs must meet applicable OSHA safety requirements.

  - Validation, editing and estimation must be performed in accordance with current CPUC requirements (see Decision 97-____, pp. 40-44 [draft]).

  - Meter reads must be published to the MDMA Server in the PG&E Meter Exchange Protocol format. In addition:

    - Validation results must be stored with and at the same interval frequency as the source data

    - Estimated usage data must be identified, along with the estimation technique used

    - Usage data must be represented in the appropriate engineering units at the same interval length that was captured in the meter.

  - Technical assistance must be provided to the UDC and ESP as needed to access data published on the MDMA Server and resolve other technical questions that may arise.

  - The MDMA data on the server awaiting transport to the MDMA user must be protected from unauthorized access by outside entities by a firewall, encryption, or some other reasonable security measure(s).

  - Systems, processes, and procedures must be in place to protect data confidentiality, including the execution of a confidentiality agreement as part of the MDMA/MRSP Service Agreement with the UDC.

  - The MDMA shall provide Scheduling Coordinators reasonable and timely access to meter data as required to allow the proper performance of billing, settlement, scheduling, forecasting and other functions.

  - Both UDC and ESP shall have access to the MDMA Server.

  - [The MDMA/MRSP shall maintain a database containing a history of meter and meter device management (i.e. when the meter/device was installed, what the device type is, what the service history has been, what the service parameters of the meter are, etc.).][Note: is this an MDMA/MRSP function or MSP?]