# Introduction

This document attempts to clarify the required data validation, editing, and estimation techniques required to participate in the California market as an MDMA as of 1/1/98.

# Required data validation tests

The following tests are required for kWh and kVARh interval data validation, and would initially be the only tests performed by a non-UDC MDMA:

- Time check of meter reading device/system

- Time check of meter

- Pulse overflow check

- Sum check

- Spike check

- High/low check

- Meter identification check

The following tests are required for monthly data validation, and would be required to be performed by a non-UDC MDMA as of 1/1/99 when non-interval metering is unbundled or when the UDCs accept actual billing determinants instead of 15 minute interval data:

- High/low usage check

- High/low demand check (applies to demand readings only)

- Time-of-use check (applies to TOU data only)

- Zero consumption for active meters

- Usage for inactive meters

- Meter reading dial quantity

- Dial decimal quantity

- External meter identification

- Given the short time frame, this document focuses on the data validation and estimation rules for interval data to meet the requirements for 1/1/98.  Additional work will be required to clarify the monthly data validation at a later date.

# Interval data collection and validation rules (for both kWh and kVARh)

Note that if interval data is read more often then required for billing, checks need to be performed at different times in the process.  Some must be done as the data is read from the meter; some can be done anytime between when the data is collected from the meter and the end of the cycle, and others have to be done on a billing period basis at the end of the billing cycle.  They are broken out that way in this description.

## Time check of  meter reading device/system - ensure that the collection device is synchronized to the national time standard before data collection begins

## Collect data

## As data is collected,

### Check meter identification - verify the meter’s identification matches what is expected

### do time tolerance check of meter

#### If time in meter is within 3 minutes of time standard, mark data as good.  Note that if the meter is within 3 minutes of the standard, the time in the meter can optionally be corrected.

#### If time in meter is off more than 3 minutes but <= 75 minutes, prorate data.  (Note: meter time must be corrected.  If the meter fails the time check for three consecutive months, the meter must be physically inspected/tested)  The data to be prorated includes all intervals from the last time the meter’s time was determined to be good (ie, within the 3 minute tolerance) and when it was discovered that the meter’s time was off more than 3 minutes and the meter was re-synched.

##### Compare the number of intervals provided by the meter during the time period in question with the actual number of intervals expected.  If the two numbers are the same (ie, the meter has the correct number of intervals), do not prorate the data.  Mark the intervals as ????

##### If the meter does not have the correct number of intervals,

##### Fill in details from Lee’s document and spreadsheets…..Mark intervals as ????

#### If time in meter is off more than 75 minutes, mark all intervals between the last time you verified the meter’s time was good (ie, within 3 minute tolerance) and when you discovered the meter’s time was off more than 75 minutes  as needing to be estimated.

## Either as data is collected or prior to publishing on MDMA Server…

### Perform pulse overflow check

#### Inspect each interval for this condition.  If a pulse overflow occurs, need to mark meter for physical meter test/maintenance.  Mark the interval that has a pulse overflow as needing to be estimated  and continue VEE process.

### Perform sum check

#### Sum the intervals for the time between the start and stop meter readings.

#### Compare sum of with difference between start and stop readings (taking into account possible rollover between start and stop readings - for example, if the meter reading rolls over at 99999, the start reading was 99968 and the stop reading was 00294, the difference would be 326).  Note that the sum and the readings must be in the same units for the comparison.

#### If difference is <= two meter multipliers (meter multiplier = ctr x vtr, where ctr is current transformer ratio and vtr is voltage transformer ratio) - mark data as good

#### If difference is greater than two meter multipliers, optionally, rerun the sum check, taking into account the differences in time between the time of the start read and the start of the first interval, and the time of the stop read and the end of the last interval.

##### Adjust the start reading by doing the following:

###### Calculate the percentage of an interval that has elapsed between the begin time of the first interval and the time of the start reading.  For example, if the first interval in an hourly interval data stream starts at 3 pm, and the start reading was performed at 3:20, this percentage would be (20 minutes / 60 minutes) = 33%.

###### Adjust the start reads by subtracting the percentage times the usage in the first interval.  For example, if the start reading was 55555 and the usage during the first interval was 45, then adjust the start reading to 55540.

##### Calculate an allowable margin of error by doing the following:

###### Calculate the percentage of an interval that has elapsed between the end time of the last good interval and the time of the stop reading.

###### Multiply the percentage by the usage in the last interval in the data stream.

###### Add two multipliers to the value calculated in the previous step.

###### Compare the sum of the intervals with the difference between the adjusted start reading and the stop reading (taking into account possible rollover between start and stop readings).

##### If difference is within the allowable margin calculated in step 3.4.2.3.2 - mark data as good

##### If difference is greater than the margin, and if some intervals are missing or incomplete, optionally prorate the difference between the adjusted start read and the stop read by the percentage of good intervals and rerun the sum check.

###### Count the number of good intervals in the data stream.

###### Calculate the percentage of good intervals by dividing the count from the previous step by the number of intervals elapsed between start time and stop time.

###### Multiply the percentage by the difference between the adjusted start reading and the stop reading.

###### Compare the new difference with the sum of the usage in the good intervals.

###### If the difference is within the allowable margin calculated in step 3.4.2.3.2 - mark good intervals as having passed sum check.

##### If the difference is greater than the allowable margin, optionally reread meter.

###### Redo sumcheck test from original start meter reading to new stop meter reading

###### If the difference is within two meter multipliers - mark data as good

###### If the difference is greater than two meter multipliers - kick out for manual inspection.

##### Other checks may be performed, based on the technology used, to verify that the interval data is an accurate representation of usage as measured by the meter readings.

##### If sumcheck still not resolved, perform manual inspection of data

###### Manually inspect the data.  If the data seems reasonable, it may be marked as verified.

###### Manual inspection should verify meter and pulse multipliers.  If  a multiplier was wrong, recalculate the intervals using the new multiplier and redo the sum check.  If data now passes the sum check, mark data as good.

###### If multipliers are ok, check for meter changeout between the start and stop meter readings.  If the meter was changed out, redo the sum check for each meter independently.  If sum check passes, mark data as good.

###### If multiplier was ok, do physical meter test/inspection.  If meter tests ok, mark data as verified.  If meter does not test ok, mark data as needing to be estimated.  If unable to visit site and perform meter test prior to posting the data, mark the data as needing to be estimated.

##### If interval data is available, but there are no meter readings to perform the sum check with, manually inspect the data.  Mark data that appears to be reasonable (compared with historical data) as verified.  Any data that does not appear to be reasonable should be marked as needing to be estimated

### Spike check

#### For each 24 hour period, determine highest and third highest peaks.  (Normally the 24 hour period is from midnight to midnight.  If the data is at the beginning and doesn’t start at midnight, use enough data from the next day of data to get 24 hours of data.  If the data is at the end and doesn’t stop at midnight, use enough data from the next to last day of data to get 24 hours.)  If (highest peak - third highest peak)/third highest peak> 1.8, a spike exists - the highest interval fails the spike check

#### If interval fails spike check, optionally reread meter.

#### If you get different value from reread, redo spike check.

#### If value is the same on reread or you cannot reread the meter, kick it out for manual analysis (Note: this is an area where further rules may be developed in the future.)

#### Manual analysis looks for similar patterns on other similar days.  May also optionally involve calling the customer to check for unusual conditions at the time of the spike.

#### If no similar pattern or other legitimate reason for spike is found, mark highest interval as needing to be estimated.  If similar pattern or other reason for legitimate spike is found, mark data as verified after  having failed the spike check

### Additional check if interval kVARh data is available

Note that if multiple kWh channels map to a single kVARh channel, or multiple kVARh channels map to single kWh channel, the appropriate channels must be totaled prior to this check.  If any intervals are determined to require estimation, all channels summed into that interval must be marked as needing estimation.

#### If there are any kWh intervals with zero consumption, check the corresponding kVARh interval.

#### If the corresponding kVARh interval is also zero, the kWh data is considered good.

#### If the corresponding kVARh interval is not zero, mark the kWh interval as missing.

## On the billing cycle for the meter…..

### High/low check

Note that for 1/1/98, this check may be done on good and verified data only (ie, not including any estimated intervals), or after validation and estimation (including good, verified, and estimated intervals), or both.  All parties should work toward doing this check both times in the future.

#### If last year’s data is available, calculate average daily usage for same billing month last year; use summed VEE or historical billing interval data if available, if not use VEE or historical billing usage (ie, difference between register readings)

#### Else if last year’s data is not available, calculate average daily usage for the previous billing month; use summed VEE or historical billing interval data if available, if not use VEE or historical billing usage (ie, difference between register readings).

#### Else if previous billing month not available - don’t do this check!

#### Calculate average daily usage for this billing month using either summed VEE data (if test includes estimated data) or summed good and verified data (if test does not include estimated data).  If there were any spikes in the data, don’t include those intervals in the average - prorate the daily average accordingly.

#### If the difference between the two daily averages is greater than 50% of the historical daily average, flag data (all the intervals in the month) as failing high/low average check and kick out for manual analysis.  Else mark data as good.

If (|historical daily average - this month’s daily average)| <= .5* historical daily average) then data is marked as good.

If (|historical daily average - this month’s daily average)| > .5* historical daily average) then data (all intervals in the month) is flagged as failing high/low average check and kicked out for manual analysis.

#### If data is flagged for manual analysis - look at the recent history of that meter.  If monthly usage has been on a trend in the appropriate direction and this seems reasonable, mark data as verified.  If not, optionally check with customer for changed usage patterns.  If changed usage patterns match change in data, mark data as verified.  If no change in usage patterns reported by customer, check perform physical meter test/inspection.  If a problem is found with the meter, mark the data as needing to be estimated.  (Note: if the problem existed prior to this billing period, previously posted data will need to be adjusted and reposted.)   Also check to see if some of the data looks reasonable; mark reasonable looking data as verified.  (For example, this may happen if a meter fails sometime during the month - the data at the beginning of the month may be ok, while the data after the failure may be obviously bad.)

#### If data fails high/low average check, mark suspect data as needing to be estimated.

### Estimate missing data; see section 4

### Optionally rerun checks after estimation to help verify estimated readings.  For example, this may include doing the sum check again if it is a mechanical meter..

# Estimation Rules

Estimate intervals marked as missing using the following estimation rules….

## If the cause of the problem is determined to a physical problem with the meter or meter installation and the data can be corrected by scaling the intervals and meter readings, the following rules apply instead of the standard estimation rules in sections 4.2 and 4.3.  (Note: the UDCs will provide the rules based on current practices and CPUC regulations.)  Examples of these situations include a meter running slow, a meter running fast, one or two phases dropped, ….

## If section of missing data is 2 hours or less in length…

Use the point to point linear interpolation method to estimate the missing data where there is a gap in the data.  If the gap occurs in the middle of the data, the “first point” is the last good interval before the gap, and the “second point” is the first good interval after the gap.

If the gap occurs at the beginning of the span, use the last interval from the historical data as the first point, if the historical data is available and the interval data is not estimated. Otherwise, use the second point (the first good interval after the gap) as the first point - this will cause the load to be estimated as a flat load.

If the gap occurs at the end of the span, use the first point (the last good interval before the gap) as the second point (- this will cause the load to be estimated as a flat load.

## If section of missing data is more than 2 contiguous hours…

### Find the three most recent “similar” days with valid data (ie, contain no estimated data) closest in time to the day with the missing data.  The “similar days” can be chosen from the current billing period and historical data up to 90 days prior to the day with the missing data.  A “similar” day means the same day of week.  Note that similar days from the same billing period should be used first, and then similar days from historical data should be used if necessary.  If the day with missing data is a holiday, the “similar days” should be holidays, not the same day of week.  If not enough historical holidays exist in the current billing period or  previous 90 day period, use Sundays. Note that a standard list of holidays will be used across the board, regardless of the tariff or service territory the meter is in.  The historical data used should be that data immediately preceding the usage period, regardless of seasonal crossover.

Calculate the average daily profile using the three selected days.

Estimate the missing data by applying the appropriate intervals from the average daily profile to fill the missing intervals.

### If only two similar days are available from the current billing period and 90 days historical data, calculate the average daily profile using the two selected days.  Estimate the missing data by applying the appropriate intervals from the average daily profile to fill the missing intervals.

### If only one similar day is available from the current billing period and 90 days historical data, estimate the missing data by applying the appropriate intervals from the similar day to fill the missing intervals

### If no similar days are available in the current billing period and 90 days historical data, look for the three “like” days that are closest chronologically to the day with missing intervals.  A like day means weekday or weekend/holiday.  For example, if the missing intervals were on Tuesday, use Monday, Wednesday, and Thursday.  Only use weekdays with weekdays; only use weekends with weekends; only use holidays or weekends with holidays. Calculate the average daily profile using the three selected days.  Estimate the missing data by applying the appropriate intervals from the average daily profile to fill the missing intervals.

### If no similar days are available and there aren’t three “like” days, select the two “like” days that are chronologically closest to the day with missing intervals.  Calculate the average daily profile using the two selected days.  Estimate the missing data by applying the appropriate intervals from the average daily profile to fill the missing intervals.

### If no similar days are available and there aren’t two “like” days, select the one “like” day that is chronologically closest to the day with missing intervals.   Estimate the missing data by applying the appropriate intervals from the similar day to fill the missing intervals

### If there are no similar days or like days, use the load profile for the customer’s class to estimate the data.  Use this month’s usage if available to scale the load profile.  If this month’s usage is not available, use last month’s usage or last year’s usage to scale the load profile, whichever is determined to be more reasonable.  Refer to the UDCs’ load profile documentation for more information on applying load profiles.

### If there is no historical data that can be used, the data must be estimated manually and the process and assumptions documentd.

# Miscellaneous Comments/Requirements

## MDMA is required to store raw and validated data

## Raw data may be stored as either pulses or consumption, but is pre-VEE

## The high/low  test is  done against consumption data, not pulses - other checks may be done against either pulses or consumption data provided the data scaling is consistent throughout the month.

## UDCs are expecting to see consumption data (i.e., kWh or kVARh) in the CMEP MEPMD01 record for intervals, not pulses

## For interval data, PG&E and SDG&E only require interval data to be posted on the MDMA Server - ie, the start and stop reads do not need to be posted with it.  SCE will provide their requirements.

## Historical data used in validation tests or estimation is VEE data or historical billing data, not raw data

## It is good practice (and will be required when supported by the CMEP MEPMD01 record) to mark each interval with one or more of the following:

- as good if the interval passed all checks

- as verified if the interval failed a check but the interval was manually ok’d

- as having failed a specific test (even if data was later verified)

- as estimated, including the estimation algorithm used

- Note that if the data is marked as good, it would not have any of the other three flags.  If the data is marked as verified, it should also have at least one flag indicating the validation test the data failed.  If the data is marked as estimated, it should include the estimation scheme used, and the data should also have at least one flag indicating which validation test the data failed.

## If kVARh interval data is read for billing, it goes through same VEE procedure as kWh data

# Open issues

## There is a requirement if data is estimated to report the estimation scheme used, but there is no field in the MEPMD01 record to report this.  Is the requirement at the interval level (ie, <2 hour rule, > 2 hour rule, kVARh rule)?  Or is the requirement at a higher level for the whole record (ie, CPUC rules, SCE rules, PG&E rules, SDG&E rules)?  Answer: the requirement is to record the estimation scheme at the interval level.  Since there is presently no way to report the estimation scheme in the MEPMD01 record, the MDMA must record the estimation scheme used for each estimated interval.  The estimation scheme will be posted with the data when the MEPMD01 record is modified to include it.

## How is data prorated when meter time is off?  Is the data marked as estimated?  Valerie Nibbler and Lee Simmons are working on a proposal for this.

## How is historical average power factor used to estimate kWh?  Is it one average value over time, or by interval?  Propose using one average value, not per interval.  Answer: this estimation technique is no longer required.

## For historical data, do you use data from the same “site” even if the customer has changed?  For example, if you need to estimate a bill this month for a customer who just moved in two months ago - to get three months of historical data you would have to go back to the previous customer.  What if the meter has been changed out?  Answer: Historical data used for checks and estimations should be from the same customer and the same site as the data being checked or estimated.  A meter changeout does not affect this - ie, if a meter was changed out, historical data from the previous meter at that same site may be used provided the customer hasn’t changed.

## Given the order of the tests (time, pulse overflow, sum) it is possible that some data has been marked as missing or estimated by the time you do the sum check.  If the meter is a solid state meter, this almost guarantees it will fail.  How should this be handled?  What data should be used for the sum check?  Answer:  The sum check can be done on good and valid data (excluding any estimated intervals), or on all VEE data, or on both.  The goal is to do it on both, although this is not a requirement 1/1/98.  If data fails the sum check but looks reasonable on manual inspection, the data should be marked as verified.

## In the high/low check, should the check be made against last year’s “billing” month?  Or against the data from the actual dates in this year’s billing month?  (Since we have interval data, it can be done either way…)  Answer: initially, for most accounts the historical data will be usage, not interval.  In this case, the comparison must be done based on billing month.  When interval data is available, the check may be done either way - against last year’s billing period that has the most overlap to the current billing period, or against the specific days.  For example, if my current billing period is from 4/2/98 to 5/5/98, and last year’s billing month was from 4/4/97 to 5/7/97, the high low check could either be done based on last year’s billing period (4/4/97 - 5/7/97), or on the exact days (4/2/97 to 5/5/97).

## In the CMEP protocol, if you are providing raw data, how are missing intervals indicated?  Kris Hardie of PG&E to provide example.

## For the sum check, the wording in the CPUC ruling states “If the difference is greater than one meter multiplier, the data needs to be verified by the MDMA. If the data comes back the same, the data should be flagged as verified.”  Does this mean that if you re-read the meter and get the same data, the data passes the sum check?  Answer:  No.  See details in section on sum check.

## In the high/low average check - what if you have performed all the tests, including a physical meter inspection and test, and no problem is found with the meter?  Answer: flag the data as verified.

## When is data considered “adjusted” vs “estimated”?.  NEEDS DISCUSSION!  The UDC’s are to provide guidelines in this area.