# Introduction

This document attempts to clarify the required data validation, editing, and estimation techniques required to participate in the California market as an MDMA as of 1/1/98.

# Required data validation tests

The following tests are required for kWh and kVARh interval data validation, and would initially be the only tests performed by a non-UDC MDMA:

- Time check of meter reading device/system

- Time check of meter

- Pulse overflow check

- Sum check

- Spike check

- High/low check

- Meter identification check

The following tests are required for monthly data validation, and would be required to be performed by a non-UDC MDMA as of 1/1/99 when non-interval metering is unbundled or when the UDCs accept actual billing determinants instead of 15 minute interval data:

- High/low usage check

- High/low demand check (applies to demand readings only)

- Time-of-use check (applies to TOU data only)

- Zero consumption for active meters

- Usage for inactive meters

- Meter reading dial quantity

- Dial decimal quantity

- External meter identification

- Given the short time frame, this document focuses on the data validation and estimation rules for interval data to meet the requirements for 1/1/98.  Additional work will be required to clarify the monthly data validation at a later date.

# Interval data collection and validation rules (for both kWh and kVARh)

Note that if interval data is read more often then required for billing, checks need to be performed at different times in the process.  Some must be done as the data is read from the meter; some can be done anytime between when the data is collected from the meter and the end of the cycle, and others have to be done on a billing period basis at the end of the billing cycle.  They are broken out that way in this description.

## Time check of  meter reading device/system - ensure that the collection device is synchronized to the national time standard before data collection begins

## Collect data

## As data is collected,

### Check meter identification - verify the meter’s identification matches what is expected

### do time tolerance check of meter

#### If time in meter is within 3 minutes of time standard, mark data as good.  Note that if the meter is within 3 minutes of the standard, the time in the meter can optionally be corrected.

#### If time in meter is off more than 3 minutes but <= 75 minutes, prorate data.  (Note: meter time must be corrected.  If the meter fails the time check for three consecutive months, the meter must be physically inspected/tested)  The data to be prorated includes all intervals from the last time the meter’s time was determined to be good (ie, within the 3 minute tolerance) and when it was discovered that the meter’s time was off more than 3 minutes and the meter was re-synched.

##### Compare the number of intervals provided by the meter during the time period in question with the actual number of intervals expected.  If the two numbers are the same (ie, the meter has the correct number of intervals), do not prorate the data.  Mark the intervals as good.

##### If the meter does not have the correct number of intervals,

###### Refer to Appendix A for a description of how to prorate the data.  Mark intervals as estimated.

#### If time in meter is off more than 75 minutes, mark all intervals between the last time you verified the meter’s time was good (ie, within 3 minute tolerance) and when you discovered the meter’s time was off more than 75 minutes  as needing to be estimated.

## Either as data is collected or prior to publishing on MDMA Server…

### Perform pulse overflow check

#### Inspect each interval for this condition.  If a pulse overflow occurs, need to mark meter for physical meter test/maintenance.  Mark the interval that has a pulse overflow as needing to be estimated  and continue VEE process.

### Perform sum check

#### Sum the intervals for the time between the start and stop meter readings.

#### Compare sum of with difference between start and stop readings (taking into account possible rollover between start and stop readings - for example, if the meter reading rolls over at 99999, the start reading was 99968 and the stop reading was 00294, the difference would be 326).  Note that the sum and the readings must be in the same units for the comparison.

#### If difference is <= two meter multipliers (meter multiplier = ctr x vtr, where ctr is current transformer ratio and vtr is voltage transformer ratio) - mark data as good

#### If difference is greater than two meter multipliers, optionally, rerun the sum check, taking into account the differences in time between the time of the start read and the start of the first interval, and the time of the stop read and the end of the last interval.

##### Adjust the start reading by doing the following:

###### Calculate the percentage of an interval that has elapsed between the begin time of the first interval and the time of the start reading.  For example, if the first interval in an hourly interval data stream starts at 3 pm, and the start reading was performed at 3:20, this percentage would be (20 minutes / 60 minutes) = 33%.

###### Adjust the start reads by subtracting the percentage times the usage in the first interval.  For example, if the start reading was 55555 and the usage during the first interval was 45, then adjust the start reading to 55540.

##### Calculate an allowable margin of error by doing the following:

###### Calculate the percentage of an interval that has elapsed between the end time of the last good interval and the time of the stop reading.

###### Multiply the percentage by the usage in the last interval in the data stream.

###### Add two multipliers to the value calculated in the previous step.

###### Compare the sum of the intervals with the difference between the adjusted start reading and the stop reading (taking into account possible rollover between start and stop readings).

##### If difference is within the allowable margin calculated in step 3.4.2.3.2 - mark data as good

##### If difference is greater than the margin, and if some intervals are missing or incomplete, optionally prorate the difference between the adjusted start read and the stop read by the percentage of good intervals and rerun the sum check.

###### Count the number of good intervals in the data stream.

###### Calculate the percentage of good intervals by dividing the count from the previous step by the number of intervals elapsed between start time and stop time.

###### Multiply the percentage by the difference between the adjusted start reading and the stop reading.

###### Compare the new difference with the sum of the usage in the good intervals.

###### If the difference is within the allowable margin calculated in step 3.4.2.3.2 - mark good intervals as having passed sum check.

##### If the difference is greater than the allowable margin, optionally reread meter.

###### Redo sumcheck test from original start meter reading to new stop meter reading

###### If the difference is within two meter multipliers - mark data as good

###### If the difference is greater than two meter multipliers - kick out for manual inspection.

##### Other checks may be performed, based on the technology used, to verify that the interval data is an accurate representation of usage as measured by the meter readings.

##### If sumcheck still not resolved, perform manual inspection of data

###### Manually inspect the data.  If the data seems reasonable, it may be marked as verified.

###### Manual inspection should verify meter and pulse multipliers.  If  a multiplier was wrong, recalculate the intervals using the new multiplier and redo the sum check.  If data now passes the sum check, mark data as good.

###### If multipliers are ok, check for meter changeout between the start and stop meter readings.  If the meter was changed out, redo the sum check for each meter independently.  If sum check passes, mark data as good.

###### If multiplier was ok, do physical meter test/inspection.  If meter tests ok, mark data as verified.  If meter does not test ok, mark data as needing to be estimated.  If unable to visit site and perform meter test prior to posting the data, mark the data as needing to be estimated.

##### If interval data is available, but there are no meter readings to perform the sum check with, manually inspect the data.  Mark data that appears to be reasonable (compared with historical data) as verified.  Any data that does not appear to be reasonable should be marked as needing to be estimated

### Spike check

#### For each 24 hour period, determine highest and third highest peaks.  (Normally the 24 hour period is from midnight to midnight.  If the data is at the beginning and doesn’t start at midnight, use enough data from the next day of data to get 24 hours of data.  If the data is at the end and doesn’t stop at midnight, use enough data from the next to last day of data to get 24 hours.)  If (highest peak - third highest peak)/third highest peak> 1.8, a spike exists - the highest interval fails the spike check

#### If interval fails spike check, optionally reread meter.

#### If you get different value from reread, redo spike check.

#### If value is the same on reread or you cannot reread the meter, kick it out for manual analysis (Note: this is an area where further rules may be developed in the future.)

#### Manual analysis looks for similar patterns on other similar days.  May also optionally involve calling the customer to check for unusual conditions at the time of the spike.

#### If no similar pattern or other legitimate reason for spike is found, mark highest interval as needing to be estimated.  If similar pattern or other reason for legitimate spike is found, mark data as verified after  having failed the spike check

### Additional check if interval kVARh data is available

Note that if multiple kWh channels map to a single kVARh channel, or multiple kVARh channels map to single kWh channel, the appropriate channels must be totaled prior to this check.  If any intervals are determined to require estimation, all channels summed into that interval must be marked as needing estimation.

#### If there are any kWh intervals with zero consumption, check the corresponding kVARh interval.

#### If the corresponding kVARh interval is also zero, the kWh data is considered good.

#### If the corresponding kVARh interval is not zero, mark the kWh interval as needing to be estimated.

## On the billing cycle for the meter…..

### High/low check

Note that for 1/1/98, this check may be done on good and verified data only (ie, not including any estimated intervals), or after validation and estimation (including good, verified, and estimated intervals), or both.  All parties should work toward doing this check both times in the future.

#### If last year’s data is available, calculate average daily usage for same billing month last year; use summed VEE or historical billing interval data if available, if not use VEE or historical billing usage (ie, difference between register readings)

#### Else if last year’s data is not available, calculate average daily usage for the previous billing month; use summed VEE or historical billing interval data if available, if not use VEE or historical billing usage (ie, difference between register readings).

#### Else if previous billing month not available - don’t do this check!

#### Calculate average daily usage for this billing month using either summed VEE data (if test includes estimated data) or summed good and verified data (if test does not include estimated data).  If there were any spikes in the data, don’t include those intervals in the average - prorate the daily average accordingly.

#### If the difference between the two daily averages is greater than 50% of the historical daily average, flag data (all the intervals in the month) as failing high/low average check and kick out for manual analysis.  Else mark data as good.

If (|historical daily average - this month’s daily average)| <= .5* historical daily average) then data is marked as good.

If (|historical daily average - this month’s daily average)| > .5* historical daily average) then data (all intervals in the month) is flagged as failing high/low average check and kicked out for manual analysis.

#### If data is flagged for manual analysis - look at the recent history of that meter.  If monthly usage has been on a trend in the appropriate direction and this seems reasonable, mark data as verified.  If not, optionally check with customer for changed usage patterns.  If changed usage patterns match change in data, mark data as verified.  If no change in usage patterns reported by customer, perform physical meter test/inspection.  If a problem is found with the meter, mark the data as needing to be estimated.  (Note: if the problem existed prior to this billing period, previously posted data will need to be adjusted and reposted.)   Also check to see if some of the data looks reasonable; mark reasonable looking data as verified.  (For example, this may happen if a meter fails sometime during the month - the data at the beginning of the month may be ok, while the data after the failure may be obviously bad.)

#### If data fails high/low average check, mark suspect data as needing to be estimated.

### Estimate data needing estimation; see section 4

### Optionally rerun checks after estimation to help verify estimated readings.  For example, this may include doing the sum check again if it is a mechanical meter..

# Estimation Rules

Estimate intervals marked as needing estimation using the following estimation rules….

## If the cause of the problem is determined to be a physical problem with the meter or meter installation and the data can be corrected by scaling the intervals and meter readings, the MDMA will be notified of the time period requiring correction and the scaling factor to be applied to each interval in that period.  When the data is posted in the CMEP format, it would be marked as estimated if it had not been previously posted, and marked as adjusted if it had previously been posted.  Data that is corrected in this fashion may be reported in a separate category on the monthly MDMA reports, and not included as part of the % estimated data for the month.  Details need to be worked out as to how MDMAs will receive this notification.  (Note: the UDCs will provide the rules based on current practices and CPUC regulations.)  Examples of these situations include a meter running slow, a meter running fast, one or two phases dropped, ….

## If section of data needing estimation is 2 hours or less in length…

Use the point to point linear interpolation method to estimate the data where there is a gap in the data.  If the gap occurs in the middle of the data, the “first point” is the last good interval before the gap, and the “second point” is the first good interval after the gap.

If the gap occurs at the beginning of the span, use the last interval from the historical data as the first point, if the historical data is available and the interval data is not estimated. Otherwise, use the second point (the first good interval after the gap) as the first point - this will cause the load to be estimated as a flat load.

If the gap occurs at the end of the span, use the first point (the last good interval before the gap) as the second point (- this will cause the load to be estimated as a flat load.

## If section of data needint estimation is more than 2 contiguous hours…

### Find the three most recent “similar” days with valid data (ie, contain no estimated data) closest in time to the day with the data needing estimation.  The “similar days” can be chosen from the current billing period and historical data up to 90 days prior to the day with the data needing estimation.  A “similar” day means the same day of week.  Note that similar days from the same billing period should be used first, and then similar days from historical data should be used if necessary.  If the day with data needing estimation is a holiday, the “similar days” should be holidays, not the same day of week.  If not enough historical holidays exist in the current billing period or  previous 90 day period, use Sundays. Note that a standard list of holidays will be used across the board, regardless of the tariff or service territory the meter is in.  The historical data used should be that data immediately preceding the usage period, regardless of seasonal crossover.

Calculate the average daily profile using the three selected days.

Estimate the data needing estimation by applying the appropriate intervals from the average daily profile to fill the missing intervals.

### If only two similar days are available from the current billing period and 90 days historical data, calculate the average daily profile using the two selected days.  Estimate the data needing estimation by applying the appropriate intervals from the average daily profile to fill the missing intervals.

### If only one similar day is available from the current billing period and 90 days historical data, estimate the data needing estimation by applying the appropriate intervals from the similar day to fill the intervals needing estimation.

### If no similar days are available in the current billing period and 90 days historical data, look for the three “like” days that are closest chronologically to the day with intervals needing estimation.  A like day means weekday or weekend/holiday.  For example, if the intervals needing estimation were on Tuesday, use Monday, Wednesday, and Thursday.  Only use weekdays with weekdays; only use weekends with weekends; only use holidays or weekends with holidays. Calculate the average daily profile using the three selected days.  Estimate the data by applying the appropriate intervals from the average daily profile to fill the intervals needing estimation.

### If no similar days are available and there aren’t three “like” days, select the two “like” days that are chronologically closest to the day with intervals needing estimation.  Calculate the average daily profile using the two selected days.  Estimate the data by applying the appropriate intervals from the average daily profile to fill the intervals needing estimation.

### If no similar days are available and there aren’t two “like” days, select the one “like” day that is chronologically closest to the day with intervals needing estimation.   Estimate the data by applying the appropriate intervals from the similar day to fill the intervals needing estimation.

### If there are no similar days or like days, use the load profile for the customer’s class to estimate the data.  Use this month’s usage if available to scale the load profile.  If this month’s usage is not available, use last month’s usage or last year’s usage, whichever is determined to be more reasonable, to scale the load profile,.  Refer to the UDCs’ load profile documentation for more information on applying load profiles.

### If there is no historical data that can be used, the data must be estimated manually and the process and assumptions documented.

# Miscellaneous Comments/Requirements

## MDMA is required to store raw and validated data

## Raw data may be stored as either pulses or consumption, but is pre-VEE

## The high/low  test is  done against consumption data, not pulses - other checks may be done against either pulses or consumption data provided the data scaling is consistent throughout the month.

## UDCs are expecting to see consumption data (i.e., kWh or kVARh) in the CMEP MEPMD01 record for intervals, not pulses

## For interval data, PG&E and SDG&E only require interval data to be posted on the MDMA Server - ie, the start and stop reads do not need to be posted with it.  SCE will provide their requirements.

## Historical data used in validation tests or estimation is VEE data or historical billing data, not raw data

## It is good practice (and will be required when supported by the CMEP MEPMD01 record) to mark each interval with one or more of the following:

- as good if the interval passed all checks

- as verified if the interval failed a check but the interval was manually ok’d

- as having failed a specific test (even if data was later verified)

- as estimated, including the estimation algorithm used

- Note that if the data is marked as good, it would not have any of the other three flags.  If the data is marked as verified, it should also have at least one flag indicating the validation test the data failed.  If the data is marked as estimated, it should include the estimation scheme used, and the data should also have at least one flag indicating which validation test the data failed.

## If kVARh interval data is read for billing, it goes through same VEE procedure as kWh data

## There is a requirement if data is estimated to report the estimation scheme used, but there is no field in the MEPMD01 record to report this.  Is the requirement at the interval level (ie, <2 hour rule, > 2 hour rule, kVARh rule)?  Or is the requirement at a higher level for the whole record (ie, CPUC rules, SCE rules, PG&E rules, SDG&E rules)?  Answer: the requirement is to record the estimation scheme at the interval level.  Since there is presently no way to report the estimation scheme in the MEPMD01 record, the MDMA must record the estimation scheme used for each estimated interval.  The estimation scheme will be posted with the data when the MEPMD01 record is modified to include it.

## How is historical average power factor used to estimate kWh?  Is it one average value over time, or by interval?  Propose using one average value, not per interval.  Answer: this estimation technique is no longer required.

## Given the order of the tests (time, pulse overflow, sum) it is possible that some data has been marked as missing or estimated by the time you do the sum check.  If the meter is a solid state meter, this almost guarantees it will fail.  How should this be handled?  What data should be used for the sum check?  Answer:  The sum check can be done on good and valid data (excluding any estimated intervals), or on all VEE data, or on both.  The goal is to do it on both, although this is not a requirement 1/1/98.  If data fails the sum check but looks reasonable on manual inspection, the data should be marked as verified.

## In the high/low check, should the check be made against last year’s “billing” month?  Or against the data from the actual dates in this year’s billing month?  (Since we have interval data, it can be done either way…)  Answer: initially, for most accounts the historical data will be usage, not interval.  In this case, the comparison must be done based on billing month.  When interval data is available, the check may be done either way - against last year’s billing period that has the most overlap to the current billing period, or against the specific days.  For example, if my current billing period is from 4/2/98 to 5/5/98, and last year’s billing month was from 4/4/97 to 5/7/97, the high low check could either be done based on last year’s billing period (4/4/97 - 5/7/97), or on the exact days (4/2/97 to 5/5/97).

## In the CMEP protocol, if you are providing raw data, how are missing intervals indicated?  Missing intervals are marked with a protocol text of N.

## For the sum check, the wording in the CPUC ruling states “If the difference is greater than one meter multiplier, the data needs to be verified by the MDMA. If the data comes back the same, the data should be flagged as verified.”  Does this mean that if you re-read the meter and get the same data, the data passes the sum check?  Answer:  No.  See details in section on sum check.

## In the high/low average check - what if you have performed all the tests, including a physical meter inspection and test, and no problem is found with the meter?  Answer: flag the data as verified.

# Open issues

## How is data prorated when meter time is off?  Is the data marked as estimated?  Valerie Nibler and Lee Simmons are working on a proposal for this.

## For historical data, do you use data from the same “site” even if the customer has changed?  For example, if you need to estimate a bill this month for a customer who just moved in two months ago - to get three months of historical data you would have to go back to the previous customer.  What if the meter has been changed out?  Answer: Historical data used for checks and estimations should be from the same customer and the same site as the data being checked or estimated.  A meter changeout does not affect this - ie, if a meter was changed out, historical data from the previous meter at that same site may be used provided the customer hasn’t changed.  Note that there are details associated with this topic that still need to be discussed and finalized.

## When is data considered “adjusted” vs “estimated”?.  NEEDS DISCUSSION!  The UDC’s are to provide guidelines in this area.

Appendix A: Prorating Time Drifted Data

We are concerned about normalizing interval data when the clock in the meter does not agree with the clock in the computer reading the meter.  This phenomena is called Clock Drift.  Clock drift can be both a negative or positive value, depending upon whether the real time (at the computer) is greater than {negative drift] or less than [positive drift] than the clock in the meter.  This is illustrated below.

Dt

0             1             2             3             4             5             6             7             8

Time

Normal

Computer

Dt

0        1         2         3         4        5         6         7         8         9        10       11

Time

Short

Interval

Dt

0                1               2                3               4                5                6               7

Time

Long

Interval

For each of the illustrations shown above, the actual interval for measurement is different.  We assume that the meter and the computer systems are synchronized at some time, T0 {for example, the last meter read} and that the meter is now being read at a read time, Tr.  For each of the cases above, assume that the meter reading system reads at the same time.  The actual elapsed time is given by

Elapsed Time  =  DTe = Tr  - T0

The elapsed time for the shorter interval case is given by

Short Interval Elapsed Time  =  DTes = Tms  - T0

where Tms is the time that the meter clock gives when the meter is read.

The elapsed time for the longer interval case is given by

Longer Interval Elapsed Time  =  DTel = Tms  - T0

where Tml is the time that the meter clock gives when the meter is read.  Note that Tms > T0 , i.e. the meter clock is running slower therefore clocking more intervals and more elapsed time. And that Tml < T0, i.e., the meter clock is running faster, hence fewer intervals and a shorter elapsed time.

In each case, the internal clock in the meter is registering that the interval length is the length that is specified for the meter, namely Dt or 15 minutes for CA interval meters.  However, since the clock is running slower for the short interval case and faster for the long interval case, we must adjust the values such that the correct usage is obtained for each meter.  The total drift time for the clock can be calculated for each case as follows:

Total Drift Time For Short Intervals  TDs = ½DTe  - DTes½= ½Tr  - Tms½

and

Total Drift Time For Long Intervals  TDl =  ½DTe  - DTel½= ½Tr  - Tml½

Note that TDl would be negative had we not taken the absolute value.

The actual number of intervals for each case can be calculated using the elapsed time measured by the meter and dividing it by the preset meter interval, Dt or 15 minutes. Or when truncated to an integer:

Actual Number of Intervals, N =  DTe / Dt

Number of Short Intervals Ns =  DTes / Dt

Number of Long Intervals Nl =  DTel / Dt

We should consider at least two cases.

Case # 1 is when N = Ns = Nl , i.e. the clock drift is small enough that no additional interval is generated.  For this situation, we could elect to do nothing since for a thirty day reading schedule for 15 minute interval data, there will be about 2880 intervals and a time drift error of less than 0.04% in each interval.  The actual drift time for each interval, ignoring any fractional intervals at the end of the read period can be calculated as

DDTs = TDs / N

and for the long interval case,

DDTl = TDl / N .

This result could be used in combination with the actual interval width to increase or decrease the usage in the particular interval.

Case #2 involves a situation when N ¹ Ns and N ¹ Nl and hence there are a fewer or greater number of intervals that expected.  Here we suggest that a procedure be adopted that distributes the measured interval values into intervals that have the correct length, namely Dt.  Thus we increase or decrease the interval length to correspond to actual interval length that should have been in the meter based on the drift, Dt + DDTl  or  Dt - DDTs .  Thus the interval distribution that is shown in the above figure would now have proper interval lengths in minutes.  The procedure for distribution this data is fairly straightforward.  We simply insert the real 15 minute interval grid on the actual interval grid taken from the meter and adjusted by the above technique.  Next we divide each of the obtain usage values at the corresponding 15 minute grid points.

Tr

T0

Time

Dt

0        1         2         3         4        5         6         7         8         9        10       11

1

Correct

3

Incorrect

Time

This figure shown how to allocate each of the respective values.  For example in the first interval of the correct result interval.  The usage here would equal the sum of the usage in the incorrect time interval case plus the fraction to the left of the corresponding interval in the correct zone.  For example, if the drift per interval was found to be 4 minutes for short interval case, then the time grid would be 0, 11, 22, 33, 44, 55, 66, 77, etc.  The amount taken from the second short interval would be the usage in interval 2 multiplied by 4/11 or 34%.  For the case of the third correct interval, there would be components from interval 3, 4, and 5 of the incorrect interval usage.  From the third interval, it would be 3/11 of the usage, from the forth interval is would be 100% of the usage, and from the fifth interval it would be 1/11 of the usage.  This scheme should be easy to implement.  The one caution is that additional manipulation of the usage data will be required if the interval values stored as kW for the interval, rather than kWh.  But this should not be a problem