I.   Tables of Standards as Requirements

The following tables provide a list of standards as minimum requirements for meters and meter equipment used in Direct Access.

Table 1:  Standards as Requirements for Meter Equipment Used in Direct Access

| Standards | Applicable for DA? | Required in CPUC’s D97-12-048 | Proposed Requirements | Recommended effective date | Comments |
| --- | --- | --- | --- | --- | --- |
| ANSI C12.1-1995, Code for Electricity Metering | Yes | Yes | Conditional “yes” as noted in Comments column | Now | To be used in conjunction with Section II below |
| ANSI C12.7-1993, Watt-hour Meter Socket | Yes | Yes | Conditional “yes” as noted in Comments column | Now | Applies only to socket meters |
| ANSI C12.8-1981 (R1997), Test Blocks and Cabinets for Installation of Self-Contained A-Based Meters | Yes | Yes | Yes | Now |  |
| ANSI C12.9-1993, Test Switches for Transformer-rated Meters | Yes | Yes | Yes | Now |  |
| ANSI C12.10-1997, Electromechanical Watt-hour Meters | Yes | Yes | Yes | Now |  |
| ANSI C12.11-1987 (R1993), Instrument Transformers for Revenue Metering, 10 kV-350 kV BIL (0.6-69 kV NSV) | Yes | Yes | Yes | Now |  |
| ANSI C12.13-1991, Electronic TOU Registers for Electricity Meters | Yes | Yes | Yes | Now |  |
| ANSI C12.20-1998, 0.2% & 0.5% Accuracy Class Meters (approved but not yet published) | Yes | Yes | Conditional “yes” as noted in Comments column | 2 years from publication date | To be used in conjunction with Section II below |
| ANSI C37.90.1-1989 (R1994), Surge Withstand Capability (SWC) Test | Yes | Yes | Yes | Now | Adds to ANSI C12.1 |
| ANSI 57.13-1978 (1987), C57.13.1-1981 (1992), C57.13.2-1991, C57.13.3-1983 (1991), Instrument Transformers | Yes | No | Yes | Now |  |
| ANSI C12.18-1996, Protocol Specification for ANSI Type 2 Optical Port | Yes | No | Conditional “yes” as noted in Comments column | Now | Applies only to Type 2 Optical Port |
| Applicable FCC Regulations | Yes | Yes | Yes | Now |  |

Table 2:  Standards Not Recommended as Requirements for Meter Equipment Used in Direct Access

| Standards | Applicable for DA? | Required in CPUC’s D97-12-048 | Proposed Requirements | Recommended effective date | Comments |
| --- | --- | --- | --- | --- | --- |
| ANSI C12.4-1984 (R1996), Mechanical Demand Registers | No | No | No | None |  |
| ANSI C12.5-1978 (R1996), Thermal Demand Meters | No | No | No | None |  |
| ANSI C12.6-1987 (R1996), Marking & Arrangement of Terminals for Phase Shifting Devices used in Metering | Yes | Yes | No | None |  |
| ANSI C12.14-1982 (R1993), Magnetic Tape Pulse Recorders for Electricity Meters | No | No | No | None |  |
| ANSI C12.15-1990, Solid State Demand Registers for Electromechanical Watt-hour Meters | No | No | No | None | Discontinued, replaced by C12.1 and C12.10 |
| ANSI C12.16-1991, Solid State Electricity Meters | No | No | No | None | Discontinued, replaced by C12.1 and C12.20 |
| ANSI C12.17-1991, Cartridge-Type Solid State Pulse Recorder for Electricity Metering | No | No | No | None |  |
| MTR1-96 Specification for ISO Applications (not required for all meters used in DA) | Yes | Yes | No | None |  |

Table 3:  Standards Belongs to Other Subgroups

| Standards | Applicable for DA? | Required in CPUC’s D97-12-048 | Proposed Requirements | Recommended effective date | Comments |
| --- | --- | --- | --- | --- | --- |
| ANSI C12.18-1996, Type 2 Optical Port | Yes | No | NA | NA | Belongs to MC Subgroup |
| ANSI C12.19-1997, Utility Industry End Device Data Table | Yes | No | NA | NA | Belongs to MC Subgroup |
| ANSI C12.21, Protocol Specification for Telephone Modem (not approved) | Yes | No | NA | NA | Belongs to MC Subgroup |
| ANSI C12.22, Meter Interface to Network Protocol Gateway (not approved) | Yes | No | NA | NA | Belongs to MC Subgroup |
| ANSI Z1.4 and ANSI Z1.9, Sampling Procedures and Tables for Inspection | Yes | Yes | NA | NA | Belongs to MI Subgroup |
| NIST Standards (specific standards to be clarified) | Yes | Yes | NA | NA | Belongs to MI Subgroup |

The following is the modified APPENDIX B of the Joint Parties Letter dated November 24, 1997:

II.	TESTING REQUIREMENTS

This Section describes the testing requirements that meters and metering equipment must comply with for use in direct access metering. These tests are extracted from the Meter Data and Communication Systems (MDCS) Workshop Report, Appendix A, filed with the California Public Utilities Commission, July 25, 1997.

DEFINITIONS OF TERMS USED IN SECTION II:

"Meter":	Device which measures, calculates, records and/or communicates energy consumption data for the purpose of determining the financial obligation for entity consuming energy.  Shall include any optional devices or modules enclosed within the cover.

II.1.	General

II.1.1	The tests specified shall be conducted by qualified facilities.  A qualified facility is a facility that has access to the necessary equipment and personnel to perform the testing requirements specified in this document.

II.1.2	Complete performance testing is required for new Meter types and for major design changes to existing Meter types.  If an incremental change or changes are made to existing meter type, applicable tests shall be performed to assure that Meters meet the certification testing requirements as stated in this section.

II.1.3	The manufacturer shall provide a certified test report documenting the tests and their results to the purchaser. The test report shall be signed by the appropriate manufacturer representative and shall include appropriate charts, graphs and data recorded during testing.

II.1.4	No equipment shall be installed before all tests as outlined in this section are conducted.

II.1.5	Each test shall be conducted by using the selection of Meters specified in Section 4.4.2 of ANSI C12.1-1995 with a minimum number of Meters specified as follows: 1) If Meter is made with a fixed-current rating, a fixed-voltage rating, one number of elements and one service configuration application, a minimum of three Meters shall be tested.  2) If Meter is made with more than one fixed-current rating, one fixed-voltage rating, one number of elements and one service configuration application, a minimum of six Meters shall be tested.  These Meters must be representative of production run meters.

II.1.6	Tests x, y, z, … (See separate table in the Word 7.0 “Cert1.doc” file) shall be conducted using the same Meters selected as specified in II.1.5 above.  Other tests may be done in parallel with the same Meter types but different groups of Meters.

II.1.7	All test Meters shall be kept as a certification proof for one year after the conclusion of the testing.  These test Meters shall be made available during this period to any purchaser for inspection if requested.

II.1.8	Meters which fail during the test shall not be repaired or tested further, but can be analyzed to identify the cause of failure.

II.1.9	When the test Meters fail to meet these testing requirements and after any correction is made on the new test Meters, all  tests shall be re-started over with the new test Meters.

II.1.10	If requested by the purchaser, the manufacturer shall notify the purchaser of the certification test schedule for purchaser’s test witnessing.

II.1.11	If more than a minimum number of meters are certification tested, the test results shall be based on all meters tested.

II.2.	Meter Failure Definition

A Meter shall be designated as failed if any of the following events occur during or after any certification test:

II.2.1	Failure of the Meter to perform all functions as specified in a test procedure.

II.2.2	Failure of the Meter to meet the technical performance specifications included in the Specification.								Alternate statement: Failure of the Meter to perform any function(s) as specified by the manufacturer.

II.2.3	Signs of physical damage as a result of a test procedure.

II.2.4	The occurrence of a loss of data or other unacceptable mode of operation for the Meter as a consequence of a test procedure.

II.2.5	Failures shall be classified as a hardware, firmware or software failure, or a combination thereof according to the following definitions:

II.2.5.1  Firmware failures are errors made during the fabrication of programmable read only memory (PROM) chips such that the required program or instruction set that the microprocessor is to perform is incorrect. Failures of DIP switches, jumpers, and links are also included.

II.2.5.2  Hardware failures are failures that are physical in nature and directly traceable to the component level. Visual observances such as discoloration, cracking, hardening of cables, poor solder joints, etc. are also included.

II.2.5.3  Software failures are failures such as the loss or unintended change of data, the inability to program the Meter, the loss of the Meter program, or the erroneous output or display of false information.

II.3.	Meter Model Rejection Criteria

A Meter model will be rejected if any of the following events occur:

II.3.1	The failure of one Meter during one test procedure, the failure of a second Meter during another test procedure, and the failure of a third Meter during another test procedure different from tests that the first two Meters fail, as specified in Table II.3.1.a:

Table II.3.1.a: Table of failures based on meters tested

|  |  |  | # Meters |  |  |  | Failures in |  | different tests | individually |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Tested |  | 0 |  | 1 |  | 2 | 3 |  |  | 4 or more |  |
|  |  | 3 |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 4 |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 5 |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 6 |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 7 |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 8 |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 9 or more |  |  |  |  |  |  |  |  |  |  |  |  |

II.3.2	The failure of two or more Meters during the same test procedure.

II.4.	Test Setup

II.4.1	The Meter shall be connected to its normal operating supply voltage with a fully charged Power Failure Backup System and shall be energized throughout the duration of the test procedures, unless otherwise stated.

II.4.2	Before testing commences, if necessary, the Meter shall be energized for a reasonable period at room temperature for stress relief.

II.5.	Recommended ANSI C12.1 Tests

All meter certifications shall be performed in accordance with the certification tests described in ANSI C12.1 (NEMA, 1995), unless noted otherwise below.

* Tests 1 through 25:	no clarifications required.

* Test 26:	expand frequency range to 14 kHz - 10gHz to accommodate the application of this meter standard to various communications (e.g. telephone, radio, satellite, power line carrier, etc.) products

* Test 27 through 29:	no clarifications required

* Test 30:	 meter covers removed during test, temperature limits are defined for operations under California weather conditions as

+85° C = T oper-max,

-20° C = T stor-min

* Test 31 through 38:	no clarifications required

* Additional test A1:	sunlight interference test is needed for optical pick-up type retrofit modules (not within scope of existing ANSI C12.1-1995 tests) and is further defined below.

* Additional test A2:	ANSI C37.90.1 Surge Withstand Testing

II.6.	Recommended ANSI C12.20 Tests

All meter certifications shall be performed in accordance with the certification tests described in ANSI C12.20 (NEMA, 1998) for 0.2% and 0.5% accuracy class meters, unless noted otherwise below.

* Tests 1 through 22:	no clarifications required.

* Test 23:	expand frequency range to 14 kHz - 10gHz to accommodate the application of this meter standard to various communications (e.g. telephone, radio, satellite, power line carrier, etc.) products

* Test 24 through 26:	no clarifications required

* Test 27:	meter covers removed during test, temperature limits are defined for operations under California weather conditions as

+85° C = T oper-max,

-20° C = t stor-min

* Test 28 through 35:	no clarifications required

* Additional test A1:	sunlight interference test is needed for optical pick-up type retrofit modules (not within scope of existing ANSI C12.20, NEMA-1998 tests) and is further defined below.

* Additional test A2:	ANSI C37.90.1 Surge Withstand Testing

II.7. 	Test A1 - Sunlight Interference Test

A.	This test verifies the Meter accuracy and full functional operations under direct sun light.

B.	The Meter cover shall be removed during this test.

C.	The Meter shall be exposed to both the incandescent light source and sunlight.

D.	The incandescent light source, Smith Vector #710 or equivalent, shall be used to simulate the sunlight.  The incandescent light shall be 600 watt and 3,200° K blackbody radiation as a minimum.

E.	The Meter shall be exposed to the incandescent light source for minimum five minutes for each position of the incandescent light source.

F.	The incandescent light source shall be pointed directly toward the Meter and positioned at a maximum direct distance of 19 inches from the center of the Meter rotor shaft as follows:

1.	Twelve positions around the Meter base.

2.	Eight positions at a 45° angle from the Meter base.

- One position at a perpendicular to the face of the Meter.

G.	Verify the Meter operations and report the direct and remote meter reads before and after each incandescent light exposure.

H.	The sunlight conditions shall be outdoors, clear sky, bright sunny day and no shades over the Meter.

I.	The Meter shall be exposed to sunlight conditions for 24 hours.

J.	The Meter shall be set in a position as normally installed the field. All Meters under test shall be exposed to the sunlight conditions at the same time and evenly face different directions starting with one Meter facing towards the sunrise direction.

K.	Record and compare direct and remote meter reads at every hour under the sunlight conditions.

L.	To pass this test the Meter shall operate as specified with no observed anomalies and have an accuracy of ±0.3% on both direct and remote meter reads.

III. Certification, Approval & Notification Process:

- Manufacturer issues a certification testing document which is verified and approved by an ESP(MSP) or UDC (user of meters), and

- Manufacturer sends a copy of its certification testing summary document to the CPUC for access to public review or posting on a web site.

IV.	REQUIREMENTS FOR STICKERS, SEALING AND LOCKING HARDWARE

IV.1. Sealing and locking hardware shall be imprinted with company name and logo and be made with recyclable material other than lead.  Sealing hardware owned by the MSPs shall be orange in color and be imprinted with its certification number.

IV.2. Life-support sealing hardware used for identifying a customer premise which has a life support system shall be white in color and imprinted with a red caduceus (medical symbol).

IV.3. A life-support sticker used for identifying a customer premise which has a life support system shall be imprinted with a caduceus (medical symbol).

IV.3. A 480 V sticker used to identify a 480 Volt service panel and meter shall be silver with the red “480 Volt” lettering.

+?. 	APPLICATIONS OF STICKERS, SEALING AND LOCKING HARDWARE (belongs to the Meter Installation Subgroup):

+?.1. Sealing hardware shall be installed on all meter panels, test switches and metering transformer panel sections.  Locking hardware will not be required.  MSPs, ESPs and UDCs may apply the locking hardware as necessary.

+?.2. If a customer premise has a life support device or equipment, a life-support sealing hardware shall be installed, in addition to the regular UDC or MSP sealing hardware, on meter covers, meter panels, test switches and/or metering transformer panel sections where deemed necessary to prevent service interruption during process of metering work.  The application of the life-support sealing hardware shall not be retroactive.

+?.3. If such life-support sticker (as found in PG&E service territory) or sealing hardware is found on customer meter covers, meter panels, test switches and/or metering transformer panel sections, meter workers shall be cautious in performing meter work and not interrupting electric service to the customer premise.  If service will be unavoidably interrupted for any meter work, the meter worker shall notify the customer and obtain customer’s consent prior to performing work.

+?.4. When work is performed on a 480 V meter installation, a 480 V sticker shall be placed on the meter panel near the meter.

V.	REQUIREMENTS FOR LABELING MANUFACTURING DATE ON NEW METERS

New meters shall be laser-edged or labeled with a manufacturing date as sold in California.

VI.	REQUIREMENTS FOR REBUILT, RETROFIT AND REPAIRED METERS

VI.1. Rebuilt Meters:  Meter shall not be rebuilt and repackaged by any entity except its original manufacturer or the manufacturer-authorized licensed agent.  Once the meter is rebuilt and repackaged, it shall be tested for accuracy, labeled as rebuilt and dated accordingly.

VI.2. Retrofit Meters:  Meter may be retrofitted and attached with other devices or modules as long as the original meter design is not modified.  The meter and attached module as a whole revenue metering unit shall be tested according the certification testing requirements.

VI.3. Repaired Meters:  Meter shall not be repaired by any entity except its original manufacturer or the manufacturer-authorized licensed agent.  Once the meter is repaired, it shall be labeled as repaired and dated accordingly.