BEFORE THE PUBLIC UTILITIES COMMISSION OF THE
STATE OF CALIFORNIA

| Order Instituting Rulemaking on the Commission’s Proposed Policies Governing Restructuring California’s Electric Services Industry and Reforming Regulation | ))))) | R.94-04-031 (Filed April 20, 1994) |
| --- | --- | --- |
| Order Instituting Investigation on the Commission’s Proposed Policies Governing Restructuring California’s Electric Services Industry and Reforming Regulation | )))))) | I.94-04-032 (Filed April 20, 1994) |

PERMANENT STANDARDS FOR METERING AND METER DATA USED IN DIRECT ACCESS

Submitted to the
California Public Utilities Commission
By
Permanent Standards Working Group

Names

Attorneys for
COMPANIES

Address
Post Office Box
City, California  9xxxx

Telephone:

Facsimile:

Dated:  July 29, 1998

PERMANENT STANDARDS FOR METERING AND METER DATA USED IN DIRECT ACCESS

Submitted to the

California Public Utilities Commission

By

Permanent Standards Working Group

July 29, 1998

Table of Contents

(To be edited when report is completed)

I. 	Executive Summary

Commission Decision 97-12-048 ordered the creation of a Permanent Standards Working Group, (PSWG) to review the interim standards adopted in the decision and recommend what permanent standards should be adopted by the Commission. The PSWG met and worked intensively from February through July 1998.  In the following report, the PSWG recommends permanent requirements for meter and meter-related data.  All recommendations included in this report were voted through by at least two-thirds of the eligible voting membership, not including abstentions and absences.  However, there were areas without 100 percent agreement.  If provided by the party(ies) alternative proposals are included.  All recommendations include the list of entities who voted to adopt the recommendation, entities who voted against, and entities who abstained.

The PSWG report includes recommendations in the following areas:

- Meter Equipment

- Meter Communications

- Meter Data Management and Meter Reading

- Including rules for validating, editing, and estimating meter usage data

- Meter Installation, Maintenance, Testing, and Calibration

- Including classifications of different levels of meter workers

Meter Equipment

The interim standards adopted by the Commission specified that a meter must be equivalent to a meter that the utility uses, be Independent System Operator (ISO) compliant, or meet ANSI standards recommended in the Meter and Data Communication Standards (MDCS) report filed with the CPUC on July 25, 1997.   Using the interim standards as a foundation, the PSWG identified issues requiring additional clarification and the list of ANSI standards. PSWG also recommendations testing and certification processes for new meters,  locking hardware and sealing hardware used for meters, and requirements for any repair or modification of a meter.  The PSWG recommendations in this area were unanimously passed without recorded dissent.

Meter Communications

The Commission in D.97-12-048 expressed a desire for the meters used for direct access have an open architecture to allow interoperability to take place.  In turn, interoperability of equipment would allow customers to chose from multiple service providers without having to replace equipment.  However, having universal interoperability and interchangeability between the meter and data retrieval technologies is not feasible without constraining technological alternatives.  The PSWG sought to define where universal interoperability and interchangeability could be realistically achieved.  The interface between the meter and hand-held devices using an optical port is one area where standards are recommended by a majority of the participants. If pulse output is used, and PSWG recommends that  contact pulses (KYZ) be used.

One of the ways to enable different devices to communicate with each other is to establish a common data format.  This offers a foundation for manufactures to develop equipment that can communicate with other manufacturers’ equipment. The PSWG recommends a data format that will allow interoperability to develop (ANSI C12.19).

To ensure the retrieval of minimal information at the meter and allow customer to read the meter, a near unanimous recommendation is that meters must have a visual display on the meter.

To ensure the integrity of meter usage information, only authorized persons should have access to read, update, reset, or reprogram the meter.   The PSWG recommends three levels of access: (1) full read, write, reprogram; (2) reset and updating for meter reading and billing functions; and (3) read only. The ESP has the responsibility for assigning passwords to the appropriate parties.

Meter Data Management and Meter Reading

The PSWG reviewed the existing definitions and standards for meter data management agents established in CPUC D.97-12-048.   The current definitions require an MDMA to perform all functions of Meter Data Management and Meter Reading.  The PSWG defined both functions and recommends that an MDMA can subcontract functions such as meter reading.   In addition, an MSP may contract with the MDMA to reprogram meters remotely.

The PSWG reviewed the standards for validating, editing, and estimating (VEE) interval data established by the CPUC and recommended modifications and enhancements based on market experience.   In addition, PSWG developed VEE rules for monthly data.

Based on recent operational experience of MDMAs, the PSWG recommends that MDMA data availability performance standards tracking begin with second billing cycle.  In addition, that the five day availability standard be reduced to 99.0 percent.

The PSWG reviewed the recent work by Utility Industry Group (UIG) on a national standard meter usage data exchange.   The PSWG recommends a process to review the EDI standards and develop a consistent statewide implementation plan to migrate to EDI.   A near unanimous recommendation is for EDI implementation to occur by December 31, 1999.

Meter Installation, Maintenance, Testing, and Calibration

The CPUC established an interim process for the certification of Meter Service Providers and sought recommendations for a uniform standards for testing and maintaining meters for direct access.  The certification process is entity based not worker based and does not recognize different meter installations require different skills.  The PSWG started with the meter worker classes that was developed in the Fall of 1997 by UDCs, MSPs, and ESPs, and was sent to Commissioner Advisor Bob Lane.  The group made additional refinements to the worker classes.  The PSWG recommends, without any opposition in attendance, standards for five levels of meter workers.   In addition, The PSWG developed and recommends a set of procedures that workers must follow when installing or removing a meter.

The PSWG develop a process of certification whereby an MSP may issue certifications for meter worker classes 1-3.  However, prior to issuing certifications, the MSP must have their training materials and program approved by the CPUC.  Certification for meter worker classes 4a, 4b, and 5 require a practical exam administered by the CPUC.  The group has near unanimous agreement on the certification process.

The Commission in D.97-12-074 recognized there needs to be a program to test and maintain meters on a regular basis.  The PSWG endorsed PG&E’s, SCE’s, and SDG&E’s recommendation filed in February 1998 for the testing and maintenance of meters.   Meters will be tested dependent upon the amount of usage of the account.  Meters with high usage are tested more often.  In brief, meters may be tested annually, biannually, or based upon statistical sampling.   The group also recommends a set of meter testing procedures and meter performance criteria.

I.1. 	Recommendations on what CPUC should adopt

PSWG recommends that the CPUC adopt all recommendations in the report and the Appendices that have no alternative positions.

I.2.	Recommendations on decisions CPUC must make

PSWG requests that the CPUC review recommendations that have an alternative position and decide how to proceed based upon the information provided.

I.3.	Process for Standard Revisions

PSWG categorized several subject areas and determined that some will require immediate ongoing work and some will only need to be addressed infrequently. PSWG recommends that the Commission formally adopt the recommendations for the various subject areas in Section X of the report.

II.	PSWG History and Organization

II.1.	History/Regulatory references

CPUC Decision 97-12-048 ordered the creation of a Permanent Standards Working Group (PSWG) to review the interim standards adopted in the decision and recommend what permanent standards should be adopted by the Commission. The decision also ordered the PSWG to indicate whether other standards are expected in the future and recommend a process for reviewing possible future changes to the permanent standards. Within 180 days of the initial workshop, the PSWG was to file proposed permanent standards with the CPUC.

Consistent with that order, the Energy Division convened a workshop on January 29, 1998. The PSWG created a structure in which participation was inclusive, open and equitable. The PSWG agreed that the scope of the group was to:

- Review interim, national, and Utility Distribution Company (UDC) standards--in progress or completed--and make recommendations to the CPUC

- Propose an ongoing process for standards selection

- Clarify functional requirements and business processes

The following evaluation criteria were applied in the selection of standards/requirements for the Direct Access Marketplace:

- Be consistent with RSIF and DQI data requirements

- Be consistent with direct access rules

- Meet safety, accuracy, and reliability consistent with the current UDC standards for meter reading or, higher, if business requirements demand

- Address interoperability and open architecture

- Promote customer choice

- Allow market innovation

- Prevent metering from being a barrier to changing suppliers

- Support cost-effective and efficient business processes

- Be feasible to implement

- Address the minimum functional/business requirements

- Promote statewide uniformity

II.2 	Organization/structure/meeting frequency

The PSWG established four subgroups, each dealing with a different technical area of review. The Meter Data Management subgroup also created a technical subcommittee to address validating, editing, and estimating of usage data.

The four subgroups are:

- Meter Equipment Subgroup—Chair, Jamie Patterson (CEC)

- Meter Communications Subgroup—Chair, Kirsten Stacey (PG&E)

- Meter Data Management & Meter Reading—Chair, Chris King (CellNet)

- Validating, Editing, and Estimating Subcommittee—Chair, Kathy Smith (ABB)

- Meter Installation, Maintenance, Testing, and Calibration—Chair, Michele Wynne (MZA Grid Services)

A separate subcommittee, chaired by Augie Nevolo (EPRI), was created to investigate the issues of national coordination and the ongoing review of evolving standards that may apply to California and to suggest a process for changing applicable standards after permanent standards are adopted by the CPUC. (See Appendix E)

The group agreed that the Plenary (full PSWG membership) would address unresolved issues, vote on final recommendations, address questions or requests from the subgroups, and review business requirements.  The facilitator for the PSWG Plenary was Kirsten Stacey (PG&E) and the Secretary was Bill Buckley (Itron). The four subgroups met once every two weeks for half a day each. Once a month, the PSWG Plenary convened to monitor overall progress and vote through the items recommended by the subgroups for adoption. Additionally several side groups held conference calls and/or worked on issues via the Internet.

The Office of Ratepayer Advocates (ORA) provided an e-mail website, administered by Jim Price, for an “e-mail exploder” for distribution of documents. E-mails sent to this exploder were distributed to all PSWG members and other subscribers who were interested in the process. On June 29, 112 individuals were subscribed to the exploder representing 64 organizations. This communication tool greatly enhanced information exchange and allowed entities who could not participate in PSWG to stay informed of developments that might affect them.

Overall the process was intense and included active input from a minimum of 25 different entities including meter service providers (MSP), meter data management agents (MDMA), meter manufacturers, Energy Service Providers (ESPs), Utility Distribution Companies (UDCs), employee representative groups, consumer representatives, and municipal utilities.

II.3	Voting Rules and Membership

On February 29, 1998, the PSWG adopted the following voting and membership rules:

Rule #1 - A quorum consists of a minimum of 50% of the total qualified voting members.

Rule #2 - Meeting attendees may speak to the group only when recognized by the facilitator. Side discussions will not be allowed. Sarcasm is not permitted and subject to censure.

Rule #3 - Final recommendations to the CPUC will be decided by a two/thirds majority vote of the qualified voting membership. The final report will include a list of every one who voted and will include any submitted minority reports. The word “consensus” will not be used.

Rule #4 - There will be a single vote for each entity.

Rule #5 - To maintain voting membership,  an entity must have representatives at two of the last three meetings.  The three meetings will include the current or most recent meeting.

Rule #6 - Membership is open to stakeholders and interested parties (firms or entities, not individuals) defined as manufacturers, government entities, trade organizations, consumer advocacy groups, consultants, utilities, employee organizations and ESPs, MDMAs, UDCs, MSPs.  Eligibility for membership is subject to challenges at the PSWG meeting.  Consultants can vote only if representing an entity.

Rule #7 - To accommodate parties’ desires, a simple majority of parties in attendance is required to approve modification of meeting dates or locations, or other minor issues.  These issues are called motions of convenience.

Rule #8 - The four subgroups will have the same voting and membership rules as the PSWG Plenary.

Rule #9 - A two/thirds majority of qualified voting members is required to change Procedures or Voting Rules.

Rule #10 - Proxies are not permitted for non attendees of meetings.  However a proxy is permitted for a voting member who attends a meeting,  in the event that the member’s absence is temporary from that meeting.  Such proxies will be submitted to the chair in writing, designating the person who is to vote on behalf of the qualified member exercising the proxy privilege.

Rule #11- A minimum notification of 14 calendar days in advance is required for meeting notifications that will include meeting location, meeting dates, and how to contact the host. Notification will consist of either posting the meeting announcement to the ORA WEB page or to the E-Mail exploder (pswg@dra1.cpuc.ca.gov)

Rule #12 - A minimum notification of 7 calendar days in advance is required for advance meeting agendas.  Agendas will include items that are to be voted on.  Any agenda is subject to the approval and changes of the membership at the meeting. Notification will consist of either posting the meeting agenda to the ORA WEB page or to the E-Mail exploder. (pswg@dra1.cpuc.ca.gov)

Rule #13 - The Roberts Rules of Order will only be utilized at the facilitator’s discretion for handling difficult, or contentious issues.  If conflicts occur between these rules and Roberts Rules of Order, these rules will prevail.

Rule #14 - When voting, the qualified members may vote “YES,” “NO,” or “Abstain.” Providing comments or reasons, by the entity voting, is optional.  A written minority report may be included with the majority report or reasons for any vote.

Rule #15 - When calculating the two thirds majority,  “abstain” votes will not be included.

III	Interconnection, Open Architecture, and Interoperability

Decision 97-12-048 includes considerable discussion on open architecture and interoperability. The issue is complex and required significant discussion by the PSWG. The first step was to determine the scope of work. The meter communications subgroup created Diagrams A and B to visually describe how meter and meter data systems are interconnected and identify potential areas where interoperability would be feasible.  The diagrams are intended to show the connections between functions and layers of possible interoperability.  The boxes in both diagrams describe functions, not specific equipment types.

Diagram A shows there are two possible places (represented by small circles) to have open architecture.  The first is between the MDM and retail market participant.  The second is between the meter and meter reading system.  The  various connections between the meter, meter mount, and communication device are grouped together in the ellipse and further detailed in the following boxes:

(1) Communication Mechanism

(2) Physical Communication Connection

(3) Meter Device Data Format

(4) Physical Communication Device

Box (1) Communication Mechanism:   Communication technology by which information is transported to and from a meter.  This includes communication protocol, speed, and medium.  The protocol includes ‘handshaking’ and data format.  The speed determines how fast the data are transmitted.  The medium is the environment in which the data are transmitted.  Examples of these communication technologies are radio, microwave, power line carrier, phone, satellite, cellular, cable, etc.

Box (2) Physical Communication Connection: is a gate way through which data or information is transmitted.  The connection may be different for each communication technology and is established when communication devices needs to communicate or transmit data among each other.  Some of the existing physical connections as seen on meters and meter devices are optical port, phone jack, antenna, wires, etc.

Box (3) Meter Device Data Format: defines how data is organized when transported through its gate way to its receiving ends.  This data format may be the same as the device data table format inside a meter or meter device or it may be different.  This data format is different from the communication protocol of data bits in which each byte or group of data bits is transmitted.

Box (4) was assigned to the Meter Equipment Subgroup.   The PSWG agreed not to recommend a standard for Box (1). The Meter Communications Subgroup focused its discussions on Boxes (2) and (3) and standards (ANSI C12.18 and  ANSI C12.19.)

Diagram B is for illustrative purposes and clarification. The group agreed not to identify or recommend standards for every interface level (numbers 1 through 5 in Diagram B).  The PSWG focused on external interfaces.  If an interface is mandatory, it cannot be embedded in another interface.   However, an optional interface can be embedded.

Diagram B

Decision 97-12-048 states (findings of fact #9) “[t]he goal of direct access is to facilitate customer choice” and (findings of fact #10) “[o]pen architecture serves as the vehicle for allowing interoperability to take place”.

“Interoperability is the ability of dissimilar devices or systems to communicate between each other in such a way that the characteristics of the device or system providing the service to the user of the data are transparent.  …In order for different metering systems to communicate with each other, consideration must be given to an open architecture standard.  … Open architecture serves as the vehicle for allowing interoperability to take place.   Interoperability in turn enables customers to choose from multiple suppliers of electric services the providers that best meet their needs.”

The group started with the description of interoperability in the CPUC decision, discussed the degree of interoperability needed for direct access, and focused on some existing standards to achieve a level of interoperability.  After several discussions, the PSWG came to the following conclusions:

- A degree of interoperability is possible and could be achieved at system levels.

- Interchangeability of all discrete components across technologies is not feasible.

- Technology-specific interchangeability requires specifying a standard at every interface and is not practical for all technologies at this time.

- Adoption of some existing communication standards allows some interchangeability within a technology and provides a foundation for the adoption of future communication standards.

The group questioned whether interoperability at the MDM server through the current mandated data format was sufficient such that no further standards needed to be recommended. However, the closer interoperability is to the point of measurement, the easier it is for a customer to switch ESPs. Therefore, this group elected to define some level of interoperability at plane 3 of Diagram B.

In conclusion, the group recommended that interoperability should be available in the following four areas:

- MDM-Output data format. The group recommended migration to Electronic Data Interchange (EDI).

- Data format tables - The meter device data format (Box #3 of diagram A) can provide a basic interoperability-functional continuity for the market place. The group recommended ANSI C12.19.

- Physical communication device Boxes #1 and #2 of Diagram A connect the device and provide the handshake. The group recommended ANSI C12.18 for type 2 optical ports.

- The meter must have a visual kiloWatt hour display.

IV. 	Meter Communications

The PSWG addressed the communication between the meter and the meter reader and how to facilitate this communication for all settlements.  The goal was to provide customer choice without imposing undue expense on the market participants or precluding product innovation.  In discussions, the group identified applicable ANSI standards and made recommendations as to which should be adopted to enhance interoperability. The group also recommends requirements for the meter display, contact output (KYZ), and meter passwords.

IV.1.	Communications Standards for Direct Access

The PSWG reviewed and discussed existing communication standards that would enable a wide number of market participants to access and retreive data from electric meters.  This could be accomplished by the following:

IV.1.1	ANSI Type 2 Optical Port Standard (C12.18)

For on-site data retrieval, ANSI C12.18 defines the physical layer, data-link layer, and a portion of the application layer for a Type 2 optical port.  It allows interchangeability at these three layers.

IV.1.2	Requirement of ANSI C12.19 Standard Application

The group discussed ANSI C12.19, a data format standard, as a means to achieve a minimal level of interoperability.

ANSI C12.19 [Title]– 1997 standard is also known as IEEE1377 – 1997 and Industry Canada MC –X XX.  These three documents  are technically identical, developed jointly, and represent a North American standard for Utility Electric, Gas, and Water metering.  The document(s) provides a standard format for metering data with flexibility to meet manufacturers’ needs which range from simple to complex meter design.  The standard(s) provides for new functionality not yet approved (via manufacturer’s tables).  The three standards bodies (ANSI, IEEE, and Industry Canada) are continuing to meet to ensure that new metering functionality are supported by the standard(s) such that the standard(s) is dynamic and responsive to the North American  metering data needs.   The new functionality of the standard(s) is "backwards compatible" meaning that the first devices using the standard will always work with communications nodes using subsequent versions of the standard(s).  The standard(s) represents "metering data structure format" which is technically placed in the application layer (Layer #7 of the ISO communications stack).  This allows the data to be carried by many different communications transport mechanisms.

The PSWG agreed that although the meter should communicate in the format specified by ANSI C12.19 it should not be required to store the data in the ANSI C12.19 format.

The discussion of ANSI C12.19 was quite extensive. The application of ANSI C12.19 alone may not provide a “plug and play” option to the marketplace (i.e. if a customer has a meter which communicates over a microwave frequency and switches to an ESP who reads meters over the telephone, the meter will have to be replaced.) Additionally, ANSI C12.19 has a table which would allow a manufacturer to program some data in a manner that is proprietary. Another concern was the costs of implementing ANSI C12.19 on the market. Although a market cost evaluation was not feasible, several of the market participants are currently developing these capabilities.

The majority of the group felt that ANSI C12.19 would create a degree of interoperability. For example, PSWG recommended that ANSI C12.18 be adopted for meters with type 2 optical ports. Meters with ANSI C12.18 compliant optical ports could switch MSPs/MDMAs transparently. Additionally, telephone modem technology is consistent enough that ANSI C12.19 would also make it largely possible for customers on telephone-read meters to switch ESPs without having to replace their meters. This would also be beneficial to the UDCs in their role of providing default services.

One issue that the group grappled over was the use of ANSI C12.19 for radio frequency technologies.  The majority agreed that currently ANSI C12.19 would not work well for radio frequency based technologies. It would have an impact on bandwidth and response times. Also it would increase the message length, making radio frequency transmissions more expensive (unless the manufacturers change bandwidth.) In order to accommodate these challenges, the group considered exempting radio frequency technologies from compliance. However the simpler alternative was to exempt all meter (TYPES OR PRODUCTS ??)products released before March 20, 2000 from compliance for the duration of their commercial product life. This would allow time for the radio technologies to design data communications to ANSI C12.19 and continue selling their current products.

ANSI C12.21 [TITLE] and C.12.22 [TITLE] were potentially identified for Box #2 of Diagram A.  They have not been approved by ANSI, but the PSWG recommends they be reviewed when they are approved.

IV.1.3 KYZ Contact Output and Consumer Protection Recommendations

Meters are not required to have a contact output . If a meter has contact output it should be KYZ per ANSI C12.1.

It was noted that many DA customers currently have energy management systems utilizing KYZ outputs.  The PSWG recommends DA customers be notified by their ESP if  a meter change will not be compatible with their energy management systems.  [VI-?]

^

IV.1.4.	Visual Meter Read Requirements:

The PSWG agreed all DA meters shall have a visual kWh display and must have a physical interface to enable on-site interrogation of all stored meter data. [VI]

There are two reasons for requiring a visual meter display; 1) For consumer protection. The consumer can verify that the meter read matches the bill, and 2) for on-site interrogation when another communications system fails. This would enable entities who are responsible for billing/settlements to obtain the meter read when investigating the communications failure. The PSWG agreed that the dials on a electromechanical meter are sufficient for on-site interrogation. However, an electronic meter must have a visual display of the total kWh energy consumption as a minimum.

Alternative position:

ABB and Nertec do not believe the requirement that all meters have a local display is in the consumer’s or industry’s best interests. The PSWG should recommend the functional requirements necessary to make the market work, but not limit the technology based on today’s products.  Two reasons for local access to total kWh have been discussed - the customer’s need for access to verify their bill, and the UDC’s need for access if all other means of obtaining a meter reading fail.  Both of these needs could be met today by different technologies.  For example, a customer with a solid state meter may prefer the convenience of having a display inside their home or business, or to access the data on their pc, rather than walking outside to read their meter.  Technologies such as CEBus or LonWorks can be used to provide this capability today.  A meter could have a local Type 2 optical port that complies with C12.18 and ANSI C12.19, providing standard access at the meter for the UDC to ALL meter data, not just total kWh.  ABB and Nertec are not pushing either of these technologies, but desires to point out there are alternate solutions.  By prescribing the technology required to meet legitimate customer and UDC needs, the PSWG is limiting product innovation and imposing additional costs on the consumer, who may need to pay for a display both on the meter and in the home or business if that is what he/she prefers.

## V. 	Meter Equipment

The PSWG reviewed the applicable national standards and recommended which performance standards should be required for direct access metering. Appendix A identifies the following requirements for direct access meter products including:

- Standards for meter hardware

- Certification and testing requirements for meter products

- Registration and centralized database of DA compliant meter types

- Stickers, sealing and locking hardware

- Labeling manufacturing date on new meter products

- Requirements for rebuilt, retrofit, and repaired meter products

Table 1 of Appendix A shows the standards that the PSWG recommends as the minimum performance, accuracy, and safety requirements for all direct access meters and metering equipment to be installed in California. Table 1 also shows additional clarification for tests for ANSI C12.1 [TITLE] and C12.20 [TITLE].

Table 2 of Appendix A shows the standards that the PSWG recommends not be required for any DA meters or metering equipment to be installed in California. These standards are either not performance based standards, are obsolete, or are applicable only to meters and metering equipment that are no longer sold or manufactured. These standards are not necessary and should remain for voluntary use only.

Description of recommended standards from Table 1:

ANSI C12.1-1995 Code for Electricity Metering:

This is the basic accuracy, safety, and performance requirement standards for meters and metering equipment. The PSWG recommends the standard be used in accordance with the requirements of Section II in Appendix A. These additional requirements in Section II of Appendix A are currently or will be required for all UDC meter purchases.  Some meters that have not met the requirements of Section II have failed to operate accurately in past meter performance trials within the State.

ANSI C12.7-1993 Watt-hour Meter Socket:

The PSWG recommends that meter sockets not be required. But, if a meter is socket mounted, then the socket and the associated meter shall meet the requirements of ANSI C12.7. This is to ensure the accuracy and safe installation of socket mounted meters.

ANSI C12.8-1981 (R1997) Test Blocks and Cabinets for Installation of Self-Contained A-

Based Meters:

This is a safety standard for the unique requirements of A-Based meters. This standard ensures that A-Based meters do not represent an electrical hazard.

ANSI C12.9-1993 Test Switches for Transformer-rated Meters:

This standard is a safety standard for the proper marking and installation of test switches.

ANSI C12.10-1997 Electromechanical Watt-hour Meters:

This standard defines the configuration, accuracy, and performance requirements of Electromechanical meters and complements ANSI C12.1-1995.

ANSI C12.11-1987 (R1993) Instrument Transformers for Revenue Metering:

This standard defines accuracy and performance requirements for Instrument Transformers for metering. This standard will ensure that UDCs continue to install the same accurate metering instrument transformers as they currently install for their own metering needs.

ANSI C12.13-1991 Electronic TOU Registers for Electricity Meters:

This standard defines accuracy and performance requirements for Time-Of Use (TOU) Registers for Electricity Meters. This standard only applies to meters that have TOU Registers.

ANSI C12.18-1996 Protocol Specification for ANSI Type 2 Optical Port:

The PSWG recommends that optical ports not be required. If a meter has an optical port that is physically identical to an ANSI Type 2 optical port, then the optical port shall meet all the requirements of ANSI C12.18. Other optical port types are exempt from this requirement.

ANSI C12.20-1998 0.2% & 0.5% Accuracy Class Meters:

This standard adds additional accuracy and performance requirements to ANSI C12.1 for the class of meters defined in this standard that would otherwise not be covered. The ANSI C12.1 standard left open to interpretation many details that could be defined by purchasers. The PSWG recommends for purchasing consistency in California,  the standard be used in accordance with the requirements of Section II in Appendix A. These additional requirements are currently or will be required for all UDC meter purchases. Some meters that have not met the requirements of Section II have failed to operate accurately in past meter performance trials within the State.

ANSI C37.90.1-1989 (R1994) Surge Withstand Capability (SWC) Test:

This safety standard adds performance requirements to ANSI C12.1.

ANSI 57.13-1978 (R1987)

ANSI 57.13.1-1981 (R1992)

ANSI 57.13.2-1991

ANSI 57.13.3-1983 (R1991) Instrument Transformers:

These are accuracy and safety performance standards to be used in conjunction with ANSI C12.11. This standard will ensure that UDCs continue to install the same accurate metering instrument transformers as they currently install for their own metering needs.

Applicable FCC Regulations:

Meters and associated equipment shall meet all applicable FCC regulations.

PSWG recommends that the CPUC adopt the standards listed in Table 1 of Appendix A. Further, PSWG recommends that the CPUC not adopt the standards listed in Table 2 of Appendix A [VI ?].

VI. 	Meter Data Management/Meter Reader

The PSWG reviewed the interim standards related to meter reading and meter data management and makes the recommendations included in the following sections.

Summary of recommendations:

- Adopt more specific definitions of MDMA functions, separately defining Meter Reading and Meter Data Management

- Allow subcontracting of MDMA functions

- Allow an MSP to subcontract with an MDMA to reprogram meters remotely

- Define specific MDMA support requirements as recommended in this report

- MDMA data availability performance standards begin with second billing cycle

- Modify the five day MDMA data availability standard to 99.0 percent (99.0%) of accounts

- Develop defined procedures for when MDMA is unable to deliver the data to the server within five days

- Adopt interval and monthly VEE standards

- Migrate to EDI data formats

#### VI. 1. 	MDMA Business Functions

The PSWG discussed the functions performed by the MDMA and recommends describing them separately as Meter Reading (MR) functions and Meter Data Management (MDM) functions.  This will facilitate approval processes for these functions, especially if they are ever approved separately.  Specific functions are listed in the recommendation in Appendix C.  [VI??]

VI.2.	Subcontracting MDM Functions

Decision D.97-12-048 requires an MDMA to be accepted for all required MDM functions.  This does not allow an MDM to easily subcontract functions, or for an entity to specialize in providing a specific MDM function such as meter reading.  The PSWG believes that while an MDMA should retain full responsibity for all required MDM functions, it should be able to subcontract sub-functions out to other approved entities.  [VI??]

VI.3.	MSP Ability to Subcontract Meter Programming to MDMA

The PSWG recognizes that reprogramming a meter remotely is in some cases more efficient than dispatching a technician to reprogram a meter on site.  MDMAs typically have remote communications capability with the meters they read.  The PSWG recommends that an MSP should be allowed to subcontrac tiwh an MDMA, with respecti to its capacity as an operator of a meter communications sytem, to reprogram meters remotely.  The MSP must retain responsible charge over meter reprogramming.  [VI??]

VI.4.	MDMA Support

The PSWG discussed the need for the MDMA to provide support to ESPs and UDCs.  It recommended required support levels in two areas [VI ??] :

- Technical and business assistance during normal business hours (8am to 5pm Pacific to address question and concerns on data availability, corruption and adjustments, and systems technical support.

- Technical assistance via a support pager available 24 hours a day/365 days a year to address issues of server availability

VI.5.	Meter Data Availability Performance Standard

The PSWG reviewed the current performance requirements associated with MDMA timeliness. These performance standards, as established in Decision 97-12-048, Section III, D, 3, e, Interim Standards for Meter Reading, (2) Timelines for Validated Meter Reading: (a) Interval Meter & (b) Non-Interval (Monthly) data, were developed based on current and historical business and retrieval practices. Now that the DA market is fully operational these new business practices and data retrieval functions can be better evaluated.

The particular performance standard at issue (2), (a), (iii), requires "99.99% of all usage data delivered to the MDMA server within five days of the scheduled reading date of the meter," and (2), (b), (iii) “99.99% must be available by 6:00 a.m. on the 5th working day after the scheduled meter reading date.”

The hand off between the UDC and ESP at times causes information to be delayed.  This problem, related to the customer’s initial switch, will exist in the market for the foreseeable future, and skews the MDMA performance statistics.  Since most problems affecting these performance standards occur during the initial switch month (commencing bill), this first month should be disregarded from the performance statistics.  The tracking of these statistics for a particular account should begin after one complete billing cycle has ended. [VI ??]

The current timeliness performance standard of 99.99% translates to 1 account in 5,000 not to the server would cause an MDMA to be out of compliance.  This has proven to be an unreasonable goal and does not reflect the current performance of the market. The PSWG recommends modifying the 5 day performance standards to 99.0%. As technology changes and new systems and processes impact the market performance, these standard should be reviewed.   [VI ??]

Furthermore, there are no defined procedures to address the situation when the MDMA is unable to deliver the data to the server within five days. Currently ESPs and MDMAs will do whatever is necessary to estimate the data and get it to the Scheduling Coordinator (SC). Since there are no guidelines or procedures for this, the process is inconsistent and unreliable. The PSWG recommends that this process be formalized and documented by the market participants (MDMAs, UDCs, ESPs) based on the VEE rules and be included in the VEE standards or other appropriate industry document.  This needs to be done as quickly as possible. [VI??]

The PSWG also discussed other situations in which the MDMA should not be penalized for being unable to read its meters in time to meet the required performance regarding the amount of estimated data.  These situations include large catastrophic events and meter failures that are out of the MDMA’s control.

The PSWG recommends that the CPUC adopt the policy that in the event of a large catastrophe (i.e., hurricanes, earthquakes, etc.) that precludes the MDMA reading meters, the MDMA should estimate and post the data.  This estimated data should be reported separately by the MDMA in their performance report, and not be included in any performance penalties assessed against the MDMA. [VI?? - VEE vote item]

The PSWG also recommends that estimated data due to meter failure where the meter is not accurately recording usage should be reported separately by the MDMA in their performance report, and not be included in any performance penalties assessed against the MDMA. [VI?? - VEE vote item]

#### VI.5.	Electronic Data Interchange (EDI)

PSWG’s recommendations for use of EDI are for implementation of subsets of standards developed by the Utility Industry Group (UIG), and for extension of those standards to meet California’s needs, through interaction with UIG.  The UIG works in the interest of the utility industry to improve the methods of transferring business information through EDI, including representing utilities, their suppliers, their customers, and other interested parties as an Industry Action Group to the American National Standards Institute (ANSI) Accredited Standards Committee (ASC) X12, specifically in the standards-setting process, for their EDI business needs.

Electric end-user meter data transmission in California during 1998 uses the California Metering Exchange Protocol (CMEP), which was developed by Pacific Gas and Electric Company (through consultation with the Meter and Data Access Working Group) and whose applicability is limited to California. CMEP was developed in order to meet the January 1, 1998, implementation date for California’s electric industry restructuring.  It’s introduction includes the statement:  "This protocol is intended for interim use while standards bodies are producing an appropriate replacement."

The PSWG recommends a migration to EDI for meter usage data following the definition of a consistent, statewide implementation guide developed by all interested parties.  Migration to EDI for usage data is to be completed by December 31, 1999.  [VI ?]

In addition, the PSWG recommends that EDI is the preferred standard for all new MDMA transactions.  [VI??]  Transactions regarding meter specific information flow should also be developed using EDI.  [VI??]

VII.4	Validating Editing and Estimating (VEE)

The VEE subcommittee held a series of conference calls and meetings to review the Interval VEE Rules 1.3 and develop VEE rules for monthly data.  Notices for all meetings and conference calls were distributed to the PSWG email exploder and website, as well as anyone who asked to be put on the mailing list; they were also announced at the joint UDC/MDMA meetings.  The meetings and calls were open to all interested parties.  Notes for each meeting or call were also distributed to the PSWG email exploder and website, as well as interested parties.

Several principles developed during the course of the meetings, which apply both to the work this spring as well as to any future work:

- The rules should promote fairness in the marketplace

- The goal of the rules is to provide quality data

- Solutions must fit the magnitude of the problem - when evaluating solutions, the costs must be considered against the frequency of occurrence and the quality of the data

- Modifications to the rules should typically be required when they result in a significant improvement in the data quality

- When modifications to the rules are made, reasonable implementation plans should be defined allowing time for all parties to comply

- Variations for different technologies should be allowed where appropriate

# Interval Data

The group reviewed the existing rules in light of market startup, clarified the rules, and addressed situations that were not addressed previously due to time constraints.  The detailed rules are included as separate documents.  Major changes and clarifications include the following:

- Spike check threshold - For very low usage customers, a valid pulse count of a few pulses may result in failing the spike check.  An optional minimum threshold was added to allow MDMAs to automate checking for this condition and passing the data.

- kVARh check threshold - For very low usage customers, a valid pulse count of a few pulses may result in failing the kVARh check.  An optional minimum threshold was added to allow MDMAs to automate checking for this condition and passing the data.

- Use of partial days as reference data for estimation - Days containing less than 24 hours of good interval data may be used as reference data to estimate data for other days

- Use of days containing power failure as reference data for estimation - Days in which a power failure occurred should not be used as reference data for estimation.

- Use of accurate meter readings to scale estimated intervals - When data is estimated based on historical data, and accurate meter readings or usage are available, the estimated data can be scaled based on the actual usage.

- Simplified proration algorithm (when meter clock is off) - A simpler method to prorate data when the meter clock was off is provided.

- Automating handling of irregular usage customers - Rules are provided to determine which customers are irregular usage, and how special tests can be designed and automated for those customers.

- Test mode intervals - The MDMA may report zero usage during times when a meter was in test mode.  The MDMA must not report the test load.  If the meter is inadvertently left in test mode, the data will be estimated.

- Clarifying interpretation of reference day selection for estimation - reference days selected as “like” days for estimation are the days chronologically closest to the day requiring estimation, whether that is in historical data or the present billing period.

- High/low usage check - The high/low usage check is always performed on the data that has passed or been verified for previous checks, with no estimated values included.  It can optionally be performed on the final data, including estimated values.

- kVARh checks - kVARh checks are only required when kVARh is used for billing.

Only 3 of the above changes were considered required by the group; the rest are optional and may be implemented at the MDMA’s discretion.  The proposed implementation plan for the changes is described in the following table.  The Optional/Required column indicates if market participants will be required to make this change.  The Earliest date acceptable column indicates the earliest a market participant is allowed to implement this change (note to UDCs - this means the VEE test would need to allow these options), and the Required by column indicates the date by which market participants must implement the option (only applies to required options).  MDMAs that were accepted prior to the required date must comply, but do not need to go through the acceptance process again.

During the discussion, it was noted that some of the optional changes have a bigger impact on some technologies than others.

The group felt examples and flowcharts would be helpful to new market participants, but did not have time to develop them.  Also, the checks should be reviewed for effectiveness after there is more actual market experience; checks that don’t uncover expected problems should be modified or deleted, and checks may need to be added to uncover problems not foreseen when the tests were written.

# Monthly Data

The group further defined the monthly validation and estimation rules found in the Commission ruling, as well as defining estimation rules for TOU data.  The rules defined include the following:

- Time check of meter reading device/system

- Time check of meter

- High/low usage check

- High/low demand check

- Time-of-Use (TOU) check

- Zero usage on active meters

- Number of dials on meter

- Number of demand decimal places

- Meter identification

The group agreed that the usage for inactive meters check was not the responsibility of the MDMA and should not be required.

Estimation rules were defined for:

- Usage

- Demand

- TOU Usage

- TOU Demand

# Recommendations

General Recommendations:

- Sanction ongoing work to clarify the rules by adding examples, flow charts, and definitions.

- Review the rules after the market has been operational.  Suggest review interval rules 4/99 and review monthly rules 6/99.  A change management procedure should be put in place, following the principles outlined in the Introduction.

- Eliminate the existing requirement to include the estimation algorithm when the data is posted.  Note that data that was estimated for any reason must always be flagged as estimated..  The MDMA must record and maintain the estimation algorithm as long as it is required to store the data (for the 3 year archive); this information will be made available upon request to the appropriate UDC or ESP.  This should be reviewed when the rules are reviewed to see if it is necessary based on market experience.

- Add an additional required code to CMEP (or other approved format) for verified data. Verified data is data which failed at least one validation check, but was determined to be valid.

- MDMA performance standards should be investigated to consider the number of consecutive months data for a given meter may be estimated.

Interval VEE Recommendations:

- Adopt modifications to interval rules as outlined in section 2 of this summary and described in detail in the Interval VEE document.

Monthly VEE Recommendations:

- Adopt monthly validation and estimation rules as outlined in section 3 of this summary and described in the Monthly VEE document.  Note that if this is not done in a timely fashion it may delay MDMAs ability to enter this market.

- Establish a group to define rules to convert interval data to billing determinants.  Monthly data validation and estimation rules would be reviewed as part of the process to determine any impact.

- Sanction ongoing work to:

- Investigate validation rules for TOU demand and usage

- Determine what is statistically valid as a minimum density requirement for rules based on similar customers.

- Determine sample calculations for optional trend factors to incorporate climatic and demographic areas in validation and estimation.

- Market participants will develop a standardized approach to acceptance testing for monthly data, commencing by 9/1/98.

## VIII. 	Meter Worker Qualifications, Meter Installation, Maintenance, Testing, and Calibration

This section addresses the permanent standards for the installation, testing, maintenance, and calibration of meters for Direct Access.  These recommendations are intended to replace the interim process established by the CPUC in D.97-12-048.  The PSWG proposal, Appendix D, covers the following topics:

- Meter worker qualifications and certification

- The minimum procedures and tests to be performed during meter installation and removal

- The standards and frequency of meter testing and maintenance for direct access meters

- MSP certification

Meter Worker Qualifications

To ensure the safe and reliable installation of meters, workers need to have the appropriate training and experience for the different levels of metering work. The PSWG agreed to use as a starting point, the Meter Worker Classes that were developed in the fall of 1997 by the joint parties comprised of ESPs, MSP, and UDCs. The five levels of meter worker classes are summarized as follows:

Class 1	Installation of single phase self contained meters

Class 2	Class 1, plus installation of poly-phase self contained meters below 600V

Class 3 	Class 2, plus installation of transformer rated meters below 600v and testing of meters with internal diagnostics

Class 4a	Class 3, plus in field testing of single phase meters up to 300 volts

Class 4b	Class 4a, plus in field testing of meters that can be installed by meter worker classes 1-4.

Class 5	Class 4b, plus installation and testing of metering equipment above 600 volts.

Any worker performing direct access meter work must be certified for the class of work performed.

MSPs can issue certifications for meter worker classes 1, 2, and 3 after the CPUC, or a designated entity, has reviewed and authorized the training materials and program. This will allow the MSP to issue certification, as needed, to their workers. Because meter classes 4a, 4b, and-5 involve higher level safety and worker skills, certification will require passing a written and practical exam administered by the CPUC, or designated entity.

The specific details of the meter worker classes are described in Appendix D.  [VI-?]

MSP entity certification will continue to be administered by the CPUC.

Meter Installation

The PSWG developed a set of minimum standards and procedures that must be followed during the installation and removal process. These recommendations promote consistency of the installations and enhance safety and reliability. The procedures include Safety, Meter Security and Accessibility, Site Verification, and Meter Install, and are detailed in Section II of Appendix D.

Meter Maintenance

These recommendations cover the frequency and tests required for the routine maintenance of meters. The schedule for meter maintenance recognizes that meters with high usage warrant more frequent testing. The minimum meter maintenance and testing schedule is found in Table III.1-1.

Meter System Testing

Appendix D, Section IV, describes the specific tests that must be performed.

The PSWG recommendations attached in Appendix D were supported by all parties in attendance.  The PSWG recommends the CPUC adopt them as permanent standards. [VI-?]

SCE’s Proposal for Certification of Meter Workers for Direct Access

Southern California Edison supports the meter worker classes and supports a certification process for meter workers.   However, the PSWG majority proposal is missing an important element regarding the entity that reviews training materials and performs the practical tests for meter worker classes 4-5.  The PSWG proposal simply states the CPUC or CPUC designated entity(ies) perform this function.  SCE proposes that this be performed by an advisory board consisting of UDC and MSP representation.  This proposal offers the advantage that experts in the metering industry are involved in the review process and promotes consistency in the implementation process.

SCE proposes the following be added to the PSWG recommendation to establish a process for the review of training materials and Class 4-5 meter worker tests.

The Meter Certification Advisory Board

The Meter Certification Advisory Board (MCAB) is granted authorization by the CPUC to administer the authorization process of MSPs’ training programs and the certification of Meter Class 4-5 workers.  The board has independent decision making ability over the safety of meter installations, however, certain issues will require CPUC approval.

I	Responsibilities of the Meter Certification Advisory Board

- Reviewing the qualifications and training materials of MSP to perform training of meter worker classes 1-3.   Once a MSP receives authorization from the MCAB it can issue individual Meter Worker Classes 1-3 certifications.

- Develop and administer the exam process for Meter Worker Classes 4-5 and determine the process for maintaining certification.

- Institute any changes required in the marketplace relating to safety training or procedures by MSPs and meter workers.

- Manage the de-authorization process for a MSP to issue meter worker certifications and de-certification of Meter Worker Classes 4-5.  The CPUC would act to resolve an appeal of any de-certification.

II	Administration of Responsibilities

The responsibilities of the MCAB could be performed by hiring a consultant.  The MCAB will provide guidance to the consultant to implement the board’s responsibilities.  If a contract is needed, the board will present it to the CPUC for approval.   The cost recovery of the contract would be from fees from MSPs and exam fees.

III	Appeal and Dispute Process

The CPUC is responsible to resolve any dispute or claim that the MCAB decision were inappropriate or unfair.

IV	Membership of the Meter Certification Advisory Board

The board consists of highly qualified persons experienced in the electrical metering field.  It is necessary that these persons are considered experts to administer the standards of safe and accurate meter installation.  Because metering is connected to the electric distribution facilities, representation from the UDCs is required on the MCAB.   The MCAB has an equal number of MSP representatives, which are selected by a voting process from MSPs.   A chair will be appointed by the CPUC.

## IX. 	Data Security

Introduction

Direct Access will require that meter data be processed and communicated between many market players and participants

. The new business environment will have many data security risks. As electric restructuring moves to electronic commerce, many of the new risks are unique to this environment. The previous integrated monopoly structure created data and data flows that was not widely shared and was difficult for non-utilities to obtain. In a restructured competitive industry, the value, accessibility, and demand for this data has dramatically increased. The methods through which this data is secured must also change.

Data security has a significant impact on data quality and integrity, and ultimately the market.

As such, the perspective should be a complete market view. The Data Quality and Integrity Working Group (DQIWG) is currently evaluating market issues that address the areas of  information flows, gaps and overall data integrity. PSWG recommends that the CPUC refer security policy development to the DQIWG. The issues contained in Appendix E are being forwarded to the DQIWG.

Appendices:

A	Requirements for Meter Products Used in Direct Access

B 	Requirements for Meter Communications in Direct Access

C 	Requirements for Meter Data Management

C-VEE	Validating, Editing, and Estimating Methodology

D 	Requirements for Meter Installation, Testing and Maintenance

E	Future of PSWG

F 	Proposal for Data Security Evaluation for use in Direct Access

G	Glossary

H	PSWG Attendees

Except for standards defining the Type 2 optical port on the meter, when optical meter reading is used.

CPUC Decision 97-12-048, page 9.