Vote Item #1

I. 	MSP/METER WORKER QUALIFICATIONS

There are five key elements to these MSP meter worker qualifications: (1) Due to varying levels of complexity, safety issues and training required, there are five classes of meter equipment, meter service activities and ultimately meter worker qualifications that are involved in direct access metering work; (2) Since many workers are already performing metering work in California, meter workers who are presently performing work for a Utility Distribution Company (UDC) or certified MSP will be considered qualified and certified for the level of work for which they have been trained and are performing as of [insert the date adopted]; (3) UDCs and certified MSPs will identify which of the five meter worker classes each of their employees performing meter work are qualified for; (4) The new meter worker certification requirements shall apply uniformly to any direct access meter worker in the employ of any UDC or MSP (ESP as MSP) after [insert the date adopted]; (5) procedures are also adopted to ensure meter workers remain qualified over time.

UDCs and MSPs will issue appropriate identification to each of their meter workers or employees who perform direct access meter work and will ensure that their workers carry this identification while performing meter work.  This identification will indicate the worker’s employer and the class of meter work which the worker is qualified to perform.  If an ESP, UDC or customer subcontracts its meter work to an MSP, the subcontracting entity must ensure that the MSP issues each meter worker or employee such identification.

All meter workers performing meter services must meet the requirements as outlined in this Section and exercise due care for the tasks performed.  Out-of-socket meter accuracy testing, meter diagnostics and sub-metering work requirements are not addressed by this report.  Also, utilization of the meter’s built-in diagnostics is not considered part of meter accuracy testing.

I.A. 	Meter Worker Skill, Safety And Qualification Requirements

The following are the descriptions and requirements of the five meter worker classes:

I.A.1.	CLASS 1

I.A.1.1.	Metering Types and Voltages

This class includes single-phase, socket-based meters, 300 volts phase-to-phase maximum and does not include transformer rated meters.  Communication wiring must be outside of energized meter panels.

I.A.1.2. Work to be Performed

Class 1 Meter Workers can install, remove and replace single-phase, 120/240 volt or 120/208 volt, self-contained meters in standard socket based residential-type metering equipment.  Connections of communication conductors must be outside the energized meter panels.

I.A.1.3.	Essential Technical Skills

I.A.1.3.1. Understanding of single phase electrical metering.

I.A.1.3.2. Understanding of electric distribution safety procedures.

I.A.1.3.3. Ability to identify energy diversion or tampering related to this class of meter work.

I.A.1.3.4. Ability to install and remove damaged and undamaged meters.

I.A.1.3.5. Understanding of the meter panel and socket layout for the metering conditions related to this class of meter work.

I.A.1.3.6. Ability to read meters used in this class.

I.A.1.3.7. Ability to properly use tools appropriate to the work in this class.

I.A.1.3.8. Ability to connect meter communications external to the meter panel.

I.A.1.3.9. Ability to initialize meter communication modules - not utilizing Type 2 optical ports and meter configuration software.

I.A.1.4.	Worker Safety and Safety Equipment

I.A.1.4.1. Job performance in accordance with employing MSP's procedures and safety rules.

I.A.1.4.2. Knowledge of hazards of electricity and ability to perform work to avoid electrical hazards.

I.A.1.4.3. Ability to comply with CAL OSHA requirements.

I.A.1.4.4. On-site use of personal protective equipment.

I.A.1.5.	Worker Qualification: How Essential Technical and Safety Skills Are Determined

I.A.1.5.1. UDCs and MSPs must develop and implement a program to train their workers to perform Class 1 meter work safely and properly.

I.A.1.5.2. Employees must be certified by their employers, based on the use of that program.

I.A.1.5.3. MSP's Class 1 meter work training program will be reviewed and certified by a Meter Worker Certification Organization (MWCO).

I.A.2.	CLASS 2

I.A.2.1.	Metering Types and Voltages

This class includes all meters and skills required for Class 1.  Class 2 includes up to 600 V, single-phase and poly-phase, safety socket and standard socket based meters and does not include transformer rated meters.  Communication wiring may be behind the panel, and work can be in and around energized circuits.

##### I.A.2.2.	Work to be Performed

Class 2 Meter Workers can install, remove and replace all meters consistent with the above.  Class 2 Meter Workers must understand the operating characteristics of test-bypass facilities and test blocks and may operate test-bypass facilities, but may not install, alter, maintain or replace wiring between the meter and test block.  On panels without test-bypass facilities, single-phase and poly-phase meters will not be removed or installed without first disconnecting the customer load.  Communication wiring may be installed inside the panel, and work can be performed in and around energized circuits.

I.A.2.3.	Essential Technical Skills

I.A.2.3.1. Cumulative including all skills for Class 1.

I.A.2.3.2. Additionally, possess skills related to meter voltages and meter forms used in Class 2.

I.A.2.3.3. Ability to perform phase rotation assessments.

I.A.2.3.4. Ability to operate test-bypass facilities or test blocks in a self-contained safety socket.

I.A.2.3.5. Ability to perform work required to route communication wiring to accommodate meter communications.

I.A.2.4.	Worker Safety and Safety Equipment

I.A.2.4.1. Cumulative including all skills and safety knowledge for Class 1

I.A.2.4.2. Electrical safety knowledge and work skills appropriate for single-phase and three-phase metering up to 600V phase-to-phase, including the ability to identify and refer to a Class 5 meter installer services above 600V phase-to-phase prior to performing work in the service equipment.

I.A.2.5.	Worker Qualification: How Essential Technical and Safety Skills Are Determined

I.A.2.5.1. UDCs and MSPs must develop and implement a program to train their workers to perform Class 2 meter work safely and properly.

I.A.2.5.2. Employees must be certified by their employers, based on the use of that program.

I.A.2.5.3. MSP's Class 2 meter work training program will be reviewed and certified by a Meter Worker Certification Organization (MWCO).

I.A.2.6.	Experience Requirements

Minimum experience requirements that must be demonstrated prior to qualification for individuals wanting to become a Class 2 Meter Worker as specified below:

I.A.2.6.1.	If entry level experience of any employee is that of a journeyman level electrician, journeyman level electric metering worker, or journeyman level line worker (e.g., lineman, troubleman), then upon successful completion of the MSP training program the worker may be certified as a Class 2 Meter Worker; or

I.A.2.6.2.	After six (6) months as a Class 1 Meter Worker which includes three (3) months “OJT” working alongside a Class 2 or higher Meter Worker and upon successful completion of the MSP training program a worker may be certified as a Class 2 Meter Worker; or

I.A.2.6.3.	If an employee has a two or four year degree in a related subject, then after four (4) months of Class 2 Meter Worker training which includes three (3) months "OJT" working alongside a Class 2 or higher Meter Worker and upon successful completion of the MSP training program a worker may be certified as a Class 2 Meter Worker; or

I.A.2.6.4.	After six (6) months of Class 2 Meter Worker training which includes three (3) months “OJT” working alongside a Class 2 or higher Meter Worker and upon successful completion of the MSP training program a worker may be certified as a Class 2 Meter Worker.

I.A.3.	CLASS 3

I.A.3.1.	Metering Types and Voltages

This class includes all meter types in Classes 1 and 2.  Class 3 work includes up to 600V, A base, K base and transformer rated meters with internal diagnostics.  Communication wiring may be behind the panel, and work can be in and around energized circuits.

I.A.3.2.	Work to be Performed

In addition to Class 1 and 2 Meter Work, Class 3 Meter Workers can install, remove and replace all meters consistent with the above including transformer-rated meters with internal diagnostics.  Class 3 Meter Workers may operate test switches, but may not install, alter, maintain or replace wiring between the meter, test switch, test block and associated equipment.

I.A.3.3.	Essential Technical Skills

I.A.3.3.1. Cumulative of Classes 1 and 2.

I.A.3.3.2. Additionally, possess skills related to meter voltages and meter forms used in Class 3.

I.A.3.3.3. Ability to understand the operating characteristics of metering transformers and how to operate test switches.

I.A.3.3.4. Ability to understand, interpret, identify and take appropriate actions based upon built-in diagnostics of solid state meters.

I.A.3.4.	Worker Safety and Safety Equipment

I.A.3.4.1. Cumulative of all safety skills for Classes 1 and 2.

I.A.3.4.2. Ability to understand, interpret and take appropriate action based on built in diagnostics of solid state meters.

I.A.3.4.3. Ability to work with transformer rated meters and operate test switches and test blocks.

I.A.3.5.	Worker Qualification: How Essential Technical and Safety Skills Are Determined

I.A.3.5.1.	UDCs and MSPs must develop and implement a program to train their workers to perform Class 3 meter work safely and properly.

I.A.3.5.2.	Employees must be certified by their employers, based on the use of that program.

I.A.3.5.3.	MSP's Class 3 meter work training program will be reviewed and certified by a Meter Worker Certification Organization (MWCO).

I.A.3.6.	Experience Requirements

Minimum experience requirements that must be demonstrated prior to qualification for individuals wanting to become a Class 3 Meter Worker as specified below:

I.A.3.6.1.	If entry level experience of any employee is that of a journeyman level electrician, journeyman level electric metering worker, or journeyman level line worker (e.g., lineman, troubleman), then upon successful completion of the MSP training program the worker may be certified as a Class 3 Meter Worker; or

I.A.3.6.2.	After 6 months as a Class 2 Meter Worker which includes 3 months "OJT" working alongside a Class 3 or higher Meter Worker and upon successful completion of the MSP training program a worker may be certified as a Class 3 Meter Worker; or

I.A.3.6.3.	If an employee has a two or four year degree in a related subject, then after six (6) months of Class 3 Meter Worker training which includes four (4) months "OJT" working alongside a Class 3 or higher Meter Worker and upon successful completion of the MSP training program a worker may be certified as a Class 3 Meter Worker; or

I.A.3.6.4.	After eight (8) months of Class 3 Meter Worker training which includes four (4) months “OJT” working alongside a Class 3 or higher Meter Worker and upon successful completion of the MSP training program a worker may be certified as a Class 3 Meter Worker.

I.A.4.	Class 4(A)

## I.A.4.1. Metering Types and Voltages

This class includes all meter types in Classes 1, 2 and 3.

I.A.4.2.	Work to be Performed

In addition to Class 1, 2, and 3 Meter Work, Class 4(A) Meter Workers can install, remove and replace all meters consistent with the above.  May perform in-field meter accuracy tests, calibrations and perform all types of meter maintenance and troubleshooting on single phase meters up to 300 Volts.  Programs and verifies internal programs and software in solid state meters.

### I.A.4.3.	Essential Technical Skills

I.A.4.3.1. Cumulative of Classes 1, 2 and 3.

I.A.4.3.2. Ability to perform work on metering switchboards.

I.A.4.3.3. Ability to perform calibration, repair, retrofit, troubleshooting, data collection of electric meters within the Class and install, maintain and program advanced metering technologies, including TOU, interval data, real time pricing, remote meter communication, and load control devices.

I.A.4.4.	Worker Safety and Safety Equipment

I.A.4.4.1. Cumulative of all safety skills for Classes 1, 2, and 3.

I.A.4.4.2.	Ability to conform processes to additional electricity hazards and complexities associated with metering switchboards, testing meters and maintaining meters in service equipment up to 300 volts.

I.A.4.5.  Worker Qualification: How Essential Technical and Safety Skills Are Determined

I.A.4.5.1. UDCs and MSPs may develop and implement a program to train workers to perform Class 4(A) meter work safely and properly (prior to and after testing).

I.A.4.5.2. All workers must be certified by the test process outlined below.

I.A.4.6.	Testing Process and Qualifications

I.A.4.6.1.	All individuals seeking to perform DA meter services for a UDC or MSP as a Class 4(A) Meter Worker must successfully pass written and practical (demonstrative) tests.

I.A.4.6.2. 	Prerequisites for taking the written and practical tests include a showing of previous work experience that includes at least one of the following:

I.A.4.6.2.1. Employment as a journeyman electrician, journeyman metering employee, or journey line worker (e.g., lineman, troubleman); or

I.A.4.6.2.2. Minimum of one year experience as a Class 3 Meter Worker; or

I.A.4.6.2.3. Minimum of one year experience in utility revenue metering.

I.A.4.7.	Testing and Re-Certification Requirements

I.A.4.7.1. Once an individual takes and passes the Class 4(A) Meter Worker Test, the individual is qualified to perform that class of DA meter work anywhere in California and need not re-take the test to perform work in each UDC service area.

I.A.4.7.2. If after being qualified a Class 4(A) meter worker the individual does not perform metering work in California for 3 years or more, re-certification will be required by written and practical testing prior to performing that class of meter work.

I.A.4.8. Continuing Education

As part of a Class 4(A) Meter Worker’s ongoing ability to remain qualified, the individual must participate in at least ten (10) hours annually of the MSP’s training program regarding standards of practice and safety related issues.

I.A.5.	Class 4(B)

## I.A.5.1.	Metering Types and Voltages

This class includes all meter types in Classes 1, 2, 3 and Class 4(A).  Class 4(B) work includes all metering up to 600V, including transformer rated meters with primary and secondary voltages less than 600V.  Communication wiring may be behind the panel, and work can be in and around energized circuits.

I.A.5.2.	Work to be Performed

In addition to Class 1, 2, 3 and 4(A) Meter Work, Class 4(B) Meter Workers can install, remove and replace all meters consistent with the above.  May perform in-field meter accuracy tests, calibrations and perform all types of meter maintenance and troubleshooting on all meters.  Programs and verifies internal programs and software in solid state meters.

### I.A.5.3.	Essential Technical Skills

I.A.5.3.1. Cumulative of Classes 1, 2, 3 and 4(A).

I.A.5.3.2. Ability to perform work on metering switchboards.

I.A.5.3.3. Ability to perform calibration, repair, retrofit, troubleshooting, data collection of electric meters and install, maintain and program advanced metering technologies, including TOU, interval data, real time pricing, remote meter communication, and load control devices.

I.A.5.4.	Worker Safety and Safety Equipment

I.A.5.4.1. Cumulative of all safety skills for Classes 1, 2, 3 and 4(A).

I.A.5.4.2. Ability to conform processes to additional electricity hazards and complexities associated with metering switchboards, testing meters and maintaining meters in service equipment up to 600 volts.

I.A.5.5.	Worker Qualification: How Essential Technical and Safety Skills Are Determined

I.A.5.5.1. UDCs and MSPs may develop and implement a program to train workers to perform Class 4(B) meter work safely and properly (prior to and after testing).

I.A.5.5.2. All workers must be certified by the test process outlined below.

I.A.5.6.	Testing Process and Qualifications

I.A.5.6.1.	All individuals seeking to perform DA meter services for a UDC or MSP as a Class 4(B) Meter Worker must successfully pass written and practical (demonstrative) tests.

I.A.5.6.2. 	Prerequisites for taking the written and practical tests include a showing of previous work experience that includes at least one of the following:

I.A.5.6.2.1. Employment as a journeyman electrician, journeyman metering employee, or journey line worker (e.g., lineman, troubleman); or

I.A.5.6.2.2. Minimum of one year experience as a Class 3 or  4(A) Meter Worker; or

I.A.5.6.2.3. Minimum of one year experience in utility revenue metering

I.A.5.7.	Testing and Re-Certification Requirements

I.A.5.7.1. Once an individual takes and passes the Class 4(B) Meter Worker Test, they are qualified to perform that class of DA meter work anywhere in California and need not re-take the test to perform work in each UDC service area.

I.A.5.7.2. If after being qualified a class 4(B) meter worker the individual does not perform metering work in California for 3 years or more, re-certification will be required by written and practical testing prior to performing that class of meter work.

I.A.5.8.	Continuing Education

As part of a Class 4(B) Meter Worker’s ongoing ability to remain qualified, the individual must participate in at least ten (10) hours annually of the MSP’s training program regarding standards of practice and safety related issues.

I.A.6.	Class 5

## I.A.6.1.	Metering Types and Voltages

This class includes all meter types in Classes 1, 2, 3, 4(A) and 4(B).  Class 5 meter work includes all metering above 600 V, including metering transformers, associated devices such as isolation relays and switches, and wiring between these transformers, associated devices and meters. Communication wiring may be behind the panel, and work can be in and around energized circuits.

# I.A.6.2.	Work to be Performed

In addition to Class 1, 2, 3, 4(A) and 4(B) meter work, Class 5 Meter Workers can install, remove and replace all meters consistent with the above including transformer-rated meters.  Replace high-voltage fuses.  Perform in-field meter accuracy tests, calibrations and perform all types of meter maintenance and troubleshooting on all meters.  Inspect wiring and instrument transformer ratios utilizing various apparatus as necessary.

### I.A.6.3.	Essential Technical Skills

I.A.6.3.1. Cumulative of Classes 1, 2, 3,4(A) and 4(B).

I.A.6.3.2. Ability to identify primary metering equipment and characteristics of service equipment rated at voltages above 600 volts.

I.A.6.3.3. Broad knowledge and familiarity of electrical distribution systems above 600 volts and operating characteristics.

I.A.6.3.4. Ability to identify UDC service voltages and Electrical Service Requirements.

I.A.6.3.5. Broad Knowledge and familiarity of State of California General Orders.

I.A.6.4.	Worker Safety and Safety Equipment

I.A.6.4.1. Cumulative of all safety skills for Classes 1, 2, 3, 4(A) and 4(B).

I.A.6.4.2. Ability to conform processes to additional electricity hazards and complexities associated with metering switchboards, testing meters and maintaining meters in service equipment above 600 volts.

I.A.6.4.3.	Meet the State of California requirements for a “Qualified Electrical Worker” to perform work on metering systems with instrument transformer at voltages above 600 volts.

I.A.6.4.4.	Must have a minimum of two years of combined training and experience with high-voltage (above 600 volts) equipment and circuits.

I.A.6.5.	Worker Qualification: How Essential Technical and Safety Skills Are Determined

I.A.6.5.1. MSP may develop and implement a program to train employees to perform Class 5 meter work safely and to comply with CAL OSHA requirements (prior to and after testing).

I.A.6.5.2. All workers will be certified by the test process outlined below.

### I.A.6.6.	Testing Process and Qualifications

I.A.6.6.1. All individuals seeking to perform DA meter services for a UDC or MSP as a class 5 Meter Worker must successfully pass written and practical skills (demonstrative) tests.I.A.6.6.2. Prerequisites for taking the written and practical skills tests including verification of previous work experience that includes at least one of the following:

I.A.6.6.2.1. Recognized employment as a journeyman electrician (above 600 volts) with qualified electrical worker status.

I.A.6.6.2.2. Recognized employment as a journeyman metering employee with two years minimum working experience on metering equipment above 600 volts.

I.A.6.6.2.3. Journeyman Line Worker, Apparatus Technician or similar position that has completed a recognized apprenticeship program that meets minimum CAL OSHA requirements.

I.A.6.6.2.4. Knowledge of CAL OSHA requirements and completed required training for a Class 4(B) Meter Worker.

### I.A.6.7.	Testing and Re-Certification Requirements

I.A.6.7.1. Once an individual takes and passes the Class 5 written and practical skills test, and has completed the requirements for performing work on energized metering equipment above 600 volts, that individual is qualified to perform work anywhere in California and need not re-take the written test to perform work in each UDC service area.

I.A.6.7.2. If after being qualified as a Class 5 Meter Worker the individual does not perform Class 5 metering work in California for 3 years or more, re-certification will be required by written and practical skills testing prior to performing Class 5 meter work.

I.A.6.8. Continuing Education

As part of a Class 5 Meter Worker’s ongoing ability to remain qualified, the individual must participate in at least ten (10) hours annually of the MSP’s training program regarding standards of practice and safety related issues.

Vote Item #2

IV.	REQUIREMENTS FOR STICKERS, SEALING AND LOCKING HARDWARE:

Below are the requirements for the stickers, sealing and locking hardware used in Direct Access.  Requirements for application of these devices are covered in the meter installation and maintenance section.

IV.1.	Sealing and locking hardware:

Sealing and locking hardware shall be imprinted with company name and/or logo and be made with material other than lead.  Sealing hardware owned by the MSPs shall be orange in color and be imprinted with its certification number.

IV.2.	Life-support sealing hardware:

Life-support sealing hardware used for identifying a customer premise which has a life support system shall be white in color and imprinted with a red caduceus (medical symbol).

IV.3.	Life-support sticker:

A life-support sticker used for identifying a customer premise which has a life support system shall be imprinted with a caduceus (medical symbol).

IV.4.	480 V sticker:

A 480 V sticker used to identify a 480 Volt service panel and meter shall be legible.

V.	REQUIREMENTS FOR LABELING MANUFACTURING DATE ON NEW METER PRODUCTS:

New meter products shall be permanently labeled with a manufacturing date.

VI.	REQUIREMENTS FOR REBUILT, RETROFIT AND REPAIRED METER PRODUCTS:

VI.1.	Rebuilt Meter Product:

A meter product shall not be rebuilt and repackaged for resale by any entity except its original manufacturer or the manufacturer-authorized licensed agent.  Once a meter product is rebuilt and repackaged, it shall be tested for accuracy, labeled as rebuilt and by whom, and dated accordingly.

VI.2.	Retrofit Meter Product:

A meter product may be retrofitted with other devices or modules.  Retrofitted meter products shall be tested in accordance with Section II.1.2 of the Certification Testing Requirements.  Prior to use, retrofitted meter products shall be tested for accuracy, labeled as retrofitted and by whom, and dated accordingly.

VI.3.	Repaired Meter Product:

A meter product shall not be repaired for resale by any entity except its original manufacturer or the manufacturer-authorized licensed agent.  Once a meter product is repaired, it shall be labeled as repaired and by whom, and dated accordingly.

Vote Item #3

"EDI for meter data should be implemented by January 1, 1999. At that point, EDI could be used instead of CMEP.  A 'narrow' version of EDI is adopted to minimize initial requirements, followed by a more robust implementation over time.  This recommendation is also to use only Transaction Set 867 for metering data, so the UDCs do not have to support both 810 and 867 for metering data."

Vote Item #4

The UDCs agree to migrate from the CMEP to EDI format for the transfer of meter data using the current server structure as proposed by ORA. However, the UDCs recommend that the conversion date from the CMEP format to the EDI format be 12/31/99 for the following reasons:

- We need to establish a statewide policy/procedure for implementation to assure uniformity of processes

- The UDC’s EDI teams are currently upgrading the 3030 version to the 3070 version of 810 as well as working on the ESP consolidated billing through transaction set 820, account maintenance updates are being mapped to  transaction set 248 and meter-specific information flow and DASRs are being mapped to transaction set 814. The above work should all have priority over the CMEP-EDI transition. Curently CMEP is working. The above issues require immediate attention and should have priority over the CMEP migration.

- There will be a transition period required for the small ESPs who haven’t participated in PSWG. They will need to be informed and given adequate time for transition.

- Inevitably, the transition will require trouble shooting with the preponderance of the work falling upon the UDCs who will have to make sure all market players can exchange market data with them. The UDCs are at the hub of the data exchange wheel and will be disproportionately affected by any wrinkles that arise in the transition.

- 1/1/99 UDC resources will be dedicated to the unbundling transition.

- 6/1/99 UDC resources will be dedicated to billing and settlement issues with monthly unbundled customers.

- Exact mapping from the CMEP format to the EDI format is essential. A missed field could easily swing programming costs up $1,000,000 for each UDC. We can’t adopt the EDI fomat hastily without making sure that all fields are included.

Vote Item #5

The future of PSWG will be discussed in the next plenary and voted into the report.

Proposal #1

For on-going modifications of CPUC metering standards/requirements, the following paragraph is proposed to include in the final report:

"Because metering technology will be changing over time, new metering standards may be beneficial to consumers, and there may be new safety issues, a process of revising the CPUC-approved permanent metering requirements will be needed.  However, it is not known how often modification of these permanent metering requirements will occur.  Therefore, the process shall be that when a need for modifying the CPUC-approved metering requirements arises, an entity (UDC, MSP, ESP, non-profit organization, etc.) shall file with the CPUC a petition to modify the CPUC-approved metering requirements.  If the CPUC can decide to modify within its technical and regulatory capabilities and after the CPUC receives and reviews comments from other entities, the CPUC will issue its decisions accordingly.  If the CPUC would like market participants to seek solutions on this issue, it will order the PSWG to reconvene, discuss the issue and make recommendations within a reasonable period.  However, PSWG shall not be reconvened more often than once within a six month period."

# Proposal 2

The CPUC mandated in its December 1997 decision that the Permanent Standards Working Group is charged to recommend in a report to the commission due by July 29, 1998 which permanent metering related standards should be adopted by the commission. Decision D.97-12-048 states “The PSWG should also indicate whether other standards are expected in the future, and recommend a process for reviewing possible future changes to the permanent standards.”

Several PSWG participants discussed these needs and Augie Nevolo prepared several drafts of this process and recommended organizational structure to address these needs. Following the latest proposal to accomplish these objectives.

### Reasons for creating a working group to address issues reviewing possible future changes to permanent standards for direct access in California.

- There are several meter and data communications standards that will be approved by ANSI, IEC and IEEE that are relevant to direct access in California.  ANSI C12.21 and C12.22 are in the final stages of work and will be voted on in the next few months.  Likewise both the IEC and the IEEE are working on a variety of data communications standards applicable to meter communications including MMS and DLMS as well as other related data communications standards that are relevant and indeed necessary to ensure interoperability of diverse metering and communications systems in California.

- There was insufficient time available during PSWG deliberations to thoroughly identify technical requirements and to review meter and, in particular, data communications standards that would foster interoperability among products and systems deployed in California.   More importantly, the data communications standards identified by the PSWG to date, while necessary are not sufficient to ensure a base level of interoperability, which was clearly identified in the CPUC M&DCS December, 1997 decision as a key objective.

- There were several standards selected for implementation including EDI and C12.19. Both of these standards will have enhancements made which will benefit the direct access participants and the consumers in California. However, in order to ensure that their needs will be met by the standards and the products and/or systems deployed based on them additional participation will be required by the vendors and users to address these issues.

### Form a Future Standards Changes Working Group (FSCWG)

Form a voluntary group of participants involved in the Direct Access market place and who have participated in the PSWG process. Ideally all entities that participated in the PSWG deliberations should continue to participate in the FSCWG.  Allowing much of the work to take place by electronic communications should facilitate maximum participation.  The informal group thus formed would comprise a Future Standards Changes Working Group (FSCWG) to address and resolve the following issues.

A.	Identify and assess for possible implementation, new meter and data communications standards that are published or up for final approval from principal national or international standards committees such as IEEE, ANSI, IEC and ISO that are relevant to direct access in California.

B.	Communicate the benefits and/or impacts of the adoption of any new meter and data communications standards to the market participants in California and the nation.

C.	Identify and assess meter and data communications standards not covered during the working period of PSWG’s existence.

1.	There are many standards that have not been specifically discussed and reviewed in depth by the PSWG that need to be assessed in order to ensure that interoperability of diverse systems can occur. See Appendix A for additional details.

D.	Identify new or changed technical requirements, which would impact the meter and data communications standards recommended by the PWSG. Assess the impact of these changes on the installed systems and systems to be installed in California based on these standards. See Appendix A for additional details.

E.	Prepare recommendations to appropriate standards bodies for enhancement of existing standards or development of new standards. See Appendix A for additional details.

F.	Identify and track common problems arising in metering and meter communications which deal with standards, standard interfaces and application of standards or common business practices recommended by the PSWG. Use e-mail to notify participants and establish a web page on the CPUC / ORA to document and track common problems and solutions.

### II.	Process to manage issues raised and to develop common solutions

A.	Identify Direct Access meter and data communications standards and/or common business practice problems or issues

1.	Any market participant that feels it has identified a problem dealing with meter and data communications standards or common business practice prepares a problem report and posts it to the appropriate CPUC/ORA web site page.  The FSCWG will need to develop and agree to a common format and rules for posting.

B.	Assess the priority of the problem identified.

1.	The priority should be established by the FSCWG. It may be beneficial to establish sub working groups to deal with general areas, i.e., metering, meter reading and data communications, electronic commerce / EDI, VEE, MDMA issues. If so the problems can be initially prioritized by the sub-working group.

B.	Analyze the problem(s) identified and the potential impact (s) on Direct Access functions and entities.

C.	Identify potential solutions from the market participants and technical experts on their staffs.

D.	Review and discuss the proposed solutions within the FSCWG as a whole.  A consensus of the group will be needed prior to proceeding further with the resolution of the problem or issue.

E.	If the FSCWG agrees that a solution must be effected, a solution is chosen by the FSCWG from the alternatives proposed in step “D” and a project is established to resolve the problem identified.  A project description including problem statement proposed solution and implementation dates are agreed to among the market participants involved.

F.	Establish liaisons between the FSCWG and appropriate standards bodies and industry groups including ANSI C12, ANSI X12, IEC and others.

1.	Establish a process / mechanism with these bodies to have informational draft copies of relevant meter, meter communications and data format standards posted to a CPUC / ORA web page for review by the sub-working groups.

G.	Establish a CPUC / ORA web page to identify and document new technical requirements that are identified by the FSCWG as part of its problem resolution process.  Discuss requirements identified among the FSCWG participants and reach a consensus on which requirements should be forwarded to the appropriate standards bodies.  Seek volunteers to submit to the appropriate standards bodies proposals to enhance existing standards to meet Direct Access needs.

### III.	Duration of the Future Standards Changes Working Group (FSCWG) and proposed meeting schedule

A.	At this time it is difficult to ascertain what the lifetime and the meeting frequency of the FSCWG should be. However, based on discussions to date It is proposed that the group meet six months after the PSWG Report has been filed and meet every quarter thereafter (or more/less frequently as necessary to resolve issues) for a period of one year.  At the end of one year the group would address whether problems relative to the meter and data communications systems employed in the Direct Access market place have stabilized and the group is no longer needed or whether if should continue for an additional six months to a year.  At the end of this 1-2 year period it is recommended by the Future Standards Changes Work Group that the CPUC host, at their discretion, a workshop once a year to deal with remaining issues.

B.	In the interim period after the formal proceedings of the PSWG have been concluded and it’s report has been filed with the commission, it is recommended that the work items described in section (I) and process described in section (II) is handled electronically.  Electronic mail can be used for issue identification and discussions and proposals and resolutions can be posting on the CPUC/ORA server.  Face-to-face meetings should be held quarterly to deal with outstanding issues and to interact on more complex issues than can be handled by electronic means.  The committee can develop specific details on the processes and work of the FSCWG using electronic means.

Appendix “A”

A.	Section 1.C.1 discusses the need for identifying and assessing standards not discussed during the PSWG proceedings, but which are essential for ensuring interoperability of products and systems.

1.	Standards that should be assessed include data communications application layer standards covering the retrieval or transmission of interval meter data from the meter to the MDMA. Existing national and international standards, which can be used for this purpose, include Manufacturing Message Specification (MMS) – ISO 9506-1,2 and Distribution Line Message Specification (DLMS) CEN/TC294 WG2/N70E. Data communications standards also need to be identified and assessed for possible use at the Transport, Networking, Data Link and Physical Layer. There are numerous national and international standards that can be used for this purpose.

B.	Section 1.D discusses the need for identifying new or changed technical requirements, which would impact the meter and data communications standards recommended by the PWSG. Following is an example of such a new or changed technical requirement.

C.	To date ANSI C12.19 has been identified as a standard that will be recommended for adoption with constraints identified in the May 26-28, 1998 PSWG meetings.  In addition, the PSWG has identified EDI and in particular ANSI X12 Utility Industry Group Implementation Guidelines and specific Transaction sets for ultimate adoption in California. Each of these standards will be undergoing changes and enhancements based on technical requirements provided by the individuals and organizations participating in the respective ANSI / IEEE committees. It is important that any technical requirements resulting in a change to these standards be tracked, assessed for impact on systems installed or about to be installed in California and communicated to the market participants in California and the nation.

D.	Section 1.C.1 discusses the need for preparing recommendations to appropriate standards bodies for enhancement of existing standards if the shortfall in existing standards used is relatively minor. In addition, recommendations for the preparation of new standards should be made if new technical requirements are significant and no existing standards meets the needs identified.

1.	Participation on standards bodies is voluntary and participants represent their own technical or company’s interests in the development of standards.  However, the Future Standards Changes Working Group participants can effectively help bring about the necessary changes to standards by making specific proposals to the committees as representative of their particular companies. Having many participants provide similar proposals to these committees will help bring about the required changes to the standards and result in significant benefits to the market participants in California.

E.	Section 1.F discusses the need for identifying and tracking common problems arising in metering and meter communications, which deal with standards, standard interfaces and application of standards or common business practices, recommended by the PSWG.

F.	As the direct access market place is relatively new, there are many situations in which problems may occur with the application of standards at the meter interface, the meter reading systems employed and/or the MDMA systems used to process the data retrieved. Some of these problems will be due to configuration problems, hardware, software and other system elements provided by particular ESPs, UDCs, MSPs, etc.

1.	If the problems fall within their business and or sub-contracted company domains they should be solved by the responsible entities. However some problems may arise which are due to particular implementation approaches used by a product supplied by vendor “x” interfacing with a system supplied by vendor “Y”, etc.  In these instances it will be very beneficial for all market participants to clearly identify the issue (standards, common business practice, implementation practice). The problem should be reviewed and assessed by the Meter and Data Communications Working Group or technical support staffs of the companies represented and a resolution of the problem identified.

2.	The generic problem(s) or issues should be communicated to the market participants in California and the nation.  It is again proposed that a web page be made available for this purpose on the CPUC / ORA server. Note that it is not the intent to get into specific detail on specific vendor equipment, but to identify problems and solutions to them, which may be faced by other market participants in implementing a particular standard in a similar environment.  It is also recommended that the CPUC server by configured to support ftp uploads and downloads of files, which can be used by market participants in working through such problems. The directory used should be accessible only when an appropriate password is used and should not be visible through general web access.

Proposal #3

The PSWG requests the CPUC order the interested market

participants to continue to work on permanent  ( w/ any required timeline for implementation) informational interactions and exchange standards including, outlining areas of responsibility and accountability, and finally compliance and enforcement issues.

Sub-metering work performed in California is presently covered by California Business and Professions Codes #12531 (Meaning and Scope of Terms) and 12532 (Engaging in Business as Device Repairman or Maintaining Device Repair Service Unlawful without Registration).

Establish a web page on the CPUC / ORA to communicate benefits and impacts, if acceptable by ORA.  This will enable market participants to be informed quickly and efficiently using a mechanism familiar to them from the PSWG activities.

Establish a web page on the CPUC / ORA server for this purpose, if acceptable by ORA.  This will enable market participants to identify and document new or changed technical requirements quickly and efficiently using a mechanism familiar to them from the PSWG activities.

A summary of the problem and proposed solution / implementation date is posted on the CPUC/ORA Web Site Server for tracking and informational purposes.