ANSI C12.19-1997

AMERICAN NATIONAL STANDARD

UTILITY INDUSTRY

END DEVICE

DATA TABLES

Secretariat

Institute of Electrical and Electronics Engineers

National Electrical Manufacturers Association

IEEE Number:  1377-1998

Approved:  March 20, 1997

American National Standards Institute, Inc.

American
National
Standard

Approval of an American National Standard requires verification by ANSI that the requirements for due process, consensus, and other criteria for approval have been met by the standards developer.

Consensus is established when, in the judgment of the ANSI Board of Standards Review, substantial agreement has been reached by directly and materially affected interests. Substantial agreement means much more than a simple majority, but not necessarily unanimity. Consensus requires that all views and objections be considered, and that a concerted effort be made toward their resolution.

The use of American National Standards is completely voluntary; their existence does not in any respect preclude anyone, whether he has approved the standards or not, from manufacturing, marketing, purchasing, or using products, processes, or procedures not conforming to the standards.

The American National Standards Institute does not develop standards and will in no circumstances give an interpretation of any American National Standard. Moreover, no person shall have the right or authority to issue an interpretation of an American National Standard in the name of the American National Standards Institute. Requests for interpretations should be addressed to the secretariat or sponsor whose name appears on the title page of this standard.

CAUTION NOTICE:  This American National Standard may be revised or withdrawn at any time. The procedures of the American National Standards Institute require that action be taken periodically to reaffirm, revise, or withdraw this standard. Purchasers of American National Standards may receive current information on all standards by calling or writing the American National Standards Institute.

Published by

National Electrical Manufacturers Association

1300 N. 17th Street, Rosslyn, Virginia  22209

© Copyright 1997 by the National Electrical Manufacturers Association. All rights including translation into other languages, reserved under the Universal Copyright Convention, the Berne Convention for the Protection of Literary and Artistic Works, and the International and Pan American Copyright Conventions.

No part of this publication may be reproduced in any

form, in an electronic retrieval system or otherwise,

without prior written permission of the publisher.

Printed in the United States of America

TABLE OF CONTENTS

Foreword	v

1 Scope

2 References

3 Definitions

4 General

4.1 Standard tables

4.2 Manufacturer tables

5 Syntax

5.1 Descriptive syntax

5.2 Flow of information

5.3 Identifiers

5.4 Basic data types	6

5.4.1 Basic data type definitions	7

5.4.2 Special data types

5.4.2.1 Signed integers

5.4.2.2 Characters

5.4.2.3 Non-integer numbers

5.4.2.4 Date and time formats

5.4.3 Miscellaneous data types

5.5 Values and constants

5.5.1 Constants

5.5.2 Value

5.6 Conditionals

5.6.1 If statements

5.6.2 Case statements

5.7 Bit field

5.7.1 Sub type definitions

5.8 Set

5.9 Array

5.10 Packed record

5.11 Table

6 Special data types

6.1 Character set selection

6.2 Non-integer formats

6.2.1 CHAR numbers

6.3 Date and time formats

6.3.1 LTIME_DATE, STIME_DATE, TIME types

6.3.2 RDATE type

6.3.3 DATE Type

6.4 Common table or procedure identifier formats

6.4.1 TABLE_IDA_BFLD bit field

6.4.2 TABLE_IDB_BFLD bit field

6.4.3 TABLE_IDC_BFLD bit field

6.5 Constants

7 Compliance

8 Table transportation issues

8.1 Minimum services and parameters

8.1.1 Read service

8.1.2 Write service

8.2 Pending event description

9 Tables

9.1 Decade 00: configuration tables

9.1.1 Table 00 general configuration table

9.1.2 Table 01 general manufacturer identification table

9.1.3 Table 02 device nameplate table

9.1.4 Table 03 ED_MODE status table

9.1.5 Table 04 pending status table

9.1.6 Table 05 device identification table

9.1.7 Table 06 utility information table

9.1.8 Table 07 procedure initiate table

9.1.8.1 Standard procedures

9.1.8.1.1 Cold start

9.1.8.1.2 Warm start

9.1.8.1.3 Save configuration

9.1.8.1.4 Clear data

9.1.8.1.5 Reset list pointers

9.1.8.1.6 Update last read entry

9.1.8.1.7 Change end device mode

9.1.8.1.8 Clear standard status flags

9.1.8.1.9 Clear Manufacturer Status Flags

9.1.8.1.10 Remote reset

9.1.8.1.11 Set date and/or time

9.1.8.1.12 Execute diagnostics procedure

9.1.8.1.13 Activate all pending tables

9.1.8.1.14 Activate specific pending table(s)

9.1.8.1.15 Clear all pending tables

9.1.8.1.16 Clear specific pending table(s)

9.1.8.1.17 Start load profile

9.1.8.1.18 Stop load profile

9.1.8.1.19 Log in

9.1.8.1.20 Log out

9.1.9 Table 08 procedure response table

9.2 Decade 10: data source tables

9.2.1 Table 10 dimension sources limiting table

9.2.2 Table 11 actual sources limiting table

9.2.3 Table 12 unit of measure entry table

9.2.4 Table 13 demand control table

9.2.5 Table 14 data control table

9.2.6 Table 15 constants table

9.2.7 Table 16 source definition table

9.3 Decade 20: register tables

9.3.1 Table 20 dimension register table

9.3.2 Table 21 actual register table

9.3.3 Table 22 data selection table

9.3.4 Table 23 current register data table

9.3.5 Table 24 previous season data table

9.3.6 Table 25 previous demand reset data table

9.3.7 Table 26 self read data table

9.3.8 Table 27 present register selection table

9.3.9 Table 28: present register data table

9.4 Decade 30: local display tables

9.4.1 Table 30 dimension display table

9.4.2 Table 31 actual display table

9.4.3 Table 32 display source table

9.4.4 Table 33 primary display list table

9.4.5 Table 34 secondary display list table

9.5 Decade 40: security tables

9.5.1 Table 40 dimension security limiting  table

9.5.2 Table 41 actual security limiting table

9.5.3 Table 42 security  table

SECURITY_ENTRIES  Array containing a list of security limiting parameters.

9.5.4 Table 43 default access control table

9.5.5 Table 44 access control table

9.5.6 Table 45 key table

9.6 Decade 50: time-of-use tables

9.6.1 Table 50 dimension time and TOU table

9.6.2 Table 51 actual time and TOU table

9.6.3 Table 52 clock table

9.6.4 Table 53 time offset table

9.6.5 Table 54 calendar table

9.6.6 Table 55 clock state table

9.6.7 Table 56 time remaining table

9.7 Decade 60: load profile tables

9.7.1 Table 60 dimension load profile table

9.7.2 Table 61 actual load profile table

9.7.3 Table 62 load profile control table

9.7.4 Table 63 load profile status table

9.7.5 Table 64 load profile data set 1 table

9.7.6 Table 65 load profile data set 2 table

9.7.7 Table 66 load profile data set 3 table

9.7.8 Table 67 load profile data set 4 table

9.8 Decade 70:  history & event logs

9.8.1 Table 70 dimension log table

9.8.2 Table 71 actual log table

9.8.3 Table 72 events  identification table

9.8.4 Table 73 history log control table

9.8.5 Table 74 history log data table

9.8.6 Table 75  event log control table

9.8.7 Table 76 event log data table

9.9 Decade 80: user defined tables

9.9.1 Table 80 dimension user defined tables function limiting table

9.9.2 Table 81 actual user defined tables function limiting table

9.9.3 Table 82 user defined tables list table

9.9.4 Table 83 user defined tables selection table

9.9.5 Table 84 user defined table zero table

9.9.6 Table 85 user defined table one table

9.9.7 Table 86 user defined table two table

9.9.8 Table 87 user defined table three table

9.9.9 Table 88 user defined table four table

9.9.10 Table 89 user defined table five table

ANNEX A (Normative) ID CODES FOR METER EQUIPMENT MANUFACTURERS 	159

ANNEX B (Normative) HISTORY & EVENT LOG CODES	161

ANNEX C (Normative) DEFAULT SETS FOR DECADE TABLES	163

ANNEX D (Normative) INDICES FOR PARTIAL TABLE ACCESS	167

Foreword	(This foreword is not part of American National Standard for Protocol Specification for ANSI C12.19-1997.)

The ANSI C12.19 standard provides a common data structure for use in transferring data to and from utility end devices, typically meters. It has been approved after considerable cooperative effort among utilities, electric meter manufacturers, Industry Canada, AMRA and other interested parties.

The standard data structure is defined as sets of tables. Table sets are grouped together into segments called decades. Each decade pertains to a particular feature set and data type such as Time of Use, Load Profile, etc. Data is transferred by reading from or writing to a particular table or portion of a table. It is anticipated that the set of standard tables will grow to meet the need for common implementations of expanded functionality.

The Secretariat of the Accredited Standards Committee on Electricity Metering, C12, is held by the National Electrical Manufacturers Association (NEMA) and the National Institute of Standards and Technology. At the time this standard was processed and approved, the C12 Committee had the following members:

Nile Oldham, Chairman

Vince Baclawski, Secretary

Organization Represented			Name of Representative

Underwriters Laboratory				Ron Breschini

Idaho Power Company				Richard Canderan

ABB Power T&D Company, Inc.			Tom C. Drew

Ted York

GE						Warren Germer

City of Los Angeles				Cruz R. Gomez

State of New York				Edmund J. Hofmann

Memphis Light					H. Carey Jones

Rural Utilities Service				George Keel

B-Line Systems, Inc.				Francis A. Marta

Clemson University				D. McAuliff

Florida Power & Light Co.			John McEvoy

Edison Electric Institute				Gary N. Miller

City of Austin Metering Operations		Herman M. Millican

T. U. Electric					James Mining

National Institute of Standards & Technology	Nile Oldham

Pacificorp					Lauren Pananen

Clark J. Smith

Florida Public Service Commission		James Ruehl

Arizona Public Service Company		Paul Taylor

Pacific Gas & Electric				Tim Vahstrom

The following members of the C12.17 Data Communications Protocols Committee were actively involved in the revision of this standard:

Wesley Ray, Chairman

Organization Represented			Name of Representative

Indianapolis Power & Light Company		Robert D. Adams

Landis & Gyr					Michael Anderson

Public Utillities Commission			Vlado Bevc

APTECH, Inc.					William C. Beverly, Jr.

ITRON						William J. Buckley

American Innovations, Ltd.			Randall Chance

Rick Darby

Entergy Services, Inc.				Lynnda K. Ell

Lucent Technologies				Stuart M. Garland

Centerior Energy Corporation			Kenneth E. Hauzer

T U Electric					Brad Johnson

James Mining (Alt.)

LILCO						Sunil Katwala

MidAmerican Energy Company			Jerry Klipkenberg

Commonwealth Edison				Larry Kotewa

Echelon					Chris Stanfield

Pradip Madan (Alt.)

Southern California Edison Company		Kit Maughan

Mario A. Natividad

Georgia Power Company			Kevin McDonald

Terry Penn

Radix Corporation				Laurel Miller

City of Austin Metering Operations		Herman M. Millican

Future DOS R&D, Inc.				Avygdor Moise

National Institute of Standards & Technology	Nile Oldham

Pacificorp					Lauren Pananen

Clark J. Smith

Pacific Gas & Electric Co.			Charles A. Partridge

GE Meter					Jack Pazdon

Schlumberger Electricity				Marc Purc

American Electric Power Servs. Corp.		William A. Randle, Jr.

Duke Energy Company				Wesley Ray

Institute of Gas Technology			William F. Rush

Utility Translation Systems			Chris M. Schafer

Bell Sotuh Telecommunications			Jerry Schull

Radix Corporation				Brian Simpson

Arizona Public Service Company		Paul Taylor (Alt.)

Wisconsin Public Service Corp.			Thomas C. Thiel

Tucker Engineering				Richard Tucker

Nertec Design					Michael Veillette

DAC						Steve Weil

ABB Power T&D Company, Inc.			Ted York

# Utility Industry End Device Data Tables

# 1	Scope

This standard defines a table structure for utility application data to be passed between an end device and a computer.  It does not define device design criteria nor specify the language or protocol used to transport that data.   The purpose of the tables is to define structures for transporting data to and from end devices.

# 2	References

ANSI C12.10-1987, Electromechanical Watthour Meters

ECMA-94, Latin 1

IEEE Std 754-1985,  Double Precision Floating Point Real Numbers

ISO/IEC 646: 1991,  Information technology - ISO 7-bit coded character set for information interchange

ISO 8859/1, Latin 1

ISO 7498/1, OSI 7 Layer Reference Model

# 3	Definitions

The definitions used in this document have been derived from the sources cited.  Only those words identified as coming from source number 5 are defined for this document with definitions specific to this document.

SOURCE:	(1) AS 4140 (Int) 1993.

(2) Edit from IEC TC13/WG14, May 1993.

(3) ANSI/IEEE 100 - 1984.

(4) Industry Canada Task Force for Data Communication Protocol

(5) AMRA/IEEE Utility Industry End Device Data Table Document.

ACT (5):  Abbreviation for "ACTUAL", indicating the programmed functional capabilities of an end device.

ADDRESS (3):  Those inputs whose states select a particular cell or group of cells.

AVERAGE DEMAND (5):  The consumption (e.g. energy, volume) recorded during the integration period divided by the integration time period.

Block average demand (5):  An average value occurring over a demand period specified by the end device.  (e.g. Watthours/hours).  The value may be saved by the end device for maximum or minimum registration.

Clock (3):  A device that generates periodic signals used for synchronization.  A device that measures and indicates time.  A register whose content changes at regular intervals in such a way as to measure time.

Cumulative demand (3):  An indicating demand meter in which the accumulated total of maximum demands during the preceding periods is indicated during the period after the meter has been reset and before it is reset again.  Note:  The maximum demand for any one period is equal or proportional to the difference between the accumulated readings before and after reset.

Customer (1):  The purchaser and/or user of a product or service supplied by a service provider or utility.

Data encryption (2):  The changing of the form of a data stream such that only the intended recipient can read or alter the information and detect unauthorized messages.

DECADE (5):  A functional grouping of tables by application into groups of ten.  The tables are numbered “X0” through “X9”, with “X” representing the decade number.

Demand (1):  The rate of consumption (e.g. power, volume/hour).

DIM (5):  Abbreviation for "DIMENSION", indicating the maximum functional capability designed into an end device.  See Function Limiting Control Table definition.

END DEVICE (5):  The closest device to the sensor or control point within a metering application communication system which is compliant with the Utility Industry End Device Data Tables.

FUNCTION LIMITING CONTROL (FLC) TABLE (5):  The first table in each decade specifies the limits designed into an end device with respect to variables used within the decade.

Load profile (5):  The recording, storage and analysis of consumption data over a period of time for a particular installation.

Maximum demand (3):  The highest demand measured over a selected period of time, such as one month.

Meter (5):  A device which measures and records the consumption or usage of the product/service.

MINIMUM DEMAND (5):  The lowest demand measured over a selected period of time, such as one month.

Octet (5):  A sequence of eight bits.  For application within this document reference Section 5.2, Flow of Information.

Peak demand (5):  Reference maximum demand.

Present average demand (5):  An average value occurring during a current demand interval or subinterval.  (e.g. Watts or VA).

Season (5):  A calendar specified period used for activation of rate schedules.

Sliding window (rolling-interval) demand (5):  The block demand calculated over an integration period which includes sub-intervals of previous demand calculations.

TABLE (5):  Functionally related utility application data elements, grouped together into a single data structure for transport.

Tariff (5):  A published list of rate schedules and terms and conditions.

Time-of-use (TOU) metering (5):  Metering equipment that separately records metered or measured quantities according to a time schedule.

Utility (3):  A provider of electricity, gas, water, telecommunications or related services to a community.

# 4	General

## 4.1	Standard tables

Standard tables are those whose structures are specified by this document.  These should be used for both end device programming and reading.  The tables provide control tables as well as data tables for a wide variety of functions to be implemented in addition to those presently defined.  This document provides for a total of 2048 standard tables, although not all are defined.

The standard tables are grouped together in decades, with each decade covering a general area of functionality.  The first table of each decade, beginning with the tens decade, is referred to as a function limiting control (FLC) table.  The purpose of the FLC table is to specify the designed DIMENSION  (DIM) limits for variables used within the decade for the end device.

If present, the table immediately following an FLC table is called the FLC+1 table.  The FLC+1 table defines the ACTUAL (ACT) limits used for variables in the end device current configuration.

If the FLC+1 table is not present, the ACTUAL (ACT) limits are identical to the designed DIMENSION (DIM) limits specified in the FLC table.

If the FLC and FLC+1 tables are not used in a decade, then the limits are defined by a default set of values.  The default sets for a particular decade are defined within this standard in Annex C.  Possible combinations of tables are defined in figure 1.

|  | FLC Table | FLC+1 Table | FLC+N Table | Where ACT Values Are Found |
| --- | --- | --- | --- | --- |
| A | Not Used | Not Used | Not Used | None - Decade not used |
| B | Not Used | Not Used | Used | Default set, per Standard |
| C | Not Used | Used | Not Used | Not practical |
| D | Not Used | Used | Used | Decade FLC+1 Table |
| E | Used | Not Used | Not Used | Not practical |
| F | Used | Not Used | Used | Decade FLC Table |
| G | Used | Used | Not Used | Not practical |
| H | Used | Used | Used | Decade FLC+1 Table |

Figure 1 – Possible combinations of FLC, FLC+1, and decade tables

## 4.2	Manufacturer tables

Manufacturer tables are those structures specified by individual end device vendors.  They should be used to allow introduction of new innovations or to provide customer requested data structures.  They also provide a path for new functions to evolve into a standard table.  This standard provides access for a total of 2048 manufacturer tables.

# 5	Syntax

## 5.1	Descriptive syntax

Describing data definitions is usually accomplished within the confines of a given language and the grammar rules of that language.  Since the data definitions embodied within this document are meant to be independent of a specific language and capable of being implemented within the confines of any language, a method for describing the data definitions has been adopted.

Symbol Meaning

< >	A string contained inside angle brackets is called a non-terminal.  That is, while it may be viewed as a single unit it  shall be redefined as consisting of one or more simpler elements.

::=	This symbol is read as "is defined as".  The non-terminal which occurs on the left hand side (LHS) of this symbol consists of the elements (non-terminals, terminals, or a combination of the two) found on the right hand side (RHS).  A line containing an LHS, ::=, and an RHS is known as a production rule.

|	The vertical bar is an OR symbol.  The OR symbol always occurs on the right hand side of a production where the left hand side can be defined in more than one way.  The OR bar separates valid alternative right hand sides.

[ ]	A symbol enclosed in square brackets is optional.  The production is valid whether or not it is included.

*	The superscript asterisk is known as the Kleene star.  A symbol followed by the Kleene star may occur zero or more times without violating the grammar.

+	The superscript plus sign is known as the Kleene cross.  A symbol followed by the Kleene cross shall occur one or more times.

{ }	Text enclosed within curly braces is a comment provided for clarity and has no impact on the syntax or data definition.

The data structure elements are indicated by bold type.  Reserved words, characters, identifiers and other symbols required for the language are also indicated by bold type.

## 5.2	Flow of information

The flow of information is a stream of objects of multiple “n” octet length, when "n" is greater than one.  Objects are transmitted in order of their appearance in the table structure.

For purposes of transmission, the elementary data type is an octet or byte, which is eight bits in length.  The bits are numbered zero to seven.  Zero is the least significant bit.  Figure 2 illustrates this bit numbering and ordering.  The order of transmission of the bits in an octet is defined elsewhere in the appropriate OSI layer, which is typically the Data Link Layer (layer 2).  An octet may also be referenced as a byte.

| MSBit |  |  |  |  |  |  | LSBit |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |

Figure 2 – Octet bit ordering

For some data types that are more than one octet in length, it is possible to transmit them either most or least significant byte first.  The order of transmission is dictated by DATA_ORDER, found in the GEN_CONFIG_TBL (Table 00).  Each data type shall indicate a specific order of transmission or refer to Order of Transmission in Basic Data Type Definitions (Section 5.4.1).  Figure 3 illustrates a multibyte structure.

| MSByte |  |  |  |  |  |  | LSByte |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Octet | Octet | Octet | Octet | Octet | Octet | Octet | Octet |
| 7-0 | 7-0 | 7-0 | 7-0 | 7-0 | 7-0 | 7-0 | 7-0 |

Figure 3 – Multibyte ordering

## 5.3	Identifiers

An identifier is a name identifying a table, a packed record, a bit field, or a member of a packed record or of a bit field.

An identifier is made of letters and/or numbers and/or the character '_'. Some suffixes have been reserved for use with specific identifiers.  An identifier ending with _TBL identifies a table, _RCD identifies a packed record and _BFLD identifies a bit field.

The identifiers used to identify the members of a packed record or of a bit field are subdivided according to the type of data they define. These identifiers are: <int-identifier>, <bool-identifier>, <set-identifier> and <array-identifier>.

<number>		::=	<digit>+

<digit>			::=	0 to 9

<lchar>			::=	<digit>|<chararacter>

<character>		::=	A to Z only, upper case.

<ID>			::=	<lchar>+[_<lchar>+]*

<tbl-identifier>		:=	<ID>_TBL

<rcd-identifier>		:=	<ID>_RCD

<bfld-identifier>		::=	<ID>_BFLD

<member-identifier>	::=	<ID>

<int-identifier>		::=	<member-identifier>

<bool-identifier>		::=	<member-identifier>

<set-identifier>		::=	<member-identifier>

<array-identifier>	::=	<member-identifier>

<cnst-identifier>		::=	<ID>_CNST

## 5.4	Basic data types

All TYPES shall be defined prior to use.  The following basic types can be used to build more complex types:

<int>	::=	<INT8>|

<INT16>|

<INT24>|

<INT32>|

<INT40>|

<INT48>|

<INT64>

<unsigned-int>	::=	<UINT8>|

<UINT16>|

<UINT32>

<floating-point>	::=	<FLOAT32>|

<FLOAT64>

<fill>	::=		<FILL8>|

<FILL16>|

<FILL32>

<spec-type>	::=	<CHAR>|

<NI_FMAT1>|

<NI_FMAT2>|

<LTIME_DATE>|

<STIME_DATE>|

<TIME>|

<DATE>|

<RDATE>

<base-type>	::=	<BCD>|

<NIL>|

<int>|

<unsigned-int>|

<floating-point>|

<fill>|

<spec-type>

### 5.4.1	Basic data type definitions

The types are defined as follows:

| TYPE | DEFINITION | ORDER OF TRANSMISSION |
| --- | --- | --- |
| INT8 | Eight bit signed integer, binary signed two's complement. | Not applicable |
| INT16 | Sixteen bit signed integer. | DATA_ORDER in GEN_CONFIG_TBL (Table 00) |
| INT24 | Twenty-four bit signed integer. | DATA_ORDER in GEN_CONFIG_TBL (Table 00) |
| INT32 | Thirty-two bit signed integer. | DATA_ORDER in GEN_CONFIG_TBL (Table 00) |
| INT40 | Forty bit signed integer. | DATA_ORDER in GEN_CONFIG_TBL (Table 00) |
| INT48 | Forty-eight bit signed. | DATA_ORDER in GEN_CONFIG_TBL (Table 00) |
| INT64 | Sixty-four bit signed integer. | DATA_ORDER in GEN_CONFIG_TBL (Table 00) |
| UINT8 | Eight bit unsigned integer. | Not applicable |
| UINT16 | Sixteen bit unsigned integer. | DATA_ORDER in GEN_CONFIG_TBL (Table 00) |
| UINT32 | Thirty-two bit unsigned integer. | DATA_ORDER in GEN_CONFIG_TBL (Table 00) |
| FLOAT32 | Single precision floating point real number, per IEEE Std 754-1988. | DATA_ORDER in GEN_CONFIG_TBL (Table 00) |
| FLOAT64 | Double precision floating point real number, per IEEE Std 754-1988. | DATA_ORDER in GEN_CONFIG_TBL (Table 00) |
| FILL8 | Eight bits of zeroes, used as space holder or filler. | Not applicable |
| FILL16 | Sixteen bits of zeroes, used as space holder or filler. | Not applicable |
| FILL32 | Thirty-two bits of zeroes, used as space holder or filler. | Not applicable |

Figure 4 – Basic type definitions and order of transmission

### 5.4.2	Special data types

In order to add flexibility to the structure of the tables, the following data types can be used.  Their specific definition is determined within the tables themselves.

#### 5.4.2.1	Signed integers

To allow signed integer values to be easily transmitted without requiring data format translations, an indicator in GEN_CONFIG_TBL (Table 00) is provided.  This indicator, INT_FORMAT, specifies the data format for all INTx types within the tables.  The presently delineated signed integer data formats are twos complement, ones complement and sign/magnitude.

Examples of signed integer formats are:

For the following three examples the number -1 is used.

Twos Complement for INT8:

1111 1111

Ones Complement for INT8:

1111 1110

Sign/Magnitude for INT8:

1000 0001

#### 5.4.2.2	Characters

To allow different character sets to be used within the tables, a data type of CHAR has been defined.  CHAR defines both the size in octets of the character and the character set being used. Special Data Types (Section 6) provides a definition for CHAR.  The value of CHAR is defined in the GEN_CONFIG_TBL (Table 00) through the use of the variable CHAR_FORMAT.

#### 5.4.2.3	Non-integer numbers

To allow non-integer numeric values to be transmitted by different methods within the tables, additional data types have been defined.  NI_FMAT1 and NI_FMAT2 are used to transmit numeric values of varying precision.  The value of the variables NI_FORMAT1 and NI_FORMAT2, which are found in the GEN_CONFIG_TBL (Table 00), define how NI_FMAT1 and NI_FMAT2 are to be interpreted when reading from or writing to tables in an end device.  Special Data Types (Section 6) provides definitions for NI_FMAT1 and NI_FMAT2 and for the different values of NI_FORMAT1 and NI_FORMAT2.

#### 5.4.2.4	Date and time formats

To allow date and time to be transmitted by different methods within the tables, additional data types have been defined.  These are LTIME_DATE, STIME_DATE, TIME, DATE, and RDATE.  The value of the variable TM_FORMAT, which is found in the GEN_CONFIG_TBL (Table 00), defines how the various date and time formats are to be interpreted when reading from or writing to tables in an end device.  Special Data Types (Section 6) provides definitions for the date and time formats.

### 5.4.3	Miscellaneous data types

The following additional types are defined:

BCD		Definition:			Each octet is two BCD values.  The more significant value of each octet is in bits (7..4).

Binary bit values of 	0000 to 1001 	used for the digits 0 to 9

1010	used for minus (-) sign

1011	used for blank ( ) character

1100	not used

1101	used for decimal point (typically a period or 	comma)

1110	not used

1111	not used

Order of transmission:		Not applicable

NIL		Definition:			Indicator for field of length zero octets.

## 5.5	Values and constants

### 5.5.1	Constants

Constants are provided for making certain tasks of table specification easier, but not for transport.  An example of this is the accessing of a bit position within a set.  The bit field is specified within a given table by a <constant> that is equated to a particular number.

<constant_type>	::=	CONSTANTS <constant> END;

<constant>	::=	<cnst-identifier> = <number>;|

<constant>+

The constants presently defined for the document are found in Section 6.5.

### 5.5.2	Value

A value shall be a number, an <int-identifier> or an arithmetic operation between two values.  Value is always an integer result.

<value> 	::=	<number>|

<cnst-identifier>|

<tbl-identifier>.<int-identifier>|

<bfld-identifier>.<int-identifier>|

-<value>|

<value> + <value>|

<value> - <value>|

<value> / <value>|

<value> * <value>

## 5.6	Conditionals

### 5.6.1	If statements

The IF condition shall be a Boolean member of a bit field, or the value of a SET, or a relation between two values.

<condition>	::=	<bfld-identifier>.<bool-identifier>|

<tbl-identifier>.<set-identifier>.(<value>)|

<value> > <value>|

<value> >= <value>|

<value> < <value>|

<value> <= <value>|

<value> <> <value>|

<value> = <value>|

<condition> OR <condition>|

<condition> AND <condition>|

<condition> XOR <condition>|

NOT <condition>

### 5.6.2	Case statements

A case expression identifies the member of a table which controls the case statement.

<case-expression>	::=	<tbl-identifier>.<int-identifier>|

<bfld-identifier>.<int-identifier>

## 5.7	Bit field

Some data types do not always lend themselves to end on an octet boundary.  Where these occur they shall be logically grouped together into a bit field definition which shall end on an octet boundary.  For purposes of description, the bit field is treated as the basic object for appearance in the table structure.  Figure 5 illustrates a sub type structure.

| Most Significant Byte |  |  |  |  | Least Significant Byte |
| --- | --- | --- | --- | --- | --- |
| Octet | Octet | Octet | Octet | Octet | Octet |
| ((n*8)-1)..((n*8)-9) | ... | ... | ... | 15..8 | 7..0 |

n = # of octets used

Figure 5 – Sub types and bit field bit ordering

A bit field may contain one or more IF or CASE statements to modify its structure under some conditions.  The dimension of a bit field and its octet ordering for the purpose of transport is defined in terms of a basic data type (Section 5.4) as expressed in <bfld-type>.

<bfld-type>	::=	TYPE <bfld-identifier> = <bfld>

<bfld>	::=	BIT FIELD OF <unsigned-int> <bfld-member> END;

<bfld-member>	::=	<member-identifier> : <sub-type>;|

<int-identifier> : INT (<value>..<value>);|

<int-identifier> : UINT (<value>..<value>);|

<bool-identifier> : BOOL (<value>);|

<bfld-case>|

<bfld-if>|

<bfld-member>+

<sub-type>	::=	BOOL (<value>)|

INT (<value>..<value>)|

UINT (<value>..<value>)|

FILL (<value>..<value>)

<bfld-if>	::=	IF <condition> THEN <bfld-member> END;|

IF <condition> THEN <bfld-member> ELSE <bfld-member> END;

<bfld-case>	::=	CASE <case-expression> OF <bfld-case-member> END;

<bfld-case-member>	::=	<value> : <bfld-member>|

<value> - <value> : <bfld-member>|

<bfld-case-member>+

### 5.7.1	Sub type definitions

BOOL(<value>)			Definition:  Boolean operand of zero(0) for FALSE or one(1) for TRUE, in 	bit x of a bit field.

INT(<value>..<value>)		Definition:	Signed binary integer of “n” bits, represented by a range of 	successive bits.

UINT(<value>..<value>)		Definition:	Unsigned binary integer of “n” bits, represented by a range of 	successive bits.

FILL(<value>..<value>)		Definition:	Fill of “n” bits, represented by a range of successive bits.  	Used to fill out unused bits in an octet, or as a separator in a 	bit field.  The value of the fill bits is always zero(0).

## 5.8	Set

A <set> is a collection of Booleans. It is defined with its dimension in octets.

<set>	::=	SET(<dim_octet>)

<dim_octet>	::=	<value>

When evaluated for sizing of a set dimension the evaluation of <value> shall produce a non-negative integer.

An example follows that illustrates the method for specifying which member of a set is to be accessed.

Example:

FLAGS_USED	: SET(16);

IF FLAGS_USED.1 THEN ...

IF GEN_CONFIG_TBL.UDT_0_CONST THEN ...

## 5.9	Array

Multiple repetitions of the same data type used to describe a single variable can be grouped together in an array.  Array elements are indexed starting with zero.  Arrays are always transmitted from element zero to the last element.  The order of transmission of an element is a function of the data type being used.

| Element 0 | Element 1 | ... | Element n-2 | Element n-1 |
| --- | --- | --- | --- | --- |

Figure 6 – Single dimension array ordering

Arrays can be multidimensional.  The right most or last dimension is incremented prior to the first dimension.  For a two dimensional array, the first dimension can be thought of as a row and the second a column.  The array shall be transmitted in row order.

| 0,0 | 0,1 |
| --- | --- |
| 1,0 | 1,1 |

Figure 7 – Two dimension array

| 0,0 | 0,1 | 1,0 | 1,1 |
| --- | --- | --- | --- |

Figure 8 – Two dimension array ordering

An array can be of a single dimension or of multiple dimensions separated by commas. Variables shall be defined before they are used in a dimension statement.

<array>		::=	ARRAY[<dim>] OF <simple-type>

<simple-type>	::=	<base-type>|

<rcd-identifier>|

<bfld-identifier>|

<tbl-identifier>.<rcd-identifier>|

<tbl-identifier>.<bfld-identifier>

<dim>	::=	<value>|

<dim>[,<dim>]*

If the value of <dim> is zero then the array collapses to a zero element array and drops out of the table.

When evaluated for sizing of an array the evaluation of <value> shall produce a non-negative integer.

When CHAR is used in an array, there is no justification implied.  Full arrays are always transported.  It is suggested that a blank ( ) be used as fill or pad.

## 5.10	Packed record

Packed records are used to group simple types, arrays, packed records and bit fields together. A packed record can contain one or more IF statements or CASE statements to modify its structure upon some conditions. The dimension of a packed record will vary with applied conditions.

Bit fields and packed records shall be defined before they are used in a packed record.

<rcd-type>	::=	TYPE <rcd-identifier> = <rcd>

<rcd>	::=	PACKED RECORD <rcd-member>

END;

<rcd-member>	::=	<member-identifier> : <simple-type>;|

<int-identifier> : <int>;|

<int-identifier> : <unsigned-int>;|

<set-identifier> : <set>;|

<array-identifier> : <array>;|

<rcd-case>|

<rcd-if>|

<rcd-member>+

<rcd-if>	::=	IF (<condition>) THEN <rcd-member> END;|

IF (<condition>) THEN <rcd-member> ELSE <rcd-member> END;

<rcd-case>	::=	CASE <case-expression> OF <rcd-case-member> END;

<rcd-case-member>	::=	<value> : <rcd-member>|

<value>..<value> : <rcd-member>|

<rcd-case-member>+

## 5.11	Table

Tables are used to group simple types, arrays, packed records and bit fields together into a final structure.

Bit fields and packed records shall be defined before they are used in a table.

<types>	::=	<rcd-type>|

<bfld-type>|

<types>+

<table>	::=	<types> TABLE <tbl-identifier> = <rcd-identifier>;

# 6	Special data types

In order to add flexibility to the definition of some of the data types used within the tables, special data types are provided.  Their definition, once selected within the GEN_CONFIG_TBL (Table 00), remains consistent throughout all of the remaining used tables.

## 6.1	Character set selection

This selection is used to determine the structure of characters used in the tables.  CHAR_FORMAT is the controlling selector and CHAR is the data type.  CHAR_FORMAT is specified in GEN_CONFIG_TBL.

Value of CHAR_FORMAT				Definition of CHAR

0						Unassigned

1						ISO 7-bit coded character set for information interchange, per ISO/IEC 646: 1991.

2						ISO 8859/1 or ECMA-94 Latin 1 character set.

3..7						Unassigned

## 6.2	Non-integer formats

This selection is used to determine the structure of non-integer numbers used in the tables.  NI_FORMAT1 and NI_FORMAT2 are the controlling selectors, NI_FMAT1 and NI_FMAT2 provide type selection control for various data items.  NI_FORMAT1 and NI_FORMAT2 are specified in GEN_CONFIG_TBL.

Value of NI_FORMAT1		Definition of NI_FMAT1 and NI_FMAT2

and NI_FORMAT2

0					FLOAT64

1					FLOAT32

2					ARRAY[12] OF CHAR

3					ARRAY[6] OF CHAR

4					INT32  (Implied decimal point between fourth and fifth digits from least significant digit.  (e.g. 0.0001 is represented as 1))

5					ARRAY[6] OF BCD

6					ARRAY[4] OF BCD

7					INT24

8					INT32

9					INT40

10					INT48

11					INT64

12..15				Unassigned.

### 6.2.1	CHAR numbers

When CHAR is used and NI_FORMAT1 or NI_FORMAT2 has a value of 2 or 3, the number shall be represented in the following way:

<char_number>	::=	[_*][+|-]<digit>+[.<digit>*][<exponent>][_*]

<exponent>	::=	E|e|^[+|-]<digit>+

_		::=	space character

A CHAR number representation can have any number of leading spaces; followed by an optional plus or minus sign; followed by a mandatory one or more digits; followed by an optional period and zero or more digits; followed by an optional exponent.  An exponent is composed of the letter “E”, “e” or “^”; followed by an optional plus or minus sign; followed by a mandatory one or more digits.  Any number of spaces can lead or follow the <char_number> but  spaces shall not be embedded within the <char_number>.  This format ensures that clear identification of any <char_number> is possible in a stream (sequence) of <char_number>+, using the space character.

Examples:

Valid <char_number>

1.0E-7

123.6478e+03

1.2345

1.^3

Invalid <char_number>

.5

1.0 E-3

e+03

## 6.3	Date and time formats

This selection is used to determine the structure of dates and times used in the tables.  TM_FORMAT is the controlling selector and LTIME_DATE, STIME_DATE, TIME, RDATE, and DATE are the resulting data types.

In general

TM_FORMAT			Data type used

0				No clock in the end device

1				BCD with discrete fields for month, day, year, hour, minute and seconds.

2				UINT8 with discrete fields for month, day, year, hour, minute and seconds.

3				Binary value relative to a starting time as referenced by either CLOCK_TBL (Table 52) or CLOCK_STATE_TBL (Table 55):

LTIME_DATE:   01/01/1970 @ 00:00:00, 	rounded to nearest second.

STIME_DATE:   01/01/1970 @ 00:00:00, 	rounded to nearest minute.

TIME: Time in seconds since  00:00:00 	local time.

4..7				Unassigned

The date and time structures are described below as packed records, but are used in the tables as data types.

### 6.3.1	LTIME_DATE, STIME_DATE, TIME types

TYPE LTIME_DATE = PACKED RECORD

CASE GEN_CONFIG_TBL.TM_FORMAT OF

0 :	NIL		: NIL;

1 :	YEAR		: BCD;

MONTH	: BCD;

DAY		: BCD;

HOUR		: BCD;

MINUTE	: BCD;

SECOND 	: BCD;

2 :	YEAR		: UINT8;

MONTH	: UINT8;

DAY		: UINT8;

HOUR		: UINT8;

MINUTE	: UINT8;

SECOND	: UINT8;

3 :	U_TIME	: UINT32;

SECOND	: UINT8

END;

END;

TYPE STIME_DATE = PACKED RECORD

CASE GEN_CONFIG_TBL.TM_FORMAT OF

0 :	NIL		: NIL;

1 :	YEAR		: BCD;

MONTH	: BCD;

DAY		: BCD;

HOUR		: BCD;

MINUTE	: BCD;

2 :	YEAR		: UINT8;

MONTH	: UINT8;

DAY		: UINT8;

HOUR		: UINT8;

MINUTE	: UINT8;

3 :	U_TIME	: UINT32;

END;

END;

TYPE TIME = PACKED RECORD

CASE GEN_CONFIG_TBL.TM_FORMAT OF

0 :	NIL		: NIL;

1 :	HOUR		: BCD;

MINUTE	: BCD;

SECOND	: BCD;

2 :	HOUR		: UINT8;

MINUTE	: UINT8;

SECOND	: UINT8;

3 :	D_TIME	: UINT32;

END;

END;

Identifier			Value	Definition

YEAR				00..89	Years 2000..2089

90..99	Years 1990..1999

> 100	Unassigned

MONTH			0	Unassigned

1..12	Month of year

> 12	Unassigned

DAY				0	Unassigned

1..31	Day of month

> 31	Unassigned

HOUR				00..23	Hour of day, 24 hour basis.

> 23	Unassigned

MINUTE			00..59	Minute of hour

> 59	Unassigned

SECOND			00..59	Seconds of minute

> 59	Unassigned

U_TIME	 			Universal time in minutes since 01/01/1970 @ 00:00:00 as referenced by either CLOCK_TBL (Table 52) or CLOCK_STATE_TBL (Table 55).

D_TIME	 			Time in seconds since  00:00:00 local time.

### 6.3.2	RDATE type

This type defines a recurrent date. This recurrence can be yearly, monthly, weekly or based on a constant cycle of up to 64 days.

TYPE RDATE = BIT FIELD OF UINT16

MONTH				: UINT(0..3);

CASE MONTH OF

1..13 :	OFFSET		: UINT(4..7);

WEEKDAY	: UINT(8..10);

DAY 		: UINT(11..15);

14 :		FILLER1	: FILL(4..7);

WEEKDAY	: UINT(8..10);

FILLER2	: FILL(11..15);

15 :		PERIOD	: UINT(4..9);

DELTA		: UINT(10..15);

END;

END;

Identifier			Value	Definition

MONTH				0	Unassigned

1..12	Month of year

13	Action is repeated monthly

14	Action is repeated weekly

15	Action is repeated each PERIOD referenced by an ANCHOR_DATE plus DELTA.  The ANCHOR_DATE shall be supplied separately.

OFFSET			0	No offset

1	Advance to WEEKDAY before date entered.

2	Postpone to the first WEEKDAY on or after date entered.

3	Postpone to the second WEEKDAY on or after date entered.

4	Postpone to the third WEEKDAY on or after date entered.

5	Postpone to the fourth WEEKDAY on or after date entered.

6	Postpone to the last WEEKDAY of the MONTH on or after date entered.

7	Observe on date entered as well as day following date entered.

8	Postpone to Monday if Sunday.

9	Advance to Friday if Sunday.

10	Postpone to Monday if Saturday.

11	Advance to Friday if Saturday.

12	Postpone to Monday if Sunday or Saturday.

13	Advance to Friday if Sunday or Saturday.

14	Postpone to Monday if Sunday, advance to Friday if Saturday.

15	Do not observe date entered. Observe on day following date entered.

WEEKDAY			0..6	Sunday to Saturday.

7	Unassigned

PERIOD			0..63	0 to 63 days.

DELTA				0..63	0 to 63 days.

### 6.3.3	DATE Type

This type defines a non recurrent date using a field having the same size as the recurrent date type "RDATE".

TYPE DATE = BIT FIELD OF UINT16

YEAR		: UINT(0..6);

MONTH	: UINT(7..10);

DAY		: UINT(11..15);

END;

Identifier			Value	Definition

YEAR				00..89	Years 2000..2089

90..99	Years 1990..1999

> 100	Unassigned

MONTH			0	Unassigned

1..12	Month of year

> 12	Unassigned

DAY				0	Unassigned

1-31	Day of month

## 6.4	Common table or procedure identifier formats

These types are provided to ease the specification of table access parameters and provide consistent specification of these table access parameters throughout the document.

### 6.4.1	TABLE_IDA_BFLD bit field

Type TABLE_IDA_BFLD provides the table or procedure number; a flag indicating standard or manufacturer table or procedure; a flag indicating pending status; and three additional fields for definition and use within the defining data structure.

type TABLE_IDA_BFLD = bIT FIELD OF uint16

TBL_PROC_NBR	: UINT(0..10);

STD_VS_MFG_FLAG	: BOOL(11);

PENDING_FLAG	: BOOL(12);

FLAG1			: BOOL(13);

FLAG2			: BOOL(14);

FLAG3			: BOOL(15);

end;

### 6.4.2	TABLE_IDB_BFLD bit field

Type TABLE_IDB_BFLD provides the table or procedure number; a flag indicating standard or manufacturer table or procedure; and a four bit unsigned integer for definition and use within the defining data structure.

type TABLE_IDB_BFLD = bIT FIELD OF uint16

TBL_PROC_NBR	: UINT(0..10);

STD_VS_MFG_FLAG	: BOOL(11);

SELECTOR		: UINT(12..15);

end;

### 6.4.3	TABLE_IDC_BFLD bit field

Type TABLE_IDC_BFLD provides the table or procedure number; a flag indicating standard or manufacturer; a flag indicating table or procedure; and three additional fields for definition and use within the defining data structure.

type TABLE_IDC_BFLD = bIT FIELD OF uint16

TBL_PROC_NBR	: UINT(0..10);

STD_VS_MFG_FLAG	: BOOL(11);

PROC_FLAG		: BOOL(12);

FLAG1			: BOOL(13);

FLAG2			: BOOL(14);

FLAG3			: BOOL(15);

end;

## 6.5	Constants

The following constants are defined for use in these tables.  Note that these constants are not transported from device to device but merely serve as an aid in the logical specification or selection of tables.  Values for the following constants are expressed in decimal form.

TYPE CONSTANTS

FALSE_CNST						= 00;

TRUE_CNST						= 01;

GEN_CONFIG_TBL_CNST				= 00;

GENERAL_MFG_ID_TBL_CNST			= 01;

DEVICE_NAMEPLATE_TBL_CNST			= 02;

ED_MODE_STATUS_TBL_CNST			= 03;

PENDING_STATUS_TBL_CNST			= 04;

DEVICE_IDENT_TBL_CNST				= 05;

UTIL_INFO_TBL_CNST				= 06;

PROC_INITIATE_TBL_CNST				= 07;

PROC_RESPONSE_TBL_CNST			= 08;

DIM_SOURCES_LIM_TBL_CNST			= 10;

ACT_SOURCES_LIM_TBL_CNST			= 11;

UOM_ENTRY_TBL_CNST				= 12;

DEMAND_CONTROL_TBL_CNST			= 13;

DATA_CONTROL_TBL_CNST				= 14;

CONSTANTS_TBL_CNST				= 15;

SOURCES_TBL_CNST					= 16;

DIM_REGS_TBL_CNST				= 20;

ACT_REGS_TBL_CNST				= 21;

DATA_SELECTION_TBL_CNST			= 22;

CURRENT_REG_DATA_TBL_CNST			= 23;

PREVIOUS_SEASON_DATA_TBL_CNST		= 24;

PREVIOUS_DEMAND_RESET_DATA_TBL_CNST	= 25;

SELF_READ_DATA_TBL_CNST			= 26;

PRESENT_REGISTER_SELECT_TBL_CNST		= 27;

PRESENT_REGISTER_DATA_TBL_CNST		= 28;

DIM_DISP_TBL_CNST					= 30;

ACT_DISP_TBL_CNST					= 31;

DISP_SOURCE_TBL_CNST				= 32;

PRI_DISP_LIST_TBL_CNST				= 33;

SEC_DISP_LIST_TBL_CNST				= 34;

DIM_SECURITY_LIMITING_TBL_CNST		= 40;

ACT_SECURITY_LIMITING_TBL_CNST		= 41;

SECURITY_TBL_CNST				= 42;

DEFAULT_ACCESS_CONTROL_TBL_CNST		= 43;

ACCESS_CONTROL_TBL_CNST			= 44;

KEY_TBL_CNST					= 45;

DIM_TIME_TOU_TBL_CNST				= 50;

ACT_TIME_TOU_TBL_CNST				= 51;

CLOCK_TBL_CNST					= 52;

TIME_OFFSET_TBL_CNST				= 53;

CALENDAR_TBL_CNST				= 54;

CLOCK_STATE_TBL_CNST				= 55;

TIME_REMAIN_TBL_CNST				= 56;

DIM_LP_TBL_CNST					= 60;

ACT_LP_TBL_CNST					= 61;

LP_CTRL_TBL_CNST					= 62;

LP_STATUS_TBL_CNST				= 63;

LP_DATA_SET1_TBL_CNST				= 64;

LP_DATA_SET2_TBL_CNST				= 65;

LP_DATA_SET3_TBL_CNST				= 66;

LP_DATA_SET4_TBL_CNST				= 67;

DIM_LOG_TBL_CNST					= 70;

ACT_LOG_TBL_CNST					= 71;

EVENTS_ID_TBL_CNST				= 72;

HISTORY_LOG_CTRL_TBL_CNST			= 73;

HISTORY_LOG_DATA_TBL_CNST			= 74;

EVENT_LOG_CTRL_TBL_CNST			= 75;

EVENT_LOG_DATA_TBL_CNST			= 76;

DIM_UDT_FUNC_LIM_TBL_CNST			= 80;

ACT_UDT_FUNC_LIM_CNST				= 81;

UDT_LIST_TBL_CNST					= 82;

UDT_SET_TBL_CNST					= 83;

UDT_0_TBL_CNST					= 84;

UDT_1_TBL_CNST					= 85;

UDT_2_TBL_CNST					= 86;

UDT_3_TBL_CNST					= 87;

UDT_4_TBL_CNST					= 88;

UDT_5_TBL_CNST					= 89;

END;

# 7	Compliance

A device is considered to be in compliance with this document if all of the following conditions are met:

a.	The device shall accept and act upon all services defined in Section 8.0, Table Transportation Issues.

b.	GEN_CONFIG_TBL (Table 00)

1.	Two way communicating devices shall transmit GEN_CONFIG_TBL (Table 00) on request.

2.	Suppliers of one way communicating devices shall, as a minimum, supply GEN_CONFIG_TBL (Table 00) in some form.

c.	Any table transported between devices shall be either a standard table as defined by this document or a manufacturer table defined by the device manufacturer.  All standard and manufacturer tables supported for the current device implementation shall be specified in GEN_CONFIG_TBL (Table 00).

d.	Any procedure written to the device shall be either a standard procedure as defined by this document or a manufacturer procedure defined by the device manufacturer.  All standard and manufacturer procedures supported for the current device implementation shall be specified in GEN_CONFIG_TBL (Table 00).

e.	Some standard tables contain data structures that can be collapsed by a control flag.  The control flag shall be determinable based on this document.  Collapsed fields shall not be transported.  An array of zero elements is a collapsed field.

f.	A device is not required to use every data structure within a table, however it shall transport all non-collapsed data structures within a table.  Unused fields are considered in compliance if byte count and format are correct and if manufacturers identify unused fields.  It is recommended that unused fields be filled with zeros or spaces.

g.	This document specifies variable formats for some data structures.  The variable formats shall be consistent with the format as specified in GEN_CONFIG_TBL (Table 00).  Refer to Section 5.0 Syntax and Section 6.0 Special Data Types for details.

h.	Dimensional function limiting tables (FLC) and actual function limiting tables (FLC+1) specify the designed and usable limits for variables used within a given decade.  (For a complete explanation of function limiting tables, see Section 4.1 Standard Tables.) The permissible combinations are listed in Figure 1.

# 8	Table transportation issues

The effective transport of table structures is dependent only on the presence of basic read and write services. While the marketplace may dictate the incorporation of more sophisticated services, it is left to the implementors of specific protocol stacks to select the specific read and write services to be included.

# 8.1	Minimum services and parameters

## 8.1.1	Read service

This service causes the transfer of data from the initiating device to the target device and is required for two way communications.

Read Request				The read request shall be capable of both a complete and a partial table read. This is accomplished by one required parameter and optional parameters. The required parameter is a table identifier. Optional parameters define partial table retrieval.

Table Identifier			This parameter has a range of 0 to 8191.  This range is further subdivided as follows:

• The range from 0 to 2047 provides access to Standard tables 0 to 2047.

• The range from 2048 to 4095 provides access to Manufacturer tables 0 to 2047.

• The range 4096 to 6143 provides access to Standard pending tables 0 to 2047.

• The range 6144 to 8191 provides access to Manufacturer pending tables 0 to 2047.

Partial Table Retrieval		The retrieval of a portion of a table, a partial table, is possible through the use of one of two methods.  These methods are offset-count and index-count. The absence of either of these methods implies the entire table shall be read.

Offset Count Method			The offset-count method is based upon supplying an offset from the beginning of the selected table and, optionally, a count of the number of octets to read from the offset point. The range of the offset from the beginning of the table is 0 to a minimum of 65,535 octets. The range of the count of the number of octets to read from the offset point is 0 to a minimum of 65,535 octets. A zero for the count value or the absence of the count value shall cause  the entire remaining table to be read starting at the offset point.

Indexed-Count Method		The index-count method is based upon accommodating a minimum of 5 indices relative to the first data structure within the table and, optionally a count of the number of octets to read from the index point. Each index shall range from 0 to a maximum of 65,535. The range of the count of the number of octets to read from the index point is 0 to a minimum of 65,535 octets. A zero for the count value or the absence of the count value shall cause the entire remaining table to be read starting at the index point.

Read Response

DATA				The read response shall contain as a minimum the table data selected by the aforementioned parameters supplied with the read request.

When the read request table identifier specifies a pending table, a six octet pending event description precedes the requested information. The pending event description parameters are described in the Pending Event Description, Section 8.2.

## 8.1.2	Write service

This service causes the transfer of un-requested data to a target device from the initiating device and is required for both one and two way communications.

Write Request				The write request shall be capable of both a complete and a partial table write. This is accomplished by one required parameter and partial table identifiers and the write data field. The required parameter is a table identifier. Optional parameters define partial table write.

Table Identifier			This parameter has a range of 0 to 8191.  This range is further subdivided as follows:

The range from 0 to 2047 provides access to Standard tables 0 to 2047.

The range from 2048 to 4095 provides access to Manufacturer tables 0 to 2047.

The range 4096 to 6143 provides access to Standard pending tables 0 to 2047. Several additional parameters are required for writing to a pending table.  These parameters are appended to the front of the table data to be written.  These parameters are described in the Table Data Write section.

The range 6144 to 8191 provides access to Manufacturer pending tables 0 to 2047. Several additional parameters are required for writing to a pending table.  These parameters are appended to the front of the table data to be written as a pending event description. The pending event description parameters are described in Pending Event Description, Section 8.2.

Partial Table Identifier		The writing of a portion of a table, a partial table, is possible through the use of one of two methods.  These methods are offset-count and index-count. The absence of either of these methods implies the entire table shall be written.

Offset-Count Method		The offset-count method is based upon supplying an offset from the beginning of the selected table and, optionally, a count of the number of octets to write to the offset point.  The range of the offset from the beginning of the table is 0 to a minimum of 65,535 octets.  The range of the count of the number of octets to write to the offset point is 0 to a minimum of 65,535 octets.  A zero for the count value or the absence of the count value shall cause the entire remaining table to be written from the offset point.

Indexed-Count Method		The indexed method is based upon accommodating a minimum of 5 indices relative to the first data structure within the table and, optionally , a count of the number of octets to write to the index point. Each index shall range from 0 to a maximum of 65,535.  The range of the count of the number of octets to write shall range from 0 to a maximum of 65,535 octets. A zero for the count value or the absence of the count value shall imply writing the entire remaining table from the index point.

Data				The data field contains the information to write.

When the write request table identifier specifies a pending table, a six octet pending event description precedes the information in the data field.

Write Response			As a minimum, no response is required to the write request. This does not preclude use of write responses supported by implementor languages or their supporting protocols.

# 8.2	Pending event description

Data read from or written into a pending table is identical to data read from or written into non-pending tables in structure with the exception of the addition of a preceding pending event descriptor.

TYPE	STATUS_BFLD	 = BIT FIELD OF UINT8

EVENT_CODE			: UINT(0..3);

SELF_READ_FLAG		: BOOL(4);

DEMAND_RESET_FLAG		: BOOL(5);

RESERVED			: FILL(6..7);

END;

TYPE	PENDING_EVENT_DESC_RCD = PACKED RECORD

EVENTS_SELECTOR		: STATUS_BFLD;

EVENT_STORAGE		: ARRAY[5] OF UINT8;

END;

Identifier			Value	Definition

STATUS_BFLD			Selectors indicating action to be performed upon activation of selected table.

EVENT_CODE			Variable that specifies the condition upon which the pending table shall be made active.  The trigger condition is stored in the EVENT_STORAGE variable.

0	The pending table is activated based on an absolute time contained in the EVENT_STORAGE variable.

1	The pending table is activated based on a relative time contained in the EVENT_STORAGE variable.

2	The pending table is activated based on a non-time associated trigger contained in the EVENT_STORAGE variable.

3..15	Reserved.

SELF_READ_FLAG	FALSE	Do not perform a self read before pending table is activated.

TRUE	Perform a self read, if capable, before pending table is activated.

DEMAND_RESET_FLAG	FALSE	Do not perform a demand reset before pending table is activated.

TRUE	Perform a demand reset, if capable, before pending table is activated.

RESERVED			Reserved for future use.

PENDING_EVENT_DESC_RCD

EVENTS_SELECTOR		Status bits indicating various conditions associated with a pending table.

EVENT_STORAGE		Variable for storage of the trigger condition that causes a pending table to become active.

STIME_DATE	0	For an EVENT_CODE of 0 this variable contains the year, month, day, hour, and minute in the format indicated.

ARRAY[5] OF UINT8	1	For an EVENT_CODE of 1 this variable contains an offset time where the array positions indicate the following:  [0]  weeks; [1] days; [2] hours; [3] minutes; and [4] seconds.

CHAR		2	For an EVENT_CODE of 2 this variable contains in the first four characters the ASCII manufacturer code per ANNEX A of this document.  The final character is an event number as defined by the manufacturer.

# 9	Tables

## 9.1	Decade 00: configuration tables

This decade contains tables associated with end device configuration, identification, procedures and responses, and information required for data manipulation due to hardware configurations.

### 9.1.1	Table 00 general configuration table

Table 00 Data Description

GEN_CONFIG_TBL (Table 00) contains general end device configuration information.  It also establishes the total set of tables, procedures, and the selection of special types used in the end device.  If a default set is used, it is indicated by this table.

type format_control_1_BFLD = bIT FIELD OF uint8

DATA_ORDER			: UINT(0..0);

CHAR_format		: uint(1..3);

MODEl_SELECT		: UINT(4..6);

FILLER				: FILL(7..7);

end;

type format_control_2_BFLD = bit field of uint8

tm_format			: uint(0..2);

DATA_ACCESS_METHOD	: UINT(3..4);

ID_FORM			: UINT(5..5);

INT_FORMAT			: UINT(6..7);

end;

type format_control_3_BFLD = bit field of uint8

NI_FORMAT1			: UINT(0..3);

NI_FORMAT2			: UINT(4..7);

end;

TYPE GEN_CONFIG_RCD = PACKED RECORD

format_control_1	: format_control_1_BFLD;

format_control_2	: format_control_2_BFLD;

format_control_3	: format_control_3_BFLD;

MANUFACTURER		: ARRAY[4] OF CHAR;

NAMEPLATE_TYPE		: UINT8;

default_set_used		: uint8;

MAX_PROC_PARM_LENGTH	: UINT8;

MAX_RESP_DATA_LEN	: UINT8;

STD_VERSION_NO		: uint8;

STD_REVISION_NO		: uint8;

DIM_STD_TBLS_USED	: uint8;

DIM_MFG_TBLS_USED	: UINT8;

DIM_STD_PROC_USED	: UINT8;

DIM_MFG_PROC_USED	: UINT8;

DIM_MFG_STATUS_USED	: UINT8;

NBR_PENDING		: UINT8;

STD_TBLS_USED		: SET(GEN_CONFIG_TBL.DIM_STD_TBLS_USED);

MFG_TBLS_USED		: SET(GEN_CONFIG_TBL.DIM_MFG_TBLS_USED);

STD_PROC_USED		: SET(GEN_CONFIG_TBL.DIM_STD_PROC_USED);

MFG_PROC_USED		: SET(GEN_CONFIG_TBL.DIM_MFG_PROC_USED);

std_tbls_write		: set(GEN_CONFIG_TBL.dim_std_tbls_used);

mfg_tbls_write		: set(GEN_CONFIG_TBL.dim_mfg_tbls_used);

END;

TABLE GEN_CONFIG_TBL = GEN_CONFIG_RCD;

Identifier				Value		Definition

FORMAT_CONTROL_1_BFLD

DATA_ORDER			Variable to define order of multibyte numeric data transfer.

0	Least significant byte first.

1	Most significant byte first.

CHAR_FORMAT		See Character Set Selection in Special Data Types, Section 6.1. Unsigned binary code where:

0	Unassigned.

1	ISO 7-bit coded character set for information interchange, per ISO/IEC 646: 1991.

2	ISO 8859/1 or ECMA-94 Latin 1 character set.

3..7	Unassigned.

MODEL_SELECT		Unsigned binary code where:

0	A code indicating the I/O model selects 
sources as an 8 bit index into the DATA_CONTROL_TBL (Table 14).

1..7	Reserved

FORMAT_CONTROL_2_BFLD

TM_FORMAT			Data type used for Dates & Time:

0	No clock in the end device

1	BCD with discrete fields for month, day, year, hour, minute and seconds.

2	UINT8 with discrete fields for month, day, year, hour, minute and seconds.

3	UINT32 with time referenced as seconds relative to a starting time. The reference point is as follows:

LTIME_DATE:   01/01/1970 @ 00:00:00 GMT, rounded to nearest second.

STIME_DATE:   01/01/1970 @ 00:00:00 GMT, rounded to nearest minute.

TIME: Time in seconds since 00:00:00 local time (including time zone offset).

4..7	Unassigned

DATA_ACCESS_METHOD		Variable to designate method of passing the table data after GEN_CONFIG_TBL (Table 00) has been interrogated.  Note:  All data access methods support complete table access.

Identifier				Value		Definition

0	Complete table access only.  No partial table access supported.

1	Offset-count access method is supported.

2	Index-count method is supported.

3	Both methods 1 and 2 of data access method are supported.

ID_FORM			Indicates the format of the  identifier field in DEVICE_IDENT_TBL (Table 05).

0	CHAR string.

1	BCD string.

INT_FORMAT			Indicates the format of signed integer types.

0	Signed integer types are represented in twos complement format.

1	Signed integer types are represented in ones complement format.

2	Signed integer types are represented in sign/magnitude format.

3	Reserved.

FORMAT_CONTROL_3_BFLD

NI_FORMAT1			Indicates the type of non-integer value used throughout the tables where specified as NI_FMAT1.  Refer to Section 6.2, Non-integer Formats, for details.

NI_FORMAT2			Indicates the type of non-integer value throughout the tables where shown as NI_FMAT2.  Refer to Section 6.2, Non-integer Formats, for details.

GEN_CONFIG_RCD

FORMAT_CONTROL_1		See descriptions above.

FORMAT_CONTROL_2		See descriptions above.

FORMAT_CONTROL_3		See descriptions above.

MANUFACTURER		End device manufacturer identification.  Refer to Annex A, ID Codes For Meter Equipment Manufacturers for list of manufacturer identifiers.

NAMEPLATE_TYPE		Entry used to select the nameplate record structure to be used in DEVICE_NAMEPLATE_TBL (Table 02).

0	Gas

1	Water

2	Electric

3..255	Unassigned

DEFAULT_SET_USED		Indicates which, if any, default sets are used.  See Annex C, DEFAULT SETS FOR DECADE TABLES, for the default set definitions.

Identifier				Value		Definition

0	No default values in use.  See Section 4.1, Standard Tables, Figure 1, conditions C through H for more detail.

1	Default set #1, Simple Meter Register, in use.

2	Default set #2, Simple Demand Meter, in use.

3	Default set #3, Simple TOU Meter, in use.

4	Default set #4, Simple Profile Recorder, in use.

5..255	Reserved for default table value sets.

MAX_PROC_PARM_LENGTH		Manufacturer defined maximum length for argument parameters passed to procedures in PROC_INITIATE_TBL (Table 07).

MAX_RESP_DATA_LEN		Manufacturer defined maximum length representing length returned by procedures in PROC_RESPONSE_TBL (Table 08).

STD_VERSION_NO		Unsigned binary number designating the version of the particular industry set of standard tables.

0	Pre-release or informal release document.

1	Original Standard Table Set, first release document.

2..255	Reserved for Standards Committee use only.

STD_REVISION_NO		Unsigned binary number that designates a minor change to a version of this standard. Within a given version of this standard, all revisions with a lower revision number shall be backward compatible. If this is not true then a new version number shall be required.

DIM_STD_TBLS_USED		Octets required to represent the set of standard tables used in  GEN_CONFIG_TBL.STD_TBLS_USED (Table 00). This is a mechanism to allow the table identifier set to expand in size from simple devices to complex devices.

DIM_MFG_TBLS_USED		Octets required to represent the set of manufacturer tables used in  GEN_CONFIG_TBL.MFG_TBLS_USED (Table 00).  This is a mechanism to allow the table identifier set to expand in size from simple devices to complex devices.

DIM_STD_PROC_USED		Octets required to represent the set of standard procedures used in GEN_CONFIG_TBL.STD_PROC_USED (Table 00).  This is a mechanism to allow the standard defined procedure identifier set to expand in size.

Identifier				Value		Definition

DIM_MFG_PROC_USED		Octets required to represent the set of manufacturer procedures used in GEN_CONFIG_TBL.MFG_PROC_USED (Table 00).  This is a mechanism to allow the manufacturer defined  procedure identifier set to expand in size.

DIM_MFG_STATUS_USED	0..255	The number of octets allocated for indicating manufacturer specific status flags.

NBR_PENDING		Number of pending status sets in PENDING_STATUS_TBL (Table 04).

STD_TBLS_USED		This set variable indicates which of the Standard Tables are implemented by the device. Tables are represented by bits 0 through (8*DIM_STD_TBLS_USED-1), with a 1 representing a TRUE or implemented condition and a 0 representing a FALSE or not implemented condition.

MFG_TBLS_USED		This set variable indicates which of the Manufacturer Tables are implemented by the device. Tables are represented by bits 0 through (8*DIM_MFG_TBLS_USED-1), with a 1 representing a TRUE or implemented condition and a 0 representing a FALSE or not implemented condition.

STD_PROC_USED		This set variable indicates which of the Standard Procedures are implemented by the device.  Procedures are represented by bits 0 through (8*DIM_STD_PROC_USED-1), with a 1 representing a TRUE or implemented condition and a 0 representing a FALSE or not implemented condition.

MFG_PROC_USED		This set variable indicates which of the Manufacturer's Procedures are implemented by the device.  Procedures are represented by bits 0 through (8*DIM_MFG_PROC_USED-1), with a 1 representing a TRUE or implemented condition and a 0 representing a FALSE or not implemented condition.

STD_TBLS_WRITE		This set variable indicates which of the standard tables are capable of being rewritten.  Tables are represented by bits 0 through (8*DIM_STD_TBLS_USED-1), with a 1 representing a writeable table and a zero representing a table that cannot be written.

Identifier				Value		Definition

MFG_TBLS_WRITE		This set variable indicates which of the standard tables are capable of being rewritten.  Tables are represented by bits 0 through (8*DIM_MFG_TBLS_USED-1), with a 1 representing a writeable table and a zero representing a table that cannot be written.

### 9.1.2	Table 01 general manufacturer identification table

Table 01 Data Description

GENERAL_MFG_ID_TBL (Table 01) is a general manufacturer identification data table for Water, Gas, and Electric Utility end devices.  The values of the data items shall be set up by the manufacturer and left unchanged since they are determined by the functionality of the device.

TYPE MANUFACTURER_IDENT_RCD = PACKED RECORD

MANUFACTURER			: ARRAY[4] OF CHAR;

ED_MODEL				: ARRAY[8] OF CHAR;

HW_VERSION_NUMBER		: UINT8;

HW_REVISION_NUMBER		: UINT8;

FW_VERSION_NUMBER		: UINT8;

FW_REVISION_NUMBER		: UINT8;

IF GEN_CONFIG_TBL.ID_FORM THEN

MFG_SERIAL_NUMBER	: ARRAY[8] OF BCD;

ELSE

MFG_SERIAL_NUMBER	: ARRAY[16] OF CHAR;

END;

END;

TABLE GENERAL_MFG_ID_TBL = MANUFACTURER_IDENT_RCD;

Identifier			Value	Definition

MANUFACTURER_IDENT_RCD

MANUFACTURER		Name of manufacturer. Refer to Annex A, ID Codes For Meter Equipment Manufacturers, ID definitions.

ED_MODEL			Model identifier of the end device left justified.  For example 'ENG M3 '.

HW_VERSION_NUMBER	0..255	Manufacturer's hardware version number.  Implies functional changes.

HW_REVISION_NUMBER	0..255	Manufacturer's hardware revision number. Implies product corrections or improvements. Recommended use of '0' to designate prototyping device.

Identifier				Value		Definition

FW_VERSION_NUMBER	0..255	Manufacturer's firmware version number. Changes in value imply functional differences.

FW_REVISION_NUMBER	0..255	Manufacturer's firmware revision number. Changes in value imply product corrections or improvements. Recommend use of '0' to designate preproduction or prototyping software.

MFG_SERIAL_NUMBER		Manufacturer's serial number for the end device. 16 BCD digits OR CHARs.

### 9.1.3	Table 02 device nameplate table

Table 02 Data Description

DEVICE_NAMEPLATE_TBL (Table 02) is the nameplate data table.  This table contains a record structure for each type of end device (e.g. water, gas, electric).  The structure to be used is specified in GEN_CONFIG_TBL.NAMEPLATE_TYPE (Table 00).  This table presently has nameplate structures defined for an electric meter, a gas meter and a water meter.

{water device structures}

TYPE W_WATER_DEVICE_BFLD = BIT FIELD OF UINT16

W_ED_TYPE			: UINT(0..2);

W_FLUID_TYPE		: UINT(3..6);

W_ED_DRIVE			: UINT(7..10);

W_ED_PIPE_SIZE		: UINT(11..15);

END;

{gas device structures}

TYPE G_ED_TYPE_BFLD = BIT FIELD OF UINT8

G_ED_TYPE			: UINT(0..2);

G_MECH_FORM		: UINT(3..5);

G_ENG_METRIC		: UINT(6..6);

FILLER				: FILL(7..7);

END;

TYPE G_PRESSURE_RCD = PACKED RECORD

G_MAX_PRESS		: NI_FMAT2;

G_UOM_PRESS		: UINT8;

END;

TYPE G_FLOW_RCD = PACKED RECORD

G_MAX_FLOW			: NI_FMAT2;

G_UOM_FLOW		: UINT8;

END;

TYPE G_SIZE_BFLD = BIT FIELD OF UINT8

G_GEAR_DRIVE		: UINT(0..2);

G_INPUT_OUTPUT_PIPE	: UINT(3..7);

END;

TYPE G_COMPENSATION_BFLD = BIT FIELD OF UINT8

G_COMP_TEMP		: UINT(0..4);

G_COMP_PRESS		: UINT(5..7);

END;

TYPE G_GAS_DEVICE_RCD = PACKED RECORD

G_ED_TYPE			: G_ED_TYPE_BFLD;

G_MAX_PRESS		: G_PRESSURE_RCD;

G_FLOW			: G_FLOW_RCD;

G_GEAR_PIPE_SIZE		: G_SIZE_BFLD;

G_COMPENSATION		: G_COMPENSATION_BFLD;

END;

{electric device structures}

TYPE E_ELEMENTS_BFLD = BIT FIELD OF UINT16

E_FREQ			: UINT(0..2);

E_NO_OF_ELEMENTS		: UINT(3..5);

E_BASE_TYPE			: UINT(6..9);

E_ACCURACY_CLASS		: UINT(10..15);

END;

TYPE E_VOLTS_BFLD = BIT FIELD OF UINT8

E_ELEMENTS_VOLTS		: UINT(0..3);

E_ED_SUPPLY_VOLTS	: UINT(4..7);

END;

TYPE E_AMPS_RCD = PACKED RECORD

E_CLASS_MAX_AMPS		: ARRAY[6] OF CHAR ;

E_TA				: ARRAY [6] OF CHAR ;

END;

TYPE E_ELECTRIC_DEVICE_RCD = PACKED RECORD

E_Kh				: ARRAY [6] OF CHAR ;

E_Kt 				: ARRAY [6] OF CHAR ;

E_INPUT_SCALAR		: UINT8;

E_ED_CONFIG			: ARRAY[5] OF CHAR;

E_ELEMENTS			: E_ELEMENTS_BFLD;

E_VOLTS			: E_VOLTS_BFLD;

E_AMPS			: E_AMPS_RCD;

END;

TYPE DEVICE_DEFINITION_RCD = PACKED RECORD

CASE GEN_CONFIG_TBL.NAMEPLATE_TYPE OF

0		: G_GAS_DEVICE		:G_GAS_DEVICE_RCD;

1		: W_WATER_DEVICE		:W_WATER_DEVICE_BFLD;

2		: E_ELECTRIC_DEVICE	:E_ELECTRIC_DEVICE_RCD;

3..255		: RESERVED			:NIL;

END;

END;

TABLE DEVICE_NAMEPLATE_TBL = DEVICE_DEFINITION_RCD;

The following structures are generally associated with Water Utility end devices. The values of the data items shall be set up by the manufacturer and left unchanged since they are determined by the functionality of the device.

Identifier			Value	Definition

W_WATER_DEVICE_BFLD

W_ED_TYPE			Code representing water end device type.

0		Meter

1		Valve

2		Pressure Regulator

3		Pressure gauge

4		Backflow

5		Other

6-7		Unassigned

W_FLUID_TYPE		Code representing type of fluid  measured by water end device.

0		Potable water

1		Hot water

2		Non-potable water

3		Sewage primary water

4		Sewage secondary water

5		Sewage tertiary water

6		Other

7		Unassigned

W_ED_DRIVE			Code representing water end device drive.

0		Piston

1		Disc

2		Multi-jet

3		Turbine

4		Compound

5		Propeller

6		Ultra-sonic

7		Magnetic-coupled

8		Differential pressure

9		Mass

10		Variable area

11		Open channel

12		Oscillatory

13		Other

14..15		Unassigned

W_ED_PIPE_SIZE		Code representing end device pipe size.

0		1/2"		13 mm

1		5/8"		15 mm

2		3/4”		20 mm

3		1"		25 mm

4		1 1/2"	40 mm

5		2"		50 mm

6		3"		80 mm

7		4"		100 mm

8		6"		160 mm

9		8"		200 mm

10		10"		250 mm

11		12"		300 mm

12		14"		350 mm

13		16"		400 mm

14		18"		450 mm

15		20"		500 mm

16		22"		Not standard

17		24"		600 mm

18		26"		Not standard

19		28"		Not standard

20		30"		Not standard

21		32"		800 mm

22		34"		Not standard

23		36"		900 mm

24		40”		1000 mm

25		48”		1200 mm

26..31		Unassigned

The following structures are generally associated with Gas Utility end devices. The values of the data items shall be set up by the manufacturer and left unchanged since they are determined by the functionality of the device.

Identifier			Value	Definition

G_ED_TYPE_BFLD

G_ED_TYPE			Code representing gas end device type.

0		Unclassified

1		Gas meter

2		Gas pressure regulator

3		Sensor

4		Load shed device

5		Cathodic protection unit

6..7		Unassigned

G_MECH_FORM		Unsigned binary number identifying the primary mechanical design principle of the device depending upon value of G_ED_TYPE.

For G_ED_TYPE = 1.

0		Unclassified

1		Bellows meter

2		Rotary

3		Turbine meter

4		Fluidic oscillator

5		Anemometer

6..7		Unassigned

For G_ED_TYPE = 2.

0		Unclassified

1		Diaphragm

2..7		Unassigned

For G_ED_TYPE = 3.

0		Unclassified

1		Physical parameter to 	voltage

2		Physical parameter to current

3		Physical parameter to 	frequency

4		Open/closed switch

5..7		Unassigned

For G_ED_TYPE = 5.

0		Unclassified

1		Pipe to soil

2		Impedance

3..7		Unassigned

G_ENG_METRIC	0		English

1		Metric

G_PRESSURE_RCD

G_MAX_PRESS		End device maximum design pressure.

G_UOM_PRESS		See field ID_CODE in UOM_ENTRY_TBL (Table 12).

G_FLOW_RCD

G_MAX_FLOW			End device maximum design flow rate.

G_UOM_FLOW		See field ID_CODE in UOM_ENTRY_TBL (Table 12).

G_SIZE_BFLD

G_GEAR_DRIVE		Code representing gas meter gear drive size.

0		None

1		1/2'

2		1'

3		2'

4		5'

5		10'

6		100'

7		1000'

G_INPUT_OUTPUT_PIPE		Code representing gas meter pipe size.

English	Metric

0	None		None

1	1/2"

2	5/8"

3	3/4"

4	1"

5	1 1/2"

6	2"

7	4"

8	6"

9	8"

10	10"

11	12"

12	14"

13	16"

14	18"

15	20"

16	22"

17	24"

18	26"

19	28"

20	30"

21	32"

22	34"

23	36"

24..31	Unassigned

G_COMPENSATION_BFLD

G_COMP_TEMP		Code representing the gas meter temperature compensation type.

0		Uncompensated

1		Mechanical

2		Sensor

3..7		Unassigned

G_COMP_PRESS		Code representing the gas meter pressure compensation type.

0		Uncompensated

1		Mechanical

2		Sensor

3..7		Unassigned

The following structures are generally associated with Electric Utility end devices. The values of the data items shall be set up by the manufacturer and left unchanged since they are determined by the functionality of the device.

Identifier			Value	Definition

E_ELEMENTS_BFLD			Contains binary codes physically describing the end device.

E_FREQ			Power frequency rating code. The codes are:

0		DC

1		25 Hz

2		50

3		50 or 60 hz

4		60 hz

5		400 hz

6		Unassigned

7		Unclassified

E_NO_OF_ELEMENTS		Number of commodity measuring elements per measuring input to the end device. This code indicates the number of elements as follows:

0		None

1		1 element

2		2 element

3		2.5 element

4		3 element

5		6 element

6		1.5 elements

7		Unassigned.

E_BASE_TYPE			Indicates the type of meter base as follows:

0		None

1		S-base (socket)

Identifier			Value	Definition

2		A-base (ANSI bottom connected)

3		K-base

4		IEC bottom connected

5		switchboard

6		rackmount

7		B-base

8		P-base (Canadian Standard)

9-15		Unassigned

E_ACCURACY_CLASS		Reserved for future ANSI solid state meter standard accuracy class definitions.

E_VOLTS_BFLD			Contains binary codes describing meter RMS voltages.

E_ELEMENTS_VOLTS		Meter element voltage code. This binary code indicates the meter voltage class as follows;

0		None

1		69.3

2		72

3		120

4		208

5		240

6		277

7		480

8		120 thru 277

9		120 thru 480

10-15		Un-assigned.

E_ED_SUPPLY_VOLTS		External supply voltage code. This value identifies the meter supply voltage as follows:

0		Internal

1		69.3 AC

2		72 AC

3		120 AC

4		208 AC

5		240 AC

6		277 AC

7		480 AC

8		120 thru 277 AC

9		120 thru 480 AC

10		48 DC

11		125 DC

12		250 DC

13-15		Unassigned

E_AMPS_RCD

E_CLASS_MAX_AMPS		End device class or IEC max amp rating.

E_TA				The RMS amperage test amps (TA) specified by the manufacturer for the main test and/or adjustment of the meter.

Identifier			Value	Definition

E_ELECTRIC_DEVICE_RCD

E_Kh				Watthours per revolution.  (May be represented as Unithours per equivalent revolution).

E_Kt				The commodity amount selected for the test pulse output.

E_INPUT_SCALAR		Divisor by which to scale input values. For example if input consists of pulses, an INPUT_SCALAR value of 2 would cause the pulse stream to be divided by 2.

E_ED_CONFIG			Form number per ANSI C12.10. Characters.

DEVICE_DEFINITION_RCD		This is full device nameplate data structure configured as a case statement for selection of water, gas or electric end devices.  The selection variable is GEN_CONFIG_TBL.NAMEPLATE_TYPE (Table 00).

### 9.1.4	Table 03 ED_MODE status table

Table 03 Data Description

ED_MODE_STATUS_TBL (Table 03) provides the current operating mode and status of various conditions in the end device.  It allows for both standard and manufacturer specific status definitions.

TYPE ED_MODE_BFLD = BIT FIELD OF UINT8

METERING_FLAG			: BOOL(0);

TEST_MODE_FLAG			: BOOL(1);

METER_SHOP_MODE_FLAG		: BOOL(2);

FILLER					: FILL(3..7);

END;

TYPE ED_STD_STATUS1_BFLD = BIT FIELD OF UINT16

UNPROGRAMMED_FLAG		: BOOL(0);

CONFIGURATION_ERROR_FLAG	: BOOL(1);

SELF_CHK_ERROR_FLAG		: BOOL(2);

RAM_FAILURE_FLAG			: BOOL(3);

ROM_FAILURE_FLAG			: BOOL(4);

NONVOL_MEM_FAILURE_FLAG	: BOOL(5);

CLOCK_ERROR_FLAG		: BOOL(6);

MEASUREMENT_ERROR_FLAG	: BOOL(7);

LOW_BATTERY_FLAG		: BOOL(8);

LOW_LOSS_POTENTIAL_FLAG	: BOOL(9);

DEMAND_OVERLOAD_FLAG		: BOOL(10);

POWER_FAILURE_FLAG 		: BOOL(11);

FILLER					: FILL(12..15);

END;

TYPE ED_STD_STATUS2_BFLD = BIT FIELD OF UINT8

FILLER			: FILL(0..7);

END;

TYPE ED_MFG_STATUS_RCD = PACKED RECORD

ED_MFG_STATUS	: SET(GEN_CONFIG_TBL.DIM_MFG_STATUS_USED);

END;

TYPE ED_MODE_STATUS_RCD = PACKED RECORD

ED_MODE		: ED_MODE_BFLD;

ED_STD_STATUS1	: ED_STD_STATUS1_BFLD;

ED_STD_STATUS2 	: ED_STD_STATUS2_BFLD;

ED_MFG_STATUS	: ED_MFG_STATUS_RCD;

END;

TABLE ED_MODE_STATUS_TBL = ED_MODE_STATUS_RCD;

Identifier			Value	Definition

TYPE ED_MODE_BFLD

METERING_FLAG	FALSE	End Device is not in Metering mode.  It may or may not be accumulating measured or input quantities.

TRUE	End Device is in Metering mode and is accumulating measured or input quantities.

TEST_MODE_FLAG	FALSE	End Device is not in Test Mode.

TRUE	End Device is in Test Mode.

METER_SHOP_MODE_FLAG	FALSE	End device is not in Meter Shop Mode.

TRUE	End device is in Meter Shop Mode.

TYPE ED_STD_STATUS1_BFLD

UNPROGRAMMED_FLAG	FALSE	End Device is programmed.

TRUE	End Device is not programmed or it is in a factory default state.

CONFIGURATION_ERROR_FLAG

FALSE	End Device did not detect a configuration error.

TRUE	End Device did detect a configuration error.

SELF_CHK_ERROR_FLAG	FALSE	End Device did not detect a self check error.

TRUE	End Device did detect a self check error.

RAM_FAILURE_FLAG	FALSE	End Device did not detect a RAM Memory failure.

TRUE	End Device did detect a RAM Memory failure.

ROM_FAILURE_FLAG	FALSE	End Device did not detect a ROM memory failure.

TRUE	End Device did detect a ROM Memory failure.

Identifier			Value	Definition

NONVOL_MEM_FAILURE_FLAG

FALSE	End Device did not detect a nonvolatile memory failure.

TRUE	End Device did detect a nonvolatile memory failure.

CLOCK_ERROR_FLAG	FALSE	End Device did not detect a clock error.

TRUE	End Device did detect a clock error.

MEASUREMENT_ERROR_FLAG

FALSE	End Device did not detect a measurement element error.

TRUE	End Device did detect a  measurement element error.

LOW_BATTERY_FLAG	FALSE	End Device  did not detect a low battery error.

TRUE	End Device did detect a low battery error.

LOW_LOSS_POTENTIAL_FLAG

FALSE	End Device did not detect a  potential that is below a predetermined value.

TRUE	End Device did detect a device potential that is below a predetermined value.

DEMAND_OVERLOAD_FLAG	FALSE	End Device did not detect a  demand threshold overload.

TRUE	End Device did detect a  demand threshold overload.

POWER_FAILURE_FLAG 	FALSE	End Device did not detect a  power failure.

TRUE	End Device did detect a  power failure.

ED_STD_STATUS2_BFLD		Standard status code bit field 2 is a place holder for future expansion.

ED_MFG_STATUS_RCD		Set containing the manufacturer specific status flags.

ED_MODE_STATUS_RCD

ED_MODE			See ED_MODE_BFLD.

ED_STD_STATUS1		See ED_STD_STATUS1_BFLD.

ED_STD_STATUS2		See ED_STD_STATUS2_BFLD.

ED_MFG_STATUS		See ED_MFG_STATUS_RCD.

ED_MODE_

### 9.1.5	Table 04 pending status table

Table 04 Data Description

PENDING_STATUS_TBL (Table 04) is established to provide an indication of the tables present in the end device with a pending status.  Information contained within this table includes table number, manufacturer or standard table indicator, conditions (events) upon which activation of a pending table is to occur, self-read or demand reset upon activation indicators and several additional status variables.

TYPE STATUS_BFLD = BIT FIELD OF UINT8

EVENT_CODE			: UINT(0..3);

SELF_READ_FLAG		: BOOL(4);

DEMAND_RESET_FLAG	: BOOL(5);

RESERVED			: FILL(6..7);

END;

TYPE EVENT_RCD = PACKED RECORD

EVENT_SELECTOR		: STATUS_BFLD;

EVENT_STORAGE		: ARRAY[5] OF UINT8;

END;

TYPE ENTRY_ACTIVATION_RCD = PACKED RECORD

EVENT				: EVENT_RCD;

TABLE_SELECTOR		: TABLE_IDA_BFLD;

END;

TYPE	PENDING_ACTIVATION_RCD = PACKED RECORD

STANDARD_PENDING			: SET(GEN_CONFIG_TBL.DIM_STD_TBLS_USED);

MANUFACT_PENDING			: SET(GEN_CONFIG_TBL.DIM_MFG_TBLS_USED);

LAST_ACTIVATION_DATE_TIME	: STIME_DATE;

NBR_PENDING_ACTIVATION		: UINT8;

PENDING_TABLES			: ARRAY[GEN_CONFIG_TBL.NBR_PENDING] OF 								ENTRY_ACTIVATION_RCD;

END;

TABLE PENDING_STATUS_TBL = PENDING_ACTIVATION_RCD;

Identifier			Value	Definition

STATUS_BFLD			Selectors indicating action to be performed upon activation of selected table.

EVENT_CODE			Variable that specifies the condition upon which the pending table shall be made active.  The trigger condition is stored in the EVENT_STORAGE variable.

0	The pending table is activated based on an absolute time contained in the EVENT_STORAGE variable.

1	The pending table is activated based on a relative time contained in the EVENT_STORAGE variable.

2	The pending table is activated based on a non-time associated trigger contained in the EVENT_STORAGE variable.

3..15	Reserved.

Identifier			Value	Definition

SELF_READ_FLAG	FALSE	Do not perform a self read before pending table is activated.

TRUE	Perform a self read, if capable, before pending table is activated.

DEMAND_RESET_FLAG	FALSE	Do not perform a demand reset before pending table is activated.

TRUE	Perform a demand reset, if capable, before pending table is activated.

RESERVED			Reserved for future use.

ENTRY_ACTIVATION_RCD

EVENTS_SELECTOR		Status bits indicating various conditions associated with a pending table.

EVENT_STORAGE		Variable for storage of the trigger condition that causes a pending table to become active.

STIME_DATE		For an EVENT_CODE of 0 this variable contains the year, month, day, hour, and minute in the format indicated.

STIME_DATE		For an EVENT_CODE of 1 this variable contains the weeks, days, hours, minutes and seconds in the format indicated.

CHAR			For an EVENT_CODE of 2 this variable contains in the first four characters the ASCII manufacturer code per ANNEX A of this document.  The final character is an event number as defined by the manufacturer.

TABLE_SELECTOR		Variable containing the table number, the standard or manufacturer flag and the pending flag.  The pending flag indicates that the associated table has not been activated.

PENDING_ACTIVATION_RCD

STANDARD_PENDING		This set variable indicates which of the standard tables are capable of being written with a pending status.

MANUFACT_PENDING		This set variable indicates which of the manufacturer tables are capable of being written with a pending status.

LAST_ACTIVATION_DATE_TIME	Date and time of the last pending table activated.

NBR_PENDING_ACTIVATION		Number of activation events in the PENDING_STATUS_TBL structure that have yet to be activated.

PENDING_TABLES		List of pending tables and associated activation triggers.

### 9.1.6	Table 05 device identification table

Table 05 Data Description

DEVICE_IDENT_TBL (Table 05)  This table provides the unique identifier for the device as specified by the user.

TYPE IDENT_RCD = PACKED RECORD

IF GEN_CONFIG_TBL.ID_FORM THEN

IDENTIFICATION	: ARRAY[10] OF BCD;

ELSE

IDENTIFICATION	: ARRAY[20] OF CHAR;

END;

END;

TABLE DEVICE_IDENT_TBL	= IDENT_RCD;

Identifier			Value	Definition

IDENT_RCD

IDENTIFICATION		Array of 20 characters or 20 BCD digits used to uniquely identify the device.

### 9.1.7	Table 06 utility information table

Table 06 Data Description

UTIL_INFO_TBL (Table 06) is for utility use in providing additional end device identifying or tracking information.

TYPE UTIL_INFO_RCD = PACKED RECORD

OWNER_NAME			: ARRAY[20] OF CHAR;

UTILITY_DIV				: ARRAY[20] OF CHAR;

IF GEN_CONFIG_TBL.ID_FORM THEN

SERVICE_POINT_ID		: ARRAY[10] OF BCD;

ELEC_ADDR			: ARRAY[10] OF BCD;

DEVICE_ID			: ARRAY[10] OF BCD;

UTIL_SER_NO			: ARRAY[10] OF BCD;

CUSTOMER_ID		: ARRAY[10] OF BCD;

ELSE

SERVICE_POINT_ID		: ARRAY[20] OF CHAR;

ELEC_ADDR			: ARRAY[20] OF CHAR;

DEVICE_ID			: ARRAY[20] OF CHAR;

UTIL_SER_NO			: ARRAY[20] OF CHAR;

CUSTOMER_ID		: ARRAY[20] OF CHAR;

END;

COORDINATE_1			: ARRAY[10] OF UINT8;

COORDINATE_2			: ARRAY[10] OF UINT8;

COORDINATE_3			: ARRAY[10] OF UINT8;

TARIFF_ID				: ARRAY[8] OF CHAR;

EX1_SW_VENDOR			: ARRAY[4] OF CHAR;

EX1_SW_VERSION_NUMBER		: UINT8;

EX1_SW_REVISION_NUMBER		: UINT8;

EX2_SW_VENDOR			: ARRAY[4] OF CHAR;

EX2_SW_VERSION_NUMBER		: UINT8;

EX2_SW_REVISION_NUMBER		: UINT8;

PROGRAMMER_NAME		: ARRAY[10] OF CHAR;

MISC_ID				: ARRAY[30] OF CHAR;

END;

TABLE UTIL_INFO_TBL = UTIL_INFO_RCD;

Identifier			Value	Definition

UTIL_INFO_RCD

OWNER_NAME		Up to 20 Characters. All printable characters are valid.

UTILITY_DIV			Utility division number. Up to 16 Characters. All printable characters are valid.

SERVICE_POINT_ID		20 Characters or BCD digits. ID number attached to the service point.

ELEC_ADDR			End device logical electrical address for mapping and study purposes.  This is used by the utility as information only.

DEVICE_ID			The ID attached to the hardware. 20 Characters or BCD digits.

UTIL_SER_NO			Utility specified serial number. Up to 20 Characters or BCD digits.

CUSTOMER_ID		Up to 20 Characters or BCD digits. All printable characters are valid if characters.

COORDINATE_1		Generalized mapping coordinate x.

COORDINATE_2                  	   	Generalized mapping coordinate y.

COORDINATE_3		Generalized mapping coordinate z.

TARIFF_ID			Identification of the billing tariff.

EX1_SW_VENDOR		Name of manufacturer, in ASCII, that provided configuration/programming software.   Refer to Annex A, Codes for Meter Equipment Manufacturers, for list of manufacturer identifiers.

EX1_SW_VERSION_NUMBER	0..255	Configuration/programming software version number, unsigned binary number. Changes in value imply functional differences.

Identifier			Value	Definition

EX1_SW_REVISION_NUMBER	0..255	Configuration/programming software revision number, unsigned binary number. Changes in value imply product corrections or improvements. Recommend use of '0' to designate preproduction or prototyping software.

EX2_SW_VENDOR		Name of manufacturer, in ASCII, that provided configuration/programming software.   Refer to Annex A, Codes for Meter Equipment Manufacturers, for list of manufacturer identifiers.

EX2_SW_VERSION_NUMBER	0..255	Configuration/programming software version number. Changes in value imply functional differences.

EX2_SW_REVISION_NUMBER	0..255	Configuration/programming software revision number, unsigned binary number. Changes in value imply product corrections or improvements. Recommend use of '0' to designate preproduction or prototyping software.

PROGRAMMER_NAME		Name of the last programmer or programming device.

MISC_ID			Thirty characters, free form. All printable characters are allowed.  This could be used to contain approval #, verification #, bar code, etc.

### 9.1.8	Table 07 procedure initiate table

Table 07 Data Description

PROC_INITIATE_TBL (Table 07) allows for the execution of commands using the table structure.  To execute a command a procedure identifier (PROC), a sequence number (SEQ_NBR), and an optional parameter list (PARM) are written into this table.  The response to the command is placed in PROC_RESPONSE_TBL (Table 08) and is available to be read.  As a minimum response, all commands produce an echo of the procedure identifier (PROC), an echo of the sequence number (SEQ_NBR), and a result code.

TYPE	PROC_FORMAT_RCD = PACKED RECORD

PROC		: TABLE_IDB_BFLD;

SEQ_NBR	: UINT8;

PARM		: PARM_RCD;

END;

TABLE	PROC_INITIATE_TBL = PROC_FORMAT_RCD;

Identifier			Value	Definition

TABLE_IDB_BFLD

TBL_PROC_NBR	0..2047	Procedure number to be executed.

STD_VS_MFG_FLAG	FALSE	Procedure selected by TBL_PROC_NBR is a standard defined procedure.

TRUE	Procedure selected by TBL_PROC_NBR is a manufacturer defined procedure.

SELECTOR 			Describes how the response to the procedure is handled.

0	Post response in PROC_RESPONSE_TBL (Table 08) on completion.

1	Post response in PROC_RESPONSE_TBL (Table 08) on exception.

2	Do not post response in PROC_RESPONSE_TBL (Table 08).

3	Post response in PROC_RESPONSE_TBL (Table 08) immediately and post another response in PROC_RESPONSE_TBL (Table 08) on completion.

4..15	Reserved.

PROC_FORMAT_RCD

PROC				Bit field indicating procedure number to be executed and whether the procedure is a standard defined procedure or a manufacturer defined procedure.  It also describes the response method.

SEQ_NBR		0..255	The sequence number is supplied by initiator of the procedure.  It shall be returned with procedure response in PROC_RESPONSE_TBL (Table 08) as a means of coordination.

PARM				Argument for procedure as defined for individual procedures in section 9.1.8.1 and sub-sections.

#### 9.1.8.1 Standard procedures

The following procedures are defined as standard procedures by this document.  STD_VS_MFG_FLAG shall be set to FALSE.

##### 9.1.8.1.1 Cold start

This procedure causes the end device to return to a manufacturer default known state. All data values, programs and conditions may be lost. Communication may be broken. If an Event Log exists, an attempt shall be made to retain it.

TBL_PROC_NBR	00	Procedure Number.

PARM_RCD			Not Used

RESP_DATA_RCD		Not Used

##### 9.1.8.1.2 Warm start

This procedure causes the end device to return to a "power-up" state.  Communication may be broken.

TBL_PROC_NBR	01	Procedure Number.

PARM_RCD			Not Used

RESP_DATA_RCD		Not Used

##### 9.1.8.1.3 Save configuration

This procedure causes the end device to save its active configuration.

TBL_PROC_NBR	02	Procedure Number.

PARM_RCD			Not Used

RESP_DATA_RCD		Not Used

##### 9.1.8.1.4 Clear data

This procedures causes the end device to purge generated data fields but retain programming fields.  Data fields to be purged are specified by the device manufacturer.

TBL_PROC_NBR	03 	Procedure Number.

PARM_RCD			Not Used

RESP_DATA_RCD		Not Used

##### 9.1.8.1.5 Reset list pointers

When invoked, the end device attempts to reset list control variables to their initial state. To execute this procedure, the initiator shall in addition be required to have access permission to the procedure and write access permission to the table containing the selected list(s).

TBL_PROC_NBR	04 	Procedure Number.

PARM_RCD			Defined below

RESP_DATA_RCD		Not used

Parameters

TYPE PARM_RCD = PACKED RECORD

LIST: UINT8;

END;

Identifier			Value	Definition

PARM_RCD

LIST			0	Reserved

1	EVENT_LOG_TBL (Table 76)

2	SELF_READ_DATA_TBL (Table 26)

3	LP_DATA_SET1_TBL (Table 64)

4	LP_DATA_SET2_TBL (Table 65)

5	LP_DATA_SET3_TBL (Table 66)

6	LP_DATA_SET4_TBL (Table 67)

7	LP_DATA_SET1_TBL (Table 64) and

LP_DATA_SET2_TBL (Table 65) and

LP_DATA_SET3_TBL (Table 66) and

LP_DATA_SET4_TBL (Table 67)

8	HISTORY_LOG_TBL (Table 74)

9..254	Reserved

255	All lists except EVENT_LOG_TBL (Table 76)

##### 9.1.8.1.6 Update last read entry

When invoked, the end device attempts to reduce the list variable NBR_UNREAD_ENTRIES by the value specified.  To execute this procedure, the initiator shall in addition be required to have access to the procedure and write access to the table containing the selected list(s).

TBL_PROC_NBR	05	Procedure Number.

PARM_RCD			Defined below

RESP_DATA_RCD		Not used

Parameters

TYPE PARM_RCD = PACKED RECORD

LIST: UINT8;

ENTRIES_READ : UINT16;

END;

Identifier			Value	Definition

PARM_RCD

LIST			0	Reserved

1	EVENT_LOG_TBL (Table 76)

2	SELF_READ_DATA_TBL (Table 26)

3	LP_DATA_SET1_TBL (Table 64)

4	LP_DATA_SET2_TBL (Table 65)

5	LP_DATA_SET3_TBL (Table 66)

6	LP_DATA_SET4_TBL (Table 67)

7	LP_DATA_SET1_TBL (Table 64) and

LP_DATA_SET2_TBL (Table 65) and

LP_DATA_SET3_TBL (Table 66) and

LP_DATA_SET4_TBL (Table 67)

8	HISTORY_LOG_TBL (Table 74)

9..254	Reserved

255	All lists except EVENT_LOG_TBL (Table 76)

ENTRIES_READ	0..65535	Number of entries confirmed.

##### 9.1.8.1.7 Change end device mode

This procedure changes the operational modes in the end device to the argument described below.

TBL_PROC_NBR	06	Procedure Number.

PARM_RCD		Defined below

RESP_DATA_RCD		Defined below

Parameters

TYPE PARM_RCD = PACKED RECORD

ED_MODE		: ED_MODE_STATUS_TBL.ED_MODE_BFLD;

END;

Identifier			Value	Definition

PARM_RCD

ED_MODE			See ED_MODE_STATUS_TBL.ED_MODE (Table 03).  This is the desired mode.

Response

TYPE RESP_DATA_RCD = PACKED RECORD

ED_MODE		: ED_MODE_STATUS_TBL.ED_MODE_BFLD;

END;

Identifier			Value	Definition

RESP_DATA_RCD

ED_MODE			See ED_MODE_STATUS_TBL.ED_MODE (Table 03).  The mode the device is in after the execution of this procedure.

##### 9.1.8.1.8 Clear standard status flags

When invoked, the end device attempts to clear all standard status flags.

TBL_PROC_NBR	07	Procedure Number.

PARM_RCD		Not used

RESP_DATA_RCD		Defined below

Response

TYPE RESP_DATA_RCD = PACKED RECORD

ED_STD_STATUS_1	: ED_MODE_STATUS_TBL.ED_STD_STATUS1;

ED_STD_STATUS_2	: ED_MODE_STATUS_TBL.ED_STD_STATUS2;

END;

Identifier			Value	Definition

RESP_DATA_RCD

ED_STD_STATUS_1		See ED_MODE_STATUS_TBL.ED_STD_STATUS1 (Table 03).

ED_STD_STATUS_2		See ED_MODE_STATUS_TBL.ED_STD_STATUS2 (Table 03).

##### 9.1.8.1.9 Clear Manufacturer Status Flags

When invoked, the end device attempts to clear all manufacturer status flags.

TBL_PROC_NBR	08	Procedure Number.

PARM_RCD		Defined below

RESP_DATA_RCD		Not used

Response

TYPE PARM_RCD = PACKED RECORD

ED_MFG_STATUS	: ED_MODE_STATUS_TBL.ED_MFG_STATUS;

END;

Identifier			Value	Definition

PARM_RCD

ED_MFG_STATUS		See ED_MODE_STATUS_TBL.ED_MFG_STATUS (Table 03).

##### 9.1.8.1.10 Remote reset

When invoked, this procedure attempts to perform the specified combination of resets and change of season.  The following resets are supported: Self Read, Demand Reset, and Season Change.

TBL_PROC_NBR	09	Procedure Number.

PARM_RCD			Defined below

RESP_DATA_RCD		Defined below

Parameters

TYPE ACTION_FLAG_BFLD = BIT FIELD OF UINT8

DEMAND_RESET_FLAG	: BOOL(0);

SELF_READ_FLAG		: BOOL(1);

SEASON_CHANGE_FLAG	: BOOL(2);

NEW_SEASON			: UINT(3..6);

FILLER				: FILL(7..7);

END;

TYPE PARM_RCD = PACKED RECORD

ACTION_FLAG			: ACTION_FLAG_BFLD;

END;

Identifier			Value	Definition

ACTION_FLAG_BFLD

DEMAND_RESET_FLAG	FALSE	Do not perform a demand reset.

TRUE	Perform a demand reset.

SELF_READ_FLAG	FALSE	Do not perform a self read.

TRUE	Perform a self read.

SEASON_CHANGE_FLAG	FALSE	Do not perform a change to the new season specified

TRUE	Perform a change to the new season specified.

NEW_SEASON		0..15	Season to change to if SEASON_CHANGE bit is set.

PARM_RCD

ACTION_FLAG			Bit mask denotes the reset actions to perform.

Response

TYPE RESP_DATA_RCD = PACKED RECORD

SUCCESS_FLAG		: ACTION_FLAG_BFLD;

END;

Identifier			Value	Definition

ACTION_FLAG_BFLD

DEMAND_RESET_FLAG	FALSE	Did not perform a demand reset.

TRUE	Performed a demand reset.

SELF_READ_FLAG	FALSE	Did not perform a self read.

TRUE	Performed a self read.

SEASON_CHANGE_FLAG	FALSE	Did not perform a change to the new season specified

TRUE	Performed a change to the new season specified.

NEW_SEASON		0..15	The season number the end device changed to if SEASON_CHANGE bit was set.

RESP_DATA_RCD

SUCCESS_FLAG		Indicates which "resets" were successful by setting corresponding bits.

##### 9.1.8.1.11 Set date and/or time

This procedure attempts to set the date and/or time in the end device.

TBL_PROC_NBR	10	Procedure Number.

PARM_RCD			Defined below

RESP_DATA_RCD		Defined below

Parameters

TYPE SET_MASK_BFLD = BIT FIELD OF UINT8

SET_TIME_FLAG		: BOOL(0);

SET_DATE_FLAG		: BOOL(1);

SET_TIME_DATE_QUAL	: BOOL(2);

FILLER				: FILL(3..7);

END;

TYPE PARM_RCD = PACKED RECORD

SET_MASK			: SET_MASK_BFLD;

DATE_TIME			: LTIME_DATE;

TIME_DATE_QUAL		: CLOCK_TBL.TIME_DATE_QUAL_BFLD;

END;

Identifier			Value	Definition

SET_MASK_BFLD

SET_TIME_FLAG	FALSE	Do not set time.

TRUE	Set time.

SET_DATE_FLAG	FALSE	Do not set date.

TRUE	Set date.

SET_TIME_DATE_QUAL	FALSE	Do not set time date qualifier.

TRUE	Set time date qualifier.

PARM_RCD

SET_MASK			Bit mask denotes the actions to perform.

DATE_TIME			New date and time.

TIME_DATE_QUAL_BFLD		Status qualifying the end device time.

DAY_OF_WEEK			Current day of the week.

0	Sunday

1	Monday

2	Tuesday

3	Wednesday

4	Thursday

5	Friday

6	Saturday

7	Unassigned

DST_FLAG			Daylight savings time status.

FALSE	End device time is not in daylight savings time.

TRUE	End device time is in daylight savings time.

GMT_FLAG		FALSE	End device time does not correspond to Greenwich Mean Time.

TRUE	End device time corresponds to Greenwich Mean Time.

TM_ZN_APPLIED_FLAG	FALSE	Time zone offset has not been applied to the end device time.

TRUE	Time zone offset has been applied to the end device time.

DST_APPLIED_FLAG	FALSE	End device time does not include daylight savings adjustment.

TRUE	End device time includes daylight savings adjustment.

Response

TYPE RESP_DATA_RCD = PACKED RECORD

DEV_DATE_TIME_BEFORE	: LTIME_DATE;

DEV_DATE_TIME_AFTER	: LTIME_DATE;

END;

Identifier			Value	Definition

RESP_DATA_RCD

DEV_DATE_TIME_BEFORE		Date and time in the end device just before set date time procedure was executed.

DEV_DATE_TIME_AFTER		Date and time in the end device just after set date time procedure was executed.

##### 9.1.8.1.12 Execute diagnostics procedure

This procedure initiates an end device diagnostic procedure.

TBL_PROC_NBR	11	Procedure Number.

PARM_RCD			Not Used

RESP_DATA_RCD		Not Used

##### 9.1.8.1.13 Activate all pending tables

This procedure causes the end device to immediately activate all pending tables regardless of activation trigger(s).

TBL_PROC_NBR	12	Procedure Number.

PARM_RCD			Not Used

RESP_DATA_RCD		Not Used

##### 9.1.8.1.14 Activate specific pending table(s)

This procedure causes the end device to immediately activate any pending table(s) with the specified activation trigger.

TBL_PROC_NBR	13	Procedure Number.

PARM_RCD			Defined below

RESP_DATA_RCD		Not Used

Parameters

TYPE PARM_RCD = PACKED RECORD

EVENT			: PENDING_STATUS_TBL.EVENT_RCD;

END;

Identifier			Value	Definition

PARM_RCD

EVENT				See EVENT_RCD (Table 04).

##### 9.1.8.1.15 Clear all pending tables

This procedure causes the end device to immediately clear the pending state all pending tables.

TBL_PROC_NBR	14	Procedure Number.

PARM_RCD			Not Used

RESP_DATA_RCD		Not Used

##### 9.1.8.1.16 Clear specific pending table(s)

This procedure causes the end device to immediately clear the pending status of all pending table(s) with the specified activation trigger.

TBL_PROC_NBR	15	Procedure Number.

PARM_RCD			Defined below

RESP_DATA_RCD		Not Used

Parameters

TYPE PARM_RCD = PACKED RECORD

EVENT		: PENDING_STATUS_TBL.EVENT_RCD;

END;

Identifier			Value	Definition

PARM_RCD

EVENT				See EVENT_RCD (Table 04).

##### 9.1.8.1.17 Start load profile

This procedure starts all defined load profile sets.

TBL_PROC_NBR	16	Procedure Number.

PARM_RCD			Not used

RESP_DATA_RCD		Not used

##### 9.1.8.1.18 Stop load profile

This procedure stops all active load profile sets.

TBL_PROC_NBR	17	Procedure Number.

PARM_RCD			Not Used

RESP_DATA_RCD		Not Used

##### 9.1.8.1.19 Log in

When invoked, this procedure establishes the active USER_ID that is used in the HISTORY_LOG_TBL (Table 74) and in the EVENT_LOG_TBL (Table 76) and supplies a password.

TBL_PROC_NBR	18	Procedure Number.

PARM_RCD			Defined below

RESP_DATA_RCD		Not Used

Parameters

TYPE PARM_RCD = PACKED RECORD

USER_ID		: UINT16;

PASSWORD		: ARRAY[20] OF UINT8;

END;

Identifier			Value	Definition

PARM_RCD

USER_ID		0..65535	ID associated with current user.

Note: USER_ID of zero and USER_ID of one should be avoided since it represents an end device initiated event and manually initiated event respectively in the loggers.

PASSWORD			Password supplied. The first character of the password shall be placed in the zero element of the array.

##### 9.1.8.1.20	Log out

Deactivates the USER_ID and password.

TBL_PROC_NBR	19	Procedure Number.

PARM_RCD			Not Used

RESP_DATA_RCD		Not Used

### 9.1.9	Table 08 procedure response table

Table 08 Data Description

PROC_RESPONSE_TBL (Table 08) is a complementary table to PROC_INITIATE_TBL (Table 07). This table contains a response, which gets posted to Table 08 as a result of a write to PROC_INITIATE_TBL (Table 07).

TYPE	PROC_RESPONSE_RCD = PACKED RECORD

PROC			: TABLE_IDB_BFLD;

SEQ_NBR		: UINT8;

RESULT_CODE	: UINT8;

RESP_DATA		: RESP_DATA_RCD;

END;

TABLE PROC_RESPONSE_TBL = PROC_RESPONSE_RCD;

Identifier			Value	Definition

TABLE_IDB_BFLD

TBL_PROC_NBR	0..2047	Procedure number executed by end device.

STD_VS_MFG_FLAG	FALSE	Procedure was a standard procedure.

TRUE	Procedure was a manufacturer defined procedure.

SELECTOR			Not used in PROC_RESPONSE_TBL (Table 08).  See PROC_INITIATE_TBL (Table 07).

PROC_RESPONSE_RCD

PROC				Bit field indicating procedure number executed and whether the procedure was a standard defined or a manufacturer defined.

Identifier			Value	Definition

SEQ_NBR		0..255	Supplied by initiator of the procedure PROC_INITIATE_TBL (Table 07).  Returned with response as a means of coordination.

RESULT_CODE		Code which identifies the status of the procedure execution. The codes are defined as follows:

0	Procedure completed.

1	Procedure accepted but not fully completed.

2	Invalid parameter for known procedure, procedure was ignored.

3	Procedure conflicts with current device setup, procedure was ignored.

4	Timing constraint, procedure was ignored.

5	No authorization for requested procedure, procedure was ignored.

6	Un-recognized procedure, procedure was ignored.

7..255	Reserved.

RESP_DATA_RCD		Procedure response record as defined for individual procedures in PROC_INITIATE_TBL (Table 07).  RESP_DATA_RCD is posted if procedure was successfully completed (RESULT_CODE = 0) and SELECTOR in PROC_INITIATE_TBL (Table 07) is not set to a value of 2.

## 9.2	Decade 10: data source tables

This decade contains tables associated with data sources.

### 9.2.1	Table 10 dimension sources limiting table

Table 10 Data Description

DIM_SOURCES_LIM_TBL (Table 10) contains maximum dimensions and end device capabilities for establishing data sources.

TYPE SOURCE_FLAGS_BFLD = BIT FIELD OF UINT8

PF_EXCLUDE_FLAG		: BOOL(0);

RESET_EXCLUDE_FLAG	: BOOL(1);

BLOCK_DEMAND_FLAG	: BOOL(2);

SLIDING_DEMAND_FLAG	: BOOL(3);

THERMAL_DEMAND_FLAG	: BOOL(4);

SET1_PRESENT_FLAG	: BOOL(5);

SET2_PRESENT_FLAG	: BOOL(6);

FILLER				: FILL(7..7);

END;

TYPE SOURCE_RCD = PACKED RECORD

SOURCE_FLAGS			: SOURCE_FLAGS_BFLD;

NBR_UOM_ENTRIES			: INT8;

NBR_DEMAND_CTRL_ENTRIES	: UINT8;

DATA_CTRL_LENGTH			: UINT8;

NBR_DATA_CTRL_ENTRIES		: UINT8;

NBR_CONSTANTS_ENTRIES		: UINT8;

CONSTANTS_SELECTOR		: UINT8;

NBR_SOURCES			: UINT8;

END;

TABLE DIM_SOURCES_LIM_TBL = SOURCE_RCD;

Identifier			Value	Definition

SOURCE_FLAGS_BFLD

PF_EXCLUDE_FLAG		Power fail exclusion is defined as ignoring demand for maximum calculations for some period immediately after a power failure.

FALSE	End device is not capable of power fail exclusion.

TRUE	End device is capable of power fail exclusion.

RESET_EXCLUDE_FLAG		Reset exclusion is defined as inhibiting demand reset for some period after a reset.

FALSE	Reset exclusion is not supported by the end device.

TRUE	Reset exclusion is supported by the end device.

BLOCK_DEMAND_FLAG	FALSE	Block demand is not supported by the end device.

TRUE	Block demand is supported by the end device.

SLIDING_DEMAND_FLAG	FALSE	Sliding demand is not supported by the end device.

TRUE	Sliding demand is supported by the end device.

THERMAL_DEMAND_FLAG	FALSE	Thermal demand is not supported by the end device.

TRUE	Thermal demand is supported by the end device.

SET1_PRESENT_FLAG	FALSE		The end device does not support the first set of optional constants in the electric record of the CONSTANTS_TBL (Table 15).

TRUE		The end device does support the first set of optional constants in the electric record of the CONSTANTS_TBL (Table 15).

SET2_PRESENT_FLAG	FALSE		The end device does not support the second set of optional constants in the electric record of the CONSTANTS_TBL (Table 15).

TRUE		The end device does support the second set of optional constants in the electric record of the CONSTANTS_TBL (Table 15).

SOURCE_RCD

Identifier			Value	Definition

SOURCE_FLAGS		Bit fields that indicate what demand and TOU register functions the end device is capable of performing.

NBR_UOM_ENTRIES	0..255	Maximum number of entries in UOM_ENTRY_TBL (Table 122).

NBR_DEMAND_CTRL_ENTRIES	0..255	Maximum number of entries in the DEMAND_CONTROL_TBL (Table 13).

DATA_CTRL_LENGTH	0..255	Manufacturer supplied value that determines the width in octets of an entry in the first array of the DATA_CONTROL_TBL (Table 14).

NBR_DATA_CTRL_ENTRIES	0..255	Maximum number of entries in the DATA_CONTROL_TBL (Table 14).

NBR_CONSTANTS_ENTRIES	0..255	Maximum number of entries in the CONSTANTS_TBL (Table 15).

CONSTANTS_SELECTOR		This value is the selector for the record structure used in the CONSTANTS_TBL (Table 15).

0	GAS_CONSTANTS_AGA3_RCD data structure selected.

1	GAS_CONSTANTS_AGA7_RCD data structure selected.

2	ELECTRIC_CONSTANTS_RCD data structure selected.

3..255	Reserved for future use.

NBR_SOURCES		0..255	Maximum number of entries in the SOURCES_TBL (Table 16).

### 9.2.2	Table 11 actual sources limiting table

Table 11 Data Description

ACT_SOURCES_LIM_TBL (Table 11) contains the actual parameters of Table 10 the end device has been configured with.

TABLE ACT_SOURCES_LIM_TBL = DIM_SOURCES_LIM_TBL.SOURCE_RCD;

Identifier			Value	Definition

SOURCE_FLAGS_BFLD

PF_EXCLUDE_FLAG		Power fail exclusion is defined as ignoring demand for maximum calculations for some period immediately after a power failure.

FALSE	Power fail exclusion is not active.

TRUE	Power fail exclusion is active.

Identifier			Value	Definition

RESET_EXCLUDE_FLAG		Reset exclusion is defined as inhibiting demand reset for some period after a reset.

FALSE	Reset exclusion is not in use by the end device.

TRUE	Reset exclusion is in use by the end device.

BLOCK_DEMAND_FLAG	FALSE	Block demand is not in use by the end device.

TRUE	Block demand is in use by the end device.

SLIDING_DEMAND_FLAG	FALSE	Sliding demand is not in use by the end device.

TRUE	Sliding demand is in use by the end device.

THERMAL_DEMAND_FLAG	FALSE	Thermal demand is not in use by the end device.

TRUE	Thermal demand is in use by the end device.

SET1_PRESENT_FLAG	FALSE		The end device is not using the first set of optional constants in the electric record of the CONSTANTS_TBL (Table 15).

TRUE		The end device is using the first set of optional constants in the electric record of the CONSTANTS_TBL (Table 15).

SET2_PRESENT_FLAG	FALSE		The end device is not using the second set of optional constants in the electric record of the CONSTANTS_TBL (Table 15).

TRUE	The end device is using the second set of optional constants in the electric record of the CONSTANTS_TBL (Table 15).

SOURCE_RCD

SOURCE_FLAGS		Bit fields that indicate what demand and TOU register functions are in use by the end device as configured.

NBR_UOM_ENTRIES	0..255	Actual number of entries in UOM_ENTRY_TBL (Table 12).

NBR_DEMAND_CTRL_ENTRIES	0..255	Actual number of entries in the DEMAND_CONTROL_TBL (Table 13).

DATA_CTRL_LENGTH	0..255	Manufacturer defined number of octets in an element of the array of the DATA_CONTROL_TBL (Table 14).

NBR_DATA_CTRL_ENTRIES	0..255	Actual number of entries in the DATA_CONTROL_TBL (Table 14).

NBR_CONSTANTS_ENTRIES	0..255	Actual number of entries in the CONSTANTS_TBL (Table 15).

CONSTANTS_SELECTOR	0..255	This value is the selector for the record structure used in the CONSTANTS_TBL (Table 15).

0	GAS_CONSTANTS_AGA3_RCD data structure selected.

Identifier			Value	Definition

1	GAS_CONSTANTS_AGA7_RCD data structure selected.

2	ELECTRIC_CONSTANTS_RCD data structure selected.

3..255	Reserved for future use.

NBR_SOURCES		0..255	Actual number of entries in the SOURCES_TBL (Table 16).

### 9.2.3	Table 12 unit of measure entry table

Table 12 Data Description

UOM_ENTRY_TBL (Table 12) provides a method for describing data attributes. It may be used to tag data sources.

TYPE UOM_ENTRY_BFLD = BIT FIELD OF UINT32

ID_CODE				: UINT(0..7);

TIME_BASE				: UINT(8..10);

MULTIPLIER				: UINT(11..13);

Q1_ACCOUNTABILITY			: BOOL(14);

Q2_ACCOUNTABILITY			: BOOL(15);

Q3_ACCOUNTABILITY			: BOOL(16);

Q4_ACCOUNTABILITY			: BOOL(17);

NET_FLOW_ACCOUNTABILITY	: BOOL(18);

SEGMENTATION			: UINT(19..21);

HARMONIC				: BOOL(22);

RESERVED				: FILL(23..30);

NFS					: BOOL(31);

END;

TYPE UOM_ENTRY_RCD = PACKED RECORD

UOM_ENTRY	: ARRAY[ACT_SOURCES_LIM_TBL.NBR_UOM_ENTRIES] OF 						UOM_ENTRY_BFLD;

END;

TABLE UOM_ENTRY_TBL = UOM_ENTRY_RCD;

Identifier			Value	Definition

UOM_ENTRY_RCD

ID_CODE			The UOM ID_CODE identifies the physical quantity of interest (equivalent to physical units in the field of physics as used for dimensional analysis). The standard defines entries for use by the Water, Gas, or Electrical Utilities and provides for generic entries for description of internal data items.  The defined units of measure have been grouped solely for readability purposes.  Note that because the unit of measure record includes a time base indicator some of the units have an extra time factor that is canceled out by the unit of measure record time base indicator.  For example, ID_CODE 77, Therm per Hr is actually Therm once the time base indicator is properly set.

{Electric Industry units}

Power:

0	Active power - W

1	Reactive power - VAR

2	Apparent power - VA

3	Phasor power - VA = sqrt(W2+VAR2)

4	Quantity power - Q(60)

5	Quantity power - Q(45)

6	Reserved

7	Reserved

Voltage:

8	RMS Volts

9	Average Volts (average of |V|)

10	RMS Volts Squared (V2)

11	Instantaneous volts

Current:

12	RMS Amps

13	Average Current (average of |I|)

14	RMS Amps Squared (I2)

15	Instantaneous current

Percent Total Harmonic Distortion:

16	T.H.D. V (IEEE—Institute of Electrical and

Electronics Engineers)

17	T.H.D. I (IEEE)

18	T.H.D. V (IC—Industry Canada)

19	T.H.D. I (IC)

Event Codes:

50	Power outages

51	Number of demand resets

52	Number of times programmed

53	Number of minutes on battery carryover

Phase Angle:

20	V-VA, Voltage phase angle

21	Vx-Vy, where x and y are phases defined in phase selector.

22	I-VA, Current phase angle

23	Ix-Iy, where x and y are phases defined in phase selector.

24	Power factor computed using apparent power, ID_CODE=2.

25	Power factor computed using phasor power, ID_CODE=3.

26	Reserved

27	Reserved

28	Reserved

Time:

29	Time of day

30	Date

31	Time of day and Date

32	Interval timer

33	Frequency

34	Counter

35	Sense input (T/F)

36..39	Reserved

40	Voltage sag

41	Voltage swells

42	Power outage

43	Voltage excursion low

44	Voltage excursion high

45	Normal voltage level

46	Voltage unbalance

47	Voltage T.H.D. excess

48	Current T.H.D. excess

49..63	Reserved

{Gas Industry units}

64	Cubic meter gas (volume un-corrected , meter index reading) per Hr.

65	Cor cubic meter gas (volume corrected to base conditions) per Hr.

66	Cor cubic meter gas(volume corrected to pressure base, without supercompressibility per Hr.

67	Cubic feet gas (volume corrected, meter index reading) per Hr.

68	Cor cubic feet gas(volume corrected to base conditions) per Hr.

69	Pcor cubic feet gas(volume corrected to pressure base, without supercompressibility per Hr.

70	Dry bulb temp degree C

71	Wet bulb temp degree C

72	Dry bulb temp degree F

73	Wet bulb temp degree F

74	Dry bulb temp degree K

75	Wet bulb temp degree K

76	Joules per Hr

77	Therm per Hr

78	Static pascal

79	Differential pascal

80	Static pound per square inch

81	Differential pound per square inch

82	Gram cm2

83	Meter HG column

84	Inch HG column

85	Inch H2O column

86	Bar

87	% relative humidity

88	Parts per million odorant

89..127	Reserved

{Water Industry units}

128	Cubic meter liquid per Hr

129	Cubic feet liquid per Hr

130	US gallons per Hr

131	IMP gallons per Hr

132	Acre feet per Hr

133	Parts per million lead

134	Turbidity

135	Parts per million chlorine

136	PH factor

137	Corrosion

138	Ionization

139	Parts per million SO_2

140	Liters

141	Cubic feet liquid

142	Pounds per sq. ft differential

143	Inches of Water

144	Feet of water

145	Atmospheres

140..189	Reserved

{Generic industry units}

190	Local currency (e.g. $)

191	Inch

192	Foot

193	Meter

194..255	Reserved

TIME_BASE			This field describes the measurement method with respect to time.

0	Bulk Quantity of Commodity (Dial Reading). Quantity of  commodity; integral of commodity usage rate.  Values have the units stated in the ID_CODE x Hour. (Energy units).

1	Instantaneous (Sampled).  This is the fastest rate at which a measurement is acquired.

2	Period based.  This is a time period based upon the period of a fundamental frequency. (Power, RMS).

3	Sub-block Average Demand. Sub-block Average Demand values are the most recent averaging demand subinterval values. (Demand).

4	Block Average Demand. Block Average Demand values may be either the average over a number of Sub-block Average Demand subintervals or the average over a single interval.  The averaging period is typically greater or equal to the Sub-block Average Demand period. (Demand).

5	Net Bulk Quantity of Commodity (Relative Dial Reading). Quantity of  commodity; integral of commodity usage rate over a specified period of time T1 to T2.  T1 and T2 are quite arbitrary and defined by mechanisms and table driven schedules. Values have the units stated in the ID_CODE x Hour, e.g. W x h = Wh (Energy)

6	Thermal quantity.  (Demand)

7	Event quantity.  (Number of occurrences of an identified item.)

MULTIPLIER			The multiplier identifies the scaling value to apply to the reported value after delivery of the tagged item; e.g. if the ID_CODE = 0 and MULTIPLIER = 2 then the UOM represents kW (other flags are assumed to have been set accordingly).

0	100

1	102

2	103

3	106

4	109

5	10-2

6	10-3

7	10-6

Q1_ACCOUNTABILITY		Indication that tagged quantity lies in Quadrant 1 of the two-dimensional cartesian co-ordinate system; eg. x ³ 0, y ³ 0.

FALSE	Tagged item is not in quadrant 1.

TRUE	Tagged item is in quadrant 1.

Q2_ACCOUNTABILITY		Indication that tagged quantity lies in Quadrant 2 of the two-dimensional cartesian co-ordinate system; eg. x ² 0, y ³ 0.

FALSE	Tagged item is not in quadrant 2.

TRUE	Tagged item is in quadrant 2.

Q3_ACCOUNTABILITY		Indication that tagged quantity lies in Quadrant 3 of the two-dimensional cartesian co-ordinate system; eg. x ² 0, y ² 0.

FALSE	Tagged item is not in quadrant 3.

TRUE	Tagged item is in quadrant 3.

Q4_ACCOUNTABILITY		Indication that tagged quantity lies in Quadrant 4 of the two-dimensional cartesian co-ordinate system; eg. x ³ 0, y ² 0.

FALSE	Tagged item is not in quadrant 4.

TRUE	Tagged item is in quadrant 4.

NET_FLOW_ACCOUNTABILITY	This bit is required to identify the manner in which the quadrants specified are being summed.

FALSE	Absolute power delivered through selected quadrants, i.e. power is added positively regardless of direction of flow.

TRUE	Net of delivered - received, where Watts are delivered in quadrants Q1 & Q4, received in quadrants Q2 & Q3; and VARs are delivered in quadrants Q1 & Q2, received in quadrants Q3 & Q4.

SEGMENTATION		When the ID_CODE field represents the electric utility industry unit of measures this bit indicates phase measurement associations.

0	Measurement is not a phase related or no phase information is applicable. e.g.  All phases on a polyphase End Device.

1	Phase A to B. i.e. A-B

2	Phase B to C. i.e. B-C

3	Phase C to A. i.e. C-A

4	Neutral to ground, or no phase information. e.g. Neutral current in a 4Y wire system.

5	Phase A to Neutral. i.e. A-N

6	Phase B to Neutral. i.e. B-N

7	Phase C to Neutral. i.e. C-N

When the ID_CODE does not represent an electric utility unit of measure then this field represents an as yet to be defined quantity, except for the value 0, which stands for all sources and flows.

HARMONIC			This identifies harmonic related quantities.

0	The identified ID_CODE is the entire signal un-filtered.

1	The identified ID_CODE is a harmonic component of an associated source.

RESERVED			Bits presently unassigned.

NFS				Bit used to indicate that this unit of measure entry does not follow the unit of measure definition in some manner

UOM_ENTRY_RCD

UOM_ENTRY			Each of the entries in this array is associated to an entry in the  SOURCES_TBL (Table 16).  This array contains one entry for each SOURCES_TBL (Table 16) entry having the UOM_ENTRY_FLAG set. The order of the parameters in this array corresponds to the order of the sources in table SOURCES_TBL (Table 16).

### 9.2.4	Table 13 demand control table

Table 13 Data Description

DEMAND_CONTROL_TBL (Table 13) contains information pertaining to the application of rates and global rate controls.

TYPE INT_CONTROL_RCD = PACKED RECORD

IF ACT_SOURCES_LIM_TBL.SLIDING_DEMAND_FLAG THEN

SUB_INT		: UINT8;

INT_MULTIPLIER	: UINT8;

ELSE

INT_LENGTH		: UINT16;

END;

END;

TYPE	DEMAND_CONTROL_RCD = PACKED RECORD

IF ACT_SOURCES_LIM_TBL.RESET_EXCLUDE_FLAG THEN

RESET_EXCLUSION		: UINT8;

END;

IF ACT_SOURCES_LIM_TBL.PF_EXCLUDE_FLAG THEN

P_FAIL_RECOGNTN_TM	: UINT8;

P_FAIL_EXCLUSION		: UINT8;

COLD_LOAD_PICKUP		: UINT8;

END;

INTERVAL_VALUE 			: ARRAY[ACT_SOURCES_LIM_TBL. 									  NBR_DEMAND_CTRL_ENTRIES] 									  OF INT_CONTROL_RCD;

END;

TABLE DEMAND_CONTROL_TBL = DEMAND_CONTROL_RCD;

Identifier			Value	Definition

INT_CONTROL_RCD

SUB_INT		0..255	The number of minutes in the subinterval.

INT_MULTIPLIER	0..255	The multiplier by which the SUB_INT is multiplied.

INT_LENGTH		0..65535	The length of the demand interval in minutes.

DEMAND_CONTROL_RCD

RESET_EXCLUSION	0..255	Number of minutes after demand reset to exclude additional reset action.

P_FAIL_RECOGNTN_TM	0..255	Number of seconds after a power failure occurs until a valid power failure is recorded and a specified action is initiated.

P_FAIL_EXCLUSION	0..255	Number of minutes after a valid power failure occurs to inhibit demand calculations.

COLD_LOAD_PICKUP	0..255	Number of minutes after a valid power failure occurs to provide cold load pickup functions.

INTERVAL_VALUE		Each of the entries in this array is associated to an entry in the  SOURCES_TBL (Table 16).  This array contains one entry for each SOURCES_TBL (Table 16) entry having the DEMAND_CTRL_FLAG set. The order of the parameters in this array corresponds to the order of the sources in table SOURCES_TBL (Table 16).

### 9.2.5	Table 14 data control table

Table 14 Data Description

DATA_CONTROL_TBL (Table 14) contains the data source information that serves as data input sources for the following tables.  This table serves as an interface between areas of the end device considered manufacturer specific and the areas of the end device to be standardized.

Each entry in the table is manufacturer defined.  Examples of entries into this table are:  entry contains address of data to be processed; or entry contains data to be processed.

TYPE DATA_RCD = PACKED RECORD

SOURCE_ID	: ARRAY[ACT_SOURCES_LIM_TBL.DATA_CTRL_LENGTH] OF UINT8;

END;

TYPE DATA_CONTROL_RCD = PACKED RECORD

SOURCES_ID	: ARRAY[ACT_SOURCES_LIM_TBL.NBR_DATA_CTRL_ENTRIES] OF 					DATA_RCD;

END;

TABLE DATA_CONTROL_TBL = DATA_CONTROL_RCD;

Identifier			Value	Definition

DATA_RCD

SOURCE_ID			Each entry in this array is defined by the manufacturer as to length and content.  The length is identical for all entries.

DATA_CONTROL_RCD

SOURCES_ID			Each of the entries in this array is associated to an entry in the  SOURCES_TBL (Table 16).  This array contains one entry for each SOURCES_TBL (Table 16) entry having the DATA_CTRL_FLAG set. The order of the parameters in this array corresponds to the order of the sources in table SOURCES_TBL (Table 16).

### 9.2.6	Table 15 constants table

Table 15 Data Description

CONSTANTS_TBL (Table 16) contains the record structures supporting constants for application to the sources.  This table has been designed for easy inclusion of new constants structures.

{gas industry constants}

TYPE GAS_PRESS_RCD = PACKED RECORD

GAS_PRESS_ZERO		: NI_FMAT2;

GAS_PRESS_FULLSCALE	: NI_FMAT2;

BASE_PRESSURE		: NI_FMAT2;

END;

TYPE GAS_TEMP_RCD = PACKED RECORD

GAS_TEMP_ZERO		: NI_FMAT2;

GAS_TEMP_FULLSCALE	: NI_FMAT2;

BASE_TEMP			: NI_FMAT2;

END;

TYPE GAS_DP_RCD = PACKED RECORD

GAS_DP_ZERO		: NI_FMAT2;

GAS_DP_FULLSCALE		: NI_FMAT2;

END;

TYPE PIPE_ORIF_DIA_RCD = PACKED RECORD

PIPE_DIA			: NI_FMAT2;

ORIF_DIA			: NI_FMAT2;

END;

TYPE GAS_AGA3_CORR_RCD = PACKED RECORD

AUX_CORR_FCTR		: NI_FMAT2;

GAS_AGA3_CORR_FCTR	: NI_FMAT2;

PIPE_ORIF_DIA		: PIPE_ORIF_DIA_RCD;

TAP_UP_DN			: UINT8;

GAS_PRESS_PARM		: GAS_PRESS_RCD;

GAS_TEMP_PARM		: GAS_TEMP_RCD;

END;

TYPE GAS_AGA7_CORR_RCD = PACKED RECORD

GAS_PRESS_PARM		: GAS_PRESS_RCD;

GAS_TEMP_PARM		: GAS_TEMP_RCD;

AUX_CORR_FCTR		: NI_FMAT2;

GAS_AGA7_CORR		: NI_FMAT2;

END;

TYPE GAS_ENERGY_RCD = PACKED RECORD

GAS_ENERGY_ZERO		: NI_FMAT2;

GAS_ENERGY_FULL		: NI_FMAT2;

END;

TYPE GAS_DP_SHUTOFF_RCD = PACKED RECORD

GAS_SHUTOFF		: NI_FMAT2;

END;

{Constant selector 0}

TYPE GAS_CONSTANTS_AGA3_RCD = PACKED RECORD

GAS_DP_PARM		: GAS_DP_RCD;

GAS_DP_SHUTOFF		: GAS_DP_SHUTOFF_RCD;

GAS_PRESS_PARM		: GAS_PRESS_RCD;

GAS_AGA3_CORR		: GAS_AGA3_CORR_RCD;

GAS_ENERGY			: GAS_ENERGY_RCD;

END;

{Constant selector 1}

TYPE GAS_CONSTANTS_AGA7_RCD = PACKED RECORD

GAS_AGA7_CORR		: GAS_AGA7_CORR_RCD;

GAS_ENERGY			: GAS_ENERGY_RCD;

END;

{Constant selector 2}

TYPE SET_CTRL_BFLD = BIT FIELD OF UINT8

SET_APPLIED_FLAG		: BOOL(0);

FILLER				: FILL(1..7);

END;

TYPE SET_APPLIED_RCD = PACKED RECORD

SET_FLAGS			: SET_CTRL_BFLD;

RATIO_F1			: NI_FMAT1;

RATIO_P1			: NI_FMAT1;

END;

TYPE ELECTRIC_CONSTANTS_RCD = PACKED RECORD

MULTIPLIER			: NI_FMAT1;

OFFSET			: NI_FMAT1;

IF ACT_SOURCES_LIM_TBL.SET1_PRESENT_FLAG THEN

SET1_CONSTANTS	: SET_APPLIED_RCD;

END;

IF ACT_SOURCES_LIM_TBL.SET2_PRESENT_FLAG THEN

SET2_CONSTANTS	: SET_APPLIED_RCD;

END;

END;

{Constants record structure selection}

TYPE	CONSTANTS_RCD = PACKED RECORD

CASE ACT_SOURCES_LIM_TBL.CONSTANTS_SELECTOR OF

0		: GAS_CONSTANTS_AGA3	:GAS_CONSTANTS_AGA3_RCD;

1		: GAS_CONSTANTS_AGA7	:GAS_CONSTANTS_AGA7_RCD;

2		: ELECTRIC_CONSTANTS	:ELECTRIC_CONSTANTS_RCD;

3..255		: RESERVED			:NIL;

END;

TYPE CONSTANT_SELECTION_RCD = PACKED RECORD

SELECTION		: ARRAY[ACT_SOURCES_LIM_TBL.NBR_CONSTANTS_ENTRIES] OF 					CONSTANTS_RCD;

END;

TABLE CONSTANTS_TBL = CONSTANT_SELECTION_RCD;

Identifier			Value	Definition

GAS_PRESS_RCD

GAS_PRESS_ZERO		Flow pressure calibration zero offset.

GAS_PRESS_FULLSCALE		Flow pressure calibration full scale.

Identifier			Value	Definition

BASE_PRESSURE		Pressure for base condition this value is absolute base pressure.

GAS_TEMP_RCD

GAS_TEMP_ZERO		Flow temperature calibration zero offset.

GAS_TEMP_FULLSCALE		Flow temperature calibration full scale.

BASE_TEMP			Temperature for base condition.

GAS_DP_RCD

GAS_DP_ZERO		Flow Differential pressure calibration zero offset. (used for AGA 3 only)

GAS_DP_FULLSCALE		Flow Differential pressure calibration full scale. (used for AGA 3 only)

PIPE_ORIF_DIA_RCD

PIPE_DIA			The pipe diameter of an orifice meter. (used for AGA 3 only)

ORIF_DIA			The orifice diameter of an orifice meter. (used for AGA 3 only)

GAS_AGA3_CORR_RCD

AUX_CORR_FCTR		Factor to provide other possible correction to the gas corrected volume.

GAS_AGA3_CORR_FCTR		Factor is used to correct the uncorrected gas volume using AGA3. (used for AGA 3 only)

PIPE_ORIF_DIA		Record structure from above.

TAP_UP_DN			Tap configuration. (used for AGA 3 only)

0	No tap or flange.

1	Up stream flange.

2	Down stream flange.

3	Upstream pipe.

4	Down stream pipe.

5..255	Reserved.

GAS_PRESS_PARM		Refer to GAS_PRESS_RCD.

GAS_TEMP_PARM		Refer to GAS_TEMP_RCD.

TYPE GAS_AGA7_CORR_RCD

GAS_PRESS_PARM		Refer to GAS_PRESS_RCD.

GAS_TEMP_PARM		Refer to GAS_TEMP_RCD.

AUX_CORR_FCTR		Factor to provide other possible correction to the gas corrected volume.

GAS_AGA7_CORR_FCTR		Factor is used to correct the uncorrected gas volume using AGA3. (used for AGA 7 only)

Identifier			Value	Definition

GAS_ENERGY_RCD

GAS_ENERGY_ZERO		Energy calibration zero offset.

GAS_ENERGY_FULL		Energy calibrations full scale.

TYPE GAS_DP_SHUTOFF_RCD

GAS_DP_SHUTOFF		This parameter is used to disable the AGA3 flow calculations when differential pressure is below the value indicated by this parameter. (used for AGA 3 only)

{Constants selector 0}GAS_CONSTANTS_AGA3_RCD

GAS_DP_PARM			Refer to GAS_DP_RCD.

GAS_DP_SHUTOFF		Refer to GAS_DP_SHUTOFF_RCD.

GAS_PRESS_PARM		Refer to GAS_PRESS_RCD.

GAS_AGA3_CORR_FCTR		Refer to GAS_AGA3_CORR_RCD.

GAS_ENERGY			Refer to GAS_ENERGY_RCD.

{Constants selector 1}

GAS_CONSTANTS_AGA7_RCD

GAS_AGA7_CORR_FCTR		Refer to GAS_AGA7_CORR_RCD.

GAS_ENERGY			Refer to GAS_ENERGY_RCD.

{Constants selector 2}

SET_CTRL_BFLD

SET_APPLIED_FLAG	FALSE	The RATIO_F1 and RATIO P1 represented by this flag have not been applied to the associated source.

TRUE	The RATIO_P1 and RATIO F1 represented by this flag have been applied to the associated source.

SET_APPLIED_RCD

SET_FLAGS			See SET_CTRL_BFLD above.

RATIO_F1			Ratio of intermediary device to allow interface of commodity flow to utility meters. For example, electric utilities use a current transformer to reduce the current at the meter. Transforming 2000 amps to 5 amps is a ratio of 400.

RATIO_P1			Ratio of intermediary device to allow interface of commodity pressure to utility meters. For example, electric utilities use a voltage transformer to reduce the voltage at the meter. Transforming 7200 volts to 120 volts is a ratio of 60.

ELECTRIC_CONSTANTS_RCD

MULTIPLIER			Storage for a value used in multiplication/division adjustment.

OFFSET			Storage for a value used in addition/subtraction adjustment.

Identifier			Value	Definition

SET1_CONSTANTS		Storage variable for the first set of constants and associated flags.

SET2_CONSTANTS		Storage variable for the second set of constants and associated flags.

CONSTANTS_RCD			Structure that selects the constant record structure to use.

CONSTANT_SELECTION_RCD		Each of the entries in this array is associated to an entry in the  SOURCES_TBL (Table 16).  This array contains one entry for each SOURCES_TBL (Table 16) entry having the CONSTANTS_FLAG set. The order of the parameters in this array corresponds to the order of the sources in table SOURCES_TBL (Table 16).

### 9.2.7	Table 16 source definition table

Table 16 Data Description

SOURCES_TBL (Table 16) contains the information regarding the sources selected by the other tables.

TYPE SOURCE_LINK_BFLD = BIT FIELD OF UINT8

UOM_ENTRY_FLAG		: BOOL(0);

DEMAND_CTRL_FLAG	: BOOL(1);

DATA_CTRL_FLAG		: BOOL(2);

CONSTANTS_FLAG		: BOOL(3);

PULSE_ENGR_FLAG		: BOOL(4);

CONSTANT_TO_BE_APPLIED	: BOOL(5);

FILLER				: FILL(6..7);

END;

TYPE	SOURCE_LINK_RCD = PACKED RECORD

SOURCES_LINK	: ARRAY[ACT_SOURCES_LIM_TBL.NBR_SOURCES] OF 							SOURCE_LINK_BFLD;

END;

TABLE SOURCES_TBL = SOURCE_LINK_RCD;

Identifier			Value	Definition

SOURCE_LINK_BFLD

UOM_ENTRY_FLAG	FALSE	A UOM_ENTRY_TBL (Table 12) entry does not exist for this source.

TRUE	A UOM_ENTRY_TBL (Table 12) entry is associated with this source. It is recommended that the UOM entries reflect the source as it is referenced or transported by other tables.

Identifier			Value	Definition

DEMAND_CTRL_FLAG	FALSE	A DEMAND_CONTROL_TBL (Table 13) entry does not exist for this source.

TRUE	A DEMAND_CONTROL_TBL (Table 13) entry is associated with this source.

DATA_CTRL_FLAG	FALSE	A DATA_CONTROL_TBL (Table 14) entry does not exist for this source.

TRUE	A DATA_CONTROL_TBL (Table 14) entry is associated with this source.

CONSTANTS_FLAG	FALSE	A CONSTANTS_TBL (Table 15) entry does not exist for this source.

TRUE	A CONSTANTS_TBL (Table 15) entry is associated with this source.

PULSE_ENGR_FLAG	FALSE	The source is in pulse units.

TRUE	The source is in engineering units.

CONSTANT_TO_BE_APPLIED	FALSE	The entry in the CONSTANTS_TBL (Table 15) if present, has been applied to the source. Examine CONSTANTS_TBL (Table 15) SET_APPLIED_FLAG to determine if constants have been applied.

TRUE	The entry in the CONSTANTS_TBL (Table 15) if present, has not been applied to the source. Examine CONSTANTS_TBL (Table 15) SET_APPLIED_FLAG to determine if constants have been applied.

## 9.3	Decade 20: register tables

This decade contains tables associated with registers for measured values.  These registers can be accumulating (energy), demand, TOU, instantaneous or other(s) as appropriate.

### 9.3.1	Table 20 dimension register table

Table 20 Data Description

DIM_REGS_TBL (Table 20) specifies the maximum dimensional values for measured values registers. The constants defined are used for setting the absolute maximum limits of arrays used in the transport of these values.

TYPE REG_FUNC1_BFLD = BIT FIELD OF UINT8

SEASON_INFO_FIELD_FLAG		: BOOL(0);

DATE_TIME_FIELD_FLAG		: BOOL(1);

DEMAND_RESET_CTR_FLAG		: BOOL(2);

DEMAND_RESET_LOCK_FLAG	: BOOL(3);

CUM_DEMAND_FLAG			: BOOL(4);

CONT_CUM_DEMAND_FLAG		: BOOL(5);

TIME_REMAINING_FLAG		: BOOL(6);

FILLER					: FILL(7..7);

END;

TYPE REG_FUNC2_BFLD = BIT FIELD OF UINT8

SELF_READ_INHIBIT_OVERFLOW_FLAG	: BOOL(0);

SELF_READ_SEQ_NBR_FLAG		: BOOL(1);

DAILY_SELF_READ_FLAG			: BOOL(2);

WEEKLY_SELF_READ_FLAG			: BOOL(3);

SELF_READ_DEMAND_RESET		: UINT(4..5);

FILLER						: FILL(6..7);

END;

TYPE REGS_RCD = PACKED RECORD

REG_FUNC1_FLAGS		: REG_FUNC1_BFLD;

REG_FUNC2_FLAGS		: REG_FUNC2_BFLD;

NBR_SELF_READS		: UINT8;

NBR_SUMMATIONS		: UINT8;

NBR_DEMANDS		: UINT8;

NBR_COIN_VALUES		: UINT8;

NBR_OCCUR			: UINT8;

NBR_TIERS			: UINT8;

NBR_PRESENT_DEMANDS	: UINT8;

NBR_PRESENT_VALUES	: UINT8;

END;

TABLE DIM_REGS_TBL = REGS_RCD;

Identifier			Value	Definition

REG_FUNC1_BFLD

SEASON_INFO_FIELD_FLAG	FALSE	End device is not capable of reporting the representative season in tables in this decade.

TRUE	End device is capable of reporting the representative season in tables in this decade

DATE_TIME_FIELD_FLAG	FALSE	End device is not capable of providing the date and time in tables in this decade.

TRUE	End device is capable of providing the date and time in tables in this decade.

DEMAND_RESET_CTR_FLAG	FALSE	End device is not capable of counting the number of activations of demand resets.

TRUE	End device is capable of counting the number of activations of demand resets.

DEMAND_RESET_LOCK_FLAG	FALSE	Demand reset lockout is not supported by the end device.

TRUE	Demand reset lockout is supported by the end device.

CUM_DEMAND_FLAG	FALSE	Cumulative demand is not supported by the end device.

TRUE	Cumulative demand is supported by the end device.

CONT_CUM_DEMAND_FLAG	FALSE	Continuous cumulative demand is not supported by the end device.

Identifier			Value	Definition

TRUE	Continuous cumulative demand is supported by the end device.

TIME_REMAINING_FLAG	FALSE	End device does not have the ability to report time remaining in demand interval.

TRUE	End device does have the ability to report time remaining in demand interval.

REG_FUNC2_BFLD

SELF_READ_INHIBIT_OVERFLOW_FLAG

FALSE	End device is not capable of inhibiting self reads once an overflow occurs.

TRUE	End device is capable of inhibiting self reads once an overflow occurs.

SELF_READ_SEQ_NBR_FLAG	FALSE	End device is not capable of providing a self read sequential number for each entry.

TRUE	End device is capable of providing a self read sequential number.

DAILY_SELF_READ_FLAG		Indicates whether daily self reads are supported.  These readings are taken at 00:00:00.

FALSE	Daily reading is not supported.

TRUE	Daily reading is supported.

WEEKLY_SELF_READ_FLAG		Indicates whether weekly self reads are supported.  These readings are taken at 00:00:00 on Sunday.

FALSE	Weekly reading is not supported.

TRUE	Weekly reading is supported.

SELF_READ_DEMAND_RESET	Specifies whether the device is capable of performing a self read whenever a demand reset (any method) is performed and whether the device is capable of performing a demand reset whenever a self read (any method) is performed.

0	End device is not capable of performing either a Self Read on every Demand Reset or a Demand Reset on every Self Read

1 	End device is capable of performing only a self read on every Demand Reset

2	End device is capable of performing only a Demand Reset on every Self Read

3	End device is capable of performing a Self Read on every Demand Reset and a Demand Reset on every Self Read

REGS_RCD

REG_FUNC1_FLAGS		See definition of REG_FUNC1_BFLD above.

REG_FUNC2_FLAGS		See definition of REG_FUNC2_BFLD above.

NBR_SELF_READS	0..255	Maximum number of Self Reads supported by end device.

Identifier			Value	Definition

NBR_SUMMATIONS	0..255	Maximum number of summation registers in each data block.

NBR_DEMANDS		0..255	Maximum number of demand registers in each data block.

NBR_COIN_VALUES	0..255	Maximum number of coincident values saved concurrently in each data block.

NBR_OCCUR		0..255	Maximum number of occurrences stored for a particular selection.

NBR_TIERS		0..255	Maximum number of tiers that data can be stored in.

NBR_PRESENT_DEMANDS	0..255	Maximum number of present demand values that can be stored.

NBR_PRESENT_VALUES	0..255	Maximum number of present values that can be stored.

### 9.3.2	Table 21 actual register table

Table 21 Data Description

ACT_REGS_TBL (Table 21) contains actual function values for registers.

TABLE ACT_REGS_TBL = DIM_REGS_TBL.REGS_RCD;

Identifier			Value	Definition

REG_FUNC1_FLAGS

SEASON_INFO_FIELD_FLAG	FALSE	End device is not reporting the representative season in tables in this decade.

TRUE	End device is reporting the representative season in tables in this decade

DATE_TIME_FIELD_FLAG	FALSE	End device is not providing the date and time in tables in this decade.

TRUE	End device is providing the date and time in tables in this decade.

DEMAND_RESET_CTR_FLAG	FALSE	End device is not counting the number of activations of demand resets.

TRUE	End device is counting the number of activations of demand resets.

DEMAND_RESET_LOCK_FLAG

FALSE	Demand reset lockout is not enabled.

TRUE	Demand reset lockout is enabled.

CUM_DEMAND_FLAG	FALSE	Cumulative demand is not in use by the end device.

TRUE	Cumulative demand is in use by the end device.

Identifier			Value	Definition

CONT_CUM_DEMAND_FLAG	FALSE	Continuous cumulative demand is not in use by the end device.

TRUE	Continuous cumulative demand is in use by the end device.

TIME_REMAINING_FLAG	FALSE	End device does not report time remaining in demand interval.

TRUE	End device does report time remaining in demand interval.

REG_FUNC2_BFLD

SELF_READ_INHIBIT_OVERFLOW_FLAG

FALSE	End device is not inhibiting self reads once an overflow occurs.

TRUE	End device is inhibiting self reads once an overflow occurs.

SELF_READ_SEQ_NBR_FLAG	FALSE	End device is not providing a self read sequential number for each entry.

TRUE	End device is providing a self read sequential number.

DAILY_SELF_READ_FLAG		Indicates whether daily self reads are in use.  These readings are taken at 00:00:00.

FALSE	Daily reading is not in use.

TRUE	Daily reading is in use.

WEEKLY_SELF_READ_FLAG		Indicates whether weekly self reads are in use.  These readings are taken at 00:00:00 on Sunday.

FALSE	Weekly reading is not in use.

TRUE	Weekly reading is in use.

SELF_READ_DEMAND_RESET	Specifies whether the device will perform a self read whenever a demand reset (any method) is performed and whether the device will perform a demand reset whenever a self read (any method) is performed.

0	End device shall not perform either a Self Read on every Demand Reset or a Demand Reset on every Self Read

1 	End device shall perform a Self read on every Demand Reset

2	End device shall perform Demand Reset on every Self Read

3	End device shall perform a Self Read on every Demand Reset and a Demand Reset on every Self Read

REGS_RCD

REG_FUNC1_FLAGS		See definition of REG_FUNC1_BFLD above.

REG_FUNC2_FLAGS		See definition of REG_FUNC2_BFLD above.

Identifier			Value	Definition

NBR_SELF_READS		Number of Self Reads in use.

NBR_SUMMATIONS	0..255	Number of summation registers in each data block.

NBR_DEMANDS		0..255	Number of demand registers in each data block.

NBR_COIN_VALUES	0..255	Number of coincident values saved in each data block.

NBR_OCCUR		0..255	Number of occurrences stored for a particular selection.

NBR_TIERS		0..255	Number of tiers in use.

NBR_PRESENT_DEMANDS	0..255	Number of present demand values that are stored.

NBR_PRESENT_VALUES	0..255	Number of present values that are stored.

### 9.3.3	Table 22 data selection table

Table 22 Data Description

DATA_SELECTION_TBL (Table 22) contains grouped lists of source indices.  These indices point towards array elements in SOURCES_TBL (Table 16) when this table is present.  These lists are used to build the table that contains the data to be captured.  The groupings are described below.

TYPE DATA_SELECTION_RCD = PACKED RECORD

SUMMATION_SELECT		: ARRAY[ACT_REGS_TBL.NBR_SUMMATIONS] OF UINT8;

DEMAND_SELECT		: ARRAY[ACT_REGS_TBL.NBR_DEMANDS] OF UINT8;

MIN_OR_MAX_FLAGS		: SET((ACT_REGS_TBL.NBR_DEMANDS+7)/8);

COINCIDENT_SELECT		: ARRAY[ACT_REGS_TBL.NBR_COIN_VALUES]OF UINT8;

COIN_DEMAND_ASSOC	: ARRAY[ACT_REGS_TBL.NBR_COIN_VALUES] OF UINT8;

END;

TABLE DATA_SELECTION_TBL = DATA_SELECTION_RCD;

Identifier			Value	Definition

DATA_SELECTION_RCD

SUMMATION_SELECT		A list of source indices that groups together bulk/energy/summation sources.

DEMAND_SELECT		A list of source indices that groups together demand sources.

MIN_OR_MAX_FLAGS		A set of bit flags, each corresponding to an entry in DEMAND_SELECT.

FALSE	Indicates that the associated DEMAND_SELECT entry is a minimum.

Identifier			Value	Definition

TRUE	Indicates that the associated DEMAND_SELECT entry is a maximum.

COINCIDENT_SELECT		A list of source indices that groups together demand sources with time period processing equal to that of the DEMAND_SELECT sources.

COIN_DEMAND_ASSOC		Each entry corresponds to an entry in COINCIDENT_SELECT and provides an index into DEMAND_SELECT identifying the demand for which this coincident value is taken.

### 9.3.4	Table 23 current register data table

Table 23 Data Description

CURRENT_REG_DATA_TBL (Table 23) contains the current register data.

TYPE COINCIDENTS_RCD = PACKED RECORD

COINCIDENT_VALUES	: ARRAY[ACT_REGS_TBL.NBR_OCCUR] OF NI_FMAT2;

END;

TYPE DEMANDS_RCD = PACKED RECORD

IF ACT_REGS_TBL.DATE_TIME_FIELD_FLAG THEN

EVENT_TIME		: ARRAY[ACT_REGS_TBL.NBR_OCCUR] OF STIME_DATE;

END;

IF ACT_REGS_TBL.CUM_DEMAND_FLAG THEN

CUM_DEMAND	: NI_FMAT1;

END;

IF ACT_REGS_TBL.CONT_CUM_DEMAND_FLAG THEN

CONT_CUM_DEMAND	: NI_FMAT1;

END;

DEMAND			: ARRAY[ACT_REGS_TBL.NBR_OCCUR] OF NI_FMAT2;

END;

TYPE DATA_BLK_RCD = PACKED RECORD

SUMMATIONS	: ARRAY[ACT_REGS_TBL.NBR_SUMMATIONS] OF NI_FMAT1;

DEMANDS	: ARRAY[ACT_REGS_TBL.NBR_DEMANDS] OF DEMANDS_RCD;

COINCIDENTS	: ARRAY[ACT_REGS_TBL.NBR_COIN_VALUES] OF COINCIDENTS_RCD;

END;

TYPE REGISTER_DATA_RCD = PACKED RECORD

IF ACT_REGS_TBL.DEMAND_RESET_CTR_FLAG THEN

NBR_DEMAND_RESETS	: UINT8;

END;

TOT_DATA_BLOCK		: DATA_BLK_RCD;

TIER_DATA_BLOCK		: ARRAY[ACT_REGS_TBL.NBR_TIERS] OF DATA_BLK_RCD;

END;

TABLE CURRENT_REG_DATA_TBL = REGISTER_DATA_RCD;

Identifier			Value	Definition

COINCIDENTS_RCD

COINCIDENT_VALUES		Coincident values selected by DATA_SELECTION_TBL.COINCIDENT_SELECT (Table 22).

DEMANDS_RCD

EVENT_TIME			Array that contains the date and time of each minimum or maximum recorded.  Entry in position 0 corresponds to the entry in position 0 of the DEMAND array.  The presence of this field is dependent on  capability flag in the ACT_REG_TBL.DATE_TIME_FIELD_FLAG (Table 21).

CUM_DEMAND		The value of the cumulative demand register.

CONT_CUM_DEMAND		The value of the continuous cumulative demand register.

DEMAND			Array that contains the minimums or maximums values.  The value in position zero is the smallest minimum or largest maximum.  In position 1 is the second smallest minimum or the second largest maximum and so on until the end of the array is reached.

DATA_BLK_RCD

SUMMATIONS			Array that contains the values of the selected summation measurements.

DEMANDS			Array that contains the values of the selected min/max demand measurements.

COINCIDENTS			Array that contains the values of the selected measurement coincident to the selected minimum/maximum demands.

REGISTER_DATA_RCD

NBR_DEMAND_RESETS		Indicates the number of demand resets executed by the end device.

TOT_DATA_BLOCK		Data block independent of Time of Use structures or other means of selection.

TIER_DATA_BLOCK		Data block dependent on Time of Use structures or other means of selection.

### 9.3.5	Table 24 previous season data table

Table 24 Data Description

PREVIOUS_SEASON_DATA_TBL (Table 24) contains a snapshot of the current register data taken at the last season change.

TYPE REGISTER_INFO_RCD = PACKED RECORD

IF ACT_REGS_TBL.DATE_TIME_FIELD_FLAG THEN

END_DATE_TIME	: STIME_DATE;

END;

IF ACT_REGS_TBL.SEASON_INFO_FIELD_FLAG THEN

SEASON		: UINT8;

END;

END;

TYPE PREVIOUS_SEASON_DATA_RCD = PACKED RECORD

REGISTER_INFO		: REGISTER_INFO_RCD;

PREV_SEASON_REG_DATA	: CURRENT_REG_DATA_TBL.REGISTER_DATA_RCD;

END;

TABLE PREVIOUS_SEASON_DATA_TBL = PREVIOUS_SEASON_DATA_RCD;

Identifier			Value	Definition

REGISTER_INFO_RCD

END_DATE_TIME		The end device time when the snapshot of the current register data occurred.

SEASON			Current season value when the snapshot of the current register data occurred.

PREVIOUS_SEASON_DATA_RCD

REGISTER_INFO		See definitions above.

PREV_SEASON_REG_DATA		Contains a snapshot of the CURRENT_DATA_REG_TBL (Table 23).  stored at the time of the last season change.  See definition in CURRENT_DATA_REG_TBL (Table 23).

### 9.3.6	Table 25 previous demand reset data table

Table 25 Data Description

PREVIOUS_DEMAND_RESET_DATA_TBL (Table 25) contains a snapshot of the current register data taken at the time of the last demand reset.

TYPE PREV_DEMAND_RESET_DATA_RCD = PACKED RECORD

REGISTER_INFO		    : PREVIOUS_SEASON_DATA_TBL.REGISTER_INFO_RCD;

PREV_DEMAND_RESET_DATA   : CURRENT_REG_DATA_TBL.REGISTER_DATA_RCD;

END;

TABLE PREVIOUS_DEMAND_RESET_DATA_TBL = PREV_DEMAND_RESET_DATA_RCD;

Identifier			Value	Definition

PREV_DEMAND_RESET_DATA_RCD

REGISTER_INFO		Contains snapshot of register information included with previous demand reset register data.

PREV_DEMAND_RESET_DATA	Contains a snapshot of the CURRENT_DATA_REG_TBL (Table 23) stored at the time of the last demand reset.

### 9.3.7	Table 26 self read data table

Table 26 Data Description

SELF_READ_DATA_TBL (Table 26) contains self read data.  Snapshots of current register data shall be taken from time to time by some sort of self read function.

TYPE SELF_READ_DATA_RCD = PACKED RECORD

IF ACT_REGS_TBL.SELF_READ_SEQ_NBR_FLAG THEN

SELF_READ_SEQ_NBR	: UINT16;

END;

REGISTER_INFO		   : PREVIOUS_SEASON_DATA_TBL.REGISTER_INFO_RCD;

SELF_READ_REGISTER_DATA  : CURRENT_REG_DATA_TBL.REGISTER_DATA_RCD;

END;

TYPE LIST_STATUS_BFLD = BIT FIELD OF UINT8

ORDER_FLAG			: BOOL(0);

OVERFLOW_FLAG		: BOOL(1);

LIST_TYPE_FLAG		: BOOL(2);

INHIBIT_OVERFLOW_FLAG	: BOOL(3);

FILLER				: FILL(4..7);

END;

TYPE SELF_READ_LIST_RCD = PACKED RECORD

LIST_STATUS			: LIST_STATUS_BFLD;

NBR_VALID_ENTRIES		: UINT8;

LAST_ENTRY_ELEMENT	: UINT8;

LAST_ENTRY_SEQ_NBR	: UINT16;

NBR_UNREAD_ENTRIES	: UINT8;

SELF_READS_ENTRIES	: ARRAY[ACT_REGS_TBL.NBR_SELF_READS] OF

SELF_READ_DATA_RCD;

END;

TABLE SELF_READ_DATA_TBL = SELF_READ_LIST_RCD;

Identifier			Value	Definition

SELF_READ_DATA_RCD

SELF_READ_SEQ_NBR		Sequence number assigned to the self read measurement.  This number is initialized to 0 when the end device is configured.  This number is incremented with each self read occurrence.

REGISTER_INFO		Contains a snapshot of register data taken at the time of the self read.

SELF_READ_REGISTER_DATA	A snapshot of current register data taken when requested by any means offered by the end device.

LIST_STATUS_BFLD

ORDER_FLAG		FALSE	Self reads are transported in ascending order (N is older than N+1).

TRUE	Self reads are transported in descending order (N is newer than N+1).

OVERFLOW_FLAG	FALSE	Overflow has not occurred.

TRUE	An attempt was made to enter a self read such that the number of unread self reads would have exceeded the actual number of possible entries in the log.

LIST_TYPE_FLAG	FALSE	FIFO (First In First Out) as placed in self read list.

TRUE	Circular list as placed in self read list.

INHIBIT_OVERFLOW_FLAG		The same value as ACT_REG_TBL.SELF_READ_INHIBIT_OVERFLOW (Table 21).

SELF_READ_LIST_RCD

LIST_STATUS			See LIST_STATUS_BFLD above.

NBR_VALID_ENTRIES	0..255	Number of valid self reads stored in the self reads array.  The range is zero (meaning no self reads in the array) to the actual dimension of the number of self reads.

LAST_ENTRY_ELEMENT	0..65535	The array element number of the newest valid entry in the self read array.  This field is valid only if NBR_VALID_ENTRIES is greater than zero.

LAST_ENTRY_SEQ_NBR	0..65535	The sequence number of the last element in the self read array.

NBR_UNREAD_ENTRIES	0..255	The number of self read entries that have not been read.  This number is only updated by a procedure.

Identifier			Value	Definition

SELF_READS_ENTRIES		An array of snapshots of register data taken at a prescribed instance in time.

### 9.3.8	Table 27 present register selection table

Table 27 Data Description

PRESENT_REGISTER_SELECT_TBL (Table 27) provides selections to sources of present demands and present values.  These indices point towards array elements in SOURCES_TBL (Table 16) when Table 16 is present.  The values selected are available in PRESENT_REGISTER_DATA_TBL (Table 28).

TYPE PRESENT_REGISTER_SELECT_RCD = PACKED RECORD

PRESENT_DEMAND_SELECT	: ARRAY[ACT_REGS_TBL.NBR_PRESENT_DEMANDS] OF 							UINT8;

PRESENT_VALUE_SELECT	: ARRAY[ACT_REGS_TBL.NBR_PRESENT_VALUES] OF 							UINT8;

END;

TABLE PRESENT_REGISTER_SELECT_TBL = PRESENT_REGISTER_SELECT_RCD;

Identifier			Value	Definition

PRESENT_REGISTER_SELECT_RCD

PRESENT_DEMAND_SELECT		Array that contains data source selectors used to measure present demand.  The present demand values shall be reported at the same index position in PRESENT_REGISTER_DATA_TBL. PRESENT_DEMAND (Table 28).

PRESENT_VALUE_SELECT		Array that contains data source selectors used to measure present value.  The present values shall be reported at the same index position in PRESENT_REGISTER_DATA_TBL.PRESENT_VALUES (Table 28).

### 9.3.9	Table 28: present register data table

Table 28 Data Description

PRESENT_REGISTER_DATA_TBL (Table 28) contains the present demand and values as selected by the PRESENT_REGISTER_SELECT_TBL (Table 27).  These indices point towards array elements in SOURCES_TBL (Table 16) when Table 16 is present.

TYPE PRESENT_DEMAND_RCD	= PACKED RECORD

IF ACT_REGS_TBL.TIME_REMAINING_FLAG THEN

TIME_REMAINING	: TIME;

END;

DEMAND_VALUE		: NI_FMAT2;

END;

TYPE PRESENT_REGISTER_DATA_RCD = PACKED RECORD

PRESENT_DEMAND	: ARRAY[ACT_REGS_TBL.NBR_PRESENT_DEMANDS] OF 							PRESENT_DEMAND_RCD;

PRESENT_VALUE	: ARRAY[ACT_REGS_TBL.NBR_PRESENT_VALUES] OF NI_FMAT1;

END;

TABLE PRESENT_REGISTER_DATA_TBL = PRESENT_REGISTER_DATA_RCD;

Identifier			Value	Definition

PRESENT_DEMAND_RCD

TIME_REMAINING		Time remaining to the end of the present demand interval

DEMAND_VALUE		The present demand value.

PRESENT_REGISTER_DATA_RCD

PRESENT_DEMAND		Array that contains present demand selected by PRESENT_REGISTER_SELECT_TBL.PRESENT_DEMAND_SELECT (Table 27).

PRESENT_VALUE		Array that contains present demand selected by PRESENT_REGISTER_SELECT_TBL.PRESENT_DEMAND_SELECT (Table 27).

## 9.4	Decade 30: local display tables

This decade contains tables associated with the transport of information required to establish a local display.

### 9.4.1	Table 30 dimension display table

Table 30 Data Description

DIM_DISP_TBL (Table 30) specifies the maximum dimensional values for local display operation in an end device. The constants defined are used for setting the absolute maximum limits of display array sizes.

TYPE DISP_FLAG_BFLD = BIT FIELD OF UINT8

ON_TIME_FLAG	: BOOL(0);

OFF_TIME_FLAG	: BOOL(1);

HOLD_TIME_FLAG	: BOOL(2);

FILLER			: FILL(3..7);

END;

TYPE DISP_RCD = PACKED RECORD

DISPLAY_CTRL			: DISP_FLAG_BFLD;

NBR_DISP_SOURCES			: UINT16;

WIDTH_DISP_SOURCES		: UINT8;

NBR_PRI_DISP_LIST_ITEMS		: UINT16;

NBR_PRI_DISP_LISTS			: UINT8;

NBR_SEC_DISP_LIST_ITEMS		: UINT16;

NBR_SEC_DISP_LISTS		: UINT8;

END;

TABLE DIM_DISP_TBL = DISP_RCD;

Identifier			Value	Definition

DISP_FLAG_BFLD

ON_TIME_FLAG	FALSE	Programmable on time is not supported by the end device.

TRUE	Programmable on time is supported by the end device.

OFF_TIME_FLAG	FALSE	Programmable off time is not supported by the end device.

TRUE	Programmable off time is supported by the end device.

HOLD_TIME_FLAG	FALSE	Programmable hold time is not supported by the end device.

TRUE	Programmable hold time is supported by the end device.

DISP_RCD

DISPLAY_CTRL		See DISP_FLAG_BFLD above.

NBR_DISP_SOURCES	0..65535	Maximum number of display sources. A number representing the maximum number of manufacturer defined display sources, described in DISP_SOURCE_TBL (Table 32), and which may be used for the creation of display lists.

WIDTH_DISP_SOURCES	0..255	Maximum number of octets a manufacturer may use to define the row width of all entries in DISP_SOURCE_TBL (Table 32).

NBR_PRI_DISP_LIST_ITEMS

0..65535	Maximum number of primary display items per display list defined in PRI_DISP_LIST_TBL (Table 33). The maximum number of items in all primary display lists shall not exceed this value.

NBR_PRI_DISP_LISTS	0..255	Maximum number of primary display lists defined in PRI_DISP_LIST_TBL (Table 33).

NBR_SEC_DISP_LIST_ITEMS

0..65535	Maximum number of secondary display items per display list defined in SEC_DISP_LIST_TBL (Table 34). The maximum number of items in all secondary display lists shall not exceed this value.

NBR_SEC_DISP_LISTS	0..255	Maximum number of secondary display lists defined in SEC_DISP_LIST_TBL (Table 34).

### 9.4.2	Table 31 actual display table

Table 31 Data Description

ACT_DISP_TBL (Table 31) specifies the actual dimensional values for local display operation in an end device. The dimensions defined are used for setting the actual limits of display array sizes.

TABLE ACT_DISP_TBL = DIM_DISP_TBL.DISP_RCD;

Identifier			Value	Definition

DISP_FLAG_BFLD

ON_TIME_FLAG	FALSE	On time is not programmable in the end device.

TRUE	On time is programmable in the end device.

OFF_TIME_FLAG	FALSE	Off time is not programmable in the end device.

TRUE	Off time is programmable in the end device.

HOLD_TIME_FLAG	FALSE	Hold time is not programmable in the end device.

TRUE	Hold time is programmable in the end device.

DISP_RCD

DISPLAY_CTRL		See DISP_FLAG_BFLD above.

NBR_DISP_SOURCES	0..65535	Actual number of display sources. A number representing the actual number of manufacturer defined display sources, described in DISP_SOURCE_TBL (Table 32), and which should be used for the creation of display lists.

WIDTH_DISP_SOURCES	0..255	Actual number of octets a manufacturer uses to define the row width of all entries in DISP_SOURCE_TBL (Table 32).

NBR_PRI_DISP_LIST_ITEMS

0..65535	Actual number of primary display items per display list defined in PRI_DISP_LIST_TBL (Table 33). The total number of items in all primary display lists shall not exceed this value.

NBR_PRI_DISP_LISTS	0..255	Actual number of primary display lists defined in PRI_DISP_LIST_TBL (Table 33).

NBR_SEC_DISP_LIST_ITEMS

0..65535	Actual number of secondary display items per display list defined in SEC_DISP_LIST_TBL (Table 34). The total number of items in all secondary display lists shall not exceed this value.

NBR_SEC_DISP_LISTS	0..255	Actual number of secondary display lists defined in SEC_DISP_LIST_TBL (Table 34).

### 9.4.3	Table 32 display source table

Table 32 Data Description

DISP_SOURCE_TBL (Table 32) defines the dimensions and size of manufacturer defined display identifications and format characteristics. Although manufacturer specific, this table’s designation and dimensions (ACT_DISP_TBL.WIDTH_DISP_SOURCES by ACT_DISP_TBL.NBR_DISP_SOURCES) (Table 31), permit the protocol to deposit local display description information. The actual interpretation of each display entry is not defined by this standard. The entry offsets to individual items in this table are used in display scroll sequences entered in tables PRI_DISP_LIST_TBL (Table 33) and SEC_DISP_LIST_TBL (Table 34).

TYPE DISP_SOURCE_DESC_RCD = PACKED RECORD

DISPLAY_SOURCE	: ARRAY[ACT_DISP_TBL.WIDTH_DISP_SOURCES] OF UINT8;

END;

TYPE DISPLAY_SOURCE_RCD = PACKED RECORD

DISPLAY_SOURCES  : ARRAY[ACT_DISP_TBL.NBR_DISP_SOURCES] OF 								DISP_SOURCE_DESC_RCD;

END;

TABLE DISP_SOURCE_TBL = DISPLAY_SOURCE_RCD;

Identifier			Value	Definition

DISP_SOURCE_DESC_RCD		Manufacturer defined display description entry.

DISPLAY_SOURCE	0..255	These entries make up the DISP_SOURCE_TBL (Table 32). Indices to these entries (starting with 0) are used in subsequent display scrolling sequences.

DISPLAY_SOURCE_RCD		Manufacturer defined display description entries.

DISPLAY_SOURCES		This array contains the manufacturer defined display description entries.

### 9.4.4	Table 33 primary display list table

Table 33 Data Description

PRI_DISP_LIST_TBL (Table 33) contains a list of operational parameters and references into the table, DISP_SOURCE_TBL, (Table 32) necessary for programming the primary display lists, timing, and scroll sequences.

TYPE DISP_SCROLL1_BFLD = BIT FIELD OF UINT8

ON_TIME		: UINT(0..3);

OFF_TIME		: UINT(4..7);

END;

TYPE DISP_SCROLL2_BFLD = BIT FIELD OF UINT8

HOLD_TIME		: UINT(0..3);

DEFAULT_LIST	: UINT(4..7);

END;

TYPE DISP_LIST_DESC_RCD = PACKED RECORD

DISP_SCROLL1 	: DISP_SCROLL1_BFLD;

DISP_SCROLL2 	: DISP_SCROLL2_BFLD;

NBR_LIST_ITEMS	: UINT8;

END;

TYPE PRI_DISP_LIST_RCD = PACKED RECORD

PRI_DISP_LIST	: ARRAY[ACT_DISP_TBL.NBR_PRI_DISP_LISTS] OF 								DISP_LIST_DESC_RCD;

PRI_DISP_SOURCES	: ARRAY[ACT_DISP_TBL.NBR_PRI_DISP_LIST_ITEMS] OF 							UINT16;

END;

TABLE PRI_DISP_LIST_TBL = PRI_DISP_LIST_RCD;

Identifier			Value	Definition

DISP_SCROLL1_BFLD

ON_TIME		0..15	The number of seconds each display item is displayed.

OFF_TIME		0..15	The number of seconds display is blank between display items. 0 = No deliberate OFF Time.

DISP_SCROLL2_BFLD

HOLD_TIME		0..15	The number of minutes to wait before automatically restarting the normal display scroll after hold has been initiated.

DEFAULT_LIST		Associates this display list with a standard display list type. The "normal" display list scrolling resumes after HOLD_TIME has expired. The following values are recognized:

0	Display selectable via communication link only,

1	Normal display

2	Alternate Display

3	Test Display

4..15	Unassigned.

DISP_LIST_DESC_RCD

DISP_SCROLL1		This contains the ON_TIME and OFF_TIME values for the associated list.

DISP_SCROLL2		This contains the HOLD_TIME and DEFAULT_LIST values for the associated list.

NBR_LIST_ITEMS	0..255	Number of items in this display list. The total number of items (list entries) in all display lists of this table shall not exceed ACT_DISP_TBL.NBR_PRI_DISP_LIST_ITEM (Table 31).

PRI_DISP_LIST_RCD

PRI_DISP_LIST		An array of list descriptor records.

PRI_DISP_SOURCES		Ordered list of references to display items contained in DISP_SOURCE_TBL (Table 32). This list establishes the order of the primary display.

This standard does not preclude additional items from popping up or being displayed out of sequence as a result of an end device error condition or an end device status report being generated.

### 9.4.5	Table 34 secondary display list table

Table 34 Data Description

SEC_DISP_LIST_TBL (Table 34) contains a list of operational parameters and references into the table, DISP_SOURCE_TBL, (Table 32) necessary for programming the secondary display lists, timing, and scroll sequences.

TYPE SEC_DISP_LIST_RCD = PACKED RECORD

SEC_DISP_LIST	: ARRAY[ACT_DISP_TBL.NBR_SEC_DISP_LISTS] OF 							PRI_DISP_LIST_TBL.DISP_LIST_DESC_RCD;

SEC_DISP_SOURCES	: ARRAY[ACT_DISP_TBL.NBR_SEC_DISP_LIST_ITEMS] OF 						UINT16;

END;

TABLE SEC_DISP_LIST_TBL = SEC_DISP_LIST_RCD;

Identifier			Value	Definition

DISP_SCROLL1_BFLD

ON_TIME		0..15	The number of seconds each display item is displayed.

OFF_TIME		0..15	The number of seconds display is blank between display items. 0 = No deliberate OFF Time.

DISP_SCROLL2_BFLD

HOLD_TIME		0..15	The number of minutes to wait before automatically restarting the normal display scroll after hold has been initiated.

DEFAULT_LIST		Associates this display list with a standard display list type. The "normal" display list scrolling resumes after HOLD_TIME has expired. The following values are recognized:

0	Display selectable via communication link only,

1	Normal display

2	Alternate Display

3	Test Display

4..15	Unassigned.

Identifier			Value	Definition

DISP_LIST_DESC_RCD

DISP_SCROLL1		This contains the ON_TIME and OFF_TIME values for the associated list.

DISP_SCROLL2		This contains the HOLD_TIME and DEFAULT_LIST values for the associated list.

NBR_LIST_ITEMS	0..255	Number of items in this display list. The total number of items (list entries) in all display lists of this table shall not exceed ACT_DISP_TBL.NBR_PRI_DISP_LIST_ITEM (Table 31).

SEC_DISP_LIST_RCD

SEC_DISP_LIST		An array of list descriptor records.

SEC_DISP_SOURCES		Ordered list of references to display items contained in DISP_SOURCE_TBL (Table 32). This list establishes the order of the secondary display.

This standard does not preclude additional items from popping up or being displayed out of sequence as a result of an end device error condition or an end device status report being generated.

## 9.5	Decade 40: security tables

The security tables provide holding areas for the placement of end device passwords and Encryption/Authentication keys used to establish group access permissions. Access permissions are used to limit table read or write access and procedure execute permissions to groups of users based on the interpretation of the password and encryption/authentication fields. The exact means for granting access are not defined by this standard.

### 9.5.1	Table 40 dimension security limiting  table

Table 40 Data Description

DIM_SECURITY_LIMITING_TBL (Table 40) defines the maximum number of passwords and security access level entries supported by the end device.

TYPE SECURITY_RCD = PACKED RECORD

NBR_PASSWORDS		: UINT8;

PASSWORD_LEN		: UINT8;

NBR_KEYS			: UINT8;

KEY_LEN			: UINT8;

NBR_PERM_USED		: UINT16;

END;

TABLE DIM_SECURITY_LIMITING_TBL = SECURITY_RCD;

Identifier			Value	Definition

SECURITY_RCD

NBR_PASSWORDS	0	Access levels cannot be established using the standard passwords mechanism.

1..255	Maximum number of passwords this end device is capable of supporting.

PASSWORD_LEN	1..20	Maximum length of passwords in octets this end device is capable of supporting.

21..255	Invalid.

NBR_KEYS		0..255	Maximum number of keys for authentication/encryption this end device is capable of supporting.

KEY_LEN		0..255	Maximum length of keys in octets this end device is capable of supporting.

NBR_PERM_USED	0..65535	Maximum number of user defined security access entries end device supports in addition to those defined through default access permissions.

### 9.5.2	Table 41 actual security limiting table

Table 41 Data Description

ACT_SECURITY_LIMITING_TBL (Table 41) defines the actual number of passwords and security access level entries supported by the end device.

TABLE ACT_SECURITY_LIMITING_TBL = DIM_SECURITY_LIMITING_TBL.SECURITY_RCD;

Identifier			Value	Definition

SECURITY_RCD

NBR_PASSWORDS	0	Actual access levels are not established through the standard passwords mechanism.

1..255	Actual number of passwords used by this end device.

PASSWORD_LEN	1..20	Actual length of passwords in octets this end device is supporting.

21..255	Invalid.

NBR_KEYS		0..255	Actual number of keys this end device is supporting.

KEY_LEN		0..255	Actual length of keys this end device is supporting.

NBR_PERM_USED	0..65535	Actual number of user defined security access entries end device supports in addition to those defined through default access permissions.

### 9.5.3	Table 42 security  table

Table 42 Data Description

SECURITY_TBL (Table 42) stores actual end device passwords. It is used to associate passwords with read, write and procedure execute access permission bits.

Any table or procedure whose access control bits match with respect to position at least one of the group access permissions bits, defined in SECURITY_TBL (Table 42) for the supplied password, can become a candidate for data transfers.

Notes:

1.	Although it may be possible to read the security table, the values reported (read back) are not defined by this standard.

2.	When access permissions are given to a procedure that accesses or modifies table data, then the invoker of that procedure shall in addition be required to have read or write access to the table that is read or modified.

3.	When access permissions are given to a User Defined table, which accesses or modifies other tables, then the invoker of that User Defined table shall in addition be required to have read or write access to the tables indirectly read or written.

TYPE ACCESS_PERMISSION_BFLD = BIT FIELD OF UINT8

GROUP_PERM_0_FLAG		: BOOL(0);

GROUP_PERM_1_FLAG		: BOOL(1);

GROUP_PERM_2_FLAG		: BOOL(2);

GROUP_PERM_3_FLAG		: BOOL(3);

GROUP_PERM_4_FLAG		: BOOL(4);

GROUP_PERM_5_FLAG		: BOOL(5);

GROUP_PERM_6_FLAG		: BOOL(6);

GROUP_PERM_7_FLAG		: BOOL(7);

END;

TYPE SECURITY_ENTRY_RCD = PACKED RECORD

PASSWORD			: ARRAY[ACT_SECURITY_LIMITING_TBL.PASSWORD_LEN] 						OF UINT8;

ACCESS_PERMISSIONS	: ACCESS_PERMISSION_BFLD;

END;

TYPE SECURITY_RCD = PACKED RECORD

SECURITY_ENTRIES	: ARRAY[ACT_SECURITY_LIMITING_TBL.NBR_PASSWORDS] OF 						SECURITY_ENTRY_RCD;

END;

TABLE SECURITY_TBL = SECURITY_RCD;

Identifier			Value	Definition

ACCESS_PERMISSIONS_BFLD

GROUP_PERM_0_FLAG	FALSE	Group 0 privileges are not granted by this password.

TRUE	Group 0 privileges are granted by this password.

GROUP_PERM_1_FLAG	FALSE	Group 1 privileges are not granted by this password.

TRUE	Group 1 privileges are granted by this password.

GROUP_PERM_2_FLAG	FALSE	Group 2 privileges are not granted by this password.

TRUE	Group 2 privileges are granted by this password.

GROUP_PERM_3_FLAG	FALSE	Group 3 privileges are not granted by this password.

TRUE	Group 3 privileges are granted by this password.

GROUP_PERM_4_FLAG	FALSE	Group 4 privileges are not granted by this password.

TRUE	Group 4 privileges are granted by this password.

GROUP_PERM_5_FLAG	FALSE	Group 5 privileges are not granted by this password.

TRUE	Group 5 privileges are granted by this password.

GROUP_PERM_6_FLAG	FALSE	Group 6 privileges are not granted by this password.

TRUE	Group 6 privileges are granted by this password.

GROUP_PERM_7_FLAG	FALSE	Group 7 privileges are not granted by this password.

TRUE	Group 7 privileges are granted by this password.

SECURITY_ENTRY_RCD

PASSWORD			Password to be matched and be associated with group access permission bits.

ACCESS_PERMISSIONS		Group access permissions bits for this password.

SECURITY_RCD

### SECURITY_ENTRIES		Array containing a list of security limiting parameters.

### 9.5.4	Table 43 default access control table

Table 43 Data Description

DEFAULT_ACCESS_CONTROL_TBL (Table 43) is used to establish default table and procedure access permissions.  These permissions are applied to any table that is not included in the ACCESS_CONTROL_TABLE (Table 44).

TYPE  DEFAULT_ACCESS_TABLE_DEF_BFLD = BIT FIELD OF UINT16

RESERVED		: FILL(0..12);

ANY_READ_FLAG	: BOOL(13);

ANY_WRITE_FLAG	: BOOL(14);

FILL2			: FILL(15..15);

END;

TYPE DEFAULT_ACCESS_CONTROL_RCD = PACKED RECORD

ACCESS_TABLE_DEFAULT	: DEFAULT_ACCESS_TABLE_DEF_BFLD;

READ				: SECURITY_TBL.ACCESS_PERMISSION_BFLD;

WRITE				: SECURITY_TBL.ACCESS_PERMISSION_BFLD;

END;

TYPE DEFAULT_ACCESS_RCD = PACKED RECORD

TABLE_DEFAULT 		: DEFAULT_ACCESS_CONTROL_RCD;

PROCEDURE_DEFAULT	: DEFAULT_ACCESS_CONTROL_RCD;

END;

TABLE DEFAULT_ACCESS_CONTROL_TBL = DEFAULT_ACCESS_RCD;

Identifier			Value	Definition

DEFAULT_ACCESS_TABLE_DEF_BFLD

RESERVED			Reserved.  See Section 6.4 Common Table or Procedure Identifier Formats.

ANY_READ_FLAG	FALSE	Any unrecognized user does not have read access permission to any tables.

TRUE	Any unrecognized user has read access permission to any table not defined in ACCESS_CONTROL_TBL (Table 44).

ANY_WRITE_FLAG	FALSE	Any unrecognized user does not have write access permission to any tables.

TRUE	Any unrecognized user has write access permission to any table not defined in ACCESS_CONTROL_TBL (Table 44).

DEFAULT_ACCESS_CONTROL_ENTRY_RCD

ACCESS_TABLE_DEF		Read and write access permissions for unrecognized users as defined above.

READ				Group security access permission bits for users that have been recognized and request read access to tables that are not listed in the ACCESS_CONTROL_TBL (Table 44).

Identifier			Value	Definition

WRITE				Group security access permission bits for users that have been recognized and request write access to tables that are not listed in the ACCESS_CONTROL_TBL (Table 44).

DEFAULT_ACCESS_RCD

TABLE_DEFAULT		Default access control for all tables, except the PROC_INITIATE_TBL (Table 07).

PROCEDURE_DEFAULT		Default access control for all procedures using PROC_INITIATE_TBL (Table 07).

### 9.5.5	Table 44 access control table

Table 44 Data Description

ACCESS_CONTROL_TBL (Table 44) establishes table and procedure access permissions on a per table and per procedure basis for those tables not using the default access level.

TYPE ACCESS_CONTROL_ENTRY_RCD = PACKED RECORD

ACCESS_TABLE_DEF	: TABLE_IDC_BFLD;

READ			: ACCESS_PERMISSION_BFLD;

WRITE			: ACCESS_PERMISSION_BFLD;

END;

TYPE ACCESS_CONTROL_RCD = PACKED RECORD

ACCESS_CONTROL	: ARRAY[ACT_SECURITY_LIMITING_TBL.NBR_PERM_USED] OF 						ACCESS_CONTROL_ENTRY_RCD;

END;

TABLE ACCESS_CONTROL_TBL = ACCESS_CONTROL_RCD;

Identifier			Value	Definition

TABLE_IDC_BFLD

TBL_PROC_NBR	0..2047	Table or procedure number associated with this access permission entry.

STD_VS_MFG_FLAG	FALSE	Entry is a standard table or standard procedure.

TRUE	Entry is a manufacturer table or manufacturer procedure.

PROC_FLAG		FALSE	Numeric ID is a table number.

TRUE	Numeric ID is a procedure number.

FLAG1			FALSE	Associated table or procedure requires read access control bits. Only approved group members may access table or procedure.

TRUE	Associated table or procedure has unrestricted read access. Any user may read the associated table or procedure.

Identifier			Value	Definition

FLAG2			FALSE	Associated table or procedure requires write access control bits. Only approved group members may write to table or procedure.

TRUE	Associated table or procedure has unrestricted write or execute permission. Any user may write into the associated table or procedure.

FLAG3				Reserved.

ACCESS_CONTROL_ENTRY_RCD

ACCESS_TABLE_DEF		Table identification and public access control.

READ				Group read access control bits. See SECURITY_TBL.ACCESS_PERMISSION_BFLD (Table 42).

WRITE				Group write access control bits See SECURITY_TBL.ACCESS_PERMISSION_BFLD (Table 42).

ACCESS_CONTROL_RCD

ACCESS_CONTROL		Array containing access permission for specific table or procedure.

### 9.5.6	Table 45 key table

Table 45 Data Description

KEY_TBL (Table 45) is a table established to contain authentication and/or encryption keys.

Note: Although it may be possible to read the KEY_TBL (Table 45), the values reported (read back) are not defined by this standard.

TYPE KEY_ENTRY_RCD = PACKED RECORD

KEY	: ARRAY[ ACT_SECURITY_LIMITING_TBL.KEY_LEN] OF UINT8;

END;

TYPE KEY_RCD = PACKED RECORD

KEY_ENTRIES		: ARRAY[ACT_SECURITY_LIMITING_TBL.NBR_KEYS] OF 							KEY_ENTRY_RCD;

END;

TABLE KEY_TBL = KEY_RCD;

Identifier			Value	Definition

KEY_ENTRY_RCD

KEY				A key to be applied in the authentication and/or encryption processes. Use of any key is not defined by this standard.

KEY_RCD

KEY_ENTRIES			Array of keys used to establish authentication and/or encryption.

## 9.6	Decade 50: time-of-use tables

The tables in this decade provide information related to end device Date & Time and Time Of Use (TOU) operation.

### 9.6.1	Table 50 dimension time and TOU table

Table 50 Data Description

DIM_TIME_TOU_TBL (Table 50) defines the maximum capabilities for Date & Time clock control and Time of Use (TOU) control for the end device.

TYPE TIME_FUNC_FLAG1_BFLD = BIT FIELD OF UINT8

TOU_SELF_READ_FLAG		: BOOL(0);

SEASON_SELF_READ_FLAG		: BOOL(1);

SEASON_DEMAND_RESET_FLAG	: BOOL(2);

SEASON_CHNG_ARMED_FLAG	: BOOL(3);

SORT_DATES_FLAG			: BOOL(4);

ANCHOR_DATE_FLAG		: BOOL(5);

FILLER					: FILL(6..7);

END;

TYPE TIME_FUNC_FLAG2_BFLD = BIT FIELD OF UINT8

CAP_DST_AUTO_FLAG		: BOOL(0);

SEPARATE_WEEKDAYS_FLAG	: BOOL(1);

SEPARATE_SUM_DEMANDS_FLAG	: BOOL(2);

SORT_TIER_SWITCHES_FLAG	: BOOL(3);

CAP_TM_ZN_OFFSET_FLAG		: BOOL(4);

FILLER					: FILL(5..7);

END;

TYPE CALENDAR_BFLD = BIT FIELD OF UINT8

NBR_SEASONS			: UINT(0..3);

NBR_SPECIAL_SCHED		: UINT(4..7);

END;

TYPE TIME_TOU_RCD = PACKED RECORD

TIME_FUNC_FLAG1		: TIME_FUNC_FLAG1_BFLD;

TIME_FUNC_FLAG2		: TIME_FUNC_FLAG2_BFLD;

CALENDAR_FUNC		: CALENDAR_BFLD;

NBR_NON_RECURR_DATES	: UINT8;

NBR_RECURR_DATES	: UINT8;

NBR_TIER_SWITCHES	: UINT16;

CALENDAR_TBL_SIZE	: UINT16;

END;

TABLE DIM_TIME_TOU_TBL = TIME_TOU_RCD;

Identifier			Value	Definition

TIME_FUNC_FLAG1_BFLD

TOU_SELF_READ_FLAG	FALSE	End device is not capable of TOU triggered self-reads.

TRUE	End device is capable of TOU triggered self-reads.

SEASON_SELF_READ_FLAG	FALSE	Self read with season change capability does not exist.

TRUE	Self read with season change capability exists.

SEASON_DEMAND_RESET_FLAG

FALSE	Automatic demand reset with season change capability does not exist.

TRUE	Automatic demand reset with season change capability exists.

SEASON_CHNG_ARMED_FLAG

FALSE	Season change arming capability does not exist.

TRUE	Season change arming capability exists. That is, the end device is only armed to do a season change as a result of an indicated change of season. The actual season change does not occur until the next demand reset occurs (by manual or other means).

SORT_DATES_FLAG	FALSE	End device does not require the   CALENDAR_TBL.NON_RECURR_DATES (Table 54) be presorted by date (Year, Month, Day) when received.

TRUE	End device does require the  CALENDAR_TBL.NON_RECURR_DATES (Table 54) be presorted by date (Year, Month, Day) when received.  Non-recurring dates starting with 1990 and ending with 2089 shall occur in that order.  No sorting of recurring dates, if present, is assumed.

ANCHOR_DATE_FLAG	FALSE	End device is not capable of accepting an anchor date for the Period/Delta RDATE type (recurring date).

Identifier			Value	Definition

TRUE	End device is capable of accepting an Anchor Date for the Period/Delta RDATE type (recurring date).

TIME_FUNC_FLAG2_BFLD

CAP_DST_AUTO_FLAG	FALSE	End device is not capable of handling daylight savings time changes independently of dates supplied by the CALENDAR_TBL (Table 54).

TRUE	End device is capable of handling daylight savings time changes independently of dates supplied by the CALENDAR_TBL (Table 54).

SEPARATE_WEEKDAYS_FLAG

FALSE	End device is not capable of having a different schedule for each of the five weekdays.

TRUE	End device is capable of having a different schedule for each of the five weekdays.

SEPARATE_SUM_DEMANDS_FLAG

FALSE	End device is not capable of switching summation and demands independently.

TRUE	End device is capable of switching summation and demands independently.

SORT_TIER_SWITCHES_FLAG

FALSE	End device does not require that  CALENDAR_TBL.TIER_SWITCHES (Table 54) be presorted.

TRUE	End device requires that  CALENDAR_TBL.TIER_SWITCHES (Table 54) be presorted.

CAP_TM_ZN_OFFSET_FLAG	FALSE	Time zone offset capability is not supported by the end device.

TRUE	Time zone offset capability is supported by the end device.

CALENDAR_BFLD

NBR_SEASONS		0..15	Maximum number of seasons supported by this end device.

NBR_SPECIAL_SCHED	0..11	Maximum number of special schedules supported by this end device.

12..15	Reserved.

TIME_TOU_RCD

TIME_FUNC_FLAG1				See TIME_FUNC_FLAG1_BFLD above.

TIME_FUNC_FLAG2				See TIME_FUNC_FLAG2_BFLD above.

CALENDAR_FUNC				See CALENDAR_BFLD above.

NBR_NON_RECURR_DATES	0..255	Maximum number of non-recurring dates supported by the end device calendar. Each entry allows the control of one or more events like demand reset, self read, daylight savings time, season change and special schedule.

Identifier			Value	Definition

NBR_RECURR_DATES	0..255	Maximum number of recurring dates supported by the end device calendar. Each entry allows the definition of a recurring event like demand reset, self read, daylight savings time, season change and special schedule.

NBR_TIER_SWITCHES	0..65535	Maximum number of tier switches supported by the end device calendar. This number comprises the total collection of tier switches for all day types in the CALENDAR_TBL.-DAILY_SCHEDULE_ID_MATRIX (Table 54).

CALENDAR_TBL_SIZE	0..65535	Maximum octets of data transported by CALENDAR_TBL (Table 54). This includes recurring dates, non-recurring dates and tier switches.  Anchor date is counted even if it is unused.

### 9.6.2	Table 51 actual time and TOU table

Table 51 Data Description

ACT_TIME_TOU_TBL (Table 51) defines the actual capabilities for Date & Time clock control limits and Time of Use (TOU) control limits for the end device. The data structure of this table is identical to DIM_TIME_TOU_TBL (Table 50).  Elements are defined below.

TABLE ACT_TIME_TOU_TBL = DIM_TIME_TOU_TBL.TIME_TOU_RCD;

Identifier			Value	Definition

TIME_FUNC_FLAG1_BFLD

TOU_SELF_READ_FLAG	FALSE	End device is not using TOU triggered self-reads.

TRUE	End device is using TOU triggered self-reads.

SEASON_SELF_READ_FLAG	FALSE	Self read with season change capability is not being used.

TRUE	Self read with season change capability is being used.

SEASON_DEMAND_RESET_FLAG

FALSE	Automatic demand reset when season change occurs is not in use.

TRUE	Automatic demand reset when season change occurs is being used.

SEASON_CHNG_ARMED_FLAG

FALSE	Season change arming is not being used.

TRUE	Season change arming is in use. That is, the end device is only armed to do a season change as a result of an indicated change of season. The actual season change does not occur until the next demand reset occurs (by manual or other means).

Identifier			Value	Definition

SORT_DATES_FLAG	FALSE	End device may or may not require the  CALENDAR_TBL.NON_RECURR_DATES (Table 54) to be presorted by date (Year, Month, Day) when received.

TRUE	End device does require the CALENDAR_TBL.NON_RECURR_DATES (Table 54) be presorted by date (Year, Month, Day) when received. Non-recurring dates starting with 1990 and ending with 2089 shall be sorted in that order. No sorting of recurring dates, if present, is required.

ANCHOR_DATE_FLAG	FALSE	End device does not accept an anchor date for the Period/Delta RDATE type (recurring date).

TRUE	End device accepts an anchor date for the Period/Delta RDATE type (recurring date).

TIME_FUNC_FLAG2_BFLD

CAP_DST_AUTO_FLAG	FALSE	End device is not handling daylight savings time changes independently of dates supplied by the CALENDAR_TBL (Table 54).

TRUE	End device is handling daylight savings time changes independently of dates supplied by the CALENDAR_TBL (Table 54).

SEPARATE_WEEKDAYS_FLAG

FALSE	End device is not using a different schedule for each of the five weekdays.

TRUE	End device is using a different schedule for each of the five weekdays.

SEPARATE_SUM_DEMANDS_FLAG

FALSE	End device is not switching summation and demands independently.

TRUE	End device is switching summation and demands independently.

SORT_TIER_SWITCHES_FLAG

FALSE	End device does not require that  CALENDAR_TBL.TIER_SWITCHES (Table 54) be presorted.

TRUE	End device requires that CALENDAR_TBL.TIER_SWITCHES (Table 54) be presorted.

CAP_TM_ZN_OFFSET_FLAG	FALSE	Time zone offset capability is not available in the end device.

TRUE	Time zone offset capability is available in the end device.

CALENDAR_BFLD

NBR_SEASONS		0..15	Actual number of seasons in use by the end device.

Identifier			Value	Definition

NBR_SPECIAL_SCHED	0..11	Actual number of special schedules in use by the end device.

12..15	Reserved.

TIME_TOU_RCD

TIME_FUNC_FLAG1				See TIME_FUNC_FLAG1_BFLD above.

TIME_FUNC_FLAG2				See TIME_FUNC_FLAG2_BFLD above.

CALENDAR_FUNC				See CALENDAR_BFLD above.

NBR_NON_RECURR_DATES	0..255	Actual number of non-recurring dates supported by the end device calendar. Each entry allows the control of one or more events like demand reset, self read, daylight savings time, season change and special schedule.

NBR_RECURR_DATES	0..255	Actual number of recurring dates supported by the end device calendar. Each entry allows the definition of a recurring event like demand reset, self read, daylight savings time, season change and special schedule.

NBR_TIER_SWITCHES	0..65535	Actual number of tier switches supported by the end device calendar. This number comprises the total collection of tier switches for all day types in the CALENDAR_TBL.-DAILY_SCHEDULE_ID_MATRIX (Table 54).

CALENDAR_TBL_SIZE	0..65535	Actual octets of data transported by CALENDAR_TBL (Table 54). This includes the recurring dates, non-recurring dates and tier switches.

### 9.6.3	Table 52 clock table

Table 52 Data Description

CLOCK_TBL (Table 52) provides the end device real time clock information.

TYPE TIME_DATE_QUAL_BFLD = BIT FIELD OF UINT8

DAY_OF_WEEK		: UINT(0..2);

DST_FLAG			: BOOL(3);

GMT_FLAG			: BOOL(4);

TM_ZN_APPLIED_FLAG	: BOOL(5);

DST_APPLIED_FLAG		: BOOL(6);

FILLER				: FILL(7..7);

END;

TYPE CLOCK_STATE_RCD = PACKED RECORD

CLOCK_CALENDAR	: LTIME_DATE;

TIME_DATE_QUAL	: TIME_DATE_QUAL_BFLD;

END;

TABLE CLOCK_TBL = CLOCK_STATE_RCD;

Identifier			Value	Definition

TIME_DATE_QUAL_BFLD		Status qualifying the end device time.

DAY_OF_WEEK			Current day of the week.

0	Sunday

1	Monday

2	Tuesday

3	Wednesday

4	Thursday

5	Friday

6	Saturday

7	Unassigned

DST_FLAG			Daylight savings time status.

FALSE	End device time is not in daylight savings time.

TRUE	End device time is in daylight savings time.

GMT_FLAG		FALSE	End device time does not correspond to Greenwich Mean Time.

TRUE	End device time corresponds to Greenwich Mean Time.

TM_ZN_APPLIED_FLAG	FALSE	Time zone offset has not been applied to the end device time.

TRUE	Time zone offset has been applied to the end device time.

DST_APPLIED_FLAG	FALSE	End device time does not include daylight savings adjustment.

TRUE	End device time includes daylight savings adjustment.

CLOCK_STATE_RCD

CLOCK_CALENDAR		Current end device time.

TIME_DATE_QUAL		See DATE_TIME_QUAL_BFLD above.

### 9.6.4	Table 53 time offset table

Table 53 Data Description

TIME_OFFSET_TBL (Table 53) provides time zone offset and daylight savings time information for the end device.

TYPE TIME_OFFSET_RCD = PACKED RECORD

DST_TIME_EFF		: TIME;

DST_TIME_AMT		: UINT8;

IF ACT_TIME_TOU_TBL.CAP_TM_ZN_OFFSET_FLAG THEN

TIME_ZONE_OFFSET	: INT16;

END;

END;

TABLE TIME_OFFSET_TBL = TIME_OFFSET_RCD;

Identifier			Value	Definition

TIME_OFFSET_RCD

DST_TIME_EFF		The time of day the end device  shifts to or from daylight savings time. The date of occurrence is based on entries in the CALENDAR_TBL (Table 54) and the ACT_TIME_TOU_TBL.CAP_DST_AUTO_FLAG (Table 51) flag.

DST_TIME_AMT	0..255	End device daylight savings time adjustment specified in minutes.

TIME_ZONE_OFFSET  -32767..32767	Offset for end device, representing the number of ± 1 minute segments of end device time offset.

### 9.6.5	Table 54 calendar table

Table 54 Data Description

CALENDAR_TBL (Table 54) is the schedule definition table for TOU metering activities.

TYPE CALENDAR_ACTION_BFLD = BIT FIELD OF UINT8

CALENDAR_CTRL		: UINT(0..4);

DEMAND_RESET_FLAG	: BOOL(5);

SELF_READ_FLAG		: BOOL(6);

FILLER				: FILL(7..7);

END;

TYPE RECURR_DATE_RCD = PACKED RECORD

RECURR_DATE	: RDATE;

CALENDAR_ACTION	: CALENDAR_ACTION_BFLD;

END;

TYPE NON_RECURR_DATE_RCD = PACKED RECORD

NON_RECURR_DATE	: DATE;

CALENDAR_ACTION	: CALENDAR_ACTION_BFLD;

END;

TYPE TIER_SWITCH_BFLD = BIT FIELD OF UINT16

NEW_TIER				: UINT(0..2);

IF ACT_TIME_TOU_TBL.SEPARATE_SUM_DEMANDS_FLAG THEN

SUMMATION_SWITCH_FLAG	: BOOL(3);

DEMANDS_SWITCH_FLAG	: BOOL(4);

ELSE

FILLER				: FILL(3..4);

END;

SWITCH_MIN				: UINT(5..10);

SWITCH_HOUR			: UINT(11..15);

END;

TYPE TIER_SWITCH_RCD = PACKED RECORD

TIER_SWITCH			: TIER_SWITCH_BFLD;

DAY_SCH_NUM		: UINT8;

END;

TYPE CALENDAR_RCD = PACKED RECORD

IF ACT_TIME_TOU_TBL.ANCHOR_DATE_FLAG THEN

ANCHOR_DATE	: DATE;

END;

NON_RECURR_DATES	: ARRAY[ACT_TIME_TOU_TBL.NBR_NON_ 									RECURR_DATES] OF 	NON_RECURR_DATE_RCD;

RECURR_DATES		: ARRAY[ACT_TIME_TOU_TBL.NBR_RECURR_DATES] OF 							RECURR_DATE_RCD;

TIER_SWITCHES		: ARRAY[ACT_TIME_TOU_TBL.NBR_TIER_SWITCHES] OF 							TIER_SWITCH_RCD;

IF ACT_TIME_TOU_TBL.SEPARATE_WEEKDAYS_FLAG THEN

DAILY_SCHEDULE_ID_MATRIX

: ARRAY[ACT_TIME_TOU_TBL.NBR_SEASONS, 								ACT_TIME_TOU_TBL.NBR_SPECIAL_SCHED+7] OF 							UINT8;

ELSE

DAILY_SCHEDULE_ID_MATRIX

: ARRAY[ACT_TIME_TOU_TBL.NBR_SEASONS, 								ACT_TIME_TOU_TBL.NBR_SPECIAL_SCHED+3] OF 							UINT8;

END;

END;

TABLE CALENDAR_TBL = CALENDAR_RCD;

Identifier			Value	Definition

CALENDAR_ACTION_BFLD

CALENDAR_CTRL		Number specifying the calendar action that takes place on the date specified. The actions and their codes are defined as follows:

0	No Action.

1	Daylight Savings Time On

2	Daylight Savings Time Off

3	Select Season 0

4	Select Season 1

.

.

.

18	Select Season 15

19	Special Schedule 0

20	Special Schedule 1

.

.

.

30	Special Schedule 11

31	End Of List

Daylight Savings Time On/Off

Daylight Savings Time On and Off actions causes a time adjustment to be made at TIME_OFFSET_TBL.DST_TIME_EFF (Table 53) time. If TIME_OFFSET_TBL (Table 53) is not supported, the time adjustment is made at 02:00 A.M. and the effectivity amount equals 1 hour.

If ACT_TIME_TOU_TBL.CAP_DST_AUTO_ FLAG (Table 51) = TRUE then Daylight Savings Time On/Off actions in this table are ignored.

Season Changes

If ACT_TIME_TOU_TBL.SEASON_CHNG_ ARMED_FLAG (Table 51) = FALSE, a season change action causes a season change to occur at 00:00 A.M. hours on the date specified. If ACT_TIME_TOU_TBL.SEASON_CHNG_ARMED_FLAG (Table 51) = TRUE, a season change action "arms" a season change, but the season change will not occur until the next demand reset.

If ACT_TIME_TOU_TBL.SEASON_DEMAND _RESET_FLAG (Table 51) = TRUE, a season change causes a demand reset to occur automatically.

A self read of the current register data is saved in the SELF_READ_DATA_TBL (Table 26) if ACT_TIME_TOU_TBL.SEASON_SELF_READ_FLAG (Table 51) = TRUE when the season change occurs.

If GEN_CONFIG_TBL.STD_TBLS_USED.-PREVIOUS_SEASON_DATA_TBL (Table 00) = TRUE, a season change causes a copy of the current register data to be saved in the PREVIOUS_SEASON_DATA_TBL (Table 24)

Special Schedules

Special schedules are used for holidays or other special daily schedules. These schedules take effect at midnight (00:00 A.M.) and end 24 hours later (23:59 P.M.). The special schedule takes precedence over the normal day of week schedule.

End of List

End of List Action is to notify the utility that the CALENDAR_TBL (Table 54) entries are approaching expiration. Notification is by history message, display, or other means defined by the device manufacturer.

DEMAND_RESET_FLAG	FALSE	Demand reset shall not occur.

TRUE	Demand reset shall occur at 00:00 A.M. on the date specified.

If GEN_CONFIG_TBL.STD_TBLS_USED. PREVIOUS_DEMAND_RESET_DATA_TBL (Table 00) = TRUE, a Demand Reset causes data to be saved in PREVIOUS_DEMAND_ RESET_DATA_TBL (Table 25).

If ACT_REGS_TBL.SELF_READ_DEMAND_ RESET_FLAG (Table 21) = 1 or 3, a self read shall occur in conjunction with the demand reset.

SELF_READ_FLAG	FALSE	Self read shall not occur.

TRUE	Self read shall occur at 00:00 A.M. on the date specified.

If ACT_REGS_TBL.SELF_READ_DEMAND _RESET_FLAG (Table 21) = 2 or 3, a demand reset shall occur in conjunction with the self read.

RECURR_DATE_RCD

RECURR_DATE		Date definition of a recurring event. The recurrence can be yearly, monthly, or weekly. The recurring event is referenced to midnight.

CALENDAR_ACTION		Defined action that shall take place on this date. See CALENDAR_ACTION_BFLD above.

NON_RECURR_DATE_RCD

NON_RECURR_DATE		Non-recurring event date.  Action shall occur at midnight.

CALENDAR_ACTION		Defined action that shall take place on this date. See CALENDAR_ACTION_BFLD above.

TIER_SWITCH_BFLD

NEW_TIER		0..7	Identifies the tier number that  becomes effective at the time specified in the tier switch on the daily schedule type defined by the DAILY_SCHEDULE_ID_MATRIX.

SUMMATION_SWITCH_FLAG		Specifies whether or not this tier switch selects a new tier for summations. Only used when  ACT_TIME_TOU_TBL.SEPARATE_SUM_ DEMANDS_FLAG (Table 51) = TRUE.

FALSE	Tier switch is not specified for  summations.

TRUE	Tier switch is specified for summations.

DEMANDS_SWITCH_FLAG		Specifies whether or not this tier switch selects a new tier for demands. Only used when ACT_TIME_TOU_TBL.SEPARATE_SUM_ DEMANDS_FLAG (Table 51) = TRUE.

FALSE	Tier switch is not specified for demands.

TRUE	Tier switch is specified for demands.

SWITCH_MIN		0..59	Minute when the tier switch occurs.

60..63	Invalid.

SWITCH_HOUR	0..23	Hour when the tier switch occurs.

24..31	Invalid.

TIER_SWITCH_RCD

TIER_SWITCH			Defines a switch point for a certain day type defined by the DAILY_SCHEDULE_ID_ MATRIX.

DAY_SCH_NUM	0..255	Specifies the daily schedule type  associated with the tier switch. All identifiers are stored in the DAILY_SCHEDULE_ID_MATRIX.

CALENDAR_RCD

ANCHOR_DATE		Anchor date is only used in conjunction with an RDATE type recurring date using the PERIOD/OFFSET mechanism.  See  Section 6.3.2, RDATE Type.  If specified, any recurring date using the PERIOD/OFFSET type shall use this date as a starting date.

NON_RECURR_DATES		Array containing non-recurring dates.

RECURR_DATES		Array containing recurring dates.

TIER_SWITCHES		Array that contains the tier switches.

DAILY_SCHEDULE_ID_MATRIX	Two-dimensional array containing daily schedule type identifiers. The array is bounded by [seasons supported * (day types supported + special schedules supported)]. Each entry in the array consists of a single octet type identifier value. The identifier is used to tie tier switch entries to specific daily schedules. An example of a daily schedule is Special Schedule 1 in Season 2 or Saturday Day Type in Season 1.

The assignment of identifier codes is left to the utility’s discretion.

If ACT_TIME_TOU_TBL.SEPARATE_ WEEKDAYS_ FLAG = TRUE, the end device is programmed with a different schedule for each of the five weekdays. In this case, day types and special schedule  definitions are:

0	Sunday

1	Monday

2	Tuesday

3	Wednesday

4	Thursday

5	Friday

6	Saturday

7	Special schedule 1

.

.

.

n	Last special schedule supported

If ACT_TIME_TOU_TBL.SEPARATE_ WEEKDAYS_FLAG = FALSE, the end device has the same schedule for each of the five weekdays, and day type and special schedules definitions are

0	Saturday

1	Sunday

2	Weekday

3	Special schedule 1 (if supported)

.

.

.

n	Last special schedule supported

### 9.6.6	Table 55 clock state table

Table 55 Data Description

CLOCK_STATE_TBL (Table 55) provides the end device real time clock information.

TYPE STATUS_BFLD = BIT FIELD OF UINT16

IF ACT_TIME_TOU_TBL.SEPARATE_SUM_DEMANDS_FLAG THEN

CURR_SUMM_TIER	: UINT(0..2);

CURR_DEMAND_TIER	: UINT(3..5);

ELSE

CURR_TIER		: UINT(0..2);

FILLER			: FILL(3..5);

END;

TIER_DRIVE			: UINT(6..7);

SPECIAL_SCHD_ACTIVE	: UINT(8..11);

SEASON			: UINT(12..15);

END;

TYPE CLOCK_STATE_RCD = PACKED RECORD

CLOCK_CALENDAR	: LTIME_DATE;

TIME_DATE_QUAL	: CLOCK_TBL.TIME_DATE_QUAL_BFLD;

STATUS		: STATUS_BFLD;

END;

TABLE CLOCK_STATE_TBL = CLOCK_STATE_RCD;

Identifier			Value	Definition

TIME_DATE_QUAL_BFLD		Status qualifying the end device time.

DAY_OF_WEEK		Current day of the week.

0	Sunday

1	Monday

2	Tuesday

3	Wednesday

4	Thursday

5	Friday

6	Saturday

7	Unassigned

Identifier			Value	Definition

DST_FLAG			Daylight savings time status.

FALSE	End device time is not daylight savings time.

TRUE	End device time is daylight savings time.

GMT_FLAG		FALSE	End device time does not correspond to Greenwich Mean Time.

TRUE	End device time corresponds to Greenwich Mean Time.

TM_ZN_APPLIED_FLAG	FALSE	Time zone offset has not been applied to the end device time.

TRUE	Time zone offset has been applied to the end device time.

DST_APPLIED_FLAG	FALSE	End device time does not include daylight savings adjustment.

TRUE	End device time includes daylight savings adjustment.

STATUS_BFLD			Array of status entries of each TOU set.  Each set contains:

CURR_SUMM_TIER	0..7	Active tier corresponding to summations. This variable is only used when the capability flag ACT_TIME_TOU_TBL.-SEPARATE_SUM_DEMANDS_FLAG (Table 51) = TRUE.

CURR_DEMAND_TIER	0..7	Active tier corresponding to demands. This variable is only used when the capability flag ACT_TIME_TOU_TBL.-SEPARATE_SUM_DEMANDS_FLAG (Table 51) = TRUE.

CURR_TIER		0..7	Number representing the tier that is currently active in the meter. This variable is only used when the capability flag ACT_TIME_TOU_TBL.-SEPARATE_SUM_DEMANDS_FLAG (Table 51) = FALSE.

TIER_DRIVE			Tier drive source code.

0	Tier selection is controlled by CALENDAR_TBL.TIER_SWITCHES (Table 54).

1..3	Tier selection is not controlled by this standard.

SPECIAL_SCHD_ACTIVE	0..11	Active special schedule number.

12..14	Reserved.

15	No special schedule active.

SEASON		0..15	Current end device season number.

CLOCK_STATE_RCD

CLOCK_CALENDAR		Current end device time.

Identifier			Value	Definition

TIME_DATE_QUAL		See TIME_DATE_QUAL_BFLD above.

STATUS					See STATUS_BFLD above.

### 9.6.7	Table 56 time remaining table

Table 56 Data Description

TIME_REMAIN_TBL (Table 56) provides predictive time quantities.

TYPE TIME_REMAIN_RCD = PACKED RECORD

IF ACT_TIME_TOU_TBL.SEPARATE_SUM_DEMANDS_FLAG THEN

SUMM_TIER_TIME_REMAIN		: UINT16;

DEMAND_TIER_TIME_REMAIN	: UINT16;

ELSE

TIER_TIME_REMAIN			: UINT16;

END;

SELF_READ_DAYS_REMAIN			: UINT8;

END;

TABLE TIME_REMAIN_TBL = TIME_REMAIN_RCD;

Identifier			  Value	Definition

TIME_REMAIN_RCD

SUMM_TIER_TIME_REMAIN	  0..65535	Minutes remaining until the next tier change which affects summations. Used when the capability flag ACT_TIME_TOU_TBL.-SEPARATE_SUM_DEMANDS_FLAG (Table 51) = TRUE.

DEMAND_TIER_TIME_REMAIN  0..65535	Minutes remaining before the next tier change which affects demands. Used when the capability flag ACT_TIME_TOU_TBL.-SEPARATE_SUM_DEMANDS_FLAG (Table 51) = TRUE.

TIER_TIME_REMAIN	  0..65535	Time in minutes, remaining before the next tier change.

SELF_READ_DAYS_REMAIN	  0..255	Days remaining before the next scheduled self read.

## 9.7	Decade 60: load profile tables

These tables provide structures for load profile data.

### 9.7.1	Table 60 dimension load profile table

Table 60 Data Description

DIM_LP_TBL (Table 60) contains function limiting constants for the load profile application. These parameters provide for up to four independent sets of load profile data.

TYPE LP_FLAGS_BFLD = BIT Field OF UINT16

LP_SET1_INHIBIT_OVF_FLAG		: BOOL(0);

LP_SET2_INHIBIT_OVF_FLAG		: BOOL(1);

LP_SET3_INHIBIT_OVF_FLAG		: BOOL(2);

LP_SET4_INHIBIT_OVF_FLAG		: BOOL(3);

blk_end_read_flag		: bool(4);

blk_end_pulse_flag		: bool(5);

SCALAR_DIVISOR_FLAG_SET1	: BOOL(6);

SCALAR_DIVISOR_FLAG_SET2	: BOOL(7);

SCALAR_DIVISOR_FLAG_SET3	: BOOL(8);

SCALAR_DIVISOR_FLAG_SET4	: BOOL(9);

EXTENDED_INT_STATUS_FLAG	: BOOL(10);

SIMPLE_INT_STATUS_FLAG		: BOOL(11);

FILLER					: FILL (12..15);

END;

type LP_fMATS_bfld = bIT FIELD OF uint8

INV_UINT8_FLAG		: BOOL(0);

INV_UINT16_FLAG		: BOOL(1);

INV_UINT32_FLAG		: BOOL(2);

INV_INT8_FLAG		: BOOL(3);

INV_INT16_flag		: BOOL(4);

INV_INT32_flag		: BOOL(5);

INV_ni_fmat1_flag		: BOOL(6);

INV_ni_fmat2_flag		: BOOL(7);

end;

TYPE LP_SET_RCD = PACKED RECORD

LP_MEMORY_LEN		: UINT32;

LP_FLAGS			: LP_FLAGS_BFLD;

LP_FMATS			: LP_fMATS_BFLD;

IF GEN_CONFIG_TBL.STD_TBLS_USED.LP_DATA_SET1_TBL_CNST THEN

NBR_BLKS_SET1	: UINT16;

NBR_BLK_INTS_SET1	: UINT16;

NBR_CHNS_SET1	: UINT8;

MAX_INT_TIME_SET1	: UINT8;

END;

IF  GEN_CONFIG_TBL.STD_TBLS_USED.LP_DATA_SET2_TBL_CNST THEN

NBR_BLKS_SET2	: UINT16;

NBR_BLK_INTS_SET2	: UINT16;

NBR_CHNS_SET2	: UINT8;

MAX_INT_TIME_SET2	: UINT8;

END;

IF  GEN_CONFIG_TBL.STD_TBLS_USED.LP_DATA_SET3_TBL_CNST THEN

NBR_BLKS_SET3	: UINT16;

NBR_BLK_INTS_SET3	: UINT16;

NBR_CHNS_SET3	: UINT8;

MAX_INT_TIME_SET3	: UINT8;

END;

IF  GEN_CONFIG_TBL.STD_TBLS_USED.LP_DATA_SET4_TBL_CNST THEN

NBR_BLKS_SET4	: UINT16;

NBR_BLK_INTS_SET4	: UINT16;

NBR_CHNS_SET4	: UINT8;

MAX_INT_TIME_SET4	: UINT8;

END;

END;

TABLE DIM_LP_TBL = LP_SET_RCD;

Identifier			Value	Definition

LP_FLAGS_BFLD			This bit field specifies load profile list management capabilities.

LP_SET1_INHIBIT_OVF_FLAG

FALSE	End device is not capable of inhibiting load profile set 1 once an overflow occurs.

TRUE	End device is capable of inhibiting load profile set 1 once an overflow occurs.

LP_SET2_INHIBIT_OVF_flag

FALSE	End device is not capable of inhibiting load profile set 2 once an overflow occurs.

TRUE	End device is capable of inhibiting load profile set 2 once an overflow occurs.

LP_SET3_INHIBIT_OVF_flag

FALSE	End device is not capable of inhibiting load profile set 3 once an overflow occurs.

TRUE	End device is capable of inhibiting load profile set 3 once an overflow occurs.

LP_SET4_INHIBIT_OVF_flag

FALSE	End device is not capable of inhibiting load profile set 4 once an overflow occurs.

TRUE	End device is capable of inhibiting load profile set 4 once an overflow occurs.

blk_end_read_flag	false	The end device is not capable of providing block register reading information.

TRUE	The end device is capable of providing block register reading information.

blk_end_pulse_flag	FALSE	The end device is not capable of having a running pulse accumulator.

TRUE	The end device is capable of having a running pulse accumulator.

Identifier			Value	Definition

SCALAR_DIVISOR_FLAG_SET1

FALSE	The end device is not capable of having scalars and divisors associated with set 1 load profile interval data.

TRUE	The end device is capable of having scalars and divisors associated with set 1 load profile interval data.

SCALAR_DIVISOR_FLAG_SET2

FALSE	The end device is not capable of having scalars and divisors associated with set 2 load profile interval data.

TRUE	The end device is capable of having scalars and divisors associated with set 2 load profile interval data.

SCALAR_DIVISOR_FLAG_SET3

FALSE	The end device is not capable of having scalars and divisors associated with set 3 load profile interval data.

TRUE	The end device is capable of having scalars and divisors associated with set 3 load profile interval data.

SCALAR_DIVISOR_FLAG_SET4

FALSE	The end device is not capable of having scalars and divisors associated with set 4 load profile interval data.

TRUE	The end device is capable of having scalars and divisors associated with set 4 load profile interval data.

EXTENDED_INT_STATUS_FLAG

FALSE	The end device is not capable of returning extended interval status with load profile interval data.

TRUE 	The end device is capable of returning extended interval status with load profile interval data.

SIMPLE_INT_STATUS_FLAG	FALSE	The end device is not capable of returning simple interval status with load profile interval data.

TRUE 	The end device is capable of returning simple interval status with load profile interval data.

LP_FMATS_BFLD			This set of booleans specifies the format(s) acceptable for use in DIM_LP_TBL (Table 60) and ACT_LP_TBL (Table 61).

INV_UINT8_FLAG	FALSE	UINT8 format for intervals is not capable of being used.

TRUE	An interval format of UINT8 is capable of being used.

Identifier			Value	Definition

INV_UINT16_FLAG	FALSE	UINT16 format for intervals is not capable of being used.

TRUE	An interval format of UINT16 is capable of being used.

INV_UINT32_FLAG	FALSE	UINT32 format for intervals is not capable of being used.

TRUE	An interval format of UINT32 is capable of being used.

INV_INT8_FLAG	FALSE	INT8 format for intervals is not capable of being used.

TRUE	An interval format of INT8 is capable of being used.

INV_INT16_FLAG	FALSE	INT16 format for intervals is not capable of being used.

TRUE 	An interval format of INT16 is capable of being used.

INV_INT32_FLAG	FALSE	INT32 format for intervals is not capable of being used.

TRUE	An interval format of INT32 is capable of being used.

INV_NI_FMAT1_FLAG	FALSE	NI_FMAT1 format for intervals is not capable of being used.

TRUE	An interval format of NI_FMAT1 is capable of being used.

INV_NI_FMAT2_FLAG	FALSE	NI_FMAT2 format for intervals is not capable of being used.

TRUE	An interval format of NI_FMAT2 is capable of being used.

LP_SET_RCD				The information defining how each set of load profile information works.

LP_MEMORY_LEN 	0..4,294,967,295

The maximum number of octets of storage available for load profile data. This reflects the combined sizes of tables LP_DATA_SET1_TBL (Table 64), LP_DATA_SET2_TBL (Table 65), LP_DATA_SET3_TBL (Table 66), and LP_DATA_SET4_TBL (Table 67).

LP_FLAGS			See LP_FLAGS_BFLD above.

LP_FMATS			See LP_FMATS_BFLD above.

NBR_BLKS_SET1	0..65535	The maximum number of interval data blocks which can be contained in LP_DATA_SET1_TBL (Table 64).

Identifier			Value	Definition

NBR_BLK_INTS_SET1	0..65535	The maximum number of intervals per data block which can be contained in LP_DATA_SET1_TBL (Table 64).

NBR_CHNS_SET1	0..255	The maximum number of channels of load profile data which can be contained in LP_DATA_SET1_TBL (Table 64).

MAX_INT_TIME_SET1	0..255	The maximum time in minutes for load profile interval duration which can be contained in LP_DATA_SET1_TBL (Table 64).

NBR_BLKS_SET2	0..65535	The maximum number of interval data blocks which can be contained in LP_DATA_SET2_TBL (Table 65).

NBR_BLK_INTS_SET2	0..65535	The maximum number of intervals per data block which can be contained in LP_DATA_SET2_TBL (Table 65).

NBR_CHNS_SET2	0..255	The maximum number of channels of load profile data which can be contained in LP_DATA_SET2_TBL (Table 65).

MAX_INT_TIME_SET2	0..255	The maximum time in minutes for load profile interval duration which can be contained in LP_DATA_SET2_TBL (Table 65).

NBR_BLKS_SET3	0..65535	The maximum number of interval data blocks which can be contained in LP_DATA_SET3_TBL (Table 66).

NBR_BLK_INTS_SET3	0..65535	The maximum number of intervals per data block which can be contained in LP_DATA_SET3_TBL (Table 66).

NBR_CHNS_SET3	0..255	The maximum number of channels of load profile data which can be contained in LP_DATA_SET3_TBL (Table 66).

MAX_INT_TIME_SET3	0.255	The maximum time in minutes for load profile interval duration which can be contained in LP_DATA_SET3_TBL (Table 66).

NBR_BLKS_SET4	0..65535	The maximum number of interval data blocks which can be contained in LP_DATA_SET4_TBL (Table 67).

NBR_BLK_INTS_SET4	0..65535	The maximum number of intervals per data block which can be contained in LP_DATA_SET4_TBL (Table 67).

Identifier			Value	Definition

NBR_CHNS_SET4	0..255	The maximum number of channels of load profile data which can be contained in LP_DATA_SET4_TBL (Table 67).

MAX_INT_TIME_SET4	0..255	The maximum time in minutes for load profile interval duration which can be contained in LP_DATA_SET4_TBL (Table 67).

### 9.7.2	Table 61 actual load profile table

Table 61 Data Description

ACT_LP_TBL (Table 61) contains actual values for the load profile application limiting parameters. These parameters provide for up to four independent sets of load profile data.

TABLE ACT_LP_TBL = DIM_LP_TBL.LP_SET_RCD;

Identifier			Value	Definition

LP_FLAGS_BFLD			This bit field specifies load profile list management capabilities.

LP_SET1_INHIBIT_OVF_FLAG

FALSE	End device is not inhibiting load profile set 1 once an overflow occurs.

TRUE	End device is inhibiting load profile set 1 once an overflow occurs.

LP_SET2_INHIBIT_OVF_FLAG

FALSE	End device is not inhibiting load profile set 2 once an overflow occurs.

TRUE	End device is inhibiting load profile set 2 once an overflow occurs.

LP_SET3_INHIBIT_OVF_FLAG

FALSE	End device is not inhibiting load profile set 3 once an overflow occurs.

TRUE	End device is inhibiting load profile set 3 once an overflow occurs.

LP_SET4_INHIBIT_OVF_FLAG

FALSE	End device is not inhibiting load profile set 4 once an overflow occurs.

TRUE	End device is inhibiting load profile set 4 once an overflow occurs.

blk_end_read_flag	fALse	The end device is not providing block register reading information.

TRUE	The end device is providing block register reading information.

Identifier			Value	Definition

blk_end_pulse_flag	FALSE	The end device does not have a running pulse accumulator.

TRUE	The end device does have a running pulse accumulator.

SCALAR_DIVISOR_FLAG_SET1

FALSE	The end device does not have scalars and divisors associated with set 1 load profile interval data.

TRUE	The end device does have scalars and divisors associated with set 1 load profile interval data.

SCALAR_DIVISOR_FLAG_SET2

FALSE	The end device does not have scalars and divisors associated with set 2 load profile interval data.

TRUE	The end device has scalars and divisors associated with set 2 load profile interval data.

SCALAR_DIVISOR_FLAG_SET3

FALSE	The end device does not have scalars and divisors associated with set 3 load profile interval data.

TRUE	The end device does have scalars and divisors associated with set 3 load profile interval data.

SCALAR_DIVISOR_FLAG_SET4

FALSE	The end device does not have scalars and divisors associated with set 4 load profile interval data.

TRUE	The end device does have scalars and divisors associated with set 4 load profile interval data.

EXTENDED_INT_STATUS_FLAG

FALSE	The end device does not return extended interval status with load profile interval data.

TRUE 	The end device returns extended interval status with load profile interval data.

SIMPLE_INT_STATUS_FLAG	FALSE	The end device does not return simple interval status with load profile interval data.

TRUE 	The end device returns simple interval status with load profile interval data.

LP_FMATS_BFLD			This set of booleans specifies the format(s) in use in LP_CTRL_TBL (Table 62).

INV_UINT8_FLAG		FALSE	UINT8 format can not be in use.

TRUE	An interval format of UINT8  is being used.

INV_UINT16_FLAG		FALSE	UINT16 format can not be in use.

TRUE	An interval format of UINT16 is being used.

Identifier			Value	Definition

INV_UINT32_FLAG		FALSE	UINT32 format can not be in use.

TRUE	An interval format of UINT32 can be used.

INV_INT8_FLAG		FALSE	INT8 format can not be in use.

TRUE	An interval format of INT8 is being used.

INV_INT16_FLAG		FALSE	INT16 format can not be in use.

TRUE	An interval format of INT16 is being used.

INV_INT32_FLAG		FALSE	INT32 format can not be in use.

TRUE	An interval format of INT32 is being used.

INV_NI_FMAT1_FLAG	FALSE	NI_FMAT1 format can not be in use.

TRUE	An interval format of NI_FMAT1 is being used.

INV_NI_FMAT2_FLAG	FALSE	NI_FMAT2 format can not be in use.

TRUE	An interval format of NI_FMAT2 is being used.

LP_SET_RCD				The information defining how each set of load profile information works.

LP_MEMORY_LEN 	0..4,294,967,295

The current number of octets of storage being used for load profile data. This reflects the combined sizes of tables LP_DATA_SET1_TBL (Table 64), LP_DATA_SET2_TBL (Table 65), LP_DATA_SET3_TBL (Table 66), and LP_DATA_SET4_TBL (Table 67).

LP_FLAGS			See LP_FLAGS_BFLD above.

LP_FMATS			See LP_FMATS_BFLD above.

NBR_BLKS_SET1	0..65535	The actual number of interval data blocks in use in LP_DATA_SET1_TBL (Table 64).

NBR_BLK_INTS_SET1	0..65535	The actual number of intervals per data block contained in LP_DATA_SET1_TBL (Table 64).

NBR_CHNS_SET1	0..255	The actual number of channels of load profile data contained in LP_DATA_SET1_TBL (Table 64).

MAX_INT_TIME_SET1	0..255	The actual interval duration in minutes for load profile contained in LP_DATA_SET1_TBL (Table 64).

NBR_BLKS_SET2	0..65535	The actual number of interval data blocks in use in LP_DATA_SET2_TBL (Table 65).

NBR_BLK_INTS_SET2	0..65535	The actual number of intervals per data block contained in LP_DATA_SET2_TBL (Table 65).

Identifier			Value	Definition

NBR_CHNS_SET2	0..255	The actual number of channels of load profile data contained in LP_DATA_SET2_TBL (Table 65).

MAX_INT_TIME_SET2	0..255	The actual interval duration in minutes for load profile contained in LP_DATA_SET2_TBL (Table 65).

NBR_BLKS_SET3	0..65535	The actual number of interval data blocks in use in LP_DATA_SET3_TBL (Table 66).

NBR_BLK_INTS_SET3	0..65535	The actual number of intervals per data block contained in LP_DATA_SET3_TBL (Table 66).

NBR_CHNS_SET3	0..255	The actual number of channels of load profile data contained in LP_DATA_SET3_TBL (Table 66).

MAX_INT_TIME_SET3	0..255	The actual interval duration in minutes for load profile contained in LP_DATA_SET3_TBL (Table 66).

NBR_BLKS_SET4	0..65535	The actual number of interval data blocks in use in LP_DATA_SET4_TBL (Table 67).

NBR_BLK_INTS_SET4	0..65535	The actual number of intervals per data block contained in LP_DATA_SET4_TBL (Table 67).

NBR_CHNS_SET4	0..255	The actual number of channels of load profile data contained in LP_DATA_SET4_TBL (Table 67).

MAX_INT_TIME_SET4	0..255	The actual interval duration in minutes for load profile contained in LP_DATA_SET4_TBL (Table 67).

### 9.7.3	Table 62 load profile control table

Table 62 Data Description

LP_CTRL_TBL (Table 62) defines the data sources and formats used in the collection of load profile data.

type LP_CTRL_FLAGS_bfld = bIT FIELD OF uint8

end_rdg_FLAG		: BOOL(0);

FILLER				: FILL(1..7);

end;

TYPE LP_SOURCE_SEL_RCD = PACKED RECORD

CHNL_FLAG				: LP_CTRL_FLAGS_bfld;

LP_SOURCE_SELECT			: UINT8;

END_BLK_RDG_SOURCE_SELECT	: UINT8;

END;

TYPE DATA_SELECTION_RCD = PACKED RECORD

IF  GEN_CONFIG_TBL.STD_TBLS_USED.LP_DATA_SET1_TBL THEN

LP_SEL_SET1		   : ARRAY[ACT_LP_TBL.NBR_CHNS_SET1] OF 								LP_SOURCE_SEL_RCD;

INT_FMT_CDE1	   : UINT8;

IF ACT_LP_TBL.SCALAR_DIVISOR_FLAG_SET1 THEN

SCALARS_SET1 : ARRAY[ACT_LP_TBL.NBR_CHNS_SET1] OF UINT16;

DIVISOR_SET1   : ARRAY[ACT_LP_TBL.NBR_CHNS_SET1] OF UINT16;

END;

END;

IF  GEN_CONFIG_TBL.STD_TBLS_USED.LP_DATA_SET2_TBL THEN

LP_SEL_SET2		    : ARRAY[ACT_LP_TBL.NBR_CHNS_SET2] OF 								LP_SOURCE_SEL_RCD;

INT_FMT_CDE2	    : UINT8;

IF ACT_LP_TBL.SCALAR_DIVISOR_FLAG_SET2 THEN

SCALARS_SET2  : ARRAY[ACT_LP_TBL.NBR_CHNS_SET2] OF UINT16;

DIVISOR_SET2    : ARRAY[ACT_LP_TBL.NBR_CHNS_SET2] OF UINT16;

END;

END;

IF  GEN_CONFIG_TBL.STD_TBLS_USED.LP_DATA_SET3_TBL THEN

LP_SEL_SET3		    : ARRAY[ACT_LP_TBL.NBR_CHNS_SET3] OF 								LP_SOURCE_SEL_RCD;

INT_FMT_CDE3	    : UINT8;

IF ACT_LP_TBL.SCALAR_DIVISOR_FLAG_SET3 THEN

SCALARS_SET3  : ARRAY[ACT_LP_TBL.NBR_CHNS_SET3] OF UINT16;

DIVISOR_SET3    : ARRAY[ACT_LP_TBL.NBR_CHNS_SET3] OF UINT16;

END;

END;

IF  GEN_CONFIG_TBL.STD_TBLS_USED.LP_DATA_SET4_TBL THEN

LP_SEL_SET4		    : ARRAY[ACT_LP_TBL.NBR_CHNS_SET4] OF 								LP_SOURCE_SEL_RCD;

INT_FMT_CDE4	    : UINT8;

IF ACT_LP_TBL.SCALAR_DIVISOR_FLAG_SET4 THEN

SCALARS_SET4  : ARRAY[ACT_LP_TBL.NBR_CHNS_SET4] OF UINT16;

DIVISOR_SET4    : ARRAY[ACT_LP_TBL.NBR_CHNS_SET4] OF UINT16;

END;

END;

END;

TABLE LP_CTRL_TBL = DATA_SELECTION_RCD;

Identifier			Value	Definition

LP_CTRL_FLAGS_BFLD

END_RDG_FLAG	FALSE	The channel does not have an associated end reading.

TRUE	The channel does have an associated end reading.

LP_SOURCE_SEL_RCD

CHNL_FLAG			Flags associated with a particular channel.

Identifier			Value	Definition

INT_SOURCE_SELECT	0..255	This is an index into SOURCES_TBL (Table 16) that identifies source of the interval data for a specific channel.

END_BLK_RDG_SOURCE_SELECT

0..255	This is an index into SOURCES_TBL (TABLE 16) that identifies source of the block end time reading data for a specific channel.

DATA_SELECTION_RCD		Record that stores all information concerning each of the selected channels.

LP_SEL_SET1			This is an array of records containing indices into the SOURCES_TBL (TABLE 16) that identifies sources of data for each channel of interval data in LP_DATA_SET1_TBL (Table 64).

INT_FMT_CDE1		This is a single code selecting the format for all interval data in LP_DATA_SET1_TBL (Table 64). These codes are defined as follows

1	UINT8

2	UINT16

4	UINT32

8	INT8

16	INT16

32	INT32

64	NI_FMAT1

128	NI_FMAT2
All other code values are currently undefined.

SCALARS_SET1		An array of scalars applied to interval data before recording pulse data in load profile set 1.

DIVISORS_SET1		An array of divisors applied to interval data before recording pulse data in load profile set 1.

LP_SEL_SET2			This is an array of records containing indices into the SOURCES_TBL (TABLE 16) that identifies sources of data for each channel of interval data in LP_DATA_SET2_TBL (Table 65).

INT_FMT_CDE2		This is a single code selecting the format for all interval data in LP_DATA_SET2_TBL (Table 65). These codes are defined as follows

1	UINT8

2	UINT16

4	UINT32

8	INT8

16	INT16

32	INT32

64	NI_FMAT1

128	NI_FMAT2
All other code values are currently undefined.

Identifier			Value	Definition

SCALARS_SET2		An array of scalars applied to interval data before recording pulse data in load profile set 2.

DIVISORS_SET2		An array of divisors applied to interval data before recording pulse data in load profile set 2.

LP_SEL_SET3			This is an array of records containing indices into the SOURCES_TBL (TABLE 16) that identifies sources of data for each channel of interval data in LP_DATA_SET3_TBL (Table 66).

INT_FMT_CDE3		This is a single code selecting the format for all interval data in LP_DATA_SET3_TBL (Table 66). These codes are defined as follows

1	UINT8

2	UINT16

4	UINT32

8	INT8

16	INT16

32	INT32

64	NI_FMAT1

128	NI_FMAT2
All other code values are currently undefined.

SCALARS_SET3		An array of scalars applied to interval data before recording pulse data in load profile set 3.

DIVISORS_SET3		An array of divisors applied to interval data before recording pulse data in load profile set 3.

LP_SEL_SET4			This is an array of records containing indices into the SOURCES_TBL (TABLE 16) that identifies sources of data for each channel of interval data in LP_DATA_SET4_TBL (Table 67).

INT_FMT_CDE4		This is a single code selecting the format for all interval data in LP_DATA_SET4_TBL (Table 67). These codes are defined as follows

1	UINT8

2	UINT16

4	UINT32

8	INT8

16	INT16

32	INT32

64	NI_FMAT1

128	NI_FMAT2
All other code values are currently undefined.

SCALARS_SET4		An array of scalars applied to interval data before recording pulse data in load profile set 4.

DIVISORS_SET4		An array of divisors applied to interval data before recording pulse data in load profile set 4.

### 9.7.4	Table 63 load profile status table

Table 63 Data Description

LP_STATUS_TBL (Table 63) contains the status of each load profile data set.

TYPE LP_SET_STATUS_BFLD = BIT FIELD OF UINT8

BLOCK_ORDER				: UINT(0..0);

OVERFLOW_FLAG				: BOOL(1);

LIST_TYPE					: UINT(2..2);

BLOCK_INHIBIT_OVERFLOW_FLAG		: BOOL(3);

INTERVAL_ORDER				: UINT(4..4);

ACTIVE_MODE_FLAG				: BOOL(5);

TEST_MODE					: UINT(6..6);

FILLER						: FILL(7..7);

END;

TYPE LP_SET_STATUS_RCD = PACKED RECORD

LP_SET_STATUS_FLAGS	: LP_SET_STATUS_BFLD;

NBR_VALID_BLOCKS		: UINT16;

LAST_BLOCK_ELEMENT	: UINT16;

LAST_BLOCK_SEQ_NBR	: UINT32;

NBR_UNREAD_BLOCKS	: UINT16;

NBR_VALID_INT		: UINT16;

END;

TYPE LP_STATUS_RCD = PACKED RECORD

IF  GEN_CONFIG_TBL.STD_TBLS_USED.LP_DATA_SET1_TBL_CNST THEN

LP_STATUS_SET1	: LP_SET_STATUS_RCD;

END;

IF  GEN_CONFIG_TBL.STD_TBLS_USED.LP_DATA_SET2_TBL_CNST THEN

LP_STATUS_SET2	: LP_SET_STATUS_RCD;

END;

IF  GEN_CONFIG_TBL.STD_TBLS_USED.LP_DATA_SET3_TBL_CNST THEN

LP_STATUS_SET3	: LP_SET_STATUS_RCD;

END;

IF  GEN_CONFIG_TBL.STD_TBLS_USED.LP_DATA_SET4_TBL_CNST THEN

LP_STATUS_SET4	: LP_SET_STATUS_RCD;

END;

END;

TABLE LP_STATUS_TBL = LP_STATUS_RCD;

Identifier			Value	Definition

LP_SET_STATUS_BFLD

BLOCK_ORDER	0	Blocks of load profile data are transported in ascending order (N is older than N+1).

1	Blocks of load profile data are transported in descending order (N is newer than N+1).

Identifier			Value	Definition

OVERFLOW_FLAG	FALSE	Overflow has not occurred.

TRUE	An attempt was made to enter an interval in a new data block such that the number of unread blocks exceeded the actual number of possible blocks in load profile storage.

LIST_TYPE		0	FIFO (First In First Out) as placed in load profile storage.

1	Circular list as placed in load profile storage.

BLOCK_INHIBIT_OVERFLOW_FLAG	The same value as ACT_LP_TBL.LP_SETn_INHIBIT_OVF_FLAG.

INTERVAL_ORDER	0	Intervals in each block of load profile are transported in ascending order (N is older than N+1).

1	Intervals in each block of load profile are transported in descending order (N is newer than N+1).

ACTIVE_MODE_FLAG	FALSE	This data set is not collecting data.

TRUE	This data set is collecting data.

TEST_MODE		0	This data set is in the normal mode.

1	This data set is in the test mode.

LP_SET_STATUS_RCD

LP_SET_STATUS_FLAGS		See LP_SET_STATUS_BFLD.

NBR_VALID_BLOCKS	0..65535	Number of valid load profile data blocks in load profile data tables LP_DATA_SET1_TBL (Table 64), LP_DATA_SET2_TBL (Table 65), LP_DATA_SET3_TBL (Table 66), and LP_DATA_SET4_TBL (Table 67), load profile block arrays.  The range is zero (meaning no data blocks in load profile Data Table) to the actual dimension of the number of load profile data blocks.  The block is considered valid when at least one interval is written.

LAST_BLOCK_ELEMENT	0..65535	The array element of the newest valid data block in the load profile data array. This field is valid only if NBR_VALID_BLOCKS is greater than zero.

LAST_BLOCK_SEQ_NBR  	0..4,294,967,295

The sequence number (LP_SEQ_NBR) of the last element (LAST_BLOCK_ELEMENT) in the load profile data array.

NBR_UNREAD_BLOCKS	0..65535	The number of load profile blocks that have not been read.  This number is only updated through a procedure.

Identifier			Value	Definition

NBR_VALID_INT	0..65535	Number of valid intervals stored in the last load profile block array. The range is zero (meaning no interval in the array) to the actual dimension of the number of intervals per block.

LP_STATUS_RCD

LP_STATUS_SET1		Status information for profile data set 1.

LP_STATUS_SET2		Status information for profile data set 2.

LP_STATUS_SET3		Status information for profile data set 3.

LP_STATUS_SET4		Status information for profile data set 4.

### 9.7.5	Table 64 load profile data set 1 table

Table 64 Data Description

LP_DATA_SET1_TBL (Table 64) contains information on load profile data set one. The parameters are as follows:

TYPE INT_FMT1_RCD = PACKED RECORD

CASE LP_CTRL_TBL.INT_FMT_CDE1 OF

1	:	ITEM	: UINT8;

2	:	ITEM	: UINT16;

4	:	ITEM	: UINT32;

8	:	ITEM	: INT8;

16	:	ITEM	: INT16;

32	:	ITEM	: INT32;

64	:	ITEM	: NI_FMAT1;

128	:	ITEM	: NI_FMAT2;

END;

END;

TYPE INT_SET1_RCD = PACKED RECORD

IF ACT_LP_TBL.EXTENDED_INT_STATUS_FLAG THEN

EXTENDED_INT_STATUS

: ARRAY[(ACT_LP_TBL.NBR_CHNS_SET1/2)+1] OF UINT8;

END;

INT_DATA	: ARRAY[ACT_LP_TBL.NBR_CHNS_SET1] OF INT_FMT1_RCD;

END;

TYPE READINGS_RCD = PACKED RECORD

IF ACT_LP_TBL.BLK_END_READ_FLAG THEN

BLOCK_END_READ	: NI_FMAT1;

END;

IF ACT_LP_TBL.BLK_END_PULSE_FLAG THEN

BLOCK_END_PULSE	: UINT32;

END;

END;

TYPE LP_BLK1_DAT_RCD = PACKED RECORD

BLK_END_TIME	: STIME_DATE;

END_READINGS	: ARRAY[ACT_LP_TBL.NBR_CHNS_SET1] OF READINGS_RCD;

IF ACT_LP_TBL.SIMPLE_INT_STATUS_FLAG THEN

SIMPLE_INT_STATUS 	: SET((ACT_LP_TBL.NBR_BLK_INTS_SET1+7)/8);

END;

LP_INT			: ARRAY[ACT_LP_TBL.NBR_BLK_INTS_SET1] OF 								INT_SET1_RCD;

END;

TYPE LP_DATA_SET1_RCD = PACKED RECORD

LP_DATA_SETS1	: ARRAY[ACT_LP_TBL.NBR_BLKS_SET1] OF 								LP_BLK1_DAT_RCD;

END;

TABLE LP_DATA_SET1_TBL = LP_DATA_SET1_RCD;

Identifier			Value	Definition

INT_FMT1_RCD			Selector for the format of the channel data.

INT_SET1_RCD

EXTENDED INT_STATUS		This is one or more single octets of interval status conditions provided for all channels. One nibble (4 bits) of status information are provided for each channel in the set, plus one nibble for status conditions common to all channels. This common status nibble is always the first nibble of the set. (That is, the high order 4 bits of the first octet of EXTENDED_INT_STATUS). Since EXTENDED_INT_STATUS is an integer number of octets in length, this field contains one nibble of FILL if the number of channels in the set is even. This fill field, when present always occupies the last nibble of EXTENDED_INT_STATUS. (That is, the low order 4 bits of the last octet of EXTENDED_INT_STATUS).

The contents of the channel status nibble is a binary value defined as follows:

0	No status flag

1	Overflow

2	Partial interval due to common state

3	Long interval due to common state

4	Skipped interval due to common state

5	Interval contains test mode data

6..15	Undefined

The contents of the common status nibble are unitary flags defined as follows:

0	Daylight savings time is in effect during or at start of interval

1	Power fail within interval

2	Clock reset forward during interval

3	Clock reset backwards during interval

Identifier			Value	Definition

INT_DATA			This is an array of interval values for each channel in the block, recorded at a single time. Channels are presented in the same order. The order of the channels matches their definition in LP_CTRL_TBL (Table 62).

READINGS_RCD

BLOCK_END_READ		The value of the block end reading both data and readings.

BLOCK_END_PULSE	0..65355	The values of the accumulator at the end of a user defined interval.

LP_BLK1_DAT_RCD

BLK_END_TIME		This parameter contains the ending date and time of the last interval of data entered in this data block.

END_READINGS		This is an array of readings of the end reading sources, taken at the interval end time of the last interval of data entered in the block. One end reading is provided for each channel in the block. The order of the readings matches their definition in LP_CTRL_TBL (Table 62). The format is controlled by READING_RCD.

SIMPLE_INT_STATUS		This is a set of status bits, one per interval, that specifies whether the corresponding interval is valid.

LP_INT				This is an array of interval records in the block. Intervals are stored in an chronological order, specified by INTERVAL_ORDER, with the oldest reading set appearing in the first record.

LP_DATA_SETS_RCD			This is an array of load profile data blocks.

LP_DATA_SETS1		This array contains the function limiting information about this load profile data set.

### 9.7.6	Table 65 load profile data set 2 table

Table 65 Data Description

LP_DATA_SET2_TBL (Table 65) contains information on load profile data set two. The parameters are as follows:

TYPE INT_FMT2_RCD = PACKED RECORD

CASE LP_CTRL_TBL.INT_FMT_CDE2 OF

1	:	ITEM	: UINT8;

2	:	ITEM	: UINT16;

4	:	ITEM	: UINT32;

8	:	ITEM	: INT8;

16	:	ITEM	: INT16;

32	:	ITEM	: INT32;

64	:	ITEM	: NI_FMAT1;

128	:	ITEM	: NI_FMAT2;

END;

END;

TYPE INT_SET2_RCD = PACKED RECORD

IF ACT_LP_TBL.EXTENDED_INT_STATUS_FLAG THEN

EXTENDED_INT_STATUS

: ARRAY[(ACT_LP_TBL.NBR_CHNS_SET2 / 2)+1] OF UINT8;

END;

INT_DATA	: ARRAY[ACT_LP_TBL.NBR_CHNS_SET2] OF INT_FMT2_RCD;

END;

TYPE READINGS_RCD = PACKED RECORD

IF ACT_LP_TBL.BLK_END_READ_FLAG THEN

BLOCK_END_READ	: NI_FMAT1;

END;

IF ACT_LP_TBL.BLK_END_PULSE_FLAG THEN

BLOCK_END_PULSE	: UINT32;

END;

END;

TYPE LP_BLK2_DAT_RCD = PACKED RECORD

BLK_END_TIME	: STIME_DATE;

END_READINGS	: ARRAY[ACT_LP_TBL.NBR_CHNS_SET2] OF READINGS_RCD;

IF ACT_LP_TBL.SIMPLE_INT_STATUS_FLAG THEN

SIMPLE_INT_STATUS 	: SET((ACT_LP_TBL.NBR_BLK_INTS_SET2+7)/8);

END;

LP_INT		: ARRAY[ACT_LP_TBL.NBR_BLK_INTS_SET2] OF 								INT_SET2_RCD;

END;

TYPE LP_DATA_SET2_RCD = PACKED RECORD

LP_DATA_SETS2	: ARRAY[ACT_LP_TBL.NBR_BLKS_SET2] OF 								LP_BLK2_DAT_RCD;

END;

TABLE LP_DATA_SET2_TBL = LP_DATA_SET2_RCD;

Identifier			Value	Definition

INT_FMT2_RCD			Selector for the format of the channel data.

INT_SET2_RCD

EXTENDED_INT_STATUS		This is one or more single octets of interval status conditions provided for all channels. One nibble (4 bits) of status information are provided for each channel in the set, plus one nibble for status conditions common to all channels. This common status nibble is always the first nibble of the set. (That is, the high order 4 bits of the first octet of EXTENDED_INT_STATUS). Since EXTENDED_INT_STATUS is an integer number of octets in length, this field contains one nibble of FILL if the number of channels in the set is even. This fill field, when present always occupies the last nibble of EXTENDED_INT_STATUS. (That is, the low order 4 bits of the last octet of EXTENDED_INT_STATUS).

The contents of the channel status nibble is a binary value defined as follows:

0	No status flag

1	Overflow

2	Partial interval due to common state

3	Long interval due to common state

4	Skipped interval due to common state

5	Interval contains test mode data

6..15	Undefined

The contents of the common status nibble are unitary flags defined as follows:

0	Daylight savings time is in effect during or at start of interval

1	Power fail within interval

2	Clock reset forward during interval

3	Clock reset backwards during interval

INT_DATA			This is an array of interval values for each channel in the block, recorded at a single time. Channels are presented in the same order. The order of the channels matches their definition in LP_CTRL_TBL (Table 62).

READINGS_RCD

BLOCK_END_READ		The value of the block end reading both data and readings.

BLOCK_END_PULSE	0..65355	The values of the accumulator at the end of a user defined interval.

Identifier			Value	Definition

LP_BLK2_DAT_RCD

BLK_END_TIME		This parameter contains the ending date and time of the last interval of data entered in this data block.

END_READINGS		This is an array of readings of the end reading sources, taken at the interval end time of the last interval of data entered in the block. One end reading is provided for each channel in the block. The order of the readings matches their definition in LP_CTRL_TBL (Table 62). The format is controlled by READING_RCD.

SIMPLE_INT_STATUS		This is a set of status bits, one per interval, that specifies whether the corresponding interval is valid.

LP_INT				This is an array of interval records in the block. Intervals are stored in an chronological order, specified by INTERVAL_ORDER, with the oldest reading set appearing in the first record.

LP_DATA_SETS_RCD			This is an array of load profile data blocks.

LP_DATA_SETS2		This array contains the function limiting information about this load profile data set.

### 9.7.7	Table 66 load profile data set 3 table

Table 66 Data Description

LP_DATA_SET3_TBL (Table 66) contains information on load profile data set three.

The parameters are as follows:

TYPE INT_FMT3_RCD = PACKED RECORD

CASE LP_CTRL_TBL.INT_FMT_CDE3 OF

1	:	ITEM	: UINT8;

2	:	ITEM	: UINT16;

4	:	ITEM	: UINT32;

8	:	ITEM	: INT8;

16	:	ITEM	: INT16;

32	:	ITEM	: INT32;

64	:	ITEM	: NI_FMAT1;

128	:	ITEM	: NI_FMAT2;

END;

END;

TYPE INT_SET3_RCD = PACKED RECORD

IF ACT_LP_TBL.EXTENDED_INT_STATUS_FLAG THEN

EXTENDED_INT_STATUS :

ARRAY[(ACT_LP_TBL.NBR_CHNS_SET3 / 2)+1] OF UINT8;

END;

INT_DATA	: ARRAY[ACT_LP_TBL.NBR_CHNS_SET3] OF INT_FMT3_RCD;

END;

TYPE READINGS_RCD = PACKED RECORD

IF ACT_LP_TBL.BLK_END_READ_FLAG THEN

BLOCK_END_READ	: NI_FMAT1;

END;

IF ACT_LP_TBL.BLK_END_PULSE_FLAG THEN

BLOCK_END_PULSE	: UINT32;

END;

END;

TYPE LP_BLK3_DAT_RCD = PACKED RECORD

BLK_END_TIME	: STIME_DATE;

END_READINGS	: ARRAY[ACT_LP_TBL.NBR_CHNS_SET3] OF READINGS_RCD;

IF ACT_LP_TBL.SIMPLE_INT_STATUS_FLAG THEN

SIMPLE_INT_STATUS 	: SET((ACT_LP_TBL.NBR_BLK_INTS_SET3+7)/8);

END;

LP_INT		: ARRAY[ACT_LP_TBL.NBR_BLK_INTS_SET3] OF 								INT_SET3_RCD;

END;

TYPE LP_DATA_SET3_RCD = PACKED RECORD

LP_DATA_SETS3	: ARRAY[ACT_LP_TBL.NBR_BLKS_SET3] OF 								LP_BLK3_DAT_RCD;

END;

TABLE LP_DATA_SET3_TBL = LP_DATA_SETS_RCD;

Identifier			Value	Definition

INT_FMT3_RCD			Selector for the format of the channel data.

INT_SET3_RCD

EXTENDED_INT_STATUS		This is one or more single octets of interval status conditions provided for all channels. One nibble (4 bits) of status information are provided for each channel in the set, plus one nibble for status conditions common to all channels. This common status nibble is always the first nibble of the set. (That is, the high order 4 bits of the first octet of EXTENDED_INT_STATUS). Since EXTENDED_INT_STATUS is an integer number of octets in length, this field contains one nibble of FILL if the number of channels in the set is even. This fill field, when present always occupies the last nibble of EXTENDED_INT_STATUS. (That is, the low order 4 bits of the last octet of EXTENDED_INT_STATUS).

Identifier			Value	Definition

The contents of the channel status nibble is a binary value defined as follows:

0	No status flag

1	Overflow

2	Partial interval due to common state

3	Long interval due to common state

4	Skipped interval due to common state

5	Interval contains test mode data

6..15	Undefined

The contents of the common status nibble are unitary flags defined as follows:

0	Daylight savings time is in effect during or at start of interval

1	Power fail within interval

2	Clock reset forward during interval

3	Clock reset backwards during interval

INT_DATA			This is an array of interval values for each channel in the block, recorded at a single time. Channels are presented in the same order. The order of the channels matches their definition in LP_CTRL_TBL (Table 62).

READINGS_RCD

BLOCK_END_READ		The value of the block end reading both data and readings.

BLOCK_END_PULSE	0..65355	The values of the accumulator at the end of a user defined interval.

LP_BLK3_DAT_RCD

BLK_END_TIME		This parameter contains the ending date and time of the last interval of data entered in this data block.

END_READINGS		This is an array of readings of the end reading sources, taken at the interval end time of the last interval of data entered in the block. One end reading is provided for each channel in the block. The order of the readings matches their definition in LP_CTRL_TBL (Table 62). The format is controlled by READING_RCD.

SIMPLE_INT_STATUS		This is a set of status bits, one per interval, that specifies whether the corresponding interval is valid.

LP_INT				This is an array of interval records in the block. Intervals are stored in an chronological order, specified by INTERVAL_ORDER, with the oldest reading set appearing in the first record.

Identifier			Value	Definition

LP_DATA_SETS_RCD			This is an array of load profile data blocks.

LP_DATA_SETS3		This array contains the function limiting information about this load profile data set.

### 9.7.8	Table 67 load profile data set 4 table

Table 67 Data Description

LP_DATA_SET4_TBL (Table 67) contains information on load profile data set four.

The parameters are as follows:

TYPE INT_FMT4_RCD = PACKED RECORD

CASE LP_CTRL_TBL.INT_FMT_CDE4 OF

1	:	ITEM	: UINT8;

2	:	ITEM	: UINT16;

4	:	ITEM	: UINT32;

8	:	ITEM	: INT8;

16	:	ITEM	: INT16;

32	:	ITEM	: INT32;

64	:	ITEM	: NI_FMAT1;

128	:	ITEM	: NI_FMAT2;

END;

END;

TYPE INT_SET4_RCD = PACKED RECORD

IF ACT_LP_TBL.EXTENDED_INT_STATUS_FLAG THEN

EXTENDED_INT_STATUS

: ARRAY[(ACT_LP_TBL.NBR_CHNS_SET4 / 2)+1] OF UINT8;

END;

INT_DATA	: ARRAY[ACT_LP_TBL.NBR_CHNS_SET4] OF INT_FMT4_RCD;

END;

TYPE READINGS_RCD = PACKED RECORD

IF ACT_LP_TBL.BLK_END_READ_FLAG THEN

BLOCK_END_READ	: NI_FMAT1;

END:

IF ACT_LP_TBL.BLK_END_PULSE_FLAG THEN

BLOCK_END_PULSE	: UINT32;

END:

END;

TYPE LP_BLK4_DAT_RCD = PACKED RECORD

BLK_END_TIME	: STIME_DATE;

END_READINGS	: ARRAY[ACT_LP_TBL.NBR_CHNS_SET4] OF READINGS_RCD;

IF ACT_LP_TBL.SIMPLE_INT_STATUS_FLAG THEN

SIMPLE_INT_STATUS 	: SET((ACT_LP_TBL.NBR_BLK_INTS_SET4+7)/8);

END;

LP_INT		: ARRAY[ACT_LP_TBL.NBR_BLK_INTS_SET4] OF 							INT_SET4_RCD;

END;

TYPE LP_DATA_SET4_RCD = PACKED RECORD

LP_DATA_SETS4	: ARRAY[ACT_LP_TBL.NBR_BLKS_SET4] OF 								LP_BLK4_DAT_RCD;

END;

TABLE LP_DATA_SET4_TBL = LP_DATA_SET4_RCD;

Identifier			Value	Definition

INT_FMT4_RCD			Selector for the format of the channel data.

INT_SET4_RCD

EXTENDED_INT_STATUS		This is one or more single octets of interval status conditions provided for all channels. One nibble (4 bits) of status information are provided for each channel in the set, plus one nibble for status conditions common to all channels. This common status nibble is always the first nibble of the set. (That is, the high order 4 bits of the first octet of EXTENDED_INT_STATUS). Since EXTENDED_INT_STATUS is an integer number of octets in length, this field contains one nibble of FILL if the number of channels in the set is even. This fill field, when present always occupies the last nibble of EXTENDED_INT_STATUS. (That is, the low order 4 bits of the last octet of EXTENDED_INT_STATUS).

The contents of the channel status nibble is a binary value defined as follows:

0	No status flag

1	Overflow

2	Partial interval due to common state

3	Long interval due to common state

4	Skipped interval due to common state

5	Interval contains test mode data

6..15	Undefined

The contents of the common status nibble are unitary flags defined as follows:

0	Daylight savings time is in effect during or at start of interval

1	Power fail within interval

2	Clock reset forward during interval

3	Clock reset backwards during interval

INT_DATA			This is an array of interval values for each channel in the block, recorded at a single time. Channels are presented in the same order. The order of the channels matches their definition in LP_CTRL_TBL (Table 62).

Identifier			Value	Definition

READINGS_RCD

BLOCK_END_READ		The value of the block end reading both data and readings.

BLOCK_END_PULSE	0..65355	The values of the accumulator at the end of a user defined interval.

LP_BLK4_DAT_RCD

BLK_END_TIME		This parameter contains the ending date and time of the last interval of data entered in this data block.

END_READINGS		This is an array of readings of the end reading sources, taken at the interval end time of the last interval of data entered in the block. One end reading is provided for each channel in the block. The order of the readings matches their definition in LP_CTRL_TBL (Table 62). The format is controlled by READING_RCD.

SIMPLE_INT_STATUS		This is a set of status bits, one per interval, that specifies whether the corresponding interval is valid.

LP_INT				This is an array of interval records in the block. Intervals are stored in an chronological order, specified by INTERVAL_ORDER, with the oldest reading set appearing in the first record.

LP_DATA_SETS_RCD			This is an array of load profile data blocks.

LP_DATA_SETS4		This array contains the function limiting information about this load profile data set.

## 9.8	Decade 70:  history & event logs

This decade contains the tables associated with the maintenance of the History and Event Logs.

### 9.8.1	Table 70 dimension log table

Table 70 Data Description

DIM_LOG_TBL (Table 70) defines the maximum size and capabilities of the History and Event Log decade.

TYPE LOG_FLAGS_BFLD = BIT FIELD OF UINT8

EVENT_NUMBER_FLAG		:  BOOL(0);

HIST_DATE_TIME_FLAG		:  BOOL(1);

HIST_SEQ_NBR_FLAG		:  BOOL(2);

HIST_INHIBIT_OVF_FLAG		:  BOOL(3);

EVENT_INHIBIT_OVF_FLAG		:  BOOL(4);

FILLER					:  FILL(5..7);

END;

TYPE LOG_RCD = PACKED RECORD

LOG_FLAGS			: LOG_FLAGS_BFLD;

NBR_STD_EVENTS		: UINT8;

NBR_MFG_EVENTS		: UINT8;

HIST_DATA_LENGTH		: UINT8;

EVENT_DATA_LENGTH	: UINT8;

NBR_HISTORY_ENTRIES	: UINT16;

NBR_EVENT_ENTRIES	: UINT16;

END;

TABLE DIM_LOG_TBL = LOG_RCD;

Identifier			Value	Definition

LOG_FLAGS_BFLD

EVENT_NUMBER_FLAG	FALSE	A common event number can not be maintained in the History & Event Logs.

TRUE	A common event number can be maintained in the History & Event Logs.

HIST_DATE_TIME_FLAG	FALSE	Date & time can not be maintained in the History Log.

TRUE	Date & time can be maintained in the History Log.

HIST_SEQ_NBR_FLAG	FALSE	A sequence number can not be transported through the History Log.

TRUE	A sequence number can be transported through the History Log.

HIST_INHIBIT_OVF_FLAG  	FALSE	History Log is not capable of inhibiting overflow.

TRUE	History Log is capable of inhibiting overflow.

EVENT_INHIBIT_OVF_FLAG	FALSE	Event Log is not capable of being blocked.

TRUE	Event Log is capable of being blocked.

TYPE LOG_RCD

LOG_FLAGS			See LOG_FLAGS_BFLD above.

NBR_STD_EVENTS	0..255	Maximum number of octets in the set  EVENTS_SUPPORTED_TBL.-STD_EVENTS_SUPPORTED (Table 72).

NBR_MFG_EVENTS	0..255	Maximum number of octets in the set EVENTS_SUPPORTED_TBL.-MFG_EVENTS_SUPPORTED (Table 72).

HIST_DATA_LENGTH	0..255	Maximum number of octets in the HISTORY_LOG_DATA_TBL.-HISTORY_ARGUMENT (Table 74).

EVENT_DATA_LENGTH	0..255	Maximum number of octets in the EVENT_LOG_DATA_TBL.EVENT_ARGUMENT (Table 76).

Identifier			Value	Definition

NBR_HISTORY_ENTRIES	0..65535	Maximum number of entries in the history log in HISTORY_LOG_DATA_TBL (Table 74).

NBR_EVENT_ENTRIES	0..65535	Maximum number of entries in the event log in. EVENT_LOG_DATA_TBL (Table 76).

### 9.8.2	Table 71 actual log table

Table 71 Data Description

ACT_LOG_TBL (Table 71) defines the actual size and capabilities of the History and Event Log decade.

TABLE ACT_LOG_TBL = DIM_LOG_TBL.LOG_RCD;

Identifier			Value	Definition

LOG_FLAGS_BFLD

EVENT_NUMBER_FLAG	FALSE	A common event number is not maintained in the History & Event Logs.

TRUE	A common event number is maintained in the History & Event Logs.

HIST_DATE_TIME_FLAG	FALSE	A date & time is not maintained in the History Log.

TRUE	A date & time is maintained in the History Log.

HIST_SEQ_NBR_FLAG	FALSE	A sequence number is not transported through the History Log.

TRUE	A sequence number is transported through the History Log.

HIST_INHIBIT_OVF_FLAG

FALSE	History Log is not inhibiting new entries when an overflow condition exists.

TRUE	History Log is inhibiting new entries when an overflow condition exists.

EVENT_INHIBIT_OVF_FLAG

FALSE	Event Log is not inhibiting new entries when an overflow condition exists.

TRUE	Event Log is inhibiting new entries when an overflow condition exists.

TYPE LOG_RCD

LOG_FLAGS			See LOG_FLAG_BFLD above.

NBR_STD_EVENTS	0..255	Number of octets in the set  EVENTS_SUPPORTED_TBL.-STD_EVENTS_SUPPORTED (Table 72).

NBR_MFG_EVENTS	0..255	Number of octets in the set EVENTS_SUPPORTED_TBL.-MFG_EVENTS_SUPPORTED (Table 72).

Identifier			Value	Definition

HIST_DATA_LENGTH	0..255	Number of octets in the HISTORY_ LOG_DATA_TBL.HISTORY_ARGUMENT (Table 74).

EVENT_DATA_LENGTH	0..255	Number of octets in the EVENT_ LOG_DATA_TBL.EVENT_ARGUMENT (Table 76).

NBR_HISTORY_ENTRIES	0..65535	Actual maximum number of entries in the History Log.

NBR_EVENT_ENTRIES	0..65535	Actual maximum number of entries in the Event Log.

### 9.8.3	Table 72 events  identification table

Table 72 Data Description

EVENTS_ID_TBL (Table 72) contains the events that are supported by the end device.

TYPE EVENTS_SUPPORTED_RCD = PACKED RECORD

STD_EVENTS_SUPPORTED	: SET(ACT_LOG_TBL.NBR_STD_EVENTS);

MFG_EVENTS_SUPPORTED	: SET(ACT_LOG_TBL.NBR_MFG_EVENTS);

END;

TABLE EVENTS_ID_TBL = EVENTS_SUPPORTED_RCD;

Identifier			Value	Definition

EVENTS_SUPPORTED_RCD

STD_EVENTS_SUPPORTED		This set variable indicates which of the standard events are supported in the Event Log.  See Annex B, History & Event Log Codes, for standard event codes. Event codes are represented by bits 0 through (8 * ACT_LOG_TBL.NBR_STD_EVENTS - 1), with a 1 representing a TRUE or implemented condition and a 0 representing a FALSE or not implemented condition.

MFG_EVENTS_SUPPORTED		This set variable indicates which of the manufacturer events are supported in the Event Log.  Events  are enabled by bits 0 through (8 * ACT_LOG_TBL.NBR_MFG_EVENTS - 1), with a 1 representing a TRUE or implemented condition and a 0 representing a FALSE or not implemented condition.

### 9.8.4	Table 73 history log control table

Table 73 Data Description

HISTORY_LOG_CTRL_TBL (Table 73) defines the History Log codes to be written to the History Log.  It also defines which specific procedures and or table writes that are to be acknowledged in the History Log.  For a specific procedure or table to be acknowledged, three independent tests shall all be true:

1) The procedure or table shall be used in the end device, per the GEN_CONFIG_TBL (Table 00).

2) The appropriate History Log code shall be used, per this table.

3) The procedure or table shall be requested to be acknowledged, per this

table.

TYPE HISTORY_CTRL_RCD = PACKED RECORD

STD_EVENTS_MONITORED_FLAGS	: SET(ACT_LOG_TBL.NBR_STD_EVENTS);

MFG_EVENTS_MONITORED_FLAGS	: SET(ACT_LOG_TBL.NBR_MFG_EVENTS);

STD_TBLS_MONITORED_FLAGS  	: SET(GEN_CONFIG_TBL.DIM_STD_TBLS_USED);

MFG_TBLS_MONITORED_FLAGS  	: SET(GEN_CONFIG_TBL.DIM_MFG_TBLS_USED);

STD_PROC_MONITORED_FLAGS  	: SET(GEN_CONFIG_TBL.DIM_STD_PROC_USED);

MFG_PROC_MONITORED_FLAGS  	: SET(GEN_CONFIG_TBL.DIM_MFG_PROC_USED);

END;

TABLE HISTORY_LOG_CTRL_TBL = HISTORY_CTRL_RCD;

Identifier			Value	Definition

HISTORY_CTRL_RCD

STD_EVENTS_MONITORED_FLAGS	Bit position is linearly associated with corresponding standard event code.

FALSE	Turns off event recording for associated event code.

TRUE	Turns on event recording for associated event code.

MFG_EVENTS_MONITORED_FLAGS	Bit position is linearly associated with corresponding manufacturer event code.

FALSE	Turns off event recording for associated event code.

TRUE	Turns on event recording for associated event code.

STD_TBLS_MONITORED_FLAGS	Bit position is linearly associated with corresponding standard table number.

FALSE	Turns off event recording for associated table.

TRUE	Turns on event recording for associated table.

MFG_TBLS_MONITORED_FLAGS	Bit position is linearly associated with corresponding manufacturer table number.

FALSE	Turns off event recording for associated table.

TRUE	Turns on event recording for associated table.

Identifier			Value	Definition

STD_PROC_MONITORED_FLAGS	Bit position is linearly associated with corresponding standard procedure number.

FALSE	Turns off event recording for associated procedure.

TRUE	Turns on event recording for associated procedure.

MFG_PROC_MONITORED_FLAGS	Bit position is linearly associated with corresponding manufacturer procedure number.

FALSE	Turns off event recording for associated procedure.

TRUE	Turns on event recording for associated procedure.

### 9.8.5	Table 74 history log data table

Table 74 Data Description

HISTORY_LOG_DATA_TBL (Table 74) provides the History Log.

TYPE LIST_STATUS_BFLD = BIT FIELD OF UINT8

ORDER			: UINT(0..0);

OVERFLOW_FLAG		: BOOL(1);

LIST_TYPE			: UINT(2..2);

INHIBIT_OVERFLOW_FLAG	: BOOL(3);

FILLER				: FILL(4..7);

END;

TYPE HISTORY_ENTRY_RCD = PACKED RECORD

IF ACT_LOG_TBL.HIST_DATE_TIME_FLAG THEN

HISTORY_TIME	: LTIME_DATE;

END;

IF ACT_LOG_TBL.EVENT_NUMBER_FLAG THEN

EVENT_NUMBER	: UINT16;

END;

IF ACT_LOG_TBL.HIST_SEQ_NBR_FLAG THEN

HISTORY_SEQ_NBR	: UINT16;

END;

USER_ID			: UINT16;

HISTORY_CODE		: TABLE_IDB_BFLD;

HISTORY_ARGUMENT		: ARRAY[ACT_LOG_TBL.HIST_DATA_LENGTH] OF UINT8;

END;

TYPE HISTORY_LOG_RCD = PACKED RECORD

HIST_FLAGS			: LIST_STATUS_BFLD;

NBR_VALID_ENTRIES		: UINT16;

LAST_ENTRY_ELEMENT	: UINT16;

LAST_ENTRY_SEQ_NBR	: UINT32;

NBR_UNREAD_ENTRIES	: UINT16;

ENTRIES			: ARRAY[ACT_LOG_TBL.NBR_HISTORY_ENTRIES] OF 							HISTORY_ENTRY_RCD;

END;

TABLE HISTORY_LOG_DATA_TBL = HISTORY_LOG_RCD;

Identifier			Value	Definition

LIST_STATUS_BFLD

ORDER		0	The log is transported in ascending order (element N is older than element N+1).

1	The log is transported in descending order (element N is newer than element N+1).

OVERFLOW_FLAG	FALSE	Overflow has not occurred.

TRUE	An attempt was made to enter an event such that the number of unread entries would have exceeded the actual number of possible entries in the log.

LIST_TYPE		0	FIFO - as placed in log.

1	Circular - as placed in log.

INHIBIT_OVERFLOW_FLAG		The same value as ACT_LOG_TBL.-HIST_INHIBIT_OVF_FLAG (Table 71).

TABLE_IDB_BFLD

TBL_PROC_NBR	0..2047	Event number logged.

STD_VS_MFG_FLAG	FALSE	Event number is standard defined.

TRUE	Event number is manufacturer defined.

SELECTOR			Not Used.

HISTORY_ENTRY_RCD

HISTORY_TIME		Date and time of History Log entry.

EVENT_NUMBER	0..65535	Event number common to both the History and Event Logs.

HISTORY_SEQ_NBR	0..65535	Sequence number associated with the History Log only.

USER_ID		0..65535	The User ID associated with this History Log entry.  It comes from the Log In Procedure or from a communication session initiation sequence. A USER_ID of zero means the end device initiated the event.  A USER_ID of one means the event was manually initiated.

HISTORY_CODE		Event code logged.  See TABLE_IDB_BFLD above.  For standard event codes, refer to Annex C, History & Event Log Codes.

HISTORY_ARGUMENT		Argument associated with a specific entry. For standard event arguments, refer to Annex C, History & Event Log Codes.

HISTORY_LOG_RCD

HIST_FLAGS			See LIST_STATUS_BFLD above.

Identifier			Value	Definition

NBR_VALID_ENTRIES	0..65535	Number of valid entries in the log.  The range is from zero (meaning the log is empty) to the actual dimension of the log.

LAST_ENTRY_ELEMENT	0..65535	The array element number of the newest valid entry in the log.

LAST_ENTRY_SEQ_NBR	0..4,294,967,295

The sequence number of the newest valid entry in the log.

NBR_UNREAD_ENTRIES	0..65535	The number of entries in the log that have not yet been read.  It is only changed through a procedure.

ENTRIES			Array of History Log entries.

### 9.8.6	Table 75  event log control table

Table 75 Data Description

EVENT_LOG_CTRL_TBL (Table 75) defines the Event Log codes to be written to the Event Log.  It also defines which specific procedures and or table writes that are to be acknowledged in the Event Log.  For a specific procedure or table to be acknowledged, three independent tests shall all be true:

1) The procedure or table shall be used in the end device, per the GEN_CONFIG_TBL (Table 00).

2) The appropriate Event code shall be used, per Table 75.

3) The procedure or table shall be requested to be acknowledged, per Table 75.

This data structure is identical to the structure in HISTORY_LOG_CTRL_TBL (Table 73).  Elements are defined below.

TABLE EVENT_LOG_CTRL_TBL = HISTORY_CTRL_RCD;

Identifier			Value	Definition

EVENT_CTRL_RCD

STD_EVENTS_MONITORED_FLAGS	Bit position is linearly associated with corresponding standard event code.

FALSE	Turns off event recording for associated event code.

TRUE	Turns on event recording for associated event code.

MFG_EVENTS_MONITORED_FLAGS	Bit position is linearly associated with corresponding manufacturer event code.

FALSE	Turns off event recording for associated event code.

TRUE	Turns on event recording for associated event code.

Identifier			Value	Definition

STD_TBLS_MONITORED_FLAGS	Bit position is linearly associated with corresponding standard table number.

FALSE	Turns off event recording for associated table.

TRUE	Turns on event recording for associated table.

MFG_TBLS_MONITORED_FLAGS	Bit position is linearly associated with corresponding manufacturer table number.

FALSE	Turns off event recording for associated table.

TRUE	Turns on event recording for associated table.

STD_PROC_MONITORED_FLAGS	Bit position is linearly associated with corresponding standard procedure number.

FALSE	Turns off event recording for associated procedure.

TRUE	Turns on event recording for associated procedure.

MFG_PROC_MONITORED_FLAGS	Bit position is linearly associated with corresponding manufacturer procedure number.

FALSE	Turns off event recording for associated procedure.

TRUE	Turns on event recording for associated procedure.

### 9.8.7	Table 76 event log data table

Table 76 Data Description

EVENT_LOG_DATA_TBL (Table 76) provides the Event Log.

TYPE LIST_STATUS_BFLD = BIT FIELD OF UINT8

ORDER			: UINT(0..0);

OVERFLOW_FLAG		: BOOL(1);

LIST_TYPE			: UINT(2..2);

INHIBIT_OVERFLOW_FLAG	: BOOL(3);

FILL				: FILL(4..7);

END;

TYPE EVENT_ENTRY_RCD = PACKED RECORD

EVENT_TIME			: LTIME_DATE;

IF ACT_LOG_TBL.EVENT_NUMBER_FLAG THEN

EVENT_NUMBER	: UINT16;

END;

EVENT_SEQ_NBR		: UINT16;

USER_ID			: UINT16;

EVENT_CODE			: TABLE_IDB_BFLD;

EVENT_ARGUMENT		: ARRAY[ACT_LOG_TBL.EVENT_DATA_LENGTH] OF UINT8;

END;

TYPE EVENT_LOG_RCD = PACKED RECORD

EVENT_FLAGS		: LIST_STATUS_BFLD;

NBR_VALID_ENTRIES		: UINT16;

LAST_ENTRY_ELEMENT	: UINT16;

LAST_ENTRY_SEQ_NBR	: UINT32;

NBR_UNREAD_ENTRIES	: UINT16;

ENTRIES			: ARRAY[ACT_LOG_TBL.NBR_EVENT_ENTRIES] OF 							EVENT_ENTRY_RCD;

END;

TABLE EVENT_LOG_DATA_TBL = EVENT_LOG_RCD;

Identifier			Value	Definition

LIST_STATUS_BFLD

ORDER		0	The log is transported in ascending order (element N is older than element N+1).

1	The log is transported in descending order (element N is newer than element N+1).

OVERFLOW_FLAG	FALSE	Overflow has not occurred.

TRUE	An attempt was made to enter an event such that the number of unread entries would have exceeded the actual number of possible entries in the log.

LIST_TYPE		0	FIFO - as placed in log.

1	Circular - as placed in log.

INHIBIT_OVERFLOW_FLAG		The same value as ACT_LOG_TBL.-EVENT_INHIBIT_OVF_FLAG.

TABLE_IDB_BFLD

TBL_PROC_NBR	0..2047	Event code number logged.

STD_VS_MFG_FLAG	FALSE	Event code is standard defined.

TRUE	Event code is manufacturer defined.

SELECTOR			Not Used.

EVENT_ENTRY_RCD

EVENT_TIME			Date and time of Event Log entry.

EVENT_NUMBER	0..65535	Event number common to both the History and Event Logs.

EVENT_SEQ_NBR	0..65535	Sequence number associated with the Event Log only.

USER_ID		0..65535	The User ID associated with this Event Log entry.  It comes from the Log In Procedure or from a communication session initiation sequence. A USER_ID of zero means the end device initiated the event.  A USER_ID of one means the event was manually initiated.

EVENT_CODE			Event code logged.  See TABLE_IDB_BFLD above.  For standard event codes, refer to Annex B.

Identifier			Value	Definition

EVENT_ARGUMENT		Argument associated with a specific entry.  Refer to Annex B or manufacturer for details.

EVENT_LOG_RCD

ENVENT_FLAGS		See LIST_STATUS_BFLD above.

NBR_VALID_ENTRIES	0..65535	Number of valid entries in the log.  The range is zero (meaning the log is empty) to the actual dimension of the log.

LAST_ENTRY_ELEMENT	0..65535	The array element number of the newest valid entry in the log.

LAST_ENTRY_SEQ_NBR	0..4,294,967,295

The sequence number of the newest valid entry in the log.

NBR_UNREAD_ENTRIES	0..65535	The number of entries in the log that have not yet been read.  It is only changed through a procedure.

ENTRIES			Array of Event Log entries.

## 9.9	Decade 80: user defined tables

These tables provide the capability for the end device user to build custom tables using the tables available in an end device.

### 9.9.1	Table 80 dimension user defined tables function limiting table

Table 80 Data Description

DIM_UDT_FUNC_LIM_TBL (Table 80) contains maximum values and control parameters for the user defined tables. These values set up to six independent sets of user defined tables. The length of user defined tables is a function of the tables defined in the GEN_CONFIG_TBL (Table 00).

type UdT_CTRL_BFLD = bIT FIELD OF uint8

NBR_UDTS			: UINT(0..2);

INSTANCE_FLAG		: BOOL(3);

DATA_ACCESS_METHOD	: UINT(4..5);

FILLER				: fill(6..7);

end;

TYPE UDT_FUNC_LIM_RCD = PACKED RECORD

NBR_XFR_LIST_ITEMS	: UINT16;

UDT_FUNC_CTRL		: UDT_CTRL_BFLD;

MAX_INSTANCE		: UINT8;

END;

IF GEN_CONFIG_TBL.STD_TBLS_USED.UDT_0_TBL_CNST THEN

UDT_0_SIZE		: UINT32;

END;

IF GEN_CONFIG_TBL.STD_TBLS_USED.UDT_1_TBL_CNST THEN

UDT_1_SIZE		: UINT32;

END;

IF GEN_CONFIG_TBL.STD_TBLS_USED.UDT_2_TBL_CNST THEN

UDT_2_SIZE		: UINT32;

END;

IF GEN_CONFIG_TBL.STD_TBLS_USED.UDT_3_TBL_CNST THEN

UDT_3_SIZE		: UINT32;

END;

IF GEN_CONFIG_TBL.STD_TBLS_USED.UDT_4_TBL_CNST THEN

UDT_4_SIZE		: UINT32;

END;

IF GEN_CONFIG_TBL.STD_TBLS_USED.UDT_5_TBL_CNST THEN

UDT_5_SIZE		: UINT32;

END;

END;

TABLE DIM_UDT_FUNC_LIM_TBL = UDT_FUNC_LIM_RCD;

Identifier			Value	Definition

UDT_CTRL_BFLD

NBR_UDTS		0..6	The maximum number of user defined tables, which can be defined concurrently by the list of data items.

7	Reserved.

INSTANCE_FLAG	FALSE	Multiple table instances are not supported. Multiple instances are not supported. Ignore MAX_INSTANCE.

TRUE	Multiple table instances are supported.

DATA_ACCESS_METHOD		Variable to designate possible methods of selecting table entries for placement in a user defined table.

0	Only complete tables can be  mapped into user tables. Partial tables cannot be mapped.

1	Offset-count access method is supported.

2	Index-count access method is supported.

3	Access methods 2 and 3 are supported.

DIM_UDT_FUNC_LIM_TBL

NBR_XFR_LIST_ITEMS	0..65535	The maximum number of UINT16 entries used to make the list.

UDT_FUNC_CTRL		These are the limiting capabilities for user defined tables selections. This defines the maximum number of user defined tables supported in this decade and the data access method, as defined by UDT_CTRL_BFLD.

MAX_INSTANCE

0	Unused

1..255	Maximum number of table sets supported by this end device. If INSTANCE_FLAG is FALSE ignore.

Identifier			Value	Definition

UDT_0_SIZE		0..4,294,967,295

Maximum number of octets used to size UDT_0_TBL (Table 84)

UDT_1_SIZE		0..4,294,967,295

Maximum number of octets used to size UDT_1_TBL (Table 85)

UDT_2_SIZE		0..4,294,967,295

Maximum number of octets used to size UDT_2_TBL (Table 86)

UDT_3_SIZE		0..4,294,967,295

Maximum number of octets used to size UDT_3_TBL (Table 87)

UDT_4_SIZE		0..4,294,967,295

Maximum number of octets used to size UDT_4_TBL (Table 88)

UDT_5_SIZE		0..4,294,967,295

Maximum number of octets used to size UDT_5_TBL (Table 89)

### 9.9.2	Table 81 actual user defined tables function limiting table

Table 81 Data Description

ACT_UDT_FUNC_LIM_TBL (Table 81) contains actual limiting values for the user defined tables. These parameters define up to six independent sets of user defined tables definitions. The length of each user defined table is a function of the tables defined in the GEN_CONFIG_TBL (Table 00).

TABLE ACT_UDT_FUNC_LIM_TBL = DIM_UDT_FUNC_LIM_TBL.UDT_FUNC_LIM_RCD;

Identifier			Value	Definition

UDT_CTRL_BFLD

NBR_UDTS		0..6	The actual number of user defined tables, which are defined concurrently by the list of data items.

7	Reserved.

INSTANCE_FLAG	FALSE	Multiple table sets are not used. Multiple instances are not supported. Ignore MAX_INSTANCE.

TRUE	Multiple table sets are in use.

DATA_ACCESS_METHOD		Designate the actual method of selecting table entries for placement in a user defined table.

0	Complete tables are mapped into user tables. Partial table are not be mapped.

1	Offset-count access method is used.

Identifier			Value	Definition

2	Index-count access method is used.

3	Not Valid.

UDT_FUNC_LIM_RCD

NBR_XFR_LIST_ITEMS	0.. 65535	The actual number of UINT16 entries used in the list.

UDT_FUNC_CTRL		This is the actual method used for user defined tables selections. This identifies the actual number of user defined tables and the data access method used in this decade as defined by UDT_FLAGS_BFLD.

MAX_INSTANCE	0	Unused.

1..255	Actual number of table sets used by this end device. If INSTANCE_FLAG is FALSE ignore.

UDT_0_SIZE		0..4,294,967,295

Actual number of octets used to size UDT_0_TBL (Table 84)

UDT_1_SIZE		0..4,294,967,295

Actual number of octets used to size UDT_1_TBL (Table 85)

UDT_2_SIZE		0..4,294,967,295

Actual number of octets used to size UDT_2_TBL (Table 86)

UDT_3_SIZE		0..4,294,967,295

Actual number of octets used to size UDT_3_TBL (Table 87)

UDT_4_SIZE		0..4,294,967,295

Actual number of octets used to size UDT_4_TBL (Table 88)

UDT_5_SIZE		0..4,294,967,295

Actual number of octets used to size UDT_5_TBL (Table 89)

### 9.9.3	Table 82 user defined tables list table

Table 82 Data Description

UDT_LIST_TBL (Table 82) defines data elements used in the generation of user defined tables for this decade.

TYPE SOURCE_ITEM_RCD = PACKED RECORD

TABLE_ID	: TABLE_IDB_BFLD;

IF ACT_UDT_FUNC_LIM_TBL.INSTANCE_FLAG THEN

TABLE_INSTANCE : UINT16;

END;

CASE ACT_UDT_FUNC_LIM_TBL.DATA_ACCESS_METHOD OF

0: NO_DATA	: NIL;

1: OFFSET	: UINT16;

2: INDEX	: ARRAY[TABLE_ID.SELECTOR] OF UINT16;

END;

COUNT		: UINT16;

END;

TYPE UDT_LIST_SEL_RCD = PACKED RECORD

UDT_LIST : ARRAY[ACT_UDT_FUNC_LIM_TBL.NBR_XFR_LIST_ITEMS] OF UINT16;

END;

TABLE UDT_LIST_TBL = UDT_LIST_SEL_RCD;

Identifier			Value	Definition

TABLE_IDB_BFLD

TBL_PROC_NBR	0..2047	Information source table number. Note: the corresponding implementation bit shall be set in GEN_CONFIG_TBL (Table 00).

STD_VS_MFG_FLAG		Identifies the data item as originating from either the standard table or a manufacturer table.

FALSE	Standard table.

TRUE	Manufacturer table.

SELECTOR		0	When DATA_ACCESS_METHOD is zero the table access method is used.

0..15	When the DATA_ACCESS_METHOD is one this field is the most significant 4 bits (bits 16..19) of the offset to the data element required to locate the data item in a table.

0..15	When DATA_ACCESS_METHOD is two this number of indices is used to select an entry in a table.

SOURCE_ITEM_RCD			Structure of a single entry in the UDT_LIST array.

TABLE_INSTANCE		0..254		Table set number.

255..65535	Not used.

OFFSET		0..65535	This field holds the least significant 16 bits of the offset to the data element required to locate the data item in a table.

INDEX				This is an array of indices, which combine to define the index to an item entry in a table.

COUNT			0..65535	Length of data item(s) in octets.  When the value is zero it is the end of the list.

UDT_LIST_SEL_RCD

UDT_LIST			An array holding ACT_UDT_FUNC_LIM_TBL. NBR_XFR_LIST_ITEM UINT16 quantities. This space is mapped using SOURCE_ITEM_RCD into variable length records which select table or partial tables for access via the user defined tables.

### 9.9.4	Table 83 user defined tables selection table

Table 83 Data Description

UDT_SEL_TBL (Table 83) specifies what data elements are used in user tables defined for this decade.  Each array entry in this table corresponds to a specific table in this decade following this table.  For example, the third entry in this array corresponds to Table 83 + 3 = Table 86.

TYPE UDT_SET_RCD = PACKED RECORD

FIRST_ITEM_NBR	: UINT16;

LAST_ITEM_NBR	: UINT16;

END;

TYPE UDT_DATA_SETS_RCD = PACKED RECORD

UDT_DATA_SETS	: ARRAY[ACT_UDT_FUNC_LIM_TBL.NBR_UDTS] OF UDT_SET_RCD;

END;

TABLE UDT_SEL_TBL = UDT_DATA_SETS_RCD;

Identifier			Value	Definition

UDT_SETS_RCD

FIRST_ITEM_NBR	0..65535	This is item number in UDT_LIST_TBL (Table 82) specifying the first item in the user defined tables selected by this entry.

LAST_ITEM_NBR	0..65535	This is item number in UDT_LIST_TBL (Table 82) specifying the last item in the user defined tables selected by this entry.

UDT_DATA_SETS_RCD

UDT_DATA_SETS		Array containing up to ACT_UDT_ FUNC_LIM_TBL.NBR_UDTS (Table 81) entries. Each entry defines the source selections for a user destination user defined table.

### 9.9.5	Table 84 user defined table zero table

Table 84 Data Description

This table is defined by the items in table UDT_LIST_TBL (Table 82) selected by the first entry in table UDT_SEL_TBL (Table 83).

TYPE UDT_0_RCD = PACKED RECORD

UDT_0_DATA		: ARRAY[ACT_UDT_FUNC_LIM_TBL.UDT_0_SIZE] OF UINT8;

END;

TABLE UDT_0_TBL = UDT_0_RCD;

Identifier			Value	Definition

UDT_0_RCD 				Array containing  ACT_UDT_FUNCT_LIM_TBL. UDT_0_SIZE octets holding data defined by the first entry in the list defined in UDT_SEL_TBL (Table 83).

### 9.9.6	Table 85 user defined table one table

Table 85 Data Description

This table is defined by the items in table UDT_LIST_TBL (Table 82) selected by the first entry in table UDT_SEL_TBL (Table 83).

TYPE UDT_1_RCD = PACKED RECORD

UDT_1_DATA 		: ARRAY[ACT_UDT_FUNC_LIM_TBL.UDT_1_SIZE] OF UINT8;

END;

TABLE UDT_1_TBL = UDT_1_RCD;

Identifier			Value	Definition

UDT_1_RCD 				Array containing  ACT_UDT_FUNCT_LIM_TBL. UDT_1_SIZE octets holding data defined by the second entry in the list defined in UDT_SEL_TBL (Table 83).

### 9.9.7	Table 86 user defined table two table

Table 86 Data Description

This table is defined by the items in table UDT_LIST_TBL (Table 82) selected by the first entry in table UDT_SEL_TBL (Table 83).

TYPE UDT_2_RCD = PACKED RECORD

UDT_2_DATA 		: ARRAY[ACT_UDT_FUNC_LIM_TBL.UDT_2_SIZE] OF UINT8;

END;

TABLE UDT_2_TBL = UDT_2_RCD;

Identifier			Value	Definition

UDT_2_RCD 				Array containing  ACT_UDT_FUNCT_LIM_TBL. UDT_2_SIZE octets holding data defined by the third entry in the list defined in UDT_SEL_TBL (Table 83).

### 9.9.8	Table 87 user defined table three table

Table 87 Data Description

This table is defined by the items in table UDT_LIST_TBL (Table 82) selected by the first entry in table UDT_SEL_TBL (Table 83).

TYPE UDT_3_RCD = PACKED RECORD

UDT_3_DATA 		: ARRAY[ACT_UDT_FUNC_LIM_TBL.UDT_3_SIZE] OF UINT8;

END;

TABLE UDT_3_TBL = UDT_3_RCD;

Identifier			Value	Definition

UDT_3_RCD 				Array containing  ACT_UDT_FUNCT_LIM_TBL. UDT_3_SIZE octets holding data defined by the fourth entry in the list defined in UDT_SEL_TBL (Table 83).

### 9.9.9	Table 88 user defined table four table

Table 88 Data Description

This table is defined by the items in table UDT_LIST_TBL (Table 82) selected by the first entry in table UDT_SEL_TBL (Table 83).

TYPE UDT_4_RCD = PACKED RECORD

UDT_4_DATA 		: ARRAY[ACT_UDT_FUNC_LIM_TBL.UDT_4_SIZE] OF UINT8;

END;

TABLE UDT_4_TBL  UDT_4_RCD;

Identifier			Value	Definition

UDT_4_RCD 				Array containing  ACT_UDT_FUNCT_LIM_TBL. UDT_4_SIZE octets holding data defined by the fifth entry in the list defined in UDT_SEL_TBL (Table 83).

### 9.9.10	Table 89 user defined table five table

Table 89 Data Description

This table is defined by the items in table UDT_LIST_TBL (Table 82) selected by the first entry in table UDT_SEL_TBL (Table 83).

TYPE UDT_5_RCD = PACKED RECORD

UDT_5_DATA 		: ARRAY[ACT_UDT_FUNC_LIM_TBL.UDT_5_SIZE] OF UINT8;

END;

TABLE UDT_5_TBL = UDT_5_RCD;

Identifier			Value	Definition

UDT_5_RCD 				Array containing  ACT_UDT_FUNCT_LIM_TBL. UDT_5_SIZE octets holding data defined by the sixth entry in the list defined in UDT_SEL_TBL (Table 83).

# ANNEX A
(Normative)

# ID CODES FOR METER EQUIPMENT MANUFACTURERS

ABB :  ABB

AMCO:  American Meter Company

APTH:  Aptech, Inc.

BM I: Badger Meter, Inc.

END :  Endacom 2000 Inc.

GE  :  General Electric

ITD :  International Teldata Corporation

JEM :  Scientific Columbus Company

L&G :  Landis & Gyr

MM  :  Master Meter, Inc.

ND  :  Nertec Design Inc.

PSI :  Process Systems Inc.

SCH :  Schlumberger

TEMP:  For new manufacturers who are not yet included in this list.

WEXL:  WeXL

# ANNEX B
(Normative)

# HISTORY & EVENT LOG CODES

Code	Event				Argument

00	No Event			None

01	Primary Power Down		None

02	Primary Power Up		None

03	Time Changed (old time)		None.  Time tag if used equals old time.

04	Time Changed (new time)		None.  Time tag if used equals new time.

05	Time Changed (old time)		Old time in STIME_DATE format.

06	Time Changed (new time)		New time in STIME_DATE format.

07	End Device Accessed for Read		None

08	End Device Accessed for Write		None

09	Procedure Invoked		Bit Field of Procedure Number and Standard/Manufacturer Flag (UINT16) TABLE_IDC_BFLD format.

10	Table Written To		Bit Field of Table Number and Standard/Manufacturer Flag (UINT16) TABLE_IDA_BFLD format.

11	End Device Programmed		None

12	Communication Terminated Normally	None

13	Communication Terminated Abnormally	None

14	Reset List Pointers		LIST(INT8) {Reference procedure 4, 9.1.8.1.5}

15	Update List Pointers		LIST (UINT8) (Reference procedure 5, 9.1.8.1.6}

16	History Log Cleared		None

17	History Log Pointers Updated		Value of Procedure Parameter (UINT16)

18	Event Log Cleared		None

19	Event Log Pointers Updated		Value of Procedure Parameter (UINT16)

20	Demand Reset Occurred		None

21	Self Read Occurred		None

22	Daylight Savings Time On		None

23	Daylight Savings Time Off		None

24	Season Change			New Season Number (UINT8)

25	Rate Change			New Rate(UINT8)

26	Special Schedule Activation		New Special Schedule (UINT8)

27	Tier Switch Change		New Current Tier(UINT8 followed by New Demand Tier (UINT8)

28	Pending Table Activation		Table number (TABLE_IDA_BFLD).

29	Pending Table Clear		Table number (TABLE_IDA_BFLD).  Table removed from end device prior to activation.

end markings

# ANNEX C
(Normative)
DEFAULT SETS FOR DECADE TABLES

The following values are assigned to the decade and decade+1 table values based upon the value of the TABLE 00 variable DEFAULT_SET_USED.

| Variable | DEFAULT_SET_USED |  |  |  |
| --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 |
| TABLE 11 |  |  |  |  |
| PF_EXCLUDE_FLAG | 0 | 0 | 1 | 0 |
| RESET_EXCLUDE_FLAG | 0 | 1 | 1 | 0 |
| BLOCK_DEMAND_FLAG | 0 | 1 | 1 | 1 |
| SLIDING_DEMAND_FLAG | 0 | 0 | 0 | 0 |
| THERMAL_DEMAND_FLAG | 0 | 0 | 0 | 0 |
| SET1_PRESENT_FLAG | 0 | 0 | 0 | 0 |
| SET2_PRESENT_FLAG | 0 | 0 | 0 | 0 |
| NBR_UOM_ENTRIES | 0 | 0 | 0 | 0 |
| NBR_DEMAND_CTRL_ENTRIES | 0 | 1 | 3 | 1 |
| DATA_CTRL_LENGTH | 1 | 1 | 1 | 1 |
| NBR_DATA_CTRL_ENTRIES | 1 | 2 | 2 | 2 |
| NBR_CONSTANTS_ENTRIES | 1 | 1 | 1 | 1 |
| CONSTANTS_SELECTOR | 2 | 2 | 2 | 2 |
| NBR_SOURCES | 1 | 2 | 2 | 2 |
| TABLE 21 |  |  |  |  |
| SEASON_INFO_FIELD_FLAG | 0 | 0 | 0 | 0 |
| DATE_TIME_FIELD_FLAG | 0 | 0 | 0 | 0 |
| DEMAND_RESET_CTR_FLAG | 0 | 1 | 1 | 0 |
| DEMAND_RESET_LOCK_FLAG | 0 | 1 | 1 | 0 |
| CUM_DEMAND_FLAG | 0 | 0 | 0 | 0 |
| CONT_CUM_DEMAND_FLAG | 0 | 0 | 0 | 0 |
| TIME_REMAINING_FLAG | 0 | 0 | 0 | 0 |
| SELF_READ_INHIBIT_OVERFLOW_FLAG | 0 | 0 | 1 | 0 |
| SELF_READ_SEQ_NBR_FLAG | 0 | 0 | 1 | 0 |
| DAILY_SELF_READ_FLAG | 0 | 0 | 0 | 0 |
| WEEKLY_SELF_READ_FLAG | 0 | 0 | 0 | 0 |
| SELF_READ_DEMAND_RESET | 0 | 0 | 1 | 0 |
| NBR_SELF_READS | 0 | 0 | 1 | 0 |
| NBR_SUMMATIONS | 1 | 1 | 1 | 1 |
| NBR_DEMANDS | 0 | 1 | 1 | 0 |
| NBR_COIN_VALUES | 0 | 0 | 0 | 0 |
| NBR_OCCUR | 0 | 1 | 1 | 0 |
| NBR_TIERS | 0 | 0 | 3 | 0 |
| NBR_PRESENT_DEMANDS | 1 | 1 | 1 | 1 |
| NBR_PRESENT_VALUES | 1 | 1 | 1 | 1 |

| Variable | DEFAULT_SET_USED |  |  |  |
| --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 |
| OFF_TIME_FLAG | 0 | 0 | 0 | 0 |
| HOLD_TIME_FLAG | 0 | 0 | 0 | 0 |
| NBR_DISP_SOURCES | 3 | 4 | 40 | 0 |
| WIDTH_DISP_SOURCES | 1 | 1 | 1 | 0 |
| NBR_PRI_DISP_LIST_ITEMS | 9 | 12 | 60 | 0 |
| NBR_PRI_DISP_LISTS | 3 | 3 | 3 | 0 |
| NBR_SEC_DISP_LIST_ITEMS | 3 | 3 | 3 | 0 |
| NBR_SEC_DISP_LISTS | 1 | 1 | 1 | 1 |
| TABLE 41 |  |  |  |  |
| NBR_PASSWORDS | 1 | 1 | 1 | 1 |
| PASSWORD_LEN | 20 | 20 | 20 | 20 |
| NBR_KEYS | 1 | 1 | 1 | 1 |
| KEY_LEN | 4 | 4 | 4 | 4 |
| NBR_PERM_USED | 1 | 1 | 1 | 1 |
| TABLE 51 |  |  |  |  |
| TOU_SELF_READ_FLAG | 0 | 0 | 1 | 0 |
| SEASON_SELF_READ_FLAG | 0 | 0 | 1 | 0 |
| SEASON_DEMAND_RESET_FLAG | 0 | 0 | 0 | 0 |
| SEASON_CHNG_ARMED_FLAG | 0 | 0 | 0 | 0 |
| SORT_DATES_FLAG | 0 | 0 | 1 | 0 |
| ANCHOR_DATE_FLAG | 0 | 0 | 0 | 0 |
| CAP_DST_AUTO_FLAG | 0 | 0 | 0 | 0 |
| SEPARATE_WEEKDAYS_FLAG | 0 | 0 | 0 | 0 |
| SEPARATE_SUM_DEMANDS_FLAG | 0 | 0 | 0 | 0 |
| SORT_TIER_SWITCHES_FLAG | 0 | 0 | 1 | 0 |
| CAP_TM_ZN_OFFSET_FLAG | 0 | 0 | 0 | 0 |
| NBR_SEASONS | 0 | 0 | 2 | 0 |
| NBR_SPECIAL_SCHED | 0 | 0 | 1 | 0 |
| NBR_NON_RECURR_DATES | 0 | 0 | 10 | 0 |
| NBR_RECURR_DATES | 0 | 0 | 10 | 0 |
| NBR_TIER_SWITCHES | 0 | 0 | 9 | 0 |
| CALENDAR_TBL_SIZE | 0 | 0 | 131 | 0 |
| TABLE 61 |  |  |  |  |
| LP_SET1_INHIBIT_OVF_FLAG | 0 | 0 | 0 | 1 |
| LP_SET2_INHIBIT_OVF_FLAG | 0 | 0 | 0 | 0 |
| LP_SET3_INHIBIT_OVF_FLAG | 0 | 0 | 0 | 0 |
| LP_SET4_INHIBIT_OVF_FLAG | 0 | 0 | 0 | 0 |
| BLK_END_READ_FLAG | 0 | 0 | 0 | 0 |
| BLK_END_PULSE_FLAG | 0 | 0 | 0 | 0 |
| SCALAR_DIVISOR_FLAG_SET1 | 0 | 0 | 0 | 1 |
| SCALAR_DIVISOR_FLAG_SET2 | 0 | 0 | 0 | 0 |
| SCALAR_DIVISOR_FLAG_SET3 | 0 | 0 | 0 | 0 |
| SCALAR_DIVISOR_FLAG_SET4 | 0 | 0 | 0 | 0 |
| EXTENDED_INT_STATUS_FLAG | 0 | 0 | 0 | 1 |
| SIMPLE_INT_STATUS_FLAG | 0 | 0 | 0 | 0 |
| INV_UINT8_FLAG | 0 | 0 | 0 | 0 |
| Variable | DEFAULT_SET_USED |  |  |  |
|  | 1 | 2 | 3 | 4 |
| INV_UINT16_FLAG | 0 | 0 | 0 | 1 |
| INV_UINT32_FLAG | 0 | 0 | 0 | 0 |
| INV_INT8_FLAG | 0 | 0 | 0 | 0 |
| INV_INT16_FLAG | 0 | 0 | 0 | 0 |
| INV_INT32_FLAG | 0 | 0 | 0 | 0 |
| INV_NI_FMAT1_FLAG | 0 | 0 | 0 | 0 |
| INV_NI_FMAT2_FLAG | 0 | 0 | 0 | 0 |
| LP_MEMORY_LEN | 0 | 0 | 0 | 16384 |
| NBR_BLKS_SET1 | 0 | 0 | 0 | 80 |
| NBR_BLK_INTS_SET1 | 0 | 0 | 0 | 96 |
| NBR_CHNS_SET1 | 0 | 0 | 0 | 1 |
| MAX_INT_TIME_SET1 | 0 | 0 | 0 | 15 |
| NBR_BLKS_SET2 | 0 | 0 | 0 | 0 |
| NBR_BLK_INTS_SET2 | 0 | 0 | 0 | 0 |
| NBR_CHNS_SET2 | 0 | 0 | 0 | 0 |
| MAX_INT_TIME_SET2 | 0 | 0 | 0 | 0 |
| NBR_BLKS_SET3 | 0 | 0 | 0 | 0 |
| NBR_BLK_INTS_SET3 | 0 | 0 | 0 | 0 |
| NBR_CHNS_SET3 | 0 | 0 | 0 | 0 |
| MAX_INT_TIME_SET3 | 0 | 0 | 0 | 0 |
| NBR_BLKS_SET4 | 0 | 0 | 0 | 0 |
| NBR_BLK_INTS_SET4 | 0 | 0 | 0 | 0 |
| NBR_CHNS_SET4 | 0 | 0 | 0 | 0 |
| MAX_INT_TIME_SET4 | 0 | 0 | 0 | 0 |
| TABLE 71 |  |  |  |  |
| EVENT_NUMBER_FLAG | 1 | 1 | 1 | 1 |
| HIST_DATE_TIME_FLAG | 1 | 1 | 1 | 1 |
| HIST_SEQ_NBR_FLAG | 0 | 0 | 0 | 0 |
| HIST_INHIBIT_OVF_FLAG | 0 | 0 | 0 | 0 |
| EVENT_INHIBIT_OVF_FLAG | 1 | 1 | 1 | 1 |
| NBR_STD_EVENTS | 4 | 4 | 4 | 4 |
| NBR_MFG_EVENTS | 0 | 0 | 0 | 0 |
| HIST_DATA_LENGTH | 2 | 2 | 2 | 2 |
| EVENT_DATA_LENGTH | 2 | 2 | 2 | 2 |
| NBR_HISTORY_ENTRIES | 100 | 100 | 100 | 100 |
| NBR_EVENT_ENTRIES | 100 | 100 | 100 | 100 |
| TABLE 81 |  |  |  |  |
| NBR_UDTS | 1 | 2 | 3 | 1 |
| DATA_ACCESS_METHOD | 2 | 2 | 2 | 2 |
| NBR_XFR_LIST_ITEMS | 2 | 3 | 6 | 2 |
| MAX_INSTANCE | 0 | 0 | 0 | 0 |
| UDT_0_SIZE | 256 | 256 | 256 | 256 |
| UDT_1_SIZE | 0 | 256 | 256 | 0 |
| UDT_2_SIZE | 0 | 0 | 256 | 0 |
| UDT_3_SIZE | 0 | 0 | 0 | 0 |
| UDT_4_SIZE | 0 | 0 | 0 | 0 |
| UDT_5_SIZE | 0 | 0 | 0 | 0 |

# ANNEX D
(Normative)
INDICES FOR PARTIAL TABLE ACCESS

The following values are for use with the partial table access method identified as index-count.

| TABLE 000 - GEN_CONFIG_TBL |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| FORMAT_CONTROL_1 | 000 |  |  |  |  |  |  |  |
| FORMAT_CONTROL_2 | 001 |  |  |  |  |  |  |  |
| FORMAT_CONTROL_3 | 002 |  |  |  |  |  |  |  |
| MANUFACTURER | 003 |  |  |  |  |  |  |  |
| NAMEPLATE_TYPE | 004 |  |  |  |  |  |  |  |
| DEFAULT_SET_USED | 005 |  |  |  |  |  |  |  |
| MAX_PROC_PARM_LENGTH | 006 |  |  |  |  |  |  |  |
| MAX_RESP_DATA_LEN | 007 |  |  |  |  |  |  |  |
| STD_VERSION_NO | 008 |  |  |  |  |  |  |  |
| STD_REVISION_NO | 009 |  |  |  |  |  |  |  |
| DIM_STD_TBLS_USED | 010 |  |  |  |  |  |  |  |
| DIM_MFG_TBLS_USED | 011 |  |  |  |  |  |  |  |
| DIM_STD_PROC_USED | 012 |  |  |  |  |  |  |  |
| DIM_MFG_PROC_USED | 013 |  |  |  |  |  |  |  |
| DIM_MFG_STATUS_USED | 014 |  |  |  |  |  |  |  |
| NBR_PENDING | 015 |  |  |  |  |  |  |  |
| STD_TBLS_USED | 016 |  |  |  |  |  |  |  |
| MFG_TBLS_USED | 017 |  |  |  |  |  |  |  |
| STD_PROC_USED | 018 |  |  |  |  |  |  |  |
| MFG_PROC_USED | 019 |  |  |  |  |  |  |  |
| STD_TBLS_WRITE | 020 |  |  |  |  |  |  |  |
| MFG_TBLS_WRITE | 021 |  |  |  |  |  |  |  |
| TABLE 001 - GENERAL_MFG_ID_TBL |  |  |  |  |  |  |  |  |
| MANUFACTURER | 000 |  |  |  |  |  |  |  |
| ED_MODEL | 001 |  |  |  |  |  |  |  |
| HW_VERSION_NUMBER | 002 |  |  |  |  |  |  |  |
| HW_REVISION_NUMBER | 003 |  |  |  |  |  |  |  |
| FW_VERSION_NUMBER | 004 |  |  |  |  |  |  |  |
| FW_REVISION_NUMBER | 005 |  |  |  |  |  |  |  |
| MFG_SERIAL_NUMBER | 006 |  |  |  |  |  |  |  |
| TABLE 002 - DEVICE_NAMEPLATE_TBL |  |  |  |  |  |  |  |  |
| (Gas Device Structure) |  |  |  |  |  |  |  |  |
| G_ED_TYPE | 000 |  |  |  |  |  |  |  |
| G_MAX_PRESS | 001 |  |  |  |  |  |  |  |
| G_MAX_PRESS | 001 | 000 |  |  |  |  |  |  |
| G_UOM_PRESS | 001 | 001 |  |  |  |  |  |  |
| G_MAX_FLOW | 002 |  |  |  |  |  |  |  |
| G_MAX_FLOW | 002 | 000 |  |  |  |  |  |  |
| G_UOM_FLOW | 002 | 001 |  |  |  |  |  |  |
| G_GEAR_PIPE_SIZE | 003 |  |  |  |  |  |  |  |
| G_COMPENSATION | 004 |  |  |  |  |  |  |  |
| (Water Device Structure) |  |  |  |  |  |  |  |  |
| W_WATER_DEVICE_BFLD | 000 |  |  |  |  |  |  |  |
| (Electric Device Structure) |  |  |  |  |  |  |  |  |
| E_Kh | 000 |  |  |  |  |  |  |  |
| E_Kt | 001 |  |  |  |  |  |  |  |
| E_INPUT_SCALAR | 002 |  |  |  |  |  |  |  |
| E_ED_CONFIG(ARRAY) | 003 |  |  |  |  |  |  |  |
| E_ED_CONFIG(ITEM) | 003 | [n] |  |  |  |  |  |  |
| E_ELEMENTS | 004 |  |  |  |  |  |  |  |
| E_VOLTS | 005 |  |  |  |  |  |  |  |
| E_AMPS | 006 |  |  |  |  |  |  |  |
| E_CLASS_MAX_AMPS | 006 | 000 |  |  |  |  |  |  |
| E_TA | 006 | 001 |  |  |  |  |  |  |
| TABLE 003 - ED_MODE_STATUS_TBL |  |  |  |  |  |  |  |  |
| ED_MODE | 000 |  |  |  |  |  |  |  |
| ED_STD_STATUS1 | 001 |  |  |  |  |  |  |  |
| ED_STD_STATUS2 | 002 |  |  |  |  |  |  |  |
| ED_MFG_STATUS | 003 |  |  |  |  |  |  |  |
| ED_MFG_STATUS | 003 |  |  |  |  |  |  |  |
| ED_MFG_STATUS (ITEM) | 003 | 000 |  |  |  |  |  |  |
| TABLE 004 - PENDING_STATUS_TBL |  |  |  |  |  |  |  |  |
| STANDARD_PENDING | 000 |  |  |  |  |  |  |  |
| MANUFACT_PENDING | 001 |  |  |  |  |  |  |  |
| LAST_ACTIVATION_DATE_TIME | 002 |  |  |  |  |  |  |  |
| NBR_PENDING_ACTIVATION | 003 |  |  |  |  |  |  |  |
| PENDING_TABLES(ARRAY) | 004 |  |  |  |  |  |  |  |
| PENDING_TABLES(ITEM) | 004 | [n] |  |  |  |  |  |  |
| EVENT | 004 | [n] | 000 |  |  |  |  |  |
| EVENT_SELECTOR | 004 | [n] | 000 | 000 |  |  |  |  |
| EVENT_STORAGE(ARRAY) | 004 | [n] | 000 | 001 |  |  |  |  |
| EVENT_STORAGE(ITEM) | 004 | [n] | 000 | 001 | [n] |  |  |  |
| TABLE_SELECTOR | 004 | [n] | 001 |  |  |  |  |  |
| TABLE 005 - DEVICE_IDENT_TBL |  |  |  |  |  |  |  |  |
| IDENTIFICATION | 000 |  |  |  |  |  |  |  |
| TABLE 006 - UTIL_INFO_TBL |  |  |  |  |  |  |  |  |
| OWNER_NAME | 000 |  |  |  |  |  |  |  |
| UTILITY_DIV | 001 |  |  |  |  |  |  |  |
| SERVICE_POINT_ID | 002 |  |  |  |  |  |  |  |
| ELEC_ADDR | 003 |  |  |  |  |  |  |  |
| DEVICE_ID | 004 |  |  |  |  |  |  |  |
| UTIL_SER_NO | 005 |  |  |  |  |  |  |  |
| CUSTOMER_ID | 006 |  |  |  |  |  |  |  |
| COORDINATE_1 | 007 |  |  |  |  |  |  |  |
| COORDINATE_2 | 008 |  |  |  |  |  |  |  |
| COORDINATE_3 | 009 |  |  |  |  |  |  |  |
| TARIFF_ID | 010 |  |  |  |  |  |  |  |
| EX1_SW_VENDOR | 011 |  |  |  |  |  |  |  |
| EX1_SW_VERSION_NUMBER | 012 |  |  |  |  |  |  |  |
| EX1_SW_REVISION_NUMBER | 013 |  |  |  |  |  |  |  |
| EX2_SW_VENDOR | 014 |  |  |  |  |  |  |  |
| EX2_SW_VERSION_NUMBER | 015 |  |  |  |  |  |  |  |
| EX2_SW_REVISION_NUMBER | 016 |  |  |  |  |  |  |  |
| PROGRAMMER_NAME | 017 |  |  |  |  |  |  |  |
| MISC_ID | 018 |  |  |  |  |  |  |  |
| TABLE 007 - PROC_INITIATE_TBL |  |  |  |  |  |  |  |  |
| PROC | 000 |  |  |  |  |  |  |  |
| SEQ_NBR | 001 |  |  |  |  |  |  |  |
| PARM | 002 |  |  |  |  |  |  |  |
| TABLE 008 - PROC_RESPONSE_TBL |  |  |  |  |  |  |  |  |
| PROC | 000 |  |  |  |  |  |  |  |
| SEQ_NBR | 001 |  |  |  |  |  |  |  |
| RESULT_CODE | 002 |  |  |  |  |  |  |  |
| RESP_DATA | 003 |  |  |  |  |  |  |  |
| TABLE 010 - DIM_SOURCES_LIM_TBL |  |  |  |  |  |  |  |  |
| SOURCE_FLAGS | 000 |  |  |  |  |  |  |  |
| NBR_UOM_ENTRIES | 001 |  |  |  |  |  |  |  |
| NBR_DEMAND_CTRL_ENTRIES | 002 |  |  |  |  |  |  |  |
| DATA_CTRL_LENGTH | 003 |  |  |  |  |  |  |  |
| NBR_DATA_CTRL_ENTRIES | 004 |  |  |  |  |  |  |  |
| NBR_CONSTANT_ENTRIES | 005 |  |  |  |  |  |  |  |
| CONSTANTS_SELECTOR | 006 |  |  |  |  |  |  |  |
| NBR_SOURCES | 007 |  |  |  |  |  |  |  |
| TABLE 011 - ACT_SOURCES_LIM_TBL |  |  |  |  |  |  |  |  |
| SOURCE_FLAGS | 000 |  |  |  |  |  |  |  |
| NBR_UOM_ENTRIES | 001 |  |  |  |  |  |  |  |
| NBR_DEMAND_CTRL_ENTRIES | 002 |  |  |  |  |  |  |  |
| DATA_CTRL_LENGTH | 003 |  |  |  |  |  |  |  |
| NBR_DATA_CTRL_ENTRIES | 004 |  |  |  |  |  |  |  |
| NBR_CONSTANT_ENTRIES | 005 |  |  |  |  |  |  |  |
| CONSTANTS_SELECTOR | 006 |  |  |  |  |  |  |  |
| NBR_SOURCES | 007 |  |  |  |  |  |  |  |
| TABLE 012 - UOM_ENTRY_TBL |  |  |  |  |  |  |  |  |
| UOM_ENTRY(ARRAY) | 000 |  |  |  |  |  |  |  |
| UOM_ENTRY(ITEM) | 000 | [n] |  |  |  |  |  |  |
| TABLE 013 - DEMAND_CONTROL_TBL |  |  |  |  |  |  |  |  |
| RESET_EXCLUSION | 000 |  |  |  |  |  |  |  |
| P_FAIR_RECOHNTN_TM | 001 |  |  |  |  |  |  |  |
| P_FAIL_EXCLUSION | 002 |  |  |  |  |  |  |  |
| COLD_LOAD_PICKUP | 003 |  |  |  |  |  |  |  |
| INTERVAL_VALUE(ARRAY) | 004 |  |  |  |  |  |  |  |
| INTERVAL_VALUE(ITEM) | 004 | [n] |  |  |  |  |  |  |
| SUB_INT | 004 | [n] | 000 |  |  |  |  |  |
| INT_MULTIPLIER | 004 | [n] | 001 |  |  |  |  |  |
| INT_LENGTH | 004 | [n] | 002 |  |  |  |  |  |
| TABLE 014 - DATA_CONTROL_RCD |  |  |  |  |  |  |  |  |
| SOURCES_ID(ARRAY) | 000 |  |  |  |  |  |  |  |
| SOURCES_ID(ITEM) | 000 | [n] |  |  |  |  |  |  |
| SOURCE_ID(ARRAY) | 000 | [n] | 000 |  |  |  |  |  |
| SOURCE_ID(ITEM) | 000 | [n] | 000 | [n] |  |  |  |  |
| TABLE 015 - CONSTANTS_TBL |  |  |  |  |  |  |  |  |
| SELECTION(ARRAY) | 000 |  |  |  |  |  |  |  |
| SELECTION(ITEM) | 000 | [n] |  |  |  |  |  |  |
| (Gas Device - AGA3) |  |  |  |  |  |  |  |  |
| GAS_DP_PARM | 000 | [n] | 000 |  |  |  |  |  |
| GAS_DP_ZERO | 000 | [n] | 000 | 000 |  |  |  |  |
| GAS_DP_FULLSCALE | 000 | [n] | 000 | 001 |  |  |  |  |
| GAS_DP_SHUTOFF | 000 | [n] | 001 |  |  |  |  |  |
| GAS_SHUTOFF | 000 | [n] | 001 | 000 |  |  |  |  |
| GAS_PRESS_PARM | 000 | [n] | 002 |  |  |  |  |  |
| GAS_PRESS_ZERO | 000 | [n] | 002 | 000 |  |  |  |  |
| GAS_PRESS_FULLSCALE | 000 | [n] | 002 | 001 |  |  |  |  |
| BASE_PRESSURE | 000 | [n] | 002 | 002 |  |  |  |  |
| GAS_AGA3_CORR_FCTR | 000 | [n] | 003 |  |  |  |  |  |
| AUX_CORR_FCTR | 000 | [n] | 003 | 000 |  |  |  |  |
| GAS_AGA3_CORR | 000 | [n] | 003 | 001 |  |  |  |  |
| PIPE_ORIF_DIA | 000 | [n] | 003 | 002 |  |  |  |  |
| PIPE_DIA | 000 | [n] | 003 | 002 | 000 |  |  |  |
| ORIF_DIA | 000 | [n] | 003 | 002 | 001 |  |  |  |
| TAP_UP_DN | 000 | [n] | 003 | 003 |  |  |  |  |
| GAS_PRESS_PARM | 000 | [n] | 003 | 004 |  |  |  |  |
| GAS_PRESS_ZERO | 000 | [n] | 003 | 004 | 000 |  |  |  |
| GAS_PRESS_FULLSCALE | 000 | [n] | 003 | 004 | 001 |  |  |  |
| BASE_PRESSURE | 000 | [n] | 003 | 004 | 002 |  |  |  |
| GAS_TEMP_PARM | 000 | [n] | 003 | 005 |  |  |  |  |
| GAS_TEMP_ZERO | 000 | [n] | 003 | 005 | 000 |  |  |  |
| GAS_TEMP_FULLSCALE | 000 | [n] | 003 | 005 | 001 |  |  |  |
| BASE_TEMP | 000 | [n] | 003 | 005 | 002 |  |  |  |
| GAS_ENERGY | 000 | [n] | 004 |  |  |  |  |  |
| GAS_ENERGY_ZERO | 000 | [n] | 004 | 000 |  |  |  |  |
| GAS_ENERGY_FULL | 000 | [n] | 004 | 001 |  |  |  |  |
| (Gas Device - AGA7) |  |  |  |  |  |  |  |  |
| GAS_AGA7_CORR | 000 | [n] | 000 |  |  |  |  |  |
| GAS_PRESS_PARM | 000 | [n] | 000 | 000 |  |  |  |  |
| GAS_PRESS_ZERO | 000 | [n] | 000 | 000 | 000 |  |  |  |
| GAS_PRESS_FULLSCALE | 000 | [n] | 000 | 000 | 001 |  |  |  |
| BASE_PRESSURE | 000 | [n] | 000 | 000 | 002 |  |  |  |
| GAS_TEMP_PARM | 000 | [n] | 000 | 001 |  |  |  |  |
| GAS_TEMP_ZERO | 000 | [n] | 000 | 001 | 000 |  |  |  |
| GAS_TEMP_FULLSCALE | 000 | [n] | 000 | 001 | 001 |  |  |  |
| BASE_TEMP | 000 | [n] | 000 | 001 | 002 |  |  |  |
| AUX_CORR_FCTR | 000 | [n] | 000 | 002 |  |  |  |  |
| GAS_AGA7_CORR | 000 | [n] | 000 | 003 |  |  |  |  |
| GAS_ENERGY | 000 | [n] | 001 |  |  |  |  |  |
| GAS_ENERGY_ZERO | 000 | [n] | 001 | 000 |  |  |  |  |
| GAS_ENERGY_FULL | 000 | [n] | 001 | 001 |  |  |  |  |
| (Electric Device) |  |  |  |  |  |  |  |  |
| MULTIPLIER | 000 | [n] | 000 |  |  |  |  |  |
| OFFSET | 000 | [n] | 001 |  |  |  |  |  |
| SET1_CONSTANTS | 000 | [n] | 002 |  |  |  |  |  |
| SET_FLAGS | 000 | [n] | 002 | 000 |  |  |  |  |
| RATIO_F1 | 000 | [n] | 002 | 001 |  |  |  |  |
| RATIO_P1 | 000 | [n] | 002 | 002 |  |  |  |  |
| SET2_CONSTANTS | 000 | [n] | 003 |  |  |  |  |  |
| SET_FLAGS | 000 | [n] | 003 | 000 |  |  |  |  |
| RATIO_F1 | 000 | [n] | 003 | 001 |  |  |  |  |
| RATIO_P1 | 000 | [n] | 003 | 002 |  |  |  |  |
| TABLE 016 - SOURCES_TBL |  |  |  |  |  |  |  |  |
| SOURCES_LINK(ARRAY) | 000 |  |  |  |  |  |  |  |
| SOURCES_LINK(ITEM) | 000 | [n] |  |  |  |  |  |  |
| TABLE 020 - DIM_REGS_TBL |  |  |  |  |  |  |  |  |
| REG_FUNC1_FLAGS | 000 |  |  |  |  |  |  |  |
| REG_FUNC2_FLAGS | 001 |  |  |  |  |  |  |  |
| NBR_SELF_READS | 002 |  |  |  |  |  |  |  |
| NBR_SUMMATIONS | 003 |  |  |  |  |  |  |  |
| NBR_DEMANDS | 004 |  |  |  |  |  |  |  |
| NBR_COIN_VALUES | 005 |  |  |  |  |  |  |  |
| NBR_OCCUR | 006 |  |  |  |  |  |  |  |
| NBR_TEIRS | 007 |  |  |  |  |  |  |  |
| NBR_PRESENT_DEMANDS | 008 |  |  |  |  |  |  |  |
| NBR_PRESENT_VALUES | 009 |  |  |  |  |  |  |  |
| TABLE 021 - ACT_REGS_TBL |  |  |  |  |  |  |  |  |
| REG_FUNC1_FLAGS | 000 |  |  |  |  |  |  |  |
| REG_FUNC2_FLAGS | 001 |  |  |  |  |  |  |  |
| NBR_SELF_READS | 002 |  |  |  |  |  |  |  |
| NBR_SUMMATIONS | 003 |  |  |  |  |  |  |  |
| NBR_DEMANDS | 004 |  |  |  |  |  |  |  |
| NBR_COIN_VALUES | 005 |  |  |  |  |  |  |  |
| NBR_OCCUR | 006 |  |  |  |  |  |  |  |
| NBR_TEIRS | 007 |  |  |  |  |  |  |  |
| NBR_PRESENT_DEMANDS | 008 |  |  |  |  |  |  |  |
| NBR_PRESENT_VALUES | 009 |  |  |  |  |  |  |  |
| TABLE 022 - DATA_SELECTION_TBL |  |  |  |  |  |  |  |  |
| SUMMATION_SELECT(ARRAY) | 000 |  |  |  |  |  |  |  |
| SUMMATION_SELECT(ITEM) | 000 | [n] |  |  |  |  |  |  |
| DEMAND_SELECT(ARRAY) | 001 |  |  |  |  |  |  |  |
| DEMAND_SELECT(ITEM) | 001 | [n] |  |  |  |  |  |  |
| MIN_OR_MAX_FLAGS | 002 |  |  |  |  |  |  |  |
| COINCIDENT_SELECT(ARRAY) | 003 |  |  |  |  |  |  |  |
| COINCIDENT_SELECT(ITEM) | 003 | [n] |  |  |  |  |  |  |
| COIN_DEMAND_ASSOC(ARRAY) | 004 |  |  |  |  |  |  |  |
| COIN_DEMAND_ASSOC(ITEM) | 004 | [n] |  |  |  |  |  |  |
| TABLE 23 - CURRENT_REG_DATA_TBL |  |  |  |  |  |  |  |  |
| NMB_DEMAND_RESETS | 000 |  |  |  |  |  |  |  |
| TOT_DATA_BLOCK | 001 |  |  |  |  |  |  |  |
| SUMMATIONS(ARRAY) | 001 | 000 |  |  |  |  |  |  |
| SUMMATIONS(ITEM) | 001 | 000 | [n] |  |  |  |  |  |
| DEMANDS(ARRAY) | 001 | 001 |  |  |  |  |  |  |
| DEMANDS(ITEM) | 001 | 001 | [n] |  |  |  |  |  |
| EVENT_TIME(ARRAY) | 001 | 001 | [n] | 000 |  |  |  |  |
| EVENT_TIME(ITEM) | 001 | 001 | [n] | 000 | [n] |  |  |  |
| CUM_DEMAND | 001 | 001 | [n] | 001 |  |  |  |  |
| CONT_CUM_DEMAND | 001 | 001 | [n] | 002 |  |  |  |  |
| DEMAND(ARRAY) | 001 | 001 | [n] | 003 |  |  |  |  |
| DEMAND(ITEM) | 001 | 001 | [n] | 003 | [n] |  |  |  |
| COINCIDENTS(ARRAY) | 001 | 002 |  |  |  |  |  |  |
| COINCIDENTS(ITEM) | 001 | 002 | [n] |  |  |  |  |  |
| COINCIDENT_VALUES(ARRAY) | 001 | 002 | [n] | 000 |  |  |  |  |
| COINCIDENT_VALUES(ITEM) | 001 | 002 | [n] | 000 | [n] |  |  |  |
| TIER_DATA_BLOCK(ARRAY) | 002 |  |  |  |  |  |  |  |
| TIER_DATA_BLOCK(ITEM) | 002 | [n] |  |  |  |  |  |  |
| SUMMATIONS (ARRAY) | 002 | [n] | 000 |  |  |  |  |  |
| SUMMATIONS(ITEM) | 002 | [n] | 000 | [n] |  |  |  |  |
| DEMANDS(ARRAY) | 002 | [n] | 001 |  |  |  |  |  |
| DEMANDS(ITEM) | 002 | [n] | 001 | [n] |  |  |  |  |
| EVENT_TIME(ARRAY) | 002 | [n] | 001 | [n] | 000 |  |  |  |
| EVENT_TIME(ITEM) | 002 | [n] | 001 | [n] | 000 | [n] |  |  |
| CUM_DEMAND | 002 | [n] | 001 | [n] | 001 |  |  |  |
| CONT_CUM_DEMAND | 002 | [n] | 001 | [n] | 002 |  |  |  |
| DEMAND(ARRAY) | 002 | [n] | 001 | [n] | 003 |  |  |  |
| DEMAND(ITEM) | 002 | [n] | 001 | [n] | 003 | [n] |  |  |
| COINCIDENTS(ARRAY) | 002 | [n] | 002 |  |  |  |  |  |
| COINCIDENTS(ITEM) | 002 | [n] | 002 | [n] |  |  |  |  |
| COINCIDENT_VALUES(ARRAY) | 002 | [n] | 002 | [n] | 000 |  |  |  |
| COINCIDENT_VALUES(ITEM) | 002 | [n] | 002 | [n] | 000 | [n] |  |  |
| TABLE 24 - PREVIOUS_SEASON_DATA_TBL |  |  |  |  |  |  |  |  |
| REGISTER_INFO | 000 |  |  |  |  |  |  |  |
| END_DATE_TIME | 000 | 000 |  |  |  |  |  |  |
| SEASON | 000 | 001 |  |  |  |  |  |  |
| PREV_SEASON_REG_DATA | 001 |  |  |  |  |  |  |  |
| NMB_DEMAND_RESETS | 001 | 000 |  |  |  |  |  |  |
| TOT_DATA_BLOCK | 001 | 001 |  |  |  |  |  |  |
| SUMMATIONS(ARRAY) | 001 | 001 | 000 |  |  |  |  |  |
| SUMMATIONS(ITEM) | 001 | 001 | 000 | [n] |  |  |  |  |
| DEMANDS(ARRAY) | 001 | 001 | 001 |  |  |  |  |  |
| DEMANDS(ITEM) | 001 | 001 | 001 | [n] |  |  |  |  |
| EVENT_TIME(ARRAY) | 001 | 001 | 001 | [n] | 000 |  |  |  |
| EVENT_TIME(ITEM) | 001 | 001 | 001 | [n] | 000 | [n] |  |  |
| CUM_DEMAND | 001 | 001 | 001 | [n] | 001 |  |  |  |
| CONT_CUM_DEMAND | 001 | 001 | 001 | [n] | 002 |  |  |  |
| DEMAND(ARRAY) | 001 | 001 | 001 | [n] | 003 |  |  |  |
| DEMAND(ITEM) | 001 | 001 | 001 | [n] | 003 | [n] |  |  |
| COINCIDENTS(ARRAY) | 001 | 001 | 002 |  |  |  |  |  |
| COINCIDENTS(ITEM) | 001 | 001 | 002 | [n] |  |  |  |  |
| COINCIDENT_VALUES(ARRAY) | 001 | 001 | 002 | [n] | 000 |  |  |  |
| COINCIDENT_VALUES(ITEM) | 001 | 001 | 002 | [n] | 000 | [n] |  |  |
| TIER_DATA_BLOCK(ARRAY) | 001 | 002 |  |  |  |  |  |  |
| TIER_DATA_BLOCK(ITEM) | 001 | 002 | [n] |  |  |  |  |  |
| SUMMATIONS(ARRAY) | 001 | 002 | [n] | 000 |  |  |  |  |
| SUMMATIONS(ITEM) | 001 | 002 | [n] | 000 | [n] |  |  |  |
| DEMANDS(ARRAY) | 001 | 002 | [n] | 001 |  |  |  |  |
| DEMANDS(ITEM) | 001 | 002 | [n] | 001 | [n] |  |  |  |
| EVENT_TIME(ARRAY) | 001 | 002 | [n] | 001 | [n] | 000 |  |  |
| EVENT_TIME(ITEM) | 001 | 002 | [n] | 001 | [n] | 000 | [n] |  |
| CUM_DEMAND | 001 | 002 | [n] | 001 | [n] | 001 |  |  |
| CONT_CUM_DEMAND | 001 | 002 | [n] | 001 | [n] | 002 |  |  |
| DEMAND(ARRAY) | 001 | 002 | [n] | 001 | [n] | 003 |  |  |
| DEMAND(ITEM) | 001 | 002 | [n] | 001 | [n] | 003 | [n] |  |
| COINCIDENTS(ARRAY) | 001 | 002 | [n] | 002 |  |  |  |  |
| COINCIDENTS(ITEM) | 001 | 002 | [n] | 002 | [n] |  |  |  |
| COINCIDENT_VALUES(ARRAY) | 001 | 002 | [n] | 002 | [n] | 000 |  |  |
| COINCIDENT_VALUES(ITEM) | 001 | 002 | [n] | 002 | [n] | 000 | [n] |  |
| TABLE 25 - PREVIOUS_ DEMAND_RESET_DATA_TBL |  |  |  |  |  |  |  |  |
| REGISTER_INFO | 000 |  |  |  |  |  |  |  |
| END_DATE_TIME | 000 | 000 |  |  |  |  |  |  |
| SEASON | 000 | 001 |  |  |  |  |  |  |
| PREV_DEMAND_RESET_DATA | 001 |  |  |  |  |  |  |  |
| NMB_DEMAND_RESETS | 001 | 000 |  |  |  |  |  |  |
| TOT_DATA_BLOCK | 001 | 001 |  |  |  |  |  |  |
| SUMMATIONS(ARRAY) | 001 | 001 | 000 |  |  |  |  |  |
| SUMMATIONS(ITEM) | 001 | 001 | 000 | [n] |  |  |  |  |
| DEMANDS(ARRAY) | 001 | 001 | 001 |  |  |  |  |  |
| DEMANDS(ITEM) | 001 | 001 | 001 | [n] |  |  |  |  |
| EVENT_TIME(ARRAY) | 001 | 001 | 001 | [n] | 000 |  |  |  |
| EVENT_TIME(ITEM) | 001 | 001 | 001 | [n] | 000 | [n] |  |  |
| CUM_DEMAND | 001 | 001 | 001 | [n] | 001 |  |  |  |
| CONT_CUM_DEMAND | 001 | 001 | 001 | [n] | 002 |  |  |  |
| DEMAND(ARRAY) | 001 | 001 | 001 | [n] | 003 |  |  |  |
| DEMAND(ITEM) | 001 | 001 | 001 | [n] | 003 | [n] |  |  |
| COINCIDENTS(ARRAY) | 001 | 001 | 002 |  |  |  |  |  |
| COINCIDENTS(ITEM) | 001 | 001 | 002 | [n] |  |  |  |  |
| COINCIDENT_VALUES(ARRAY) | 001 | 001 | 002 | [n] | 000 |  |  |  |
| COINCIDENT_VALUES(ITEM) | 001 | 001 | 002 | [n[ | 000 | [n] |  |  |
| TIER_DATA_BLOCK(ARRAY) | 001 | 002 |  |  |  |  |  |  |
| TIER_DATA_BLOCK(ITEM) | 001 | 002 | [n] |  |  |  |  |  |
| SUMMATIONS(ARRAY) | 001 | 002 | [n] | 000 |  |  |  |  |
| SUMMATIONS(ITEM) | 001 | 002 | [n] | 000 | [n] |  |  |  |
| DEMANDS(ARRAY) | 001 | 002 | [n] | 001 |  |  |  |  |
| DEMANDS(ITEM) | 001 | 002 | [n] | 001 | [n] |  |  |  |
| EVENT_TIME(ARRAY) | 001 | 002 | [n] | 001 | [n] | 000 |  |  |
| EVENT_TIME(ITEM) | 001 | 002 | [n] | 001 | [n] | 000 | [n] |  |
| CUM_DEMAND | 001 | 002 | [n] | 001 | [n] | 001 |  |  |
| CONT_CUM_DEMAND | 001 | 002 | [n] | 001 | [n] | 002 |  |  |
| DEMAND(ARRAY) | 001 | 002 | [n] | 001 | [n] | 003 |  |  |
| DEMAND(ITEM) | 001 | 002 | [n] | 001 | [n] | 003 | [n] |  |
| COINCIDENTS(ARRAY) | 001 | 002 | [n] | 002 |  |  |  |  |
| COINCIDENTS(ITEM) | 001 | 002 | [n] | 002 | [n] |  |  |  |
| COINCIDENT_VALUES(ARRAY) | 001 | 002 | [n] | 002 | [n] | 000 |  |  |
| COINCIDENT_VALUES(ITEM) | 001 | 002 | [n] | 002 | [n] | 000 | [n] |  |
| TABLE 26 - SELF_READ_DATA_TBL |  |  |  |  |  |  |  |  |
| LIST_STATUS | 000 |  |  |  |  |  |  |  |
| NBR_VALID_ENTRIES | 001 |  |  |  |  |  |  |  |
| LAST_ENTRY_ELEMENT | 002 |  |  |  |  |  |  |  |
| LAST_ENTRY_SEQ_NUM | 003 |  |  |  |  |  |  |  |
| NBR_UNREAD_ENTRIES | 004 |  |  |  |  |  |  |  |
| SELF_READS_ENTRIES(ARRAY) | 005 |  |  |  |  |  |  |  |
| SELF_READS_ENTRIES(ITEM) | 005 | [n] |  |  |  |  |  |  |
| SELF_READ_SEQ_NUM | 005 | [n] | 000 |  |  |  |  |  |
| REGISTER_INFO | 005 | [n] | 001 |  |  |  |  |  |
| END_DATE_TIME | 005 | [n] | 001 | 000 |  |  |  |  |
| SEASON | 005 | [n] | 001 | 001 |  |  |  |  |
| SELF_READ_REGISTER_DATA | 005 | [n] | 002 |  |  |  |  |  |
| NMB_DEMAND_RESETS | 005 | [n] | 002 | 000 |  |  |  |  |
| TOT_DATA_BLOCK | 005 | [n] | 002 | 001 |  |  |  |  |
| SUMMATIONS(ARRAY) | 005 | [n] | 002 | 001 | 000 |  |  |  |
| SUMMATIONS(ITEM) | 005 | [n] | 002 | 001 | 000 | [n] |  |  |
| DEMANDS(ARRAY) | 005 | [n] | 001 | 001 | 001 |  |  |  |
| DEMANDS(ITEM) | 005 | [n] | 002 | 001 | 001 | [n] |  |  |
| EVENT_TIME(ARRAY) | 005 | [n] | 002 | 001 | 001 | [n] | 000 |  |
| EVENT_TIME(ITEM) | 005 | [n] | 002 | 001 | 001 | [n] | 000 | [n] |
| CUM_DEMAND | 005 | [n] | 002 | 001 | 001 | [n] | 001 |  |
| CONT_CUM_DEMAND | 005 | [n] | 002 | 001 | 001 | [n] | 002 |  |
| DEMAND(ARRAY) | 005 | [n] | 002 | 001 | 001 | [n] | 003 |  |
| DEMAND(ITEM) | 005 | [n] | 002 | 001 | 001 | [n] | 003 | [n] |
| COINCIDENTS(ARRAY) | 005 | [n] | 002 | 001 | 002 |  |  |  |
| COINCIDENTS(ITEM) | 005 | [n] | 002 | 001 | 002 | [n] |  |  |
| COINCIDENT_VALUES(ARR) | 005 | [n] | 002 | 001 | 002 | [n] | 000 |  |
| COINCIDENT_VALUES(ITM) | 005 | [n] | 002 | 001 | 002 | [n] | 000 | [n] |
| TIER_DATA_BLOCK(ARRAY) | 005 | [n] | 003 |  |  |  |  |  |
| TIER_DATA_BLOCK(ITEM) | 005 | [n] | 003 | [n] |  |  |  |  |
| SUMMATIONS(ARRAY) | 005 | [n] | 003 | [n] | 000 | 000 |  |  |
| SUMMATIONS(ITEM) | 005 | [n] | 003 | [n] | 000 | [n] |  |  |
| DEMANDS(ARRAY) | 005 | [n] | 003 | [n] | 001 |  |  |  |
| DEMANDS(ITEM) | 005 | [n] | 003 | [n] | 001 | [n] |  |  |
| EVERY_TIME(ARRAY) | 005 | [n] | 003 | [n] | 001 | [n] | 000 |  |
| EVERY_TIME(ITEM) | 005 | [n] | 003 | [n] | 001 | [n] | 000 | [n] |
| CUM_DEMAND | 005 | [n] | 003 | [n] | 001 | [n] | 001 |  |
| DEMAND(ARRAY) | 005 | [n] | 003 | [n] | 001 | [n] | 002 |  |
| DEMAND(ITEM) | 005 | [n] | 003 | [n] | 001 | [n] | 002 | [n] |
| COINCIDENTS(ARRAY) | 005 | [n] | 003 | [n] | 002 |  |  |  |
| COINCIDENTS(ITEM) | 005 | [n] | 003 | [n] | 002 | [n] |  |  |
| COINCIDENT_VALUES(ARR) | 005 | [n] | 003 | [n] | 002 | [n] | 000 |  |
| COINCIDENT_VALUES(ITM) | 005 | [n] | 003 | [n] | 002 | [n] | 000 | [n] |
| TABLE 027 - PRESENT_REGISTER_SELECT_TBL |  |  |  |  |  |  |  |  |
| PRESENT_DEMAND_SELECT(ARRAY) | 000 |  |  |  |  |  |  |  |
| PRESENT_DEMAND_SELECT(ITEM) | 000 | [n] |  |  |  |  |  |  |
| PRESENT_VALUE_SELECT(ARRAY) | 001 |  |  |  |  |  |  |  |
| PRESENT_VALUE_SELECT(ITEM) | 001 | [n] |  |  |  |  |  |  |
| TABLE 028 - PRESENT_REGISTER_DATA_TBL |  |  |  |  |  |  |  |  |
| PRESENT_DEMAND(ARRAY) | 000 |  |  |  |  |  |  |  |
| PRESENT_DEMAND(ITEM) | 000 | [n] |  |  |  |  |  |  |
| TIME_REMAINING | 000 | [n] | 000 |  |  |  |  |  |
| DEMAND_VALUE | 000 | [n] | 001 |  |  |  |  |  |
| PRESENT_VALUE(ARRAY) | 001 |  |  |  |  |  |  |  |
| PRESENT_VALUE(ITEM) | 001 | [n] |  |  |  |  |  |  |
| TABLE 030 - DIM_DISP_TBL |  |  |  |  |  |  |  |  |
| DISPLAY_CTRL | 000 |  |  |  |  |  |  |  |
| NBR_DISP_SOURCES | 001 |  |  |  |  |  |  |  |
| WIDTH_DISP_SOURCES | 002 |  |  |  |  |  |  |  |
| NBR_PRI_DISP_LIST_ITEMS | 003 |  |  |  |  |  |  |  |
| NBR_PRI_DISP_LISTS | 004 |  |  |  |  |  |  |  |
| NBR_SEC_DISP_LIST_ITEMS | 005 |  |  |  |  |  |  |  |
| NBR_SEC_DISP_LISTS | 006 |  |  |  |  |  |  |  |
| TABLE 031 - ACT_DISP_TBL |  |  |  |  |  |  |  |  |
| DISPLAY_CTRL | 000 |  |  |  |  |  |  |  |
| NBR_DISP_SOURCES | 001 |  |  |  |  |  |  |  |
| WIDTH_DISP_SOURCES | 002 |  |  |  |  |  |  |  |
| NBR_PRI_DISP_LIST_ITEMS | 003 |  |  |  |  |  |  |  |
| NBR_PRI_DISP_LISTS | 004 |  |  |  |  |  |  |  |
| NBR_SEC_DISP_LIST_ITEMS | 005 |  |  |  |  |  |  |  |
| NBR_SEC_DISP_LISTS | 006 |  |  |  |  |  |  |  |
| TABLE 032 - DISP_SOURCE_TBL |  |  |  |  |  |  |  |  |
| DISPLAY_SOURCES(ARRAY) | 000 |  |  |  |  |  |  |  |
| DISPLAY_SOURCES(ITEM) | 000 | [n] |  |  |  |  |  |  |
| DISPLAY_SOURCE(ARRAY) | 000 | [n] | 000 |  |  |  |  |  |
| DISPLAY_SOURCE(ITEM) | 000 | [n] | 000 | [n] |  |  |  |  |
| TABLE 033 - PRI_DISP_LIST_TBL |  |  |  |  |  |  |  |  |
| PRI_DISP_LIST(ARRAY) | 000 |  |  |  |  |  |  |  |
| PRI_DISP_LIST(ITEM) | 000 | [n] |  |  |  |  |  |  |
| DISP_SCROLL1 | 000 | [n] | 000 |  |  |  |  |  |
| DISP_SCROLL2 | 000 | [n] | 001 |  |  |  |  |  |
| NBR_LIST_ITEMS | 000 | [n] | 002 |  |  |  |  |  |
| PRI_DISP_SOURCES(ARRAY) | 001 |  |  |  |  |  |  |  |
| PRI_DISP_SOURCES(ITEM) | 001 | [n] |  |  |  |  |  |  |
| TABLE 034 - SEC_DISP_LIST_TBL |  |  |  |  |  |  |  |  |
| SEC_DISP_LIST(ARRAY) | 000 |  |  |  |  |  |  |  |
| SEC_DISP_LIST(ITEM) | 000 | [n] |  |  |  |  |  |  |
| DISP_SCROLL1 | 000 | [n] | 000 |  |  |  |  |  |
| DISP_SCROLL2 | 000 | [n] | 001 |  |  |  |  |  |
| NBR_LIST_ITEMS | 000 | [n] | 002 |  |  |  |  |  |
| SEC_DISP_SOURCES(ARRAY) | 001 |  |  |  |  |  |  |  |
| SEC_DISP_SOURCES(ITEM) | 001 | [n] |  |  |  |  |  |  |
| TABLE 040 - DIM_SECURITY_LIMITING_TBL |  |  |  |  |  |  |  |  |
| NBR_PASSWORDS | 000 |  |  |  |  |  |  |  |
| PASWWORD_LEN | 001 |  |  |  |  |  |  |  |
| NBR_KEYS | 002 |  |  |  |  |  |  |  |
| KEY_LEN | 003 |  |  |  |  |  |  |  |
| NBR_PERM_USED | 004 |  |  |  |  |  |  |  |
| TABLE 041 - ACT_SECURITY_LIMITING_TBL |  |  |  |  |  |  |  |  |
| NBR_PASSWORDS | 000 |  |  |  |  |  |  |  |
| PASWWORD_LEN | 001 |  |  |  |  |  |  |  |
| NBR_KEYS | 002 |  |  |  |  |  |  |  |
| KEY_LEN | 003 |  |  |  |  |  |  |  |
| NBR_PERM_USED | 004 |  |  |  |  |  |  |  |
| TABLE 042 - SECURITY_TBL |  |  |  |  |  |  |  |  |
| SECURITY_ENTRIES(ARRAY) | 000 |  |  |  |  |  |  |  |
| SECURITY_ENTRIES(ITEM) | 000 | [n] |  |  |  |  |  |  |
| PASSWORD | 000 | [n] | 000 |  |  |  |  |  |
| ACCESS_PERMISSIONS | 000 | [n] | 001 |  |  |  |  |  |
| TABLE 043 - DEFAULT_ACCESS_CONTROL_TBL |  |  |  |  |  |  |  |  |
| TABLE_DEFAULT | 000 |  |  |  |  |  |  |  |
| ACCESS_TABLE_DEFAULT | 000 | 000 |  |  |  |  |  |  |
| READ | 000 | 001 |  |  |  |  |  |  |
| WRITE | 000 | 002 |  |  |  |  |  |  |
| PROCEDURE_DEFAULT | 001 |  |  |  |  |  |  |  |
| ACCESS_TABLE_DEFAULT | 001 | 000 |  |  |  |  |  |  |
| READ | 001 | 001 |  |  |  |  |  |  |
| WRITE | 001 | 002 |  |  |  |  |  |  |
| TABLE 044 - ACCESS_CONTROL_TBL |  |  |  |  |  |  |  |  |
| ACCESS_CONTROL(ARRAY) | 000 |  |  |  |  |  |  |  |
| ACCESS_CONTROL(ITEM) | 000 | [n] |  |  |  |  |  |  |
| ACCESS_TABLE_DEF | 000 | [n] | 000 |  |  |  |  |  |
| READ | 000 | [n] | 001 |  |  |  |  |  |
| WRITE | 000 | [n] | 002 |  |  |  |  |  |
| TABLE 045 - KEY_TBL |  |  |  |  |  |  |  |  |
| KEY_ENTRIES(ARRAY) | 000 |  |  |  |  |  |  |  |
| KEY_ENTRIES(ITEM) | 000 | [n] |  |  |  |  |  |  |
| KEY(ARRAY) | 000 | [n] | 000 |  |  |  |  |  |
| KEY(ITEM) | 000 | [n] | 000 | [n] |  |  |  |  |
| TABLE 050 - DIM_TIME_TOU_TBL |  |  |  |  |  |  |  |  |
| TIME_FUNC_FLAG1 | 000 |  |  |  |  |  |  |  |
| TIME_FUNC_FLAG2 | 001 |  |  |  |  |  |  |  |
| CALENDAR_FUNC | 002 |  |  |  |  |  |  |  |
| NBR_NON_RECURR_DATES | 003 |  |  |  |  |  |  |  |
| NBR_RECURR_DATES | 004 |  |  |  |  |  |  |  |
| NBR_TEIR_SWITCHES | 005 |  |  |  |  |  |  |  |
| CALENDAR_TBL_SIZE | 006 |  |  |  |  |  |  |  |
| TABLE 051- ACT_TIME_TOU_TBL |  |  |  |  |  |  |  |  |
| TIME_FUNC_FLAG1 | 000 |  |  |  |  |  |  |  |
| TIME_FUNC_FLAG2 | 001 |  |  |  |  |  |  |  |
| CALENDAR_FUNC | 002 |  |  |  |  |  |  |  |
| NBR_NON_RECURR_DATES | 003 |  |  |  |  |  |  |  |
| NBR_RECURR_DATES | 004 |  |  |  |  |  |  |  |
| NBR_TEIR_SWITCHES | 005 |  |  |  |  |  |  |  |
| CALENDAR_TBL_SIZE | 006 |  |  |  |  |  |  |  |
| TABLE 052 - CLOCK_TBL |  |  |  |  |  |  |  |  |
| CLOCK_CALENDAR | 000 |  |  |  |  |  |  |  |
| TIME_DATE_QUAL | 001 |  |  |  |  |  |  |  |
| TABLE 053 - TIME_OFFSET_TBL |  |  |  |  |  |  |  |  |
| DST_TIME_EFF | 000 |  |  |  |  |  |  |  |
| DST_TIME_AMT | 001 |  |  |  |  |  |  |  |
| TIME_ZONE_OFFSET | 002 |  |  |  |  |  |  |  |
| TABLE 054 - CALENDAR_TBL |  |  |  |  |  |  |  |  |
| ANCHOR_DATE | 000 |  |  |  |  |  |  |  |
| NON_RECURR_DATES(ARRAY) | 001 |  |  |  |  |  |  |  |
| NON_RECURR_DATES(ITEM) | 001 | [n] |  |  |  |  |  |  |
| NON_RECURR_DATE | 001 | [n] | 000 |  |  |  |  |  |
| CALENDAR_ACTION | 001 | [n] | 001 |  |  |  |  |  |
| RECURR_DATES(ARRAY) | 002 |  |  |  |  |  |  |  |
| RECURR_DATES(ITEM) | 002 | [n] |  |  |  |  |  |  |
| RECURR_DATE | 002 | [n] | 000 |  |  |  |  |  |
| CALENDAR_ACTION | 002 | [n] | 001 |  |  |  |  |  |
| TIER_SWITCHES(ARRAY) | 003 |  |  |  |  |  |  |  |
| TIER_SWITCHES(ITEM) | 003 | [n] |  |  |  |  |  |  |
| TIER_SWITCH | 003 | [n] | 000 |  |  |  |  |  |
| DAY_SCH_NUM | 003 | [n] | 001 |  |  |  |  |  |
| DAY_SCHEDULE_ID_MATRIX(ARRAY) | 004 |  |  |  |  |  |  |  |
| DAY_SCHEDULE_ID_MATRIX(ITEM) | 004 | [n] |  |  |  |  |  |  |
| TABLE 055 - CLOCK_STATE_TBL |  |  |  |  |  |  |  |  |
| CLOCK_CALANDER | 000 |  |  |  |  |  |  |  |
| TIME_DATE_QUAL | 001 |  |  |  |  |  |  |  |
| STATUS | 002 |  |  |  |  |  |  |  |
| TABLE 056 - TIME_REMAIN_TBL |  |  |  |  |  |  |  |  |
| SUMM_TIER_TIME_REMAIN | 000 |  |  |  |  |  |  |  |
| DEMAND_TIER_TIME_REMAIN | 001 |  |  |  |  |  |  |  |
| TIER_TIME_REMAIN | 002 |  |  |  |  |  |  |  |
| SELF_READ_DAYS_REMAIN | 003 |  |  |  |  |  |  |  |
| TABLE 060 - DIM_LP_TBL |  |  |  |  |  |  |  |  |
| LP_MEMORY_LEN | 000 |  |  |  |  |  |  |  |
| LP_FLAGS | 001 |  |  |  |  |  |  |  |
| LP_FMATS | 002 |  |  |  |  |  |  |  |
| NBR_BLKS_SET1 | 003 |  |  |  |  |  |  |  |
| NBR_BLK_INTS_SET1 | 004 |  |  |  |  |  |  |  |
| NBR_CHNS_SET1 | 005 |  |  |  |  |  |  |  |
| MAX_INT_TIME_SET1 | 006 |  |  |  |  |  |  |  |
| NBR_BLKS_SET2 | 007 |  |  |  |  |  |  |  |
| NBR_BLK_INTS_SET2 | 008 |  |  |  |  |  |  |  |
| NBR_CHNS_SET2 | 009 |  |  |  |  |  |  |  |
| MAX_INT_TIME_SET2 | 010 |  |  |  |  |  |  |  |
| NBR_BLKS_SET3 | 011 |  |  |  |  |  |  |  |
| NBR_BLK_INTS_SET3 | 012 |  |  |  |  |  |  |  |
| NBR_CHNS_SET3 | 013 |  |  |  |  |  |  |  |
| MAX_INT_TIME_SET3 | 014 |  |  |  |  |  |  |  |
| NBR_BLKS_SET4 | 015 |  |  |  |  |  |  |  |
| NBR_BLK_INTS_SET4 | 016 |  |  |  |  |  |  |  |
| NBR_CHNS_SET4 | 017 |  |  |  |  |  |  |  |
| MAX_INT_TIME_SET4 | 018 |  |  |  |  |  |  |  |
| TABLE 061- ACT_LP_TBL |  |  |  |  |  |  |  |  |
| LP_MEMORY_LEN | 000 |  |  |  |  |  |  |  |
| LP_FLAGS | 001 |  |  |  |  |  |  |  |
| LP_FMATS | 002 |  |  |  |  |  |  |  |
| NBR_BLKS_SET1 | 003 |  |  |  |  |  |  |  |
| NBR_BLK_INTS_SET1 | 004 |  |  |  |  |  |  |  |
| NBR_CHNS_SET1 | 005 |  |  |  |  |  |  |  |
| MAX_INT_TIME_SET1 | 006 |  |  |  |  |  |  |  |
| NBR_BLKS_SET2 | 007 |  |  |  |  |  |  |  |
| NBR_BLK_INTS_SET2 | 008 |  |  |  |  |  |  |  |
| NBR_CHNS_SET2 | 009 |  |  |  |  |  |  |  |
| MAX_INT_TIME_SET2 | 010 |  |  |  |  |  |  |  |
| NBR_BLKS_SET3 | 011 |  |  |  |  |  |  |  |
| NBR_BLK_INTS_SET3 | 012 |  |  |  |  |  |  |  |
| NBR_CHNS_SET3 | 013 |  |  |  |  |  |  |  |
| MAX_INT_TIME_SET3 | 014 |  |  |  |  |  |  |  |
| NBR_BLKS_SET4 | 015 |  |  |  |  |  |  |  |
| NBR_BLK_INTS_SET4 | 016 |  |  |  |  |  |  |  |
| NBR_CHNS_SET4 | 017 |  |  |  |  |  |  |  |
| MAX_INT_TIME_SET4 | 018 |  |  |  |  |  |  |  |
| TABLE 062 - LP_CNTL_TBL |  |  |  |  |  |  |  |  |
| LP_SEL_SET1(ARRAY) | 000 |  |  |  |  |  |  |  |
| LP_SEL_SET1(ITEM) | 000 | [n] |  |  |  |  |  |  |
| CHNL_FLAG | 000 | [n] | 000 |  |  |  |  |  |
| INT_SOURCE_SELECT | 000 | [n] | 001 |  |  |  |  |  |
| END_BLK_RDG_SOURCE_SELECT | 000 | [n] | 002 |  |  |  |  |  |
| INT_FMT_CDE1 | 001 |  |  |  |  |  |  |  |
| SCALARS_SET1 | 002 |  |  |  |  |  |  |  |
| DIVISORS_SET1 | 003 |  |  |  |  |  |  |  |
| LP_SEL_SET2(ARRAY) | 004 |  |  |  |  |  |  |  |
| LP_SEL_SET2(ITEM) | 004 | [n] |  |  |  |  |  |  |
| CHNL_FLAG | 004 | [n] | 000 |  |  |  |  |  |
| INT_SOURCE_SELECT | 004 | [n] | 001 |  |  |  |  |  |
| END_BLK_RDG_SOURCE_SELECT | 004 | [n] | 002 |  |  |  |  |  |
| INT_FMT_CDE2 | 005 |  |  |  |  |  |  |  |
| SCALARS_SET2 | 006 |  |  |  |  |  |  |  |
| DIVISORS_SET2 | 007 |  |  |  |  |  |  |  |
| LP_SEL_SET3(ARRAY) | 008 |  |  |  |  |  |  |  |
| LP_SEL_SET3(ITEM) | 008 | [n] |  |  |  |  |  |  |
| CHNL_FLAG | 008 | [n] | 000 |  |  |  |  |  |
| INT_SOURCE_SELECT | 008 | [n] | 001 |  |  |  |  |  |
| END_BLK_RDG_SOURCE_SELECT | 008 | [n] | 002 |  |  |  |  |  |
| INT_FMT_CDE3 | 009 |  |  |  |  |  |  |  |
| SCALARS_SET3 | 010 |  |  |  |  |  |  |  |
| DIVISORS_SET3 | 011 |  |  |  |  |  |  |  |
| LP_SEL_SET4(ARRAY) | 012 |  |  |  |  |  |  |  |
| LP_SEL_SET4(ITEM) | 012 | [n] |  |  |  |  |  |  |
| CHNL_FLAG | 012 | [n] | 000 |  |  |  |  |  |
| INT_SOURCE_SELECT | 012 | [n] | 001 |  |  |  |  |  |
| END_BLK_RDG_SOURCE_SELECT | 012 | [n] | 002 |  |  |  |  |  |
| INT_FMT_CDE4 | 013 |  |  |  |  |  |  |  |
| SCALARS_SET4 | 014 |  |  |  |  |  |  |  |
| DIVISORS_SET4 | 015 |  |  |  |  |  |  |  |
| TABLE 063 - LP_STATUS_TBL |  |  |  |  |  |  |  |  |
| LP_STATUS_SET1 | 000 |  |  |  |  |  |  |  |
| LP_SET_STATUS_FLAGS | 000 | 000 |  |  |  |  |  |  |
| NBR_VALID_BLOCKS | 000 | 001 |  |  |  |  |  |  |
| LAST_BLOCK_ELEMENT | 000 | 002 |  |  |  |  |  |  |
| LAST_BLOCK_SEQ_NUM | 000 | 003 |  |  |  |  |  |  |
| NBR_UNREAD_BLOCKS | 000 | 004 |  |  |  |  |  |  |
| NBR_VALID_INT | 000 | 005 |  |  |  |  |  |  |
| LP_STATUS_SET2 | 001 |  |  |  |  |  |  |  |
| LP_SET_STATUS_FLAGS | 001 | 000 |  |  |  |  |  |  |
| NBR_VALID_BLOCKS | 001 | 001 |  |  |  |  |  |  |
| LAST_BLOCK_ELEMENT | 001 | 002 |  |  |  |  |  |  |
| LAST_BLOCK_SEQ_NUM | 001 | 003 |  |  |  |  |  |  |
| NBR_UNREAD_BLOCKS | 001 | 004 |  |  |  |  |  |  |
| NBR_VALID_INT | 001 | 005 |  |  |  |  |  |  |
| LP_STATUS_SET3 | 002 |  |  |  |  |  |  |  |
| LP_SET_STATUS_FLAGS | 002 | 000 |  |  |  |  |  |  |
| NBR_VALID_BLOCKS | 002 | 001 |  |  |  |  |  |  |
| LAST_BLOCK_ELEMENT | 002 | 002 |  |  |  |  |  |  |
| LAST_BLOCK_SEQ_NUM | 002 | 003 |  |  |  |  |  |  |
| NBR_UNREAD_BLOCKS | 002 | 004 |  |  |  |  |  |  |
| NBR_VALID_INT | 002 | 005 |  |  |  |  |  |  |
| LP_STATUS_SET4 | 003 |  |  |  |  |  |  |  |
| LP_SET_STATUS_FLAGS | 003 | 000 |  |  |  |  |  |  |
| NBR_VALID_BLOCKS | 003 | 001 |  |  |  |  |  |  |
| LAST_BLOCK_ELEMENT | 003 | 002 |  |  |  |  |  |  |
| LAST_BLOCK_SEQ_NUM | 003 | 003 |  |  |  |  |  |  |
| NBR_UNREAD_BLOCKS | 003 | 004 |  |  |  |  |  |  |
| NBR_VALID_INT | 003 | 005 |  |  |  |  |  |  |
| TABLE 064 - LP_DATA_SET1_TBL |  |  |  |  |  |  |  |  |
| LP_DATA_SETS1(ARRAY) | 000 |  |  |  |  |  |  |  |
| LP_DATA_SETS1(ITEM) | 000 | [n] |  |  |  |  |  |  |
| BLK_END_TIME | 000 | [n] | 000 |  |  |  |  |  |
| END_READINGS(ARRAY) | 000 | [n] | 001 |  |  |  |  |  |
| END_READINGS(ITEM) | 000 | [n] | 001 | [n] |  |  |  |  |
| BLOCK_END_READ | 000 | [n] | 001 | [n] | 000 |  |  |  |
| BLOCK_END_PLUSE | 000 | [n] | 001 | [n] | 001 |  |  |  |
| SIMPLE_INT_STATUS | 000 | [N] | 002 |  |  |  |  |  |
| LP_INT(ARRAY) | 000 | [n] | 003 |  |  |  |  |  |
| LP_INT(ITEM) | 000 | [n] | 003 | [n] |  |  |  |  |
| EXTENDED_INT_STATUS(ARRAY) | 000 | [n] | 003 | [n] | 000 |  |  |  |
| EXTENDED_INT_STATUS(ITEM) | 000 | [n] | 003 | [n] | 000 | [n] |  |  |
| INT_DATA(ARRAY) | 000 | [n] | 003 | [n] | 001 |  |  |  |
| INT_DATA(ITEM) | 000 | [n] | 003 | [n] | 001 | [n] |  |  |
| ITEM(UINT8) | 000 | [n] | 003 | [n] | 001 | [n] | 000 |  |
| ITEM(UINT16) | 000 | [n] | 003 | [n] | 001 | [n] | 001 |  |
| ITEM(UINT32) | 000 | [n] | 003 | [n] | 001 | [n] | 002 |  |
| ITEM(INT8) | 000 | [n] | 003 | [n] | 001 | [n] | 003 |  |
| ITEM(INT16) | 000 | [n] | 003 | [n] | 001 | [n] | 004 |  |
| ITEM(INT32) | 000 | [n] | 003 | [n] | 001 | [n] | 005 |  |
| ITEM(NI_FMAT1) | 000 | [n] | 003 | [n] | 001 | [n] | 006 |  |
| ITEM(NI_FMAT2) | 000 | [n] | 003 | [n] | 001 | [n] | 007 |  |
| TABLE 065 - LP_DATA_SET2_TBL |  |  |  |  |  |  |  |  |
| LP_DATA_SETS2(ARRAY) | 000 |  |  |  |  |  |  |  |
| LP_DATA_SETS2(ITEM) | 000 | [n] |  |  |  |  |  |  |
| BLK_END_TIME | 000 | [n] | 000 |  |  |  |  |  |
| END_READINGS(ARRAY) | 000 | [n] | 001 |  |  |  |  |  |
| END_READINGS(ITEM) | 000 | [n] | 001 | [n] |  |  |  |  |
| BLOCK_END_READ | 000 | [n] | 001 | [n] | 000 |  |  |  |
| BLOCK_END_PLUSE | 000 | [n] | 001 | [n] | 001 |  |  |  |
| SIMPLE_INT_STATUS | 000 | [n] | 002 |  |  |  |  |  |
| LP_INT(ARRAY) | 000 | [n] | 003 |  |  |  |  |  |
| LP_INT(ITEM) | 000 | [n] | 003 | [n] |  |  |  |  |
| EXTENDED_INT_STATUS(ARRAY) | 000 | [n] | 003 | [n] | 000 |  |  |  |
| EXTENDED_INT_STATUS(ITEM) | 000 | [n] | 003 | [n] | 000 | [n] |  |  |
| INT_DATA(ARRAY) | 000 | [n] | 003 | [n] | 001 |  |  |  |
| INT_DATA(ITEM) | 000 | [n] | 003 | [n] | 001 | [n] |  |  |
| ITEM(UINT8) | 000 | [n] | 003 | [n] | 001 | [n] | 000 |  |
| ITEM(UINT16) | 000 | [n] | 003 | [n] | 001 | [n] | 001 |  |
| ITEM(UINT32) | 000 | [n] | 003 | [n] | 001 | [n] | 002 |  |
| ITEM(INT8) | 000 | [n] | 003 | [n] | 001 | [n] | 003 |  |
| ITEM(INT16) | 000 | [n] | 003 | [n] | 001 | [n] | 004 |  |
| ITEM(INT32) | 000 | [n] | 003 | [n] | 001 | [n] | 005 |  |
| ITEM(NI_FMAT1) | 000 | [n] | 003 | [n] | 001 | [n] | 006 |  |
| ITEM(NI_FMAT2) | 000 | [n] | 003 | [n] | 001 | [n] | 007 |  |
| TABLE 066 - LP_DATA_SET3_TBL |  |  |  |  |  |  |  |  |
| LP_DATA_SETS3(ARRAY) | 000 |  |  |  |  |  |  |  |
| LP_DATA_SETS3(ITEM) | 000 | [n] |  |  |  |  |  |  |
| BLK_END_TIME | 000 | [n] | 000 |  |  |  |  |  |
| END_READINGS(ARRAY) | 000 | [n] | 001 |  |  |  |  |  |
| END_READINGS(ITEM) | 000 | [n] | 001 | [n] |  |  |  |  |
| BLOCK_END_READ | 000 | [n] | 001 | [n] | 000 |  |  |  |
| BLOCK_END_PLUSE | 000 | [n] | 001 | [n] | 001 |  |  |  |
| SIMPLE_INT_STATUS | 000 | [n] | 002 |  |  |  |  |  |
| LP_INT(ARRAY) | 000 | [n] | 003 |  |  |  |  |  |
| LP_INT(ITEM) | 000 | [n] | 003 | [n] |  |  |  |  |
| EXTENDED_INT_STATUS(ARRAY) | 000 | [n] | 003 | [n] | 000 |  |  |  |
| EXTENDED_INT_STATUS(ITEM) | 000 | [n] | 003 | [n] | 000 | [n] |  |  |
| INT_DATA(ARRAY) | 000 | [n] | 003 | [n] | 001 |  |  |  |
| INT_DATA(ITEM) | 000 | [n] | 003 | [n] | 001 | [n] |  |  |
| ITEM(UINT8) | 000 | [n] | 003 | [n] | 001 | [n] | 000 |  |
| ITEM(UINT16) | 000 | [n] | 003 | [n] | 001 | [n] | 001 |  |
| ITEM(UINT32) | 000 | [n] | 003 | [n] | 001 | [n] | 002 |  |
| ITEM(INT8) | 000 | [n] | 003 | [n] | 001 | [n] | 003 |  |
| ITEM(INT16) | 000 | [n] | 003 | [n] | 001 | [n] | 004 |  |
| ITEM(INT32) | 000 | [n] | 003 | [n] | 001 | [n] | 005 |  |
| ITEM(NI_FMAT1) | 000 | [n] | 003 | [n] | 001 | [n] | 006 |  |
| ITEM(NI_FMAT2) | 000 | [n] | 003 | [n] | 001 | [n] | 007 |  |
| TABLE 067 - LP_DATA_SET4_TBL |  |  |  |  |  |  |  |  |
| LP_DATA_SETS4(ARRAY) | 000 |  |  |  |  |  |  |  |
| LP_DATA_SETS4(ITEM) | 000 | [n] |  |  |  |  |  |  |
| BLK_END_TIME | 000 | [n] | 000 |  |  |  |  |  |
| END_READINGS(ARRAY) | 000 | [n] | 001 |  |  |  |  |  |
| END_READINGS(ITEM) | 000 | [n] | 001 | [n] |  |  |  |  |
| BLOCK_END_READ | 000 | [n] | 001 | [n] | 000 |  |  |  |
| BLOCK_END_PLUSE | 000 | [n] | 001 | [n] | 001 |  |  |  |
| SIMPLE_INT_STATUS | 000 | [n] | 002 |  |  |  |  |  |
| LP_INT(ARRAY) | 000 | [n] | 003 |  |  |  |  |  |
| LP_INT(ITEM) | 000 | [n] | 003 | [n] |  |  |  |  |
| EXTENDED_INT_STATUS(ARRAY) | 000 | [n] | 003 | [n] | 000 |  |  |  |
| EXTENDED_INT_STATUS(ITEM) | 000 | [n] | 003 | [n] | 000 | [n] |  |  |
| INT_DATA(ARRAY) | 000 | [n] | 003 | [n] | 001 |  |  |  |
| INT_DATA(ITEM) | 000 | [n] | 003 | [n] | 001 | [n] |  |  |
| ITEM(UINT8) | 000 | [n] | 003 | [n] | 001 | [n] | 000 |  |
| ITEM(UINT16) | 000 | [n] | 003 | [n] | 001 | [n] | 001 |  |
| ITEM(UINT32) | 000 | [n] | 003 | [n] | 001 | [n] | 002 |  |
| ITEM(INT8) | 000 | [n] | 003 | [n] | 001 | [n] | 003 |  |
| ITEM(INT16) | 000 | [n] | 003 | [n] | 001 | [n] | 004 |  |
| ITEM(INT32) | 000 | [n] | 003 | [n] | 001 | [n] | 005 |  |
| ITEM(NI_FMAT1) | 000 | [n] | 003 | [n] | 001 | [n] | 006 |  |
| ITEM(NI_FMAT2) | 000 | [n] | 003 | [n] | 001 | [n] | 007 |  |
| TABLE 070 - DIM_LOG_TBL |  |  |  |  |  |  |  |  |
| LOG_FLAGS | 001 |  |  |  |  |  |  |  |
| NBR_STD_EVENTS | 002 |  |  |  |  |  |  |  |
| NBR_MFG_EVENTS | 003 |  |  |  |  |  |  |  |
| HIST_DATA_LENGTH | 004 |  |  |  |  |  |  |  |
| EVENT_DATA_LENGTH | 005 |  |  |  |  |  |  |  |
| NBR_HISTORY_ENTRIES | 006 |  |  |  |  |  |  |  |
| NBR_EVENT_ENTRIES | 007 |  |  |  |  |  |  |  |
| TABLE 071 - ACT_LOG_TBL |  |  |  |  |  |  |  |  |
| LOG_FLAGS | 001 |  |  |  |  |  |  |  |
| NBR_STD_EVENTS | 002 |  |  |  |  |  |  |  |
| NBR_MFG_EVENTS | 003 |  |  |  |  |  |  |  |
| HIST_DATA_LENGTH | 004 |  |  |  |  |  |  |  |
| EVENT_DATA_LENGTH | 005 |  |  |  |  |  |  |  |
| NBR_HISTORY_ENTRIES | 006 |  |  |  |  |  |  |  |
| NBR_EVENT_ENTRIES | 007 |  |  |  |  |  |  |  |
| TABLE 072 - EVENTS_ID_TBL |  |  |  |  |  |  |  |  |
| STD_EVENTS_SUPPORTED | 000 |  |  |  |  |  |  |  |
| MFG_EVENTS_SUPPORTED | 001 |  |  |  |  |  |  |  |
| TABLE 073 -HISTORY_LOG_CTRL_TBL |  |  |  |  |  |  |  |  |
| STD_EVENTS_MONITORED_FLAGS | 000 |  |  |  |  |  |  |  |
| MFG_EVENTS_MONITORED_FLAGS | 001 |  |  |  |  |  |  |  |
| STD_TBLS_MONITORED_FLAGS | 002 |  |  |  |  |  |  |  |
| MFG_TBLS_MONITORED_FLAGS | 003 |  |  |  |  |  |  |  |
| STD_PROC_MONITORED_FLAGS | 004 |  |  |  |  |  |  |  |
| MFG_PROC_MONITORED_FLAGS | 005 |  |  |  |  |  |  |  |
| TABLE 074 - HISTORY_LOG_DATA_TBL |  |  |  |  |  |  |  |  |
| HIST_FLAGS | 000 |  |  |  |  |  |  |  |
| NBR_VALID_ENTRIES | 001 |  |  |  |  |  |  |  |
| LAST_ENTRY_ELEMENT | 002 |  |  |  |  |  |  |  |
| LAST_ENTRY_SEQ_NBR | 003 |  |  |  |  |  |  |  |
| NBR_UNREAD_ENTRIES | 004 |  |  |  |  |  |  |  |
| ENTRIES(ARRAY) | 005 |  |  |  |  |  |  |  |
| ENTRIES(ITEM) | 005 | [n] |  |  |  |  |  |  |
| HISTORY_TIME | 005 | [n] | 000 |  |  |  |  |  |
| EVENT_NUMBER | 005 | [n] | 001 |  |  |  |  |  |
| HISTORY_SEQ_NBR | 005 | [n] | 002 |  |  |  |  |  |
| USER_ID | 005 | [n] | 003 |  |  |  |  |  |
| HISTORY_CODE | 005 | [n] | 004 |  |  |  |  |  |
| HISTORY_ARGUMENT(ARRAY) | 005 | [n] | 005 |  |  |  |  |  |
| HISTORY_ARGUMENT(ITEM) | 005 | [n] | 005 | [n] |  |  |  |  |
| TABLE 075 - EVENT_LOG_CTRL_TBL |  |  |  |  |  |  |  |  |
| STD_EVENTS_MONITORED_FLAGS | 000 |  |  |  |  |  |  |  |
| MFG_EVENTS_MONITORED_FLAGS | 001 |  |  |  |  |  |  |  |
| STD_TBLS_MONITORED_FLAGS | 002 |  |  |  |  |  |  |  |
| MFG_TBLS_MONITORED_FLAGS | 003 |  |  |  |  |  |  |  |
| STD_PROC_MONITORED_FLAGS | 004 |  |  |  |  |  |  |  |
| MFG_PROC_MONITORED_FLAGS | 005 |  |  |  |  |  |  |  |
| TABLE 076 - EVENT_LOG_DATA_TBL |  |  |  |  |  |  |  |  |
| EVENT_FLAGS | 000 |  |  |  |  |  |  |  |
| NBR_VALID_ENTRIES | 001 |  |  |  |  |  |  |  |
| LAST_ENTRY_EMLEMENT | 002 |  |  |  |  |  |  |  |
| LAST_ENTRY_SEQ_NBR | 003 |  |  |  |  |  |  |  |
| NBR_UNREAD_ENTRIES | 004 |  |  |  |  |  |  |  |
| ENTRIES(ARRAY) | 005 |  |  |  |  |  |  |  |
| ENTRIES(ITEM) | 005 | [n] |  |  |  |  |  |  |
| EVENT_TIME | 005 | [n] | 000 |  |  |  |  |  |
| EVENT_NUMBER | 005 | [n] | 001 |  |  |  |  |  |
| EVENT_SEQ_NBR | 005 | [n] | 002 |  |  |  |  |  |
| USER_ID | 005 | [n] | 003 |  |  |  |  |  |
| EVENT_CODE | 005 | [n] | 004 |  |  |  |  |  |
| EVENT_ARGUMENT(ARRAY) | 005 | [n] | 005 |  |  |  |  |  |
| EVENT_ARGUMENT(ITEM) | 005 | [n] | 005 | [n] |  |  |  |  |
| TABLE 080 - DIM_UDT_FUNC_LIM_TBL |  |  |  |  |  |  |  |  |
| NBR_XFR_LIST_ITEMS | 000 |  |  |  |  |  |  |  |
| UDT_FUNC_CTRL | 001 |  |  |  |  |  |  |  |
| MAX_INSTANCE | 002 |  |  |  |  |  |  |  |
| UDT_0_SIZE | 003 |  |  |  |  |  |  |  |
| UDT_1_SIZE | 004 |  |  |  |  |  |  |  |
| UDT_2_SIZE | 005 |  |  |  |  |  |  |  |
| UDT_3_SIZE | 006 |  |  |  |  |  |  |  |
| UDT_4_SIZE | 007 |  |  |  |  |  |  |  |
| UDT_5_SIZE | 008 |  |  |  |  |  |  |  |
| TABLE 081 - ACT_UDT_FUNC_LIM_TBL |  |  |  |  |  |  |  |  |
| NBR_XFR_LIST_ITEMS | 000 |  |  |  |  |  |  |  |
| UDT_FUNC_CTRL | 001 |  |  |  |  |  |  |  |
| MAX_INSTANCE | 002 |  |  |  |  |  |  |  |
| UDT_0_SIZE | 003 |  |  |  |  |  |  |  |
| UDT_1_SIZE | 004 |  |  |  |  |  |  |  |
| UDT_2_SIZE | 005 |  |  |  |  |  |  |  |
| UDT_3_SIZE | 006 |  |  |  |  |  |  |  |
| UDT_4_SIZE | 007 |  |  |  |  |  |  |  |
| UDT_5_SIZE | 008 |  |  |  |  |  |  |  |
| TABLE 082 - UDT_LIST_TBL |  |  |  |  |  |  |  |  |
| UDT_LIST(ARRAY) (BYTE/OFFSET) | 000 |  |  |  |  |  |  |  |
| UDT_LIST(ITEM) | 000 | [n] |  |  |  |  |  |  |
| TABLE 083 - UDT_SET_TBL |  |  |  |  |  |  |  |  |
| UDT_DATA_SETS(ARRAY) | 000 |  |  |  |  |  |  |  |
| UDT_DATA_SETS(ITEM) | 000 | [n] |  |  |  |  |  |  |
| FIRST_ITEM_NUMBER | 000 | [n] | 000 |  |  |  |  |  |
| LAST_ITEM_NUMBER | 000 | [n] | 001 |  |  |  |  |  |
| TABLE 084 - UDT_0_TBL |  |  |  |  |  |  |  |  |
| UDT_0_TBL(ARRAY) | 000 |  |  |  |  |  |  |  |
| UDT_0_TBL(ITEM) | 000 | [n] |  |  |  |  |  |  |
| TABLE 085 - UDT_1_TBL |  |  |  |  |  |  |  |  |
| UDT_1_TBL(ARRAY) | 000 |  |  |  |  |  |  |  |
| UDT_1_TBL(ITEM) | 000 | [n] |  |  |  |  |  |  |

| TABLE 086 - UDT_2_TBL |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| UDT_2_TBL(ARRAY) | 000 |  |  |  |  |  |  |  |
| UDT_2_TBL(ITEM) | 000 | [n] |  |  |  |  |  |  |
| TABLE 087 - UDT_3_TBL |  |  |  |  |  |  |  |  |
| UDT_3_TBL(ARRAY) | 000 |  |  |  |  |  |  |  |
| UDT_3_TBL(ITEM) | 000 | [n] |  |  |  |  |  |  |
| TABLE 088 - UDT_4_TBL |  |  |  |  |  |  |  |  |
| UDT_4_TBL(ARRAY) | 000 |  |  |  |  |  |  |  |
| UDT_4_TBL(ITEM) | 000 | [n] |  |  |  |  |  |  |
| TABLE 089 - UDT_5_TBL |  |  |  |  |  |  |  |  |
| UD_5_TBL(ARRAY) | 000 |  |  |  |  |  |  |  |
| UDT_5_TBL(ITEM) | 000 | [n] |  |  |  |  |  |  |