# Introduction

This document defines the interval data validation, editing, and estimation techniques required to participate in the California market as an MDMA.

# Required Data Validation Checks

Data validation checks are designed to identify things that can go wrong at the meter/recorder and cause the data collected to not reflect actual usage.

These rules apply to both kWh and kVARh data, depending on the data required by the meter’s tariff(s).  If data is provided for informational purposes only (not used for billing purposes), validation is not required.  Data that has not gone through the validation process is raw data.

General MDMA and MSP business practices should ensure that the meter is programmed correctly for the required revenue data and that the MDMA system is set up to accurately maintain information such as interval size, meter constants, and what quantity is recorded by what channel.  These VEE rules do not require or describe how the MDMA verifies that the meter is programmed correctly.

All validation checks must be run.  Failure of one check does not preclude the MDMA from performing other validation checks.

Several words are used to describe the quality of interval data.

- Raw data - data that has not gone through the VEE process

- Valid data - data that has gone through all required validation checks and either passed them all or been verified

- Verified data - data that failed at least one of the required validation checks but was determined to represent actual usage

- Estimated - data that has been calculated based on standard estimation rules because the raw data was not valid

The following validation checks are required for interval kWh and kVARh data.  They are described in section 3 of this document:

| Check | Purpose |
| --- | --- |
| Time check of meter reading device/system | Check for the following: - time drift of meter reading device/system outside CPUC standard |
| - Meter identification check | Check for the following: - meter ID was reported correctly - meter has not been changed out - data is being reported for the correct meter |
| - Time check of meter | Check for the following: - time drift of meter clock outside CPUC standard |
| - Pulse Overflow check | Check for the following: - improper scaling factor in meter - improperly sized transformer - hardware problem |
| - Test Mode check | Check for the following: - Data collected when meter was in test mode that represents test load rather than actual usage |
| - Sum check | Check for the following in combination meter/recorder installations: - Crossed channels between meter and recorder - pulse relay problems - Check for the following for all installations: - invalid PT and CT ratios, - invalid meter constants |
| - Spike check | Check for the following for all installations: - transmission error - spike resulting from meter test. - Note that a spike can also occur after an outage - in this case the data is valid, but may or may not be used for peak billing depending on the tariff and company policy. |
| - kVARh check (for kWh data only if corresponding kVARh data available) | Check for the following: - kWh channels are correctly mapped to kVARh channel - meter is operating correctly |

| High/Low Usage check | Check for the following in all installations: - dropped phases - inaccurate meter constants - energy diversion - fast/slow meters - Also check for the following in combination meter/recorder installations: - erratic pulse input to recorder |
| --- | --- |

# 3	Interval data collection and validation rules

If interval data is read more often than required for billing, checks need to be performed at different times in the process.  Some must be done as the data is read from the meter; some can be done anytime between when the data is collected from the meter and the end of the cycle, and others have to be done on a billing period basis at the end of the billing cycle.  They are broken out that way in this description.

## Time check of meter reading device/system ensures that the collection device is synchronized to the national time standard before data collection begins.

## Collect data

## As data is collected,

### Check meter identification – verify that the meter’s identification matches what is expected.

### Perform Time Tolerance check on meter and data.

The time tolerance check is performed to minimize and correct meter clock drift and to minimize and correct the data problems associated with meter clock drift.

How to do Time Tolerance check on meter

To perform a time tolerance check on the meter, compare meter time to data collection device time.  Note that depending on the communication technology used, network latency must be taken into account.

Pass/Fail Criteria

- If meter time is within 3 minutes of time standard, the meter passes the time tolerance check.  (Note that if the meter time is within the 3-minute tolerance, the meter time can optionally be corrected.)

- If meter time is off by more than 3 minutes, the meter time must be corrected.  If the meter fails the time tolerance check for three consecutive months, the meter must be physically inspected/tested.

How to do Time Tolerance check on data

To perform a time tolerance check on the data, compare the number of intervals retrieved from the meter to the number of intervals expected given the elapsed time.

Pass/Fail Criteria

- If the actual number of intervals is equal to the expected number, the data passes the time tolerance check.

- If the actual number of intervals differs from the expected number, the data fails the time tolerance check.  The data to be corrected includes all intervals from the last time the meter time was determined to be good (i.e., within the 3-minute tolerance) and when it was discovered that the meter time was off by more than 3 minutes and the meter time was reset.

If data fails the Time Tolerance Check…

- If the meter time was off by less than or equal to 75 minutes, prorate the data using one of the algorithms in Appendix A, Section 1.

- If the meter time was off by more than 75 minutes, the data must be estimated.

## Either as data is collected or prior to publishing on MDMA Server…

### Perform Pulse Overflow check

Inspect each interval for this condition.  If a pulse overflow occurs, the meter requires physical meter test/maintenance.  Intervals with pulse overflows must be estimated.

### Perform Test Mode check

If the MDMA determines the meter was in test mode, the MDMA must ensure that the customer is not billed for the test load.  If no actual customer usage data is available for the time in which the meter was in test mode, zero usage is reported for that period; this data is valid.  If the meter is inadvertently left in test mode, the data must be estimated if actual usage data is not available from the meter .

### Perform Sum Check

The sum check is performed to ensure that the difference between the energy use recorded in the intervals and the energy use recorded in the meter over the same time period is within an acceptable range.  This check may be done on either consumption or pulse data, provided the data scaling is consistent throughout the period.

How to do the Sum Check

- Calculate the energy use recorded in the intervals by summing the intervals between the start and stop meter readings.

- Calculate the energy use recorded by the meter by taking the difference between the start and stop readings accounting for possible rollover between start and stop readings.  For example, if the start reading was 99968 and the stop reading was 00294, and the meter reading rolls over at 99999, the difference would be 326.

- Compare the energy use recorded in the intervals to the energy use recorded by the meter.  Note that the values must be in the same units for the comparison.

Pass/Fail Criteria

- If difference is <= two meter multipliers, the data passes the sum check.  (meter multiplier = CTR x VTR, where CTR is current transformer ratio and VTR is voltage transformer ratio)

- If difference is > two meter multipliers, the data fails the sum check.

If data fails the Sum Check…

- 1)	Several optional steps may be taken to resolve the sum check failure.

- (a)	Reread the meter and redo the sum check from original start meter reading to new stop meter reading.

- (b)	Redo the sum check, taking into account the differences between the time of the start read and the start of the first interval, and the time of the stop read and the end of the last interval.  See Appendix A, Section 2.1 for more information.

- (c)	Redo the sum check, taking into account missing or incomplete intervals.  See Appendix A, Section 2.2 for more information.

- (d)	Additional checks may be performed, based on the technology used, to verify that the interval data is an accurate representation of usage as measured by the meter readings.

- 2)	If sum check is not resolved, perform manual inspection of data.

- (a)	Verify meter and pulse multipliers.  If a multiplier was incorrect, redo the sum check using the correct multipliers.

- (b)	Check for a meter change between the start and stop meter readings.  If the meter was changed, redo the sum check for each meter independently.

- (c)	Manually inspect data.  If the data seems reasonable, it can be considered verified.

- (d)	If the data does not seem reasonable, perform physical meter test/inspection.  If meter tests OK, the data can be considered verified.  If a problem is found with the meter, the data must be estimated.  (Note: if the problem existed prior to this billing period, previously posted data must be adjusted and re-posted.)  If unable to visit site and perform meter test prior to posting the data, the data must be estimated.

- (e)	If interval data is available but meter readings are not available, manually inspect the data.  Data that seems reasonable (compared with historical data) can be considered verified.  Any data that does not seem reasonable must be estimated.

- 3)	If the sum check failure cannot be resolved, the data must be estimated.

### Perform Spike Check

The spike check is performed to identify intervals with suspiciously high usage relative to the surrounding intervals.  This check may be done on either consumption or pulse data, provided the data scaling is consistent throughout the period.

How to do the Spike Check

- For each 24-hour period, identify the highest and third highest peaks.  (Normally the 24-hour period is from midnight to midnight.  If the data is at the beginning of the span and doesn’t start at midnight, use enough data from the next day of data to get 24 hours of data.  If the data is at the end of the span and doesn’t stop at midnight, use enough data from the next to last day of data to get 24 hours.)

- If the highest peak is less than or equal to the spike check threshold of 10 pulses, skip the spike check.  (A spike check threshold is used to eliminate false spikes for meters with very low usage.)

- If the highest peak is greater than the spike check threshold of 10 pulses, subtract the third highest peak from the highest peak and divide by the third highest peak.

Pass/Fail Criteria

- If ((highest peak - third highest peak)/third highest peak) <= 1.8, the interval passes the spike check.

- If ((highest peak - third highest peak)/third highest peak) > 1.8, the interval fails the spike check.

If data fails the Spike Check…

- 1)	Optionally reread the meter. If you get different value from reread, redo spike check.

- 2)	If value is the same on reread or you cannot reread the meter, perform manual inspection of data.

- (a)	Look for similar patterns on similar days.  If a similar pattern is found and this seems reasonable, the data can be considered verified.

- (b)	Optionally check with customer for unusual conditions at the time of the spike.  If a legitimate reason for spike is found, the data can be considered verified.

- 3)	If no similar pattern or legitimate reason for spike is found, the interval with the spike must be estimated.

- 4)	If there is a regular pattern of failing this check, the customer may be an irregular usage customer.  See section on Irregular Usage Customers for additional information.

### If interval kVARh data is available, perform kVARh Check

The kVARh check is performed to identify intervals where reactive load (kVARh) is present and active load (kWh) is not, indicating a suspicious usage pattern and possible meter malfunction.  This check is only required when both kWh and kVARh are used for billing.  If kVARh data is available but not used for billing, the check is optional.  This check may be done on either consumption or pulse data, provided the data scaling is consistent throughout the period.

How to do the kVARh Check

- If multiple kWh channels map to a single kVARh channel, or multiple kVARh channels map to single kWh channel, the appropriate channels must be totaled prior to this check.

- If there are any kWh intervals with zero consumption, check the corresponding kVARh interval.

Pass/Fail Criteria

- If the corresponding kVARh interval is also zero or less than or equal to the kVARh check threshold of 4 pulses, the kWh data passes the kVARh check.  (A kVARh check threshold is used to eliminate false errors for meters with very low usage.)

- If the corresponding kVARh interval is greater than the kVARh check threshold of 4 pulses, the kWh interval fails the kVARh check.

If data fails the kVARh Check…

- 1)	Several optional steps may be taken to resolve the kVARh failure.

- (a)	Investigate to determine if this data represents actual customer usage, in which case the data can be considered verified.

- (b)	If multiple kWh channels map to a single kVARh channel, investigate to determine if the problem can be directly traced to specific kWh channels.  If this is the case, only data for those channels must be estimated.  If the problem is not attributable to specific channels, all kWh channels need to be estimated.

- 2)	If no legitimate reason for the kVARh failure is found, the intervals with failures must be estimated.

- 3)	If there is a regular pattern of failing this check, the customer may be an irregular usage customer.  See section on Irregular Usage Customers for additional information.

## On the billing cycle for the meter…

### High/Low Usage Check

This test must be performed on the data that has passed or been verified for previous checks, with no estimated values included.  This identifies metered usage that is suspiciously high or low relative to historical usage.  It may optionally also be performed on all data (valid and estimated) to provide a reasonableness check on the estimates derived using the standard estimation techniques.

This check must be done on consumption data, not pulses.

How to do the High/Low Usage Check

- If last year’s data is available, calculate average daily usage for same billing month last year; use summed VEE or historical billing interval data if available, if not use VEE or historical billing usage (i.e., difference between register readings).

- If last year’s data is not available, calculate average daily usage for the previous billing month; use summed VEE or historical billing interval data if available, if not use VEE or historical billing usage (i.e., difference between register readings).

- If last year’s data and last month’s data are not available, skip the high/low usage check.

- Calculate average daily usage for this billing month using either summed VEE data (if check includes estimated data) or sum of all intervals not requiring estimation (if check does not include estimated data).  If not all intervals are included in the sum, prorate the sum accordingly.

Pass/Fail Criteria

- If |(historical daily average - this month’s daily average)| <= 0.5* historical daily average, the data passes the high/low usage check.

- If |(historical daily average - this month’s daily average)| > 0.5* historical daily average, all data in the billing month fails the high/low usage check.

If data fails the High/Low Usage Check…

- 1)	Perform manual inspection of data.

- (a)	Look at recent history for the meter.  If monthly usage has been on a trend in the appropriate direction and this seems reasonable, the data can be verified.

- (b)	Optionally check with customer for changed usage patterns.  If changed usage patterns match change in data, the data can be verified.

- (c)	Check to see if some of the data looks reasonable; reasonable looking data can be verified.  For example, if a meter fails sometime during the month, the data at the beginning of the month may be OK, while the data after the meter failure may be obviously bad.

- (d)	If the data does not seem reasonable, perform physical meter test/inspection. If meter tests OK, the data can be verified.  If a problem is found with the meter, the data must be estimated.  (Note: if the problem existed prior to this billing period, previously posted data must be adjusted and re-posted.)  If unable to visit site and perform meter test prior to posting the data, the data must be estimated.

- 2)	If the data is investigated and found to be accurate, the data is verified.

- 3)	If the data fails high/low usage check, suspect data must be estimated.

- 4)	If there is a regular pattern of failing this check, the customer may be an irregular usage customer.  See section on Irregular Usage Customers for additional information.

## After all validation checks have been performed and required data has been estimated, optionally rerun validation checks to ensure reasonableness of estimates.

## Record Keeping Requirements

If data failed one or more validation checks, the specific checks that the data failed must be recorded on an interval level, and:

- (a)	If the data was manually verified, that information must be recorded on an interval level. Verified data is valid.

- (b)	If the validation failure(s) were not resolved through accepted methods, the data must be estimated.

For each interval that is estimated, the MDMA must record the estimation algorithm used.  Interval data estimation algorithms include:

- less than 2 hours (4.1)

- greater than 2 hours (4.2) – not scaled based on usage

- greater than 2 hours (4.2) – scaled based on usage

- time-drifted intervals prorated (Appendix A, Section 1.1)

- time-drifted intervals prorated (Appendix A, Section 1.2)

- intervals adjusted (4.3)

- intervals manually estimated (4.2.8)

- intervals estimated due to meter interval programmed incorrectly (4.4)

- Load profile template used (4.2.7)

## Irregular Usage Customers

An irregular usage customer is one whose usage pattern does not follow normal usage patterns and consistently fails the spike check, kVARh check, or high/low usage check.  An MDMA can identify a customer as an irregular usage customer if:

- 1)	the customer data fails the standard validation check for three consecutive months and the MDMA verifies that the data represents the actual customer usage, OR

- 2)	MDMA is notified by the customer’s ESP or previous MDMA of the irregular usage pattern.

The data used to identify an irregular usage customer could be data collected by the MDMA, or historical data provided by the previous ESP or MDMA.  An MDMA may modify the spike check and/or high/low usage check, and skip the kVARh check if an irregular usage customer consistently fails the check.  The MDMA must notify both the customer’s ESP and UDC of the customer’s irregular usage status and what modified checks will be performed.

The goal of the modified checks is to automate the manual procedures the MDMA would perform to verify that this is the customer’s normal usage pattern.  An MDMA may use a variation of the spike check or high/low usage check based on the actual usage pattern.  Note that the MDMA may not skip the spike check or high/low usage check.  If the data passes the modified check, the data is valid and does not need to be marked as verified.

- Examples of modifications for the spike check include modifying the spike check value (180%) or the pulse threshold value (10 pulses).

- Examples of modifications for the high/low usage check include changing the percentages (+/- 50%), using the year’s average instead of one billing period’s average, or comparing to the minimum and maximum values for the past year.

For some customers, irregular usage patterns are symptomatic of the business and will always be present, such as co-generation customers.  For other customers, irregular usage patterns may be a temporary condition, such as when a factory adds a second shift and fails the high/low usage check for the first 12 months.  The MDMA must determine whether a customer is a permanent or temporary irregular usage customer.  Temporary irregular usage customers must be reviewed annually to determine if they are still irregular usage customers or should be returned to the normal checks.

# Interval Data Estimation Rules

Estimate intervals needing estimation using the following estimation rules…

## If section of data needing estimation is 2 hours or less in length, use point-to-point linear interpolation to estimate the data.  Intervals containing a power failure cannot be used as end points for interpolation.

How to apply Point-to-Point Linear Interpolation

- 1)	If the section occurs in the middle of the data, the “first point” is the last valid interval before the section, and the “second point” is the first valid interval after the section.

- 2)	If the section occurs at the beginning of the span, use the last interval from the historical data as the first point if the historical data is available and valid.  Otherwise, use the second point (the first valid interval after the section) as the first point – this will cause the load to be estimated as a flat load.

- 3)	If the section occurs at the end of the span, use the first point (the last valid interval before the section) as the second point – this will cause the load to be estimated as a flat load.

## If the section of data needing estimation is more than 2 contiguous hours, use the average of selected reference days to estimate the data.

Rules and definitions for selecting reference days for estimation:

- “Same weekdays” are defined as the same day of week as the day that needs estimation.  In the case of holidays, “same weekdays” are holidays.

- “Like days” are defined as the same daytype (i.e., weekday, weekend, or holiday) as the day that needs estimation.

- A standard list of holidays will be used, regardless of the tariff or service territory of the meter.  The “legal” definitions of the holiday is used; if the holiday falls on a Sunday, the “legal” holiday is the following Monday.  Otherwise the “legal” holiday is the same date as the actual holiday.  The holidays used are the following:

- New Years Day

- Presidents Day

- Memorial Day

- Independence Day

- Labor Day

- Veterans Day

- Thanksgiving Day

- Christmas Day

- Only “valid” intervals can be used for estimation.  Valid intervals are defined as those that have passed all validation checks or have been verified.  Estimated intervals cannot be used for estimation.

- Data from days with a power failure cannot be used for estimation.  Power failures can cause irregular usage patterns, resulting in data that is not typical for the customer.

- Valid intervals from “partial” days can optionally be used for estimation.  “Partial” days are defined as those containing estimated data or those on which data collection began at some time other than midnight.

- Historical data up to 90 days prior to the day needing estimation and from the current billing period may be used for estimation.

- Reference days are chosen to be the closest chronologically to the data needing estimation, regardless of seasonal crossover.  This may include days after the day requiring estimation.  If two potential reference days are equidistant from the day requiring estimation, use the earlier day first.  For example, if June 2, 1998 needed estimation and the billing period was from June 1 to June 30, the reference days used would be May 19, May 26, and June 9, provided they contained valid data.

### Develop a daily profile

- 1)	Find the three “same weekdays” with valid data closest in time to the day with the data needing estimation based on the rules listed in the previous section.  If the day with data needing estimation is a holiday, the “same weekdays” are holidays, not the same day of week.  If not enough historical holidays exist in the current billing period or previous 90-day period, use Sundays.  Calculate the average daily profile using the three selected days.

- 2)	If only two same weekdays are available from the current billing period and 90 days of historical data, calculate the average daily profile using the two selected days.

- 3)	If only one same weekday is available from the current billing period and 90 days of historical data, use it as the daily profile.

- 4)	If no same weekdays are available in the current billing period and 90 days of historical data, look for the three “like” days that are closest chronologically to the day with intervals needing estimation.  For example, if the intervals needing estimation were on Tuesday, use Monday, Wednesday, and Thursday.  Only use weekdays with weekdays; only use weekends with weekends; only use holidays or Sundays with holidays.  Calculate the average daily profile using the three selected days.

- 5)	If only two like days are available from the current billing period and 90 days of historical data, calculate the average daily profile using the two selected days.

- 6)	If only one like day is available from the current billing period and 90 days of historical data, use it as the daily profile.

### Use the daily profile to estimate the required data

- 1)	Estimate the data needing estimation by applying the appropriate intervals from the average daily profile to fill the missing intervals.

- 2)	If start and stop meter readings are available and known to be good, they may optionally be used to scale the estimated interval data.  See Appendix A, Section 3 for more information.

### If there are no similar days or like days, use the load profile for the customer’s class to estimate the data.  Use this month’s usage, if available, to scale the load profile.  If this month’s usage is not available, use last month’s usage or last year’s usage, whichever is determined to be more reasonable, to scale the load profile.  Refer to the UDCs’ load profile documentation for more information on applying load profiles.  Note that the load profiles are for hourly data.  If 15 minute data is required, assume a flat load throughout the hour (i.e., each 15-minute interval would have 1/4th the hourly usage).

### If there is no historical data that can be used, the data must be estimated manually and the process and assumptions documented.

## Correcting Data Problems Attributable to Metering Problems

If on investigation the cause of the data problem is determined to be a problem with the meter or meter installation and the data can be corrected by scaling the intervals and meter readings, the MDMA will be notified of:

- 1)	The time period requiring correction.

- 2)	The scaling factor to be applied to each interval in that period.

Examples of these situations include a meter running slow, a meter running fast, one or two phases dropped, etc.

When the data is posted, it is marked as estimated if it had not been previously posted, and marked as adjusted if it had previously been posted

## Interval in meter doesn’t match tariff or settlement requirements

If the meter programming and the MDMA requirements are inconsistent, the data is calculated as follows:

- 1)	The meter is programmed to collect data at a smaller interval than required by its tariffs, and the meter's interval evenly divides into the interval required by the tariff – for example, the meter was programmed to collect 5-minute data, and the tariff requires 15-minute data. Sum the 5-minute intervals into 15-minute intervals on even 15-minute boundaries.  If the data passed all the other validation checks, it is valid and does not need to be marked as estimated or verified.

- 2)	The meter is programmed to collect data at a larger interval than required by the meter’s tariff.  For example, the meter is programmed to collect 60-minute intervals, but the tariff require 15-minute intervals.  Prorate the data by assuming an even load distribution during the interval.  In this example, the usage in the 60-minute interval would be divided by 4 to estimate the usage in a 15-minute interval.  The data is marked as estimated.  The meter must be reprogrammed to the correct interval.

- 3)	The meter is programmed to collect data at a smaller interval than required by its tariff, but the meter’s interval doesn't evenly divide into the interval required by the tariff.  For example, the meter is programmed to collect 10-minute intervals, and the tariff requires 15-minute intervals. The data would be estimated and marked as estimated.  To estimate data, all collected intervals that are contained within the required reporting interval are included in the appropriate reporting interval.  Collected intervals that cross the boundaries of required reporting intervals are included proportionally in both reporting intervals.  In this example, if there were three 10-minute intervals containing 10 kWh, 20 kWh, and 30 kWh, the corresponding estimated 15-minute intervals would contain 20 kWh (10 + 0.5*20) and 40 kWh (0.5*20 + 30).   This is similar to the prorating technique discussed in Appendix A Section 1.1.  The meter must be reprogrammed to the correct interval.