1.	Introduction

This document defines the data validation, editing, and estimation techniques required to participate in the California market as an MDMA.

2.	Required data validation tests

Data validation checks are designed to identify things that can go wrong at the meter/recorder and cause the data collected not to reflect actual usage.

The following tests are required for kWh and kVARh interval data and are described in section 3 of this document:

| Test | Purpose |
| --- | --- |
| Time check of meter reading device/system | Check for time drift of meter reading device/system outside CPUC standard |
| Time check of meter | Check for time drift of meter clock outside CPUC standard |
| Pulse overflow check | Check for the following: · improper scaling factor in meter · improperly sized transformer · hardware problem |
| Sum check | Check for the following in combination meter/recorder installations: · crossed channels between meter and recorder · pulse relay problems Check for the following for all installations: · invalid PT and CT ratios, · invalid meter constants |
| Spike check | Check for the following for all installations: · transmission error · spike resulting from meter test. Note that a spike can also occur after an outage - in this case the data is valid, but may or may not be used for peak billing depending on the tariff and company policy. |
| High/low check | Check for the following in all installations: · dropped phases · inaccurate meter constants · energy diversion · fast/slow meters Also check for the following in combination meter/recorder installations: · erratic pulse input to recorder |
| Meter identification check | Check for the following: · that the meter ID was reported correctly · the meter has not been changed out · the data is being reported for the correct meter |
| kVARh check (for kWh data only if corresponding kVARh data available) | Check that: · kWh channels are correctly mapped to kVARh channel · meter is operating correctly |
| Test mode check | Check for: · Data collected when meter was in test mode that represents test load rather than actual usage |

The following tests are required for monthly data validation for kWh and kVARh where required.  They are discussed in section 5 of this document.

| Test | Purpose |
| --- | --- |
| Time check of meter reading device/system (applies to devices/systems collecting TOU data only) | Check for time drift of meter reading device/system outside CPUC standard |
| Time check of meter (applies to meters collecting TOU data only) | Check for time drift of meter clock outside CPUC standard |
| High/low usage check | Check for the following: · misread · fast/slow meter · broken meter · incorrect multipliers · energy diversion · dropped phases |
| High/low demand check (applies to demand readings only) | Check for the following: · misread · fast/slow meter · broken meter · incorrect multipliers · energy diversion · dropped phases |
| Time-of-use check (applies to TOU data only) | Check for the following: · misread · fast/slow meter · broken meter · incorrect multipliers · energy diversion · dropped phases |
| Zero consumption for active meters | Check for the following: · energy diversion · meter doesn’t register |
| Usage for inactive meters | Check for unauthorized usage at a site for which there is no customer with financial responsibility |
| Number of dials on meter | Check for: · wrong meter · misread |
| Dial decimal quantity | Check for: · wrong meter · misread |
| Meter identification | Check for the following: · that the meter ID was reported correctly · the meter has not been changed out · the data is being reported for the correct meter |

3.	Interval data collection and validation rules

These rules apply to both kWh and kVARh data, depending on the data required by the meter’s tariff(s).  General MDMA and MSP business practices should ensure that the meter is programmed correctly for the required revenue data and that the MDMA system is set up to accurately maintain information such as interval size, meter constants, and what quantity is recorded by what channel.  These VEE rules do not require or describe how the MDMA verifies that the meter is programmed correctly.

Note that if interval data is read more often than required for billing, checks need to be performed at different times in the process.  Some must be done as the data is read from the meter; some can be done anytime between when the data is collected from the meter and the end of the cycle, and others have to be done on a billing period basis at the end of the billing cycle.  They are broken out that way in this description.

Note also that all validation checks should be run.  Failure of one check should not preclude the MDMA from performing other validation checks.

3.1.	Time check of meter reading device/system – ensure that the collection device is synchronized to the national time standard before data collection begins.

3.2.	Collect data

3.3.	As data is collected,

3.3.1.	Check meter identification – verify that the meter’s identification matches what is expected.

3.3.2.	Do time tolerance check on meter and data.

To perform a time tolerance check on the meter, compare meter time to data collection device time.  Note that depending on the communication technology used, network latency must be taken into account.

3.3.2.1	If meter time is within 3 minutes of time standard, the meter passes the Time Tolerance check.  (Note that if the meter time is within the 3-minute tolerance, the meter time can optionally be corrected.)

3.3.2.2	If meter time is off by more than 3 minutes, the meter time must be corrected.  If the meter fails the Time Tolerance check for three consecutive months, the meter must be physically inspected/tested.

To perform a time tolerance check on the data, compare the number of intervals retrieved from the meter to the number of intervals expected given the elapsed time.

3.3.2.3	If the actual number of intervals is equal to the expected number, the data passes the time tolerance check.

3.3.2.4	If the actual number of intervals differs from the expected number, the data must be corrected.  The data to be corrected includes all intervals from the last time the meter time was determined to be good (i.e., within the 3-minute tolerance) and when it was discovered that the meter time was off by more than 3 minutes and the meter time was reset.

3.3.2.4.1	If the meter time was off by less than or equal to 75 minutes, prorate the data using one of the algorithms in Appendix A.1.

3.3.2.4.2	If the meter time was off by more than 75 minutes, estimate the data.

3.4.	Either as data is collected or prior to publishing on MDMA Server…

3.4.1.	Perform pulse overflow check

Inspect each interval for this condition.  If a pulse overflow occurs, the meter requires physical meter test/maintenance.  Intervals with pulse overflows need to be estimated.

3.4.2.	Perform test mode check

If MDMA determines meter was in test mode, the MDMA must ensure that the customer is not billed for the test load.  Zero data reported in intervals while the meter is being tested are left as zero and considered good data.  If the meter is inadvertently left in test mode, the data must be estimated.

3.4.3.	Perform Sum Check

To perform the sum check, compare the energy use recorded in the intervals to the energy use recorded in the meter over the same time period to ensure that the difference is within an acceptable range.  (This check may be done against either consumption or pulse data, provided the data scaling is consistent throughout the period.)

3.4.3.1.	Calculate the energy use recorded in the intervals by summing the intervals between the start and stop meter readings.

3.4.3.2.	Calculate the energy use recorded by the meter by taking the difference between the start and stop readings accounting for possible rollover between start and stop readings.  For example, if the start reading was 99968 and the stop reading was 00294, and the meter reading rolls over at 99999, the difference would be 326.

3.4.3.3.	Compare the energy use recorded in the intervals to the energy use recorded by the meter.  Note that the values must be in the same units for the comparison.

3.4.3.4.	If difference is <= two meter multipliers, the data passes the sum check.  (meter multiplier = CTR x VTR, where CTR is current transformer ratio and VTR is voltage transformer ratio)

3.4.3.5.	If difference is > two meter multipliers, the data fails the sum check.  Several optional steps may be taken to resolve the failure.

3.4.3.5.1.	  Reread the meter and redo the sum check from original start meter reading to new stop meter reading.

3.4.3.5.2.	  Redo the sum check, taking into account the differences in time between the time of the start read and the start of the first interval, and the time of the stop read and the end of the last interval.  See Appendix A, Section 2.1 for more information.

3.4.3.5.3.	  Redo the sum check, taking into account missing or incomplete intervals.  See Appendix A, Section 2.2 for more information.

3.4.3.5.4.	  Additional checks may be performed, based on the technology used, to verify that the interval data is an accurate representation of usage as measured by the meter readings.

3.4.3.6.	If sum check is still not resolved, perform manual inspection of data.

3.4.3.6.1.	  Verify meter and pulse multipliers.  If a multiplier was wrong, redo the sum check using the correct multipliers.

3.4.3.6.2.	  Check for a meter change between the start and stop meter readings.  If the meter was changed, redo the sum check for each meter independently.

3.4.3.6.3.	  Manually inspect data.  If the data seems reasonable, it can be considered verified.

3.4.3.6.4.	  If data does not seem reasonable, perform physical meter test/inspection.  If meter tests OK, the data can be considered verified.  If a problem is found with the meter, the data needs to be estimated.  If unable to visit site and perform meter test prior to posting the data, the data needs to be estimated.

3.4.3.6.5.	 If interval data is available but meter readings are not available, manually inspect the data.  Data that seems reasonable (compared with historical data) can be considered verified.  Any data that does not seem reasonable needs to be estimated.

3.4.4.	Spike check

This check may be done against either consumption or pulse data, provided the data scaling is consistent throughout the period.

3.4.4.1.	For each 24-hour period, identify the highest and third highest peaks.  (Normally the 24-hour period is from midnight to midnight.  If the data is at the beginning and doesn’t start at midnight, use enough data from the next day of data to get 24 hours of data.  If the data is at the end and doesn’t stop at midnight, use enough data from the next to last day of data to get 24 hours.)

3.4.4.1.1.	  If the highest peak is non-zero but less than or equal to the spike check threshold of 10 pulses, the interval passes the spike check.  (A spike check threshold is used to eliminate false spikes for meters with very low usage.)

3.4.4.1.2.	  If the highest peak is greater than the spike check threshold and ((highest peak - third highest peak)/third highest peak) <= 1.8, the interval passes the spike check.

3.4.4.1.3.	  If the highest peak is greater than the spike check threshold and ((highest peak - third highest peak)/third highest peak) > 1.8, the interval fails the spike check.

3.4.4.2.	If interval fails spike check, optionally reread meter. If you get different value from reread, redo spike check.

3.4.4.3.	If value is the same on reread or you cannot reread the meter, perform manual inspection of data.

3.4.4.3.1.	  Look for similar patterns on similar days.  If a similar pattern is found, the data can be considered verified.

3.4.4.3.2.	Manual analysis may optionally involve calling the customer to check for unusual conditions at the time of the spike.  If a legitimate reason for spike is found, the data can be considered verified.

3.4.4.3.3.	  If no similar pattern or legitimate reason for spike is found, the interval with the spike needs to be estimated.

3.4.4.4.	 If there is a regular pattern of failing this check, the customer may be an irregular usage customer.  See section on Irregular Usage Customers for additional information.

3.4.5.	Additional check if interval kVARh data is available

This check may be done against either consumption or pulse data, provided the data scaling is consistent throughout the period.

Note that if multiple kWh channels map to a single kVARh channel, or multiple kVARh channels map to single kWh channel, the appropriate channels must be totaled prior to this check.

3.4.5.1.	If there are any kWh intervals with zero consumption, check the corresponding kVARh interval.

3.4.5.2.	If the corresponding kVARh interval is also zero or less than or equal to the kVARh check threshold of 4 pulses, the kWh data passes the kVARh check.  (A kVARh check threshold is used to eliminate false errors for meters with very low usage.)

3.4.5.3.	If the corresponding kVARh interval is greater than the kVARh check threshold of 4 pulses, the kWh interval fails the kVARh check.

3.4.5.4.	The MDMA may optionally investigate to determine if this data represents actual customer usage, in which case the data can be considered verified.  If there is a regular pattern of failing this check, the customer may be an irregular usage customer.  See section on Irregular Usage Customers for additional information.

3.4.5.5.	If multiple kWh channels map to a single kVARh channel, the MDMA may optionally investigate to determine if the problem can be directly traced to specific kWh channels.  If this is the case, only data for those channels needs to be estimated.  If the problem is not attributable to specific channels, all kWh channels need to be estimated.

3.5.	On the billing cycle for the meter…

3.5.1.	High/low check

Note that for 1/1/98, this check may be done on good and verified data only (i.e., not including any estimated intervals) to check the raw data, or after validation and estimation (including good, verified, and estimated intervals) to verify the estimated data, or both.  All parties should work toward doing this check both times in the future.

This check is done against consumption data, not pulses.

3.5.1.1.	If last year’s data is available, calculate average daily usage for same billing month last year; use summed VEE or historical billing interval data if available, if not use VEE or historical billing usage (i.e., difference between register readings)

3.5.1.2.	Else if last year’s data is not available, calculate average daily usage for the previous billing month; use summed VEE or historical billing interval data if available, if not use VEE or historical billing usage (i.e., difference between register readings).

3.5.1.3.	Else if previous billing month not available, don’t perform this check!

3.5.1.4.	Calculate average daily usage for this billing month using either summed VEE data (if test includes estimated data) or summed good and verified data (if test does not include estimated data).  If there were any spikes in the data, don’t include those intervals in the average - prorate the daily average accordingly.

3.5.1.5.	If the difference between the two daily averages is greater than 50% of the historical daily average, flag data (all the intervals in the month) as failing high/low average check and kick out for manual analysis.  Else data has passed High/Low Check.

If (|historical daily average - this month’s daily average)| <= .5* historical daily average) data passes the High/Low Check.

If (|historical daily average - this month’s daily average)| > .5* historical daily average) data (all intervals in the month) fails high/low average check and is kicked out for manual analysis.

3.5.1.6.	If data fails the High/Low Check, perform manual inspection of data.

3.5.1.6.1.	  Look at recent history for the meter.  If monthly usage has been on a trend in the appropriate direction and this seems reasonable, data can be considered verified.

3.5.1.6.2.	  Optionally check with customer for changed usage patterns.  If changed usage patterns match change in data, the data can be considered verified.

3.5.1.6.3.	  If data does not seem reasonable, perform physical meter test/inspection. If meter tests OK, the data can be considered verified.  If a problem is found with the meter, the data needs to be estimated.  (Note: if the problem existed prior to this billing period, previously posted data will need to be adjusted and re-posted.)

3.5.1.6.4.	  Check to see if some of the data looks reasonable; reasonable looking data can be considered verified.   (For example, this may happen if a meter fails sometime during the month – the data at the beginning of the month may be ok, while the data after the failure may be obviously bad.)

3.5.1.7.	If the data is investigated and found to be accurate, the data can be considered verified.

3.5.1.8.	If the data fails high/low average check, suspect data needs to be estimated.

3.5.1.9.	If there is a regular pattern of failing this check, the customer may be an irregular usage customer.  See section on Irregular Usage Customers for additional information.

3.5.2.	If data has passed all appropriate validation tests without manual verification, data has been validated.  If data failed one or more validation tests but was manually verified, the specific tests the data failed and the fact that it was manually verified must be recorded on an interval level.  If data did not pass all appropriate validation tests or was not manually verified, the specific tests the data failed must be recorded on an interval level, and the data needs to be estimated.  If an interval fails more than one test, all failed tests must be recorded.

3.5.3.	Estimate data needing estimation; see section 4.  Note that for each interval that is estimated, the MDMA must record the estimation algorithm used.  The estimation algorithm will be reported when the data is posted when it is supported by CMEP.  Interval data estimation algorithms include:

·	less than 2 hours (4.1)

·	greater than 2 hours (4.2) - not scaled based on usage

·	greater than 2 hours (4.2) - scaled based on usage

·	time-drifted intervals prorated (Appendix A  - method 1)

·	time-drifted intervals prorated (Appendix A  - method 2)

·	intervals adjusted (4.3)

·	intervals manually estimated (4.2.8)

·	intervals estimated due to meter interval programmed incorrectly (4.4)

·	Load profile template used (4.2.7)

3.5.4.	Optionally redo checks after estimation to help verify estimated readings.

3.6.	Irregular Usage Interval Data

An irregular usage customer is one whose usage pattern does not follow normal usage patterns and consistently fails the spike check, kVARh check, or high/low usage check.  A customer may be determined to be an irregular usage customer by an MDMA if the MDMA verifies that:

1.	the customer data fails the standard validation check for three consecutive months, and that the data represents the actual customer usage, OR

2.	the MDMA is notified by the customer’s previous MDMA.

The data used to identify an irregular usage customer could be data collected by the MDMA, or historical data provided by the previous ESP or MDMA.  An MDMA may modify the spike check and/or high/low usage check, and skip the kVARh check if an irregular usage customer consistently fails the check.  The MDMA must notify both the customer’s ESP and UDC of the customer’s irregular usage status and what modified tests will be performed.

The goal of the modified checks is to automate the manual procedures the MDMA would perform to verify that this is the customer’s normal usage pattern.  An MDMA may use a variation of the spike check or high/low usage check based on the actual usage pattern.  Note that the MDMA may not skip the spike check or high/low usage check.  If the data passes the modified test, the data is validated.

·	Possible modifications for the spike test include modifying the spike check threshold value (180%) or the pulse threshold value (10 pulses).

·	Possible modifications for the high/low check include changing the percentages (+/- 50%), using the year’s average instead of one billing period’s average, or comparing to the minimum and maximum values for the past year.

For some customers, irregular usage patterns are symptomatic of the business and will always be present, such as co-gen customers.  For other customers, irregular usage patterns may be a temporary condition, such as when a factory adds a second shift and fails the high/low usage check for the first 12 months.  The MDMA must determine whether a customer is a permanent or temporary irregular usage customer.  Temporary irregular usage customers must be reviewed annually to determine if they are still irregular usage customers or should be returned to the normal checks.

4.	Interval Data Estimation Rules

Estimate intervals needing estimation using the following estimation rules….

4.1.	If section of data needing estimation is 2 hours or less in length…

4.1.1.	Use the point to point linear interpolation method to estimate the data where there is a gap in the data.  If the gap occurs in the middle of the data, the “first point” is the last good interval before the gap, and the “second point” is the first good interval after the gap.

4.1.2.	If the gap occurs at the beginning of the span, use the last interval from the historical data as the first point, if the historical data is available and the interval data is not estimated. Otherwise, use the second point (the first good interval after the gap) as the first point - this will cause the load to be estimated as a flat load.

4.1.3.	If the gap occurs at the end of the span, use the first point (the last good interval before the gap) as the second point (- this will cause the load to be estimated as a flat load.

4.2.	If section of data needing estimation is more than 2 contiguous hours…

Rules and definitions for selecting reference days for estimation:

·	“Same weekdays” are defined as the same day of week as the day that needs estimation.  In the case of holidays, “same weekdays” are holidays.

·	 “Like days” are defined as the same daytype (i.e., weekday, weekend, or holiday) as the day that needs estimation.

·	A standard list of holidays will be used across the board, regardless of the tariff or service territory of the meter.

·	Only “valid” intervals can be used for estimation.  Valid intervals are defined as those that have passed all validation checks or have been verified.  Estimated intervals cannot be used for estimation.

·	Data from days with a power failure cannot be used for estimation.  Power failures can cause irregular usage patterns, resulting in data that is not typical for the customer.

·	Valid intervals from “partial” days can optionally be used for estimation.  “Partial” days are defined as those containing estimated data or those on which data collection began at some time other than midnight.

·	Historical data up to 90 days prior to the day needing estimation may be used for estimation.  Use the historical data immediately preceding the usage period, regardless of seasonal crossover.

·	Reference days must be chosen first from the present billing period; historical data is only used if enough days are not available in the present billing period.  For example, if June 2, 1998 needed estimation and the billing period was from June 1 to June 30, the reference days used would be June 9, 16, and 23, provided they contained valid data.

·	If two potential reference days are equidistant from the day requiring estimation, use the earlier day first.  For example, if June 16, 1998 needed estimation and the billing period was from June 1 to June 30, the reference days used would be June 2, 9, and 23, provided they contained valid data.

·	Reference days from the current billing period may be a later date than the day needing estimation.

4.2.1.	Develop a daily profile

4.2.1.1.	Find the three “same weekdays” with valid data closest in time to the day with the data needing estimation.  Note that same weekdays from the same billing period are used first, and then same weekdays from historical data are used if necessary.  If the day with data needing estimation is a holiday, the “same weekdays” are holidays, not the same day of week.  If not enough historical holidays exist in the current billing period or previous 90-day period, use Sundays.  Calculate the average daily profile using the three selected days.

4.2.1.2.	If only two same weekdays are available from the current billing period and 90 days of historical data, calculate the average daily profile using the two selected days.

4.2.1.3.	If only one same weekday is available from the current billing period and 90 days of historical data, use it as the daily profile.

4.2.1.4.	If no same weekdays are available in the current billing period and 90 days of historical data, look for the three “like” days that are closest chronologically to the day with intervals needing estimation.  For example, if the intervals needing estimation were on Tuesday, use Monday, Wednesday, and Thursday.  Only use weekdays with weekdays; only use weekends with weekends; only use holidays or weekends with holidays.  Calculate the average daily profile using the three selected days.

4.2.1.5.	If only two like days are available from the current billing period and 90 days of historical data, calculate the average daily profile using the two selected days.

4.2.1.6.	If only one like day is available from the current billing period and 90 days of historical data, use it as the daily profile.

4.2.2.	Use the daily profile to estimate the required data

4.2.2.1.	Estimate the data needing estimation by applying the appropriate intervals from the average daily profile to fill the missing intervals.

4.2.2.2.	If beginning and ending meter readings are available and are known to be good, they may optionally be used to scale the estimated interval data as follows:

4.2.2.2.1.	Determine the total usage for the time period based upon the meter readings.  ((End-Start)*Meter Mult.)

4.2.2.2.2.	Sum together the valid intervals.

4.2.2.2.3.	Subtract the sum of the valid intervals from the total usage to determine the total estimated usage.

4.2.2.2.4.	Sum together the previously estimated intervals.

4.2.2.2.5.	Calculate the scaling factor by dividing the total estimated usage (from 4.2.2.2.3) by the sum of the estimated intervals (from 4.2.2.2.4).

4.2.2.2.6.	Multiply each estimated interval by the scaling factor.

4.2.3.	If there are no similar days or like days, use the load profile for the customer’s class to estimate the data.  Use this month’s usage if available to scale the load profile.  If this month’s usage is not available, use last month’s usage or last year’s usage, whichever is determined to be more reasonable, to scale the load profile.  Refer to the UDCs’ load profile documentation for more information on applying load profiles.  Note that the load profiles are for hourly data.  If 15 minute data is required, assume a flat load throughout the hour (i.e., each 15 minute interval would have 1/4th the hourly usage).

4.2.4.	If there is no historical data that can be used, the data must be estimated manually and the process and assumptions documented.  This must be coordinated with the customer’s UDC and ESP within the 5-day window required to report interval data.

4.3.	If the cause of the problem is determined to be a physical problem with the meter or meter installation and the data can be corrected by scaling the intervals and meter readings, the MDMA will be notified of the time period requiring correction and the scaling factor to be applied to each interval in that period.  When the data is posted in the CMEP format, it would be marked as estimated if it had not been previously posted, and marked as adjusted if it had previously been posted.  Data that is corrected in this fashion may be reported in a separate category on the monthly MDMA reports, and not included as part of the % estimated data for the month.  (Details need to be worked out as to how MDMAs will receive this notification.  This has been forwarded to the PSWG.)  Examples of these situations include a meter running slow, a meter running fast, one or two phases dropped, ….

4.4.	Interval in meter doesn’t match tariff or settlement requirements

If the meter programming and the MDMA requirements are inconsistent, the data is calculated as follows:

a)	If the meter is programmed to collect data at a smaller interval than required by its tariffs, and the meter's interval evenly divides into the interval required by the tariff - for example, the meter was programmed to collect 5 minute data, and the tariff requires 15 minute data. Sum the 5-minute intervals into 15-minute intervals on even 15-minute boundaries.  If the data passed all the other Validation tests, it is considered validated.

b)	If the meter is programmed to collect data at a larger interval than required by the meter’s tariff.  For example, the meter is programmed to collect 60 minute intervals, but the MDMA Server and tariff require 15 minute intervals.  Prorate the data by assuming an even load distribution during the interval.  In this example, the usage in the 60-minute interval would be divided by 4 to estimate the usage in a 15-minute interval.  The data is marked as estimated.  The meter needs to be reprogrammed to the correct interval.

c)	If the meter is programmed to collect data at a smaller interval than required by its tariff, but the meter’s interval doesn't evenly divide into the interval required by the tariff.  For example, the meter is programmed to collect 10 minute intervals, and the tariff requires 15 minute intervals. The data would be estimated and marked as estimated.  To estimate data, all collected intervals that are contained within the required reporting interval are included in the appropriate reporting interval.  Collected intervals that cross the boundaries of required reporting intervals are included proportionally in both reporting intervals.  In this example, if there were three 10 minute intervals containing 10 kWh, 20 kWh, and 30 kWh, the corresponding estimated 15 minute intervals would contain 20 kWh (10 + .5*20) and 40 kWh (.5*20 + 30).   This is similar to the prorating technique discussed in Appendix A.  The meter needs to be reprogrammed to the correct interval.