# Appendix C

# This document proposes the interim minimum standards and requirements for installation, maintenance and testing of Direct Access meters and metering equipment that meters and metering equipment must comply with for use in direct access metering starting in 1998.  These standards and requirements are extracted from the Meter Data and Communication Systems (MDCS) Workshop Report, Appendix B, filed with the California Public Utilities Commission, July 25, 1997.

# I.  VISUAL INSPECTION

For safety reasons, an initial visual inspection must be completed prior to performing any metering work on site and visual observations must continue to be employed as the work progresses. Metering work includes, but is not limited to meter installation, replacement, maintenance, programming and testing.

A.	All Meter Sites: Visual inspections for all meter sites shall include or identify 	the following:

1.	Electrical Hazards.

2.	Physical Hazards.

## 3.	Infractions and Evidence of Tampering/Energy Diversion.

4.  	Clock Load.

- DA Metering Verification.

6.	DA Communication Verification.

7.	Unsafe conditions at customers’ premises.

8.	Vermins in panels.

B.	Transformer Rated Meter Sites:  In addition to the inspections described in 	the “All Meter Sites” section above, a visual inspection of all Transformer Rated 	Meter 	sites must include or identify the following:

1.	Billing Constant Verification.

2.	Improper Wiring.

C.	Pole Mounted Meter Sites: In addition to the inspections described in sections 	A. and B. above, a visual inspection of pole-mounted meter sites must include 	or identify the following:

1.	Open cutouts and blown triple link fuses.

2.	Broken grounding connections.

D.	Ground Fault Conditions on Any Phase: If detected, report the hazards to the UDC immediately for emergency corrections and notify the customer or customer’s representative

## II.   TESTING

A voltage test and register verification test shall be performed on all direct access metering installations and removals.  All tests specified below shall be performed as required by the CPUC-approved tariff and on a meter testing schedule.  This schedule shall be the same as or better than the current UDC test standard or policy.  The following is the list of applicable tests for metering systems, sockets and current transformers.

Tests on metering systems1

- Light & full load test

- Demand test

- Register verification

- Separate element test2

Tests on sockets

- Voltage test

- Phase angle test3

1 Metering system tests may be performed at a qualified testing facility.  The metering systems may be 1) the meter itself, or 2) the meter and its attached device(s) which is used for billing data storage, communications, or any other purposes.

2  Only required for installations with test switches or test blocks.

3  Only required for installations with a phase-shifting transformer

## III.   REPORTING

## A.  Reporting Unacceptable Service Conditions:

Whenever service conditions are not safe or affect metering accuracy, the Meter Service Provider shall report such conditions to ESP, UDC and customers.  Reporting procedures between the ESP and UDC will be included in the ESP agreement.

## Third Party Equipment

- The Meter Service Provider shall correct the unsafe equipment or inaccurate metering conditions and notify UDC of its before-and-after-correction conditions. If the Meter Service Provider is not responsible for the equipment, the Meter Service Provider shall notify the third party of this unsafe or inaccurate condition for corrective action and report to the UDC.

## UDC Equipment

- Upon the Meter Service Provider’s notification, the UDC shall correct the unsafe equipment or inaccurate metering conditions caused by its own equipment within a reasonable period.  If a condition is considered to be hazardous and can be easily corrected, the Meter Service Provider should immediately correct it.  If the hazard is unable to be resolved, the Meter Service Provider must work in conjunction with the UDC to resolve the dangerous situation.

### 3.	Customer Equipment

- The Meter Service Provider shall send a letter to notify the customer of the equipment that is unsafe or affects the metering accuracy for corrective actions, and send a copy of such letter to the UDC.  The customer will be given a reasonable period of time to repair and provide to the ESP, Meter Agent and UDC the name and phone number of a party who does the work to correct this condition.  If repairs are not performed to correct this condition within a reasonable period, the Meter Service Provider shall follow up with the customer to ensure the repair work is performed.

4.	Notification

The Meter Service Provider shall notify the customer, UDC and ESP all unsafe and inaccurate meter site conditions as found via inspection and testing.

## B.  Documentation of Inspection and Meter Testing

The Meter Service Providers shall document all site inspections and meter test appropriately. This documentation should be available to all involved parties upon request.  If there is a need for a consistent format of site inspection and meter testing documentation, the interest parties and UDCs shall work together to develop such documentation format for use statewide.

# ATTACHMENT 1  -  APPENDIX C

# I.  VISUAL INSPECTION

A.	All Meter Sites: Visually inspect all meter sites for the following conditions:

1.	Electrical Hazards:

- Exposed wiring, damaged sockets (loose or burnt wiring or jaws), auto-bypass devices (load jaws still hot when meter removed), loose or missing screws (i.e., in bypass area), missing panels, loose or broken service insulators, service wires in bad condition/order, missing meter, improper grounding conditions, fused neutral conductor of a 2 wire or 3 wire single phase service, defective service switch/disconnect, new installations which fail to conform with the UDC’s electric service requirements, etc.

- UDC installed voltage arrestors: Should be remove or cut in clear if present unless UDC requests to keep arrestors in place.

2.	Physical Hazards

- Tripping hazards (slippery or uneven surfaces), debris or materials stored in the working space, overhead hazards (stored materials or workers above meters).

- Environmental hazards: Chemical, caustic, hearing, biological, etc.

- Inadequate or unsafe access

- Meter Mounting: loose meter mounting, undue vibration, inability to securely seal metering, unleveled meter.

## 3.	Infractions and Evidence of Tampering/Energy Diversion

a) 	Meter Installation

- Awareness of significant connected loads compared to a customer's monthly energy consumption.

- Irregularities in the service conductor's insulation ("skinned" insulation, newly-taped sections of conductors, burned or pitted service conductors, etc.)

- Unauthorized connection in overhead service entrance, on line side of metering transformers, or in unsealed underground pull section.

- Unauthorized seals, and unsealed or improperly sealed conditions on gutters, wire ways, pull sections, test block compartments, test switch covers, and meter sealing rings.

- Suspicious wiring.

- Jumpers across current leads at bottom of test switch unsealed.

- Meter Coil Jumpered - Check and correct if the neutral service wire is found connected through the series coil of the meter and there are grounds on the load circuits that act as a jumper.

- Lock Fuse Jumpered - Check for lock fuse jumper and perform a regular meter test.  Jumper will be left as found, and this condition will be reported on the test report.

- Blown (or loosened) fuse in one leg of a 3-wire old sequence service.

- Wiring in unsealed raceway or pull box.

- Rate infractions in the meter program/register.

b)	Meter Cover: An unusually clean cover, small holes in the cover, burn marks on or near the cover, visible fingerprints inside the cover, etc.

c)	KWH Register: KWH dial pointer alignment, register mesh and register gears

d)	Meter Disk: Disk alignment to magnets, irregularity of disk rotation, foreign objects or materials on disk/bearing, scratches or wear marks on the disk

e)	Test Blocks: Damaged wiring between test block and meter, unusual marks, scratches or burns on test blocks, defective test blocks, etc.

f)	Meter Base: Unusual marks and mushroomed screw slots on potential links; broken meter seals; unusual wear or scratches, burn or pit marks on meter stabs/blades/terminals; etc.

g)	Meter Socket: Unusual wear or scratches, burnt or pit marks, irregular meter socket voltages, circuit bypass jumper, etc.

h)	Hidden "Service Riser" Taps and Unmetered Circuits Utilizing Relay Devices: Unusual noises that could indicate a relay opening when the meter is removed from the socket.

- Clock Load : Calculate and record customer's load at time of arrival.

5.	DA Metering Verification:

- Check for proof of DA meter certification or meter types that had been installed prior to 1/1/98 and grandfathered.

- Verify for correct billing information (records versus meters) including billing constant, meter number, accuracy test results, customer information, etc.

- Verify for correct meter and service (voltage, form, etc.)

6.	DA Communication Verification:

- Verify for correct phone or other communication devices and connections if remote read

- Verify for successful communication handshakes and data retrieval if remote read (This can be done by another person at a remote location, and data accuracy is not verified at this time).

- Verify for successful meter reading if manual read.

7.	Customer premises: Unsafe conditions of customer-owned stairs, railings, platforms, etc.

8.	Vermins: Watch out for insects, snakes, and rodents when opening doors or removing panels.

B.	Transformer Rated Meter Sites

In addition to the inspections described in the All Meter Sites section above, visually inspect all Transformer Rated Meter sites for the following conditions:

1.	Billing Constant: Compare between records versus sites (CT’s/PT’s ratios)

2.	Improper Wiring: Shorted current by-pass links, reverse current secondary wired, unmatched voltage and current circuits, pinched or rubbed secondary wires near panel hinges.

C.	Pole Mounted Meter Sites

In addition to the inspections described in the All Meter Sites section above, visually inspect pole-mounted meter sites for the following conditions:

1.	Cutouts: Open cutouts, blown triple link fuses.

2.	Grounding: Ground conductors and connections shall not be broken at any point between the meter enclosure and the ground rod.

D.	Grounding

- PG&E, SCE, and SDG&E have three phase services with ground connection on one of the phases.  In situations where A, B, or C, phase is not grounded and there is a voltage reading at or near zero volts on any phase and reading above zero volts on any other phases, report the hazard to the UDC immediately for emergency corrections and contact the customer or customer’s representative to inform them of the hazardous conditions.  If it is unclear whether a phase is intentionally grounded, contact the local UDC to clarify the configuration of the service.  Additionally, take an extreme caution on primary (above 600 V), 480 V phase to phase or 277 V phase to ground service.

II. METER TESTING

1. 	Matrix of Meter Testing Requirements

|  |  | TASK |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| C O D E | Type of Meters/Registers | 1 Voltage Test | 2 Light & Full Load Test | 3 Demand Test | 4 Register Verification | 5 Phase Angle Test | 6 Separate Element Test | 7 Burden Test | Possible Other Types Í | COMMENTS | C O D E |
| (a) | Self-Contained kWh Meters | X | X |  |  |  | X |  | (g), (j) | Mechanical Meter | (a) |
| (b) | Transformer-Rated kWh Meters | X | X |  |  |  | X | X | (g), (j) | Mechanical Meter | (b) |
| (c) | Hybrid Meters | X | X | X | X |  | X |  | (i), (j) |  | (c) |
| (d) | Solid State Meters | X | X | X | X |  |  |  | (g), (i), (j) |  | (d) |
| (e) | Transformer-Rated kVARh Meters | X | X |  |  | X | X | X | (j) | Mechanical Meter | (e) |
| (f) | Multi-Quadrant Meters | X | X |  | X |  | X | X | (g), (j) |  | (f) |
| (g) | Solid State Recorders | X |  | X |  |  |  |  |  |  | (g) |
| (h) | Mechanical Registers |  |  |  |  |  |  |  | (g), (j) |  | (h) |
| (i) | Electronic Registers |  |  |  |  |  |  |  | (g), (j) |  | (i) |
| (j) | Pulse Devices |  |  | X |  |  |  |  |  |  | (j) |
| (k) | Self-Contained Network Meters | X |  |  |  |  |  |  | (g), (j) |  | (k) |

 Performed if demand is present.   Energy Consumption Investigation (ECI) is necessary.   Performed when deemed necessary or requested by customers.

 The alphabetical codes in the “Possible Other Types” column refer to the “Code” column on this matrix and indicate that additional tests must be performed

as required if the other types exist at the sites.

2.	Task #1: Voltage Test

On all services, measure the secondary voltage, with an approved volt meter,  between the line phases and line to ground even if it is an ungrounded service and record all voltage readings on the test tag.  All nominal voltages have an allowable tolerance of ±5%.

A.  Secondary Distribution Voltages: 	Normal rating of 120 Vac.

Table 1: Nominal Voltages and allowable limits on Secondary

| Nominal Voltage (Volt) | Maximum (Volt) | Minimum (Volt) |
| --- | --- | --- |
| 120 | 126 | 114 |
| 208 | 218 | 198 |
| 240 | 252 | 228 |
| 277 | 291 | 263 |
| 480 | 504 | 456 |

Table 2: Service Voltages and allowable limits on Secondary

| Service Voltage (Volt) | Measured Voltage (Volt) | Maximum (Volt) | Minimum (Volt) |
| --- | --- | --- | --- |
| 120/240V 3w 1ø | 120V Phase to Ground 240V Phase to Phase | 126 252 | 114 228 |
| 120/208V 3w 1ø | 120V Phase to Ground 208V Phase to Phase | 126 218 | 114 198 |
| 120/208V 4w 3ø | 120V Phase to Ground 208V Phase to Phase | 126 218 | 114 198 |
| 120/240V 4w 3ø | 120V Phase to Ground 208V Phase to Ground 240V Phase to Phase | 126 218 252 | 114 198 228 |
| 277/480V 4w 3ø | 277V Phase to Ground 480V Phase to Phase | 291 504 | 263 456 |
| 240V 3w 3ø | 240V Phase to Phase | 252 | 228 |
| 480V 3w 3ø | 480V Phase to Phase | 504 | 456 |

B.  Primary Distribution and Transmission Voltages: These voltages have secondary voltage rating of 115 Vac or 120 Vac.   The voltage transformer primary may be connected either wye or delta.

Table 3: Primary and Transmission Voltages with their secondary voltages and ratios

| Possible System L-L Voltage (Volt) | VT Primary Voltage (Volt) | Secondary Rating (Volt) | Ratio |
| --- | --- | --- | --- |
| 2,400 or 4,200 | 2,400 | 120 | 20:1 |
| 4,200 or 7,200 | 4,200 | 120 | 35:1 |
| 7,200 or 12,000 | 7,200 | 120 | 60:1 |
| 12,000 or 20,125 | 12,000 | 120 | 100:1 |
| 17,200 | 18,000 | 120 | 150:1 |
| 20,125 or 34,500 | 20,125 | 115/67.08 | 175/300:1 |
| 60,000 | 34,500 | 115/69 | 300/500:1 |
| 69,000 | 40,250 | 115/67.08 | 350/600:1 |
| 115,000 | 69,000 | 115/69 | 600/1000:1 |
| 138,000 | 80,500 | 115/69 | 700:1 |
| 230,000 | 138,000 | 115/69 | 1,200/2000:1 |
| 500,000 | 287,500 | 115/69 | 2,500/4200:1 |

3.	Task #2: Light Load & Full Load Test

Light load is 10% of name plate or test Amp rating, and full load is 100% of name plate or test Amp rating.  The light and full load test is performed at 100% power factor to verify the accuracy of the meter by comparing its test results with a Standard Meter of known traceable accuracy.

- No Load or Creep Test (for mechanical and hybrid meters only):

Test meters will be energized with no connected load, and the disk observed for rotation.  A minimum amount of creep is acceptable if the rotation stops when an anti-creep hole reaches the meter stator.

- Accuracy test:

Single phase and polyphase meters are to be tested with potential coils connected in parallel and the current coils connected in series.  The minimum duration of the test will be 1 disk revolution for light load and 10 disk revolutions for full load.  For solid state meters, calculated pseudo revolutions will be used.

- Adjustments:

Meters found within the limits required by the local UDC need not be adjusted.

- Reporting:

Correction factors for light load and full load tests will be recorded as the meter accuracy results.

Example: A 0.5% fast and slow meter:

Correction Factor		Accuracy

Fast			0.995				+0.5%

Slow			1.005				-0.5%.

- UDC Notification
Meter Agent must notify the UDC’s upon finding a defective meter that affects billing.

- Single Phase Services:

This task is not required for single phase services.

4.	Task #3: Demand Test

This test procedure can be done on site or at the responsible agency’s testing facility.

A.  Mechanical Demand Meters

Test for the accuracy of the demand registers by checking the marked register ratio and time interval as follows:

- Advancing Mechanism:

Visually inspect the pusher arm and gears for worn out parts.

- Clutch:

Check that the pusher arm returns to zero at the end of interval when the clutch releases it.  Verify that this is a smooth operation and the pusher arm it returns to the stop position.

- Timing Motor:

Check that the timing motor is operating.  If the motor is not operating the demand reading will most likely be off scale.

- Time Interval and Demand Test:

Test the time interval to insure that it is as marked on the register name plate by timing the motor gear and clocking an interval, or performing a demand test.  The demand test is performed by minimally applying full load current for 125 disk revolutions on 15 minute demand meters and for 250 disk revolutions on 30 minute demand meters.

- Demand Mechanism:

Check that the demand reset returns the pointer to zero on a reset action and that the pointer will advance to full scale.

- Reporting:

Correction factor for the demand test will be recorded as the meter accuracy result.

Example: A 0.5% fast and slow meter:

Correction Factor		Accuracy

Fast			0.995				+0.5%

Slow			1.005				-0.5%.

B.  Solid State Meters and Electronic Registers

Below is a procedure for a demand test on a solid state meter or an electronic register.

- Place the meter register in the TEST MODE.

- Press reset button to clear all test registers and start new demand interval.

- Apply full load current for 25 disk revolutions as a minimum.

- Scroll the register display to show present kW demand.  If the kW value is in pulses, calculate the actual kW value.

- Calculate and record the correction factor by comparing the meter kW value with the kW in the test standard.

- Return the meter to the NORMAL MODE.

5.	Task #4: Register Verification

A.  Mechanical Register

Visually inspect and verify that the register is correct for the watt-hour meter, and  that the register constant, gear ratio, and register ratio are correct for the register.

- Gear mechanism:

Check that the gears are clean, and check the proper engagement between gears and between the first gear and the disk shaft.

- Mechanical register:

Check that the register ratio is the same as marked.  The register ratio (Rr) is determined by counting the number of revolutions required of the first gear to cause the first dial pointer to make one complete revolution.

B.  Electronic register

Because electronic registers are different for each type and manufacturer, manufacturer’s manual should be referred to for specific procedures for these registers.   Below is a typical procedure for verifying electronic registers after they are programmed with proper parameters:

- Check all numerical segments and identifiers on the meter display.

- Check the meter is scrolling properly through all registers.

- Check the function of the registers by disconnecting and then restoring power on the meter.  The meter should resume normal display operations and reading after this power outage.

- Verify the programming parameters are correct.

- Check the register memory and load profile data memory to verify that data is being stored.

6.	Task #5: Phase Angle Test

Check for correct wiring on a reactive metering site and proper phase shift on each phase circuit.  If the rotation is not correct, the site will have a leading Power Factor.  When the rotation is correct, the site will have a lagging Power Factor.

- Reactiformer voltage:

Measure the voltage on the top of the reactiformer to insure the proper voltage is applied to the potential coil in the RKVAh meter.  If the voltage is not correct, the following are possibilities of errors:

1) Factory incorrect wiring on the reactiformer

2) Incorrect voltage for the applied service

3) Incorrect wiring at the site during installation.

- Power Factor Calculation:

Calculate the load on the KWH and the RKVAH meters and the power factor for the site.  This power factor is used as a cross check for the measured phase angle.

- Current Measurement:

Measure each phase current and record it accordingly.

- Phase Angle Measurement:

Use phase angle meter to measure each phase angle and record it accordingly.

- Phase Angle Plot:

After measuring all voltages, currents and phase angles, plot a phase angle test and cross check with the calculated power factor.

7.	Task #6: Separate Element Test

Check individual elements of transformer rated and self contained meters for proper disk rotation or registration by performing the following:

- Testing

Energize with the appropriate phase potentials and place current on individual elements, and check for forward rotation or positive registration

- Correct phasing

Check that the proper potential coil and current coil are wired correctly in the meter.  If the meter is installed correctly on the socket, the meter disk will rotate forward.

- No forward rotation

If an element has no rotation check the following:

- Open potential coil (Check with a magnet or an ohmmeter.)

- No load current.

- Note

u	Phase angle relationships may cause slight reverse rotation in cases where there is a poor power factor.  If any substantial reverse rotation is observed, the service should be checked for unmetered loads.  This will only occur on three wire three phase metered service sites.

- Single Phase Services:

This task is not required for single phase services.

8.	Task #7: Burden Test

This test procedure can be done on site or at the responsible agency’s testing facility.

Check the operating conditions of current transformers in the field by performing the following conditions:

- Method

Put built-in burdens of a multi-range Amp meter in series with the secondary of the test current transformers (CT) to obtain the Amp readings. These amp readings should have the same deflection.

- Possible Problems

If one CT has a reading significantly different from the others, check for shorted turns or other problem stated below:

u	Short circuited primary turns.

u	Short circuited secondary turns.

u	High resistance connections in the secondary circuit.

u	Short circuited secondary wiring.

u	Grounding of normally ungrounded wire.