APPENDIX B

This document proposes the interim minimum standards and testing requirements that meters and metering equipment must comply with for use in direct access metering starting in 1998. These standards and tests are extracted from the Meter Data and Communication Systems (MDCS) Workshop Report, Appendix A, filed with the California Public Utilities Commission, July 25, 1997.

I.	MINIMUM STANDARDS FOR DIRECT ACCESS METERS

AND METERING EQUIPMENT

DEFINIITONS:

"Meter":	Device which measures and records energy consumption data for the purpose of determining the financial obligation for entity consuming energy.

"Optical port":   The device attached to the meter which transfers energy consumption data to a handheld or laptop computer via optical signal.

______________________________________________________________________

Standard 							Applicablity

______________________________________________________________________

ANSI C12.1-1995, Code for Electricity Metering	All Meters

ANSI C12.7 Watt-hour Meter Socket				All Meters

ANSI C12.10 Electromechanical Watt-hour Meters	Electro-												mechanical Meters

ANSI C12.13, Electronic TOU Registers 			Electronic TOU

for Electricity Meters					Registers

ANSI C12.18, Type 2 Optical Port				Optical Ports

ANSI C37.90.1, Surge Withstand Test			All Meters

ANSI Z1.4 and ANSI Z1.9,Sampling Procedures		All Meters and

and Tables for Inspecton					Optical Ports

______________________________________________________________________

APPENDIX B, page 2

II.	TESTING REQUIREMENTS FOR DIRECT ACCESS METERS

1.	General

1.1	In addition to the applicable testing requirements of the ANSI Standards, the tests specified shall be conducted by qualified facilities to confirm correct operation of the Meter. A qualified facility is a facility that has the neccessary equipment and personnel to perform the testing requirements specified in this document.

1.2	Performance testing is required for new Meter designs and for Meter product changes as defined below:

1.2.1   Design changes that can affect the reliability or performance of the Meter.

1.2.2  Design revisions made to increase manufacturing process efficiency on a qualified Meter are exempt from re-certification testing.

1.3	The manufacturer or  qualified facility shall provide a certified test report documenting the tests and their results to the purchaser. The test report will be signed by the chief engineer or manager of the qualified facility and include all charts, graphs and data recorded during testing. The purchasor  shall make available all test reports to the local UDC ,for those meters which are installed within the local UDC area, upon request.

1.4	No equipment shall be installed before all tests as outlined in this section are conducted.

1.5	Each test shall be conducted by using the number of Meters specified in Section 4.4.2 of ANSI C12.1-1995.  These Meters are representative of production run meters.

1.6	All tests shall be conducted using the same test Meters selected as specified in Section 4.4.2 of ANSI C12.1-1995.

1.7	All test Meters shall be kept as a certification proof for one year after the conclusion of the testing.  These test Meters shall be submitted to any organization who wants to inspect them and shall be returned to the manufacturers.

1.8	Meters which fail during the test shall not be repaired or tested further.

1.9	When the test Meters fails to meet these testing requirements and after any correction is made on the new test Meters, all  tests shall be re-started over with the new test Meters.

1.10	The purchasor reserves the right to witness the tests.

APPENDIX B, page 3

2.	Meter Failure Definition

A Meter shall be designated as failed if any of the following events occur:

2.1	Failure of the Meter to perform all of the specified functions.

2.2	Failure of the Meter to meet the technical performance specifications included in the Specification.

2.3	Signs of physical damage or performance degradation as a result of a test procedure, including effects which could shorten the service life of the meter.

2.4	The occurrence of an unexpected change of state, loss of data or other unacceptable mode of operation for the Meter as a consequence of a test procedure.

2.5	Failures shall be classified as a hardware, firmware or software failure, or a combination according to the following definitions:

2.5.1  Firmware failures are errors made during the fabrication of programmable read only memory (PROM) chips such that the required program or instruction set that the microprocessor is to perform is incorrect. Failures of DIP switches, jumpers, and links are also included.

2.5.2  Hardware failures are failures that are physical in nature and directly traceable to the component level. Visual observances such as discoloration, cracking, hardening of cables, poor solder joints, etc. are also included.

2.5.3  Software failures are failures such as the loss or unintended change of data, the inability to program the Meter, the loss of the Meter program, or the erroneous output or display of false information.

3.	Meter Model Rejection Criteria

A Meter model will be rejected if any of the following events occur:

3.1	The failure of one Meter during one test procedure and the failure of a second Meter during another test procedure.

3.2	The failure of two or more Meters during the same test procedure.

APPENDIX B, page 4

4.	Test Setup

4.1	The Meter shall be connected to its normal operating supply voltage with a fully charged Power Failure Backup System. The Meter shall be energized throughout the duration of the test

procedures, unless otherwise stated.

4.2	Before testing commences, the Meter shall be energized for a minimum of two hours at room temperature for stress relief.

4.3	All tests shall be conducted at room temperature unless otherwise specified.

4.4	The Meter shall be loaded to the nameplate test amperes at 100% power factor for all tests unless otherwise indicated.

4.5	If part of the Meter is electromechanical, the Meter accuracy of (0.5% (instead of (0.3%) shall be acceptable.

4.6	Full load test is 100% of the meter test amps, and light load test is 10% of the meter test amps.

5.	Recommended ANSI Tests 									All meter certifications will be performed in accordance with the certification tests described in ANSI C12.1 (NEMA, 1995), unless noted otherwise below.

* Tests 1 through 24:	no clarifications required.

* Test 25:			substitute ANSI C37.90.1 for this test

* Test 26:			expand frequency range to 14 kHz - 10gHz to 					accommodate the application of this meter 					standard to various communications (e.g. 					telephone, radio, satellite, power line 					carrier, etc.) products

* Test 27 through 29:	no clarifications required

* Test 30:			no clarifications required on test 					methodology, temperature limits are defined 					for operations under California weather 					conditions as +85 C = T oper-max,

-20 C = stor-min

* Test 31 through 38:	no clarifications required

* Additional test A1:	sunlight interference test is needed for 					optical pick-up type retrofit modules (not 					within scope of existing ANSI C12.1-1995 					tests) and is further defined below.

APPENDIX B, page 5

Test A1: Sunlight Interference Test

A.	This test verifies the Meter accuracy and full functional operations under direct sun light.

B.	The Meter cover shall be removed during this test.

C.	The Meter shall be exposed to both the incandescent light source and sunlight.

D.	The incandescent light source, Smith Vector #710 or equivalent, shall be used to simulate the sunlight.  The incandescent light shall be 600 watt and 3,200( K blackbody radiation as a minimum.

E.	The Meter shall be exposed to the incandescent light source for minimum five minutes for each position of the incandescent light source.

F.	The incandescent light source shall be pointed directly toward the Meter and positioned at a maximum direct distance of 16 inches from the Meter as follows:

1.	Twelve positions around the Meter base.

2.	Eight positions at a 45( angle from the Meter base.

3.	One position at a 90( angle from the Meter base 			(perpendicular to the face of the Meter).

G.	Verify the Meter operations and report the direct and remote meter reads before and after each incandescent light exposure.

H.	The sunlight conditions shall be outdoors, clear sky, bright sunny day and no shades over the Meter.

I.	The Meter shall be exposed to the sunlight conditions for 24 hours.

J.	The Meter shall be set in a position as normally installed the field. All Meters under test shall be exposed to the sunlight conditions at the same time and evenly face different directions starting with one Meter facing towards the sunrise direction.

K.	Record and compare direct and remote meter reads at every hour under the sunlight conditions.

L.	To pass this test the Meter shall operate as specified with no observed anomalies and have an accuracy of  (0.3% on both direct and remote meter reads.