# DA Meter Site Installation Inspection and Testing Requirements

# APPENDIX B

It is understood that the approved meter installation and maintenance standards must reflect the minimum requirements for the industry.  Currently, there are not available national standards for meter installation, maintenance and work.  Therefore, the meter inspection and testing practices must be carefully reviewed to insure that the legacy UDC process be appropriately applied and adopted for Direct Access.

# Purpose of this Appendix

Appendix B is intended to provide a compilation of UDCs’ practices for inspecting and testing meter installations.  In addition, this Appendix provides some procedures for rectifying unsafe and inaccurate metering conditions discovered during routine meter installation and testing.

TABLE OF CONTENTS

SITE INSPECTIONS

Page

I.	Visual Inspection																		1

A.	All Meter Sites 									1

B.	Transformer Rated Meter Sites I							4

C.	Pole Mounted Meter Sites							4

D. 	Grounding									5

E.	Identification of Primary (above 480 V) Metering Installations			6

II.	Reporting Unacceptable Service Conditions						6

A.	Third Party Equipment								6

B.	UDC Equipment									7

C.	Customer Equipment								7

D.	Reporting Conditions								8

TESTING REQUIREMENTS

I. 	Matrix of Testing Requirements							9

II.	Task #1:  Voltage Test									10

A.	Secondary Distribution Voltages							10

B.	Primary Distribution and Transmission Voltages					11

III.	Task #2:  Light Load & Full Load Test							12

IV.	Task #3:  Demand Test								14

A.	Mechanical Demand Meters							14

B.	Solid State Meters and Electronic Registers					15

V.	Task #4:  Register Verification								16

A.	Mechanical Register								16

B.	Electronic Register																16

VI.	Task #5:  Phase Angle Test								17

VII.	Task #6:  Separate Element Test							18

VIII.	Task #7:  Burden Test									19

DOCUMENTATION REQUIREMENTS

I. 	Site Inspection and Meter Testing Documentation					20

# SITE INSPECTIONS

# i.	Visual Inspection:

A.	All Meter Sites: Visually inspect all meter sites for the following conditions:

1.	Electrical Hazards:

- Exposed wiring.

- Damaged sockets: Loose or burnt wiring or jaws.

- Auto-bypass devices: Load jaws still hot when meter is removed.

- Loose or missing screws in the field meter person's working area (i.e., bypass area).

- Missing panels.

- UDC installed voltage arrestors: Remove or cut in clear if present.

2.	Physical Hazards

- Tripping hazards.

- Slippery or uneven surfaces.

- Debris or materials stored in the working space

- Overhead hazards: Stored materials or workers above meter locations.

- Environmental hazards: Chemical, caustic, hearing, biological, etc.

- Inadequate or unsafe access

## 3.	Infractions and Evidence of Tampering

- Meter Coil Jumpered - Check and correct if the neutral service wire is found connected through the series coil of the meter and there are grounds on the load circuits that act as a jumper.

- Lock Fuse Jumpered - Check for lock fuse jumper and perform a regular meter test.  Jumper will be left as found, and this condition will be reported on the test report.

- Blown (or loosened) Fuse in one Leg of a 3-wire Old Sequence Service.

- Wiring in Unsealed Raceway or Pull Box.

- Rate Infractions in the meter program/register - Where applicable, verify the rate parameters in the meter.

4.  	Energy Diversion:

a) 	Meter Installation

- Awareness of significant visual connected loads (i.e., swimming pool pump, spas, central air conditioning, ornamental yard lighting, or occupied out buildings) compared to a customer's monthly energy consumption.

- Irregularities in the service conductor's insulation:  "skinned" insulation, newly taped sections of conductors, burned or pitted service conductors), etc..

- Unauthorized connection or “tap” in service entrance “weather head”, on line side of metering transformers, or in unsealed underground pull section.

- Unauthorized seals, and unsealed or improperly sealed conditions on gutters, wire ways, pull sections, test block compartments, test switch covers, and meter sealing rings.

- Suspicious wiring.

- Jumpers across current leads at bottom of test switch unsealed.

b)	Meter Cover

- The overall appearance of the cover (a clean cover is unusual)

- Small holes in the cover

- Burn marks on or near the cover

- Visible fingerprints inside the cover

- Any unusual conditions inside cover

c)	kWh Register

- KWH dial pointer alignment

- KWH register mesh and register gears

d)	Meter Disk

- Disk alignment to magnets

- Irregularity of disk rotation

- Foreign objects or material on disk/bearing

- Scratches or wear marks on the disk

e)	Test Blocks

- Visual line, load and meter loop wiring check

- Unusual marks, scratches or burns

f.)	Underground Pull Section

- Service conductor termination

- Meter loop buss

g)	Meter Base

- Meter seal

- Meter potential link (i.e., unusual marks, mushroomed screw slots)

- Meter stabs/blades or terminals (i.e., unusual wear or scratches, burn or pit marks, external bypass)

h)	Meter Socket

- Unusual wear or scratches

- Burn or “pit” marks

- Meter socket voltages

- Unmetered circuit

- Bypass jumper

i)	Hidden "Service Riser" Taps and Unmetered Circuits Utilizing Relay Devices

- Check for irregularities in the vicinity of the "riser" (Unusual noises that could indicate a relay opening when the meter is removed from the socket).

- Clock Load :

- Calculate customer's load at time of arrival and record on test form if necessary or required by the local UDC.

6.	DA Metering Verification:

- Check for proof of DA meter certification or meter types that had been installed prior to 1/1/98 and grandfathered.

- Verify for correct billing information (records versus meters) including billing constant, meter number, accuracy test results, customer information, etc.

- Verify for correct meter and service (voltage, form, etc.)

7.	DA Communication Verification:

- Verify for correct phone or other communication devices and connections if remote read

- Verify for successful communication handshakes and data retrieval if remote read (This can be done by another person at a remote location, and data accuracy is not verified at this time).

- Verify for successful meter reading if manual read.

8.	Meter Mounting:

- Verify that the meter is securely mounted and properly leveled.

- If the mounting board is loose on the customer structure and repair work on the customer’s property is required and can be done safely, the Meter Agent shall obtain the customer’s permission prior to performing the repair work and notified the local UDC of this repair work.

- If repair or replacement of damaged sockets, panels and associated equipment needs to be done and can be done safely and may affect the meter accuracy, the Meter Agent or customer shall notify the UDC of the situation for the UDC’s assistance if necessary.

B.	Transformer Rated Meter Sites

In addition to the inspections described in the All Meter Sites section above, visually inspect all Transformer Rated Meter sites for the following conditions:

1.	Billing Constant:

- Verify for correct billing constant (records versus sites: metering transformers’ ratios).

2.	Proper Wiring:

- Current by-pass links not shorted.

- Current secondary wired in reverse.

- Voltage and current circuits not matched.

- Secondary wires pinched or rubbing near panel hinges.

C.	Pole Mounted Meter Sites

In addition to the inspections described in the All Meter Sites section above, visually inspect pole-mounted meter sites for the following conditions:

1.	Cutouts

- Open Cutouts

- Blown Triple Link Fuses: This condition should be corrected before performing any work at the site.

2.	Ground

- Proper ground: Ensure that the ground conductor and connections are not broken at any point between the meter enclosure and the ground rod.

3.	Customer premises

- Customer Owned Stairs, Railings, Platforms etc.: Observe them to ensure a safe workplace and refer unsafe conditions to the UDC for replacement or repair.

4.	Vermins

- Doors and Panels: Carefully inspect for insects, snakes, and rodents when opening doors or removing panels because surprises may cause you to throw a cover or body part into an energized bus.

D.	Grounding

PG&E, SCE, and SDG&E all have three phase services with ground connection on one of the phases.   In situations where A, B, or C, phase is not grounded and there is a voltage reading at or near zero volts on any phase and reading above zero volts on any other phases, report the hazard to the UDC immediately for emergency corrections and contact the customer or customer’s representative to inform them of the hazardous conditions.If it is unclear whether a phase is intentionally grounded, contact the local UDC to clarify the configuration of the service Additionally, take an extreme caution on 480 V phase to phase or 277 V phase to ground service.

- Ground Faults in Customer's Panel or Equipment:

- Once the ground fault has been located in the customer’s equipment, the following action shall be taken:

- In no instance while investigating a ground fault, will the Meter Agent operate customer's equipment or make repairs to wiring.

- Monitor voltmeter readings while the customer operates to open their load disconnects.

- If defective equipment is the cause of the ground fault and the customer elects to immediately discontinue using the defective equipment, state the customer’s corrective actions on the test report. If the customer decides not to discontinue using the defective equipment,  inform the customer that UDC will be notified for emergency service disconnection and immediately notify UDC for service shutdown.

- Once the ground fault condition has been corrected, notify UDC of the resolution.

### 2.	Ground Faults at Meter or Metering equipment

- If the ground fault condition is caused by a defective meter, replace the defective meter and verify if the ground fault condition is eliminated.  In those instances where a replacement meter is not available, remove the defective meter, leave service cut-in-flat until a replacement meter is available, and notify UDC of this situation.

- When the ground fault condition is located on the line-side of the metering, immediately notify UDC and customer of this hazard condition.  UDC will immediately correct this condition.

E.	Identification of Primary (above 480 V) Metering Installations

## Extreme cautions shall be taken when working on the primary metering installations.

The following are  features to assist in  identifying primary installations.

- Panel has "High Voltage" signs attached.

- Data plates attached to the panel show voltage and amperage rating.

- On switchboard panels, the main disconnect is located on the line side of the metering (old sequence).

- Large metal or wood box mounted on the pole above or near the meters.

- Primary voltages of metering transformers range 2.4 kV to 220 kV.

- Substations or transformers located on the customer's premises.

- Billing meters are always 120 volts.

- Meters usually, but not always, have a large multiplier.

- Self-contained meters located on a primary rated panel will have a "Caution" label affixed to the panel.

## II. 	Reporting Unacceptable Service Conditions:

Whenever service conditions are not safe or affect metering accuracy, the Meter Agent shall report such conditions to ESP, UDC and customers.  Reporting procedures between the ESP and UDC will be included in the ESP agreement.

## Third Party Equipment

- The Meter Agent shall correct the unsafe equipment or inaccurate metering conditions and notify UDC of its before-and-after-correction conditions. If the Meter Agent is not responsible for the equipment, the Meter Agent shall notify the third party of this unsafe or inaccurate condition for corrective action and report to the UDC.

## UDC Equipment

- Upon the Meter Agent’s notification, the UDC  shall correct the unsafe equipment or inaccurate metering conditions caused by its own equipment within a reasonable period.  If a condition is considered to be hazardous then the unsafe condition should be corrected by the Meter Agent.  If the hazard is unable to be resolved, the Meter Agent must work in conjunction with the UDC to resolve the dangerous situation.

### C.	Customer Equipment

- The Meter Agent shall notify the customer (with a customer notification letter) of the equipment that is unsafe or affects the metering accuracy for corrective actions, and send a copy of such letter to the UDC.  The customer will be given a reasonable period of time to repair and provide to the ESP, Meter Agent and UDC the name and phone number of a party who does the work to correct this condition.  If repairs are not performed to correct this condition within a reasonable period, the Meter Agent shall follow up with the customer to ensure the repair work is performed.

D.	Reporting Conditions:

The Meter Agent shall notify the customer, UDC and ESP the following conditions which may affect the continuity or quality of service to the customer:

#### Service insulators are loose or broken.

#### Service wires are in bad order (i.e., too low, contacting structures, bare insulation and running through trees, etc.)

#### When a meter is apparently missing or stolen, the Meter Agent should cover and seal all exposed energized metering equipment.

#### Line and/or load wires are cut.  The Meter Agent shall remove meter and have an online request issued to the UDC to remove or de-energize the service as appropriate.

#### Transformer neutral is not properly grounded.

#### Customer initiates a high or low voltage complaint.

#### Neutral conductor of a 2 wire or 3 wire single phase service is fused.

#### Defective service switch, not causing errors in registration.

#### Meter mounting loose or "out of plumb," where condition cannot be readily corrected by the Meter Agent.

#### Meter accessibility inadequate for testing due to location, mounting, or adjacent structures.

#### Undue vibration of the meter mounting.

#### Inability to securely seal metering due to construction.

#### "Series coil in Neutral," when condition cannot be corrected by the Meter Agent.

#### Defective test block, when condition cannot be corrected by the Meter Agent.

#### Defective service switch on a 3 wire old sequence service where the meter registration may be affected.

#### In general, any condition (except tampering) which interferes with the proper registration of the meter or presents a safety hazard.

#### New installations which fail to conform with the UDC’s Electric Service Requirements.

TESTING REQUIREMENTS

I. 	Matrix of Testing Requirements

|  |  | TASK |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| C O D E | Type of Meters/Registers | 1 Voltage Test | 2 Light & Full Load Test | 3 Demand Test | 4 Register Verification | 5 Phase Angle Test | 6 Separate Element Test | 7 Burden Test | Possible Other Types Í | COMMENTS | C O D E |
| (a) | Self-Contained kWh Meters | X | X |  |  |  | X |  | (g), (j) | Mechanical Meter | (a) |
| (b) | Transformer-Rated kWh Meters | X | X |  |  |  | X | X | (g), (j) | Mechanical Meter | (b) |
| (c) | Hybrid Meters | X | X | X | X |  | X |  | (i), (j) |  | (c) |
| (d) | Solid State Meters | X | X | X | X |  |  |  | (g), (i), (j) |  | (d) |
| (e) | Transformer-Rated kVARh Meters | X | X |  |  | X | X | X | (j) | Mechanical Meter | (e) |
| (f) | Multi-Quadrant Meters | X | X |  | X |  | X | X | (g), (j) |  | (f) |
| (g) | Solid State Recorders | X |  | X |  |  |  |  |  |  | (g) |
| (h) | Mechanical Registers |  |  |  |  |  |  |  | (g), (j) |  | (h) |
| (i) | Electronic Registers |  |  |  |  |  |  |  | (g), (j) |  | (i) |
| (j) | Pulse Devices |  |  | X |  |  |  |  |  |  | (j) |
| (k) | Self-Contained Network Meters | X |  |  |  |  |  |  | (g), (j) |  | (k) |

 Performed if demand is present.   Energy Consumption Investigation (ECI) is necessary.   Performed when deemed necessary or requested by customers.

 The alphabetical codes in the “Possible Other Types” column refer to the “Code” column on this matrix and indicate that additional tests must be performed

as required if the other types exist at the sites.

II.	Task #1: Voltage Test

On all services, measure the voltage, with an approved volt meter,  between the line phases and line to ground even if it is an ungrounded service and record all voltage readings on the test tag.  All nominal voltages have an allowable tolerance of ±5%.

A.  Secondary Distribution Voltages: 	Normal rating of 120 Vac.

Table 1: Nominal Voltages and allowable limits on Secondary

| Nominal Voltage (Volt) | Maximum (Volt) | Minimum (Volt) |
| --- | --- | --- |
| 120 | 126 | 114 |
| 208 | 218 | 198 |
| 240 | 252 | 228 |
| 277 | 291 | 263 |
| 480 | 504 | 456 |

Table 2: Service Voltages and allowable limits on Secondary

| Service Voltage (Volt) | Measured Voltage (Volt) | Maximum (Volt) | Minimum (Volt) |
| --- | --- | --- | --- |
| 120/240V 3w 1ø | 120V Phase to Ground 240V Phase to Phase | 126 252 | 114 228 |
| 120/208V 3w 1ø | 120V Phase to Ground 208V Phase to Phase | 126 218 | 114 198 |
| 120/208V 4w 3ø | 120V Phase to Ground 208V Phase to Phase | 126 218 | 114 198 |
| 120/240V 4w 3ø | 120V Phase to Ground 208V Phase to Ground 240V Phase to Phase | 126 218 252 | 114 198 228 |
| 277/480V 4w 3ø | 277V Phase to Ground 480V Phase to Phase | 291 504 | 263 456 |
| 240V 3w 3ø | 240V Phase to Phase | 252 | 228 |
| 480V 3w 3ø | 480V Phase to Phase | 504 | 456 |

B.  Primary Distribution and Transmission Voltages: These voltages have secondary voltage rating of 115 Vac or 120 Vac.   The voltage transformer primary may be connected either wye or delta.

Table 3: Primary and Transmission Voltages with their secondary voltages and ratios

| Possible System L-L Voltage (Volt) | VT Primary Voltage (Volt) | Secondary Rating (Volt) | Ratio |
| --- | --- | --- | --- |
| 2,400 or 4,200 | 2,400 | 120 | 20:1 |
| 4,200 or 7,200 | 4,200 | 120 | 35:1 |
| 7,200 or 12,000 | 7,200 | 120 | 60:1 |
| 12,000 or 20,125 | 12,000 | 120 | 100:1 |
| 17,200 | 18,000 | 120 | 150:1 |
| 20,125 or 34,500 | 20,125 | 115/67.08 | 175/300:1 |
| 60,000 | 34,500 | 115/69 | 300/500:1 |
| 69,000 | 40,250 | 115/67.08 | 350/600:1 |
| 115,000 | 69,000 | 115/69 | 600/1000:1 |
| 138,000 | 80,500 | 115/69 | 700:1 |
| 230,000 | 138,000 | 115/69 | 1,200/2000:1 |
| 500,000 | 287,500 | 115/69 | 2,500/4200:1 |

III.	Task #2: Light Load & Full Load Test

Perform the light load and full load test to check for the accuracy of the meter under test by comparing its test results with a Standard Meter of known traceable accuracy.  The following tests and corrective actions can either be performed on site or at the responsible agency’s testing facility.  The following tests need to be performed for this test:

- No Load or Creep Test (for mechanical and hybrid meters only):

Test meters will be energized with no connected load, and the disk observed for rotation.  A minimum amount of creep is acceptable if the rotation stops when an anti-creep hole reaches the meter stator.

- Accuracy test:

Single phase and polyphase meters are to be tested with potential coils connected in parallel and the current coils connected in series.  Tests will be done at light load (normally 10% of name plate or test Amp rating) and at full load (normally 100% of name plate or test Amp rating).  Both are performed at 100% power factor, and their results are compared with the Standard and reported on the electric measurement test form.  The minimum duration of the test will be 1 disk revolution for light load and 10 disk revolutions for full load.

Note:	For solid state meters, calculated pseudo revolutions will be used.  Changing the Kh constants on these solid state meters will vary the speed of the pseudo disk or the disk simulator.  Because the KWH is calculated directly from the measured voltage and current in the meter, there is no real Kh in these solid state meters as well as no real disk.  Because the mechanical meters have been used in the industry for many years and people are very much familiar with disk revolutions and Kh values, these terms are still applied for solid state meters to avoid confusions and they are simply the byproducts of the calculated KWH in the meters.  This also means that changing the Kh values inside the solid state meters will not affect the calculated KWH or meter accuracy.

- Adjustments:

Meters found within the limits required by the local UDC need not be adjusted.

- Correction Factor Calculation:

Correction factors for light load and full load will be determined by dividing the observed value displayed on the test standard by the expected test constant.  The correction factor of the test meter is different from the correction factor of the site.  The correction factor of the site is to be recorded in proper keypunch boxes on the test form.  SDG&E applies no correction factors to meters.

- UDC Notification
Meter Agent must notify the UDC’s upon finding a defective meter that affects billing.

- Single Phase Services:

This task is not required for single phase services.

IV.	Task #3: Demand Test

This test procedure can be done on site or at the responsible agency’s testing facility.

A.  Mechanical Demand Meters

Test for the accuracy of the demand registers by checking the marked register ratio and time interval as follows:

- Advancing Mechanism:

Visually inspect the pusher arm and gears for worn out parts.  The pusher arm and gears should be clean.

- Clutch:

Check that the pusher arm returns to zero at the end of interval when the clutch releases it.  Verify that this is a smooth operation and the pusher arm it returns to the stop position.

- Timing Motor:

Check that the timing motor is operating.  If the motor is not operating the demand reading will most likely be off scale.

- Time Interval:

Test the time interval to insure that it is as marked on the register name plate.  This may be done by timing the motor gear and clocking an interval, or performing a demand test.

- Demand Mechanism:

Check that the demand reset returns the pointer to zero on a reset action and that the pointer will advance to full scale.

- Reporting:

Record the demand test results on the electric measurement test form.

Task #3: Demand Test (Cont.)

B.  Solid State Meters and Electronic Registers

Test for the accuracy of the demand registers by measuring and comparing the demand of the test meter with the standard.  Because solid state meters and electronic registers are designed differently, they required slightly different procedures when performing a demand test.  Below is a typical procedure for a demand test on a solid state meter or an electronic register.

| Step | Action |
| --- | --- |
| 1 | Place the meter register in the TEST MODE . |
| 2 | Press reset button to clear all test registers and start new demand interval. |
| 3 | Apply full load current for 25 disk revolutions as a minimum. |
| 4 or... | Scroll the register display to show present kW demand or display KW (i.e., 000.72) |
| 4 | Scroll the register display to show pulses (i.e., 00300) and calculate the display KW as follows: · · |
| - 5 | Use of Revolutions IB-10 or SC-10 Test Standards to calculate the standard KW · · |
| or ... 5 | Use of Watt-hours-Radian Test Standard to calculate the standard KW · · |
| 6 | Return the meter to the NORMAL MODE. Calculate the correction factor by dividing the standard KW by the display KW and record the results on the electric measurement test form. |

V.	Task #4: Register Verification

This test can either be performed on site or at the responsible agency’s testing facility.

A.  Mechanical Register

Visually inspect and verify that the register is correct for the watt-hour meter, and  that the register constant, gear ratio, and register ratio are correct for the register.

- Gear mechanism:

Check that the gears are clean, and check the proper engagement between gears and between the first gear and the disk shaft.  Some meters have intermediate gears which are part of the over all gear ratio.

- Mechanical register test:

Check that the register ratio is the same as marked.  The register ratio (Rr) is determined by counting the number of revolutions required of the first gear to cause the first dial pointer to make one complete revolution.  Check the watt-hour constant Kh by running a 1 kW load test on the meter. It is recommended that this function be completed but is not required.

B.  Electronic register

Because electronic registers are different for each type and manufacturer, manufacturer’s manual should be referred to for specific procedures for these registers.  Some registers can be self-tested once a day for demand rate schedules, at midnight for TOU rate schedules, upon power-up, or upon optical communication.  Below is a typical procedure for verifying electronic registers after they are programmed with proper parameters:

- Check all numerical segments and display identifiers are displayed on the LCD.

- Check the meter is scrolling properly through all registers.  This indicates that the meter and its internal components are functional.

- Check the function of the registers by disconnecting and then restoring power on the meter.  If the meter resumes normal display operations and reading after this power outage, this verifies normal operation of the registers.

- Verify the programming parameters are correct.

- Check the register memory and load profile data memory to verify that data is being stored.

VI.	Task #5: Phase Angle Test

Check for correct wiring on a reactive metering site and proper phase shift on each phase circuit.  If the rotation is not correct, the site will have a leading Power Factor.  When the rotation is correct, the site will have a lagging Power Factor.

- Reactiformer voltage:

Measure the voltage on the top of the reactiformer to insure the proper voltage is applied to the potential coil in the RKVAh meter.  If the voltage is not correct, the following are possibilities of errors:

1) Factory incorrect wiring on the reactiformer

2) Incorrect voltage for the applied service

3) Incorrect wiring at the site during installation.

- Power Factor Calculation:

Calculate the load on the KWH and the RKVAH meters and the power factor for the site.  This power factor is used as a cross check for the measured phase angle.  It is recommended that this function be performed.

- Current Measurement:

Measure each phase current and record it accordingly.

- Phase Angle Measurement:

Use phase angle meter to measure each phase angle and record it accordingly.

- Phase Angle Plot:

After measuring all voltages, currents and phase angles, plot a phase angle test and cross check with the calculated power factor.

VII.	Task #6: Separate Element Test

Check individual elements of transformer rated and self contained meters for proper disk rotation or registration by performing the following:

- Testing

Energize with the appropriate phase potentials and place current on individual elements, and check for forward rotation or positive registration

- Correct phasing

Check that the proper potential coil and current coil are wired correctly in the meter.  If the meter is installed correctly on the socket, the meter disk will rotate forward.

- No forward rotation

If an element has no rotation check the following:

- Open potential coil - Check for an open potential coil with a magnet or an ohmmeter.

- No load current - Clamp an Amp meter on all phase conductors to ensure no customer load.

- Note

u	Phase angle relationships may cause slight reverse rotation in cases where there is a poor power factor.  If any substantial reverse rotation is observed, the service should be checked for unmetered loads.  This will only occur on three wire three phase metered service sites.

u	Some solid state meters may appear to have a cross phase condition.  This is the nature of the electronic circuit design and power measurement in these meters.

- Single Phase Services:

This task is not required for single phase services.

VIII.	Task #7: Burden Test

This test procedure can be done on site or at the responsible agency’s testing facility.  Periodic burden testing is not required, however during on site testing it is recommended that this test procedure be performed.

Check the operating conditions of current transformers in the field by performing the following conditions:

- Method

Put built-in burdens of a multi-range Amp meter in series with the secondary of the test current transformers (CT) to obtain the Amp readings. These amp readings should have the same deflection for any given balanced load because most three phase sites have the same brand, size, and type of current transformers.  Imposing additional secondary burden on a good CT does not cause any change in the secondary current amp reading.

- Possible Problems

If one CT has a reading significantly different from the others, it probably has shorted turns or other problem stated below:

u	Short circuited primary turns.

u	Short circuited secondary turns.

u	High resistance connections in the secondary circuit.

u	Short circuited secondary wiring.

u	Grounding of normally ungrounded wire.

DOCUMENTATION REQUIREMENTS

I.	Site Inspection and Meter Testing Documentation

All site inspections and meter tests will require appropriate documentation. This documentation should be available to all involved parties upon request. Furthermore, the format of site inspection and meter testing documentation should be consistent on a statewide basis. The UDCs will submit a proposed format for this documentation to the CPUC by October 1, 1997. In the proposal, the UDCs will not require the documentation to be handwritten. This will allow Meter Agents to use MDT (Mobile Data Transmitter) systems to enter their site inspection and meter testing data. However, this documentation should be available to all involved parties in hardcopy form.