A. Skills requirements by meter work/functions (e.g. voltage levels, amperage rating)

1.	CLASS 1

A.	Metering Types and Voltages

This class includes single phase, socket-based meters, 300 volts phase-to-phase maximum and does not include transformer rated meters.    Communication wiring must be outside of energized meter panels.

B.	Work to be Performed

Class 1 Meter Workers can install, remove and replace single-phase, 120/240 volt or 120/208 volt, self-contained meters in standard socket based residential-type metering equipment.    Connections of communication conductors must be outside the energized meter panels.

D.	Essential Technical Skills

1. Understanding of single phase electrical metering

2. Understanding of electric distribution safety procedures

3. Ability to identify energy diversion or tampering related to this class of meter work

4. Ability to install and remove damaged and undamaged meters

5. Understanding of the meter panel and socket layout for the metering conditions related to this class of meter work

6. Ability to read meters used in this class

7. Ability to properly use tools appropriate to the work in this class

8. Ability to connect meter communications external to the meter panel

9. Ability to initialize meter communication modules - not utilizing Type 2 optical ports and meter configuration software

2.	CLASS 2

A.	Metering Types and Voltages

This class includes all meters and skills required for Class 1.    Class 2    includes poly-phase, safety socket and standard socket-based meters, 300 volts phase-to-phase maximum and does not include transformer rated meters. Communication wiring may be behind the panel, and work can be in and around energized circuits.

B.	Work to be Performed

Class 2 Meter Workers can install, remove and replace single-phase and poly-phase, 120/240 volt or 120/208 volt, self-contained meters in safety socket and standard socket based metering equipment. Operates test-bypass facilities in self-contained safety sockets.    Communication wiring may be installed inside the panel, and work can be performed in and around energized circuits. On panels without test-bypass facilities, polyphase meters will not be removed or installed without first disconnecting the customer load.

D.	Essential Technical Skills

1. Cumulative including all skills for Class 1

2. Additionally, possess skills related to meter voltages and meter forms used in Class 2

3. Ability to perform phase rotation assessments

4. Ability to operate test-bypass facilities or test blocks in a self-contained safety socket

5. Ability to perform work required to route communication wiring to accommodate meter communications

3.	CLASS 3

A.	Metering Types and Voltages

This class includes all meter types in Classes 1 and 2.    Class 3 includes up to 600V, poly-phase, safety socket or socket-based, A-base, K-base, and transformer rated meters with internal diagnostics.      Communication wiring may be routed inside the panel, and work can be in and around energized circuits.

B.	Work to be Performed

In addition to Class 1 and 2 Meter Work, Class 3 Meter Workers can install, remove and replace all meters consistent with the above including transformer-rated meters with internal diagnostics (if detected, metering problems with test switches, panel wiring or transformers and transformer wiring will be corrected by a Class 4 or 5 Meter Worker).    Class 3 Meter Workers may operate test switches, but may not install, alter, maintain or replace wiring between the meter, test switch, test block and associated equipment.

D.	Essential Technical Skills

1. Cumulative of all Technical skills for Classes 1 and 2

2. Ability to perform work required to route communication wiring to accommodate meter communications

3. Ability to understand, interpret, identify and take appropriate actions based upon built-in diagnostics of solid state meters

4. Ability to run tests on meters in locations other than in the meter socket using semi-automatic meter test equipment

4.	CLASS 4

A.	Metering Types and Voltages

This class includes all meter types in Classes 1,2 and 3.    Class 4 work includes all metering up to 600V, including transformer rated meters with primary and secondary voltages less than 600V.      Communication wiring may be behind the panel, and work can be in and around energized circuits.

B.	Work to be Performed

In addition to Class 1, 2, and 3 Meter Work, Class 4 Meter Workers can install, remove and replace all meters consistent with the above including transformer-rated meters.    Understands operating characteristics of metering transformers and operates test switches and test blocks.    May perform in-field meter accuracy tests, calibrations and perform all types of meter maintenance and troubleshooting on all meters.    Programs and verifies internal programs and software in solid state meters.

D.	Essential Technical Skills

1. Cumulative of Classes 1, 2 and 3.

2. Ability to perform work on metering switchboards

3. Ability to understand the operating characteristics of metering transformers and how to operate test switches and test blocks.

4. Ability to perform calibration, repair, retrofit, troubleshooting, data collection of electric meters and install, maintain and program advanced metering technologies, including TOU, interval data, real time pricing, remote meter communication, and load control devices

5.	CLASS 5

Class 5 Meter Workers must demonstrate the same skill requirements as Class 4 Workers, plus the additional skills needed to perform work on metering systems with instrument transformer primary side voltages over 600V.    Safety and technical skills are under development but will reflect the heightened degree of electrical hazards and requisite skills, experience and training.    Like the Class 4 Meter Worker, individuals wanting to be qualified for a Class 5 Meter Worker must pass a written and practical test.    Additionally, candidates must possess comparable backgrounds similar to those identified in Class 4 above.    UDC employees in classifications performing these functions are considered qualified.

NOTE: The written and practical test will be jointly developed by the Joint Parties and others, based upon tests currently in use by UDCs and meter service provider entities.

B. Worker safety and minimum safety equipment requirements.

1.	CLASS 1

C.	Safety Skills

1. Job performance in accordance with employing MSP's procedures and safety rules

2. Knowledge of hazards of electricity and ability to perform work to avoid electrical hazards

3. Ability to comply with OSHA requirements

4. On-site use of personal protective equipment

2.	CLASS 2

C.	Safety Skills

1. Same as Class 1 with the addition of the skills necessary for the added voltages and meter forms

2. Electrical safety knowledge and work skills appropriate for three-phase metering less than 300V phase-to-phase, including the ability to identify and refer to a Class 3 or higher meter installer services above 300V phase-to-phase prior to performing work in the service equipment, or if voltage rating is not labeled, at the time of initial voltage check

3.	CLASS 3

C.	Safety Skills

1. Cumulative of all safety skills for Classes 1 and 2

2. Additionally must have the knowledge needed for up to 600V poly-phase, service and the forms and voltages applicable to Class 3 Meter Work

3. Ability to understand, interpret and take appropriate action based on built in diagnostics of solid state meters

4. Ability to work with transformer rated meters and operate test switches and test blocks

4.	CLASS 4

C.	Safety Skills

1. Cumulative of all safety skills for Classes 1, 2 and 3.

2. Ability to conform processes to additional electricity hazards and complexities associated with metering switchboards, testing meters and    maintaining meters.

5.	CLASS 5

Class 5 Meter Workers must demonstrate the same skill requirements as Class 4 Workers, plus the additional skills needed to perform work on metering systems with instrument transformer primary side voltages over 600V.    Safety and technical skills are under development but will reflect the heightened degree of electrical hazards and requisite skills, experience and training.    Like the Class 4 Meter Worker, individuals wanting to be qualified for a Class 5 Meter Worker must pass a written and practical test.    Additionally, candidates must possess comparable backgrounds similar to those identified in Class 4 above.    UDC employees in classifications performing these functions are considered qualified.

NOTE: The written and practical test will be jointly developed by the Joint Parties and others, based upon tests currently in use by UDCs and meter service provider entities.

C. Worker and MSP qualification/certification requirements

1.	CLASS 1

E.	How Essential Technical and Safety Skills Are Determined

1. MSPs will develop and implement a program to train their workers to perform Class 1 meter work safely and properly.

2. Employees will be certified by their employers, based on the use of that program.

3. To facilitate a UDC/ESP agreement for performing meter work in this class, prior to the initiation of a Commission program to certify meter installers, the MSP's training program will be shared with UDCs    and ESPs (in accordance with appropriate non-disclosure agreements).

4. MSP's work can be reviewed by the UDCs

5. UDC employees in classifications performing these functions are considered qualified.

6.    {this wording is now in the opening paragraphs - delete here and the rest of the “how Determined” sections)

2.	CLASS 2

E.	How Essential Technical and Safety Skills Are Determined

1. MSPs will develop and implement a program to train their workers to perform Class 2 meter work safely and properly, including a minimum of 50 hours of "OJT" on operating test-bypass facilities and routing communication wiring in energized panels.

2. Employees will be certified by their employers, based on the use of that program.

3. To facilitate a UDC/ESP agreement for performing meter work in this class, prior to the initiation of a Commission program to certify meter installers, the MSP's training program will be shared with UDCs and ESPs (in accordance with appropriate non-disclosure agreements).

4. MSP's work can be reviewed by the UDCs.

5. UDC employees in classifications performing these functions are considered qualified.

3.	CLASS 3

E.	How Essential Technical and Safety Skills Are Determined

1. MSPs will develop and implement a program to train their workers to perform Class 3 meter work safely and properly.

2. Employees will be certified by their employers, based on the use of that program.

3. To facilitate a UDC/ESP agreement for performing meter work in this class, prior to the initiation of a Commission program to certify meter installers, the MSP's training program will be shared with UDCs and ESPs (in accordance with appropriate non-disclosure agreements).

4. MSP's work can be reviewed by the UDCs

5. UDC employees in classifications performing these functions are considered qualified

F.	Experience Requirements

Minimum experience requirements that must be demonstrated prior to qualification for individuals wanting to become a Class 3 Meter Worker.

A. If entry level experience of any employee is that of a journeyman level electrician, journeyman level electric metering worker, or journeyman level line worker (e.g.    lineman, troubleman), then upon successful completion of the MSP training program the worker may be certified as a Class 3 Meter Worker.

or

B.	After 12 months as a Class 2 Meter Worker which includes 6 months "OJT" working alongside a Class 3 or higher Meter Worker and upon successful completion of the MSP training program a worker may be certified as a Class 3 Meter Worker

or

C.	If an employee has a two or four year degree in a related subject, then after 4 months "OJT" working alongside a Class 3 or higher Meter Worker and upon successful completion of the MSP training program a worker may be certified as a Class 3 Meter Worker.

4.	CLASS 4

E.	How Essential Technical and Safety Skills Are Determined

1. MSPs may develop and implement a program to train workers to perform Class 4 meter work safely and properly (prior to and after testing).

2. All workers will be certified by the test process outlined below

3. MSP's work can be reviewed by the UDCs

4. UDC employees in classifications performing these functions are considered qualified

Testing Process and Qualifications

All individuals seeking to perform DA meter services for an MSP as a Class 4 Meter Worker must successfully pass written and practical (demonstrative) tests.

Prerequisites for taking the written and practical tests include a showing of previous work experience that includes at least one of the following:

1. employment as a journeyman electrician, journeyman metering employee, or journey line worker (e.g., lineman, troubleman),

or

2. minimum of one year experience as a Class 3 Meter Worker,

or

3. minimum of one year experience in utility revenue meter installation, testing and    maintenance

Testing and Re-Certification Requirements

Once an individual takes and passes either the Class 4 or Class 5 Meter Worker Test, they are qualified to perform that class of DA meter work anywhere in California and need not re-take the test to perform work in each UDC service area.

If after being qualified a meter worker does not perform metering work in California for 3 years or more, re-certification will be required prior to performing that class of meter work.

5.	CLASS 5

Class 5 Meter Workers must demonstrate the same skill requirements as Class 4 Workers, plus the additional skills needed to perform work on metering systems with instrument transformer primary side voltages over 600V.    Safety and technical skills are under development but will reflect the heightened degree of electrical hazards and requisite skills, experience and training.    Like the Class 4 Meter Worker, individuals wanting to be qualified for a Class 5 Meter Worker must pass a written and practical test.    Additionally, candidates must possess comparable backgrounds similar to those identified in Class 4 above.    UDC employees in classifications performing these functions are considered qualified.

NOTE: The written and practical test will be jointly developed by the Joint Parties and others, based upon tests currently in use by UDCs and meter service provider entities.

D. Administration of qualifications and disqualification process.