I. 	MSP/METER WORKER QUALIFICATIONS

PSWG recommends the following: 1) four classes of meter equipment, meter service activities and meter workers which are set as criteria for MSPs to perform direct access meter services in California, 2) meter workers currently performing meter work who have previously qualified as a utility journeyman meter tester or utility metering electrician within the State of California will be considered qualified, and 3)UDCs and permanently-certified MSPs (independent MSPs or ESPs) shall certify their direct access meter workers to the correct meter worker classes accordingly, and 4) the meter worker qualification requirements shall uniformly apply to any direct access meter worker, without regard to the meter worker’s employer (UDCs, ESPs or MSPs).

MSPs will issue appropriate identification to each of their meter workers or employees who perform direct access meter work and will ensure that their workers carry this identification during meter work performance.  This identification will indicate the worker’s employer and the class of meter work which the worker is qualified to perform.  If an ESP, UDC or customer subcontracts its meter work to an MSP , the subcontracting entity must ensure that the MSP have issued to each meter worker or employee such identification.

All meter workers performing meter services on behalf of an ESP must meet the requirements as outlined in this Section and exercise due care for the tasks performed.

Below are the descriptions and requirements of these four classes:

I.A. Skills requirements by meter work/functions (e.g. voltage levels, amperage rating)

I.A.1.	CLASS 1

I.A.1.1.	Metering Types and Voltages

This class includes single-phase, socket-based meters, 300 volts phase-to-phase maximum and does not include transformer rated meters.  Communication wiring must be outside of energized meter panels.

I.A.1.2.	Work to be Performed

Class 1 Meter Workers can install, remove and replace single-phase, 120/240 volt or 120/208 volt, self-contained meters in standard socket based residential-type metering equipment.  Connections of communication conductors must be outside the energized meter panels.

I.A.1.3.	Essential Technical Skills

I.A.1.3.1. Understanding of single phase electrical metering

I.A.1.3.2. Understanding of electric distribution safety procedures

I.A.1.3.3. Ability to identify energy diversion or tampering related to this class of meter work

I.A.1.3.4. Ability to install and remove damaged and undamaged meters

I.A.1.3.5. Understanding of the meter panel and socket layout for the metering conditions related to this class of meter work

I.A.1.3.6. Ability to read meters used in this class

I.A.1.3.7. Ability to properly use tools appropriate to the work in this class

I.A.1.3.8. Ability to connect meter communications external to the meter panel

I.A.1.3.9. Ability to initialize meter communication modules - not utilizing Type 2 optical ports and meter configuration software

I.A.1.3.10. Ability to run tests on meters in locations other than in the meter socket using semi-automatic meter test equipment.

I.A.2.	CLASS 2

I.A.2.1.	Metering Types and Voltages

I.A.2.1.1. This class includes all meters and skills required for Class 1.  Class 2  includes up to 600 V, single-phase and poly-phase, safety socket, socket based, A-base, K-base,and transformer rated meters with internal diagnostics.    Communication wiring may be behind the panel, and work can be in and around energized circuits.

##### I.A.2.2.	Work to be Performed

I.A.2.2.1.	Class 2 Meter Workers can install, remove and replace all meters consistent with the above including transformer-rated meters with internal diagnostics (if detected, metering problems with test switches, panel wiring or transformers and transformer wiring will be corrected by a Class 3 or 4 Meter Worker.  Class 2 Meter Workers will understand the operating characteristics of metering transformers and may operate test-bypass facilities and test switches, but may not install, alter, maintain or replace wiring between the meter, test switch, or test block, and associated equipment.  On panels without test-bypass facilities, single-phase and polyphase meters will not be removed or installed without first disconnecting the customer load.  Communication wiring may be installed inside the panel, and work can be performed in and around energized circuits.

I.A.2.3.	Essential Technical Skills

I.A.2.3.1. Cumulative including all skills for Class 1

I.A.2.3.2. Additionally, possess skills related to meter voltages and meter forms used in Class 2

I.A.2.3.3. Ability to perform phase rotation assessments

I.A.2.3.4. Ability to operate test-bypass facilities or test blocks in a self-contained safety socket

I.A.2.3.5. Ability to understand the operating characteristics of metering transformers and how to operate test switches.

I.A.2.3.6. Ability to understand, interpret, identify and take appropriate actions based upon built-in diagnostics of solid state meters

I.A.2.3.7. Ability to perform work required to route communication wiring to accommodate meter communications

I.A.3.	CLASS 3

I.A.3.1.	Metering Types and Voltages

I.A.4.1.1. This class includes all meter types in Class 1 and 2   Class 3  work includes all metering up to 600V, including transformer rated meters with primary and secondary voltages less than 600V.  Communication wiring may be behind the panel, and work can be in and around energized circuits.

.

I.A.3.2.	Work to be Performed

I.A.3.2.1. In addition to Class 1 and 2, Meter Work, Class 3  Meter Workers can install, remove and replace all meters consistent with the above.(Note now covered in Class 2)  May perform in-field meter accuracy tests, calibrations and perform all types of meter maintenance and troubleshooting on all meters.  Programs and verifies internal programs and software in solid state meters.

I.A.3.3.	Essential Technical Skills

I.A.3.3.1. Cumulative of Class 1 and 2.

I.A.3.3.2. Ability to perform work on metering switchboards

(Note now covered in Class 2)

I.A.3.3.3. Ability to perform calibration, repair, retrofit, troubleshooting, data collection of electric meters and install, maintain and program advanced metering technologies, including TOU, interval data, real time pricing, remote meter communication, and load control devices

I.A.4.	Class 4

## I.A.4.1		Metering Types and Voltages

Class 4 Meter Workers must demonstrate the same skill requirements as Class 3 Meter Workers, plus meet the State of California requirements for a “Qualified Electrical Worker” to perform work on metering systems with instrument transformer primary side voltages above 600 volts.  Class 4 Meter Workers must have a minimum of two years of training and experience with high-voltage (above 600 volts) equipment and circuits and who has demonstrated by performance familiarity with the work to be performed and the hazards involved.  In addition, individuals wanting to be qualified for a Class 4 Meter Worker must pass a written and practical test.

# I.A.4.2		Work to be Performed

Work performed within metering compartments or equipment rated above 600 volts shall be conducted by UDC personnel.  In addition to Class 1, 2, and 3 meter work, Class 4 Meter Workers can install, remove and replace all meters consistent with the above including transformer-rated meters.  In addition, Class 4 Meter Workers may approach energized primary side (above 600 volts) metering current and potential transformers to perform primary side metering voltage indication tests including the use of live-line tools.  Replace high-voltage fuses.  May perform in-field meter accuracy tests, calibrations and perform all types of meter maintenance and troubleshooting on all meters.  Inspects wiring and instrument transformer ratios utilizing various apparatus as necessary on circuits of all voltages including advance metering principles.  Performs overall tests on energized circuits up to and including 5.0 K.V.  The Class 4 Meter Worker when working on conductors or equipment energized above 600 volts shall work with another qualified electrical worker or an employee in training. UDC employees in classifications performing these functions are considered qualified.

### I.A.4.3		Essential Technical Skills

I.A.4.3.1	Cumulative of Classes 1, 2 and 3.

I.A.4.3.2	Ability to identify primary metering equipment and characteristics of service equipment rated at voltages above 600 volts.

I.A.4.3.3	Broad knowledge and familiarity of electrical distribution systems above 600 volts and operating characteristics.

I.A.4.3.4	Ability to identify UDC service voltages and Electrical Service Requirements.

I.A.4.3.5	Broad Knowledge and familiarity of State of California General Orders.

I.B. Worker safety and minimum safety equipment requirements.

I.B.1.	CLASS 1

I.B.1.1. Job performance in accordance with employing MSP's procedures and safety rules

I.B.1.2. Knowledge of hazards of electricity and ability to perform work to avoid electrical hazards

I.B.1.3. Ability to comply with OSHA requirements

I.B.1.4. On-site use of personal protective equipment

I.B.2.	CLASS 2

I.B.2.1. Cumulative including all skills and safety knowledge for Class 1

I.B.2.2. Electrical safety knowledge and work skills appropriate for single-phase and three-phase metering up to 600V phase-to-phase, including the ability to identify and refer to a Class 3 or higher meter installer services above 600V phase-to-phase prior to performing work in the service equipment.

I.B.2.3. Ability to perform phase rotation assessments.

I.B.2.4. Ability to operate test-bypass facilities or test blocks in a self-contained safety socket.

I.B.2.5. Ability to perform work required to route communication wiring to accommodate meter communications.

I.B.2.6. Additionally must have the knowledge needed for up to 600V single-phase and poly-phase service, and the forms and voltages applicable to Class 2 Meter Work.

I.B.2.7. Ability to understand, interpret and take appropriate action based on built in diagnostics of solid state meters.

I.B.2.8. Ability to work with transformer rated meters and operate test switches and test blocks.

I.B.3.	CLASS 3

I.B.3.1. Cumulative of all safety skills for Classes 1 and 2.

I.B.3.2. Ability to conform processes to additional electricity hazards and complexities associated with metering switchboards, testing meters and  maintaining meters.

I.B.4.	CLASS 4

I.B.4.1 Cumulative of all safety skills for Classes 1, 2, and 3.

I.B.4.2	Ability to conform processes to additional electricity hazards and complexities associated with metering switchboards, testing meters and maintaining meters in service equipment above 600 volts.

I.C. Worker and MSP qualification/certification requirements

I.C.1.	CLASS 1

I.C.1.1.	How Essential Technical and Safety Skills Are Determined

I.C.1.1.1. MSPs will develop and implement a program to train their workers to perform Class 1 meter work safely and properly.

I.C.1.1.2. Employees will be certified by their employers, based on the use of that program.

I.C.1.1.3. To facilitate a UDC/ESP agreement for performing meter work in this class, prior to the initiation of a Commission program to certify meter installers, the MSP's training program will be shared with UDCs  and ESPs (in accordance with appropriate non-disclosure agreements).

I.C.1.1.4. MSP's work can be reviewed by the UDCs

I.C.1.1.5. UDC employees in classifications performing these functions are considered qualified.

I.C.1.1.6. ESP and MSP employees, who in current employment are or, previous employment were, in classifications performing these functions are considered qualified.

I.C.1.1.7.  MSPs will develop and implement a program to train their workers to perform Class 1 meter work safely and properly, including a minimum of fifty (50) hours of  on the job training (“OJT”) working alongside a Class 1 Meter Worker, or higher.

I.C.2.	CLASS 2

I.C.2.1.	How Essential Technical and Safety Skills Are Determined

I.C.2.1.1. MSPs will develop and implement a program to train their workers to perform Class 2 meter work safely and properly.

I.C.2.1.2. Employees will be certified by their employers, based on the use of that program.

I.C.2.1.3. To facilitate a UDC/ESP agreement for performing meter work in this class, prior to the initiation of a Commission program to certify meter installers, the MSP's training program will be shared with UDCs and ESPs (in accordance with appropriate non-disclosure agreements).

I.C.2.1.4. MSP's work can be reviewed by the UDCs.

I.C.2.1.5. UDC employees in classifications performing these functions are considered qualified.

I.C.2.1.6.  ESP and MSP employees, who in current employment are, or previous employment were, in classifications performing these functions are considered qualified.

I.C.2.2.		Experience Requirements

Minimum experience requirements that must be demonstrated prior to qualification for individuals wanting to become a Class 2 Meter Worker.

I.C.2.2.1.	If entry level experience of any employee is that of a journeyman level electrician, journeyman level electric metering worker, or journeyman level line worker (e.g.,  lineman, troubleman), then upon successful completion of the MSP training program the worker may be certified as a Class 2 Meter Worker,

or

I.C.2.2.2.	After 12 months as a Class 1 Meter Worker which includes 6 months “OJT” working alongside a Class 2 or higher Meter Worker and upon successful completion of the MSP training program a worker may be certified as a Class 2 Meter Worker,

or

I.C.2.2.3.	If an employee has a two or four year degree in a related subject, then after four (4) months "OJT" working alongside a Class 2 or higher Meter Worker and upon successful completion of the MSP training program a worker may be certified as a Class 2 Meter Worker.

I.C.3.	CLASS 3

I.C.3.1.	How Essential Technical and Safety Skills Are Determined

I.C.3.1.1. MSPs may develop and implement a program to train workers to perform Class 3 meter work safely and properly (prior to and after testing).

I.C.3.1.2. All workers will be certified by the test process outlined below

I.C.3.1.3. MSP's work can be reviewed by the UDCs

I.C.3.1.4. UDC employees in classifications performing these functions are considered qualified

I.C.3.1.5.  ESP and MSP employees, who in current employment are, or previous employment were, in classifications performing these functions are considered qualified.

I.C.3.2 	Testing Process and Qualifications

All individuals seeking to perform DA meter services for an MSP as a Class 3 Meter Worker must successfully pass written and practical (demonstrative) tests.

Prerequisites for taking the written and practical tests include a showing of previous work experience that includes at least one of the following:

I.C.3.2.1. employment as a journeyman electrician, journeyman metering employee, or journey line worker (e.g., lineman, troubleman),

or

I.C.3.2.2. minimum of one year experience as a Class 2 Meter Worker,

or

I.C.3.2.3. minimum of one year experience in utility revenue meter installation, testing and  maintenance

I.C.3.3 	Testing and Re-Certification Requirements

I.C.3.3.1. Once an individual takes and passes either the Class 3 or Class 4 Meter Worker Test, they are qualified to perform that class of DA meter work anywhere in California and need not re-take the test to perform work in each UDC service area.

I.C.3.3.2. If after being qualified a meter worker does not perform metering work in California for 3 years or more, re-certification will be required prior to performing that class of meter work.

I.C.3.4.	Continuing Education (submitted by Phaser)As part of a Class 3 Meter Worker’s ongoing ability to remain qualified the individual must participate in at least ten (10) hours annually of  the MSP’s training program regarding standards of practice and safety related issues.

I.C.4.	CLASS 4

I.C.4.1		How Essential Technical and Safety Skills are Determined.

I.C.4.1.1	MSP may develop and implement a program to train employees to perform Class 4 meter work safely and properly follow OSHA guideline (prior to and after testing).

I.C.4.1.2	ESP and MSP employees who in current employment or previous employment were in classifications performing functions meeting qualified electrical worker requirements.

I.C.4.1.3	UDC employees in classifications performing qualified electrical worker functions are considered qualified for Class 4.

I.C.4.1.4	All workers will be certified by the test process outlined below.

### I.C.4.2		Testing Process and Qualifications

I.C.4.2.1	All individuals seeking to perform DA meter services for an MSP as a class 4 Meter Worker must successfully pass written and practical skills (demonstrative) tests.

I.C.4.2.2	Prerequisites for taking the written and practical skills tests including verification of previous work experience that includes at least one of the following:

I.C.4.2.2.1	Recognized employment as a journeyman electrician (above 600 volts) with qualified electrical worker status.

I.C.4.2.2.2	Recognized employment as a journeyman metering employee with two years minimum working experience on metering equipment above 600 volts.

I.C.4.2.2.3	Journeyman Line Worker, Line Mechanic, Lineman, Apparatus Technician or similar position that has completed a recognized apprenticeship program that meets minimum OSHA requirements.

I.C.4.2.2.4	Minimum OSHA experiences and required training as a Class 3 Meter Worker.

### I.C.4.3		Testing and Re-Certification Requirements

I.C.4.3.1	Once an individual takes and passes the Class 4 written and practical skills test, and has completed the requirements for performing work on energized metering equipment above 600 volts, that individual is qualified to perform work anywhere in California and need not re-take the written test to perform work in each UDC.  However, each employer may require additional practical skills testing to determine appropriate skill levels.

I.C.4.3.2	If after being qualified as a Class 4 Meter Worker and the individual does not perform Class 4 metering work in California for 3 years or more, re-certification will be required by written and practical skills testing.

I.D. Administration of qualification and disqualification process

(to be developed…)

I.E. Implementation of MSP Certification (Joint Meets)

I.E.1.	Joint meet check list (see Section II.D)

I.E.1.1 UDCs will use the joint meet check list to evaluate an MSP’s meter installation.

I.E.1.2 The check list will include safety items, critical and non-critical procedures.   Safety items are for ensuring safety of the general public and meter workers, and the critical procedures are those that must be completed to ensure successful operations of UDCs, ESPs and MDMAs.

I.E.2.	Failure criteria for a failed joint meet

The following is the criteria for failing a joint meet:

I.E.2.1 Any one item of safety and critical procedures is not performed correctly.

I.E.1.2.2 30% of non-critical procedures are not performed correctly.

I.E.3.	Joint meet log (see Attachment ?? - to be developed with a consistent format):

I.E.3.1 UDCs will prepare the joint meet log and send its copy to the MSP.

II. 	METER INSTALLATION AND MAINTENANCE

This section proposes the minimum requirements for installation, maintenance and testing for meters and metering equipment that are used in direct access. These requirements are extracted from the MDCS Workshop Report, Appendix B, filed with the CPUC on July 25, 1997.

II.A.	SAFETY (customer life support, public, etc.)

For safety reasons, the following requirements must be completed prior to performing any meter work on site and visual observations must continually apply as the meter work progresses.  Meter work includes, but not limited to, meter installation, meter replacement, maintenance, programming and testing.  Visually inspect all meter sites for the following conditions:

II.A.1.	Customer life support

A medical meter ring seal, white in color with a red caduceus (medical seal), will be placed through the UDC’s or ESP’s meter ring seal.  An existing label or sign may be attached on customer’s meter nameplate or panel, but is not required and should be removed when life support is no longer present.  This medical seal requires no avoidable power interruption to the customer because the customer has a life support system in the premise.

II.A.2.	Electrical Hazards:

II.A.2.1. Exposed wiring, damaged sockets (loose or burnt wiring or jaws), auto-bypass devices (load jaws still hot when meter removed), loose or missing screws (i.e., in bypass area), missing panels, loose or broken service insulators, service wires in bad condition/order, missing meter, improper grounding conditions, fused neutral conductor of a 2 wire or 3 wire single phase service, defective service switch/disconnect, new installations which fail to conform with the UDC’s electric service requirements, etc.

II.A.2.2.  REMOVAL OF 600 VOLT AUTO VALVE:

Auto valves may be found on 480 volt overhead meter installations, both self contained and instrument rated.  Functional in the field the auto valve can safely be removed from the meter installation.  The auto valve can be identified as a round or square metal can the size of a large human fist.  The auto valve is mounted through a knock out and secured with a net on the inside of the can.  There will be 3 black wires and 1 white wire.  The 3 black wires are electrically connected to each of the 3 phase wires on the service.  The white wire is connected to an earth ground.

The auto valve is attached to the socket side of the test block or test switches.  By de-energizing the socket, the wires from the auto valve can be removed and disposed of. Ensure that the hole left in the service equipment is properly closed and sealed for weather.

II.A.3.	Physical Hazards:

II.A.3.1. Tripping hazards (slippery or uneven surfaces), debris or materials stored in the working space, overhead hazards (stored materials or workers above meters).

II.A.3.2. Environmental hazards: Chemical, caustic, hearing, biological, etc.

II.A.3.3 Inadequate or unsafe access

II.A.3.4. Meter Mounting: loose meter mounting, undue vibration, inability to securely seal metering, unleveled meter.

II.A.4.	Customer premises:

Unsafe conditions of customer-owned stairs, railings, platforms, etc.

II.A.5.	Vermins:

Watch out for insects, snakes, and rodents when opening doors or removing panels.

II.B.	Meter security and accessibility

The following requirements must be completed when performing any meter work on site and visual observations must continually apply as the meter work progresses.  Visually inspect all meter sites for the following conditions:

II.B.1.	Infraction and evidence of tampering/energy diversion:

II.B.1.a. Meter Installation

II.B.1.a.1 Awareness of significant connected loads compared to a customer's monthly energy consumption.

II.B.1.a.2 Irregularities in the service conductor's insulation ("skinned" insulation, newly-taped sections of conductors, burned or pitted service conductors, etc.)

II.B.1.a.3 Unauthorized connection in overhead service entrance, on line side of meter, or metering transformers, or in unsealed underground pull sections or pull cans.

II.B.1.a.4 Unauthorized seals, and unsealed or improperly sealed conditions on line side raceways,  test block compartments, test switch covers, and meter sealing rings.

II.B.1.a.5 Suspicious wiring.

II.B.1.a.6 Jumpers across current leads at bottom of test switch unsealed.

II.B.1.a.7 Meter Coil Jumpered - Check and correct if the neutral service wire is found connected through the series coil of the meter and there are grounds on the load circuits that act as a jumper.

II.B.1.a.8 Lock Fuse Jumpered - Check for lock fuse jumper and perform a regular meter test.  Jumper will be left as found, and this condition will be reported on the test report.

II.B.1.a.9 Blown (or loosened) fuse in one leg of a 3-wire old sequence service.

(See II.B.1.a.4).

II.B.1.a.10 Rate infractions in meter program/register.

II.B.1.b) Meter Cover

An unusually clean cover, small holes in the cover, burn marks on or near the cover, visible fingerprints inside the cover, etc.

II.B.1.c) KWH Register

KWH dial pointer alignment, register mesh and register gears

II.B.1.d) Meter Disk

Disk alignment to magnets, irregularity of disk rotation, foreign objects or materials on disk/bearing, scratches or wear marks on the disk

II.B.1.e) Test Blocks

Damaged wiring between test block and meter, unusual marks, scratches or burns on test blocks, defective test blocks, etc.

II.B.1.f) Meter Base

Unusual marks and mushroomed screw slots on potential links; broken meter seals; unusual wear or scratches, burn or pit marks on meter stabs/blades/terminals; etc.

II.B.1.g) Meter Socket

Unusual wear or scratches, burnt or pit marks, irregular meter socket voltages, circuit bypass jumper, etc.

II.B.1.h) Hidden "Service Riser" Taps and Unmetered Circuits Utilizing Relay Devices:

Unusual noises that could indicate a relay opening when the meter is removed from the socket.

II.B.2.	Meter Security

Meters and meter panels installations shall be secured with appropriate locking devices such as seals, locking rings.  Also, if a meter is programmable, a security password shall be applied to prevent unauthorized access to the meter and unauthorized modifications of meter data and program.

II.B.3	Meter Security – Data

Electrical meters or metering devices should have the capacity of supporting password or other protection means to restrict access to information contained therein. Passwords should be controlled by following generally accepted practices, similar to the protection afforded MDMA. Meter manufacturer should be consulted on extending the degree of protection offered by a particular metering device.

II.C.	Site verification

Visually inspect all meter sites for the following conditions:

II.C.1.	DA Metering Verification

II.C.1.1 Check for proof of DA meter certification or meter types that were  installed prior to 1/1/98 and grandfathered.

II.C.1.2 Verify for correct customer and customer account (records versus meters) including billing constant, meter number, accuracy test results, customer information, address, etc.

II.C.1.3 Verify for correct meter for  service characteristics (voltage, form, etc.).

II.C.2.	DA Communication Verification:

II.C.2.1.Verify for correct phone or other communication devices and connections if remote read

II.C.2.2.Verify for successful communication handshakes and data retrieval if remote read (This can be done by another person at a remote location, and data accuracy is not verified at this time).

II.C.2.3.Verify for successful meter reading if manual read.

II.C.3.	Transformer rated meter sites:

II.C.3.1.Billing Constant: Compare between records versus sites (CT’s/PT’s ratios)

II.C.3.2.Improper Wiring: Shorted current by-pass links, reverse current secondary wired, unmatched voltage and current circuits, pinched or rubbed secondary wires near panel hinges.

II.C.4.	Pole mounted meter sites

II.C.4.1.Cutouts: Open cutouts, blown triple link fuses.

II.C.4.2.Grounding: Grounding electrode conductors and connections shall not be broken at any point between the service equipment  enclosure and the ground rods, or other approved grounding electrode.

II.C.5.	Pad-mounted meter sites:

(to be developed?)

II.C.5.1.Metering: Unusual metering locations, such as current transformer metering installed on a UDC’s pad-mounted transformer, will require ESPs to consult with the UDC for their policy regarding who can perform metering work at these locations.

II.C.6.	Grounding:

PG&E, SCE, and SDG&E have three phase services with ground connection on one of the phases.  In situations where A, B, or C, phase is not grounded and there is a voltage reading at or near zero volts on any phase and reading above zero volts on any other phases, report the hazard to the UDC immediately for emergency corrections and contact the customer or customer’s representative to inform them of the hazardous conditions.  If it is unclear whether a phase is intentionally grounded, contact the local UDC to clarify the configuration of the service.  Additionally, take an extreme caution on primary (above 600 V), 480 V phase to phase or 277 V phase to ground service.

II.c.7.	Clock Load:

Calculate and record customer's load at time of arrival. Changes below submitted by SDG&E

II.C.8.	Task #8: Ground Fault Protection 	The purpose is to ensure that the technicians, while engaged in testing or inspecting a customer’s three phase, 4W wye metering installation, do not cause an unscheduled interruption of the service.

II.C.8.1. National Electric Code:  The National Code, Article 230-95, states that ground-fault protection of equipment shall be provided for solidly grounded wye electrical services of more than 150 volts to ground, but not exceeding 600 volts phase-to-phase for each service disconnecting means rated 1000 amperes or more.  This protection is mandatory on all new 1000 ampere 277/480 volt services, with two exceptions; however, some customers may have installed GFP on lower voltage/amperage of a 4-wire wye service.

II.C.8.2. General:  	The proper operation of some ground-fault detection systems requires a single ground point on the customer’s neutral.  The code requires the customer to establish a ground connection between the neutral, the grounding electrode conductor, the equipment grounding conductor and the service equipment enclosure(s).

II.C.8.3. Precautions:

II.C.8.3.1.  There have been occasions where an unscheduled interruption of the customer’s service while testing or inspecting a metering installation equipped with ground-fault protection occurred.  One of the most unpredictable protection devices found in operation is the GTE-Sylvania Zinsco Model GTS-3 relay.  An SCR within the relay could be triggered by transients generated simply by opening or closing the potential switch.

II.C.8.3.2. On panels with a Zinsco GRS-3 relay, the technician is to contact the customer and request that an authorized representative be present to witness the test/inspection procedure or render the ground-fault relay inoperative.

II.D.	Meter Installation

###### II.D.1	 Verify Address

###### II.D.1.1	Notify customer of activity

###### II.D.2	Site Safety

II.D.2.1	Look or and identify electrical and physical hazards that may be present at the site. Hazards shall be corrected immediately.

II.D.2.2	Inspect for unsafe conditions at the customer’s premises. If unsafe conditions exit, take necessary action to correct.

II.D.3		Personal Safety

II.D.3.1	Long sleeves of  natural fabric shall be worn when exposed to energized equipment. Appropriate fire retardant clothing shall be worn.

II.D.3.2	Appropriate style gloves for work being performed

II.D.3.3	Safety shoes rated for electrical hazard protection

II.D.3.4	Jewelry shall not  be worn where there is danger of electrical contact.

II.D.3.5	Safety glasses shall be worn when exposed to energized equipment.

###### II.D.4	Self Contained Meters

###### II.D.4.1	Read meter

II.D.4.2	Verify meter information: form, voltage, meter number

###### II.D.4.3	 For meters with no bypass, the load shall be disconnected before replacing the meter

II.D.4.4	For meters with a bypass, the meter shall be bypassed and de-energized, if possible, before replacing the meter.

II.D.4.5	Open test block cover

II.D.4.6	Verify voltage

II.D.4.7	Verify 0 Volts between line and load side of test blocks

II.D.4.8	Install test-by-pass jumper

II.D.4.9	Open center bolts on test block

II.D.4.10	Remove meter

II.D.4.11	Install new meter

II.D.4.12	Use approved locking device

II.D.4.13	Close center bolts on test blocks

II.D.4.14	Remove jumpers

II.D.4.15	Reseal test block cover

II.D.4.16	Take initial meter read

II.D.5	Transformer Rated Meters (CT Meter)

###### II.D.4.1	Read meter

II.D.4.2	Verify meter information: form, voltage, constant, meter number

###### II.D.4.3	Verify if meter is supplying customer with pulses (ie isolation relay)

II.D.4.4	Open test switch cover and verify voltage at the test switch.

II.D.4.5	Open CT compartment and verify ratio of CT’s against meter constant

II.D.4.6	Verify wiring from CT compartment to test switch

II.D.4.7	Verify wiring from test switch to meter socket

II.D.4.8	Install test-by-pass jumper

II.D.4.9	Remove meter

II.D.4.10	Install new meter

II.D.4.11	Use approved locking device

II.D.4.12	Close voltage switches on test switch

II.D.4.13	Verify meter is programmed

II.D.4.14	Closed current switches and verify rotation

II.D.4.15	Re-seal CT compartment and test swithc

II.D.4.16	Take initial meter read

II.E.	TESTING AND CALIBRation

The following are requirements that specify which situation a specific testing task will be applied and which traceable standards for testing equipment will be applied:

II.E.1 Pre-installation: Task #1 applies.

II.E.2 Upon installation: Tasks #3 and #7 apply.

II.E.3 Post installation, in service: All tasks #1 through #7 apply.

II.E.4 Traceable standards for testing equipment: Use NIST standards to accurately check and calibrate all test standards as specified in Section II.E.9 below.

II.E.1. 	Matrix of Meter Testing Requirements

|  |  | TASK |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| C O D E | Type of Meters/Registers | 1 Voltage Test | 2 Light & Full Load Test | 3 Demand Test | 4 Register Verification | 5 Phase Angle Test | 6 Separate Element Test | 7 Burden Test | Possible Other Types Í | COMMENTS | C O D E |
| (a) | Self-Contained kWh Meters | X | X |  |  |  | X |  | (g), (j) | Mechanical Meter | (a) |
| (b) | Transformer-Rated kWh Meters | X | X |  |  |  | X | X | (g), (j) | Mechanical Meter | (b) |
| (c) | Hybrid Meters | X | X | X | X |  | X |  | (i), (j) |  | (c) |
| (d) | Solid State Meters | X | X | X | X |  |  |  | (g), (i), (j) |  | (d) |
| (e) | Transformer-Rated kVARh Meters | X | X |  |  | X | X | X | (j) | Mechanical Meter | (e) |
| (f) | Multi-Quadrant Meters | X | X | Œ | X | Ž | X | X | (g), (j) |  | (f) |
| (g) | Solid State Recorders | X |  | X |  |  |  |  |  |  | (g) |
| (h) | Mechanical Registers |  |  | Œ |  |  |  |  | (g), (j) |  | (h) |
| (i) | Electronic Registers |  |  | Œ |  |  |  |  | (g), (j) |  | (i) |
| (j) | Pulse Devices |  |  | X |  |  |  |  |  |  | (j) |
| (k) | Self-Contained Network Meters | X | Ž |  |  |  | Ž |  | (g), (j) |  | (k) |

Œ Performed if demand is present.   Energy Consumption Investigation (ECI) is necessary.  Ž Performed when deemed necessary or requested by customers.

 The alphabetical codes in the “Possible Other Types” column refer to the “Code” column on this matrix and indicate that additional tests must be performed

as required if the other types exist at the sites.

II.E.2. 	Task #1: Voltage Test

On all services, measure the secondary voltage, with an approved volt meter,  between the line phases and line to ground even if it is an ungrounded service and record all voltage readings on the test tag.  All nominal voltages have an allowable tolerance of ±5%.

II.E.2.a 	 Secondary Distribution Voltages: 	Normal rating of 120 Vac.

Table II.E.2.a-1: Nominal Voltages and allowable limits on Secondary

| Nominal Voltage (Volt) | Maximum (Volt) | Minimum (Volt) |
| --- | --- | --- |
| 120 | 126 | 114 |
| 208 | 218 | 198 |
| 240 | 252 | 228 |
| 277 | 291 | 263 |
| 480 | 504 | 456 |

Table II.E.2.a-2: Service Voltages and allowable limits on Secondary

| Service Voltage (Volt) | Measured Voltage (Volt) | Maximum (Volt) | Minimum (Volt) |
| --- | --- | --- | --- |
| 120/240V 3w 1ø | 120V Phase to Ground 240V Phase to Phase | 126 252 | 114 228 |
| 120/208V 3w 1ø | 120V Phase to Ground 208V Phase to Phase | 126 218 | 114 198 |
| 120/208V 4w 3ø | 120V Phase to Ground 208V Phase to Phase | 126 218 | 114 198 |
| 120/240V 4w 3ø | 120V Phase to Ground 208V Phase to Ground 240V Phase to Phase | 126 218 252 | 114 198 228 |
| 277/480V 4w 3ø | 277V Phase to Ground 480V Phase to Phase | 291 504 | 263 456 |
| 240V 3w 3ø | 240V Phase to Phase | 252 | 228 |
| 480V 3w 3ø | 480V Phase to Phase | 504 | 456 |

II.E.2.a 	 Primary Distribution and Transmission Voltages: These voltages have secondary voltage rating of 115 Vac or 120 Vac.  The voltage transformer primary may be connected either wye or delta.

Table II.E.2.b-1: Primary and Transmission Voltages with their secondary voltages and ratios

| Possible System L-L Voltage (Volt) | VT Primary Voltage (Volt) | Secondary Rating (Volt) | Ratio |
| --- | --- | --- | --- |
| 2,400 or 4,200 | 2,400 | 120 | 20:1 |
| 4,200 or 7,200 | 4,200 | 120 | 35:1 |
| 7,200 or 12,000 | 7,200 | 120 | 60:1 |
| 12,000 or 20,125 | 12,000 | 120 | 100:1 |
| 17,200 | 18,000 | 120 | 150:1 |
| 20,125 or 34,500 | 20,125 | 115/67.08 | 175/300:1 |
| 60,000 | 34,500 | 115/69 | 300/500:1 |
| 69,000 | 40,250 | 115/67.08 | 350/600:1 |
| 115,000 | 69,000 | 115/69 | 600/1000:1 |
| 138,000 | 80,500 | 115/69 | 700:1 |
| 230,000 | 138,000 | 115/69 | 1,200/2000:1 |
| 500,000 | 287,500 | 115/69 | 2,500/4200:1 |

II.E.3. 	Task #2: Light Load & Full Load Test

Light load is 10% of name plate or test Amp rating, and full load is 100% of name plate or test Amp rating.  The light and full load test is performed at 100% power factor to verify the accuracy of the meter by comparing its test results with a Standard Meter of known traceable accuracy.

II.E.1 No Load or Creep Test (for mechanical & hybrid meters only): Test meters will be energized with no connected load, and the disk observed for rotation.  A minimum amount of creep is acceptable if the rotation stops when an anti-creep hole reaches the meter stator.

II.E.2 Accuracy test: Single phase and polyphase meters are to be tested with potential coils connected in parallel and the current coils connected in series.  The minimum duration of the test will be 1 disk revolution for light load and 10 disk revolutions for full load.  For solid state meters, calculated pseudo revolutions will be used.

II.E.3 Adjustments: Meters found within the limits required by the local UDC need not be adjusted.

II.E.4 Reporting: Correction factors for light load and full load tests will be recorded as the meter accuracy results. Example: A 0.5% fast and slow meter:

Correction Factor		Accuracy

Fast			0.995				+0.5%

Slow			1.005				-0.5%.

II.E.5 UDC Notification: Meter Agent must notify the UDC’s upon finding a defective meter that affects billing.

II.E.6 Single Phase Services: This task is not required for single phase services.

II.E.4. 	Task #3: Demand Test

This test procedure can be done on site or at a testing facility.

II.E.4.a.	Mechanical Demand Meters

Test for the accuracy of the demand registers by checking the marked register ratio and time interval as follows:

II.E.4.a.1 Advancing Mechanism: Visually inspect the pusher arm and gears for worn out parts.

II.E.4.a.2 Clutch: Check that the pusher arm returns to zero at the end of interval when the clutch releases it.  Verify that this is a smooth operation and the pusher arm it returns to the stop position.

II.E.4.a.3 Timing Motor: Check that the timing motor is operating.  If the motor is not operating the demand reading will most likely be off scale.

II.E.4.a.4 Time Interval and Demand Test: Test the time interval to insure that it is as marked on the register name plate by timing the motor gear and clocking an interval, or performing a demand test.  The demand test is performed by minimally applying full load current for 125 disk revolutions on 15 minute demand meters and for 250 disk revolutions on 30 minute demand meters.

II.E.4.a.5 Demand Mechanism: Check that the demand reset returns the pointer to zero on a reset action and that the pointer will advance to full scale.

II.E.4.a.6 Reporting: Correction factor for the demand test will be recorded as the meter accuracy result.  Example: A 0.5% fast and slow meter:

Correction Factor		Accuracy

Fast			0.995				+0.5%

Slow			1.005				-0.5%.

II.E.4.b.	Solid State Meters and Electronic Registers

II.E.4.b.1 Below is a procedure for a demand test on a solid state meter or an electronic register:

II.E.4.b.2 Place the meter register in the TEST MODE.

II.E.4.b.3 Press reset button to clear all test registers and start new demand interval.

II.E.4.b.4 Apply full load current for 25 disk revolutions as a minimum.

II.E.4.b.5 Scroll the register display to show present kW demand.  If the kW value is in pulses, calculate the actual kW value.

II.E.4.b.5 Calculate and record the correction factor by comparing the meter kW value with the kW in the test standard.

II.E.4.b.6 Return the meter to the NORMAL MODE.

II.E.5. 	Task #4: Register Verification

II.E.5.a.	Mechanical Register

Visually inspect and verify that the register is correct for the watt-hour meter, and  that the register constant, gear ratio, and register ratio are correct for the register.

II.E.5.a.1 Gear mechanism: Check that the gears are clean, and check the proper engagement between gears and between the first gear and the disk shaft.

II.E.5.a.2 Mechanical register: Check that the register ratio is the same as marked.  The register ratio (Rr) is determined by counting the number of revolutions required of the first gear to cause the first dial pointer to make one complete revolution.

II.E.5.b.	Electronic Register

Because electronic registers are different for each type and manufacturer, manufacturer’s manual should be referred to for specific procedures for these registers.   Below is a typical procedure for verifying electronic registers after they are programmed with proper parameters:

II.E.5.b.1 Check all numerical segments and identifiers on the meter display.

II.E.5.b.2 Check the meter is scrolling properly through all registers.

II.E.5.b.3 Check the function of the registers by disconnecting and then restoring power on the meter.  The meter should resume normal display operations and reading after this power outage.

II.E.5.b.4 Verify the programming parameters are correct.

II.E.5.b.5 Check the register memory and load profile data memory to verify that data is being stored.

II.E.6. 	Task #5: Phase Angle Test

II.E.6.1.

Phase measurements depend on:

II.E.6.1.1  phase rotation unique to the utility,

II.E.6.1.2 load,

II.E.6.1.3  delta vs. wye connected meter application.

Refer to specific utility requirements regarding phase angle measurements before proceeding with this test.

II.E.6.2

II.E.6.3. Power Factor Calculation: Calculate the load on the (real power)KWH and the (reactive power)RKVAH meters and the power factor for the site.  This power factor is used as a cross check for the measured phase angles.

II.E.6.4. Current Measurement: Measure each phase current and record it accordingly.

II.E.6.5 Phase Angle Measurement: Use phase angle meter to measure each phase angle and record it accordingly.

II.E.6.6 Phase Angle Plot: After measuring all voltages, currents and phase angles, plot a phase angle test and cross check with the calculated power factor.

II.E.7. 	Task #6: Separate Element Test

Check individual elements of transformer rated and self contained meters for proper disk rotation or registration by performing the following:

II.E.7.1 Testing: Energize with the appropriate phase potentials and place current on individual elements, and check for forward rotation or positive registration

II.E.7.2 Correct phasing: Check that the proper potential coil and current coil are wired correctly in the meter.  If the meter is installed correctly on the socket, the meter disk will rotate forward.

II.E.7.3 No forward rotation: If an element has no rotation check for no load current and for open potential coil with a magnet or an ohmmeter.

II.E.7.4 Note: Phase angle relationships may cause reverse rotation in cases where there is a poor power factor. This may occur when one line current has been shorted. (changes from LADWP).  This will only occur on three wire three phase metered service sites.

II.E.7.5 Single Phase Services: This task is not required for single phase services.

II.E.8. 	Task #7: Burden Test

This test procedure can be done on site or at a testing facility.  Check the operating conditions of current transformers by performing the following:

II.E.8.1 Procedure: Put built-in burdens of a multi-range Ammeter in series with the secondary of the test current transformers (CT) to obtain the Amp readings.  These Amp readings should have the same deflection.

II.E.8.2 Possible Problems: If a CT has a reading significantly different from the others, check for shorted turns or other problems, such as short circuited primary turns, short circuited secondary turns, high resistance connections in the secondary circuit, short circuited secondary wiring, or grounding of normally ungrounded wire.

# II.E.9. 	Requirements on Test Standards

The following are the requirements for maintenance and calibration of test standards which are used for testing the accuracy of electric meters in the field or in the shop:

II.E.9.1	Out-of-calibration: A test standard that is found to have accuracy greater than +/-0.5% of a reference test standard.

II.E.9.2	 Reference test standard: A test standard that is accurately calibrated according to NIST requirements and used as a accuracy reference in the lab or meter shop by comparing its accuracy against that of other test standards.

II.E.9.3	Routine accuracy check requirements: Each test function of a test standard shall be checked and compared with a reference standard monthly.  If a test standard used in testing meters has a result of three consecutive meters tested out of the CPUC-required accuracy limits, this test standard shall be checked against the reference standard.

II.E.9.4 	Once a test standard is checked and found out-of-calibration, it shall be calibrated according to NIST requirements, and meters that were tested by this test standard since the last routine check or calibration shall be retested with an accurately-calibrated test standard according to the following.

II.E.9.4.1	 If it is determined the number of meters tested by this portable standard since the last calibration were:

II.E.9.4.1.1	3 – 20 All meter will be re-tested for accuracy.

II.E.9.4.1.2	20–100 A random sample of 20% or 20 meters, which ever is less, will be re-tested for accuracy.

II.E.9.4.1.3	101–200 A random sample of 10% or 20 meters, which ever is less, will be re-tested for accuracy.

II.E.9.4.1.4 	201–1000 A random sample of 10% or 50 meters, which ever is less, will be re-tested for accuracy.

II.E.9.4.2 	If at least 95% of the first sample pass the meter test for accuracy, all the meters will be considered accurate.

II.E.9.4.3 	If less than 95% of the first sample pass the meter test for accuracy, a second sample of the same size will be tested.

II.E.9.4.4 	If a second sample is drawn, 95% of the meters must pass the meter test standard for accuracy.

II.E.9.4.5 	If the second sample fails the meter test standard for accuracy all the meters calibrated by the portable standard will be tested and re-calibrated for accuracy.

II.F.	Maintenance

II.F.1.	Maintenance Schedule

Electric meters used in Direct Access will be maintained, as a minimum, according to the following meter maintenance and testing schedule:

Table G1-1; Minimum meter maintenance and testing schedule

| Maintenance and Testing Frequency | Customer Maintenance and Testing Criteria |
| --- | --- |
| One Year Interval | Customer’s annual usage of 2 million kWh or higher |
| Two Year Interval | Customer’s annual usage between 720,000 and 2 million kWh |
| Statistical Sample | Non residential customer’s annual usage less than 720,000 kWh |
| Residential Meters | No formal sampling plan. Tests done upon request and removal, where applicable |
| Direct Current (DC) Meters | No formal sampling plan. Tests done upon request and removal, where applicable |

II.F.2.	Maintenance upon request

Testing and maintenance is required upon a reasonable request by a customer, ESP, or UDC.

II.F.3.	Statistical Sampling Requirements

The ANSI Z1.4 or Z1.9 Standards will be used as the statistical sampling requirements for testing meters.

II.F.4.	Criteria for required corrections

The criteria for required corrections include the trigger criteria and action criteria which shall be at 4% and 10% Acceptable Quality Levels (AQL), respectively.  When the trigger criteria are not met during a scheduled maintenance and testing, further testing and checking shall be performed to monitor the accuracy performance of meter groups until the action criteria are no longer met.  Upon the violation of the action criteria, the corrective actions shall be taken to correct the problems.  Such corrective actions may lead to removals of certain inaccurate and aging meter groups.

II.F.5.	Troubleshooting and corrective actions

Troubleshooting shall include all applicable tasks as indicated above and shall be performed to verify the meter operation and accuracy as required.  If the troubleshooting indicates hazard or out-of limit accuracy condition at a meter site, the responsible party shall take corrective actions within 48 hours of this finding.

II.G.	PT/CT secondary wiring and maintenance requirements

Upon routine testing and maintenance as required in Section II.F., secondary wiring shall be verified for correct wiring and no sign of tampering, and PT’s and CT’s shall be checked for normal operating conditions.  If abnormal conditions exist, ESPs and UDCs serving the customers shall be notified within 24 hours.

II.H.	DEMARCATION POINT OF METER WORK

As part of these meter worker qualifications, a clear scope of metering work must be established.  Decision No.97-10-087, Appendix A: Direct Access Tariff, Section H(1)(b) states

“Potential and current transformers shall be considered part of the distribution system and shall remain the responsibility of the UDC.”

Accordingly, and pursuant to this decision, all instrument transformers, test switches and associated wiring up to the meter socket shall remain the responsibility of the UDCs.

II.I. MDMA Communications (submitted by ABB)

The MSP will notify the MDMA of a problem with the meter requiring the meter data to be adjusted, including the cause and correction factor.