III.	METER Maintenance

III.1.	Maintenance Schedule

Electric meters used in Direct Access will be maintained, as a minimum, according to the following meter maintenance and testing schedule:

Table III.1-1; Minimum meter maintenance and testing schedule

| Maintenance and Testing Frequency | Customer Maintenance and Testing Criteria |
| --- | --- |
| One Year Interval | Customer’s annual usage of 2 million kWh or higher |
| Two Year Interval | Customer’s annual usage between 720,000 and 2 million kWh |
| Statistical Sample | Non residential customer’s annual usage less than 720,000 kWh |
| Residential Meters | Either formal sampling plan or tests done upon request and removal, where applicable |
| Direct Current (DC) Meters | Either formal sampling plan or tests done upon request and removal, where applicable |

III.2.	Maintenance upon request

Testing and maintenance is required upon a reasonable request by a customer, ESP, or UDC.

III.3.	Statistical Sampling Requirements

The ANSI Z1.4 or Z1.9 Standards will be used as the statistical sampling requirements for testing meters.

III.4.	Criteria for required corrections  (This section still under review – input expected based on review of AQL ranges from PG&E)

The criteria for required corrections include the trigger criteria and action criteria which shall be at 4% and 10% Acceptable Quality Levels (AQL), respectively.  When the trigger criteria are not met during a scheduled maintenance and testing, further testing and checking shall be performed to monitor the accuracy performance of meter groups until the action criteria are no longer met.  Upon the violation of the action criteria, the corrective actions shall be taken to correct the problems.  Such corrective actions may lead to removals of certain inaccurate and aging meter groups.

III.5.	Troubleshooting and corrective actions

Troubleshooting shall include all applicable tasks as indicated above and shall be performed to verify the meter operation and accuracy as required.  If the troubleshooting indicates hazard or out-of limit accuracy condition at a meter site, the responsible party shall take corrective actions within 48 hours of this finding.

#### III.6 	MDMA Communications

The MSP will notify the MDMA of a problem with the meter requiring the meter data to be adjusted, including the cause and correction factor.

- METER SYSTEM TESTING

(PG&E and Pacificorp  will provide a revised introduction that describes the functions of  meter system testing for which the recommendations here are a guideline.)

In general, there are seven tasks involved in testing an electric meter system.  The metering system, defined for use in Section IV.E. only, is 1) the meter itself, or 2) the meter and its attached equipment or module(s).  These tasks are described in Appendix 1, Guideline for Meter Testing, which meter workers may use as a guideline for their meter work.

The following requirements shall are applied when testing  is performed on meters, sockets, and metering systems:

IV.1. Meter Socket: Voltage test (Task #1 in Appendix 1) shall be performed on meter sockets or service connections to verify correct voltages.  When a phase shifting transformer is in use, a phase angle test  (Task #5 in Appendix 1) shall be required.

IV.2. Metering System: The following tests are required to be performed on a metering system:

IV.2.1	Light and full load test  or Customer Load Test (Task #2 in Appendix 1).

IV.2.2.	Demand test (Task #3 in Appendix 1).

IV.2.3	Register verification (Task #4 in Appendix 1).

IV.2.4	Separate element check (Task #6 in Appendix 1).

IV.3. Notification: Meter worker shall notify the UDCs, ESPs and MDMAs upon finding a defective meter that affects billing.

IV.4. Matrix of Meter Testing

The following matrix indicates which meter technology certain testing task can be applied and serves as a guide in meter testing. Some of the specific tasks may not apply to newer meters:

|  |  | TASK |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| C O D E | Type of Meters/Registers | 1 Voltage Test | 2 Light & Full Load or Customer Test | 3 Demand Test | 4 Register Verification | 5 Phase Angle Test | 6 Separate Element Check | 7 Burden Test | Possible Other Types Í | COMMENTS | C O D E |
| (a) | Self-Contained kWh Meters | X | X |  |  |  |  |  | (g), (j) | Mechanical Meter | (a) |
| (b) | Transformer-Rated kWh Meters | X | X |  |  |  | X | X | (g), (j) | Mechanical Meter | (b) |
| (c) | Hybrid Meters | X | X | X | X |  | X |  | (i), (j) |  | (c) |
| (d) | Solid State Meters | X | X | X | X |  | X |  | (g), (i), (j) |  | (d) |
| (e) | Transformer-Rated kVARh Meters | X | X |  |  | X | X | X | (j) | Mechanical Meter | (e) |
| (f) | Multi-Quadrant Meters | X | X | Œ | X | Ž | X | X | (g), (j) |  | (f) |
| (g) | Solid State Recorders | X |  | X |  |  |  |  |  |  | (g) |
| (h) | Mechanical Registers |  |  | Œ |  |  |  |  | (g), (j) |  | (h) |
| (i) | Electronic Registers |  |  | Œ |  |  |  |  | (g), (j) |  | (i) |
| (j) | Pulse Devices |  |  | X |  |  |  |  |  |  | (j) |
| (k) | Self-Contained Network Meters | X | Ž |  |  |  | Ž |  | (g), (j) |  | (k) |

Œ Performed if demand is present.   Energy Consumption Investigation (ECI) is necessary.  Ž Performed when deemed necessary or requested by customers.

 The alphabetical codes in the “Possible Other Types” column refer to the “Code” column on this matrix and indicate that additional tests must be performed

as required if the other types exist at the sites.

IV.4.1. Task #1: Voltage Test

On all services, measure the secondary voltage, with an approved volt meter,  between the line phases and line to ground even if it is an ungrounded service and record all voltage readings on the test tag.  All nominal voltages have an allowable tolerance of ±5%.

IV.4.1.a. 	 Secondary Distribution Voltages: 	Normal rating of 120 Vac.

Table IV.4.1.a-1: Nominal Voltages and allowable limits on Secondary

| Nominal Voltage (Volt) | Maximum (Volt) | Minimum (Volt) |
| --- | --- | --- |
| 120 | 126 | 114 |
| 208 | 218 | 198 |
| 240 | 252 | 228 |
| 277 | 291 | 263 |
| 480 | 504 | 456 |

Table IV.4.1.a-2: Service Voltages and allowable limits on Secondary

| Service Voltage (Volt) | Measured Voltage (Volt) | Maximum (Volt) | Minimum (Volt) |
| --- | --- | --- | --- |
| 120/240V 3w 1ø | 120V Phase to Ground 240V Phase to Phase | 126 252 | 114 228 |
| 120/208V 3w 1ø | 120V Phase to Ground 208V Phase to Phase | 126 218 | 114 198 |
| 120/208V 4w 3ø | 120V Phase to Ground 208V Phase to Phase | 126 218 | 114 198 |
| 120/240V 4w 3ø | 120V Phase to Ground 208V Phase to Ground 240V Phase to Phase | 126 218 252 | 114 198 228 |
| 277/480V 4w 3ø | 277V Phase to Ground 480V Phase to Phase | 291 504 | 263 456 |
| 240V 3w 3ø | 240V Phase to Phase | 252 | 228 |
| 480V 3w 3ø | 480V Phase to Phase | 504 | 456 |

IV.4.1.b. 	 Primary Distribution and Transmission Voltages: These voltages have secondary voltage rating of 115 Vac or 120 Vac.  The voltage transformer primary may be connected either wye or delta.

Table IV.4.1.b-1: Primary and Transmission Voltages with their secondary voltages and ratios

| Possible System L-L Voltage (Volt) | VT Primary Voltage (Volt) | Secondary Rating (Volt) | Ratio |
| --- | --- | --- | --- |
| 2,400 or 4,200 | 2,400 | 120 | 20:1 |
| 4,200 or 7,200 | 4,200 | 120 | 35:1 |
| 7,200 or 12,000 | 7,200 | 120 | 60:1 |
| 12,000 or 20,125 | 12,000 | 120 | 100:1 |
| 17,200 | 18,000 | 120 | 150:1 |
| 20,125 or 34,500 | 20,125 | 115/67.08 | 175/300:1 |
| 60,000 | 34,500 | 115/69 | 300/500:1 |
| 69,000 | 40,250 | 115/67.08 | 350/600:1 |
| 115,000 | 69,000 | 115/69 | 600/1000:1 |
| 138,000 | 80,500 | 115/69 | 700:1 |
| 230,000 | 138,000 | 115/69 | 1,200/2000:1 |
| 500,000 | 287,500 | 115/69 | 2,500/4200:1 |

IV.4.2. 	Task #2: Light Load & Full Load Test  or Customer Test

Light load is 10% of test Amp rating, and full load is 100% of or test Amp rating.  The light and full load test is performed at 100% power factor to verify the accuracy of the meter by comparing its test results with a Standard Meter of known traceable accuracy.

IV.4.2.1. No Load or Creep Test (for mechanical & hybrid meters only): Test meters will be energized with no connected load, and the disk observed for rotation.  A minimum amount of creep is acceptable if the rotation stops when an anti-creep hole reaches the meter stator.

IV.4.2.2. Accuracy test: Single phase and polyphase meters are to be tested with potential coils connected in parallel and the current coils connected in series; or on site test can be performed using customer load.  The minimum duration of the test will be 1 disk revolution for light load and 10 disk revolutions for full load.  For solid state meters, calculated pseudo revolutions will be used.

IV.4.2.3. Adjustments: Meters found within the limits required by the local UDC need not be adjusted.

IV.4.2.4. Reporting: Correction factors for light load and full load tests will be recorded as the meter accuracy results as specified in ANSI C.12.1 (1995)

For example, for a 0.5% fast and slow meter:

Correction Factor		Accuracy

Fast			0.995				+0.5%

Slow			1.005				-0.5%.

IV.4.3. 	Task #3: Demand Test

IV.4.3.1.	Mechanical Demand Meters

Test for the accuracy of the demand registers by checking the marked register ratio and time interval as follows:

IV.4.3.1.1. Advancing Mechanism: Visually inspect the pusher arm and gears for worn out parts.

IV.4.3.1.2. Clutch: Check that the pusher arm returns to zero at the end of interval when the clutch releases it.  Verify that this is a smooth operation and the pusher arm it returns to the stop position.

IV.4.3.1.3. Timing Motor: Check that the timing motor is operating.  If the motor is not operating the demand reading will most likely be off scale.

IV.4.3.1.4. Time Interval and Demand Test: Test the time interval to insure that it is as marked on the register name plate by timing the motor gear and clocking an interval (ie. 900 seconds for 15 minutes), or performing a demand test.  The demand test is performed by minimally applying full load current for 125 disk revolutions on 15 minute demand meters and for 250 disk revolutions on 30 minute demand meters.

IV.4.3.1.5 Demand Mechanism: Check that the demand reset returns the pointer to zero on a reset action and that the pointer will advance to full scale.

IV.4.3.1.6. Reporting: Correction factor for the demand test will be recorded as the meter accuracy result.

For example for a 0.5% fast and slow meter:

Correction Factor		Accuracy

Fast			0.995				+0.5%

Slow			1.005				-0.5%.

IV.4.3.2.	Solid State Meters and Electronic Registers

Below is a procedure for a demand test on a solid state meter or an electronic register:

IV.4.3.2.1. Place the meter register in the TEST MODE.

IV.4.3.2.2. Press reset button to clear all test registers and start new demand interval.

IV.4.3.2.3. Apply full load current for 25 disk revolutions as a minimum.

IV.4.3.2.4. Scroll the register display to show present kW demand.  If the kW value is in pulses, calculate the actual kW value.

IV.4.3.2.5. Calculate and record the correction factor by comparing the meter kW value with the kW in the test standard.

IV.4.3.2.6. Return the meter to the NORMAL MODE.

IV.4.4. 	Task #4: Register Verification

IV.4.4.1.	Mechanical Register

Visually inspect and verify that the register is correct for the watt-hour meter, and  that the register constant, gear ratio, and register ratio are correct for the register.

IV.4.4.1.1. Gear mechanism: Check that the gears are clean, and check the proper engagement between gears and between the first gear and the disk shaft.

IV.4.4.1.2. Mechanical register: Check that the register ratio is the same as marked.  The register ratio (Rr) is determined by counting the number of revolutions required of the first gear to cause the first dial pointer to make one complete revolution.

IV.4.4.2.	Electronic Register

Because electronic registers are different for each type and manufacturer, manufacturer’s manual should be referred to for specific procedures for these registers.   Below is a typical procedure for verifying electronic registers after they are programmed with proper parameters:

IV.4.4.2.1. Check all numerical segments and identifiers on the meter display.

IV.4.4.2.2. Check the meter is scrolling properly through all registers.

IV.4.4.2.3. Check the function of the registers by disconnecting and then restoring power on the meter.  The meter should resume normal display operations and reading after this power outage.

IV.4.4.2.4. Verify the programming parameters are correct.

IV.4.4.2.5. Check the register memory and load profile data memory to verify that data is being stored.

IV.4.5. 	Task #5: Phase Angle Test

The phase angle measurements depend on a unique ABC phase rotation applied at a UDC, customer load and service wiring (delta vs. wye and three wires vs. four wires).  The following procedures will be followed when performing a phase angle test:

IV.4.5.1.  Utility phase rotation requirements: Refer to specific UDC requirements regarding ABC phase rotation prior to performing this test, and check for correct wiring on a reactive metering site and proper phase shift on each phase circuit.

IV.4.5.2.  Phase shifting transformer (reactive-former) voltage: Measure the secondary voltage to insure voltage is applied to the potential coil in the kVarhr meter.  If the phase voltage is not correct, check for the following possible errors: 1) incorrect wiring on the phase shifting transformers, and 2) incorrect service voltage.

IV.4.5.3. Power Factor Calculation: Calculate the load on the (real power)kWhr and the (reactive power) kVarhr meters and the power factor for the site.  This power factor is used as a cross check for the measured phase angles.

IV.4.5.4. Current Measurement: Measure each phase current and record it accordingly.

IV.4.5.5 Phase Angle Measurement: Use phase angle meter to measure each phase angle and record it accordingly.

IV.4.5.6 Phase Angle Plot: After measuring all voltages, currents and phase angles, plot a phase angle test and cross check with the calculated power factor.

IV.4.6. 	Task #6: Separate Element Check

Check individual elements of transformer rated and self contained meters for proper disk rotation or registration by performing the following:

IV.4.6.1. Testing: Energize with the appropriate phase potentials and place current on individual elements, and check for forward rotation or positive registration

IV.4.6.2. Correct phasing: Check that the proper potential coil and current coil are wired correctly in the meter.  If the meter is installed correctly on the socket, the meter disk will rotate forward.

IV.4.6.3. No forward rotation: If an element has no rotation check for no load current and for open potential coil with a magnet or an ohmmeter.

IV.4.6.4. Cautions: Phase angle relationships may cause reverse rotation in cases where there is a poor power factor, possible un-metered load and/or short circuit.  This will only occur on three wire three phase metered service sites.

IV.4.7. 	Task #7: Burden Test

Check the operating conditions of current transformers by performing the following:

IV.4.7.1. Procedure: Put built-in burdens of a multi-range Ammeter in series with the secondary of the test current transformers (CT) to obtain the Amp readings.  These Amp readings should have the same deflection.

IV.4.7.2. Possible Problems: If a CT has a reading significantly different from the others, check for shorted turns or other problems, such as short circuited primary turns, short circuited secondary turns, high resistance connections in the secondary circuit, short circuited secondary wiring, or grounding of normally ungrounded wire.

- METER CALIBRATION

#### V.1. 	Calibration and Maintenance of Watt-hour Standards

The following are the requirements for maintenance and calibration of Watt-hour standards which are used for testing the accuracy of electric meters in the field or in the shop:

V.1.1 	Out-of-calibration

A test standard that is found to have accuracy greater than +/-0.1% of a reference test standard.

V.1.2 	Basic Reference test standard

A standard that is certified according to NIST requirements and used as an accuracy reference in the laboratory or meter shop.

# V.1.3.	Portable Standard

A standard that is used to certify the accuracy of meters in the field.

V.1.4.	Routine accuracy check requirements

Each test function of a test standard shall be checked and compared with a reference standard monthly.  If a test standard used in testing meters has a result of three consecutive meters tested out of the CPUC-required accuracy limits, this test standard shall be checked against the reference standard.

V.1.	Meter Retesting.

Once a test standard is checked and found out-of-calibration, it shall be calibrated according to NIST requirements, and meters that were tested by this test standard since the last routine check or calibration shall be retested with an accurately-calibrated test standard according to the following.

V.1.1. 	 If it is determined the number of meters tested by this portable standard since the last calibration were:

V.1.1.1	3 – 20 meters:  All meter will be re-tested for accuracy.

V.1.1.2	20–100 meters: A random sample of 20% or 20 meters, which ever is less, will be re-tested for accuracy.

V.1.1.3	101–200 meters: A random sample of 10% or 20 meters, which ever is less, will be re-tested for accuracy.

V.1.1.4 	201–1000  meters: A random sample of 10% or 50 meters, which ever is less, will be re-tested for accuracy.

V.1.2  If at least 95% of the first sample pass the meter test for accuracy, all the meters will be considered accurate.

V.1.3  If less than 95% of the first sample pass the meter test for accuracy, a second sample of the same size will be tested.

V.1.4  If a second sample is drawn, 95% of the meters must pass the meter test standard for accuracy.

V.1.5  If the second sample fails the meter test standard for accuracy all the meters calibrated by the portable standard will be tested and re-calibrated for accuracy.