I. 	MSP/METER WORKER QUALIFICATIONS

There are five key elements to these MSP meter worker qualifications: (1) Due to varying levels of complexity, safety issues and training required, there are five classes of meter equipment, meter service activities and ultimately meter worker qualifications that are involved in direct access metering work; (2) Since many workers are already performing metering work in California, meter workers who are presently performing work for a Utility Distribution Company (UDC) or certified MSP will be considered qualified and certified for the level of work for which they have been trained and are performing as of [insert the date adopted]; (3) UDCs and certified MSPs will identify which of the five meter worker classes each of their employees performing meter work are qualified for; (4) The new meter worker certification requirements shall apply uniformly to any direct access meter worker in the employ of any UDC or MSP (ESP as MSP) after [insert the date adopted]; (5) procedures are also adopted to ensure meter workers remain qualified over time.

UDCs and MSPs will issue appropriate identification to each of their meter workers or employees who perform direct access meter work and will ensure that their workers carry this identification while performing meter work.  This identification will indicate the worker’s employer and the class of meter work which the worker is qualified to perform.  If an ESP, UDC or customer subcontracts its meter work to an MSP, the subcontracting entity must ensure that the MSP issues each meter worker or employee such identification.

All meter workers performing meter services must meet the requirements as outlined in this Section and exercise due care for the tasks performed.  Out-of-socket meter accuracy testing, meter diagnostics and sub-metering work requirements are not addressed by this report.  Also, utilization of the meter’s built-in diagnostics are not considered part of meter accuracy testing.

I.A. 	Meter Worker Skill, Safety And Qualification Requirements

The following are the descriptions and requirements of the five meter worker classes:

I.A.1.	CLASS 1

I.A.1.1.	Metering Types and Voltages

This class includes single-phase, socket-based meters, 300 volts phase-to-phase maximum and does not include transformer rated meters.  Communication wiring must be outside of energized meter panels.

I.A.1.2. Work to be Performed

Class 1 Meter Workers can install, remove and replace single-phase, 120/240 volt or 120/208 volt, self-contained meters in standard socket based residential-type metering equipment.  Connections of communication conductors must be outside the energized meter panels.

I.A.1.3.	Essential Technical Skills

I.A.1.3.1. Understanding of single phase electrical metering.

I.A.1.3.2. Understanding of electric distribution safety procedures.

I.A.1.3.3. Ability to identify energy diversion or tampering related to this class of meter work.

I.A.1.3.4. Ability to install and remove damaged and undamaged meters.

I.A.1.3.5. Understanding of the meter panel and socket layout for the metering conditions related to this class of meter work.

I.A.1.3.6. Ability to read meters used in this class.

I.A.1.3.7. Ability to properly use tools appropriate to the work in this class.

I.A.1.3.8. Ability to connect meter communications external to the meter panel.

I.A.1.3.9. Ability to initialize meter communication modules - not utilizing Type 2 optical ports and meter configuration software.

I.A.1.4.	Worker Safety and Safety Equipment

I.A.1.4.1. Job performance in accordance with employing MSP's procedures and safety rules.

I.A.1.4.2. Knowledge of hazards of electricity and ability to perform work to avoid electrical hazards.

I.A.1.4.3. Ability to comply with CAL OSHA requirements.

I.A.1.4.4. On-site use of personal protective equipment.

I.A.1.5.	Worker Qualification: How Essential Technical and Safety Skills Are Determined

I.A.1.5.1. UDCs and MSPs must develop and implement a program to train their workers to perform Class 1 meter work safely and properly.

I.A.1.5.2. Employees must be certified by their employers, based on the use of that program.

I.A.1.5.3. MSP's Class 1 meter work training program will be reviewed and certified by a Meter Worker Certification Organization (MWCO).

I.A.2.	CLASS 2

I.A.2.1.	Metering Types and Voltages

This class includes all meters and skills required for Class 1.  Class 2 includes up to 600 V, single-phase and poly-phase, safety socket and standard socket based meters and does not include transformer rated meters.  Communication wiring may be behind the panel, and work can be in and around energized circuits.

##### I.A.2.2.	Work to be Performed

Class 2 Meter Workers can install, remove and replace all meters consistent with the above.  Class 2 Meter Workers must understand the operating characteristics of test-bypass facilities and test blocks and may operate test-bypass facilities, but may not install, alter, maintain or replace wiring between the meter and test block.  On panels without test-bypass facilities, single-phase and poly-phase meters will not be removed or installed without first disconnecting the customer load.  Communication wiring may be installed inside the panel, and work can be performed in and around energized circuits.

I.A.2.3.	Essential Technical Skills

I.A.2.3.1. Cumulative including all skills for Class 1.

I.A.2.3.2. Additionally, possess skills related to meter voltages and meter forms used in Class 2.

I.A.2.3.3. Ability to perform phase rotation assessments.

I.A.2.3.4. Ability to operate test-bypass facilities or test blocks in a self-contained safety socket.

I.A.2.3.5. Ability to perform work required to route communication wiring to accommodate meter communications.

I.A.2.4.	Worker Safety and Safety Equipment

I.A.2.4.1. Cumulative including all skills and safety knowledge for Class 1

I.A.2.4.2. Electrical safety knowledge and work skills appropriate for single-phase and three-phase metering up to 600V phase-to-phase, including the ability to identify and refer to a Class 5 meter installer services above 600V phase-to-phase prior to performing work in the service equipment.

I.A.2.5.	Worker Qualification: How Essential Technical and Safety Skills Are Determined

I.A.2.5.1. UDCs and MSPs must develop and implement a program to train their workers to perform Class 2 meter work safely and properly.

I.A.2.5.2. Employees must be certified by their employers, based on the use of that program.

I.A.2.5.3. MSP's Class 2 meter work training program will be reviewed and certified by a Meter Worker Certification Organization (MWCO).

I.A.2.6.	Experience Requirements

Minimum experience requirements that must be demonstrated prior to qualification for individuals wanting to become a Class 2 Meter Worker as specified below:

I.A.2.6.1.	If entry level experience of any employee is that of a journeyman level electrician, journeyman level electric metering worker, or journeyman level line worker (e.g., lineman, troubleman), then upon successful completion of the MSP training program the worker may be certified as a Class 2 Meter Worker; or

I.A.2.6.2.	After six (6) months as a Class 1 Meter Worker which includes three (3) months “OJT” working alongside a Class 2 or higher Meter Worker and upon successful completion of the MSP training program a worker may be certified as a Class 2 Meter Worker; or

I.A.2.6.3.	If an employee has a two or four year degree in a related subject, then after four (4) months of Class 2 Meter Worker training which includes three (3) months "OJT" working alongside a Class 2 or higher Meter Worker and upon successful completion of the MSP training program a worker may be certified as a Class 2 Meter Worker; or

I.A.2.6.4.	After six (6) months of Class 2 Meter Worker training which includes three (3) months “OJT” working alongside a Class 2 or higher Meter Worker and upon successful completion of the MSP training program a worker may be certified as a Class 2 Meter Worker.

I.A.3.	CLASS 3

I.A.3.1.	Metering Types and Voltages

This class includes all meter types in Classes 1 and 2.  Class 3 work includes up to 600V, A base, K base and transformer rated meters with internal diagnostics.  Communication wiring may be behind the panel, and work can be in and around energized circuits.

I.A.3.2.	Work to be Performed

In addition to Class 1 and 2, Meter Work, Class 3 Meter Workers can install, remove and replace all meters consistent with the above including transformer-rated meters with internal diagnostics (if detected, problems with test switches, panel wiring or metering transformers and metering transformer wiring will be corrected by Class 5 meter worker).  Class 3 Meter Workers may operate test switches, but may not install, alter, maintain or replace wiring between the meter, test switch, test block and associated equipment.

I.A.3.3.	Essential Technical Skills

I.A.3.3.1. Cumulative of Classes 1 and 2.

I.A.3.3.2. Additionally, possess skills related to meter voltages and meter forms used in Class 3.

I.A.3.3.3. Ability to understand the operating characteristics of metering transformers and how to operate test switches.

I.A.3.3.4. Ability to understand, interpret, identify and take appropriate actions based upon built-in diagnostics of solid state meters.

I.A.3.4.	Worker Safety and Safety Equipment

I.A.3.4.1. Cumulative of all safety skills for Classes 1 and 2.

I.A.3.4.2. Ability to understand, interpret and take appropriate action based on built in diagnostics of solid state meters.

I.A.3.4.3. Ability to work with transformer rated meters and operate test switches and test blocks.

I.A.3.5.	Worker Qualification: How Essential Technical and Safety Skills Are Determined

I.A.3.5.1.	UDCs and MSPs must develop and implement a program to train their workers to perform Class 3 meter work safely and properly.

I.A.3.5.2.	Employees must be certified by their employers, based on the use of that program.

I.A.3.5.3.	MSP's Class 3 meter work training program will be reviewed and certified by a Meter Worker Certification Organization (MWCO).

I.A.3.6.	Experience Requirements

Minimum experience requirements that must be demonstrated prior to qualification for individuals wanting to become a Class 3 Meter Worker as specified below:

I.A.3.6.1.	If entry level experience of any employee is that of a journeyman level electrician, journeyman level electric metering worker, or journeyman level line worker (e.g., lineman, troubleman), then upon successful completion of the MSP training program the worker may be certified as a Class 3 Meter Worker; or

I.A.3.6.2.	After 6 months as a Class 2 Meter Worker which includes 3 months "OJT" working alongside a Class 3 or higher Meter Worker and upon successful completion of the MSP training program a worker may be certified as a Class 3 Meter Worker; or

I.A.3.6.3.	If an employee has a two or four year degree in a related subject, then after five (6) months of Class 3 Meter Worker training which includes four (4) months "OJT" working alongside a Class 3 or higher Meter Worker and upon successful completion of the MSP training program a worker may be certified as a Class 3 Meter Worker; or

I.A.3.6.4.	After eight (8) months of Class 3 Meter Worker training which includes four (4) months “OJT” working alongside a Class 3 or higher Meter Worker and upon successful completion of the MSP training program a worker may be certified as a Class 3 Meter Worker.

I.A.4.	Class 4(A)

## I.A.4.1. Metering Types and Voltages

This class includes all meter types in Classes 1, 2 and 3.

I.A.4.2.	Work to be Performed

In addition to Class 1, 2, and 3 Meter Work, Class 4(A) Meter Workers can install, remove and replace all meters consistent with the above.  May perform in-field meter accuracy tests, calibrations and perform all types of meter maintenance and troubleshooting on single phase meters up to 300 Volts.  Programs and verifies internal programs and software in solid state meters.

### I.A.4.3.	Essential Technical Skills

I.A.4.3.1. Cumulative of Classes 1, 2 and 3.

I.A.4.3.2. Ability to perform work on metering switchboards.

I.A.4.3.3. Ability to perform calibration, repair, retrofit, troubleshooting, data collection of electric meters within the Class and install, maintain and program advanced metering technologies, including TOU, interval data, real time pricing, remote meter communication, and load control devices.

I.A.4.4.	Worker Safety and Safety Equipment

I.A.4.4.1. Cumulative of all safety skills for Classes 1, 2, and 3.

I.A.4.4.2.	Ability to conform processes to additional electricity hazards and complexities associated with metering switchboards, testing meters and maintaining meters in service equipment up to 300 volts.

I.A.4.5.  Worker Qualification: How Essential Technical and Safety Skills Are Determined

I.A.4.5.1. UDCs and MSPs may develop and implement a program to train workers to perform Class 4(A) meter work safely and properly (prior to and after testing).

I.A.4.5.2. All workers must be certified by the test process outlined below.

I.A.4.6.	Testing Process and Qualifications

I.A.4.6.1.	All individuals seeking to perform DA meter services for a UDC or MSP as a Class 4(A) Meter Worker must successfully pass written and practical (demonstrative) tests.

I.A.4.6.2. 	Prerequisites for taking the written and practical tests include a showing of previous work experience that includes at least one of the following:

I.A.4.6.2.1. Employment as a journeyman electrician, journeyman metering employee, or journey line worker (e.g., lineman, troubleman); or

I.A.4.6.2.2. Minimum of one year experience as a Class 3 Meter Worker; or

I.A.4.6.2.3. Minimum of one year experience in utility revenue meter installation, testing and maintenance

I.A.4.7.	Testing and Re-Certification Requirements

I.A.4.7.1. Once an individual takes and passes the Class 4(A) Meter Worker Test, they are qualified to perform that class of DA meter work anywhere in California and need not re-take the test to perform work in each UDC service area.

I.A.4.7.2. If after being qualified a Class 4(A) meter worker the individual does not perform metering work in California for 3 years or more, re-certification will be required by written and practical testing prior to performing that class of meter work.

I.A.4.8. Continuing Education

As part of a Class 4(A) Meter Worker’s ongoing ability to remain qualified, the individual must participate in at least ten (10) hours annually of the MSP’s training program regarding standards of practice and safety related issues.

I.A.5.	Class 4(B)

## I.A.5.1.	Metering Types and Voltages

This class includes all meter types in Classes 1, 2 and 3.  Class 4(B) work includes all metering up to 600V, including transformer rated meters with primary and secondary voltages less than 600V.  Communication wiring may be behind the panel, and work can be in and around energized circuits.

I.A.5.2.	Work to be Performed

In addition to Class 1, 2, and 3 Meter Work, Class 4(B) Meter Workers can install, remove and replace all meters consistent with the above.  May perform in-field meter accuracy tests, calibrations and perform all types of meter maintenance and troubleshooting on all meters.  Programs and verifies internal programs and software in solid state meters.

### I.A.5.3.	Essential Technical Skills

I.A.5.3.1. Cumulative of Classes 1, 2, 3 and 4(A).

I.A.5.3.2. Ability to perform work on metering switchboards.

I.A.5.3.3. Ability to perform calibration, repair, retrofit, troubleshooting, data collection of electric meters and install, maintain and program advanced metering technologies, including TOU, interval data, real time pricing, remote meter communication, and load control devices.

I.A.5.4.	Worker Safety and Safety Equipment

I.A.5.4.1. Cumulative of all safety skills for Classes 1, 2, 3 and 4(A).

I.A.5.4.2. Ability to conform processes to additional electricity hazards and complexities associated with metering switchboards, testing meters and maintaining meters in service equipment up to 600 volts.

I.A.5.5.	Worker Qualification: How Essential Technical and Safety Skills Are Determined

I.A.5.5.1. UDCs and MSPs may develop and implement a program to train workers to perform Class 4(B) meter work safely and properly (prior to and after testing).

I.A.5.5.2. All workers must be certified by the test process outlined below.

I.A.5.6.	Testing Process and Qualifications

I.A.5.6.1.	All individuals seeking to perform DA meter services for a UDC or MSP as a Class 4(B) Meter Worker must successfully pass written and practical (demonstrative) tests.

I.A.5.6.2. 	Prerequisites for taking the written and practical tests include a showing of previous work experience that includes at least one of the following:

I.A.5.6.2.1. Employment as a journeyman electrician, journeyman metering employee, or journey line worker (e.g., lineman, troubleman); or

I.A.5.6.2.2. Minimum of one year experience as a Class 3 Meter Worker; or

I.A.5.6.2.3. Minimum of one year experience in utility revenue meter installation, testing and maintenance

I.A.5.7.	Testing and Re-Certification Requirements

I.A.5.7.1. Once an individual takes and passes the Class 4(B) Meter Worker Test, they are qualified to perform that class of DA meter work anywhere in California and need not re-take the test to perform work in each UDC service area.

I.A.5.7.2. If after being qualified a class 4(B) meter worker the individual does not perform metering work in California for 3 years or more, re-certification will be required by written and practical testing prior to performing that class of meter work.

I.A.5.8.	Continuing Education

As part of a Class 4(B) Meter Worker’s ongoing ability to remain qualified, the individual must participate in at least ten (10) hours annually of the MSP’s training program regarding standards of practice and safety related issues.

I.A.6.	Class 5

## I.A.6.1.	Metering Types and Voltages

This class includes all meter types in Classes 1, 2, 3 and 4.  Class 5 meter work includes all metering above 600 V, including metering transformers, associated devices such as isolation relays and switches, and wiring between these transformers, associated devices and meters. Communication wiring may be behind the panel, and work can be in and around energized circuits.

# I.A.6.2.	Work to be Performed

In addition to Class 1, 2, 3, and 4 meter work, Class 5 Meter Workers can install, remove and replace all meters consistent with the above including transformer-rated meters.  Replace high-voltage fuses.  Perform in-field meter accuracy tests, calibrations and perform all types of meter maintenance and troubleshooting on all meters.  Inspect wiring and instrument transformer ratios utilizing various apparatus as necessary.

### I.A.6.3.	Essential Technical Skills

I.A.6.3.1. Cumulative of Classes 1, 2, 3 and 4.

I.A.6.3.2. Ability to identify primary metering equipment and characteristics of service equipment rated at voltages above 600 volts.

I.A.6.3.3. Broad knowledge and familiarity of electrical distribution systems above 600 volts and operating characteristics.

I.A.6.3.4. Ability to identify UDC service voltages and Electrical Service Requirements.

I.A.6.3.5. Broad Knowledge and familiarity of State of California General Orders.

I.A.6.4.	Worker Safety and Safety Equipment

I.A.6.4.1. Cumulative of all safety skills for Classes 1, 2, 3 and 4.

I.A.6.4.2. Ability to conform processes to additional electricity hazards and complexities associated with metering switchboards, testing meters and maintaining meters in service equipment above 600 volts.

I.A.6.4.3.	Meet the State of California requirements for a “Qualified Electrical Worker” to perform work on metering systems with instrument transformer at voltages above 600 volts.

I.A.6.4.4.	Must have a minimum of two years of training and experience with high-voltage (above 600 volts) equipment and circuits.

I.A.6.5.	Worker Qualification: How Essential Technical and Safety Skills Are Determined

I.A.6.5.1. MSP may develop and implement a program to train employees to perform Class 5 meter work safely and to comply with CAL OSHA requirements (prior to and after testing).

I.A.6.5.2. All workers will be certified by the test process outlined below.

### I.A.6.6.	Testing Process and Qualifications

I.A.6.6.1. 	All individuals seeking to perform DA meter services for a UDC or MSP as a class 5 Meter Worker must successfully pass written and practical skills (demonstrative) tests.

I.A.6.6.2. 	Prerequisites for taking the written and practical skills tests including verification of previous work experience that includes at least one of the following:

I.A.6.6.2.1. Recognized employment as a journeyman electrician (above 600 volts) with qualified electrical worker status.

I.A.6.6.2.2. Recognized employment as a journeyman metering employee with two years minimum working experience on metering equipment above 600 volts.

I.A.6.6.2.3. Journeyman Line Worker, Apparatus Technician or similar position that has completed a recognized apprenticeship program that meets minimum CAL OSHA requirements.

I.A.6.6.2.4. Knowledge of CAL OSHA requirements and completed required training for a Class 4(B) Meter Worker.

### I.A.6.7.	Testing and Re-Certification Requirements

I.A.6.7.1. Once an individual takes and passes the Class 5 written and practical skills test, and has completed the requirements for performing work on energized metering equipment above 600 volts, that individual is qualified to perform work anywhere in California and need not re-take the written test to perform work in each UDC service area.

I.A.6.7.2. If after being qualified as a Class 5 Meter Worker the individual does not perform Class 5 metering work in California for 3 years or more, re-certification will be required by written and practical skills testing prior to performing Class 5 meter work.

I.A.6.8. Continuing Education

As part of a Class 5 Meter Worker’s ongoing ability to remain qualified, the individual must participate in at least ten (10) hours annually of the MSP’s training program regarding standards of practice and safety related issues.

I.B.	CERTIFICATION OF METER SERVICE PROVIDER (MSP)

An entity may be certified as an MSP and obtain a permanent certification number by following the CPUC-approved process described in the CPUC Decision 97-12-048 dated December 3, 1997.  In brief, this process is as follows: (1) In accordance with this decision the UDCs are declared to be a Certified Meter Service Provider.  (2) Other entities wishing to be certified shall submit a written request including the requested documents to the CPUC in accordance with the decision (See Appendix MI-5: MSP Registration Packet).  (3) After CPUC review and approval, provisional certification will be granted.  (4) UDCs and MSPs will assign only qualified and certified metering workers to the DA metering under their control, as defined in the CPUC Decision D97-10-087, Appendix A, Section (H) of Metering Services and pursuant to this decision on the PSWG permanent standards.  (5) UDCs and MSPs will schedule up to 50 joint meetings to ensure that essential work procedures, hand-offs and processes are clearly understood and in place.  (6) Upon successful completion of steps 2-5, an MSP may apply to the CPUC for Permanent Certification.

###### I.B.1.	Implementation

UDCs and MSPs (or ESPs as MSPs) shall implement the CPUC-approved MSP entity certification process as specified in CPUC Decision D97-12-048 or other CPUC Decisions thereafter.  Since the worker certification process is changing, the purpose of the 50 joint meetings between UDCs and MSPs must also change.  The meets will no longer be UDCs’ evaluations of the MSPs workers’ technical qualifications.  Instead, these meets shall confirm MSP’s CPUC process awareness, orientation for UDC or local issues (if any), and verifications of the processes used by UDCs and MSPs to install meters, perform needed documentation and effectively hand off all essential data. As is the case today, once the objectives of the joint meet process have been achieved, the UDCs may waive the remainder of the 50 joint meets.

I.B.1.1 Joint meet check list (Appendix MI-3)

To achieve a consistent application of the Joint Meet process, the parties will use the joint meet check list described as Appendix MI-3.  This form will document the processes used to conduct business,  the MSP meter worker’s knowledge of CPUC requirements, documentation and hand-off processes which may have impacts on UDCs, ESPs and MDMAs and to provide feedback to the MSP accordingly.

I.B.1.2. Joint meet log (Appendix MI-4)

The UDCs and MSPs shall continue to maintain the joint meet log as required by the CPUC Decision D97-12-048.  The attached form (Appendix MI-4) shall be used by all parties.

#### I.C	CERTIFICATION OF METER WORKERS

I.C.1. 	CLASSES 1, 2 AND 3:

MSPs and UDCs may develop and implement a training program to train and certify their individual meter workers in these three meter worker classes.  MSPs and UDCs must ensure that all appropriate meter worker prerequisites are met before a meter worker is certified.  Only MSPs and UDCs that have certified training programs may self certify Class 1, 2 or 3 meter workers based on each respectively certified training program.  Prior to receiving approval to self-certify their workers in these classes, each MSP or UDC shall submit each of the training programs for each of meter worker Classes 1, 2 and 3 that they are not already qualified to perform and for which an MSP or UDC wishes to self-certify its workers.  Within 30 days, or a time frame otherwise agreed to by the [CPUC designated entity] and the applying MSP or UDC, the [CPUC designated entity]shall review and either provide recommendations for changes needed prior to program certification for each class of certification sought or notification of the certifications granted.  Upon certification of each training program, the [CPUC designated entity] will provide a written letter and numbered certificate of such approval to the requesting MSP or UDC.

I.C.2. CLASSES 4(A), 4(B) AND 5:

Meter workers seeking Class 4(A), (B), or 5 certification shall be required to take and pass a test, composed of both written and practical components, to qualify for performing Class 4(A), 4(B), or 5 of meter work, respectively.  Although individual workers may individually prepare and seek certification in these classes, MSPs, UDCs, or other entities may also, at their option, develop and offer classes or training to prepare Class 3, or other workers, for the tests and for Class 4(A), 4(B) or 5 certification.  Individual workers, MSPs or UDCs may schedule certification tests with an [CPUC designated entity].  Work experience or other qualifications required by the definitions of each worker class (in addition to the test itself) must be verified by the MSP or UDC prior to scheduling the test and shall be provided to the MWCO at the time of the workers test.  This will ensure that the MWCO has the information necessary to issue a certification.  After a meter worker has taken and passed the certification test, the [CPUC designated entity] will issue a permanent and numbered certification card to the worker as evidence of certification.

I.C.3.	REQUIREMENTS FOR PREPARING PRACTICAL AND WRITTEN TESTS:

The [CPUC designated entity]  shall develop and prepare a number of different tests for each worker classification.  The tests will be periodically revised and updated to remain up to date with market needs and to ensure testing integrity.  The initial set of test questions shall be developed based on examples described in Appendix MI-2.  Additionally, questions also must be periodically reviewed by various MSP/UDC entities and knowledgeable metering employees to verify questions for their technical validity and assurance of fairness.

I.C.4.	IMPLEMENTATION OF METER WORKER CERTIFICATION REQUIREMENTS:

These California Direct Access (DA) meter worker certification requirements will apply to all workers who are either hired or trained by any entity to perform DA meter services after [insert the date adopted].

I.D. 	Administration of qualification and disqualification process

One new organization will be created to manage the qualification and disqualification process for DA meter workers.  This organization is the Meter Worker Certification Organization (MWCO).  This is a type of organization independent of the existing role of UDCs and MSPs.  There may be as many MWCO companies as determined by the market.  Because these organizations do not exist, and because it will take a period of time for such an organization to emerge and develop, an interim MWCO process will be formed as authorized by the CPUC to function for 6 months or until an MWCO is CPUC-certified and ready to operate, whichever is earlier.  Below are details and a chart describing the process overviews.

I.D.1.  	CERTIFICATION OF METER WORKER CERTIFICATION ORGANIZATION

A new entity shall carry out the functions of certifying both meter worker training processes and individual high skill meter workers.  This entity will be known as a Meter Worker Certification Organization (MWCO).  Specifically, an MWCO will used by the market to review, evaluate and certify the training materials to be used by MSPs and UDCs for Classes 1, 2 and 3 meter workers as well as to develop and offer practical and written tests to certify meter workers in Classes 4(A), 4(B) and 5.  The MWCO will establish reasonable fees for its work.  This organization shall be knowledgeable about the metering services they will certify.  If the MWCO is also a UDC or MSP, it shall not certify its own Class 1, 2, or 3 meter worker training program, nor its own Class 4(A), 4(B), or 5 meter workers.  An entity wishing to be an MWCO shall apply with the CPUC, and the CPUC shall assign a certification number to all approved MWCOs.  MWCO certification shall be accomplished by an entity submitting a written application to the CPUC along with the following information: name of the person or entity; business address and telephone number; name of the person or entity in which a business license is issued, the business license number and expiration date; a description of meter work training experience, materials and facilities that it has or uses to train or qualify meter workers.  In addition to the written application, the MWCO shall arrange a bond in favor of the State of California in the amount of $100,000, or provide the Energy Division with a proof of a general liability insurance that meets the specifications described below:

If a bond is used, it shall be submitted with the written application.  The bond shall be for the benefit of anyone who may be damaged as a result of the MWCO’s actions in connection with the review and certification of Classes 1, 2 and 3 training meter worker programs and testing and certification of Classes 4(A), 4(B) and 5 meter workers.  Should a complaint for damages arising from the MWCO’s actions be filed in civil court, and a claim is made against the bond, a copy of the complaint shall be served by registered or certified mail upon the Commission’s Executive Director.  The bond requirement will ensure that the MWCOs adhere to all applicable provisions governing the review and certification of Classes 1, 2 and 3 meter worker training programs and testing and certification of Classes 4(A), 4(B) and 5 meter workers.  Should an end-use customer suffer damages as a result of the MWCO’s actions, the bond will provide a source of compensation.

If the MWCO elects to provide proof of liability insurance, the insurance shall meet the following specifications: (1) the insurance policy shall be commercial general liability insurance with coverage that, at a minimum, is the same as what is provided for in the Insurance Services Office Commercial General Liability Coverage occurrence form; (2) the policy shall not be less than $1 million for each occurrence for bodily injury, property damage and personal injury, and if the coverage is subject to a general aggregate limit, the aggregate limit shall not be less than $2 million; (3) the policy shall include, as an additional insured, the UDCs and MSPs whose training programs and meter workers the MWCO is certifying; and (4) the liability insurance policy shall include a statement that thirty days’ written notice shall be provided to the Commission, the UDCs and the MSPs before the policy is canceled.  Proof of liability insurance will ensure that the MSP has sufficient insurance coverage to cover any claims that might be brought against the MWCO for metering-certification-related activities.

The MWCO does not exist today, and it will take a period of time for such an organization to be ready to administer the qualification process.  Therefore, an interim MWCO process shall be established.  A small group will establish the interim MWCO process and will consist of one volunteer representative from each entity of UDCs and permanently-certified MSPs.  This group will be formed within 7 calendar days pursuant to this decision and will: 1) Finalize the test contents which will be used to test and certify the Classes 4(A), 4(B) and 5 meter workers; 2) Establish pass/fail criteria for the Classes 4(A), 4(B) and 5 meter workers testing; 3) Identify and assign an entity to administer this testing and certification; 4) ) Identify an interim entity to receive, review, evaluate and certify the Classes 1, 2 and 3 meter worker training programs as well as administer the tests for Classes 4(A), 4(B) and 5 meter workers; and 5) Publish the information on how to submit the training materials for certification and how to apply for meter worker Classes 4(A), 4(B) and 5 testing.

Within 90 days following this decision, these five tasks assigned must be completed and a brief report of what was implemented will be filed with the CPUC and posted on the PSWG web site.

Appendix MI-2: Class 4(A), 4(B) and 5 Meter Workers Certification Tests

Part 1: Written Exam

The written test includes questions which are combination of multiple choices, description and problem solution.  Below is the summary list that can be developed into one or several specific questions for each item:

SAFETY:

- Given a specific condition at a metering site, describe safety procedures that metering personnel need to perform.

- Describe the conditions or procedures, if any, when opening the secondary of CT’s and PT’s.  Why?

- Given customer’s operating load conditions and six voltage reads on both phase-to-phase and phase-to-ground during a field test of a meter, ask for the following:

- Provide preliminary diagnosis of the metering.

- If OK, describe what will happen if an accuracy test is conducted.

- If not OK, what troubleshooting steps & customer information are needed prior to leaving the site.

- Describe safety procedures when disconnecting a meter from CT’s secondary while CT’s primary is carrying load or energized.

- When performing work on or around the meter site, what dictates the safety protection equipment that must be used and when it should be used.

- TECHNICAL METERING:

- List the phase voltages to ground conductors of some specific services.

- Provide a gear ratio of a typical residential meter given stamped register ratio and Kh.

- Define Kh of a watt-hour meter.

- Describe the driving torque component in an induction meter.

- Describe the phase shifting transformer component for reactive metering.

- What are the functions, purpose and procedures for using a phase angle meter.

- How to safely connect voltmeters, ammeters and wattmeters in electrical circuits.

- Relationship between current and voltage in some specific meters at unity PF load.

- Describe various aspects of the 3 wire network service.

- Given a circuit diagram of a meter and service connection and load in amperes, provide one or more of the following types of values: the total load registered by the meter, the voltage drop across the potential coil, the form and number of elements of the meter, etc.

- Using the given base values of Kh, current and voltage, calculate new Kh based on different current and voltage.

- Calculate the light load accuracy or correction factor on a specific self-contained meter, given its Kh and disk revolutions in a specific time period.

- Calculate the kW load and dial multiplier for a specific transformer-rated meter given its current transformer ratio, Kh and disk revolutions in a specific time period.

- Describe if a test result is right or wrong given specific test conditions and result (i.e., in a 2 element meter test, a rotating standard register 2 times the number of revolutions it should, and the meter is properly connected for the test with the potential coils in parallel and current coil in series).

- Calculate disk revolutions given a demand reading on a specific interval and a Kh value.

- Complete a meter jaw configuration for a specific meter and label expected terminal-to-ground voltage reads on each line terminal (jaw).  Will be given a blank circle representing meter base along with meter form, class, voltage, wires, phase and connection.

- Understand detent, describe when it should and should not be used.

- Given a specific meter diagram (connected to a socket with 4,5, or 8 jaws) answer questions on its metering performance and ask for explanations.

- Given customer’s operating load condition and six voltage reads on both phase-to-phase and phase-to-ground during a field test of a meter, ask for the following:

- Provide preliminary diagnosis of the metering.

- If OK, describe what will happen if an accuracy test is conducted.

- If not OK, what troubleshooting steps & customer information are needed prior to leaving the site.

- Given a specific meter and a service, question its metering accuracy on a certain portion of the service load and ask for why it is so (i.e. 3-wire single phase meter on a 3 wire network load: what is the error (if any) and why there is an error on 1) a single phase load, and 2) line to line load.)

- Given a service (phase, wires, voltage and connection) and customer’s kW load demand and phase angle, calculate the load current and show the calculations.

- Calculate power factors of element tests on a 3-wire 3-phase meter, given a meter Kh and disk revolutions in a certain time interval.

- Given a picture of the transformer winding diagram, meter socket diagram and internal wiring between the meter and transformer, provide the meter information: class, volt(s), wire(s), phase(s).

- Given a picture of a complete wiring diagram for a complicated metering installation which includes a service connection diagram, CT’s, 10-pole test switch and 13-jaw meter diagram; also given a specific meter, customer service main ampacity, color-coded wires and all detailed information on service (i.e. volt, wire, connection, phase, etc.); questions on the following: 1) CT’s primary/secondary rating, 2) billing constant, 3) which wires are connected to what (switch, transformers, hot legs, power legs, etc.), 4) phase to neutral voltage readings, 5) phase to phase voltage readings, 6) which wire(s) should be connected to ground, and 7) Describe if anything is wrong with the installation.

- Given a specific service connection along with CT’s, a specific meter diagram, the option of either a 6-pole test switch or a 10-pole test switch, each of which has numbered and connected wires, complete the following: 1) select the test switch, 2) identify potential and current wires, and common wires for CT’s, 3) provide billing constant, and 4) identify ground wire(s).

- Given an internal diagram of a single phase meter with the meter jaws numbered, perform a single phase test the meter, describe step-by-step how to place the current coils in series and potential coils in parallel, and accordingly label the input and output of each jumper placed in the circuit diagram (Assume that test switch is not needed and meter is not energized).

- Part 2: Practical Exam

- The practical exam is prepared to include two parts: 1) the description of the metering work that a test candidate needs to hands-on perform, and 2) the check list of all necessary steps (including safety) that the test observer needs to record for scoring.  All necessary test equipment, tools, meters and associated devices will be provided to the candidate for performing meter testing.  Below is the sample questions on some metering work:

- Set up the wiring for the test standards and phantom load box for a field meter test.

- Perform test on a specific meter on a 200 ampere meter panel that has a test bypass facility.

- Perform meter removal, installation and test of specific CT rated meters.  Describe any abnormalities, if observed, and corrections to be applied.

- Appendix MI-3: Joint Meet Check List

- STATE OF CALIFORNIA

- CPUC JOINT MEET CHECKLIST

- Customer Name:_____________________________	Joint Meet Date:_________________________________

- Site Address: ______________________________	UDC Acc't #: ___________________________________

- __________________________________________	UDC  Meter # (Out Meter): ________________________

- MSP Name:________________________________   	MSP Meter # (New meter):  ________________________

- MSP Certification #: _________________________ 	ESP: __________________________________________

- This Joint Meet Checklist shall be used by all UDC representatives pursuant to the CPUC Decision on permanent standards.

- Note: If the MSP employee is working unsafely, the UDC representative will state that the work is not being performed safely, request the individual to stop the unsafe action and to continue only when the work can be done safely. If the individual refuses to stop the unsafe work, the reviewer will document the unsafe work, leave the site and report said action to the meter worker’s MSP for its action.

- CPUC Requirements Met

- Safety

- All safety rules must be followed to ensure the worker, customer and public’s safety:	Yes____  No____

- Worker Qualifications

- Worker shows proof of certification for meter work to be performed: …………………	Yes____  No____

- Meter certified and approved: ……………….…	Meter Type____________________	Yes____  No____

- Meter site operations:

- Meter checked and working properly:………….…………….………………….…	Yes____  No____

- Communications operational and data accessible for down load: …..……….……. 	Yes____  No____

- Documentation and Hand-off Process

- Out and in reads recorded: ……………………………………………………………..	Yes____  No____

- All information reported and data recorded correctly: …………………………………	Yes____  No____

- Conclusion

- Pass____			Fail____ (If failed, describe in comments section below)

Comments:___________________________________________________________________________________ ____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

MSP Installer : __________________________________ UDC Reviewer: _______________________________

(Print)	 (Print)

Signed, MSP: ___________________________________ Signed, UDC:_________________________________

Appendix MI-4

STATE OF CALIFORNIA

CPUC JOINT MEET LOG

|  | MSP: _______________ Cert. No.: _________ |  |  |  | UDC: ______________________________ |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ESP Name | MSP Employee Name | Joint Meet Date | ESP/MSP Meter Number | Type of Meter Work | Reviewer Name | Account No. | Meter Number | Meter Site Address | Meter Site City | Comments or Notes |

Appendix MI - 5: MSP Registration Packet

APPLICATION  FOR  PROVISIONAL

METER  SERVICE  AND INSTALLATION  CERTIFICATION

Provisional MSP No.  _______________________________

Date Granted  ________________

***PLEASE PRINT OR TYPE***

# Name of Person or Entity:

- ____________________________________________________

# Current Business Address:

- _________________________________________________________________________________________

- Street Address

- _________________________________________________________________________________________
                         City                                                State                                             Zip Code

# Current Business Telephone Number:   ______________________________________________

# CALIFORNIA ELECTRICAL CONTRACTOR’S LICENSE: (attach a copy to this Application)

- Name of the person or entity in which the

- General Electrical Contractor’s License is issued:

- License #						  Expiration Date:

# BOND OR GENERAL LIABILITY INSURANCE REQUIREMENT:  the Applicant shall arrange a bond in favor of the State of California in the amount of $100,000 or provide the Engorge Division with a proof that the Applicant has general liability insurance meeting the specifications described in the CPUC Decision D98-05-044.  The bond or proof of insurance shall be submitted with this application.

# Please attach a detailed description of  all of the applicant’s electric meter installation, maintenance, repair and removal experience, including Meter Worker Classes as specified in the CPUC Decision [insert the Decision No.]

# Please attach a detailed description of the applicant’s training and experience regarding electrical safety.

# Please attach a detailed description of the educational and training requirements (or programs) in electrical work and electrical safety that have been certified according the CPUC-approved certification process and that the applicant will implement to certify and require of its employees before they are allowed to install, maintain, repair, or remove electrical meters or metering devices.  However, these educational and training requirements (or programs) will not be required if the Applicant employs only meter workers who have already been certified according to the CPUC-approved meter worker qualification process.

# By submitting this Application, the Applicant shall comply with any and all of the CPUC-approved requirements for Meter Service Provider, meter installation and maintenance work, applications of the approved ANSI Standards on electric meters or metering devices, CAL OSHA, and applicable laws, rules and regulations in California.

DECLARATION

I, (print name and title)   ____________________________________________________ declare
under the penalty of perjury that the above statements are true and correct.

Dated this ____________day of __________________ 19______ at ____________________________

(day)                          (month)                (year)              (place of execution)

Signature:__________________________________________________________

Note:  if this Application is verified outside California, the verification must be made by an affidavit sworn or affirmed before a notary public.

Return this Application with required attachments to:

MSP Certification Unit

California Public Utilities Commission

505 Van Ness Avenue

San Francisco, CA  94102

INCOMPLETE APPLICATIONS

CANNOT BE PROCESSED

FOR CPUC USE ONLY

Application Processed

By:    ________________________

Date:  ________________________

Sub-metering work performed in California is presently covered by California Business and Professions Codes #12531 (Meaning and Scope of Terms) and 12532 (Engaging in Business as Device Repairman or Maintaining Device Repair Service Unlawful without Registration).