- METER INSTALLATION

This section proposes the minimum requirements for installation, maintenance and testing for meters and metering equipment used in direct access. Decision No.97-10-087, Appendix A: Direct Access Tariff, Section H(1)(b) states “Potential and current transformers shall be considered part of the distribution system and shall remain the responsibility of the UDC.” Accordingly, and pursuant to this decision, all instrument transformers, test switches and associated wiring up to the meter socket shall remain the responsibility of the UDCs.  However, reconnecting existing wires to a replacement of the existing meter sockets, A-base socket adapters, or A-base meters may be performed by either UDCs or MSPs.

II.1.	Safety (customer life support, public, etc.)

For safety reasons, the following requirements must be completed prior to performing any meter work on site and visual observations must continually apply as the meter work progresses.  Meter work includes, but not limited to, meter installation, meter replacement, maintenance, programming and testing.  Visually inspect all meter sites for the following conditions:

II.1.1.	Customer Life Support

II.1.1.1.	If a customer premise has a life support device or equipment and UDCs require a life-support sealing hardware or sticker, such sealing hardware or sticker shall be installed on meter covers, meter panels, test switches and/or metering transformer panel sections where deemed necessary to prevent service interruption during process of metering work.  Specifically, the life-support sealing hardware and/or sticker is required to be used in areas of which UDCs currently require and use such life support device.  As of the date that the PSWG report submitted to the CPUC, PG&E uses only life support stickers and SDG&E uses both life support seals and stickers.   However, SCE does not use either of those.

II.1.1.2.	If such life-support sticker (in PG&E & SDG&E service territory) or sealing hardware (in SDG&E) is found on customer meter covers, meter panels, test switches and/or metering transformer panel sections, meter workers shall be cautious in performing meter work and not interrupting electric service to the customer premise.  If service will be unavoidably interrupted for any meter work, the meter worker shall notify the customer and obtain customer’s consent prior to performing work.

II.1.2.	Electrical Hazards:

II.1.2.1.	Various Hazardous Conditions:

The hazardous condition may include exposed wiring, damaged sockets (loose or burnt wiring or jaws), auto-bypass devices (load jaws still hot when meter removed), loose or missing screws (i.e., in bypass area), missing panels, loose or broken service insulators, service wires in bad condition/order, missing meter, improper grounding conditions, fused neutral conductor of a 2 wire or 3 wire single phase service, defective service switch/disconnect, new installations which fail to conform with the UDC’s electric service requirements, etc.

II.1.2.2.	600 Volt Auto Valve (or Meter Protector, or Transformer Surge Arrestor)

II.1.2.2.1.	Auto valves are also called meter protectors or transformer surge arrestors and may be found on 480 volt overhead meter installations, both self-contained and transformer-rated.  Functional in the field the auto valve may be safely removed from the meter installation.  If MSP meter workers find that these valves cannot be safely removed, they must notify UDCs to schedule for removals.

II.A2.2.2.	The auto valve can be identified as a round or square metal can the size of a large human fist.  The auto valve is mounted through a knock out and secured with a net on the inside of the can.  There will be 3 black wires and 1 white wire.  The 3 black wires are electrically connected to each of the 3 phase wires on the service.  The white wire is connected to an earth ground.  The auto valve is attached to the socket side of the test block or test switches.  By de-energizing the socket, the wires from the auto valve can be removed. Ensure that the hole left in the service equipment is properly closed and sealed for weather.

II.1.2.3.  480 Sticker:

A 480 V sticker shall be placed on the meter panel near the meter when meter worker is at the meter site.

II.1.3.	Physical Hazards:

II.1.3.1.	Tripping hazards (slippery or uneven surfaces), debris or materials stored in the working space, overhead hazards (stored materials or workers above meters).

II.1.3.2.	Environmental hazards: Chemical, caustic, hearing, biological, etc.

II.1.3.3.	Inadequate or unsafe access

II.1.3.4.	Meter Mounting: loose meter mounting, undue vibration, inability to securely seal metering, unleveled meter.

II.1.4.	Customer Premises:

Unsafe conditions of customer-owned stairs, railings, platforms, etc.

II.1.5.	Vermin:

Watch out for insects, snakes, and rodents when opening doors or removing panels.

II.2.	Meter Security and Accessibility

The following requirements must be completed when performing any meter work on site and visual observations must continually apply as the meter work progresses.  Visually inspect all meter sites for the following conditions:

II.2.1.	Infraction and Evidence of Tampering/Energy Diversion:

II.2.1.1. Meter Installation

II.2.1.1.1. Awareness of significant connected loads compared to a customer's monthly energy consumption.

II.2.1.1.2.	Irregularities in the service conductor's insulation ("skinned" insulation, newly-taped sections of conductors, burned or pitted service conductors, etc.)

II.2.1.1.3.	Unauthorized connection in overhead service entrance, on line side of meter, or metering transformers, or in unsealed underground pull sections or pull cans.

II.2.1.1.4.	Unauthorized seals, and unsealed or improperly sealed conditions on line side raceways, test block compartments, test switch covers, and meter sealing rings.

II.2.1.1.5.	Suspicious wiring.

II.2.1.1.6. Jumpers across current leads at bottom of test switch unsealed.

II.2.1.1.7. Meter Coil Jumpered - Check and correct if the neutral service wire is found connected through the series coil of the meter and there are grounds on the load circuits that act as a jumper.

II.2.1.1.8. Lock Fuse Jumpered - Check for lock fuse jumper and perform a regular meter test.  Jumper will be left as found, and this condition will be reported on the test report.

II.2.1.1.9. Blown (or loosened) fuse in one leg of a 3-wire old sequence service.

II.2.1.1.10. Rate infractions in meter program/register.

II.2.1.2.	Meter Cover

An unusually clean cover, small holes in the cover, burn marks on or near the cover, visible fingerprints inside the cover, etc.

II.2.1.3.  KWH Register

KWH dial pointer alignment, register mesh and register gears.

II.2.1.4.  Meter Disk

Disk alignment to magnets, irregularity of disk rotation, foreign objects or materials on disk/bearing, scratches or wear marks on the disk.

II.2.1.5.  Test Blocks

Damaged wiring between test block and meter, unusual marks, scratches or burns on test blocks, defective test blocks, etc.

II.2.1.6.  Meter Base

Unusual marks and mushroomed screw slots on potential links; broken meter seals; unusual wear or scratches, burn or pit marks on meter stabs/blades/terminals; etc.

II.2.1.7.  Meter Socket

Unusual wear or scratches, burnt or pit marks, irregular meter socket voltages, circuit bypass jumper, etc.

II.2.1.8.  Hidden "Service Riser" Taps and Un-metered Circuits Utilizing Relay Devices:

Unusual noises that could indicate a relay opening when the meter is removed from the socket.

II.2.2.	Meter Security

The following are the requirements for securing physical meters, panels, programmable meters and data:

II.2.2.1.	Physical Meters and Panels

Meters and meter panels shall be secured with appropriate locking devices such as seals, locking rings.

II.2.2.1.	Programmable Meters and Data

Only programmable meters capable of supporting password or other protection means to restrict access to information contained therein shall be used for Direct Access, and a security password shall be applied to prevent unauthorized access to a programmable meter and unauthorized modifications of the meter data and program.  Passwords should be controlled by following generally accepted practices, similar to the protection afforded in MDMA process.  Meter manufacturers should be consulted on extending the degree of protection offered by a particular metering device.

II.3.	Site Verification

Visually inspect all meter sites for the following conditions:

II.3.1.	DA Metering Verification

II.3.1.1.	Check for proof of DA meter certification or meter types that meet the CPUC requirements for Direct Access.

II.3.1.2. Verify for correct customer and customer account (records versus meters) including billing constant, meter number, accuracy test results, customer information, address, etc.

II.3.1.3. Verify for correct meter for  service characteristics (voltage, form, etc.).

II.3.2.	DA Communication Verification:

II.3.2.1.	Verify for correct phone or other communication devices and connections if remote read

II.3.2.2.	Verify for successful communication handshakes and data retrieval if remote read (This can be done by another person at a remote location, and data accuracy is not verified at this time).

II.3.2.3.	Verify for successful meter reading if manual read.

II.3.3.	Transformer-rated Meter Sites:

II.3.3.1.	Billing Constant: Compare between records versus sites (CT’s/PT’s ratios).

II.3.3.2.	Improper Wiring: Shorted current by-pass links, reverse current secondary wired, unmatched voltage and current circuits, pinched or rubbed secondary wires near panel hinges.

II.3.4.	Pole-mounted Meter Sites

II.3.4.1.	Cutouts: Open cutouts, blown triple link fuses.

II.3.4.2.	Grounding: Grounding electrode conductors and connections shall not be broken at any point between the service equipment  enclosure and the ground rods, or other approved grounding electrode.

II.3.5.	Pad-mounted Meter Sites:

II.3.5.1. Cabinet Safety

II.3.5.1.1.	Insure secondary non-polarity neutral points and meter enclosure/pedestal electrically connected to ground bus.

II.3.5.1.2.	Electrical connections secure and properly made.

II.3.6.	Grounding:

PG&E, SCE, and SDG&E have three phase services with ground connection on one of the phases.  In situations where A, B, or C, phase is not grounded and there is a voltage reading at or near zero volts on any phase and reading above zero volts on any other phases, this hazard shall be reported to the UDC immediately for emergency corrections and the customer or customer’s representative shall be contacted to inform them of the hazardous conditions.  If it is unclear whether a phase is intentionally grounded, the local UDC shall be contacted to clarify the configuration of the service.  Additionally, extreme caution must be taken on primary (above 600V), 480V phase-to-phase or 277V phase-to-ground service.

II.3.7.	Clock Load:

Calculate and record customer's load at time of arrival.

### II.3.8.	Customer’s Ground Fault Protection Device

Check for the existence of a ground fault protection device or equipment in customer’s electrical panel or switchboard.  The purpose of this verification is to ensure that meter workers, while performing meter work on a customer’s three phase, 4-wire wye metering installation, do not inadvertently cause an unscheduled interruption on this service.

# II.3.8.1.	Background

According to the National Electrical Code, Article 230-95, ground-fault protection shall be provided for solidly ground wye electrical services of more than 150 volts to ground, but not exceeding 600 volts phase-to-phase for each service disconnecting means rated 1000 amperes or more.  The proper operation of some ground-fault detection systems requires a single neutral-ground point which can be established by connecting the neutral, the equipment grounding conductors and the service equipment enclosures.  Even though this protection is mandatory on all new 1000 ampere 277/480 volt services, some customers may have installed it on lower voltage and amperage of a 4-wire wye service.  Therefore, meter workers must follow the procedures below to avoid unscheduled service interruption while performing meter work on 4-wire wye metering installations.

# II.3.8.2.	Procedures

II.3.8.2.1.	Visual check:

Prior to performing meter work, visually inspect for the existence of a ground fault protection device in customer’s panel, switchboard or electrical facilities.  Note: One of the most sensitive ground fault protection devices is the GTE-Sylvania Zinsco Model GTS-3 relay.  A silicon control rectifier (SCR) in this relay could be triggered by transients generated simply by opening or closing the by-pass potential switch.

II.3.8.2.2.	Actions:

If a ground fault protection device is found, the meter worker must contact the customer and request that the customer’s representative render the ground-fault relay inoperative or be present to witness the meter work performed.

II.3.9.	PT/CT Secondary Wiring

Secondary wiring shall be verified for correct wiring and no sign of tampering, and PT’s and CT’s shall be checked for normal operating conditions.  If abnormal conditions exist, responsible ESP and UDC serving the customers shall be notified within 24 hours for their corrective actions.

II.4.	Meter Install

###### Below are the required procedures that a meter worker must follow when installing and/or removing meters.  These procedures do not necessarily include all procedures of a meter installation.

# II.4.1. 	Pre-Installation

# II.4.1.1.	Verify that the location corresponds to the address provided on the work order. If necessary, notify customer of meter installation.

II.4.1.2.	Verify type and size of metering is appropriate for site.

II.4.1.3.	Look for and identify electrical and physical hazards that may be present at the site. Hazards shall be corrected immediately.

II.4.1.4.	Inspect for unsafe conditions at the customer’s premises. If any unsafe condition exists, take necessary action to correct it.

II.4.1.5.	Look for a life-support seal and/or sticker.  If such life-support device exists, notify customer and obtain customer’s consent prior to performing work.

II.4.1.6.	Comply with CAL OSHA requirements.

###### I.4.2.	Self Contained Meters

###### II.4.2.1.	Take closing read on existing meter.

II.4.2.2.	Verify meter information: form, voltage, meter number.

###### II.4.2.3.	For meters with no bypass, the load shall be disconnected before replacing the meter.

II.4.2.4.	For meters with a bypass, the meter shall be bypassed and de-energized, if possible, before replacing the meter.

II.4.2.5.	Open test block cover.

II.4.2.6.	Verify voltage.

II.4.2.7.	Verify 0 volts between line and load side of test blocks.

II.4.2.8.	Install test-by-pass jumper.

II.4.2.9.	Open center bolts on test block..

II.4.2.10.	Remove meter.

II.4.2.11.	Install new meter.

II.4.2.12.	Use approved locking device.

II.4.2.13.	Close center bolts on test blocks.

II.4.2.14.	Remove jumpers.

II.4.2.15.	Reseal test block cover.

II.4.2.16.	Take initial meter read.

II.4.3.	Transformer Rated Meters (CT Meter)

###### II.4.3.1.	Take closing read on existing meter read.

II.4.3.2.	Verify meter information: form, voltage, constant, meter number.

###### II.4.3.3.	Verify if meter is supplying customer with pulses (i.e. isolation relay).

II.4.3.4.	Open test switch cover and verify voltages at the test switch.

II.4.3.5.	If metering site is less than 600 V, open CT compartment and verify ratio of CT’s against meter constant.

II.4.3.6.	Verify wiring from CT compartment to test switch.

II.4.3.7.	Verify wiring from test switch to meter socket.

II.4.3.8.	Operate test switch/test block to de-energize meter sockets.

II.4.3.9.	Remove meter.

II.4.3.10.	Install new meter.

II.4.3.11.	Apply approved locking device on meter.

II.4.3.12.	Close voltage switches on test switch.

II.4.3.13.	Verify meter is programmed.

II.4.3.14.	Closed current switches and verify rotation.

II.4.3.15.	Re-seal CT compartment and test switch.

II.4.3.16.	Take initial meter read

###### II.4.4.	Meter Installation at New Sites

Installations of meters on newly-constructed premises that customers have decided, prior to service connections, to sign up for Direct Access service.  Because there are many UDC’s new business processes (including customer contacts, engineering, estimating, constructions of line, transformers and service wires, and service connections) that need to be coordinated, these meter installations must also be coordinated accordingly to assure safety.  Therefore, ESPs and MSPs must contact the responsible UDC to schedule for such installation.  (Submitted by PG&E)

# II.4.5.	Locking Device

Insure appropriate locking device is in place.