Communications for Meter-Specific Services

Jim Price, ORA, 10/14/98

PSWG has recommended:

- For any new transactions between MDMAs and market participants, the preferred method is EDI.

- For electronic communications concerning Meter-Specific Information Flows, such as those described in the October 15, 1997, report to the CPUC, the preferred method is EDI.

This applies to a number of transactions:

| Possible EDI Transactions | Possible Non-EDI Transactions |
| --- | --- |
| Meter Configuration Data Response (info needed in DASR process for ESP to perform MDMA and meter maintenance functions, and identify needs for meter replacement - to date, 814 development has assumed load profile customer) | Meter Numbers & Characteristics |
| Meter Investigation (info needed for meter replacement - same as above?) |  |
| Installation Scheduling | Meter Return Manifest |
| Meter Installation/ Removal Notification | Meter Return Receipt (EDI may be useful) |
| Report of Abnormal Site Conditions | Report of Hazardous Conditions |
| Report of Changed Site Conditions |  |
| Report of Changed Meter Configuration | Password Management |
| Results of Meter Test |  |
| Report of Meter-related Usage Adjustment | Energy Diversion |

MCDR = Meter Configuration Data Response (Meter Investigation?)

Sched = Installation Scheduling

MIRN = Meter Installation/ Removal Notification, Report of Changed Meter Configuration

Site = Report of Abnormal Site Conditions, Report of Changed Site Conditions

Test = Report of Test Results

Usage = Report of Meter-related Usage Adjustment

| No |  | Title | Description | X12 | MCDR | Sched | MIRN | Site | Test | Usage |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Header Information |  |  |  |  |  |  |  |  |  |  |
| 1a |  | UDC and reference number | The UDC area where the meter(s) is to be installed as follows: PG&E: Pacific Gas and Electric Company SCE: Southern California Edison SDG&E: San Diego Gas and Electric SP: Sierra Pacific | N1*8S | Ö | Ö | Ö | Ö | Ö | Ö |
| 1b |  | Original Transaction # | Direct Access Service Request number or other EDI transaction number | BGN06 | Ö | Ö | Ö |  |  |  |
| 1c |  | Additional Reference # | Order number for PG&E. Meter Investigation (MI) number for SCE. | REF*TN |  |  |  |  |  |  |
| 2 |  | Service Delivery Point Identifier (Future) |  | REF*LU | Ö | Ö | Ö | Ö | Ö | Ö |
| 3 |  | Meter Activity | The type of the meter work performed as follows: Change: Removing and setting a meter at the same time. Set: Setting a meter at a site for the first time. Remove: Removing a meter without installing another meter. Config. Chg: | HL03 |  | Ö | Ö | Ö | Ö | Ö |
| 4 |  | Event Date | Date that the meter work occurred. | DTM07 |  |  | Ö | Ö | Ö | Ö |
| 5 |  | Event Time | Time that the meter work occurred. In the case of a customer going DA, enter the time that the new meter is set. | DTM07 |  |  | Ö |  | Ö | Ö |
| 6a |  | ESP Name | Name of the Energy Service Provider. | N1*SJ | Ö | Ö | Ö | Ö | Ö | Ö |
| 6b |  | ESP Contact Name | Name of the Energy Service Provider’s contact person. | PER02 |  |  |  |  |  |  |
| 6c |  | ESP Contact Phone | Phone number of the Energy Service Provider’s contact person. | PER04 |  |  |  |  |  |  |
| 6d |  | ESP Contact E-mail | E-mail address of the Energy Service Provider’s contact person. | PER04 |  |  |  |  |  |  |
| 7 |  | MSP Name | Name of the Meter Service Provider. | N1*28,H8 |  | Ö | Ö | Ö | Ö | Ö |
| 8 |  | UDC Account Number | UDC account number for the customer and site. | N1*8R | Ö | Ö | Ö | Ö | Ö | Ö |
| 9 |  | Service Address | Address of the metering site. | N301 |  |  | Ö | Ö |  |  |
| 10 |  | City | City in which the metering site is located. | N401 |  |  | Ö | Ö |  |  |
| 11 |  | Customer Name | Name of the customer responsible for the account. | N1*8R |  |  | Ö | Ö |  |  |
| 12 |  | Business Name | Business name of the account, if different from customer name. | N201 |  |  | Ö | Ö |  |  |
| Meter Information (As Found and As Left) |  |  |  |  |  |  |  |  |  |  |
| 21A |  | As Found Meter Number | UDC number for old meter. (AEP Number or UDC meter number) | REF*46 |  | Ö | Ö |  |  |  |
| 21B |  | As Left Meter Number | Meter number for new or existing meter. (AEP Number or UDC meter number) | REF*MG | Ö |  | Ö | Ö | Ö | Ö |
| 23A |  | As Found RKVA Meter Number | Any old associated RKVA/Demand meter number that is separate from the watthour meter; where applicable |  |  |  | Ö |  |  |  |
| 23B |  | As Left RKVA Meter Number | Any new or existing associated RKVA/Demand meter number that is separate from the watthour meter. |  | Ö |  | Ö |  | Ö |  |
| 24A |  | As Found External Recorder Number | Number used to identify a separate recorder or meter/recorder for an old meter/recorder. You can find this information on the recorder’s plate. |  |  |  | Ö |  |  |  |
| 24B |  | As Left External Recorder Number | Number used to identify a separate recorder or meter/recorder for a new or existing set. You can find this information on the recorder’s plate. Separate recorders are not common in DA metering. |  | Ö |  | Ö |  | Ö |  |
| 32 |  | Meter Date | Internal meter date when the meter is installed/removed. | DTM*230 | Ö | Ö | Ö |  | Ö |  |
| 33 |  | Meter Time | Internal meter time when the installation/removal is completed. | DTM*230 |  |  | Ö |  |  |  |
| 34 |  | Total Kwh Read | Total Kwh read of the meter at the time of installation/removal. | MEA03 (MEA04 = KH) |  |  | Ö |  | Ö | Ö |
| 35 |  | Total Kw Read | Total demand read of the meter at the time of installation/removal. | MEA03 (MEA04 = K1) |  |  | Ö |  | Ö | Ö |
| 36 | Total Reactive Read (RKVA) |  | Total RKVA reactive read of the meter at the time of installation/removal. | MEA03 (MEA04 = K2) |  |  | Ö |  | Ö | Ö |
| 37 to 56 | TOU Read |  | Time of Use read of the meter at the time of installation/removal. | MEA03 (MEA07 = 42 etc.) |  |  | Ö |  | Ö | Ö |
| New or Change Meter & Site Configuration |  |  |  |  |  |  |  |  |  |  |
| Meter Config |  |  |  |  |  |  |  |  |  |  |
| 61 | Manufacturer |  | Manufacturer of the meter. Included in AEP code. | NM1*MF | Ö | Ö | Ö |  | Ö |  |
| 62 | Model/Mtr Type |  | Meter or recorder type listed on the plate. Included in AEP code. | REF*MJ | Ö | Ö 1 | Ö |  | Ö |  |
| 62a | AEP standard code Prefix |  | American Electric Power code identifies service type and manufacturer (3 character code). AEP code indicates Form, Wires, Phase, Volts, Test Amps, and Kh. |  | Ö |  | Ö |  | Ö |  |
| 63 | Model/Recorder Type |  |  |  | Ö | Ö 1 | Ö |  | Ö |  |
| 64 | Form |  | Meter Form that contains condensed meter information for the meter. Included in AEP code. | REF*FQ | Ö |  | Ö |  | Ö |  |
| 65 | Meter Class |  | Class of the meter or recorder. Meter rating in Amps. | MEA03 (MEA02 = QC) | Ö |  | Ö |  | Ö |  |
| 66 | Meter Voltage |  | Voltage of the meter. Note if auto ranging. | MEA03 (MEA02 = VO) | Ö |  | Ö |  | Ö |  |
| 67 | Test Amps |  | Amps at which the meter is calibrated. Included in AEP code | MEA03 (MEA02 = B1) | Ö |  | Ö |  | Ö |  |
| Solid State |  |  |  |  |  |  |  |  |  |  |
| 70 | Register Type |  | The type of register designated by the manufacturer that the meter uses to record and store energy usage. | REF*DM | Ö | Ö 1 | Ö |  | Ö |  |
| 71 | Optical port (Y/N) |  | Asks whether or not the meter has an optical port that allows for communication with the meter and another device. Answer Yes (Y) or No (N). | YNQ02 (YNQ09 = OPT) | Ö |  | Ö |  |  |  |
| 72 | Radio communicate (Y/N) |  | Asks whether or not the meter has a radio communicator that passes data through radio waves. Answer Yes (Y) or No (N). | YNQ02 (YNQ09 = RADIO) | Ö |  | Ö |  |  |  |
| 73 | Number of Display Segments |  |  |  | Ö |  | Ö |  | Ö |  |
| 74 | Pgm ID name |  | Software program name with which the meter is programmed. | REF*S3 | Ö |  | Ö |  | Ö |  |
| 75 | Meter Ke3 |  | The Ke value is the programmed weighted value of the meter/recorder pulse in watthours found in the meter software. (watthours per pulse) Ke Value Formula: Pulse Constant / Billing Constant x 1000 = Ke | MEA03 (MEA02 = T3) | Ö |  | Ö |  | Ö |  |
| 76 | Pulse Multiplier |  | The factor used to convert pulses of energy to kilowatt usage per hour (also known as the pulse constant). Formula (for meters with Ke values): Billing Constant x Ke / 1000 = Pulse Multiplier | MEA03 (MEA02 = ??) | Ö |  | Ö |  | Ö |  |
| Mechanical |  |  |  |  |  |  |  |  |  |  |
| 80 | Number of Dials |  | Number of dials (or segments) of the meter. | REF*IX | Ö |  | Ö |  | Ö |  |
| 81 | Meter Kh3 |  | The Kh value is the number of watthours per disk revolution. | MEA03 (MEA02 = UG) | Ö |  | Ö |  | Ö |  |
| 82 | Dial K (Rgstr Cnstnt) |  | Billing constant used on self-contained meters, applied to meter display to obtain correct values. This is usually 1, but for extended-range meters use 10. | MEA03 (MEA02 = RR) | Ö |  | Ö |  | Ö |  |
| 83 | Register Ratio |  | Register ratio of the meter. | MEA03 (MEA02 = RY) | Ö |  | Ö |  | Ö |  |
| 84 | Billing Constant |  | The factor multiplied by the monthly meter usage to obtain the true kilowatt hour usage. Formula: CT Ratio x PT Ratio x DK = Billing Constant | MEA03 (MEA02 = MU) | Ö |  | Ö |  | Ö |  |
| 85 | KYZ Output (External) 3 |  | Number of disk revolutions per output pulse of external pulse output. | MEA03 (MEA02 = PH) | Ö |  | Ö |  | Ö |  |
| Meter Capability (# of dials, # of decimals) |  |  |  |  |  |  |  |  |  |  |
|  | kWh |  | Unit of measure in kilowatthours (1000 wtthours). |  | Ö |  |  |  | Ö |  |
|  | kW |  | Unit of measure in kilowatts (1000 watts) (Demand). |  | Ö |  |  |  | Ö |  |
|  | kVARh |  | Unit of measure in kilovolt ampere hours reactive. |  | Ö |  |  |  | Ö |  |
|  | kVAR |  | Unit of measure in kilovolt amperes reactive (Reactive Demand). |  | Ö |  |  |  | Ö |  |
| Demand Data |  |  |  |  |  |  |  |  |  |  |
| Demand is the measured energy usage over a specified interval of time divided by that interval of time. |  |  |  |  |  |  |  |  |  |  |
|  | Interval length |  | The time increment, in minutes, used to record demand data; for example, energy usage may be recorded every 5, 15, or 30 minutes. |  | Ö |  |  |  | Ö |  |
|  | Full Scale Maximum Read |  | The highest capacity of the meter to measure demand. Show the demand. | MEA03 (MEA02 = F3) | Ö |  |  |  | Ö |  |
| TOU Reads for the following rate periods |  |  |  |  |  |  |  |  |  |  |
| Enter the Time of Use time periods for the meter readings by kilowatthours (kWh) and kilowatts (kW) as follows: (Being Investigated; Possibly Backend) |  |  |  |  |  |  |  |  |  |  |
|  | On |  | On peak time period. |  | Ö |  |  |  | Ö |  |
|  | Off |  | Off peak time period. |  | Ö |  |  |  | Ö |  |
|  | Mid |  |  |  | Ö |  |  |  | Ö |  |
|  | Super Off |  |  |  | Ö |  |  |  | Ö |  |
| IDR (Interval Data Recorder) |  |  |  |  |  |  |  |  |  |  |
|  | Interval Data |  | Energy usage. | YNQ02 (YNQ09 = IDR) | Ö |  |  |  | Ö |  |
|  | # of Channels |  | The number of channels on the recorder. | MEA03 (MEA02 = NA) | Ö |  |  |  | Ö |  |
|  | Interval Length |  | The time increment, in minutes, used to record interval data; for example, energy usage may be recorded every 5, 15, or 30 minutes. | REF*MT | Ö |  |  |  | Ö |  |
|  | Memory Size (K) |  | The memory size of the meter/ recorder in kilobytes (thousands). | MEA03 (MEA02 = NOR) | Ö |  |  |  | Ö |  |
| Site Info |  |  |  |  |  |  |  |  |  |  |
| 90 | Phase |  | Number of phases of the service and/or meter. | MEA03 (MEA02 = 36) | Ö |  | Ö |  | Ö |  |
| 91 | Number of Wires |  | Number of wires of the service and/or meter. | MEA03 (MEA02 = 35) | Ö |  | Ö |  | Ö |  |
| 92 | Delta/Wye |  | Transformer configuration of the service. - For 3 phase/3 wire, use Delta - For 3 phase/4 wire, use Delta or Wye (choose the appropriate configuration) - Wye is the same as Star. | REF*QB | Ö |  | Ö |  | Ö |  |
| 93 | Service Voltage |  | Voltage of the meter site. | MEA03 (MEA02 = VSO) | Ö |  | Ö |  | Ö |  |
| 94 | CT Quantity3 |  | The number of CTs associated with the meter at the site. | MEA03 (MEA02 = NC) | Ö |  | Ö |  | Ö |  |
| 95 | CT Ratio3 |  | The CT Ratio (Current Transformer Ratio) is the ratio between primary and secondary current. Formula (5-to-1 Ratio): CT Amps / 5 = CT Ratio | MEA03 (MEA02 = OG) | Ö |  | Ö |  | Ö |  |
| 96 | PT Quantity3 |  | The number of PTs associated with the meter at the site. | MEA03 (MEA02 = NB) | Ö |  | Ö |  | Ö |  |
| 97 | PT Ratio3 |  | The PT Ratio (Potential Transformer Ratio) is the ratio between primary and secondary voltage. Formula (120-to-1 Ratio): PT Volts Primary / 120 = PT Ratio | MEA03 (MEA02 = OF) | Ö |  | Ö |  | Ö |  |
| Com Info |  |  |  |  |  |  |  |  |  |  |
| 100 | Meter Com. Telephone # |  | The remote telephone number attached to the meter or recorder used to upload meter site information. | COM02 | Ö |  | Ö |  | Ö |  |
| 101 | Internal Meter ID |  | Internal meter identifier (also known as the Device ID). | REF*SE | Ö |  | Ö |  | Ö |  |
| 102 | Remarks |  | Any remarks about the condition of the meter or meter site. | MTX02 | Ö |  | Ö | Ö | Ö | Ö |

In the context of scheduling, designation of meter, recorder, and register types should be understood to include the phrase “or equivalent”.