| No |  | Title | Description |
| --- | --- | --- | --- |
| Header Information |  |  |  |
| 1 |  | UDC and reference number | Order number for PG&E. Meter Investigation (MI) number for SCE. Direct Access Service Request number for SDG&E. Direct Access Service Request number for SP. |
| 2 |  | Service Delivery Point Identifier (Future) |  |
| 3 |  | Meter Activity | The type of the meter work performed as follows: Change: Removing and setting a meter at the same time. Set: Setting a meter at a site for the first time. Remove: Removing a meter without installing another meter. Config. Chg: |
| 4 |  | Event Date | Date that the meter work occurred. |
| 5 |  | Event Time | Time that the meter work occurred. In the case of a customer going DA, enter the time that the new meter is set. |
| 6 |  | ESP Name | Name of the Energy Service Provider. |
| 7 |  | MSP Name | Name of the Meter Service Provider. |
| 8 |  | UDC Account Number | UDC account number for the customer and site. |
| 9 |  | Service Address | Address of the metering site. |
| 10 |  | City | City in which the metering site is located. |
| 11 |  | Customer Name | Name of the customer responsible for the account. |
| 12 |  | Business Name | Business name of the account, if different from customer name. |
| Meter Information (As Found and As Left) |  |  |  |
| 21A |  | As Found Meter Number | UDC number for old meter. (AEP Number or UDC meter number) |
| 21B |  | As Left Meter Number | Meter number for new meter. (AEP Number or UDC meter number) |
| 23A |  | As Found RKVA Meter Number | Any old associated RKVA/Demand meter number that is separate from the watthour meter; where applicable |
| 23B |  | As Left RKVA Meter Number | Any new associated RKVA/Demand meter number that is separate from the watthour meter. |
| 24A |  | As Found External Recorder Number | Number used to identify a separate recorder or meter/recorder for an old meter/recorder. You can find this information on the recorder’s plate. |
| 24B |  | As Left External Recorder Number | Number used to identify a separate recorder or meter/recorder for a new set. You can find this information on the recorder’s plate. Separate recorders are not common in DA metering. |
| 32 |  | Meter Date | Internal meter date when the meter is installed/removed. |
| 33 |  | Meter Time | Internal meter time when the installation/removal is completed. |
| 34 |  | Total Kwh Read | Total Kwh read of the meter at the time of installation/removal. |
| 35 |  | Total Kw Read | Total demand read of the meter at the time of installation/removal. |
| 36 | Total Reactive Read (RKVA) |  | Total RKVA reactive read of the meter at the time of installation/removal. |
| 37 | TOU Read |  | Time of Use read of the meter at the time of installation/removal. |

| No |  | Title | Description |
| --- | --- | --- | --- |
| New or Change Meter & Site Configuration |  |  |  |
| Meter Config |  |  |  |
| 61 | Manufacturer |  | Manufacturer of the meter. Included in AEP code. |
| 62 | Model/Mtr Type |  | Meter or recorder type listed on the plate. Included in AEP code. |
| 63 | Model/Recorder Type |  |  |
| 64 | Form |  | Meter Form that contains condense meter information for the new meter. Included in AEP code. |
| 65 | Meter Class |  | Class of the meter or recorder. |
| 66 | Meter Voltage |  | Voltage of the meter. |
| 67 | Test Amps |  | Amps at which the meter is calibrated. Included in AEP code |
| Solid State |  |  |  |
| 70 | Register Type |  |  |
| 71 | Optical port (Y/N) |  | Asks whether or not the meter has an optical port that allows for communication with the meter and another device. Answer Yes (Y) or No (N). |
| 72 | Radio communicate (Y/N) |  | Asks whether or not the meter has a radio communicator that passes data through radio waves. Answer Yes (Y) or No (N). |
| 73 | Number of Display Segments |  |  |
| 74 | Pgm ID name |  | Software program name with which the meter is programmed. |
| 75 | Meter Ke3 |  | The Ke value is the programmed weighted value of the meter/recorder pulse in watthours found in the meter software. Ke Value Formula: Pulse Constant / Billing Constant x 1000 = Ke |
| 76 | Pulse Multiplier |  | The factor used to convert pulses of energy to kilowatt usage per hour (also known as the pulse constant). Formula (for meters with Ke values): Billing Constant x Ke / 1000 = Pulse Multiplier |
| Mechanical |  |  |  |
| 80 | Number of Dials |  | Number of dials (or segments) of the meter. |
| 81 | Meter Kh3 |  | The Kh value is the number of watthours per disk revolution. |
| 82 | Dial K (Rgstr Cnstnt) |  | Billing constant used on self-contained meters. This is usually 1, but for extended-range meters use 10. |
| 83 | Register Ratio |  | Register ratio of the meter. |
| 84 | Billing Constant |  | The factor multiplied by the monthly meter usage to obtain the true kilowatt hour usage. Formula: CT Ratio x PT Ratio x DK = Billing Constant |
| 85 | KYZ Output (External) 3 |  | Number of disk revolutions per output pulse of external pulse output. |

| No | Title | Description |
| --- | --- | --- |
| Site Info |  |  |
| 90 | Phase | Number of phases of the service and/or meter. |
| 91 | Number of Wires | Number of wires of the service and/or meter. |
| 92 | Delta/Wye | Transformer configuration of the service. - For 3 phase/3 wire, use Delta - For 3 phase/4 wire, use Delta or Wye (choose the appropriate configuration) - Wye is the same as Star. |
| - 93 | Service Voltage | Voltage of the meter site. |
| 94 | CT Quantity3 | The number of CTs associated with the meter at the site. |
| 95 | CT Ratio3 | The CT Ratio (Current Transformer Ratio) is the ratio between primary and secondary current. Formula (5-to-1 Ratio): CT Amps / 5 = CT Ratio |
| 96 | PT Quantity3 | The number of PTs associated with the meter at the site. |
| 97 | PT Ratio3 | The PT Ratio (Potential Transformer Ratio) is the ratio between primary and secondary voltage. Formula (120-to-1 Ratio): PT Volts Primary / 120 = PT Ratio |
| Com Info |  |  |
| 100 | Meter Com. Telephone # | The remote telephone number attached to the meter or recorder used to upload meter site information. |
| 101 | Internal Meter ID | Internal meter identifier (also known as the Device ID). |
| 102 | Remarks | Any remarks about the condition of the meter or meter site. |